## Cover
QUALITY PATH UNPLANNED SAIDI/SAIFI MODEL
Final
2020-05-12
Document information
Author: | Aurora Energy | Commission note: These unplanned SAIDI and SAIFI forecasts were provided with Aurora's CPP proposal on 12 June. Following this, Aurora provided alternative forecast of its unplanned SAIDI and SAIFI on 23 July 2020 for our consideration, which we have also published on our website.
Created: | Michael Kean
Last updated: | 2020-05-12
Status: | Final

## Approach
Purpose
This model projects total network unplanned SAIDI and SAIFI for the period RY2021 - 2026.
a) the historical trends in reliability statistics
b) back-cast and projected asset unit quantities in each sub-network per fleet
Forecasting Approach
The forecast consists of equipment deterioration, vegetation and all other "non-asset" related interruptions (i.e. weather, human interferance and unknown cause types).
Equipment Deterioration
The equipment deterioration compoment of the forecast is based on the relationship between observed statistics for reliability and assumed asset health using age as a proxy indicator for condition. The RY2020 base-year of was projected forwards and back-cast to provide a means to infer changes in asset health that might influence asset failure using a generalized linear model. The model selected regressed consumer counts associated with the failure of assets in health grades H1 and H2, as well as the change in the volume of assets year on year in H3. It was also necessary to center the distribution of asset health volumes (i.e. mean=0, stdev=1) to remove the imbalance between the number of assets in each grade. The model was run in Python, and the code has been provided in the file named "equip_deterioration_v_1.1.py"
Vegetation
This cateogry was modelled by stepping down the 3-year average from RY2018-RY2020 to a target average value for SAIFI of 0.2 interruptions per annum
Non-Asset
The remainder of fault interruptions was modelled using a simple 3-year average for RY2018 - RY202.
Structure
Workbook colour coding
Input worksheets are
Model worksheets are |  | NOT USED
Output worksheets are
Worksheet structure
Direct input cells are: |  | NOT USED
Inputs from other model outputs
Worksheet Type | Worksheets | Description
Input | Histrocial Fault Information | Actual reliability statistics for unplanned interruptions (Raw & Normalised)
Input | Total ICPs | Actual and forecast ICP volumes
Input | Normalisation Scaling | Factors used to adjust the raw forecast to represent expected furture reported annual totals for SAIDI and SAIFI
Input | Model Inputs | Prpprocessing output dataframe used in the GLM wihtin the python code (equip_deterioration_v1.1.py)
Input | Asset Health Quantities | Projected and back-cast fleet volumes RY2014 - RY2026.
Output | Summary Output | Output sheet
End

## Historical Fault Information
Unplanned
Historical SAIDI Data
| SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIDI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI | SAIFI
Historical Actuals
Network Region | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Non-Normalised | 57.3116 | 61.3853 | 94.6748 | 131.406 | 52.9091 | 71.0814 | 105.7618 | 198.6806 | 107.1067 | 117.9813 | 168.0007 | 161.3215 | 1.3715 | 1.2829 | 1.3671 | 1.5525 | 1.7464 | 0.97464 | 1.2568 | 1.4332 | 2.2507 | 1.416 | 2.416 | 1.8908 | 1.9504
Normalised | 57.3116 | 61.3853 | 94.1198 | 104.4118 | 52.9091 | 71.0814 | 105.7618 | 108.3143 | 77.38 | 108.463 | 108.34 | 132.0349 | 1.3715 | 1.2829 | 1.3671 | 1.5525 | 1.7464 | 0.97464 | 1.2568 | 1.4332 | 1.8916 | 1.3574 | 2.3235 | 1.7539 | 1.8131

## Total ICPs
ICP Forecast
ICPs - Total
| Actual | [11 empty] | Forecast
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Total Customers | 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222
Used for ID | 310941 | 314565 | 316453 | 318388 | 319987 | 322126 | 324692 | 327394 | 330714 | 333925
ICPs - By Region
| Actual | [11 empty] | Forecast - Scaled to match historical ID ICP numbers
Aurora Network | 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Dunedin | 52598 | 52962 | 53254 | 53514 | 53699 | 53861.5 | 53985.5 | 54227 | 54476.5 | 54675 | 55017.5 | 55332 | 55660.5 | 55982 | 56307 | 56630.25 | 56954.375 | 57278.0625 | 57601.9688 | 57925.7656 | 58249.6172 | 58573.4414 | 58897.2793 | 59221.1104 | 59544.9448 | 59868.7776 | 60192.6112 | 60516.4444
Central Otago | 26439 | 27241 | 27824 | 28404.5 | 28879.5 | 29349.5 | 29930 | 30615.5 | 31374.5 | 32291 | 33369 | 34371 | 35411 | 36432 | 37462.5 | 38488.25 | 39516.375 | 40543.3125 | 41570.8438 | 42598.0781 | 43625.4609 | 44652.7695 | 45680.1152 | 46707.4424 | 47734.7788 | 48762.1106 | 49789.4447 | 50816.7776
ChkSum | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Growth Rates
Planning Area | [12 empty] | RY20 | RY21 | RY22 | RY23 | RY24 | RY25 | RY26 | RY27 | RY28 | RY29 | RY30 | RY31 | RY32 | RY33 | RY34 | RY35
Dunedin | [12 empty] | 0.5937% | 0.5776% | 0.5805% | 0.5741% | 0.5724% | 0.5683% | 0.5655% | 0.5621% | 0.5591% | 0.5559% | 0.5529% | 0.5498% | 0.5468% | 0.5438% | 0.5409% | 0.538%
Central Otago | [12 empty] | 3.026% | 2.883% | 2.829% | 2.738% | 2.671% | 2.599% | 2.534% | 2.471% | 2.412% | 2.355% | 2.301% | 2.249% | 2.2% | 2.152% | 2.107% | 2.063%
[5 empty] | Historical actual number of ICPs | [7 empty] | RY27: Forecast number of ICPs
AMP Region | RY08 | RY09 | RY10 | RY11 | RY12 | RY13 | RY14 | RY15 | RY16 | RY17 | RY18 | RY19 | RY20 | RY21 | RY22 | RY23 | RY24 | RY25 | RY26 | RY27 | RY28 | RY29 | RY30 | RY31 | RY32 | RY33 | RY34 | RY35
Dunedin | 52598 | 52962 | 53254 | 53514 | 53699 | 53861.5 | 53985.5 | 54227 | 54476.5 | 54675 | 55017.5 | 55332 | 55660.5 | 55982 | 56307 | 56630.25 | 56954.375 | 57278.0625 | 57601.9688 | 57925.7656 | 58249.6172 | 58573.4414 | 58897.2793 | 59221.1104 | 59544.9448 | 59868.7776 | 60192.6112 | 60516.4444
Central Otago | 26439 | 27241 | 27824 | 28404.5 | 28879.5 | 29349.5 | 29930 | 30615.5 | 31374.5 | 32291 | 33369 | 34371 | 35411 | 36432 | 37462.5 | 38488.25 | 39516.375 | 40543.3125 | 41570.8438 | 42598.0781 | 43625.4609 | 44652.7695 | 45680.1152 | 46707.4424 | 47734.7788 | 48762.1106 | 49789.4447 | 50816.7776
| 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222

## DPP3 Normalisation Scaling
Normalisation Scaling
Total
| SAIDI DPP3 to DPP2 % Reduction | 27.04
| SAIFI DPP3 to DPP2 % Reduction | 7.64
| SAIDI DPP3 Scaler | 0.7296
| SAIFI DPP3 Scaler | 0.9236

## Model Inputs
Fleet | RY | NETWORK | NO_CONSUMERS | NO_CONSUMERS_annual | NO_CONSUMERS_OFFSET | H1 | H2 | H3_diff | FREQ_WEIGHT
Crossarms | 2014 | CEN | 705 | 705 | 1 | 0 | 0 | 0 | 0.5
Crossarms | 2015 | CEN | 1588 | 2376 | 0.66835 | 0 | 0 | 0 | 0.5
Crossarms | 2015 | DUN | 2016 | 2575 | 0.78291 | 0 | 0 | 0 | 0.5
Crossarms | 2016 | CEN | 1116 | 1116 | 1 | 0 | 0 | 0 | 1
Crossarms | 2016 | DUN | 433 | 976 | 0.44365 | 0 | 0 | 0 | 1
Crossarms | 2017 | CEN | 410 | 410 | 1 | 0 | 0 | 0 | 1
Crossarms | 2017 | DUN | 622 | 622 | 1 | 0 | 0 | 0 | 1
Crossarms | 2018 | CEN | 260 | 260 | 1 | 0 | 0 | 0 | 1
Crossarms | 2018 | DUN | 4100 | 4100 | 1 | 0 | 0 | 0 | 1
Crossarms | 2019 | CEN | 1020 | 1020 | 1 | 0 | 0 | 0 | 1
Crossarms | 2019 | DUN | 5760 | 6386 | 0.90197 | 0 | 0 | 0 | 1
Crossarms | 2020 | CEN | 1050 | 1050 | 1 | 0 | 0 | 0 | 1
Crossarms | 2020 | DUN | 1198 | 2175 | 0.5508 | 0 | 0 | 0 | 1
Distribution Conductors | 2014 | CEN | 6574 | 6574 | 1 | -0.4013 | -0.54031 | -0.10979 | 0.5
Distribution Conductors | 2014 | DUN | 630 | 630 | 1 | -0.38593 | -0.51422 | -0.10417 | 0.5
Distribution Conductors | 2015 | CEN | 6631 | 6631 | 1 | -0.39911 | -0.53379 | -0.10979 | 0.5
Distribution Conductors | 2015 | DUN | 3164 | 3164 | 1 | -0.38373 | -0.5077 | -0.10979 | 0.5
Distribution Conductors | 2016 | CEN | 4823 | 5616 | 0.8588 | -0.39691 | -0.53053 | -0.11541 | 1
Distribution Conductors | 2016 | DUN | 4727 | 4727 | 1 | -0.37934 | -0.50118 | -0.10417 | 1
Distribution Conductors | 2017 | CEN | 4135 | 4135 | 1 | -0.39472 | -0.524 | -0.12103 | 1
Distribution Conductors | 2017 | DUN | 1852 | 1852 | 1 | -0.37495 | -0.49466 | -0.10417 | 1
Distribution Conductors | 2018 | CEN | 7985 | 7985 | 1 | -0.39252 | -0.51748 | -0.10979 | 1
Distribution Conductors | 2018 | DUN | 3488 | 5882 | 0.593 | -0.36836 | -0.48487 | -0.10979 | 1
Distribution Conductors | 2019 | CEN | 3159 | 3159 | 1 | -0.38813 | -0.51422 | -0.11541 | 1
Distribution Conductors | 2019 | DUN | 938 | 938 | 1 | -0.36397 | -0.47835 | -0.10417 | 1
Distribution Conductors | 2020 | CEN | 2827 | 2827 | 1 | -0.38813 | -0.51422 | -0.13227 | 1
Distribution Conductors | 2020 | DUN | 4000 | 4709 | 0.84944 | -0.36397 | -0.47835 | -0.13227 | 1
Distribution Transformers | 2014 | CEN | 122 | 122 | 1 | -0.23439 | -0.34791 | -0.08169 | 0.5
Distribution Transformers | 2014 | DUN | 116 | 116 | 1 | -0.32663 | -0.38052 | -0.0086306 | 0.5
Distribution Transformers | 2015 | CEN | 513 | 1307 | 0.3925 | -0.21902 | -0.33161 | -0.07607 | 0.5
Distribution Transformers | 2015 | DUN | 21 | 21 | 1 | -0.31346 | -0.35443 | -0.0086306 | 0.5
Distribution Transformers | 2016 | CEN | 4829 | 4829 | 1 | -0.20365 | -0.3153 | -0.07607 | 1
Distribution Transformers | 2016 | DUN | 270 | 270 | 1 | -0.29808 | -0.32835 | -0.02549 | 1
Distribution Transformers | 2017 | CEN | 1257 | 1257 | 1 | -0.18608 | -0.29574 | -0.07607 | 1
Distribution Transformers | 2017 | DUN | 127 | 127 | 1 | -0.28051 | -0.29574 | -0.014251 | 1
Distribution Transformers | 2018 | CEN | 1462 | 1462 | 1 | -0.16851 | -0.27943 | -0.07607 | 1
Distribution Transformers | 2018 | DUN | 150 | 150 | 1 | -0.26075 | -0.26313 | -0.014251 | 1
Distribution Transformers | 2019 | CEN | 44 | 44 | 1 | -0.14874 | -0.25987 | -0.07607 | 1
Distribution Transformers | 2019 | DUN | 2495 | 2870 | 0.86934 | -0.23879 | -0.22726 | -0.0086306 | 1
Distribution Transformers | 2020 | CEN | 2330 | 2330 | 1 | -0.14874 | -0.25987 | -0.13227 | 1
Distribution Transformers | 2020 | DUN | 95 | 95 | 1 | -0.23879 | -0.22726 | -0.13227 | 1
Ground Mounted Switchgear | 2014 | CEN | 286 | 286 | 1 | -0.42327 | -0.58922 | -0.12665 | 0.5
Ground Mounted Switchgear | 2015 | CEN | 389 | 389 | 1 | -0.42327 | -0.58922 | -0.12665 | 0.5
Ground Mounted Switchgear | 2017 | CEN | 1206 | 1206 | 1 | -0.42327 | -0.58922 | -0.12103 | 1
Ground Mounted Switchgear | 2017 | DUN | 24 | 24 | 1 | -0.26294 | -0.36748 | -0.13789 | 1
Ground Mounted Switchgear | 2018 | DUN | 965 | 965 | 1 | -0.26075 | -0.36748 | -0.13789 | 1
Ground Mounted Switchgear | 2019 | CEN | 2351 | 2351 | 1 | -0.42327 | -0.58596 | -0.12665 | 1
Ground Mounted Switchgear | 2019 | DUN | 196 | 770 | 0.25455 | -0.25196 | -0.36096 | -0.13789 | 1
Ground Mounted Switchgear | 2020 | CEN | 1267 | 1267 | 1 | -0.42327 | -0.58596 | -0.13227 | 1
Ground Mounted Switchgear | 2020 | DUN | 82 | 82 | 1 | -0.25196 | -0.36096 | -0.13227 | 1
Other | 2014 | CEN | 519 | 519 | 1 | 0 | 0 | 0 | 0.5
Other | 2014 | DUN | 258 | 258 | 1 | 0 | 0 | 0 | 0.5
Other | 2015 | CEN | 1038 | 1038 | 1 | 0 | 0 | 0 | 0.5
Other | 2015 | DUN | 2106 | 3766 | 0.55921 | 0 | 0 | 0 | 0.5
Other | 2016 | CEN | 5229 | 5229 | 1 | 0 | 0 | 0 | 1
Other | 2016 | DUN | 5697 | 5697 | 1 | 0 | 0 | 0 | 1
Other | 2017 | CEN | 1249 | 1249 | 1 | 0 | 0 | 0 | 1
Other | 2017 | DUN | 1259 | 1259 | 1 | 0 | 0 | 0 | 1
Other | 2018 | CEN | 2682 | 2682 | 1 | 0 | 0 | 0 | 1
Other | 2018 | DUN | 22261 | 22261 | 1 | 0 | 0 | 0 | 1
Other | 2019 | CEN | 3484 | 4906 | 0.71015 | 0 | 0 | 0 | 1
Other | 2019 | DUN | 9848 | 11202 | 0.87913 | 0 | 0 | 0 | 1
Other | 2020 | CEN | 3235 | 5750 | 0.56261 | 0 | 0 | 0 | 1
Other | 2020 | DUN | 6027 | 6027 | 1 | 0 | 0 | 0 | 1
Pole Mounted Fuses | 2014 | CEN | 81 | 81 | 1 | -0.37715 | -0.52074 | -0.087309 | 0.5
Pole Mounted Fuses | 2014 | DUN | 649 | 649 | 1 | -0.33981 | -0.4327 | -0.01987 | 0.5
Pole Mounted Fuses | 2015 | CEN | 201 | 669 | 0.30045 | -0.37275 | -0.51422 | -0.08169 | 0.5
Pole Mounted Fuses | 2015 | DUN | 819 | 819 | 1 | -0.32663 | -0.40661 | -0.02549 | 0.5
Pole Mounted Fuses | 2016 | CEN | 279 | 279 | 1 | -0.36617 | -0.50444 | -0.07607 | 1
Pole Mounted Fuses | 2016 | DUN | 5217 | 5217 | 1 | -0.30906 | -0.38052 | -0.01987 | 1
Pole Mounted Fuses | 2017 | CEN | 908 | 1314 | 0.69102 | -0.35958 | -0.49466 | -0.07607 | 1
Pole Mounted Fuses | 2017 | DUN | 1235 | 1235 | 1 | -0.29149 | -0.35443 | -0.03111 | 1
Pole Mounted Fuses | 2018 | CEN | 359 | 359 | 1 | -0.35299 | -0.48487 | -0.07045 | 1
Pole Mounted Fuses | 2018 | DUN | 3348 | 3726 | 0.89855 | -0.27392 | -0.32509 | -0.03111 | 1
Pole Mounted Fuses | 2019 | CEN | 561 | 561 | 1 | -0.3442 | -0.47183 | -0.07045 | 1
Pole Mounted Fuses | 2019 | DUN | 2449 | 2907 | 0.84245 | -0.25196 | -0.29574 | -0.03111 | 1
Pole Mounted Fuses | 2020 | CEN | 473 | 1071 | 0.44164 | -0.3442 | -0.47183 | -0.13227 | 1
Pole Mounted Fuses | 2020 | DUN | 1521 | 1953 | 0.7788 | -0.25196 | -0.29574 | -0.13227 | 1
Pole Mounted Switches | 2014 | CEN | 202 | 202 | 1 | -0.4035 | -0.5664 | -0.13789 | 0.5
Pole Mounted Switches | 2014 | DUN | 1591 | 1591 | 1 | -0.28051 | -0.39683 | -0.13227 | 0.5
Pole Mounted Switches | 2015 | CEN | 2859 | 2859 | 1 | -0.4013 | -0.56314 | -0.12665 | 0.5
Pole Mounted Switches | 2015 | DUN | 2 | 2 | 1 | -0.26734 | -0.38704 | -0.14351 | 0.5
Pole Mounted Switches | 2016 | CEN | 869 | 869 | 1 | -0.4013 | -0.56314 | -0.13227 | 1
Pole Mounted Switches | 2016 | DUN | 1890 | 1890 | 1 | -0.25855 | -0.37726 | -0.14351 | 1
Pole Mounted Switches | 2017 | CEN | 3329 | 3329 | 1 | -0.39911 | -0.55987 | -0.12665 | 1
Pole Mounted Switches | 2017 | DUN | 1027 | 3348 | 0.30675 | -0.24537 | -0.37074 | -0.14351 | 1
Pole Mounted Switches | 2018 | CEN | 1884 | 1884 | 1 | -0.39691 | -0.55987 | -0.12665 | 1
Pole Mounted Switches | 2018 | DUN | 2763 | 2763 | 1 | -0.23439 | -0.36096 | -0.13789 | 1
Pole Mounted Switches | 2019 | CEN | 3421 | 3421 | 1 | -0.39472 | -0.55661 | -0.12665 | 1
Pole Mounted Switches | 2019 | DUN | 60 | 60 | 1 | -0.22122 | -0.35443 | -0.14351 | 1
Pole Mounted Switches | 2020 | CEN | 925 | 925 | 1 | -0.39472 | -0.55661 | -0.13227 | 1
Pole Mounted Switches | 2020 | DUN | 296 | 296 | 1 | -0.22122 | -0.35443 | -0.13227 | 1
Poles | 2014 | CEN | 1202 | 1202 | 1 | 0.16751 | 2.1206 | 0.0026092 | 0.5
Poles | 2014 | DUN | 58 | 58 | 1 | 4.1075 | 2.6522 | 0.092528 | 0.5
Poles | 2015 | CEN | 524 | 524 | 1 | 0.18948 | 2.2087 | 0.13187 | 0.5
Poles | 2015 | DUN | 688 | 688 | 1 | 4.2371 | 2.7206 | 0.092528 | 0.5
Poles | 2016 | CEN | 1286 | 1286 | 1 | 0.20046 | 2.2576 | -0.05921 | 1
Poles | 2016 | DUN | 1460 | 1460 | 1 | 4.2854 | 2.7435 | 0.013849 | 1
Poles | 2017 | CEN | 2325 | 3814 | 0.6096 | 0.22022 | 2.3261 | 0.030709 | 1
Poles | 2017 | DUN | 386 | 386 | 1 | 4.3557 | 2.7728 | -0.0030107 | 1
Poles | 2018 | CEN | 4027 | 4505 | 0.8939 | 0.22901 | 2.3489 | -0.21095 | 1
Poles | 2018 | DUN | 217 | 2121 | 0.10231 | 4.314 | 2.7337 | -0.18847 | 1
Poles | 2019 | CEN | 2355 | 2355 | 1 | 0.18948 | 2.1728 | -1.29 | 1
Poles | 2019 | DUN | 77 | 77 | 1 | 3.8527 | 2.4174 | -1.1382 | 1
Poles | 2020 | CEN | 1607 | 1607 | 1 | 0.18948 | 2.1728 | -0.13227 | 1
Poles | 2020 | DUN | 648 | 648 | 1 | 3.8527 | 2.4174 | -0.13227 | 1
Protection | 2014 | CEN | 1657 | 1657 | 1 | 0 | 0 | 0 | 0.5
Protection | 2016 | CEN | 2039 | 2039 | 1 | 0 | 0 | 0 | 1
Protection | 2016 | DUN | 4121 | 4121 | 1 | 0 | 0 | 0 | 1
Protection | 2019 | CEN | 5118 | 5118 | 1 | 0 | 0 | 0 | 1
Protection | 2019 | DUN | 329 | 329 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2014 | CEN | 3436 | 3436 | 1 | 0 | 0 | 0 | 0.5
Subtransmission Conductors | 2015 | CEN | 772 | 772 | 1 | 0 | 0 | 0 | 0.5
Subtransmission Conductors | 2016 | CEN | 1281 | 1281 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2017 | CEN | 3146 | 3146 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2018 | CEN | 2256 | 2256 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2019 | CEN | 4596 | 4596 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2019 | DUN | 329 | 329 | 1 | 0 | 0 | 0 | 1
Subtransmission Conductors | 2020 | CEN | 8922 | 8922 | 1 | 0 | 0 | 0 | 1
Distribution Conductors | 2021 | CEN | 0 | 0 | 0 | -0.37715 | -0.51422 | -0.13227 | 1
Distribution Conductors | 2022 | CEN | 0 | 0 | 0 | -0.37056 | -0.51748 | -0.13227 | 1
Distribution Conductors | 2023 | CEN | 0 | 0 | 0 | -0.36836 | -0.51748 | -0.13227 | 1
Distribution Conductors | 2024 | CEN | 0 | 0 | 0 | -0.36836 | -0.51748 | -0.13227 | 1
Distribution Conductors | 2025 | CEN | 0 | 0 | 0 | -0.37056 | -0.51748 | -0.13227 | 1
Distribution Conductors | 2026 | CEN | 0 | 0 | 0 | -0.37715 | -0.51748 | -0.12665 | 1
Distribution Conductors | 2021 | DUN | 0 | 0 | 0 | -0.35079 | -0.48487 | -0.14351 | 1
Distribution Conductors | 2022 | DUN | 0 | 0 | 0 | -0.3464 | -0.49139 | -0.14351 | 1
Distribution Conductors | 2023 | DUN | 0 | 0 | 0 | -0.3442 | -0.49466 | -0.14351 | 1
Distribution Conductors | 2024 | DUN | 0 | 0 | 0 | -0.3464 | -0.49792 | -0.13789 | 1
Distribution Conductors | 2025 | DUN | 0 | 0 | 0 | -0.35079 | -0.50118 | -0.13789 | 1
Distribution Conductors | 2026 | DUN | 0 | 0 | 0 | -0.35738 | -0.50118 | -0.13227 | 1
Distribution Transformers | 2021 | CEN | 0 | 0 | 0 | -0.10701 | -0.29248 | -0.19409 | 1
Distribution Transformers | 2022 | CEN | 0 | 0 | 0 | -0.091639 | -0.31856 | -0.17723 | 1
Distribution Transformers | 2023 | CEN | 0 | 0 | 0 | -0.10042 | -0.34139 | -0.16037 | 1
Distribution Transformers | 2024 | CEN | 0 | 0 | 0 | -0.12019 | -0.3577 | -0.15475 | 1
Distribution Transformers | 2025 | CEN | 0 | 0 | 0 | -0.14654 | -0.36748 | -0.14913 | 1
Distribution Transformers | 2026 | CEN | 0 | 0 | 0 | -0.17729 | -0.37726 | -0.13227 | 1
Distribution Transformers | 2021 | DUN | 0 | 0 | 0 | -0.18388 | -0.22074 | -0.15475 | 1
Distribution Transformers | 2022 | DUN | 0 | 0 | 0 | -0.15313 | -0.21421 | -0.15475 | 1
Distribution Transformers | 2023 | DUN | 0 | 0 | 0 | -0.14654 | -0.21747 | -0.16037 | 1
Distribution Transformers | 2024 | DUN | 0 | 0 | 0 | -0.15533 | -0.21747 | -0.17723 | 1
Distribution Transformers | 2025 | DUN | 0 | 0 | 0 | -0.17729 | -0.21747 | -0.17723 | 1
Distribution Transformers | 2026 | DUN | 0 | 0 | 0 | -0.19706 | -0.224 | -0.18285 | 1
Ground Mounted Switchgear | 2021 | CEN | 0 | 0 | 0 | -0.42107 | -0.58596 | -0.11541 | 1
Ground Mounted Switchgear | 2022 | CEN | 0 | 0 | 0 | -0.42107 | -0.58922 | -0.10417 | 1
Ground Mounted Switchgear | 2023 | CEN | 0 | 0 | 0 | -0.42107 | -0.59248 | -0.098549 | 1
Ground Mounted Switchgear | 2024 | CEN | 0 | 0 | 0 | -0.42327 | -0.58922 | -0.098549 | 1
Ground Mounted Switchgear | 2025 | CEN | 0 | 0 | 0 | -0.42327 | -0.58596 | -0.092929 | 1
Ground Mounted Switchgear | 2026 | CEN | 0 | 0 | 0 | -0.42107 | -0.5827 | -0.087309 | 1
Ground Mounted Switchgear | 2021 | DUN | 0 | 0 | 0 | -0.25416 | -0.40009 | -0.18847 | 1
Ground Mounted Switchgear | 2022 | DUN | 0 | 0 | 0 | -0.26953 | -0.42944 | -0.17161 | 1
Ground Mounted Switchgear | 2023 | DUN | 0 | 0 | 0 | -0.29808 | -0.44248 | -0.17723 | 1
Ground Mounted Switchgear | 2024 | DUN | 0 | 0 | 0 | -0.33542 | -0.45552 | -0.15475 | 1
Ground Mounted Switchgear | 2025 | DUN | 0 | 0 | 0 | -0.37275 | -0.46857 | -0.16037 | 1
Ground Mounted Switchgear | 2026 | DUN | 0 | 0 | 0 | -0.38154 | -0.47509 | -0.15475 | 1
Pole Mounted Fuses | 2021 | CEN | 0 | 0 | 0 | -0.3486 | -0.47509 | -0.10417 | 1
Pole Mounted Fuses | 2022 | CEN | 0 | 0 | 0 | -0.35518 | -0.47183 | -0.10417 | 1
Pole Mounted Fuses | 2023 | CEN | 0 | 0 | 0 | -0.35958 | -0.46857 | -0.098549 | 1
Pole Mounted Fuses | 2024 | CEN | 0 | 0 | 0 | -0.36177 | -0.46857 | -0.087309 | 1
Pole Mounted Fuses | 2025 | CEN | 0 | 0 | 0 | -0.36617 | -0.46531 | -0.087309 | 1
Pole Mounted Fuses | 2026 | CEN | 0 | 0 | 0 | -0.37056 | -0.45879 | -0.08169 | 1
Pole Mounted Fuses | 2021 | DUN | 0 | 0 | 0 | -0.25635 | -0.28922 | -0.14913 | 1
Pole Mounted Fuses | 2022 | DUN | 0 | 0 | 0 | -0.26075 | -0.28595 | -0.15475 | 1
Pole Mounted Fuses | 2023 | DUN | 0 | 0 | 0 | -0.26514 | -0.28595 | -0.16037 | 1
Pole Mounted Fuses | 2024 | DUN | 0 | 0 | 0 | -0.27173 | -0.28595 | -0.16037 | 1
Pole Mounted Fuses | 2025 | DUN | 0 | 0 | 0 | -0.27832 | -0.28922 | -0.16037 | 1
Pole Mounted Fuses | 2026 | DUN | 0 | 0 | 0 | -0.28491 | -0.29248 | -0.16037 | 1
Pole Mounted Switches | 2021 | CEN | 0 | 0 | 0 | -0.39691 | -0.56314 | -0.13789 | 1
Pole Mounted Switches | 2022 | CEN | 0 | 0 | 0 | -0.39911 | -0.5664 | -0.13789 | 1
Pole Mounted Switches | 2023 | CEN | 0 | 0 | 0 | -0.4013 | -0.56966 | -0.13227 | 1
Pole Mounted Switches | 2024 | CEN | 0 | 0 | 0 | -0.4013 | -0.57292 | -0.12665 | 1
Pole Mounted Switches | 2025 | CEN | 0 | 0 | 0 | -0.4035 | -0.57292 | -0.12665 | 1
Pole Mounted Switches | 2026 | CEN | 0 | 0 | 0 | -0.4035 | -0.57292 | -0.12665 | 1
Pole Mounted Switches | 2021 | DUN | 0 | 0 | 0 | -0.19047 | -0.39683 | -0.23905 | 1
Pole Mounted Switches | 2022 | DUN | 0 | 0 | 0 | -0.20584 | -0.4327 | -0.21657 | 1
Pole Mounted Switches | 2023 | DUN | 0 | 0 | 0 | -0.2322 | -0.46205 | -0.19971 | 1
Pole Mounted Switches | 2024 | DUN | 0 | 0 | 0 | -0.26953 | -0.48487 | -0.18285 | 1
Pole Mounted Switches | 2025 | DUN | 0 | 0 | 0 | -0.30687 | -0.50118 | -0.17723 | 1
Pole Mounted Switches | 2026 | DUN | 0 | 0 | 0 | -0.3464 | -0.51748 | -0.16037 | 1
Poles | 2021 | CEN | 0 | 0 | 0 | 0.25097 | 2.15 | -0.44698 | 1
Poles | 2022 | CEN | 0 | 0 | 0 | 0.32125 | 2.1174 | -0.49194 | 1
Poles | 2023 | CEN | 0 | 0 | 0 | 0.40251 | 2.0782 | -0.51442 | 1
Poles | 2024 | CEN | 0 | 0 | 0 | 0.48377 | 2.0326 | -0.5088 | 1
Poles | 2025 | CEN | 0 | 0 | 0 | 0.46839 | 1.9804 | 11.4223 | 1
Poles | 2026 | CEN | 0 | 0 | 0 | 0.45302 | 1.9217 | 4.3018 | 1
Poles | 2021 | DUN | 0 | 0 | 0 | 2.9743 | 2.1956 | -0.95278 | 1
Poles | 2022 | DUN | 0 | 0 | 0 | 2.1134 | 1.9967 | 0.3117 | 1
Poles | 2023 | DUN | 0 | 0 | 0 | 1.2612 | 1.8793 | 0.99171 | 1
Poles | 2024 | DUN | 0 | 0 | 0 | 0.41788 | 1.6967 | 2.8688 | 1
Poles | 2025 | DUN | 0 | 0 | 0 | 0.36956 | 1.5141 | 0.98047 | 1
Poles | 2026 | DUN | 0 | 0 | 0 | 0.31246 | 1.3804 | 1.2334 | 1

## Asset Heatlh Quantities
Index | Fleet | Subnet | AHI | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Distribution Conductors-AUR | Distribution Conductors | AUR | 1 | 28.5682 | 31.2728 | 34.2537 | 37.4563 | 40.9546 | 44.5495 | 44.5495 | 55.6902 | 61.2308 | 62.4314 | 61.5621 | 58.9127 | 52.7634
Distribution Conductors-AUR | Distribution Conductors | AUR | 2 | 44.0106 | 47.4448 | 51.0795 | 54.9003 | 59.0665 | 63.2 | 63.2 | 60.71 | 58.68 | 57.07 | 55.84 | 54.93 | 54.23
Distribution Conductors-AUR | Distribution Conductors | AUR | 3 | 155.6449 | 163.5955 | 171.2562 | 178.9902 | 187.5471 | 195.53 | 195.53 | 192.44 | 190.24 | 188.78 | 187.91 | 187.59 | 187.76
Distribution Conductors-AUR | Distribution Conductors | AUR | 4 | 254.0266 | 258.5449 | 261.7454 | 264.4965 | 268.7934 | 272.27 | 272.27 | 274.29 | 276.76 | 279.65 | 282.99 | 286.68 | 290.71
Distribution Conductors-AUR | Distribution Conductors | AUR | 5 | 1864.0342 | 1836.3365 | 1808.7346 | 1785.8726 | 1759.7102 | 1731.7078 | 1731.7078 | 1724.1272 | 1720.3465 | 1719.3259 | 1718.9553 | 1719.1446 | 1721.794
Distribution Conductors-DUN | Distribution Conductors | DUN | 1 | 17.8478 | 19.4378 | 21.3753 | 23.4618 | 25.631 | 27.9347 | 27.9347 | 33.959 | 36.1832 | 36.7974 | 36.0016 | 34.0158 | 31.05
Distribution Conductors-DUN | Distribution Conductors | DUN | 2 | 25.7438 | 27.5915 | 29.7928 | 32.1388 | 34.5222 | 36.99 | 36.99 | 34.95 | 33.28 | 31.95 | 30.93 | 30.17 | 29.56
Distribution Conductors-DUN | Distribution Conductors | DUN | 3 | 84.8783 | 89.088 | 93.6341 | 98.5836 | 103.3841 | 108.24 | 108.24 | 105.58 | 103.59 | 102.13 | 101.05 | 100.27 | 99.74
Distribution Conductors-DUN | Distribution Conductors | DUN | 4 | 127.0803 | 130.3202 | 132.8501 | 135.9932 | 138.6457 | 141.2 | 141.2 | 140.67 | 140.11 | 139.5 | 138.83 | 138.06 | 137.18
Distribution Conductors-DUN | Distribution Conductors | DUN | 5 | 508.3938 | 495.5521 | 484.1683 | 470.6868 | 457.1584 | 443.5733 | 443.5733 | 442.7791 | 444.7748 | 447.5606 | 451.1264 | 455.4222 | 460.408
Distribution Conductors-CEN | Distribution Conductors | CEN | 1 | 10.7204 | 11.8349 | 12.8784 | 13.9944 | 15.3236 | 16.6148 | 16.6148 | 21.7312 | 25.0476 | 25.6341 | 25.5605 | 24.8969 | 21.7134
Distribution Conductors-CEN | Distribution Conductors | CEN | 2 | 18.2668 | 19.8532 | 21.2867 | 22.7616 | 24.5443 | 26.21 | 26.21 | 25.76 | 25.4 | 25.12 | 24.91 | 24.76 | 24.67
Distribution Conductors-CEN | Distribution Conductors | CEN | 3 | 70.7666 | 74.5074 | 77.6221 | 80.4067 | 84.163 | 87.29 | 87.29 | 86.86 | 86.65 | 86.65 | 86.86 | 87.32 | 88.02
Distribution Conductors-CEN | Distribution Conductors | CEN | 4 | 126.9463 | 128.2246 | 128.8952 | 128.5033 | 130.1477 | 131.07 | 131.07 | 133.62 | 136.65 | 140.15 | 144.16 | 148.62 | 153.53
Distribution Conductors-CEN | Distribution Conductors | CEN | 5 | 1355.6404 | 1340.7844 | 1324.5663 | 1315.1858 | 1302.5518 | 1288.1346 | 1288.1346 | 1281.3481 | 1275.5717 | 1271.7653 | 1267.8288 | 1263.7224 | 1261.386
Pole Mounted Fuses-AUR | Pole Mounted Fuses | AUR | 1 | 60.1368 | 69.2402 | 79.3455 | 90.4934 | 102.7033 | 116 | 116 | 112 | 107 | 103 | 99 | 94 | 89
Pole Mounted Fuses-AUR | Pole Mounted Fuses | AUR | 2 | 74.944 | 84.8617 | 95.5536 | 107.0022 | 119.1613 | 132 | 132 | 133 | 135 | 136 | 136 | 136 | 137
Pole Mounted Fuses-AUR | Pole Mounted Fuses | AUR | 3 | 333.0611 | 361.4807 | 390.2097 | 419.1386 | 448.072 | 477 | 477 | 479 | 480 | 481 | 484 | 487 | 491
Pole Mounted Fuses-AUR | Pole Mounted Fuses | AUR | 4 | 613.4646 | 635.1184 | 656.9197 | 679.2345 | 702.1075 | 726 | 726 | 739 | 755 | 774 | 794 | 817 | 841
Pole Mounted Fuses-AUR | Pole Mounted Fuses | AUR | 5 | 3862.5839 | 3911.5605 | 4007.98 | 4067.6177 | 4126.8903 | 4221 | 4221 | 4209 | 4195 | 4178 | 4159 | 4138 | 4114
Pole Mounted Fuses-DUN | Pole Mounted Fuses | DUN | 1 | 38.6171 | 45.1939 | 52.5091 | 60.5822 | 69.412 | 79 | 79 | 77 | 75 | 73 | 70 | 67 | 64
Pole Mounted Fuses-DUN | Pole Mounted Fuses | DUN | 2 | 51.4218 | 58.7553 | 66.6208 | 74.9865 | 83.7952 | 93 | 93 | 95 | 96 | 96 | 96 | 95 | 94
Pole Mounted Fuses-DUN | Pole Mounted Fuses | DUN | 3 | 238.9436 | 258.4007 | 277.5746 | 296.3293 | 314.4935 | 332 | 332 | 329 | 325 | 320 | 315 | 310 | 305
Pole Mounted Fuses-DUN | Pole Mounted Fuses | DUN | 4 | 395.7302 | 402.0703 | 407.775 | 413.0445 | 418.0705 | 423 | 423 | 419 | 417 | 416 | 415 | 414 | 413
Pole Mounted Fuses-DUN | Pole Mounted Fuses | DUN | 5 | 1188.1867 | 1183.0984 | 1183.6292 | 1178.8291 | 1179.6161 | 1181 | 1181 | 1188 | 1195 | 1203 | 1212 | 1222 | 1232
Pole Mounted Fuses-CEN | Pole Mounted Fuses | CEN | 1 | 21.5197 | 24.0463 | 26.8364 | 29.9112 | 33.2913 | 37 | 37 | 35 | 32 | 30 | 29 | 27 | 25
Pole Mounted Fuses-CEN | Pole Mounted Fuses | CEN | 2 | 23.5222 | 26.1064 | 28.9327 | 32.0157 | 35.3662 | 39 | 39 | 38 | 39 | 40 | 40 | 41 | 43
Pole Mounted Fuses-CEN | Pole Mounted Fuses | CEN | 3 | 94.1174 | 103.08 | 112.6351 | 122.8094 | 133.5785 | 145 | 145 | 150 | 155 | 161 | 169 | 177 | 186
Pole Mounted Fuses-CEN | Pole Mounted Fuses | CEN | 4 | 217.7344 | 233.0481 | 249.1447 | 266.19 | 284.037 | 303 | 303 | 320 | 338 | 358 | 379 | 403 | 428
Pole Mounted Fuses-CEN | Pole Mounted Fuses | CEN | 5 | 2674.3973 | 2728.4622 | 2824.3507 | 2888.7886 | 2947.2742 | 3040 | 3040 | 3021 | 3000 | 2975 | 2947 | 2916 | 2882
Poles-AUR | Poles | AUR | 1 | 2334.026 | 2403.4527 | 2429.5689 | 2470.6813 | 2456.3668 | 2228 | 2223 | 1852 | 1493 | 1143 | 798 | 770 | 737
Poles-AUR | Poles | AUR | 2 | 1831.7579 | 1878.7813 | 1900.5964 | 1931.356 | 1926.4123 | 1775 | 1775 | 1700 | 1629 | 1582 | 1512 | 1439 | 1380
Poles-AUR | Poles | AUR | 3 | 5466.4192 | 5554.7454 | 5593.0424 | 5644.89 | 5620.5485 | 5236 | 5236 | 5034 | 5050 | 5181 | 5648 | 7902 | 8934
Poles-AUR | Poles | AUR | 4 | 12693.9077 | 12789.1503 | 12814.9374 | 12848.7234 | 12791.8665 | 12223 | 12223 | 12936 | 13288 | 13470 | 13256 | 11010 | 10206
Poles-AUR | Poles | AUR | 5 | 30312.8321 | 29798.6012 | 29537.3682 | 29186.9636 | 29218.9829 | 30733 | 30738 | 30673 | 30735 | 30819 | 30981 | 31074 | 30938
Poles-DUN | Poles | DUN | 1 | 2063.8035 | 2122.9605 | 2144.5672 | 2176.5405 | 2158.269 | 1948 | 1948 | 1548 | 1156 | 768 | 384 | 362 | 336
Poles-DUN | Poles | DUN | 2 | 997.4095 | 1018.1966 | 1025.0949 | 1033.9798 | 1022.2649 | 925 | 925 | 857 | 796 | 760 | 704 | 648 | 607
Poles-DUN | Poles | DUN | 3 | 2506.58 | 2547.4825 | 2572.6886 | 2596.2592 | 2585.9407 | 2407 | 2407 | 2261 | 2340 | 2540 | 3074 | 3272 | 3515
Poles-DUN | Poles | DUN | 4 | 5733.0748 | 5879.102 | 6017.9402 | 6139.2579 | 6215.1229 | 6107 | 6107 | 6862 | 7328 | 7627 | 7403 | 7317 | 7278
Poles-DUN | Poles | DUN | 5 | 16376.3539 | 15964.7223 | 15733.2104 | 15469.9385 | 15415.2868 | 16230 | 16230 | 16089 | 15997 | 15922 | 16052 | 16018 | 15881
Poles-CEN | Poles | CEN | 1 | 270.2225 | 280.4922 | 285.0016 | 294.1408 | 298.0978 | 280 | 280 | 308 | 340 | 377 | 414 | 407 | 400
Poles-CEN | Poles | CEN | 2 | 834.3483 | 860.5847 | 875.5015 | 897.3761 | 904.1474 | 850 | 850 | 843 | 833 | 821 | 807 | 791 | 773
Poles-CEN | Poles | CEN | 3 | 2959.8392 | 3007.263 | 3020.3539 | 3048.6308 | 3034.6078 | 2829 | 2829 | 2773 | 2709 | 2641 | 2574 | 4630 | 5419
Poles-CEN | Poles | CEN | 4 | 6960.8329 | 6910.0483 | 6796.9971 | 6709.4655 | 6576.7436 | 6116 | 6116 | 6074 | 5960 | 5843 | 5853 | 3693 | 2928
Poles-CEN | Poles | CEN | 5 | 13936.4782 | 13833.8789 | 13804.1579 | 13717.0251 | 13803.6961 | 14503 | 14503 | 14580 | 14736 | 14896 | 14930 | 15057 | 15058
Distribution Transformers-AUR | Distribution Transformers | AUR | 1 | 131.2393 | 144.9016 | 159.3013 | 175.338 | 192.3617 | 211 | 211 | 255 | 276 | 275 | 262 | 240 | 217
Distribution Transformers-AUR | Distribution Transformers | AUR | 2 | 143.2268 | 156.611 | 170.2595 | 185.3701 | 201.0293 | 218 | 218 | 210 | 204 | 196 | 191 | 188 | 183
Distribution Transformers-AUR | Distribution Transformers | AUR | 3 | 512.2123 | 543.281 | 572.2402 | 603.7744 | 634.5124 | 667 | 667 | 652 | 640 | 630 | 618 | 607 | 598
Distribution Transformers-AUR | Distribution Transformers | AUR | 4 | 786.8649 | 795.9709 | 801.202 | 809.64 | 816.143 | 825 | 825 | 815 | 804 | 797 | 792 | 789 | 788
Distribution Transformers-AUR | Distribution Transformers | AUR | 5 | 4855.2293 | 4907.9032 | 4974.5826 | 5039.8989 | 5085.7856 | 5142 | 5142 | 5131 | 5139 | 5165 | 5200 | 5239 | 5277
Distribution Transformers-DUN | Distribution Transformers | DUN | 1 | 2.0047 | 2.4353 | 2.8766 | 3.4713 | 4.1643 | 5 | 5 | 6 | 5 | 5 | 5 | 6 | 7
Distribution Transformers-DUN | Distribution Transformers | DUN | 2 | 3.4111 | 4.0964 | 4.7838 | 5.7019 | 6.7504 | 8 | 8 | 9 | 10 | 11 | 13 | 15 | 16
Distribution Transformers-DUN | Distribution Transformers | DUN | 3 | 24.4458 | 28.3256 | 32.0601 | 36.8444 | 42.0231 | 48 | 48 | 53 | 59 | 65 | 71 | 76 | 82
Distribution Transformers-DUN | Distribution Transformers | DUN | 4 | 94.8898 | 102.9442 | 110.1225 | 118.4042 | 126.4082 | 135 | 135 | 142 | 148 | 153 | 157 | 161 | 164
Distribution Transformers-DUN | Distribution Transformers | DUN | 5 | 743.5618 | 742.5643 | 742.5416 | 740.1184 | 748.8517 | 755 | 755 | 741 | 729 | 717 | 705 | 693 | 682
Distribution Transformers-CEN | Distribution Transformers | CEN | 1 | 0.92388 | 1.0695 | 1.261 | 1.5025 | 1.7484 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1
Distribution Transformers-CEN | Distribution Transformers | CEN | 2 | 0.99574 | 1.1439 | 1.325 | 1.5395 | 1.7633 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Distribution Transformers-CEN | Distribution Transformers | CEN | 3 | 4.5478 | 5.1156 | 5.7414 | 6.4257 | 7.1739 | 8 | 8 | 9 | 10 | 11 | 12 | 13 | 15
Distribution Transformers-CEN | Distribution Transformers | CEN | 4 | 16.0383 | 17.7082 | 19.4949 | 21.4718 | 23.629 | 26 | 26 | 28 | 30 | 33 | 36 | 39 | 42
Distribution Transformers-CEN | Distribution Transformers | CEN | 5 | 1737.4013 | 1808.0068 | 1886.3817 | 1953.4947 | 2014.3867 | 2074 | 2074 | 2071 | 2068 | 2065 | 2061 | 2057 | 2052
Pole Mounted Switches-AUR | Pole Mounted Switches | AUR | 1 | 76.1052 | 82.3002 | 87.6752 | 93.8385 | 100.3699 | 107 | 107 | 120 | 112 | 99 | 82 | 64 | 46
Pole Mounted Switches-AUR | Pole Mounted Switches | AUR | 2 | 72.7498 | 76.3193 | 78.8371 | 81.8913 | 85.0254 | 88 | 88 | 73 | 61 | 51 | 43 | 38 | 33
Pole Mounted Switches-AUR | Pole Mounted Switches | AUR | 3 | 155.9354 | 155.3615 | 153.0165 | 152.1668 | 151.5937 | 151 | 151 | 131 | 115 | 103 | 95 | 88 | 84
Pole Mounted Switches-AUR | Pole Mounted Switches | AUR | 4 | 114.3521 | 113.5601 | 112.8205 | 114.2913 | 116.3977 | 119 | 119 | 119 | 121 | 123 | 124 | 127 | 130
Pole Mounted Switches-AUR | Pole Mounted Switches | AUR | 5 | 410.5622 | 409.1404 | 419.0125 | 439.6901 | 446.9572 | 461 | 461 | 483 | 517 | 550 | 582 | 609 | 633
Pole Mounted Switches-DUN | Pole Mounted Switches | DUN | 1 | 66.3661 | 71.6565 | 76.3562 | 81.835 | 87.3876 | 93 | 93 | 107 | 100 | 88 | 71 | 54 | 36
Pole Mounted Switches-DUN | Pole Mounted Switches | DUN | 2 | 62.4841 | 65.4034 | 67.5305 | 70.1885 | 72.6792 | 75 | 75 | 62 | 51 | 42 | 35 | 30 | 25
Pole Mounted Switches-DUN | Pole Mounted Switches | DUN | 3 | 129.6496 | 128.2991 | 125.697 | 124.3174 | 122.7315 | 121 | 121 | 102 | 87 | 75 | 66 | 58 | 53
Pole Mounted Switches-DUN | Pole Mounted Switches | DUN | 4 | 76.9477 | 73.6851 | 70.7855 | 69.2431 | 68.001 | 67 | 67 | 64 | 62 | 60 | 58 | 57 | 56
Pole Mounted Switches-DUN | Pole Mounted Switches | DUN | 5 | 135.2599 | 131.7408 | 132.0813 | 131.2427 | 131.5426 | 133 | 133 | 154 | 189 | 224 | 259 | 290 | 319
Pole Mounted Switches-CEN | Pole Mounted Switches | CEN | 1 | 9.7391 | 10.6437 | 11.3191 | 12.0035 | 12.9823 | 14 | 14 | 13 | 12 | 11 | 11 | 10 | 10
Pole Mounted Switches-CEN | Pole Mounted Switches | CEN | 2 | 10.2657 | 10.9158 | 11.3066 | 11.7028 | 12.3462 | 13 | 13 | 11 | 10 | 9 | 8 | 8 | 8
Pole Mounted Switches-CEN | Pole Mounted Switches | CEN | 3 | 26.2857 | 27.0624 | 27.3195 | 27.8493 | 28.8622 | 30 | 30 | 29 | 28 | 28 | 29 | 30 | 31
Pole Mounted Switches-CEN | Pole Mounted Switches | CEN | 4 | 37.4045 | 39.875 | 42.035 | 45.0482 | 48.3968 | 52 | 52 | 55 | 59 | 63 | 66 | 70 | 74
Pole Mounted Switches-CEN | Pole Mounted Switches | CEN | 5 | 275.3023 | 277.3996 | 286.9312 | 308.4473 | 315.4147 | 328 | 328 | 329 | 328 | 326 | 323 | 319 | 314
Ground Mounted Switchgear-AUR | Ground Mounted Switchgear | AUR | 1 | 64.0369 | 68.1676 | 72.2025 | 74.6921 | 75.9919 | 80 | 80 | 80 | 73 | 60 | 42 | 25 | 22
Ground Mounted Switchgear-AUR | Ground Mounted Switchgear | AUR | 2 | 67.9775 | 70.4485 | 73.0272 | 74.1304 | 74.8756 | 77 | 77 | 65 | 55 | 50 | 47 | 44 | 43
Ground Mounted Switchgear-AUR | Ground Mounted Switchgear | AUR | 3 | 161.6035 | 164.1737 | 166.3819 | 166.536 | 166.8109 | 167 | 167 | 160 | 158 | 156 | 158 | 160 | 164
Ground Mounted Switchgear-AUR | Ground Mounted Switchgear | AUR | 4 | 241.5374 | 244.6125 | 246.4065 | 248.1602 | 250.7382 | 253 | 253 | 261 | 270 | 278 | 286 | 295 | 305
Ground Mounted Switchgear-AUR | Ground Mounted Switchgear | AUR | 5 | 826.7026 | 834.5333 | 828.9818 | 892.482 | 961.4371 | 1015 | 1015 | 1026 | 1036 | 1048 | 1059 | 1068 | 1058
Ground Mounted Switchgear-DUN | Ground Mounted Switchgear | DUN | 1 | 63.11 | 67.3321 | 71.3094 | 73.81 | 75.0422 | 79 | 79 | 78 | 71 | 58 | 41 | 24 | 20
Ground Mounted Switchgear-DUN | Ground Mounted Switchgear | DUN | 2 | 64.6687 | 67.3065 | 69.623 | 70.6545 | 71.0573 | 73 | 73 | 61 | 52 | 48 | 44 | 40 | 38
Ground Mounted Switchgear-DUN | Ground Mounted Switchgear | DUN | 3 | 152.1816 | 154.0091 | 155.008 | 153.9611 | 152.7115 | 152 | 152 | 142 | 135 | 127 | 123 | 118 | 114
Ground Mounted Switchgear-DUN | Ground Mounted Switchgear | DUN | 4 | 180.9754 | 176.7463 | 170.273 | 162.8457 | 155.5153 | 148 | 148 | 142 | 137 | 131 | 125 | 120 | 117
Ground Mounted Switchgear-DUN | Ground Mounted Switchgear | DUN | 5 | 293.0753 | 306.5796 | 294.0726 | 297.3679 | 311.4404 | 305 | 305 | 334 | 362 | 393 | 424 | 455 | 468
Ground Mounted Switchgear-CEN | Ground Mounted Switchgear | CEN | 1 | 0.92694 | 0.83554 | 0.89303 | 0.882 | 0.94967 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 2
Ground Mounted Switchgear-CEN | Ground Mounted Switchgear | CEN | 2 | 3.3088 | 3.142 | 3.4042 | 3.4759 | 3.8183 | 4 | 4 | 4 | 3 | 2 | 3 | 4 | 5
Ground Mounted Switchgear-CEN | Ground Mounted Switchgear | CEN | 3 | 9.4219 | 10.1646 | 11.3739 | 12.5748 | 14.0994 | 15 | 15 | 18 | 23 | 29 | 35 | 42 | 50
Ground Mounted Switchgear-CEN | Ground Mounted Switchgear | CEN | 4 | 60.5621 | 67.8662 | 76.1334 | 85.3145 | 95.2229 | 105 | 105 | 119 | 133 | 147 | 161 | 175 | 188
Ground Mounted Switchgear-CEN | Ground Mounted Switchgear | CEN | 5 | 533.6272 | 527.9537 | 534.9092 | 595.1141 | 649.9967 | 710 | 710 | 692 | 674 | 655 | 635 | 613 | 590

## Model parameters (old) (hidden)
Forecast parameters
|  |  |  | Trend Impact | Note: method changed for determining ICP numbers in 2009. Therefore only average from 2009 onwards
| Faults |  | Duration | 0.2 | ICP Numbers
Distribution Cables
need to update to 2017 as base year
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate per Day (RY2017-19) |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| AUR | #N/A | #REF! | 0.2 | #REF!
| DUN | #N/A | #REF! | 0.2 | #REF!
| CEN | #N/A | #REF! | 0.2 | #REF!
Distribution Conductors
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate per Day (RY2017-19) |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
| Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| AUR | #N/A | #REF! | 0.2 | #REF!
| DUN | #N/A | #REF! | 0.2 | #REF!
| CEN | #N/A | #REF! | 0.2 | #REF!
Ground Mount Transformers
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate per Day (RY2017-19) |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Weighted average
| AUR | #N/A | #REF! | 0.2 | #REF!
| DUN | #N/A | #REF! | 0.2 | #REF!
| CEN | #N/A | #REF! | 0.2 | #REF!
Ground Mount Switchgear
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Average | Weighted average
| AUR | 0.12311 | #REF! | 0.2 | #REF!
| DUN | 0.12311 | #REF! | 0.2 | #REF!
| CEN | 0.05609 | #REF! | 0.2 | #REF!
Pole Mounted Fuses
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| AUR | 0.18262 | #REF! | 0.2 | #REF!
| DUN | 0.18262 | #REF! | 0.2 | #REF!
| CEN | 0.091161 | #REF! | 0.2 | #REF!
Pole Mounted Switches
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Average | Weighted average
| AUR | #REF! | #REF! | 0.2 | #REF! | #REF!
| DUN | #REF! | #REF! | 0.2 | #REF! | #REF!
| CEN | #REF! | #REF! | 0.2 | #REF! | #REF!
Poles
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | co-efficent | Average | Trend Impact | Weighted average
| AUR | #REF! | #REF! | 0.2 | #REF!
| DUN | #REF! | #REF! | 0.2 | #REF!
| CEN | #REF! | #REF! | 0.2 | #REF!
Non-Asset Exclusing Veg
Moderator: | 0.9
Area | Faults |  | Duration |  | ICP Numbers
Approach | Average adjusted for reactive tree count |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | co-efficent | Average | Trend Impact | Weighted average
| AUR | #REF! | #REF! | 0.2 | #REF!
| DUN | #REF! | #REF! | 0.2 | #REF!
| CEN | #REF! | #REF! | 0.2 | #REF!
Vegetation
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Average 2010 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2010 to 2017 average
Co-efficents | Planning Area | Average | Average | Trend Impact | Average
| AUR | #REF! | #REF! | 0.2 | #REF!
| DUN | #REF! | #REF! | 0.2 | #REF!
| CEN | #REF! | #REF! | 0.2 | #REF!
Unknown

## Summary Output
Output - Unplanned SAIDI and SAIFI
|  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
| SAIDI | 71.0814 | 105.7618 | 198.6806 | 107.1067 | 117.9813 | 168.0007 | 161.3215 | 148.7965 | 153.1974 | 155.3437 | 153.4528 | 150.9995 | 145.5597
| SAIFI | 1.2568 | 1.4332 | 2.2507 | 1.416 | 2.416 | 1.8908 | 1.9504 | 1.993 | 2.0985 | 2.1598 | 2.1417 | 2.0893 | 1.9875
Unplanned SAIDI
CPP
|  |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
|  |  | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
| Actual (Raw) |  | 2014: 71.0814; 2015: 105.7618; 2016: 198.6806; 2017: 107.1067; 2018: 117.9813; 2019: 168.0007; 2020: 161.3215
| Actual Disclosed (Normalised) |  | 2014: 71.0814; 2015: 105.7618; 2016: 108.3143; 2017: 77.38; 2018: 108.463; 2019: 108.34; 2020: 131
| Reported |  | 2014: 71.0814; 2015: 105.7618; 2016: 108.3143; 2017: 77.38; 2018: 108.463; 2019: 108.34; 2020: 131
| Normalised |  | 2014: 0; 2015: 0; 2016: 90.3663; 2017: 29.7267; 2018: 9.5183; 2019: 59.6607; 2020: 30.3215
| Composite Model (DPP3 Normalised) |  | 2021: 148.7965; CPP 2022: 153.1974; CPP 2023: 155.3437; CPP 2024: 153.4528; CPP 2025: 150.9995; CPP 2026: 145.5597
| 5-Year Moving Average |  | 2014: 71.0814; 2015: 75.0891; 2016: 79.6584; 2017: 74.1261; 2018: 78.7005; 2019: 84.1162; 2020: 90.3189
| Proposed Limit (Cap) |  | 2021: 146.2935; CPP 2022: 146.2935; CPP 2023: 146.2935; CPP 2024: 146.2935; CPP 2025: 146.2935; CPP 2026: 146.2935
| DPP3 Backcast |  | 2014: 71.0814; 2015: 79.0967; 2016: 88.797; 2017: 57.5293; 2018: 96.9982; 2019: 98.1599; 2020: 110.11
| Forecast (Reported) |  | 2021: 108.5619; CPP 2022: 111.7728; CPP 2023: 113.3388; CPP 2024: 111.9592; CPP 2025: 110.1693; CPP 2026: 106.2004
| DPP3 Limit (Cap) |  | 2021: 81.886; CPP 2022: 81.886; CPP 2023: 81.886; CPP 2024: 81.886; CPP 2025: 81.886
| Proposed Target |  | 2021: 113.3388; CPP 2022: 113.3388; CPP 2023: 113.3388; CPP 2024: 113.3388; CPP 2025: 113.3388; CPP 2026: 113.3388
| Model 2 Composite Model |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
| Crossarms |  | 0.73785 | 4.6812 | 2.0012 | 0.93995 | 2.8755 | 7.3128 | 3.1143 | 4.5383 | 4.5383 | 4.5383 | 4.5383 | 4.5383 | 4.5383 | linear fit to SAIFI
| Distribution Cables |  | 3.5898 | 1.7463 | 1.2344 | 1.1251 | 6.4241 | 4.5365 | 5.8401 | 5.1125 | 5.1125 | 5.1125 | 5.1125 | 5.1125 | 5.1125 | linear fit to SAIFI
| Distribution Conductors |  | 3.2029 | 11.6347 | 12.4193 | 4.931 | 5.7623 | 3.0608 | 6.3761 | 8.0289 | 14.0044 | 17.7398 | 17.0957 | 14.5082 | 8.9949 | linear fit to SAIFI
| Distribution Transformers |  | 0.70634 | 1.3408 | 2.1328 | 0.48316 | 0.24834 | 1.3936 | 2.4315 | 2.3344 | 2.7164 | 2.5947 | 2.2822 | 2.0161 | 1.8016 | linear fit to SAIFI
| Ground Mounted Switchgear |  | 1.7777 | 0.21669 | 0 | 0.59209 | 0.26743 | 10.4255 | 0.75852 | 0 | 0 | 0 | 0.51328 | 1.5723 | 1.8614 | linear fit to SAIFI
| Other |  | 0.36654 | 1.2163 | 4.4632 | 1.5686 | 2.9125 | 7.0889 | 5.8012 | 4.5543 | 4.5543 | 4.5543 | 4.5543 | 4.5543 | 4.5543 | linear fit to SAIFI
| Pole Mounted Fuses |  | 0.53696 | 1.7663 | 0.99574 | 0.91704 | 1.3127 | 1.5974 | 2.3653 | 1.29 | 1.2926 | 1.2943 | 1.2984 | 1.3011 | 1.3058 | linear fit to SAIFI
| Pole Mounted Switches |  | 1.1509 | 3.0389 | 3.242 | 2.6237 | 0.41835 | 1.1061 | 0.47995 | 1.1651 | 1.164 | 1.1957 | 1.2488 | 1.2549 | 1.2546 | linear fit to SAIFI
| Poles |  | 1.2848 | 2.4125 | 2.3975 | 12.2549 | 6.619 | 2.4085 | 2.7839 | 1.9655 | 1.3076 | 1.1072 | 0.90264 | 0.23515 | 0.22976 | linear fit to SAIFI
| Protection |  | 1.0586 | 0 | 1.7324 | 0 | 0 | 0.59786 | 0 | 0.45659 | 0.45659 | 0.45659 | 0.45659 | 0.45659 | 0.45659 | linear fit to SAIFI
| Subtransmission Conductors |  | 3.6921 | 1.5634 | 3.7516 | 2.2602 | 0.5098 | 3.0224 | 9.3253 | 5.0143 | 5.0143 | 5.0143 | 5.0143 | 5.0143 | 5.0143 | linear fit to SAIFI
| Non-Asset |  | 35.5816 | 43.1439 | 127.834 | 60.0593 | 69.3589 | 99.8451 | 96.0855 | 90.4358 | 90.4358 | 90.4358 | 90.4358 | 90.4358 | 90.4358 | linear fit to SAIFI
| Vegetation |  | 17.3953 | 33.0006 | 36.4766 | 19.3519 | 21.2725 | 25.6053 | 25.9598 | 23.9008 | 22.6005 | 21.3003 | 20 | 20 | 20 | linear fit to SAIFI
Historic Statistics (RY2010 - RY2019)
| Raw Mean (RY2010 - RY2019) | 81.9437
| DPP3 Quality Standards | [17 empty] | `
| * SAIDI Standard Deviation | 9.223
| Adjusted SAIDI Target | 63.44
| Adjusted SAIDI Cap | 81.886
Forecast Statistics (RY2021 - RY2026)
| Max forecast annual total | 113.3388
| Scaled DPP3 standard deviation | 16.4774
| Proposed Limit | 146.2935
* This value differs from Aurora's calculation of standard deviation (16.659)
Unplanned SAIFI
CPP
|  |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
|  |  | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
| Actual (Raw) |  | 2014: 1.2568; 2015: 1.4332; 2016: 2.2507; 2017: 1.416; 2018: 2.416; 2019: 1.8908; 2020: 1.9504
| Actual Disclosed (Normalised) |  | 2014: 1.2568; 2015: 1.4332; 2016: 1.8916; 2017: 1.3574; 2018: 2.3235; 2019: 1.7539; 2020: 1.813
| Reported |  | 2014: 1.2568; 2015: 1.4332; 2016: 1.8916; 2017: 1.3574; 2018: 2.3235; 2019: 1.7539; 2020: 1.813
| Normalised |  | 2014: 0; 2015: 0; 2016: 0.3591; 2017: 0.05862; 2018: 0.0925; 2019: 0.13689; 2020: 0.096003
| Composite Model (DPP3 Normalised) |  | 2021: 1.993; CPP 2022: 2.0985; CPP 2023: 2.1598; CPP 2024: 2.1417; CPP 2025: 2.0893; CPP 2026: 1.9875
| 5-Year Moving Average |  | 2014: 1.1662; 2015: 1.2467; 2016: 1.3483; 2017: 1.3201; 2018: 1.4574; 2019: 1.5301; 2020: 1.5847
| Proposed Limit (Cap) |  | 2021: 2.5067; CPP 2022: 2.5067; CPP 2023: 2.5067; CPP 2024: 2.5067; CPP 2025: 2.5067; CPP 2026: 2.5067
| DPP3 Backcast |  | 2014: 1.1662; 2015: 1.3272; 2016: 1.5514; 2017: 1.2356; 2018: 2.0069; 2019: 1.5297; 2020: 1.6
| Forecast (Reported) |  | 2021: 1.8407; CPP 2022: 1.9382; CPP 2023: 1.9948; CPP 2024: 1.9781; CPP 2025: 1.9297; CPP 2026: 1.8356
| DPP3 Limit (Cap) |  | 2021: 1.469; CPP 2022: 1.469; CPP 2023: 1.469; CPP 2024: 1.469; CPP 2025: 1.469
| Proposed Target |  | 2021: 1.9948; CPP 2022: 1.9948; CPP 2023: 1.9948; CPP 2024: 1.9948; CPP 2025: 1.9948; CPP 2026: 1.9948
Linear Fit SAIFI -> SAIDI
| Category |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | m | c | Forecast Method
| Crossarms |  | 0.0084 | 0.05828 | 0.02433 | 0.01184 | 0.04924 | 0.08246 | 0.03565 | 0.055783 | 0.055783 | 0.055783 | 0.055783 | 0.055783 | 0.055783 | 84.0111 | -0.14815 | 3-Year Average
| Distribution Cables |  | 0.03786 | 0.02229 | 0.02669 | 0.03176 | 0.12006 | 0.04801 | 0.07364 | 0.08057 | 0.08057 | 0.08057 | 0.08057 | 0.08057 | 0.08057 | 55.4357 | 0.64602 | 3-year average
| Distribution Conductors |  | 0.08583 | 0.11532 | 0.12035 | 0.06876 | 0.15667 | 0.04562 | 0.08339 | 0.11955 | 0.2286 | 0.29677 | 0.28502 | 0.23779 | 0.13717 | 54.7939 | 1.4785 | Unit Based
| Distribution Transformers |  | 0.00283 | 0.01563 | 0.0593 | 0.01589 | 0.01823 | 0.03241 | 0.0268 | 0.01562 | 0.022592 | 0.020371 | 0.014668 | 0.009811 | 0.0058953 | 54.7939 | 1.4785 | Unit Based
| Ground Mounted Switchgear |  | 0.0034 | 0.00458 | 0 | 0.01413 | 0.01089 | 0.03474 | 0.01491 | 0.0043673 | 0.0042436 | 0.0044882 | 0.0064996 | 0.010267 | 0.011295 | 281.133 | -1.314 | Unit Based
| Other |  | 0.00926 | 0.05654 | 0.12709 | 0.02881 | 0.28187 | 0.17925 | 0.13025 | 0.19712 | 0.19712 | 0.19712 | 0.19712 | 0.19712 | 0.19712 | 14.9316 | 1.611 | 3-year average
| Pole Mounted Fuses |  | 0.00868 | 0.0175 | 0.06391 | 0.02926 | 0.04615 | 0.0386 | 0.03343 | 0.0089706 | 0.0099788 | 0.010627 | 0.012144 | 0.013193 | 0.014948 | 2.6417 | 1.2663 | Unit Based
| Pole Mounted Switches |  | 0.02137 | 0.03367 | 0.0321 | 0.07668 | 0.0525 | 0.03875 | 0.01351 | 0.0022968 | 0.0022234 | 0.0042721 | 0.007708 | 0.0081023 | 0.0080861 | 15.4612 | 1.1296 | Unit Based
| Poles |  | 0.01501 | 0.01429 | 0.03194 | 0.04824 | 0.07486 | 0.02705 | 0.02492 | 0.014385 | 0.0089458 | 0.0072887 | 0.0055976 | 7.8787e-05 | 3.4216e-05 | 120.9501 | 0.22562 | Unit Based
| Protection |  | 0.01974 | 0 | 0.07167 | 0 | 0 | 0.06064 | 0 | 0.020213 | 0.020213 | 0.020213 | 0.020213 | 0.020213 | 0.020213 | 18.2519 | 0.087656 | 3-year average
| Subtransmission Conductors |  | 0.04094 | 0.00909 | 0.01491 | 0.03613 | 0.02549 | 0.05483 | 0.09869 | 0.05967 | 0.05967 | 0.05967 | 0.05967 | 0.05967 | 0.05967 | 79.7551 | 0.25529 | 3-year average
| Non-Asset |  | 0.74452 | 0.76999 | 1.3874 | 0.90167 | 1.3431 | 1.0582 | 1.1888 | 1.1967 | 1.1967 | 1.1967 | 1.1967 | 1.1967 | 1.1967 | 102.8667 | -32.6647 | 3-year average
| Vegetation |  | 0.25891 | 0.31605 | 0.2907 | 0.15285 | 0.23667 | 0.19023 | 0.22641 | 0.21777 | 0.21185 | 0.20592 | 0.2 | 0.2 | 0.2 | 79.7428 | 6.5352 | 3-year average Interpolated to RY2024 Target
Historic Statistics (RY2010 - RY2019)
| Raw Mean | 1.4695
DPP3 Quality Standards
| * SAIFI Standard Deviation | 0.15
| Adjusted SAIFI Target | 1.169
| Adjusted SAIFI Cap | 1.469
Forecast Statistics (RY2021 - RY2026)
| Max forecast annual total | 1.9948
| Scaled DPP3 standard deviation | 0.25596
| Proposed Limit | 2.5067
* This value differs from Aurora's calucation of standard deviation (0.3148)
End
3-Year CPP
Annualised
DPP3 Limit
Total
Reported
Forecast
Proposed
Target
Proposed Limit
Normalised
DPP3
Backcast
Total
Reported
Annualised
DPP3 Limit
3-Year CPP
Proposed Limit
DPP3
Backcast
Normalised
Proposed
Target
Forecast