## Cover
QUALITY PATH
Planned SAIDI/SAIFI MODEL
2020-05-20
Document information
Author: | Aurora Energy
Created: | 2019-12-08
Last updated: | 2020-05-20
Status: | v5.05
Version | Final

## Approach
Purpose
This model projects total network SAIDI and SAIFI for the fleet categories which contribute significantly to annual reliability, for the period RY2021 - 2026 on the basis of:
a) the historical trends in reliability statistics in the period relative to the retirements by fleet occurring in associated periods,
b) projected fleet quantities for each subnetwork (Dunedin or Central Otago) per regulatory year,
c) the relationship between expenditure and reliability performance at a network level per annum.
Forecasting Approach
The modelling took the form of an ensemble approach, averaging the output of two models to arrive at the raw forecast:
A generalized linear model was used to model the count data underlying SAIDI and SAIFI statistics relative to fleet retirements per quarter.
A linear regression of asset replacement & renewal expenditure against SAIDI and SAIFI.
Primary inputs are as below:
CAPEX asset replacement & renewals
The baseline projected expenditure scenario.
Historical Retirements
Derived by aggregating assets removed from service due to end of life, according to fleet categories.
Network Development allocation
Uses FY16 Growth & Security Capex base rate, and prorates additional SAIDI/SAIFI requirements Capex based on forecast Growth & Security & Automation Uplift
Renewals allocation
Projected replacement quantities by year and fleet and subnetwork region.
Structure
Workbook colour coding
Input worksheets are
Model worksheets are
Output worksheets are
Worksheet structure
Direct input cells are:
Inputs from other model outputs
Worksheet Type | Worksheets | Description
Input | Total ICPs | Actual and forecast ICP volumes
Input | Expenditure Forecast | Actual and projected expenditure for asset reaplcement & renewals
Input | Fleet Renewal Quantities | Actual and projected fleet renewal quantities
Model | Model 1 | Expenditure regression modelling relating fleet expedniture to fleet reliability
Model | Model 2 | Unit-based modelling
Output | Summary Output | Output sheet
End

## Total ICPs
ICP Forecast
ICPs - Total
| Actual | [11 empty] | Forecast |  |  |  | CPP
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Total Customers | 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222
Used for ID | 310941 | 314565 | 316453 | 318388 | 319987 | 322126 | 324692 | 327394 | 330714 | 333925
ICPs - By Region
| Actual | [11 empty] | Forecast - Scaled to match historical ID ICP numbers
Aurora Network | 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Dunedin | 52598 | 52962 | 53254 | 53514 | 53699 | 53861.5 | 53985.5 | 54227 | 54476.5 | 54675 | 55017.5 | 55332 | 55660.5 | 55982 | 56307 | 56630.25 | 56954.375 | 57278.0625 | 57601.9688 | 57925.7656 | 58249.6172 | 58573.4414 | 58897.2793 | 59221.1104 | 59544.9448 | 59868.7776 | 60192.6112 | 60516.4444
Central Otago | 26439 | 27241 | 27824 | 28404.5 | 28879.5 | 29349.5 | 29930 | 30615.5 | 31374.5 | 32291 | 33369 | 34371 | 35411 | 36432 | 37462.5 | 38488.25 | 39516.375 | 40543.3125 | 41570.8438 | 42598.0781 | 43625.4609 | 44652.7695 | 45680.1152 | 46707.4424 | 47734.7788 | 48762.1106 | 49789.4447 | 50816.7776
ChkSum | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Growth Rates
CPP
Planning Area | [12 empty] | RY20 | RY21 | RY22 | RY23 | RY24 | RY25 | RY26 | RY27 | RY28 | RY29 | RY30 | RY31 | RY32 | RY33 | RY34 | RY35
Dunedin | [12 empty] | 0.5937% | 0.5776% | 0.5805% | 0.5741% | 0.5724% | 0.5683% | 0.5655% | 0.5621% | 0.5591% | 0.5559% | 0.5529% | 0.5498% | 0.5468% | 0.5438% | 0.5409% | 0.538%
Central Otago | [12 empty] | 3.026% | 2.883% | 2.829% | 2.738% | 2.671% | 2.599% | 2.534% | 2.471% | 2.412% | 2.355% | 2.301% | 2.249% | 2.2% | 2.152% | 2.107% | 2.063%
[5 empty] | Historical actual number of ICPs | [7 empty] | CPP RY27: Forecast number of ICPs
AMP Region | RY08 | RY09 | RY10 | RY11 | RY12 | RY13 | RY14 | RY15 | RY16 | RY17 | RY18 | RY19 | RY20 | RY21 | RY22 | RY23 | RY24 | RY25 | RY26 | RY27 | RY28 | RY29 | RY30 | RY31 | RY32 | RY33 | RY34 | RY35
Dunedin | 52598 | 52962 | 53254 | 53514 | 53699 | 53861.5 | 53985.5 | 54227 | 54476.5 | 54675 | 55017.5 | 55332 | 55660.5 | 55982 | 56307 | 56630.25 | 56954.375 | 57278.0625 | 57601.9688 | 57925.7656 | 58249.6172 | 58573.4414 | 58897.2793 | 59221.1104 | 59544.9448 | 59868.7776 | 60192.6112 | 60516.4444
Central Otago | 26439 | 27241 | 27824 | 28404.5 | 28879.5 | 29349.5 | 29930 | 30615.5 | 31374.5 | 32291 | 33369 | 34371 | 35411 | 36432 | 37462.5 | 38488.25 | 39516.375 | 40543.3125 | 41570.8438 | 42598.0781 | 43625.4609 | 44652.7695 | 45680.1152 | 46707.4424 | 47734.7788 | 48762.1106 | 49789.4447 | 50816.7776
| 79037 | 80203 | 81078 | 81918.5 | 82578.5 | 83211 | 83915.5 | 84842.5 | 85851 | 86966 | 88386.5 | 89703 | 91071.5 | 92414 | 93769.5 | 95118.5 | 96470.75 | 97821.375 | 99172.8125 | 100523.8438 | 101875.0781 | 103226.2109 | 104577.3945 | 105928.5527 | 107279.7236 | 108630.8882 | 109982.0559 | 111333.222

## Expenditure Forecast
Expenditure Forecast for Asset Replacement & Renewal (Fleet Categories) | [16 empty] | Expenditure Forecast for Asset Replacement & Renewal (Information Disclosure Categories)
Aurora's forward forecast for asset replacement and renewal by fleet category. In order to reconcile this with Auroar's historical reported expenditure, fleets were transformed into the Commision's asset categories. Refer to table in this sheet located in columns V to AM. | [16 empty] | Historical expenditure used in the planned reliability model was sourced from reporting disclosed to the Commerce Commision. Therefore, the fleet-based spend forecast is transformed in this table to the ID categories to be consistent with the historical categories. This table is aggregated in the pivot table in sheet "planned forecast", cells Q9 to AA19.
Fleet | RY15 | RY16 | RY17 | RY18 | RY19 | RY20 | RY21 | RY22 | RY23 | RY24 | RY25 | RY26 | RY27 | RY28 | RY29 | RY30 | Column Offset for lookup |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Poles | 46550 | 3879 | 8209 | 41156 | 26990 | 14198 | 14352 | 12780 | 11472 | 10908 | 6660 | 6048 | 5484 | 5148 | 5760 | 5376 | Fleet | Information Disclosure Category | RY2015 | RY2016 | RY2017 | RY2018 | RY2019 | RY2020 | RY2021 | RY2022 | RY2023 | RY2024 | RY2025 | RY2026 | RY2027 | RY2028 | RY2029 | RY2030
Crossarms | 0 | 0 | 0 | 0 | 0 | 1141 | 3661 | 6629 | 8417 | 8420 | 8418 | 8425 | 5807 | 5812 | 5821 | 5836 | Distribution Cables | Distribution and LV cables | 1700 | 154 | 333 | 487 | 74 | 1035 | 850 | 2018 | 2079 | 2112 | 1942 | 1210 | 1339 | 1480 | 1636 | 1810
Subtransmission Conductors | 0 | 0 | 0 | 0 | 0 | 939 | 6770 | 6622 | 7875 | 958 | 398 | 408 | 418 | 430 | 434 | 448 | Low Voltage Cables | Distribution and LV cables | 1500 | 318 | 423 | 281 | 223 | 252 | 397 | 445 | 499 | 560 | 609 | 687 | 775 | 875 | 987 | 1113
Distribution Conductors | 0 | 0 | 0 | 0 | 0 | 4172 | 4184 | 4692 | 5538 | 5968 | 6134 | 5727 | 5169 | 4840 | 4794 | 4797 | Poles | Distribution and LV lines | 46550 | 3879 | 8209 | 41156 | 26990 | 14198 | 14352 | 12780 | 11472 | 10908 | 6660 | 6048 | 5484 | 5148 | 5760 | 5376
Low Voltage Conductors | 3363 | 0 | 26 | 195 | 31 | 0 | 0 | 2268 | 4108 | 4271 | 4523 | 4460 | 4196 | 3704 | 3125 | 2646 | Crossarms | Distribution and LV lines | 0 | 0 | 0 | 0 | 0 | 1141 | 3661 | 6629 | 8417 | 8420 | 8418 | 8425 | 5807 | 5812 | 5821 | 5836
Subtransmission Cables | 705 | 48 | 211 | 2183 | 1329 | 2703 | 200 | 0 | 1996 | 2994 | 2851 | 4277 | 3405 | 5108 | 0 | 0 | Distribution Conductors | Distribution and LV lines | 0 | 0 | 0 | 0 | 0 | 4172 | 4184 | 4692 | 5538 | 5968 | 6134 | 5727 | 5169 | 4840 | 4794 | 4797
Distribution Cables | 1700 | 154 | 333 | 487 | 74 | 1035 | 850 | 2018 | 2079 | 2112 | 1942 | 1210 | 1339 | 1480 | 1636 | 1810 | Low Voltage Conductors | Distribution and LV lines | 3363 | 0 | 26 | 195 | 31 | 0 | 0 | 2268 | 4108 | 4271 | 4523 | 4460 | 4196 | 3704 | 3125 | 2646
Low Voltage Cables | 1500 | 318 | 423 | 281 | 223 | 252 | 397 | 445 | 499 | 560 | 609 | 687 | 775 | 875 | 987 | 1113 | Ground Mounted Distribution Transformers | Distribution substations and transformers | 3539 | 462 | 365 | 513 | 143 | 101 | 218 | 326 | 326 | 326 | 326 | 381 | 435 | 490 | 490 | 598
Zone Substations | 4464 | 276 | 966 | 6150 | 4283 | 6166 | 8752 | 10495 | 5802 | 10000 | 9623 | 5761 | 9533 | 7479 | 7529 | 6225 | Pole Mounted Distribution Transformers | Distribution substations and transformers | 2799 | 110 | 20 | 9 | 183 | 1359 | 1471 | 2146 | 2982 | 3600 | 3900 | 4029 | 4008 | 3893 | 3916 | 3666
Ground Mount Switchgear | 1111 | 113 | 325 | 86 | 0 | 1223 | 3098 | 3098 | 3225 | 3120 | 3150 | 1875 | 1950 | 2025 | 1950 | 2100 | Voltage Regulators | Distribution substations and transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole Mounted Fuses | 957 | 39 | 374 | 174 | 706 | 75 | 215 | 245 | 260 | 275 | 285 | 285 | 290 | 295 | 305 | 310 | Mobile Distribution Substations and Generators | Distribution substations and transformers | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole Mounted Switches | 0 | 0 | 0 | 0 | 0 | 294 | 382 | 588 | 588 | 588 | 529 | 470 | 368 | 353 | 206 | 191 | Ground Mount Switchgear | Distribution switchgear | 1111 | 113 | 325 | 86 | 0 | 1223 | 3098 | 3098 | 3225 | 3120 | 3150 | 1875 | 1950 | 2025 | 1950 | 2100
Reclosers and Sectionalisers | 141 | 0 | 129 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole Mounted Fuses | Distribution switchgear | 957 | 39 | 374 | 174 | 706 | 75 | 215 | 245 | 260 | 275 | 285 | 285 | 290 | 295 | 305 | 310
Low Voltage Enclosures | 0 | 0 | 0 | 0 | 0 | 575 | 1385 | 2525 | 2755 | 2830 | 2775 | 2505 | 1690 | 1460 | 1300 | 1250 | Pole Mounted Switches | Distribution switchgear | 0 | 0 | 0 | 0 | 0 | 294 | 382 | 588 | 588 | 588 | 529 | 470 | 368 | 353 | 206 | 191
Ancillary Distribution Substation Equipment | 0 | 0 | 0 | 0 | 0 | 876 | 772 | 772 | 1288 | 1088 | 1088 | 1088 | 1088 | 572 | 1088 | 1088 | Low Voltage Enclosures | Distribution switchgear | 0 | 0 | 0 | 0 | 0 | 575 | 1385 | 2525 | 2755 | 2830 | 2775 | 2505 | 1690 | 1460 | 1300 | 1250
Ground Mounted Distribution Transformers | 3539 | 462 | 365 | 513 | 143 | 101 | 218 | 326 | 326 | 326 | 326 | 381 | 435 | 490 | 490 | 598 | Reclosers and Sectionalisers | Distribution switchgear | 141 | 0 | 129 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole Mounted Distribution Transformers | 2799 | 110 | 20 | 9 | 183 | 1359 | 1471 | 2146 | 2982 | 3600 | 3900 | 4029 | 4008 | 3893 | 3916 | 3666 | Ancillary Distribution Substation Equipment | Distribution switchgear | 0 | 0 | 0 | 0 | 0 | 876 | 772 | 772 | 1288 | 1088 | 1088 | 1088 | 1088 | 572 | 1088 | 1088
Voltage Regulators | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Protection | Other network assets | 16 | 1 | 5 | 50 | 2904 | 1260 | 2360 | 2360 | 2360 | 1930 | 1320 | 1320 | 1320 | 1320 | 1320 | 1305
Mobile Distribution Substations and Generators | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DC Systems | Other network assets | 0 | 0 | 0 | 0 | 173 | 300 | 679 | 679 | 758 | 758 | 823 | 823 | 758 | 758 | 875 | 694
Protection | 16 | 1 | 5 | 50 | 2904 | 1260 | 2360 | 2360 | 2360 | 1930 | 1320 | 1320 | 1320 | 1320 | 1320 | 1305 | Remote Terminal Units | Other network assets | 12997 | 418 | 7604 | 1169 | 3563 | 0 | 0 | 84 | 84 | 231 | 294 | 315 | 315 | 294 | 294 | 315
DC Systems | 0 | 0 | 0 | 0 | 173 | 300 | 679 | 679 | 758 | 758 | 823 | 823 | 758 | 758 | 875 | 694 | Metering | Other network assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Terminal Units | 12997 | 418 | 7604 | 1169 | 3563 | 0 | 0 | 84 | 84 | 231 | 294 | 315 | 315 | 294 | 294 | 315 | - | Routine and corrective maintenance and inspection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metering | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | Routine and corrective maintenance and inspection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Total | 79842 | 5818 | 18990 | 52453 | 40602 | 36714 | 49746 | 58772 | 62412 | 60937 | 55648 | 50094 | 48348 | 46336 | 41830 | 39768 | Subtransmission Conductors | Subtransmission | 0 | 0 | 0 | 0 | 0 | 939 | 6770 | 6622 | 7875 | 958 | 398 | 408 | 418 | 430 | 434 | 448
[17 empty] | Subtransmission Cables | Subtransmission | 705 | 48 | 211 | 2183 | 1329 | 2703 | 200 | 0 | 1996 | 2994 | 2851 | 4277 | 3405 | 5108 | 0 | 0
[17 empty] | - | Vegetation management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Power Transformers | Zone substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Indoor Switchgear | Zone substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Buildings and Grounds | Zone substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Outdoor Switchgear | Zone substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Ancillary Zone Substation Equipment | Zone substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Total |  | 75378 | 5542 | 18024 | 46303 | 36319 | 30548 | 40994 | 48277 | 56610 | 50937 | 46025 | 44333 | 38815 | 38857 | 34301 | 33543
Indicative Costs for Pole Reinforcement
[17 empty] | Units |  |  |  | 1424 | 443 | 2206 | 155
[17 empty] | Indicative Unit Rate |  |  |  | 1592 | 1592 | 1592 | 1592
[17 empty] | Pole Reinforcement |  |  |  | 2267008 | 705256 | 3511952 | 246760

## Fleet Renewal Quantities
Asset Renewals Historic and Forecast Quantities
Note:Linear asset units = kilometers
Historic Quantities
Historic renewal quantities recorded as retired in the asset register
| Fleet | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
| Crossarms | 8 | 18 | 36 | 94 | 141 | 203 | 495 | 572 | 938 | 945 | 1602 | 326
| Distribution Conductors | 14 | 15 | 16 | 16 | 10 | 20 | 34 | 30 | 19 | 25 | 21 | 22
| Fuses | 0 | 0 | 4 | 7 | 23 | 124 | 115 | 112 | 134 | 146 | 201 | 204
| Ground Mounted Switchgear | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 10
| Pole Mounted Switchgear | 0 | 2 | 0 | 1 | 6 | 4 | 20 | 9 | 14 | 25 | 27 | 16
| Poles | 432 | 296 | 511 | 532 | 594 | 504 | 989 | 1098 | 2007 | 3155 | 1700 | 1010
| Transformers | 153 | 88 | 61 | 89 | 82 | 67 | 75 | 25 | 127 | 2 | 6 | 3
Forecast Quantities
Forecast renewal quantities from renewals forecast expenditure models
CPP
Portfolios | Fleet | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Distribution Switchgear | Ancillary Distribution Substation Equipment |  | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2
Support Structures | Crossarms | 723 | 1313 | 2408 | 3058 | 3058 | 3059 | 3059 | 2047 | 2048 | 2048 | 2051
Cables | Distribution Cables |  | 0 | 2.6254 | 2.7695 | 2.8429 | 2.6751 | 2.9573 | 3.2631 | 3.5974 | 3.9666 | 4.3784
Overhead Conductors | Distribution Conductors | 25.1505 | 21.1394 | 25.3794 | 28.5894 | 29.7594 | 30.8294 | 33.8094 | 36.7594 | 34.5894 | 34.3194 | 34.9694
Distribution Transformers | Ground Mount Transformers | 15 | 4 | 6 | 7 | 6 | 6 | 7 | 8 | 9 | 9 | 11
Distribution Switchgear | Ground Mounted Switchgear | 37 | 42 | 42 | 43 | 43 | 42 | 25 | 22 | 22 | 21 | 22
Distribution Transformers | Pole Mount Transformers | 30 | 39 | 60 | 80 | 93 | 98 | 98 | 99 | 100 | 101 | 99
Distribution Switchgear | Pole Mounted Fuses | 15 | 43 | 49 | 52 | 55 | 57 | 57 | 58 | 59 | 61 | 62
Distribution Switchgear | Pole Mounted Switches | 20 | 26 | 40 | 40 | 40 | 36 | 32 | 25 | 24 | 14 | 13
Support Structures | Poles | 1030 | 1126 | 992 | 881 | 837 | 482 | 435 | 390 | 362 | 422 | 388
Secondary Systems | Protection | 18 | 30 | 30 | 30 | 26 | 29 | 29 | 29 | 29 | 29 | 26
Reliability, Safety and Environment | Quality of Supply |  | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 1 | 1
Reliability, Safety and Environment | Quality of Supply |  | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 3 | 3 | 3
Reliability, Safety and Environment | Quality of Supply |  | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 10 | 10 | 10
Overhead Conductors | Subtransmission Conductors | 1 | 22.24 | 21.01 | 26.27 | 2.33 | 2.41 | 2.47 | 2.53 | 2.6 | 2.63 | 2.71
|  |  | 0.11246 | 0.20302 | 0.25758 | 0.25767 | 0.25761 | 0.25782

## Model 1
Model 1: Expenditure Regression
Author |  | Michael Kean
Status |  | v5.05
Last modified |  | 2020-05-20
MODEL 1 - LINEAR REGRESSION ON RENEWAL & REPLACEMENT EXPENDITURE
This model uses the relationships between annual metrics and expenditure for renewal and replacement activities by fleet
Base SAIDI/SAIFI Annual reliability statistics
Historic Raw SAIDI/SAIFI Figures
| 5 | 6 | 7 | 8 | 9 | 11 | 12
Reliability measure | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Planned SAIDI | 21.8076 | 23.44 | 24.26 | 35.4294 | 62.4655 | 290.012 | 154.2963 | 111.4167
Planned SAIFI | 0.12997 | 0.1073 | 0.12164 | 0.2304 | 0.35716 | 1.7058 | 0.73255 | 0.61303
Actual and Projected Asset Replacement & Renewal Expenditure
Expenditure (000's)
Row Labels | Sum of RY2016 | Sum of RY2017 | Sum of RY2018 | Sum of RY2019 | Sum of RY2020 | Sum of RY2021 | Sum of RY2022 | Sum of RY2023 | Sum of RY2024 | Sum of RY2025 | Sum of RY2026
Ancillary Distribution Substation Equipment | 0 | 0 | 0 | 0 | 876 | 772 | 772 | 1288 | 1088 | 1088 | 1088
Ancillary Zone Substation Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Buildings and Grounds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crossarms | 0 | 0 | 0 | 0 | 1141 | 3661 | 6629 | 8417 | 8420 | 8418 | 8425
DC Systems | 0 | 0 | 0 | 173 | 300 | 679 | 679 | 758 | 758 | 823 | 823
Distribution Cables | 154 | 333 | 487 | 74 | 1035 | 850 | 2018 | 2079 | 2112 | 1942 | 1210
Distribution Conductors | 0 | 0 | 0 | 0 | 4172 | 4184 | 4692 | 5538 | 5968 | 6134 | 5727
Ground Mount Switchgear | 113 | 325 | 86 | 0 | 1223 | 3098 | 3098 | 3225 | 3120 | 3150 | 1875
Ground Mounted Distribution Transformers | 462 | 365 | 513 | 143 | 101 | 218 | 326 | 326 | 326 | 326 | 381
Indoor Switchgear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Low Voltage Cables | 318 | 423 | 281 | 223 | 252 | 397 | 445 | 499 | 560 | 609 | 687
Low Voltage Conductors | 0 | 26 | 195 | 31 | 0 | 0 | 2268 | 4108 | 4271 | 4523 | 4460
Low Voltage Enclosures | 0 | 0 | 0 | 0 | 575 | 1385 | 2525 | 2755 | 2830 | 2775 | 2505
Metering | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Distribution Substations and Generators | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0
Outdoor Switchgear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole Mounted Distribution Transformers | 110 | 20 | 9 | 183 | 1359 | 1471 | 2146 | 2982 | 3600 | 3900 | 4029
Pole Mounted Fuses | 39 | 374 | 174 | 706 | 75 | 215 | 245 | 260 | 275 | 285 | 285
Pole Mounted Switches | 0 | 0 | 0 | 0 | 294 | 382 | 588 | 588 | 588 | 529 | 470
Poles | 3879 | 8209 | 41156 | 26990 | 14198 | 14352 | 12780 | 11472 | 10908 | 6660 | 6048
Power Transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Protection | 1 | 5 | 50 | 2904 | 1260 | 2360 | 2360 | 2360 | 1930 | 1320 | 1320
Reclosers and Sectionalisers | 0 | 129 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Remote Terminal Units | 418 | 7604 | 1169 | 3563 | 0 | 0 | 84 | 84 | 231 | 294 | 315
Subtransmission Cables | 48 | 211 | 2183 | 1329 | 2703 | 200 | 0 | 1996 | 2994 | 2851 | 4277
Subtransmission Conductors | 0 | 0 | 0 | 0 | 939 | 6770 | 6622 | 7875 | 958 | 398 | 408
Voltage Regulators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 5542 | 18024 | 46303 | 36319 | 30548 | 40994 | 48277 | 56610 | 50937 | 46025 | 44333
Pole Reinforcement | 0 | 2267.008 | 705.256 | 3511.952 | 246.76
Pole Replacements | 3879 | 5941.992 | 40450.744 | 23478.048 | 13951.24
fleet totals in regression model | 4564 | 8919 | 41764 | 27316 | 22194 | 26984 | 29671 | 31960 | 32342 | 28588 | 26485
%fleet totoals to annual in regression model | 82.35% | 49.48% | 90.2% | 75.21% | 72.65%
Distribution Transformers | 572 | 385 | 522 | 326 | 1460 | 1689 | 2472 | 3308 | 3926 | 4226 | 4410
Pole Mount and Ground Mount total
| 1 | 2 | 3 | 4 | 5
| SAIDI | [5 empty] | CPP
| Historical |  |  |  |  | Forecast | [5 empty] | Regression Coeficients
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | m | c
Crossarms | 0.01783 | 0.06101 | 0 | 0.2683 | 3.7588 | 11.8687 | 21.4203 | 27.1745 | 27.1842 | 27.1777 | 27.2003 | 0.0032182 | 0.086785
Distribution Conductors | 3.9223 | 1.5768 | 4.997 | 3.8749 | 4.3882 | 4.3904 | 4.4873 | 4.6486 | 4.7306 | 4.7622 | 4.6846 | 0.00019065 | 3.5927
Fuses | 3.0703 | 6.4696 | 3.1796 | 9.1032 | 5.424 | 4.9689 | 5.2149 | 5.3378 | 5.4608 | 5.5428 | 5.5428 | 0.0081991 | 3.2061
Ground Mounted Switchgear | 0.44965 | 0.11979 | 5.5053 | 5.2825 | 15.6787 | 33.3845 | 33.3845 | 34.6772 | 33.6084 | 33.9138 | 20.9359 | 0.010179 | 1.8507
Poles | 8.8318 | 45.2168 | 261.0489 | 122.9653 | 72.7682 | 81.4696 | 71.2648 | 62.7737 | 59.1124 | 31.536 | 27.5631 | 0.0064916 | -11.6982
Transformers | 7.6058 | 1.1956 | 5.848 | 8.7979 | 6.5095 | 6.8088 | 7.4267 | 8.0863 | 8.574 | 8.8107 | 8.9559 | 0.00078907 | 5.4761
| 23.8977 | 54.6397 | 280.5788 | 150.2921 | 108.5273 | 142.8909 | 143.1984 | 142.6982 | 138.6704 | 111.7433 | 94.8826
| 1 | 2 | 3 | 4 | 5
| SAIFI | [5 empty] | CPP
| Historical |  |  |  |  | Forecast | [5 empty] | Regression Coeficients
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | m | c
Crossarms | 0.00116 | 0.00095 | 0 | 0.00091 | 0.03557 | 0.11246 | 0.20302 | 0.25758 | 0.25767 | 0.25761 | 0.25782 | 3.0513e-05 | 0.000755
Distribution Conductors | 0.03371 | 0.02195 | 0.06982 | 0.01328 | 0.01555 | 0.015495 | 0.013164 | 0.0092832 | 0.0073104 | 0.0065489 | 0.0084161 | -4.5877e-06 | 0.03469
Fuses | 0.01722 | 0.04739 | 0.034 | 0.06763 | 0.05804 | 0.041931 | 0.043428 | 0.044177 | 0.044926 | 0.045425 | 0.045425 | 4.992e-05 | 0.031198
Ground Mounted Switchgear | 0.0267 | 0.00183 | 0.11302 | 0.12106 | 0.11716 | 0.141 | 0.141 | 0.144 | 0.14152 | 0.14223 | 0.11206 | 2.3664e-05 | 0.067686
Poles | 0.05724 | 0.20287 | 1.405 | 0.47564 | 0.31014 | 0.38048 | 0.32639 | 0.28139 | 0.26199 | 0.11583 | 0.094774 | 3.4406e-05 | -0.11331
Transformers | 0.02894 | 0.00737 | 0.01815 | 0.0289 | 0.02759 | 0.029614 | 0.035225 | 0.041216 | 0.045645 | 0.047795 | 0.049113 | 7.1661e-06 | 0.017511
| 0.16497 | 0.28236 | 1.64 | 0.70742 | 0.56405 | 0.72098 | 0.76223 | 0.77765 | 0.75905 | 0.61544 | 0.56761
[6 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
[5 empty] | Crossarms | 0.003072% | 0.003063% | 0.00306% | 0.00306% | 0.00306% | 0.00306%
[5 empty] | Distribution Conductors | 0.0003703% | 0.0002806% | 0.0001676% | 0.0001225% | 0.0001068% | 0.000147%
[5 empty] | Fuses | 0.0195% | 0.01773% | 0.01699% | 0.01634% | 0.01594% | 0.01594%
[5 empty] | Ground Mounted Switchgear | 0.004551% | 0.004551% | 0.004465% | 0.004536% | 0.004515% | 0.005976%
[5 empty] | Poles | 0.002651% | 0.002554% | 0.002453% | 0.002402% | 0.001739% | 0.001567%
[5 empty] | Transformers | 0.01358% | 0.01081% | 0.01264% | 0.014% | 0.01466% | 0.01289%

## Model 2
Model 2: Unit based Model
The count based data undelying reliability statistics was modelled relative to unit retirements, providing a sound basis to forecast SAIDI and SAIFI alongwith projections of customer volumes in future years.
This was achieved by modelling consumer-minutes and frequency data according to a Poisson distribution, using a generalized linear model.
This data was modelled outside of this workbook in Python, and the results have been entered from external queries into this workbook.
MODEL 2 - UNIT-BASED FORECAST
SAIDI
This model is based the number of customer-minutes generated by planned outages per fleet per quarter, and historical retirements.
CPP
| Historical |  |  |  |  | Forecast
Fleet | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Crossarms | 0.01783 | 0.06101 | 0 | 0.2683 | 3.7588 | 11.4713 | 20.1528 | 30.3165 | 29.8916 | 29.5015 | 29.0993
Distribution Conductors | 3.9223 | 1.5768 | 4.997 | 3.8749 | 4.3882 | 5.7413 | 5.6611 | 5.583 | 5.5056 | 5.4302 | 5.3581
Fuses | 3.0703 | 6.4696 | 3.1796 | 9.1032 | 5.424 | 1.0748 | 1.0867 | 1.0786 | 1.0707 | 1.0626 | 1.0463
Ground Mounted Switchgear | 0.44965 | 0.11979 | 5.5053 | 5.2825 | 15.6787 | 4.5121 | 3.1278 | 3.0835 | 3.0403 | 4.2627 | 4.2046
Poles | 8.8318 | 45.2168 | 261.0489 | 122.9653 | 72.7682 | 142.1265 | 95.0122 | 67.9226 | 57.626 | 17.2121 | 15.2661
Transformers | 7.6058 | 1.1956 | 5.848 | 8.7979 | 6.5095 | 1.0342 | 0.81077 | 0.6779 | 0.64343 | 0.62933 | 0.62991
| 23.8977 | 54.6397 | 280.5788 | 150.2921 | 108.5273 | 165.96 | 125.8514 | 108.662 | 97.7776 | 58.0984 | 55.6044
SAIFI
This model is based the number of customers affected by planned outages per fleet per quarter, and historical retirements.
CPP
| Historical |  |  |  |  | Forecast
Fleet | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Crossarms | 0.00116 | 0.00095 | 0 | 0.00091 | 0.03557 | 0.059155 | 0.1119 | 0.17965 | 0.17713 | 0.17484 | 0.17246
Distribution Conductors | 0.03371 | 0.02195 | 0.06982 | 0.01328 | 0.01555 | 0.026362 | 0.025995 | 0.025638 | 0.025282 | 0.024937 | 0.024606
Fuses | 0.01722 | 0.04739 | 0.034 | 0.06763 | 0.05804 | 0.0096543 | 0.0099968 | 0.010542 | 0.011143 | 0.011363 | 0.011367
Ground Mounted Switchgear | 0.0267 | 0.00183 | 0.11302 | 0.12106 | 0.11716 | 0.026358 | 0.014127 | 0.013927 | 0.013732 | 0.024901 | 0.024561
Poles | 0.05724 | 0.20287 | 1.405 | 0.47564 | 0.31014 | 0.81731 | 0.52837 | 0.36719 | 0.30686 | 0.077558 | 0.068059
Transformers | 0.02894 | 0.00737 | 0.01815 | 0.0289 | 0.02759 | 0.0039261 | 0.0032752 | 0.0028518 | 0.002715 | 0.0026519 | 0.0026384
Total | 0.16497 | 0.28236 | 1.64 | 0.70742 | 0.56405 | 0.94277 | 0.69366 | 0.5998 | 0.53687 | 0.31625 | 0.30369
End

## Summary Output
Outputs
This summary averages Model 1 and Model 2 to produce the raw forecast, which is then further modeified using assumptions for notification compiace (SAIDI) and future operational efficieny (SAIFI) to arrive at a baseline forecast.
Total Forecasts
CPP
| RY09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
SAIDI (Not de-weighted) | 8.82 | 11.3 | 16.92 | 13.5 | 21.8076 | 23.44 | 24.26 | 35.4294 | 62.4655 | 290.012 | 154.2963 | 111.4167 | 154.4255 | 134.5249 | 125.6801 | 118.224 | 84.9208 | 75.2435
SAIFI (Not de-weighted) | 0.05 | 0.08892 | 0.1207 | 0.09658 | 0.12997 | 0.1073 | 0.12164 | 0.2304 | 0.35716 | 1.7058 | 0.73255 | 0.61303 | 0.83187 | 0.72794 | 0.68872 | 0.64796 | 0.46584 | 0.43565
CAIDI | 176.4 | 127.0805 | 140.1823 | 139.7805 | 167.7895 | 218.4529 | 199.441 | 153.7734 | 174.895 | 170.0113 | 210.629 | 181.7476 | 185.6363 | 184.8014 | 182.4828 | 182.4556 | 182.2945 | 172.7157
Network Planned SAIDI
CPP
| RY09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
Actual (Raw) | 8.82 | 11.3 | 16.92 | 13.5 | 21.8076 | 23.44 | 24.26 | 35.4294 | 62.4655 | 290.012 | 154.2963 | 111.4167
Actual (Normalised) |  | 0 | 0 | 0 | 0 | 0 | 0 | 17.7147 | 31.2327 | 145.006 | 77.1482 | 55.7084
Reported (Raw) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7147 | 31.2327 | 145.006 | 77.1482 | 55.7084
Reported (De-weighted) | 8.82 | 11.3 | 16.92 | 13.5 | 21.8076 | 23.44 | 24.26 | 17.7147 | 31.2327 | 145.006 | 77.1482 | 55.7084
Model 1 (Expenditure Linear Regression - Raw)) | [7 empty] | 35.4294 | 62.4655 | 290.012 | 154.2963 | 111.4167 | 142.8909 | 143.1984 | 142.6982 | 138.6704 | 111.7433 | 94.8826
Model 2 (Unit based Renewals - Raw) | [7 empty] | 23.8977 | 54.6397 | 280.5788 | 150.2921 | 108.5273 | 165.96 | 125.8514 | 108.662 | 97.7776 | 58.0984 | 55.6044
Estimated Notification Compliance | 21: 10%; 22: 25%; CPP 23: 32.5%; CPP 24: 35%; CPP 25: 37.5%; CPP 26: 40%
Forecast (Raw) | 21: 154.4255; 22: 134.5249; CPP 23: 125.6801; CPP 24: 118.224; CPP 25: 84.9208; CPP 26: 75.2435
Forecast (Baseline) | 21: 138.9829; 22: 100.8937; CPP 23: 84.8341; CPP 24: 76.8456; CPP 25: 53.0755; CPP 26: 45.1461
5-year CPP Average | 22: 72.159; CPP 23: 72.159; CPP 24: 72.159; CPP 25: 72.159; CPP 26: 72.159
DPP3 annualised limit | 21: 195.96; 22: 195.96; CPP 23: 195.96; CPP 24: 195.96; CPP 25: 195.96
Network Planned SAIFI
*RY2020 is inflated from YTD | CPP 23: CPP
| RY09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
Actual (Raw) | 0.05 | 0.08892 | 0.1207 | 0.09658 | 0.12997 | 0.1073 | 0.12164 | 0.2304 | 0.35716 | 1.7058 | 0.73255 | 0.61303
Actual Normalised | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1152 | 0.17858 | 0.85292 | 0.36628 | 0.30651
Reported (De-weighted) | 0.05 | 0.08892 | 0.1207 | 0.09658 | 0.12997 | 0.1073 | 0.12164 | 0.1152 | 0.17858 | 0.85292 | 0.36628 | 0.30651
Reported (Raw) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1152 | 0.17858 | 0.85292 | 0.36628 | 0.30651
Model 1 (Expenditure Linear Regression - Raw)) | [7 empty] | 0.2304 | 0.35716 | 1.7058 | 0.73255 | 0.61303 | 0.72098 | 0.76223 | 0.77765 | 0.75905 | 0.61544 | 0.56761
Model 2 (Unit based Renewals - Raw) | [7 empty] | 0.16497 | 0.28236 | 1.64 | 0.70742 | 0.56405 | 0.94277 | 0.69366 | 0.5998 | 0.53687 | 0.31625 | 0.30369
Efficiency in planned outage coordination | 21: 1; 22: 0.95; CPP 23: 0.9; CPP 24: 0.9; CPP 25: 0.85; CPP 26: 0.85
Forecast (Raw) | 21: 0.83187; 22: 0.72794; CPP 23: 0.68872; CPP 24: 0.64796; CPP 25: 0.46584; CPP 26: 0.43565
Forecast (Baseline) | 21: 0.83187; 22: 0.69155; CPP 23: 0.61985; CPP 24: 0.58316; CPP 25: 0.39597; CPP 26: 0.3703
5-year CPP Average | 22: 0.53217; CPP 23: 0.53217; CPP 24: 0.53217; CPP 25: 0.53217; CPP 26: 0.53217
DPP3 annualised limit | 21: 1.1077; 22: 1.1077; CPP 23: 1.1077; CPP 24: 1.1077; CPP 25: 1.1077
z`z`
3-Year CPP
3-Year CPP

## Model Performance
Performance Metrics
Fleet | N Obs | Df Residuals | Df Model | SAIDI R2 Coefficient | SAIFI R2 Coefficient
Poles | 40 | 37 | 2 | 0.61 | 0.75
Transformers | 17 | 14 | 2 | 0.34 | 0.21
Fuses | 40 | 37 | 2 | 0.2 | 0.19
Distribution Conductors * | 16 | 13 | 2 | 0.61 | 0.75
Ground Mounted Switchgear | 7 | 4 | 2 | 0.99 | 0.98
Crossarms * | 11 | 8 | 2 | 0.61 | 0.76
* These fleet were modelled using performance statistics for poles, based on an assumed unit modifier per interruption:
Crossarms | 0.2
Distribution Conductors | 0.05