1 | 13759888 | 2016-09-22 13:01 | 2016-09-22 15:45 | 163 | 1 | 163.65 | 0.0004914 | 0.000482 | 3.0027e-06 |  | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2717T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Over 250v - Electrician on site three days ago - all appliances off. Electrical inspection Tuesday afternoon - 246v before solar. FM has confirmed high voltage - will be organising via Control/Release Planning an urgent shutdown to replace Tx with no tap change. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000482 | 6.6 | 2017 | 2016-09-22 | C | 1 | 0.000482 | 3.0027e-06
1 | 13759928 | 2016-09-22 13:07 | 2016-09-22 15:10 | 123 | 68 | 3632.3333 | 0.010907 | 0.010294 | 0.00040837 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H0113 | INSULATOR | CB 1 Tripped on E/F to lock out 2R - A temporary linebreak required for Fault finding 2 customers called us directly to notify they've had outage Sunday 18th AM, Monday 19th 8.00pm till late and Tuesday 20th during milking. NCTL has requested Tech to Site due to suspected Circuit breaker issue. Break checked over Faulty insulator found at Pole H0113 - Isolated at ABS's IC757 & IC622 used Isulator and binder | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.010294 | 11 | 2017 | 2016-09-22 | C | 68 | 0.010294 | 0.00040837
1 | 13761073 | 2016-09-23 11:20 | 2016-09-23 13:13 | 113 | 93 | 10509 | 0.031556 | 0.030717 | 0.00027925 | NAPA ID:24806 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | 024806 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4041 | NONE | URGENT - Replace arcing HV termination on TX TC4041. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.015359 | 5.5 | 2017 | 2016-09-23 | B | 93 | 0.030717 | 0.00027925
1 | 13761980 | 2016-09-23 05:37 | 2016-09-23 10:55 | 317 | 445 | 57880.8167 | 0.1738 | 0.16979 | 0.0014293 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 211669 | CONDUCTOR - REPAIR/REHANG | 2 x 1R for patrol. Lines down at pole 211669. 2R request for Repair to Lines. Lines down repaired, all supply restored. 5 metres of Namu conductor and 3 sleeves material required. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.16979 | 11 | 2017 | 2016-09-23 | C | 445 | 0.16979 | 0.0014293
1 | 13764020 | 2016-10-17 09:40 | 2016-10-17 14:26 | 286 | 5 | 1430 | 0.0042926 | 0.004247 | 1.5009e-05 | NAPA ID:23530 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 023530 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1537 | NONE | To replace the 11kV term arm, 11kV fuse arm & 400V pin arm. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0021235 | 5.5 | 2017 | 2016-10-17 | B | 5 | 0.004247 | 1.5009e-05
1 | 13764130 | 2016-09-25 21:03 | 2016-09-25 21:07 | 4 | 23 | 92 | 0.00027624 | 6.9e-05 | 6.9061e-05 | NAPA ID:24742 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 4 | 11 | Planned | 024742 | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer G9 | NONE | Require outage on G9 to lower voltage due to high voltage issue overnight. Works location: Cook St. WO 30031805 | F2 | PASCAL ST 4 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 3.45e-05 | 5.5 | 2017 | 2016-09-25 | B | 23 | 6.9e-05 | 6.9061e-05
1 | 13764262 | 2016-09-23 08:53 | 2016-09-23 10:45 | 112 | 2 | 224.1667 | 0.00067311 | 0.000655 | 6.0054e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 826677 | FUSE - ELEMENT/LINK (HV) | 3x10amp HV fuses blown at 7674. Line patrolled & check No fault found. Reloaded & Livened. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.000655 | 11 | 2017 | 2016-09-23 | C | 2 | 0.000655 | 6.0054e-06
1 | 13764347 | 2016-10-13 10:20 | 2016-10-13 13:40 | 200 | 1 | 200 | 0.0006004 | 0.000591 | 3.0019e-06 | NAPA ID:23440 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 023440 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O3097 | NONE | TO REPLACE XARMS AND HARDWARE ON POLES O3097,O12826 & O12825. Works location: Hwy 2, Kerepehi. WO 30010109 | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0002955 | 5.5 | 2017 | 2016-10-13 | B | 1 | 0.000591 | 3.0019e-06
1 | 13764582 | 2016-10-13 09:15 | 2016-10-13 11:34 | 139 | 11 | 1529 | 0.00459 | 0.00449 | 3.3022e-05 | NAPA ID:23469 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 023469 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses SE5-284 | NONE | change 2xcross arms. Works location: Waitao Rd, Tauranga. WO 30018942 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002245 | 5.5 | 2017 | 2016-10-13 | B | 11 | 0.00449 | 3.3022e-05
1 | 13764998 | 2016-10-13 08:58 | 2016-10-13 14:36 | 338 | 52 | 17576 | 0.052763 | 0.052294 | 0.0001561 | NAPA ID:23627 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023627 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP506 | NONE | Replace poles,hardware and conductor. Works location: Pukehina Parade, Te Puke. WO 30019859 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.026147 | 5.5 | 2017 | 2016-10-13 | B | 52 | 0.052294 | 0.0001561
1 | 13765276 | 2016-09-23 13:40 | 2016-09-23 15:55 | 135 | 5 | 675 | 0.0020268 | 0.001981 | 1.5013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837581 | CONDUCTOR - REPAIR/REHANG | 2R - FM required to remove Trees from Lines and Repair Lines. Kevin From Treescape is on his way (0274698531) SRC -115066. Lines removed Tree felled. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.001981 | 11 | 2017 | 2016-09-23 | C | 5 | 0.001981 | 1.5013e-05
1 | 13765321 | 2016-10-15 08:30 | 2016-10-15 14:48 | 378 | 78 | 29484 | 0.088508 | 0.087805 | 0.00023415 | NAPA ID:23589 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023589 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S383 | NONE | Replace multiple poles. Works location: Willow Park Dr, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.043902 | 5.5 | 2017 | 2016-10-15 | B | 78 | 0.087805 | 0.00023415
1 | 13767599 | 2016-10-20 09:05 | 2016-10-20 13:04 | 239 | 52 | 12428 | 0.037305 | 0.036837 | 0.00015609 | NAPA ID:23632 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023632 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP506 | NONE | Replace poles,hardware and conductor. Works location: Pukehina Parade, Te Puke. WO 30019859 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.018419 | 5.5 | 2017 | 2016-10-20 | B | 52 | 0.036837 | 0.00015609
1 | 13767779 | 2016-10-17 08:54 | 2016-10-17 11:37 | 163 | 2 | 326 | 0.0009786 | 0.00096 | 6.0036e-06 | NAPA ID:23297 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023297 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 834652 | NONE | Pole replacement. Works location: Opaki Kaipororo Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.00048 | 5.5 | 2017 | 2016-10-17 | B | 2 | 0.00096 | 6.0036e-06
1 | 13767882 | 2016-09-23 12:19 | 2016-09-23 14:15 | 115 | 4 | 462.3333 | 0.0013883 | 0.001352 | 1.2011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP316 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses at FP316 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.001352 | 11 | 2017 | 2016-09-23 | C | 4 | 0.001352 | 1.2011e-05
1 | 13768129 | 2016-10-18 09:18 | 2016-10-18 15:08 | 350 | 20 | 7008.6667 | 0.021039 | 0.020858 | 6.0036e-05 | NAPA ID:23806 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 023806 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2933 | NONE | replaceing railway iron poles and X arms. Works location: Aldworth Rd, Hunterville. WO 30018289 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.010429 | 5.5 | 2017 | 2016-10-18 | B | 20 | 0.020858 | 6.0036e-05
1 | 13771878 | 2016-09-23 17:39 | 2016-09-23 18:35 | 55 | 5 | 277.9167 | 0.0008345 | 0.000789 | 1.5013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7-004 | FUSE - ELEMENT/LINK (HV) | 2 X 8A HV Fuses at SE7-004 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000789 | 11 | 2017 | 2016-09-23 | C | 5 | 0.000789 | 1.5013e-05
1 | 13772256 | 2016-09-24 05:22 | 2016-09-24 14:35 | 552 | 7 | 3869.7167 | 0.01162 | 0.011556 | 2.1019e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2477T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced transformer 2477T | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.011556 | 11 | 2017 | 2016-09-24 | C | 7 | 0.011556 | 2.1019e-05
1 | 13773666 | 2016-09-24 09:12 | 2016-09-24 14:25 | 312 | 2 | 625.5 | 0.0018782 | 0.00186 | 6.0053e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE5-199 | CABLE - REPLACE LESS THAN 5 METRES | Suspect cable fault between fuses SE5-199 & transformer TE5-252. 2 r created for tests/repairs & installation of generator Generator connected to transformer TE5-252 at 14:25. Cable fault location may take some time due to terrain (cable route through orchards) Cable fault location to recommence 26/09/16 Cable will be DNO'ed when Cable fault confirmed Mark Askin Confirmed this is HV Cable Fault. - 28/09/16 - DNO 160924 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.00186 | 11 | 2017 | 2016-09-24 | C | 2 | 0.00186 | 6.0053e-06
1 | 13774167 | 2016-09-24 13:34 | 2016-09-24 14:18 | 44 | 25 | 1100 | 0.0033029 | 0.003077 | 7.5067e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 28217 | NONE | Isolated lines from fuses H142 to remove branch from lines @ pole 28217 NDR No 30800 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.003077 | 11 | 2017 | 2016-09-24 | C | 25 | 0.003077 | 7.5067e-05
1 | 13774196 | 2016-09-24 12:53 | 2016-09-24 13:52 | 59 | 1 | 59.25 | 0.00017791 | 0.000168 | 3.0026e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8407 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a hv fuses @ 8407 | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000168 | 11 | 2017 | 2016-09-24 | C | 1 | 0.000168 | 3.0026e-06
1 | 13774520 | 2016-09-24 16:36 | 2016-09-24 21:16 | 279 | 313 | 11629.1333 | 0.034919 | 0.032099 | 0.00093984 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 840292 | POLE | Car vs Pole F2157093 - ETA 4.40pm SMC and control advised Pole 840292 replaced. isolated at ABS 6389 & 6395. Back feed from Recloser 8820/2. Materials 1x11pole, 1xcrossarm complete | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.032099 | 11 | 2017 | 2016-09-24 | C | 313 | 0.032099 | 0.00093984
1 | 13775151 | 2016-09-24 20:04 | 2016-09-26 10:58 | 2333 | 15 | 13335.8 | 0.040043 | 0.039907 | 5.4048e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4779 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Found recloser 9929 Tripped. sectionalised & found transformer TC4779 faulty. Customer has own generator. Arrangements made to replace transformer next day Replaced 1 x 15kvA single phase transformer. Isolated at fuses FP1552 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.039907 | 11 | 2017 | 2016-09-24 | C | 15 | 0.039907 | 5.4048e-05
1 | 13777864 | 2016-09-25 15:41 | 2016-09-26 14:40 | 1378 | 26 | 30741.5667 | 0.092306 | 0.092071 | 0.00010209 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 783221 | POLE | Line break cut at transformer 810W tried a recloser, tripped. left off over night due to assess issues. All power restored , Temp Line Break Closed Burnt Pole Found - To be replaced - Helicopter required - Referral Created | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.092071 | 11 | 2017 | 2016-09-25 | C | 26 | 0.092071 | 0.00010209
1 | 13779088 | 2016-09-25 21:14 | 2016-09-26 00:36 | 201 | 1138 | 60784.7 | 0.18251 | 0.17226 | 0.003417 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 204737 | CABLE - REPLACE 5 METRES OR MORE | CB 5 & CB 7 Triton sub tripped to L/O simultaneously. Lines down located on Totara St on CB 5 feeder. On investigation, it was established a digger had contacted the line at the Port of Tauranga. Fault current probably bought the conductors down, and line repulsion probably caused conductor clash between CB 5 & CB 7 tripping CB 7 as the lines were on a double circuit for several span towards Triton sub. Supply was restored to CB 7 feeder and bottom end of CB 5 feeder via back feed from Sw/gear SC4-079. Faulted section of line was isolated at ABS SC4-060, Sw/gear S4600 & Sw/gear SC4-496 for repairs. Materials required - 30 metres Wasp conductor & 4 x Wasp sleeves All supply restored following repairs. NDR number to be forwarded by Downer | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.17226 | 11 | 2017 | 2016-09-25 | C | 1138 | 0.17226 | 0.003417
1 | 13783525 | 2016-09-25 23:24 | 2016-09-26 10:03 | 639 | 927 | 49915.8 | 0.14988 | 0.14153 | 0.0027834 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 4 | NONE | CB 4 tripped to L/O. O/C flag. There had been 3 previous A/R on the feeder over 12 minute period after which NOC disabled the A/R, opened recloser 9228/2 during the 3rd of the A/R, and closed sectionaliser 9235/2 for backfeed for that part of feeder. Line was sectionalised & patrolled after lockout with no apparent fault being found. All supply restored with back feed from sectionaliser 9235 being left in place in case of further trippings. High winds were experienced at time of trips but had gone down by end of sectionalising/patrolling. Rechecked line OK. Closed Sw/Gear IC3114, recloser 9228/2 tripped, reclosed 9228/2 & opened 9235/2. Found no power beyound recloser 9228/2, recloser was showing closed on SCADA. Found that the control panel indicated closed but recloser was showing open. Closed bypass 9228/1 to restore power. DNO 160922 | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.14153 | 11 | 2017 | 2016-09-25 | C | 927 | 0.14153 | 0.0027834
1 | 13784022 | 2016-09-26 05:26 | 2016-09-26 06:39 | 72 | 2 | 145.0667 | 0.00043558 | 0.000417 | 6.0052e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842777 | FUSE - ELEMENT/LINK (HV) | 2x HV fuses blown at 5661. Line cross country. Reloaded Relivened | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.000417 | 11 | 2017 | 2016-09-26 | C | 2 | 0.000417 | 6.0052e-06
1 | 13785546 | 2016-09-26 08:42 | 2016-09-26 10:09 | 86 | 1 | 86.25 | 0.00025897 | 0.000249 | 3.0026e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | C14339 | FUSE - LV ELEMENT/LINK - HRC (LV) | Dispatcher also sign off 13785843 (4479 NO 8 Road, Tx TC2737) 1 X 80 AMP FUSE REPLACED AT TX DUE TO BIRD STRIKE | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.000249 | 11 | 2017 | 2016-09-26 | C | 1 | 0.000249 | 3.0026e-06
1 | 13785567 | 2016-09-26 08:40 | 2016-09-26 09:20 | 40 | 7 | 280 | 0.00084073 | 0.000777 | 2.1018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W12829 | JUMPER | Reconnect jumper to Transformer TC1165 DDO. Used 1 x Crimp | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000777 | 11 | 2017 | 2016-09-26 | C | 7 | 0.000777 | 2.1018e-05
1 | 13788210 | 2016-09-26 13:44 | 2016-09-26 14:50 | 66 | 2 | 132 | 0.00039634 | 0.000378 | 6.0052e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SD3-054 | CABLE - REPLACE LESS THAN 5 METRES | Found HT fuse blown at fuses SD3-054, replaced and it re blew. isolated at SD3-054 to test cables & transformer. 26/09/16 - Generator connected to Transformer TD3-069. Testing to continue tomorrow -27/09/16 28/09/16 DNO 160125 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.000378 | 11 | 2017 | 2016-09-26 | C | 2 | 0.000378 | 6.0052e-06
1 | 13789903 | 2016-09-26 14:11 | 2016-09-26 19:37 | 325 | 214 | 14747.7 | 0.044282 | 0.042353 | 0.0010089 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1536 | BINDER | A & B O/C During line patrol Found floating conductor @ transformer 1536 | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.042353 | 11 | 2017 | 2016-09-26 | C | 214 | 0.042353 | 0.0010089
1 | 13790803 | 2016-10-07 20:20 | 2016-10-07 21:02 | 42 | 7 | 294 | 0.00088265 | 0.000819 | 2.1015e-05 | NAPA ID:24639 TP_HUIRANGI GXP > BELL BLOCK SUB | 11 | Planned | 024639 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Restoration switching for commissioning of the new BBK bus section for T2, this now includes bus energisation and individual feeder outages to restore line breaks. Phasing to be carried out with the CB racked in and open. | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0004095 | 5.5 | 2017 | 2016-10-07 | B | 7 | 0.000819 | 2.1015e-05
1 | 13791161 | 2016-09-26 16:48 | 2016-09-26 17:44 | 56 | 5 | 280 | 0.00084073 | 0.000795 | 1.5013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 725011 | FUSE - ELEMENT/LINK (HV) | Please check if OMS 13791354 is related part power 568 Morea Road. Branch on line at pole 725011 Fuses CA465 opened to remove branch. With branch removed all service restored Material 1 x 10 A H/V O/H fuse NDR No N100230 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000795 | 11 | 2017 | 2016-09-26 | C | 5 | 0.000795 | 1.5013e-05
1 | 13791184 | 2016-09-26 15:38 | 2016-09-26 16:00 | 21 | 35 | 761.25 | 0.0022857 | 0.00197 | 0.00010509 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 850745 | BINDER | C830 A/R Floating conductor found at Pole 850745. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.00197 | 11 | 2017 | 2016-09-26 | C | 35 | 0.00197 | 0.00010509
1 | 13791357 | 2016-09-27 10:00 | 2016-09-27 12:07 | 127 | 166 | 20867.65 | 0.062657 | 0.061161 | 0.00049843 | NAPA ID:24916 TP_GREYTOWN GXP > HAU NUI SUB > WINDFARM | 33 | Planned | 024916 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 811207 | INSULATOR | emergency shutdown to replace faulty 33kv insulator pole 811207 Installing new surge arrestors at recloser 642 | S5 | HAU NUI 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.030581 | 16.5 | 2017 | 2016-09-27 | B | 166 | 0.061161 | 0.00049843
1 | 13791535 | 2016-09-26 19:54 | 2016-09-26 23:07 | 192 | 1 | 192.7667 | 0.0005788 | 0.000569 | 3.0026e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3508T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Isolation from fuses 5461 to replace faulty transformer 3508T | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000569 | 11 | 2017 | 2016-09-26 | C | 1 | 0.000569 | 3.0026e-06
1 | 13792251 | 2016-09-27 06:34 | 2016-09-27 08:00 | 86 | 4 | 344.6 | 0.0010347 | 0.000998 | 1.201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 202160 | FUSE - ELEMENT/LINK (HV) | Please link up OMS: 13793172 when signing off. Replace 2 x 3A at SB2-036 Birds? This fuse blew again at 15:24 and a branch was found on the line. | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.000998 | 11 | 2017 | 2016-09-27 | C | 4 | 0.000998 | 1.201e-05
1 | 13793420 | 2016-10-18 09:30 | 2016-10-18 15:26 | 356 | 100 | 20763.1333 | 0.062327 | 0.061426 | 0.00075645 | NAPA ID:23740 TP_KAITIMAKO GXP > WELCOME BAY SUB > OHAUITI RD | 11 | Planned | 023740 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212581 | NONE | change 11KV pole 212581. Works location: Rowe Rd, Tauranga. WO 30010386 | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.030713 | 5.5 | 2017 | 2016-10-18 | B | 100 | 0.061426 | 0.00075645
1 | 13793447 | 2016-10-19 08:30 | 2016-10-19 14:38 | 368 | 6 | 2112 | 0.0063397 | 0.006285 | 1.801e-05 | NAPA ID:23591 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023591 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 834470 | NONE | Replace poles and crossarm. Works location: Hwy 2, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0031425 | 5.5 | 2017 | 2016-10-19 | B | 6 | 0.006285 | 1.801e-05
1 | 13793545 | 2016-09-27 11:45 | 2016-09-27 13:45 | 120 | 5 | 600 | 0.0018015 | 0.001756 | 1.5013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772624 | BINDER | Floating conductor at pole 772624. Replace 2 X HT Insulator as they were cracked | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001756 | 11 | 2017 | 2016-09-27 | C | 5 | 0.001756 | 1.5013e-05
1 | 13795012 | 2016-10-03 12:51 | 2016-10-03 15:12 | 141 | 22 | 3102 | 0.0093133 | 0.009115 | 6.6052e-05 | NAPA ID:24959 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 024959 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 783221 | NONE | Replace 11kv pole 783221 burn't down by floating conductor. Works location: Te Komai Rd, Parihauhau. WO 30024971 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0045575 | 5.5 | 2017 | 2016-10-03 | B | 22 | 0.009115 | 6.6052e-05
1 | 13795555 | 2016-09-27 15:43 | 2016-09-27 17:14 | 90 | 83 | 7537.7833 | 0.022633 | 0.021885 | 0.00024921 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T1302 | NONE | at 15:43, Thames Sub, CB 4 Thames Coast Feeder. Faultman attended to tree that had broken and was leaning towards lines. Asplundh called to attend for tree removal. Faultman requested isolation only as tree crew were not working near lines but were concerned that if the support that was currently holding tree in place was to give way it could fall down on lines. Isolated lines at ABS 1354. Tree removed. All Power Restored on Completion. Stu Simpson Attened. Tree was outside zone. Pole T1302. Branch about to drop on lines, ASPLUNDH is there to cut trees now. Stew is heading up there now 3.05pm advised Sammy at svs hub of job | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.021885 | 11 | 2017 | 2016-09-27 | C | 83 | 0.021885 | 0.00024921
1 | 13795624 | 2016-09-27 15:24 | 2016-09-27 16:30 | 65 | 4 | 262.4 | 0.00078787 | 0.000751 | 1.201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 202160 | FUSE - ELEMENT/LINK (HV) | T J Tanoa Attended. Tree branch had fallen down onto the line and blown 2x HV Fuses at SB2-036. Reloaded, Relivened 2x 2A HV Fuses. All Power Restored on completion. tree on line outside property -This fuse had blown earlier in the day (OMS 13792251) and it was thought to be birds? | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.000751 | 11 | 2017 | 2016-09-27 | C | 4 | 0.000751 | 1.201e-05
1 | 13796791 | 2016-09-28 08:12 | 2016-09-28 09:01 | 49 | 638 | 6536.4333 | 0.019626 | 0.013879 | 0.0019156 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 826269 | CONDUCTOR - REPAIR/REHANG | Cause called in for this feeder fault was from Daniel 027 422 9135 - lines pulled down by excavator, lines are hanging over the machine, driver is stuck inside - corner of Perrys Road and Taratahi roads. TX - T230. Had individual site inspection in on OMS 13797463 to respond at 30 Perrys Road. Shan confirmed this was the cause of the feeder fault and Jason was onsite at lines down. Cancelled site inspection. Lines repaired at Pole 826269. Used 1 x 11M Pole, Crossarm, 3 x 33kV Insulators, 10M of Wire and 6 x Joints. NDR:21956 | S3 | GLADSTONE 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 0.013879 | 33 | 2017 | 2016-09-28 | C | 638 | 0.013879 | 0.0019156
1 | 13798293 | 2016-10-19 11:05 | 2016-10-19 13:19 | 133 | 54 | 7228.8 | 0.021699 | 0.021212 | 0.00016209 | NAPA ID:24009 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 024009 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O13293 | NONE | Straighten Pole O13293. Works location: Canal Wests Rd, Waitakaruru. WO 30019219 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.010606 | 5.5 | 2017 | 2016-10-19 | B | 54 | 0.021212 | 0.00016209
1 | 13798657 | 2016-09-28 10:44 | 2016-09-28 12:03 | 79 | 4 | 319.6667 | 0.00095981 | 0.000923 | 1.201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 13798657 | CONDUCTOR - REPAIR/REHANG | Urgent isolation & Earthing at Fuses 7745 to re-sag lines at Pole 834418. No Materials. Please note: Adam Whale attended as 2R. Job closed without him being put on site. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000923 | 11 | 2017 | 2016-09-28 | C | 4 | 0.000923 | 1.201e-05
1 | 13798812 | 2016-09-28 11:30 | 2016-09-28 14:46 | 196 | 316 | 39232.9667 | 0.1178 | 0.11495 | 0.0009488 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 827305 | CONDUCTOR - REPAIR/REHANG | Have advised Control of lines down at 22 LEES PAKARAKA ROAD Trees hit lines down at Pole 827305 NDR 34891 Used 20m Squirrel Conductor, 4 x joints. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.11495 | 11 | 2017 | 2016-09-28 | C | 316 | 0.11495 | 0.0009488
1 | 13800929 | 2016-10-19 10:00 | 2016-10-19 11:10 | 70 | 32 | 2240 | 0.0067239 | 0.006435 | 9.6056e-05 | NAPA ID:24089 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11 | Planned | 024089 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1903 | NONE | To install a 400V Disconnector on TC1903. Works location: Station Rd, Matamata. WO 30019182 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0032175 | 5.5 | 2017 | 2016-10-19 | B | 32 | 0.006435 | 9.6056e-05
1 | 13800996 | 2016-10-19 13:00 | 2016-10-19 14:45 | 105 | 19 | 1995 | 0.0059885 | 0.005817 | 5.7033e-05 | NAPA ID:24091 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11 | Planned | 024091 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1693 | NONE | To install a 400V Fuse Disconnector on TC1693. Works location: Waharoa East Rd, Matamata. WO 30019182 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0029085 | 5.5 | 2017 | 2016-10-19 | B | 19 | 0.005817 | 5.7033e-05
1 | 13802431 | 2016-09-28 15:27 | 2016-09-28 17:40 | 133 | 241 | 24497.8333 | 0.073556 | 0.071384 | 0.0013001 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773594 | INSULATOR | CB 6 A/R, L/O, E/F. Sectionalised & Patrolled. Broken Insulator found and replaced. Materials used: 11kV Pin & Insulator, 1x Line Gaurd, 1x Ali binder | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.071384 | 11 | 2017 | 2016-09-28 | C | 241 | 0.071384 | 0.0013001
1 | 13803166 | 2016-09-28 15:37 | 2016-09-28 21:36 | 359 | 1 | 359.3333 | 0.0010789 | 0.001069 | 3.0025e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2164T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2164T on at 01:47. (1R) No power - Lightning has hit pole, fuses have popped out. Has affected a number of ICPs on the same property. 2 R Replace Transformer Jacob Northcote assisting | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001069 | 11 | 2017 | 2016-09-28 | C | 1 | 0.001069 | 3.0025e-06
1 | 13803246 | 2016-09-28 15:47 | 2016-09-29 03:15 | 688 | 2 | 932.9167 | 0.0028011 | 0.002783 | 6.005e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 737096 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced transformer 4379T | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.002783 | 11 | 2017 | 2016-09-28 | C | 2 | 0.002783 | 6.005e-06
1 | 13803335 | 2016-09-28 16:07 | 2016-09-28 17:05 | 57 | 2 | 115.9333 | 0.00034809 | 0.00033 | 6.005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 843850 | UNKNOWN | Recloser 6942 (Cheal Opunake Hydro) tripped open after lightning strike. Ef, Ph A & B & C OC Restored at 17:05 | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00033 | 11 | 2017 | 2016-09-28 | C | 2 | 0.00033 | 6.005e-06
1 | 13803339 | 2016-09-28 16:07 | 2016-09-28 18:26 | 138 | 1566 | 122158.2167 | 0.36678 | 0.35268 | 0.0063864 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB 4 | UNKNOWN | CB 4 Tripped A,B,C Ph, O/C E/F O/C INVT, Ground No Fault found while sectionlising 4 faultman on fault due to 2 feeders effected Lots of Lightning in area | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.35268 | 11 | 2017 | 2016-09-28 | C | 1566 | 0.35268 | 0.0063864
1 | 13806540 | 2016-09-28 16:19 | 2016-09-29 15:57 | 1418 | 48 | 33428 | 0.10037 | 0.099936 | 0.00028824 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2018T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 4.26pm advised at svs hub of job OMS 13806540 3 CLAUDIUS STREET - 1R Check for safety - Customer called to report tx blown as lightning went through - advised Dave in control. Generator Connected Power Back on at 21:05 Transformer Replaced 1 x 300KVA 3Ph 3 x HV Fuse Carriers and Base | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.099936 | 11 | 2017 | 2016-09-28 | C | 48 | 0.099936 | 0.00028824
1 | 13806605 | 2016-09-28 16:28 | 2016-09-29 11:04 | 1115 | 5 | 5579.25 | 0.016752 | 0.016706 | 1.5013e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740697 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | called customer at 939 SALISBURY ROAD 06 762 8715 - customer advised no power at pump house no water at house 103 Beaconsfield Road, called customer no answer on cellphone. Transformer isolated at fuses on same pole Transformer replaced under faultmans AP | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.016706 | 11 | 2017 | 2016-09-28 | C | 5 | 0.016706 | 1.5013e-05
1 | 13806788 | 2016-09-28 16:48 | 2016-09-28 18:10 | 81 | 4 | 327.8667 | 0.00098443 | 0.000948 | 1.201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M12888 | FUSE - ELEMENT/LINK (HV) | Reload at TC3029 3 x 3A Lightening | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000948 | 11 | 2017 | 2016-09-28 | C | 4 | 0.000948 | 1.201e-05
1 | 13806992 | 2016-09-28 16:50 | 2016-09-28 23:02 | 372 | 1 | 372.1833 | 0.0011175 | 0.001108 | 3.0025e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3286T | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 2amp fuses at 3286 | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.001108 | 6.6 | 2017 | 2016-09-28 | C | 1 | 0.001108 | 3.0025e-06
1 | 13807027 | 2016-09-28 18:23 | 2016-09-29 03:28 | 545 | 252 | 76217.55 | 0.22885 | 0.22657 | 0.00075664 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | D12736 | POLE | Car vs Pole . 4.55pm advised Cindy at svs hub & emailed Check 177 Hicks Rd, OMS 13807016 is related 5.36pm Sammy advised eta 10-15mins - advised Fire service of eta. Pole D12736 is down. OMS 13807206 is outage NDR 53806 Isolated line at fuses fp1313. Once men on site isolated pole at abs 2518 replace pole & relivened 1 pole & 1 HT pin requires pole to be reblock later as ground to wet | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.22657 | 11 | 2017 | 2016-09-28 | C | 252 | 0.22657 | 0.00075664
1 | 13808973 | 2016-09-28 19:08 | 2016-09-29 02:18 | 430 | 1 | 430.4333 | 0.0012924 | 0.001283 | 3.0025e-06 |  | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4826T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Blown transformer 4826T. Replasced Transformer | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.001283 | 6.6 | 2017 | 2016-09-28 | C | 1 | 0.001283 | 3.0025e-06
1 | 13808982 | 2016-09-28 17:33 | 2016-09-28 19:39 | 125 | 2 | 251.7333 | 0.00075584 | 0.000737 | 6.005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5779 | FUSE - ELEMENT/LINK (HV) | 3 X 15 Amp Fuses at FABS 5779 Lightning. This was part of feeder fault earlier and they were not restored when OMS 13803339 was completed. Call at 19:08. | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000737 | 11 | 2017 | 2016-09-28 | C | 2 | 0.000737 | 6.005e-06
1 | 13809523 | 2016-09-28 21:09 | 2016-09-28 23:15 | 125 | 1 | 125.7167 | 0.00037747 | 0.000368 | 3.0025e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tp1629 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 3amp ht fuse Replaced 4 x 63amp lt fuses | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000368 | 11 | 2017 | 2016-09-28 | C | 1 | 0.000368 | 3.0025e-06
1 | 13810145 | 2016-09-28 23:29 | 2016-09-29 06:26 | 417 | 451 | 74847.5833 | 0.22473 | 0.22067 | 0.0013541 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 200142 | POLE | Recloser 9924 L/O E/F Car verse pole Moffatt near Orange lane - NDR 34422 Pole 200142 replaced Used 1 x Pole 1 x HV Crossarm assembly 1 x LV Crossarm assembly | F3 | MOFFAT RD | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.22067 | 11 | 2017 | 2016-09-28 | C | 451 | 0.22067 | 0.0013541
1 | 13811067 | 2016-09-29 04:29 | 2016-09-29 07:27 | 178 | 80 | 4108.55 | 0.012336 | 0.011615 | 0.0002402 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 845354 | CONDUCTOR - REPAIR/REHANG | Conductor on Ground - (suspect LV hit by truck flicking up into HV lines bringing them down) Used 20m Gopher wire 4 x Joints 10m x 16mm Copper 10m x 10mm Copper 6 x 10 Sleeves NDR 21939 | F3 | TOTARA ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.011615 | 11 | 2017 | 2016-09-29 | C | 80 | 0.011615 | 0.0002402
1 | 13811354 | 2016-09-29 08:00 | 2016-09-29 08:23 | 23 | 14 | 322 | 0.0009668 | 0.00084 | 4.2035e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N12955 | CABLE - SERVICE CABLE | TX: TC554 Transformer HV isolated to repair LV used 1 x LV Quick Lug | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.00084 | 11 | 2017 | 2016-09-29 | C | 14 | 0.00084 | 4.2035e-05
1 | 13811624 | 2016-09-29 11:15 | 2016-09-29 11:35 | 20 | 1 | 20 | 6.005e-05 | 5.1e-05 | 3.0024e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 721493 | FUSE - ELEMENT/LINK (HV) | Voltage low at transformer W5220 Fuse found blown at transformer W5220 - cause Lightening Volatge still a little low so Tap increased by one Used 1 x 2 amp fuses | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 5.1e-05 | 11 | 2017 | 2016-09-29 | C | 1 | 5.1e-05 | 3.0024e-06
1 | 13812255 | 2016-09-29 11:04 | 2016-09-29 12:48 | 104 | 3 | 312 | 0.00093678 | 0.000909 | 9.0074e-06 | NAPA ID:25042 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 025042 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2717T | NONE | We are replacing transformer 2717T because of high voltage and it can't be tapped down. Works Location: 366 Ratapiko Road, Ratapiko, Inglewood. Work Order 30033551. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.0004545 | 3.3 | 2017 | 2016-09-29 | B | 3 | 0.000909 | 9.0074e-06
1 | 13812281 | 2016-10-04 10:15 | 2016-10-04 11:45 | 90 | 172 | 15480 | 0.046476 | 0.044926 | 0.0005164 | NAPA ID:24998 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 024998 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 227194 | NONE | REPLACE ALL ARMS AT POLE # 227194. Works location: Pukehina Parade, Te Puke. WO 30012292 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.022463 | 5.5 | 2017 | 2016-10-04 | B | 172 | 0.044926 | 0.0005164
1 | 13812406 | 2016-10-04 11:00 | 2016-10-04 14:33 | 213 | 61 | 12993 | 0.039009 | 0.038459 | 0.00018314 | NAPA ID:24438 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | 024438 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | Install temporary links 78 at pole 712918 & temporary links 77 at pole 712945 for Saidi mitigation for applications 23521,23534 & 23545 Note: 10 day lead time used to install these isolation points prior to 1st outage on 6/10/16 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.01923 | 5.5 | 2017 | 2016-10-04 | B | 61 | 0.038459 | 0.00018314
1 | 13812452 | 2016-09-29 10:07 | 2016-09-29 11:20 | 72 | 2 | 145.7667 | 0.00043766 | 0.000419 | 6.0049e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 757961 | FUSE - ELEMENT/LINK (HV) | Reload at 4563T 3 x 3A Lightning | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000419 | 6.6 | 2017 | 2016-09-29 | C | 2 | 0.000419 | 6.0049e-06
1 | 13814537 | 2016-10-07 09:49 | 2016-10-07 16:00 | 371 | 7 | 2597 | 0.0077967 | 0.007733 | 2.1015e-05 | NAPA ID:23521 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | 023521 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace existing network poles 712928 & 712919 for new 11m Busck pole complete with new hardware. pull up wires to new poles and connect wire into existing network. Note; poles 712926,712925,712924,712923,712922,712921 will be all replaced/installed with new hardware and conductor prior to the HV outage. On completion of this outage the existing line breaks at poles 712928 & 889250 will be removed | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0038665 | 5.5 | 2017 | 2016-10-07 | B | 7 | 0.007733 | 2.1015e-05
1 | 13814568 | 2016-10-12 09:15 | 2016-10-12 15:28 | 373 | 7 | 2611 | 0.0078383 | 0.007775 | 2.1014e-05 | NAPA ID:23534 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | 023534 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace poles 712930, 712939. Temporarily terminate 11kv conductor at these 2 sites. remove HV spans between poles 712939 & 712938, and between poles 712930 & 712932 Pole 712932 has LV on it also but is not feeding anything, we will also remove the LV span from 712930 - 712932. From pole 712932 to pole 712936 will be therefore isolated to commence building of the line. Install line break pole 712930 Another outage will be applied for to connect in the new line to the network. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0038875 | 5.5 | 2017 | 2016-10-12 | B | 7 | 0.007775 | 2.1014e-05
1 | 13814586 | 2016-10-27 09:30 | 2016-10-27 14:12 | 282 | 7 | 1974 | 0.0059249 | 0.005861 | 2.101e-05 | NAPA ID:23545 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | 023545 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Reinstate 11KV conductor to poles 712939 and 712930. terminate and sleeve through to existing network. Line break at pole 712930 reinstated . | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0029305 | 5.5 | 2017 | 2016-10-27 | B | 7 | 0.005861 | 2.101e-05
1 | 13815842 | 2016-09-29 17:12 | 2016-09-29 23:26 | 373 | 92 | 20987.4 | 0.063015 | 0.062185 | 0.00033328 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 380736 | CONDUCTOR - REPAIR/REHANG | at 17:20, Te Puke Sub, CB 8 Te Matai Rd Feeder. Fire comms advise trees have fallen on HV lines. Sectionaliser 9781 Opened by Control to de-energise effected area. Isolated lines at Fuses SG5-001, then Sectionaliser reclosed. Permit issued & repairs carried out. Also note: When closing SG5-001, jumper to top of Fuses came out. Isolated Lines at Fuses SF5-019. Permit issued & fuses repaired. All Power Restored on completion. 1 span all 3 phases replaced (60m of conductor). Also had to reload, reliven 3x Fuses, 1 fuse blown at each of the following fuse numbers: SG5-001, SF5-019, SF5-004. Brian Sperling Attended. Jess Fire F2160236 Power lines down - tree has possibly bourght lines down and sparking into bushes Te Matai Road - near intersection with State Highway 36 eta required 09 486 7949 mark 0274 745 769 15 - 20 mins Report of lines down Sectionaliser 9781 opened Report of trees in lines at pole 380736 with in line fuses blown at Fuses SF5 019 & SF5 004 Isolation at Fuses SG5 001 There also lines down 4km down Te Matai Rd. Have advised Fire comms are requesting fault man to that site as well. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.062185 | 11 | 2017 | 2016-09-29 | C | 92 | 0.062185 | 0.00033328
1 | 13816220 | 2016-09-29 18:59 | 2016-09-29 19:33 | 33 | 751 | 19102.0167 | 0.057354 | 0.050589 | 0.0022549 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 386759 | CONDUCTOR - REPAIR/REHANG | 7pm advised Dianne at svs hub & emailed & advised control eta 20-30mins advised fire service of eta Replaced 2m of conductor, 3 links, repaired another line and cut trees away from lines line between 386759 and 200641 - cause tree NDR# 17992 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.050589 | 11 | 2017 | 2016-09-29 | C | 751 | 0.050589 | 0.0022549
1 | 13817092 | 2016-09-29 19:53 | 2016-09-29 20:04 | 10 | 1412 | 11432.95 | 0.034327 | 0.021608 | 0.0042395 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X76 | JUMPER | Blown Jumper at 33kV ABS X76 with resulting LOS to Apiti, Rangiwahia and Waituna feeders. Use 2m Conductor 1X Lug 1X Sleeve | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.021608 | 33 | 2017 | 2016-09-29 | C | 1412 | 0.021608 | 0.0042395
1 | 13818789 | 2016-09-30 01:43 | 2016-09-30 07:20 | 336 | 76 | 22870.9 | 0.068669 | 0.067984 | 0.00022819 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 780425 | CONDUCTOR - REPAIR/REHANG | Recloser 1406 tripped on E/F flags, line was patrolled and a trees were found to have damaged lines at pole 780425, line was isolated at ABS 1372 to repair the lines. NDR: 41492 5 meters of Squirrel conductor used. 5 X tension sleeves used. 5 x binders used. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.067984 | 11 | 2017 | 2016-09-30 | C | 76 | 0.067984 | 0.00022819
1 | 13819384 | 2016-09-30 08:33 | 2016-09-30 11:20 | 166 | 1 | 166.6833 | 0.00050046 | 0.000491 | 3.0024e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 731619 | FUSE - ELEMENT/LINK (HV) | Fuses found Blown at Transformer 3067T - cause possium Used 2 x 2 amp | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.000491 | 11 | 2017 | 2016-09-30 | C | 1 | 0.000491 | 3.0024e-06
1 | 13819532 | 2016-09-30 09:05 | 2016-09-30 15:11 | 365 | 143 | 21251.9 | 0.063808 | 0.062519 | 0.00042935 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 843711 | CONDUCTOR - REPAIR/REHANG | Recloser 2032 tripped on A phase O/C & E/F flags. line was sectionalised and patrolled and faultman found a tree had come down through the lines at pole 843711, line was isolated at ABS 1026 to repair the lines. NDR:41493 10 meters Squirrel conductor. 2 X 11KV insulators 2 X Dead ends. 2 X tension sleeves 2 X Eye bolts | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.062519 | 11 | 2017 | 2016-09-30 | C | 143 | 0.062519 | 0.00042935
1 | 13820141 | 2016-10-20 12:05 | 2016-10-20 12:36 | 31 | 6 | 186 | 0.00055832 | 0.000504 | 1.801e-05 | NAPA ID:24166 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024166 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2072 | NONE | To install a 400V Isolator on TC2072. Works location: Ngutumanga Rd, Te Aroha. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000252 | 5.5 | 2017 | 2016-10-20 | B | 6 | 0.000504 | 1.801e-05
1 | 13820231 | 2016-10-20 10:05 | 2016-10-20 11:05 | 60 | 2 | 120 | 0.00036021 | 0.000342 | 6.0034e-06 | NAPA ID:24164 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024164 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1771 | NONE | To install a 400V Isolator on TC1771. Works location: Ngutumanga Rd, Te Aroha. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000171 | 5.5 | 2017 | 2016-10-20 | B | 2 | 0.000342 | 6.0034e-06
1 | 13820913 | 2016-10-20 09:15 | 2016-10-20 12:00 | 165 | 7 | 1155 | 0.003467 | 0.003403 | 2.1012e-05 | NAPA ID:24122 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11 | Planned | 024122 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3634 | NONE | Upgrade transformer TC3634 to a 50kVA. Works location: Hwy 27, Waharoa. WO 30019176 | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0017015 | 5.5 | 2017 | 2016-10-20 | B | 7 | 0.003403 | 2.1012e-05
1 | 13820924 | 2016-09-30 12:00 | 2016-09-30 13:23 | 83 | 423 | 2214.1667 | 0.006648 | 0.002837 | 0.00127 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 2742 | UNKNOWN | CB 2742 tripped open with E/F Flag. Fully Patrolled as much as possible NOTE - Jo/Ken multiple trippings on this line in the last Year with 4 Helicopter patrols due to long inaccessible terrain - What is possibility of having LFI's installed to help with location faults? Please Discuss further with ASW | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.002837 | 33 | 2017 | 2016-09-30 | C | 423 | 0.002837 | 0.00127
1 | 13822215 | 2016-10-19 08:02 | 2016-10-19 15:48 | 466 | 9 | 4195.5 | 0.012594 | 0.012512 | 2.7016e-05 | NAPA ID:24098 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024098 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV MIK CB 10 | NONE | Mikkelsen Rd Additional feeder. Install new ABB CB to LH end of existing MIK switchboard (connecting beside CB8). Carry out testing including SCADA and pre-commission. Note: Field end of new Feeder 10 cable will be left capped & buried ready for connection at a later date under another NAPA Application. Works location: Mikkelsen Rd, Waihou. WO 30026131 Job to be completed on 27.10.2016 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.006256 | 5.5 | 2017 | 2016-10-19 | B | 9 | 0.012512 | 2.7016e-05
1 | 13822638 | 2016-09-30 16:39 | 2016-09-30 18:33 | 113 | 1 | 113.75 | 0.00034153 | 0.000332 | 3.0024e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220673 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 5A HV Fuses at SD5-187. Unknown cause. 2x pole fuses blown and contractor onsite herd a load bang from TX by shed 16.50pm advised Dianne at svs hub | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000332 | 11 | 2017 | 2016-09-30 | C | 1 | 0.000332 | 3.0024e-06
1 | 13822706 | 2016-09-30 17:26 | 2016-10-01 08:52 | 925 | 140 | 14158.7833 | 0.042511 | 0.04125 | 0.001165 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 784280 | CONDUCTOR - REPAIR/REHANG | Recloser 2032 tripped on C phase O/C & E/F flags. Line patrolled until Links 728, fault past this point, no access on safety grounds due to being remote rural. Next morning, crew located a 749m span down between Poles 784280 and 784281. EFSA NOTE: require KPI exception on safety grounds due to being dark in remote rural area. Powerco to discuss with landowners regarding required tree works. Requires trees to be removed to allow safety re-hang of conductor using chopper. Unable to restore power until tree works completed. Colin Winch working through the tree issues now. Generation has been installed at X2290, X2939 & X1763. Private generation installed at X1760. All other transformer sites are vacant properties or rural sheds. Still waiting for NDR. All works complete. Attn NOC Accts: Fiona, there was considerable tree works done but not sure what may be billed to us. Also helicopter, generators, fuel and and considerable Downers charges to be applied to this account. Any issues, please contact Wayne Stanford for details. ASW Attn NOC Reporting Manager: SAIDi component will be messy at best, note generators connected at sites, all others were vacant sites, not inhabited. ASW | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.04125 | 11 | 2017 | 2016-09-30 | C | 140 | 0.04125 | 0.001165
1 | 13824483 | 2016-10-01 01:47 | 2016-10-01 03:21 | 93 | 317 | 18297.5333 | 0.054937 | 0.052081 | 0.00127 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 23 A/R, L/O, E/F IDMT. Sectionalised & Patrolled. No fault found | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.052081 | 11 | 2017 | 2016-10-01 | C | 317 | 0.052081 | 0.00127
1 | 13826198 | 2016-10-01 03:56 | 2016-10-01 06:59 | 182 | 317 | 22773.65 | 0.068376 | 0.06552 | 0.0028283 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P16467 | INSULATOR | CB 23 tripped on E/F flags line was sectionalised and patrolled and a faulty insulator was found on pole P16467. 1 X 11 KV insulator replaced | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.06552 | 11 | 2017 | 2016-10-01 | C | 317 | 0.06552 | 0.0028283
1 | 13827670 | 2016-10-01 10:03 | 2016-10-01 10:24 | 21 | 5 | 105.25 | 0.00031601 | 0.00027 | 1.5012e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CA465 | FUSE - ELEMENT/LINK (HV) | pls check if related to 568 Morea Rd, Hawera (also low voltage) 13829295 Faultman found blown fuses at Fuses CA465. 2 X 10 amp HV fuses replaced. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.00027 | 11 | 2017 | 2016-10-01 | C | 5 | 0.00027 | 1.5012e-05
1 | 13828321 | 2016-10-01 08:59 | 2016-10-01 12:30 | 211 | 559 | 37085.85 | 0.11135 | 0.10631 | 0.0017714 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 2037 | SWITCH (HV) | CB 6 tripped on O/C & E/F flags, Countdown called advising a switch unit 2037 on fire outside the store, is out now - advised control. Faultman found Sw/Gear 2037 was a bit black inside line was isolated at ABS 1388 and Sw/Gear 2050/3 Faultman found that moisture had caused a flash over on the 11KV bus bar, bus bar was all cleaned up and sealed. | F2 | COLLEGE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.10631 | 11 | 2017 | 2016-10-01 | C | 559 | 0.10631 | 0.0017714
1 | 13829607 | 2016-10-01 11:33 | 2016-10-01 13:45 | 132 | 1 | 132.3833 | 0.00039747 | 0.000388 | 3.0024e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3931T | FUSE - ELEMENT/LINK (HV) | Advised FM not to reliven, will need to call wells to advise ready to reconnect... Faultman install 2 x 2 amp HV fuses & 1 X fuse holder to reliven transformer 3931T so Wells can connect new customer that is moving in to house. LV fuses are not installed faultman will notify Wells that transformer is alive and ready for customer to be connected. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000388 | 11 | 2017 | 2016-10-01 | C | 1 | 0.000388 | 3.0024e-06
1 | 13871178 | 2016-10-01 16:50 | 2016-10-01 17:40 | 49 | 2 | 99.8333 | 0.00029974 | 0.000281 | 6.0048e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T2/410 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses on transformer T2/410 2 X 2 amp HV fuses used | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000281 | 11 | 2017 | 2016-10-01 | C | 2 | 0.000281 | 6.0048e-06
1 | 13871218 | 2016-10-01 17:11 | 2016-10-01 17:50 | 39 | 3 | 117.3 | 0.00035218 | 0.000325 | 9.0072e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T7/266 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer T7/266. 2 X 2 amp HV fuses replaced. | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000325 | 11 | 2017 | 2016-10-01 | C | 3 | 0.000325 | 9.0072e-06
1 | 13871335 | 2016-10-01 18:05 | 2016-10-01 19:02 | 57 | 1 | 57.0667 | 0.00017134 | 0.000162 | 3.0024e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P43145 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at transformer T7/155 - cause Lightning Used 2 x 3 amp | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000162 | 11 | 2017 | 2016-10-01 | C | 1 | 0.000162 | 3.0024e-06
1 | 13871344 | 2016-10-01 18:14 | 2016-10-02 09:15 | 900 | 1 | 900.9167 | 0.0027049 | 0.002695 | 3.0024e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P43140 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses found blown at Transformer T7/157 and Fuses R49 - Cause Lightning Used 2 x 6amp at Fuses R49 Transformer T7/157 faulty and needs to be replaced Customer advised will be replaced in morning 15 kva 3P replaced with 50kva 3P as no smaller transformers available | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002695 | 11 | 2017 | 2016-10-01 | C | 1 | 0.002695 | 3.0024e-06
1 | 13871827 | 2016-10-01 21:40 | 2016-10-01 21:50 | 10 | 123 | 959.4 | 0.0028805 | 0.001772 | 0.0003693 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4236 | UNKNOWN | 11kV Recloser 4236 tripped to lockout, no flags @ 2142 hrs. Auto reclose function disabled by NOC at 2146 hrs. Recloser 4236 closed on it's own with no command at 2149 Hrs. Requires protection investigation, Safety Manager 665047 recloser after A/R disabled, load checked ok. faultman stood down on the way to job, feeder monitored with no furhter issues | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.001772 | 11 | 2017 | 2016-10-01 | C | 123 | 0.001772 | 0.0003693
1 | 13872221 | 2016-10-01 23:26 | 2016-10-02 01:33 | 127 | 1088 | 26952.1 | 0.080922 | 0.071121 | 0.0027082 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | Rata transformer t1 | TRANSFORMER - ZONE TRANSFORMER (HV) | 33kV CB 3035 tripped Restricted Earth Fault at 2325 hrs.LOS to RAT Sub. Back feed installed via 22kV. Inspection found a Magpie on the ground by 33kV fuses 4732 and a rat below the transformer. Cause determined to be the RAT. Both were within the res E/F zone. Next day after site inspection and protection checks and discussion with NCTL, Transformer re-livened and load restored to sub. NOTE: this has occurred a few time with Birds on the BUS at this sub, is there any way to improve bird protection at this sub being that is has an elongated exposed outside BUS? (ASW) Safety Manager 665040 | S4 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 0.071121 | 33 | 2017 | 2016-10-01 | C | 1088 | 0.071121 | 0.0027082
1 | 13875027 | 2016-10-02 06:33 | 2016-10-02 08:54 | 141 | 1188 | 119806.6333 | 0.35971 | 0.34901 | 0.0035668 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A | UNKNOWN | Report received of loud bang near 41 Wanganui road . Line sectionalised and patrolled with nothing obvious found . Supply restored ... | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.34901 | 11 | 2017 | 2016-10-02 | C | 1188 | 0.34901 | 0.0035668
1 | 13879862 | 2016-10-02 11:20 | 2016-10-02 13:28 | 127 | 1 | 127.85 | 0.00038386 | 0.000374 | 3.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L4467 | FUSE - ELEMENT/LINK (HV) | please contact Roger on 06 273 4010 Replaced 2x 2a HV fuses | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000374 | 11 | 2017 | 2016-10-02 | C | 1 | 0.000374 | 3.0023e-06
1 | 13879887 | 2016-10-02 14:13 | 2016-10-02 15:11 | 58 | 36 | 2105.5 | 0.0063215 | 0.005997 | 0.00010809 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714939 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced HV drop out holder @ pole 714939 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.005997 | 11 | 2017 | 2016-10-02 | C | 36 | 0.005997 | 0.00010809
1 | 13879953 | 2016-10-02 14:36 | 2016-10-02 15:24 | 48 | 53 | 2544 | 0.0076381 | 0.00716 | 0.00015913 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760004 | CONDUCTOR - REPAIR/REHANG | called svs hub and emailed re 999 called customer to advised hazard process Escalated to 2R as trafic management required .Line isolated from ABS 5325 to repair line materials used 10m ngamu conductor and 4 sleeves | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00716 | 6.6 | 2017 | 2016-10-02 | C | 53 | 0.00716 | 0.00015913
1 | 13880793 | 2016-10-02 21:47 | 2016-10-02 23:29 | 101 | 4 | 407.7333 | 0.0012242 | 0.001188 | 1.201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217641 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TE3 087 faulty & requires replacement Own isolation & AP to replace Materials 1 x transformer , 1 x 63A L/V base & fuse | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001188 | 11 | 2017 | 2016-10-02 | C | 4 | 0.001188 | 1.201e-05
1 | 13881907 | 2016-10-03 08:25 | 2016-10-03 08:54 | 29 | 19 | 551 | 0.0016543 | 0.001483 | 5.7044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P23543 | JUMPER | repaired jumper @ pole P23543 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001483 | 11 | 2017 | 2016-10-03 | C | 19 | 0.001483 | 5.7044e-05
1 | 13882326 | 2016-10-03 08:36 | 2016-10-03 10:35 | 118 | 1 | 118.95 | 0.00035713 | 0.000348 | 3.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 796151 | FUSE - ELEMENT/LINK (HV) | Reload at X2343 3 x 2 A Lightning | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000348 | 11 | 2017 | 2016-10-03 | C | 1 | 0.000348 | 3.0023e-06
1 | 13883447 | 2016-10-18 13:15 | 2016-10-18 13:48 | 33 | 2 | 66 | 0.00019812 | 0.00018 | 6.0035e-06 | NAPA ID:24088 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | 024088 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1085 | NONE | To install a 400V Disconnector on TP1085. Works location: Hinuera Rd, Matamata. WO 30019182 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 9e-05 | 5.5 | 2017 | 2016-10-18 | B | 2 | 0.00018 | 6.0035e-06
1 | 13883520 | 2016-10-20 09:34 | 2016-10-20 10:44 | 70 | 6 | 420 | 0.0012607 | 0.001206 | 1.801e-05 | NAPA ID:24058 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024058 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S4638 | NONE | change xarm. Works location: Pahoia Rd, Tauranga. WO 30029891 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000603 | 5.5 | 2017 | 2016-10-20 | B | 6 | 0.001206 | 1.801e-05
1 | 13885893 | 2016-10-26 08:31 | 2016-10-26 13:03 | 272 | 7 | 1904 | 0.0057149 | 0.005651 | 2.101e-05 | NAPA ID:23426 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 023426 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 814615 | NONE | replace defective pole 814615. Works location: Donald St, Featherston. WO 30030519 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.0028255 | 5.5 | 2017 | 2016-10-26 | B | 7 | 0.005651 | 2.101e-05
1 | 13887278 | 2016-10-03 18:15 | 2016-10-03 19:35 | 80 | 9 | 720.3 | 0.0021626 | 0.002081 | 2.7021e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7768 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses 7768 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.002081 | 11 | 2017 | 2016-10-03 | C | 9 | 0.002081 | 2.7021e-05
1 | 13887320 | 2016-10-03 18:27 | 2016-10-03 19:51 | 83 | 8 | 671.3333 | 0.0020156 | 0.001943 | 2.4019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X76 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses on transformer X76 caused by lightning. 2 X 3 amp HV fuses replaced | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001943 | 11 | 2017 | 2016-10-03 | C | 8 | 0.001943 | 2.4019e-05
1 | 13888033 | 2016-10-03 00:26 | 2016-10-03 01:30 | 64 | 8 | 512 | 0.0015372 | 0.001465 | 2.4019e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1646 TP1477 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformers TC1646 & TP1477 replaced. Damaged by lightning strike earlier in night. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001465 | 11 | 2017 | 2016-10-03 | C | 8 | 0.001465 | 2.4019e-05
1 | 13888159 | 2016-10-03 21:05 | 2016-10-03 21:26 | 21 | 50 | 1050 | 0.0031525 | 0.002702 | 0.00015012 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L3095 | JUMPER | Repaired 1 x lv joint and checked all connections TX: L3095 Cause: deterioration Nothing else repaired or replaced | F4 | PATEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.002702 | 11 | 2017 | 2016-10-03 | C | 50 | 0.002702 | 0.00015012
1 | 13896130 | 2016-10-04 06:23 | 2016-10-04 07:20 | 57 | 7 | 399.35 | 0.001199 | 0.001135 | 2.1016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 221275 | FUSE - ELEMENT/LINK (HV) | 2x amp HV fuses blown at SF6-003 due to bird strike. Line patrolled & reloaded & Livened | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001135 | 11 | 2017 | 2016-10-04 | C | 7 | 0.001135 | 2.1016e-05
1 | 13896144 | 2016-10-04 06:30 | 2016-10-04 08:32 | 122 | 1 | 122.8 | 0.00036868 | 0.000359 | 3.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 837444 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses 6539 2 x 6A Bird Strike | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000359 | 11 | 2017 | 2016-10-04 | C | 1 | 0.000359 | 3.0023e-06
1 | 13896440 | 2016-10-04 14:00 | 2016-10-04 14:45 | 45 | 2 | 90 | 0.00027021 | 0.000252 | 6.0046e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1255 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 R request to replace 50 KVA tx N1255 at pole 850662 Replaced transformer N1255, own sis & ap | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.000252 | 11 | 2017 | 2016-10-04 | C | 2 | 0.000252 | 6.0046e-06
1 | 13896529 | 2016-10-03 19:00 | 2016-10-03 20:35 | 95 | 2 | 190 | 0.00057045 | 0.000552 | 6.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 269759 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses FP1032 2 x 6A Lightning This outage was a recreation so the off time is estimated at around the time all the other outages occurred. On time was recorded on sheet. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000552 | 11 | 2017 | 2016-10-03 | C | 2 | 0.000552 | 6.0046e-06
1 | 13896592 | 2016-10-04 07:35 | 2016-10-04 09:00 | 84 | 4 | 338.4 | 0.001016 | 0.000979 | 1.2009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1821 | FUSE - ELEMENT/LINK (HV) | 2x amp HV fuses blown at fuses FP1666 due to swan striking lines. line checked reloaded & livened | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000979 | 11 | 2017 | 2016-10-04 | C | 4 | 0.000979 | 1.2009e-05
1 | 13896928 | 2016-10-25 08:40 | 2016-10-25 14:00 | 320 | 6 | 1920 | 0.0057629 | 0.005708 | 1.8009e-05 | NAPA ID:24123 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 024123 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC360 | NONE | Upgrade transformer TC360 to a 50kVA. Works location: Troughton Rd, Waharoa. WO 30019176 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.002854 | 5.5 | 2017 | 2016-10-25 | B | 6 | 0.005708 | 1.8009e-05
1 | 13896937 | 2016-10-25 14:35 | 2016-10-25 14:56 | 21 | 6 | 126 | 0.00037819 | 0.000324 | 1.8009e-05 | NAPA ID:24913 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024913 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5474 | NONE | Install set of LV fuses on transformer TC5474. Works location: Ngutumanga Rd, Waihou. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-10-25 | B | 6 | 0.000324 | 1.8009e-05
1 | 13896998 | 2016-10-25 09:45 | 2016-10-25 12:26 | 161 | 1 | 161 | 0.00048325 | 0.000474 | 3.0015e-06 | NAPA ID:24739 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024739 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4029 | NONE | Physically disconnect 11kV leads from main line using live-line techniques and then replace 11kV drop-out fuse and install LV disconnector on the transformer. Reconnect leads to main line using live-line techniques. Works location: Ngutumanga Rd, Waihou. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000237 | 5.5 | 2017 | 2016-10-25 | B | 1 | 0.000474 | 3.0015e-06
1 | 13897110 | 2016-10-03 21:46 | 2016-10-03 23:30 | 104 | 2 | 208 | 0.00062449 | 0.000606 | 6.0046e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M0216 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced Transformer TP1477 damaged by Lightning | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000606 | 11 | 2017 | 2016-10-03 | C | 2 | 0.000606 | 6.0046e-06
1 | 13897579 | 2016-10-25 09:15 | 2016-10-25 16:10 | 415 | 9 | 3735 | 0.011211 | 0.011129 | 2.7014e-05 | NAPA ID:24012 TP_GREYTOWN GXP > MARTINBOROUGH SUB > COLOGNE ST | 11 | Planned | 024012 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7375 | NONE | isolation for tree trimming hikawera road m/boro from fuses 7375 to end of dead end line treescape supplyed poles for issuer apply earths at poles 816694 and 357364 downer have not seen weather access will be a problem with these site on the day will co ordninate with n o c if issuer apply earth are move to more accessable site. Works location: Hikawera Rd. WO 30026281 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.0055645 | 5.5 | 2017 | 2016-10-25 | B | 9 | 0.011129 | 2.7014e-05
1 | 13898258 | 2016-10-28 09:30 | 2016-10-28 16:26 | 416 | 4 | 1664 | 0.0049944 | 0.004958 | 1.2006e-05 | NAPA ID:23594 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023594 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7462 | NONE | Replace multiple poles. Works location: Racecourse Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002479 | 5.5 | 2017 | 2016-10-28 | B | 4 | 0.004958 | 1.2006e-05
1 | 13898376 | 2016-10-04 11:00 | 2016-10-04 11:25 | 25 | 8 | 200 | 0.00060046 | 0.000528 | 2.4018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3287 | JUMPER | Found jumper broken at TC3287. Isolated at fuses FP947, repaired jumper & relivened | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000528 | 11 | 2017 | 2016-10-04 | C | 8 | 0.000528 | 2.4018e-05
1 | 13898462 | 2016-10-27 09:30 | 2016-10-27 14:30 | 300 | 34 | 10200 | 0.030615 | 0.030308 | 0.00010205 | NAPA ID:24153 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | 024153 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 756230 | NONE | We are installing a new 11kv Sectos switch at pole 756230 feeding a new 11kv underground cable section to 11kv switch gear 264/2. We are removing the 11kv over head section of wire because of the palm trees. We are removing 11kv ABS 484. Works location: Hau Lane. WO 30031074 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.015154 | 5.5 | 2017 | 2016-10-27 | B | 34 | 0.030308 | 0.00010205
1 | 13898661 | 2016-10-04 09:43 | 2016-10-04 09:47 | 4 | 13 | 52 | 0.00015612 | 3.9e-05 | 3.903e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 212817 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Tranformer TE4-031 isolated to lower taps because of high voltage from PQI report. carried out by Shay Deegan | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 3.9e-05 | 11 | 2017 | 2016-10-04 | C | 13 | 3.9e-05 | 3.903e-05
1 | 13899644 | 2016-10-28 09:50 | 2016-10-28 14:45 | 295 | 25 | 7375 | 0.022136 | 0.02191 | 7.5036e-05 | NAPA ID:24080 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 024080 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5348 | NONE | Replace various poles and xarms in work area. Works location: Ross Rd. WO 30018291 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.010955 | 3.3 | 2017 | 2016-10-28 | B | 25 | 0.02191 | 7.5036e-05
1 | 13899938 | 2016-10-04 14:23 | 2016-10-04 15:51 | 88 | 171 | 15048 | 0.045179 | 0.043638 | 0.00051339 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811281 | JUMPER | blown jumper at pole 811281 used 2 joints a n 1m conductor isolated at fuses 7362 7330 8179 Abs 5543 | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.043638 | 11 | 2017 | 2016-10-04 | C | 171 | 0.043638 | 0.00051339
1 | 13900033 | 2016-10-31 09:33 | 2016-10-31 14:20 | 287 | 4 | 1148 | 0.0034455 | 0.003409 | 1.2005e-05 | NAPA ID:24102 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 024102 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2272 | NONE | To replace the 11kV arm, 11kV Fuse arm, 400V arm & install LV Isolator. Works location: Hwy 5, Tirau. WO 30019182 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0017045 | 5.5 | 2017 | 2016-10-31 | B | 4 | 0.003409 | 1.2005e-05
1 | 13900045 | 2016-10-07 09:00 | 2016-10-07 16:57 | 476 | 69 | 32861.25 | 0.098656 | 0.098034 | 0.00020715 | NAPA ID:24053 TP_BUNNYTHORPE GXP > FEILDING SUB > WORKS | 11 | Planned | 024053 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | This is a Powerco tender, to replace 33kv xarms and poles, and 11kv xarms and hardware between 2 pole structure P32325/P32326 and 4 pole structure P32397/P32396/P32395/P32398. Note: Per switching will need to be done on 33kV prior to 9am to ensure AP can be issued at 9am | F2 | WORKS | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.049017 | 5.5 | 2017 | 2016-10-07 | B | 69 | 0.098034 | 0.00020715
1 | 13900085 | 2016-10-04 11:19 | 2016-10-04 12:16 | 57 | 1 | 57.0833 | 0.00017138 | 0.000162 | 3.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1209 | UNKNOWN | 1R no power - have checked and seems to be fed off TX that is not part of planned outage 24188 in area. Transformer feed is 1209. Emailed NI for update. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000162 | 11 | 2017 | 2016-10-04 | C | 1 | 0.000162 | 3.0023e-06
1 | 13900455 | 2016-10-25 09:15 | 2016-10-25 13:14 | 239 | 55 | 13145 | 0.039455 | 0.038959 | 0.00016508 | NAPA ID:23636 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023636 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP 66, 67 | NONE | Replace poles,hardware and conductor. Pukehina Parade, Pongakawa, Te Matai. W/O 30019859. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.01948 | 5.5 | 2017 | 2016-10-25 | B | 55 | 0.038959 | 0.00016508
1 | 13900969 | 2016-10-27 09:25 | 2016-10-27 14:50 | 325 | 55 | 17875 | 0.053651 | 0.053155 | 0.00016508 | NAPA ID:23648 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023648 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace poles,hardware and conductor | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.026578 | 5.5 | 2017 | 2016-10-27 | B | 55 | 0.053155 | 0.00016508
1 | 13901632 | 2016-10-04 14:12 | 2016-10-04 15:33 | 80 | 3 | 241.75 | 0.00072581 | 0.000698 | 9.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 762438 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 5172 2 x 2A Bird strike | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000698 | 11 | 2017 | 2016-10-04 | C | 3 | 0.000698 | 9.0069e-06
1 | 13902184 | 2016-10-05 18:40 | 2016-10-05 19:20 | 40 | 26 | 1040 | 0.0031224 | 0.002888 | 7.8059e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F1280 | CROSSARM - WHOLE ASSEMBLY | Check for safety, old rotting crossarm HV Line isolated between ABS IC797 & 720 to replace crossarm on pole F1280. Materials required - 1 x 33kv crossarms, 3 x pins & insulators, 3 x binders. All supply restored. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.002888 | 11 | 2017 | 2016-10-05 | C | 26 | 0.002888 | 7.8059e-05
1 | 13903339 | 2016-10-04 19:28 | 2016-10-04 21:26 | 118 | 208 | 218 | 0.0006545 | 0 | 6.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | NG382 | FUSE - ELEMENT/LINK (HV) | ARC A+B+C Phase fault Report received of lines down in a paddock on investigation found to be fuses blown @ NG382 Replaced 2x 10a HV fuses | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-10-04 | C | 208 | 0 | 6.0046e-06
1 | 13904337 | 2016-11-01 09:30 | 2016-11-01 15:08 | 338 | 60 | 20280 | 0.060866 | 0.060325 | 0.00018008 | NAPA ID:25108 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 025108 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 747538, 747541 | NONE | Replace pole 747538 and reinstall existing tx 1931N. Remove abs 577 from network. removal of conductor between poles 747538 and 747541. 1564 Egmont Road, Egmont Village, Inglewood, Carrington. W/O 30032634 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.030162 | 5.5 | 2017 | 2016-11-01 | B | 60 | 0.060325 | 0.00018008
1 | 13904573 | 2016-10-05 08:25 | 2016-10-05 10:19 | 114 | 2 | 228.2667 | 0.00068532 | 0.000667 | 6.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819275 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuses cuase bird | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000667 | 11 | 2017 | 2016-10-05 | C | 2 | 0.000667 | 6.0045e-06
1 | 13905317 | 2016-10-19 23:00 | 2016-10-20 00:08 | 68 | 357 | 24276 | 0.072871 | 0.069655 | 0.0010716 | NAPA ID:25268 TP_MASTERTON GXP > CLAREVILLE SUB > WYNDHAM ST | 11 | Planned | 025268 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C833 TX T2919 | NONE | Replace links 7589. William Wong Place, Carterton, Masterton. W/O 13905317. | F2 | WYNDHAM ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.034827 | 5.5 | 2017 | 2016-10-19 | B | 357 | 0.069655 | 0.0010716
1 | 13905722 | 2016-10-05 10:04 | 2016-10-05 11:29 | 84 | 8 | 678.4 | 0.0020367 | 0.001964 | 2.4018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13630 | FUSE - ELEMENT/LINK (HV) | Check to see if 13905936 (451 Woodlands Rd ) is related fuses FC2225? 2 x 6amp wind | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.001964 | 11 | 2017 | 2016-10-05 | C | 8 | 0.001964 | 2.4018e-05
1 | 13906155 | 2016-10-26 09:45 | 2016-10-26 16:10 | 385 | 18 | 6930 | 0.0208 | 0.020638 | 5.4027e-05 | NAPA ID:24647 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 024647 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36426 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Install Dble 11 m Transformer poles beside 2 pole structure. Temp number 7419 is to be applied to old TX T1/335, the new transformer will be livened with existing number T1/335 applied to it. The old site temp 7419 will be removed at a later date once all LV has been transferred to the new transformer Work earlier in the week meant Fuses already installed so Transformer only outage | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.010319 | 5.5 | 2017 | 2016-10-26 | B | 18 | 0.020638 | 5.4027e-05
1 | 13906162 | 2016-10-25 09:45 | 2016-10-25 14:40 | 295 | 93 | 27435 | 0.082347 | 0.081509 | 0.00027914 | NAPA ID:24640 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 024640 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/335 | NONE | Install Dble 11 m Transformer poles beside 2 pole structure. Temp number 7419 is to be applied to old TX T1/335, the new transformer will be livened with existing number T1/335 applied to it. The old site temp 7419 will be removed at a later date once all LV has been transferred to the new transformer. Harris Lane, Sanson, Bunnythorpe. W/O 30018765. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.040754 | 5.5 | 2017 | 2016-10-25 | B | 93 | 0.081509 | 0.00027914
1 | 13906267 | 2016-10-07 10:23 | 2016-10-07 18:24 | 481 | 207 | 99567 | 0.29892 | 0.29706 | 0.00062146 | NAPA ID:25283 TP_WAIKINO GXP | 11 | Planned | 025283 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N2212 | POLE | This job ran over time by more than 3 hours. Power was suppose to be back on by 15:00. supply wasn't restored until 18:24. Part of the reason for this was the weater. Crew advised Control that due to swamp ground the Pole kept sinking - needed to get more loose metal to support pole. Remove pole N2212 and install new pole away from eroded river wall | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.14853 | 5.5 | 2017 | 2016-10-07 | B | 207 | 0.29706 | 0.00062146
1 | 13909186 | 2016-10-25 09:55 | 2016-10-25 15:16 | 321 | 1 | 321 | 0.00096349 | 0.000954 | 3.0015e-06 | NAPA ID:24011 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024011 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-025 | NONE | Short spur to pump. Change out 3 x HV Poles. 221 Kumikumi Road, Lower Kaimai, Tauranga. W/O 30017842. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000477 | 5.5 | 2017 | 2016-10-25 | B | 1 | 0.000954 | 3.0015e-06
1 | 13909554 | 2016-10-26 10:29 | 2016-10-26 15:35 | 306 | 1 | 306 | 0.00091846 | 0.000909 | 3.0014e-06 | NAPA ID:24017 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024017 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-025 | NONE | Re-conductor 300mtr down to Pump TX. 211 Kumikumi Road, Lower Kaimai, Tauranga. W/O 30017842. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0004545 | 5.5 | 2017 | 2016-10-26 | B | 1 | 0.000909 | 3.0014e-06
1 | 13911257 | 2016-10-05 14:45 | 2016-10-05 15:38 | 53 | 3 | 159 | 0.00047736 | 0.00045 | 9.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850888 | CROSSARM - COMPONENT(S) ONLY | Check for safety Nut has come off the (crossarm?) on this pole, is on a significant lean, only holding on by the stays. Reported by Henry (06) 761 240 Advised Joanne at svs hub of job Isolated at fuses TA181 to make repairs, Replaced bolt for crossarm | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.00045 | 11 | 2017 | 2016-10-05 | C | 3 | 0.00045 | 9.0068e-06
1 | 13913664 | 2016-11-01 09:00 | 2016-11-01 15:14 | 374 | 86 | 32164 | 0.096533 | 0.095758 | 0.00025811 | NAPA ID:24114 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024114 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses LC2142 | NONE | To replace 11kV & 400V Arms Isolated side of Fuses LC2142. Ngutamanga Road, Waihou, Te Aroa, Mikkelsen. W/O 30017829. Switching under 25779 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.047879 | 5.5 | 2017 | 2016-11-01 | B | 86 | 0.095758 | 0.00025811
1 | 13914146 | 2016-10-27 08:32 | 2016-10-27 15:10 | 398 | 92 | 36247 | 0.10879 | 0.10797 | 0.00027613 | NAPA ID:23430 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 023430 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX T3334 | NONE | replace defective poles between poles 814521 & 814539. Waite Street, Featherston, Greytown. W/O 30030519. | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.053983 | 5.5 | 2017 | 2016-10-27 | B | 92 | 0.10797 | 0.00027613
1 | 13914184 | 2016-11-02 09:15 | 2016-11-02 12:22 | 187 | 61 | 11345 | 0.034049 | 0.033499 | 0.00018308 | NAPA ID:24469 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | 024469 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX T3300 | NONE | Remove temporary isolation points (HV fuses) at poles 712945 & 712918 and reinstate conductor to original state. Arawhata Road, Oaonui, Tasman, Opunake. W/O 30030991. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.01675 | 5.5 | 2017 | 2016-11-02 | B | 61 | 0.033499 | 0.00018308
1 | 13914210 | 2016-10-05 14:57 | 2016-10-05 19:57 | 300 | 873 | 64353.6333 | 0.19321 | 0.18534 | 0.00084364 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 393504 | CROSSARM - WHOLE ASSEMBLY | Fire service advised tree has fallen across power lines near this address, used nearest ICP - called in by person white baiting in the area Fire F2163382 333 Papaiti Road, Wanganui white baiters number 022 102 8245 x1127 - advised paul in control Repaired HV & LV crossarms @ pole 393504 . Cursorary line patrol carried out beyond CB 575 with nothing obvious found supply restored | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.18534 | 11 | 2017 | 2016-10-05 | C | 873 | 0.18534 | 0.00084364
1 | 13915450 | 2016-11-08 09:15 | 2016-11-08 15:14 | 359 | 95 | 34105 | 0.10235 | 0.10149 | 0.0002851 | NAPA ID:24158 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 024158 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1241 | NONE | Change x-arms DDO's ect | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.050747 | 5.5 | 2017 | 2016-11-08 | B | 95 | 0.10149 | 0.0002851
1 | 13915564 | 2016-10-06 10:49 | 2016-10-06 11:46 | 57 | 59 | 3363 | 0.010097 | 0.009565 | 0.00017713 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | G0170 | POLE | Check for safety - Pole just before the bridge has been taken out a car over night. Lines are still up but the pole is on the ground. Customer has advised this happened over night some time and he has just discovered it. No loss of supply Have advised SMC 11kv network pole on the ground, OH wires still at a acceptable height. Pole will need to be replaced No loss of supply NDR 55726 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.009565 | 11 | 2017 | 2016-10-06 | C | 59 | 0.009565 | 0.00017713
1 | 13915711 | 2016-10-05 13:48 | 2016-10-05 16:25 | 156 | 24 | 3747.2 | 0.01125 | 0.011033 | 7.2055e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 22457 | JUMPER | Broken Jumper found at Pole 22457 - Isolated at Fuses SG5-001 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.011033 | 11 | 2017 | 2016-10-05 | C | 24 | 0.011033 | 7.2055e-05
1 | 13916002 | 2016-10-05 16:17 | 2016-10-05 20:03 | 226 | 1 | 226.3 | 0.00067941 | 0.00067 | 3.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 831056 | JUMPER | Check for safety - Wind has caused lines to come down and they are on the Street ETA required - Fire Comms Wellington Fire comms unable to provide customer details. 16.25 - ETA 15mins, advised fire comms | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.00067 | 11 | 2017 | 2016-10-05 | C | 1 | 0.00067 | 3.0022e-06
1 | 13916179 | 2016-10-05 17:16 | 2016-10-05 18:04 | 48 | 262 | 12576 | 0.037757 | 0.035396 | 0.0007866 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 831056 | JUMPER | Have been unable to get in contact with customer. Advised SMC Jumper broken at pole 831056. Isolation at ABS S181, S96 &S99 back feed from ABS S141 CHA C857. material 1m 16mm copper conductor 2xHD12 connecters See Safety Manager: | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.035396 | 11 | 2017 | 2016-10-05 | C | 262 | 0.035396 | 0.0007866
1 | 13916266 | 2016-10-05 16:40 | 2016-10-05 17:42 | 61 | 1 | 61.75 | 0.00018539 | 0.000176 | 3.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | Fuses M83. 2 X 6 amp Wind | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000176 | 11 | 2017 | 2016-10-05 | C | 1 | 0.000176 | 3.0022e-06
1 | 13916318 | 2016-10-05 16:56 | 2016-10-05 21:54 | 298 | 145 | 31027.8333 | 0.093154 | 0.091848 | 0.00068752 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227517 | CONDUCTOR - REPAIR/REHANG | line down at pole 227517. isolations pushed out recloser S6029 due to no isolation at regulator 9148/1. partial back feed from PKW CB 3 via sectionaliser 9679/2. isolations at ABS SE8-013 ABS SE8-004 ABS SE8-003 Links IP100. Material 5m conductor 3 sleeves | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.091848 | 11 | 2017 | 2016-10-05 | C | 145 | 0.091848 | 0.00068752
1 | 13917628 | 2016-10-05 18:33 | 2016-10-05 18:37 | 4 | 101 | 425.8833 | 0.0012786 | 0.000368 | 0.00030323 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Jumper broken at pole 831056. Isolation at ABS S181, S96 &S99 back feed from ABS S141 CHA C857. material 1m 16mm copper conductor 2xHD12 connectors. This is associated with OMS 13916179. See Safety Manager: | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000368 | 11 | 2017 | 2016-10-05 | C | 101 | 0.000368 | 0.00030323
1 | 13917784 | 2016-10-05 20:05 | 2016-10-05 20:55 | 50 | 2 | 100 | 0.00030023 | 0.000282 | 6.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209724 | JUMPER | Isolation of Transformer TD2-034 due to Broken jumper from fuses to transformer. Own AP issued. materials 1m 16mm copper conductor 2xHD12 connectors | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000282 | 11 | 2017 | 2016-10-05 | C | 2 | 0.000282 | 6.0045e-06
1 | 13918422 | 2016-10-05 23:01 | 2016-10-06 03:20 | 258 | 91 | 9242 | 0.027747 | 0.026927 | 0.00032725 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 851785 | CONDUCTOR - REPAIR/REHANG | Recloser 8156/2 A,B OC Trip, Fault found to be passed ABS S1204. work to continue in the morning Tree found through lines at Pole 851785 - Isolated at ABS S1204 Lines Repaired, used 20 mtrs of conductor 1 x tension joiner, 1 x non tension joiner Faultman to supply NDR # | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.026927 | 11 | 2017 | 2016-10-05 | C | 91 | 0.026927 | 0.00032725
1 | 13918821 | 2016-10-06 01:32 | 2016-10-06 03:08 | 96 | 345 | 29579 | 0.088803 | 0.085695 | 0.0011619 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | cb 6 | UNKNOWN | CB 6 Trip A,B,C O/C, OC INVT. LFI's flashing at Sw/Gear 9567/4, line sectionalised & patrolled. No LFI's flasing past 9660. Feeder restored. no fault found | F3 | STERLING GATE | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.085695 | 11 | 2017 | 2016-10-06 | C | 345 | 0.085695 | 0.0011619
1 | 13919929 | 2016-10-06 07:16 | 2016-10-06 10:32 | 195 | 10 | 1953 | 0.0058634 | 0.005773 | 3.0022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712499 | FUSE - ELEMENT/LINK (HV) | 100 cows to be milked. 3 x 6amp fuse lightening | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.005773 | 11 | 2017 | 2016-10-06 | C | 10 | 0.005773 | 3.0022e-05
1 | 13920042 | 2016-10-06 07:41 | 2016-10-06 10:17 | 156 | 1 | 156.3167 | 0.0004693 | 0.00046 | 3.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762052 | FUSE - ELEMENT/LINK (HV) | **Invoicing - the FM did not go to site for this job. Power was restored on OMS 13920250 - appears this ICP has been loaded against incorrect TX. Site visit request in to BI team. Closed with same notes. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00046 | 11 | 2017 | 2016-10-06 | C | 1 | 0.00046 | 3.0022e-06
1 | 13920070 | 2016-10-27 09:05 | 2016-10-27 15:15 | 370 | 5 | 1850 | 0.0055527 | 0.005507 | 1.5007e-05 | NAPA ID:24052 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 024052 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 804675, 804661 | NONE | Replacing railway iron poles and X arms. State Highway 1, Aldworth Road, Hunterville, Marton. W/O 30018289. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.0027535 | 5.5 | 2017 | 2016-10-27 | B | 5 | 0.005507 | 1.5007e-05
1 | 13920120 | 2016-10-06 10:43 | 2016-10-06 11:25 | 42 | 16 | 672 | 0.0020175 | 0.001873 | 4.8036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 824951 | JUMPER | 9:58am - FM advised jumper hanging off 11kV. Will work through Control for isolation. 1 jumper blown isolate at Fuses 7856 materials 1 sleeve 1/2 mtr conductor 1 jumper | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001873 | 11 | 2017 | 2016-10-06 | C | 16 | 0.001873 | 4.8036e-05
1 | 13920250 | 2016-10-06 08:24 | 2016-10-06 09:44 | 80 | 7 | 561.05 | 0.0016844 | 0.001621 | 2.1016e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762052 | FUSE - ELEMENT/LINK (HV) | 5268 2x10 cause weather | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.001621 | 6.6 | 2017 | 2016-10-06 | C | 7 | 0.001621 | 2.1016e-05
1 | 13920516 | 2016-10-06 08:39 | 2016-10-06 09:49 | 69 | 4 | 279.5333 | 0.00083923 | 0.000803 | 1.2009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712917 | FUSE - ELEMENT/LINK (HV) | Transformer 20 metres down the road from the cow shed, made a loud bang Advised it sounded like it blew up, and now has no power supply to the cow shed called through to SMC 2 x 2amp lightning | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000803 | 11 | 2017 | 2016-10-06 | C | 4 | 0.000803 | 1.2009e-05
1 | 13920544 | 2016-10-06 08:41 | 2016-10-06 11:17 | 156 | 1 | 156.1333 | 0.00046875 | 0.000459 | 3.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835414 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp fuse weather | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.000459 | 11 | 2017 | 2016-10-06 | C | 1 | 0.000459 | 3.0022e-06
1 | 13920561 | 2016-10-06 08:43 | 2016-10-06 10:14 | 91 | 7 | 639.1 | 0.0019187 | 0.001855 | 2.1016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712901 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp lightning | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001855 | 11 | 2017 | 2016-10-06 | C | 7 | 0.001855 | 2.1016e-05
1 | 13920685 | 2016-11-09 09:45 | 2016-11-09 13:31 | 226 | 3 | 678 | 0.0020347 | 0.002007 | 9.0029e-06 | NAPA ID:25061 TP_HUIRANGI GXP > INGLEWOOD SUB > KAIMATA | 6.6 | Planned | 025061 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 759631 | NONE | Install Lightning Arrestors & Reblock Pole & Replace Staywires @ Transformer 2329T | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.0010035 | 3.3 | 2017 | 2016-11-09 | B | 3 | 0.002007 | 9.0029e-06
1 | 13920798 | 2016-11-07 09:28 | 2016-11-07 11:20 | 112 | 23 | 2576 | 0.0077307 | 0.007523 | 6.9024e-05 | NAPA ID:24715 TP_STRATFORD GXP > ELTHAM SUB > TE ROTI | 11 | Planned | 024715 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4937 | NONE | Replacing rotten crossarm at pole 733482 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0037615 | 5.5 | 2017 | 2016-11-07 | B | 23 | 0.007523 | 6.9024e-05
1 | 13922574 | 2016-11-08 09:30 | 2016-11-08 15:06 | 336 | 20 | 6720 | 0.020167 | 0.019986 | 6.002e-05 | NAPA ID:24445 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 024445 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12109 | NONE | Replace various poles and xarms in work area | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.009993 | 3.3 | 2017 | 2016-11-08 | B | 20 | 0.019986 | 6.002e-05
1 | 13922635 | 2016-11-10 09:30 | 2016-11-10 15:21 | 351 | 20 | 7020 | 0.021067 | 0.020886 | 6.0019e-05 | NAPA ID:24446 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 024446 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12109 | NONE | Replace various poles and xarms in work area | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.010443 | 3.3 | 2017 | 2016-11-10 | B | 20 | 0.020886 | 6.0019e-05
1 | 13922700 | 2016-10-13 09:38 | 2016-10-13 15:20 | 342 | 27 | 9234 | 0.02772 | 0.027477 | 8.1054e-05 | NAPA ID:24192 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 024192 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 2106 | NONE | Pole Replacement of R12922 to Faciliate new RL15 at site. Replace Transformer TC3381 (like for like). Pole R12922 Wentworth Valley Road, Whangamata, Waikino. W/O 30019235. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.013739 | 5.5 | 2017 | 2016-10-13 | B | 27 | 0.027477 | 8.1054e-05
1 | 13922713 | 2016-11-29 09:30 | 2016-11-29 14:56 | 326 | 25 | 8150 | 0.024451 | 0.024226 | 7.5004e-05 | NAPA ID:24447 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 024447 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5348 | NONE | Reconductor 6.6kv lines | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.012113 | 3.3 | 2017 | 2016-11-29 | B | 25 | 0.024226 | 7.5004e-05
1 | 13922808 | 2016-11-03 10:00 | 2016-11-03 10:20 | 20 | 9 | 180 | 0.00054022 | 0.000459 | 2.7011e-05 | NAPA ID:25013 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025013 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To install a 400V fuse disconnector on TC508 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0002295 | 5.5 | 2017 | 2016-11-03 | B | 9 | 0.000459 | 2.7011e-05
1 | 13922871 | 2016-11-03 12:00 | 2016-11-03 12:25 | 25 | 2 | 50 | 0.00015006 | 0.000132 | 6.0024e-06 | NAPA ID:25015 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 0.41499999999999998 | Planned | 025015 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | . | NONE | To install a 400V Fuse Disconnector on TC1276 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 6.6e-05 | 0.2075 | 2017 | 2016-11-03 | B | 2 | 0.000132 | 6.0024e-06
1 | 13922882 | 2016-11-03 14:00 | 2016-11-03 14:20 | 20 | 8 | 160 | 0.00048019 | 0.000408 | 2.401e-05 | NAPA ID:25016 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025016 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To install a 400V fuse unit on TC2304 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000204 | 5.5 | 2017 | 2016-11-03 | B | 8 | 0.000408 | 2.401e-05
1 | 13922899 | 2016-11-07 14:35 | 2016-11-07 15:07 | 32 | 10 | 320 | 0.00096034 | 0.00087 | 3.0011e-05 | NAPA ID:25018 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025018 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC765 | NONE | To install a 400V fuse Disconnector on TC765 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000435 | 5.5 | 2017 | 2016-11-07 | B | 10 | 0.00087 | 3.0011e-05
1 | 13922922 | 2016-11-08 10:00 | 2016-11-08 10:40 | 40 | 7 | 280 | 0.00084029 | 0.000777 | 2.1007e-05 | NAPA ID:25019 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025019 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1423 | NONE | To install a 400V Fuse Disconnector on TC1423 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0003885 | 5.5 | 2017 | 2016-11-08 | B | 7 | 0.000777 | 2.1007e-05
1 | 13923182 | 2016-11-08 12:00 | 2016-11-08 12:25 | 25 | 3 | 75 | 0.00022508 | 0.000198 | 9.003e-06 | NAPA ID:25020 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025020 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC368 | NONE | To install a 400V Fuse Disconnector on TC368 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 9.9e-05 | 5.5 | 2017 | 2016-11-08 | B | 3 | 0.000198 | 9.003e-06
1 | 13923203 | 2016-11-08 14:00 | 2016-11-08 14:58 | 58 | 2 | 116 | 0.00034812 | 0.00033 | 6.002e-06 | NAPA ID:25021 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025021 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1007 | NONE | To install a 400V Fuse Disconnector on tP1804 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000165 | 5.5 | 2017 | 2016-11-08 | B | 2 | 0.00033 | 6.002e-06
1 | 13923262 | 2016-11-09 09:40 | 2016-11-09 10:25 | 45 | 3 | 135 | 0.00040513 | 0.000378 | 9.0029e-06 | NAPA ID:25022 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025022 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12826 | NONE | To install a 400V Fuse Disconnector on TC1995 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000189 | 5.5 | 2017 | 2016-11-09 | B | 3 | 0.000378 | 9.0029e-06
1 | 13923305 | 2016-11-09 11:30 | 2016-11-09 12:30 | 60 | 4 | 240 | 0.00072023 | 0.000684 | 1.2004e-05 | NAPA ID:25023 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025023 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12867 | NONE | To install a 400V Fuse Disconnector on TC2303 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000342 | 5.5 | 2017 | 2016-11-09 | B | 4 | 0.000684 | 1.2004e-05
1 | 13923623 | 2016-10-06 08:39 | 2016-10-06 09:38 | 59 | 1 | 59 | 0.00017713 | 0.000168 | 3.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 859250 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp lightning | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000168 | 11 | 2017 | 2016-10-06 | C | 1 | 0.000168 | 3.0022e-06
1 | 13923724 | 2016-11-09 13:45 | 2016-11-09 14:05 | 20 | 6 | 120 | 0.00036012 | 0.000306 | 1.8006e-05 | NAPA ID:25024 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025024 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12883 | NONE | To install a 400V Fuse Disconnector on TC370 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000153 | 5.5 | 2017 | 2016-11-09 | B | 6 | 0.000306 | 1.8006e-05
1 | 13923798 | 2016-10-06 11:51 | 2016-10-06 12:00 | 8 | 334 | 2833.4333 | 0.0085066 | 0.005498 | 0.0010027 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | no outage gis error | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.005498 | 11 | 2017 | 2016-10-06 | C | 334 | 0.005498 | 0.0010027
1 | 13924602 | 2016-11-10 12:15 | 2016-11-10 13:30 | 75 | 4 | 300 | 0.00090028 | 0.000864 | 1.2004e-05 | NAPA ID:25026 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025026 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D1672 | NONE | To install a 400V Fuse disconnector on TC1694 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000432 | 5.5 | 2017 | 2016-11-10 | B | 4 | 0.000864 | 1.2004e-05
1 | 13924664 | 2016-11-30 12:30 | 2016-11-30 13:40 | 70 | 4 | 280 | 0.00084003 | 0.000804 | 1.2e-05 | NAPA ID:25030 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025030 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12975 | NONE | To install a 400V Fuse Disconnector on TC2519 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000402 | 5.5 | 2017 | 2016-11-30 | B | 4 | 0.000804 | 1.2e-05
1 | 13924692 | 2016-11-30 10:24 | 2016-11-30 11:35 | 71 | 8 | 568 | 0.0017041 | 0.001632 | 2.4001e-05 | NAPA ID:25031 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025031 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX TC 667 | NONE | To install a 400V Fuse Disconnector on TC667. 1 Waimakarere Road , Tirau, Hinuera. W/O 30019182. | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000816 | 5.5 | 2017 | 2016-11-30 | B | 8 | 0.001632 | 2.4001e-05
1 | 13924741 | 2016-10-06 13:48 | 2016-10-06 18:20 | 272 | 7 | 1905.9833 | 0.0057222 | 0.005659 | 2.1016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | T3345 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace faulty transformer T3345 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.005659 | 11 | 2017 | 2016-10-06 | C | 7 | 0.005659 | 2.1016e-05
1 | 13924898 | 2016-10-30 09:01 | 2016-10-30 16:27 | 446 | 253 | 112838 | 0.33867 | 0.33639 | 0.00075934 | NAPA ID:24172 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 024172 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX's T2721, T579 | NONE | Replace 11kv conductor and poles at multiple site. State Highway 2, Willow Park Drive, Masterton. W/O 30030270. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.16819 | 5.5 | 2017 | 2016-10-30 | B | 253 | 0.33639 | 0.00075934
1 | 13924940 | 2016-11-11 09:15 | 2016-11-11 11:36 | 141 | 4 | 564 | 0.0016925 | 0.001656 | 1.2004e-05 | NAPA ID:25130 TP_STRATFORD GXP > ELTHAM SUB > RAWHITIROA | 11 | Planned | 025130 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 2168T | NONE | Install new 11m Busck pole mid span to stop 11kv line clash. 345 Rawhitiroa Road, Eltham, Stratford. W/O 30033484. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000828 | 5.5 | 2017 | 2016-11-11 | B | 4 | 0.001656 | 1.2004e-05
1 | 13924948 | 2016-11-14 09:00 | 2016-11-14 13:57 | 297 | 8 | 2374 | 0.0071238 | 0.007051 | 2.4006e-05 | NAPA ID:24118 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 024118 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3684 | NONE | Upgrade transformer TC3684 to a 50kVA and upgrade 400V underbuilt conductor between poles I1594 and I1598. 198-238 Morrinsville-Walton Road, Morrinsville, Piako. W/O 30019176. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0035255 | 5.5 | 2017 | 2016-11-14 | B | 8 | 0.007051 | 2.4006e-05
1 | 13925116 | 2016-11-04 11:00 | 2016-11-04 15:06 | 246 | 60 | 13665 | 0.041011 | 0.04047 | 0.00018007 | NAPA ID:25118 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 025118 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 747538, 747514 | NONE | closing line break. installing new regulator site 12171 ready for commissioning. 1564 Egmont Road, Egmont Village, Inglewood, Carrington. W/O 30032634. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.020235 | 5.5 | 2017 | 2016-11-04 | B | 60 | 0.04047 | 0.00018007
1 | 13925144 | 2016-10-26 09:37 | 2016-10-26 15:29 | 352 | 11 | 3872 | 0.011622 | 0.011522 | 3.3016e-05 | NAPA ID:24062 TP_BUNNYTHORPE GXP | 11 | Planned | 024062 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P32397 | POLE | This is a Powerco tender, to replace 33kv xarms and poles, and 11kv xarms and hardware between 4 pole structure P32397/P32396/P32395/P32398 and P38742. Note: Per switching will need to be done on 33kV prior to 9am to ensure AP can be issued at 9am | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.005761 | 5.5 | 2017 | 2016-10-26 | B | 11 | 0.011522 | 3.3016e-05
1 | 13927451 | 2016-10-07 09:53 | 2016-10-07 11:08 | 75 | 17 | 1275 | 0.0038278 | 0.003674 | 5.1037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 723960 | POLE | Car vs pole Called in by Police P026943698. Fire will be in attendance. Police call by member of public no rapid number available. ( LIV LI1 ) Emergency switching to replace pole 723960 Isolation at Fuses LI 107 ( spur no back feed ) pole replaced all service restored Materials 1 x pole, 1 x H/V arm complete NDR 43161 | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.003674 | 11 | 2017 | 2016-10-07 | C | 17 | 0.003674 | 5.1037e-05
1 | 13927552 | 2016-10-05 16:25 | 2016-10-05 17:25 | 60 | 34 | 2040 | 0.0061246 | 0.005818 | 0.00010208 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 816558 | FUSE - ELEMENT/LINK (HV) | 2 x 10amp fuse weather | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.005818 | 11 | 2017 | 2016-10-05 | C | 34 | 0.005818 | 0.00010208
1 | 13928092 | 2016-10-07 09:10 | 2016-10-07 10:38 | 87 | 26 | 2286.2667 | 0.0068638 | 0.006629 | 7.8057e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 783185 | CONDUCTOR - REPAIR/REHANG | Recloser 2713 trip B, C Ph O/C L/O Branch found on lines at Pole 783185, cleared using hot sticks | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.006629 | 11 | 2017 | 2016-10-07 | C | 26 | 0.006629 | 7.8057e-05
1 | 13928333 | 2016-10-07 09:31 | 2016-10-07 09:36 | 5 | 138 | 692.3 | 0.0020784 | 0.000835 | 0.0004143 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | A0417 | CONDUCTOR - REPAIR/REHANG | rec 9402 opened to remove tree branch from line at pole A0417 | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000835 | 11 | 2017 | 2016-10-07 | C | 138 | 0.000835 | 0.0004143
1 | 13928736 | 2016-11-04 09:39 | 2016-11-04 15:15 | 336 | 2 | 672 | 0.0020168 | 0.001998 | 6.0023e-06 | NAPA ID:24540 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 6.6 | Planned | 024540 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 759733 | NONE | to replace trany structure 2576t with new pole and 30kv trany after putting in live line break. 1: OFF LOAD 6.6kV Transformer 2576T. 2:Create 6.6kV Line Break at pole 759733. 3: replace 6.6kV TX 2576T. 4: Close 6.6kV Line Break at pole 759733. 5: Liven new TX 2576T. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000999 | 3.3 | 2017 | 2016-11-04 | B | 2 | 0.001998 | 6.0023e-06
1 | 13929297 | 2016-10-07 11:41 | 2016-10-07 12:08 | 27 | 15 | 405 | 0.0012159 | 0.00108 | 4.5033e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2011868 | CROSSARM - COMPONENT(S) ONLY | Find and fix - HV Roland McLean. Putting in new arm strap bolt. Need to take off power SB3-006. | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.00108 | 11 | 2017 | 2016-10-07 | C | 15 | 0.00108 | 4.5033e-05
1 | 13941070 | 2016-10-07 12:27 | 2016-10-07 13:21 | 53 | 630 | 33841.5 | 0.1016 | 0.095924 | 0.0018914 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | Taihape CB 5 | UNKNOWN | Taihape CB 5 tripped on PH B & C OC - Tree Trimmer near lines under CAC 29439-01 Treescape returned call Confirmed they had contacted lines. Faultman sent to site to check lines before relivening | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.095924 | 11 | 2017 | 2016-10-07 | C | 630 | 0.095924 | 0.0018914
1 | 13944515 | 2016-10-07 14:45 | 2016-10-07 16:24 | 99 | 475 | 20045.6667 | 0.060181 | 0.055902 | 0.001426 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | H1513 | CONDUCTOR - REPAIR/REHANG | 16 Duncan Road, Waharo - Tree was on the line and there was a huge burst of electricity in the house and the tree piece was on fire. Have advised Control link OMS: 13946005 CB 3 tripped C Ph O/C, E/F, L/O tree through line Isolation at ABS 1142 ( spur no back feed ) CB 3 returned to service Line repaired all service restored Materials 3 meters conductor, 5 x H/V comp sleeves NDR No 17993 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.055902 | 11 | 2017 | 2016-10-07 | C | 475 | 0.055902 | 0.001426
1 | 13948617 | 2016-10-08 06:06 | 2016-10-08 07:30 | 84 | 1 | 84.4667 | 0.00025358 | 0.000244 | 3.0021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | D88 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses D88 caused by ducks.Transformer that was affected was T2/220. 2 X 6 amp HV fuses replaced | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.000244 | 11 | 2017 | 2016-10-08 | C | 1 | 0.000244 | 3.0021e-06
1 | 13948698 | 2016-10-08 07:07 | 2016-10-08 13:36 | 388 | 143 | 29236.5167 | 0.087773 | 0.086484 | 0.00042931 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | S13170 | CONDUCTOR - REPAIR/REHANG | 07:45. Report from a member of the public that there is a tree branch on the lines at 519 Kauaeranga Valley Rd. Grant informed. Tree on lines past ABS IC2128. Fault isolated and rest of feeder restored at 08:49 | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.086484 | 11 | 2017 | 2016-10-08 | C | 143 | 0.086484 | 0.00042931
1 | 13949855 | 2016-10-08 15:13 | 2016-10-08 16:30 | 76 | 1 | 76.5167 | 0.00022972 | 0.00022 | 3.0021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at Fuses M83 2 X 3 amp HV fuses replaced | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00022 | 11 | 2017 | 2016-10-08 | C | 1 | 0.00022 | 3.0021e-06
1 | 13950359 | 2016-10-08 18:50 | 2016-10-08 19:44 | 54 | 25 | 1350.4167 | 0.0040542 | 0.003829 | 7.5054e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB U10 Trip, No flags. Patrolled. No fault found. Re livened ok | F4 | WAITARA EAST TOWN | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003829 | 11 | 2017 | 2016-10-08 | C | 25 | 0.003829 | 7.5054e-05
1 | 13951428 | 2016-10-09 04:18 | 2016-10-09 06:18 | 120 | 5 | 600 | 0.0018013 | 0.001756 | 1.5011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | MA233 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV Links | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001756 | 11 | 2017 | 2016-10-09 | C | 5 | 0.001756 | 1.5011e-05
1 | 13951436 | 2016-10-09 04:18 | 2016-10-09 05:40 | 81 | 23 | 1876.4167 | 0.0056332 | 0.005426 | 6.9049e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | MA 233 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at multiple sites due to lightning. Fuses MA 233 - 2 X 10 amp HV fuses replaced. Pole 717799 2 X 60 amp LV HRC fuses replaced. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.005426 | 11 | 2017 | 2016-10-09 | C | 23 | 0.005426 | 6.9049e-05
1 | 13951443 | 2016-10-09 04:19 | 2016-10-09 07:50 | 210 | 1 | 210.8667 | 0.00063305 | 0.000624 | 3.0021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3360T | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses on transformer 3360T 3 X 3 amp HV fuses replaced | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000624 | 11 | 2017 | 2016-10-09 | C | 1 | 0.000624 | 3.0021e-06
1 | 13951449 | 2016-10-09 04:19 | 2016-10-09 07:35 | 195 | 18 | 3520.5 | 0.010569 | 0.010406 | 5.4038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718758 | FUSE - ELEMENT/LINK (HV) | 3 x 20amp lightning | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.010406 | 11 | 2017 | 2016-10-09 | C | 18 | 0.010406 | 5.4038e-05
1 | 13951663 | 2016-10-09 04:45 | 2016-10-10 16:38 | 2152 | 121 | 4632.8833 | 0.013909 | 0.012818 | 0.00036626 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2019 | UNKNOWN | Recloser 2754 tripped on B phase O/C flags, faultman suspects Fuse/Sw 2019 at Silver Fern Farms may be faulty as it is all black and the lid has a bulge in it..Faultman isolated line at ABS 2523 to replace Fuse/Sw 2019. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.012818 | 11 | 2017 | 2016-10-09 | C | 121 | 0.012818 | 0.00036626
1 | 13951961 | 2016-10-09 04:50 | 2016-10-09 11:12 | 382 | 82 | 12305.0833 | 0.036941 | 0.036202 | 0.00049535 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 839919 | INSULATOR | CB C 935 Tripped B,C Ph O/C E/F Damaged Insulator Found at Pole 839919 while sectionlising Isolated at ABS's S161, S707 & S10 - with backfeed Via ABS S176 Replaced HV Insulator - Used 1 x HV Insulator, 1 X Dead End Also fuses reported blown at Fuses 7869, faultman said they had been blown for a number of weeks, line partialed with no fault found fuses reloaded , used 2 x 8 amp fuses | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.036202 | 11 | 2017 | 2016-10-09 | C | 82 | 0.036202 | 0.00049535
1 | 13952047 | 2016-10-09 04:51 | 2016-10-10 13:19 | 1947 | 1 | 1947.9333 | 0.0058479 | 0.005838 | 3.0021e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5192E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace faulty transformer 5192E | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.005838 | 11 | 2017 | 2016-10-09 | C | 1 | 0.005838 | 3.0021e-06
1 | 13952070 | 2016-10-09 04:54 | 2016-10-09 08:19 | 205 | 4 | 820 | 0.0024617 | 0.002425 | 1.2009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | PU364 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at various sites due to lightning Fuses PU 364 - 1 X 10 amp HV fuse replaced. Fuses 6783 - (1 X 2 amp HV fuse replaced) Transformer P2370 - ( 3 X 2 amp HV fuses replaced). This outage is for P2370. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.002425 | 11 | 2017 | 2016-10-09 | C | 4 | 0.002425 | 1.2009e-05
1 | 13952076 | 2016-10-09 04:59 | 2016-10-09 07:46 | 167 | 1099 | 123574.55 | 0.37099 | 0.36109 | 0.0034645 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB 5 | UNKNOWN | CB 5 tripped on O/C & E/F flags, line was patrolled and sectionalised no fault was found suspect due to lightning. Faultman did replace blown fuses at transformer X403 ( 1 X 25 amp HV Fuse 07:10) they also did a safety disconnect to a house off transformer X1159 due to a house fire caused by lightning. | F2 | GILBERD ST | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 0.36109 | 11 | 2017 | 2016-10-09 | C | 1099 | 0.36109 | 0.0034645
1 | 13953187 | 2016-10-09 14:30 | 2016-10-09 15:30 | 60 | 19 | 1140 | 0.0034224 | 0.003251 | 5.704e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M4305 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | HV line down in the middle of the road - 50 meter down the rd from 123 INAHA ROAD advised Customer of safety hazard process. fire coms reported as well event # F2165360 ETA required ETA 15mins - advised fire Ben coms Faultman replaced broken fuse holder on transformer M4305, line was isolated at Fuses MA550. 1 X 11KV fuse holder replaced | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003251 | 11 | 2017 | 2016-10-09 | C | 19 | 0.003251 | 5.704e-05
1 | 13954047 | 2016-10-09 05:46 | 2016-10-09 09:20 | 213 | 9 | 1925.1 | 0.0057794 | 0.005698 | 2.7019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | R46 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses R46 due to lightning. 2 X 10 amp HV fuses replaced | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.005698 | 11 | 2017 | 2016-10-09 | C | 9 | 0.005698 | 2.7019e-05
1 | 13954361 | 2016-10-09 07:32 | 2016-10-09 11:25 | 232 | 1 | 232.7 | 0.0006986 | 0.000689 | 3.0021e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3761T | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer 3761T 2 X 3 amp HV fuses replaced | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000689 | 6.6 | 2017 | 2016-10-09 | C | 1 | 0.000689 | 3.0021e-06
1 | 13954458 | 2016-10-09 07:46 | 2016-10-09 10:30 | 163 | 1 | 163.8 | 0.00049175 | 0.000482 | 3.0021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M2257 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer M2257 2 X 3 amp HV fuses replaced | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.000482 | 11 | 2017 | 2016-10-09 | C | 1 | 0.000482 | 3.0021e-06
1 | 13954627 | 2016-10-09 08:05 | 2016-10-09 11:20 | 194 | 2 | 389.8 | 0.0011702 | 0.001152 | 6.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1482 | FUSE - ELEMENT/LINK (HV) | check if OMS 13956309 (739 Koatanui Road) is reltaed Faultman found blown fuses at transformer X1482. 2 X 2 amp HV fuses replaced | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001152 | 11 | 2017 | 2016-10-09 | C | 2 | 0.001152 | 6.0042e-06
1 | 13954760 | 2016-10-09 08:25 | 2016-10-09 09:25 | 60 | 13 | 780.8667 | 0.0023443 | 0.002227 | 3.9028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2679 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 2679 & at transformer X4394 due to lightning. 2 X 10 amp HV fuses replaced. - (Fuses 2679) 1 X 2 amp HV fuse replaced - (X4394) | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002227 | 11 | 2017 | 2016-10-09 | C | 13 | 0.002227 | 3.9028e-05
1 | 13954775 | 2016-10-09 08:28 | 2016-10-09 10:22 | 114 | 2 | 228.1 | 0.00068479 | 0.000666 | 6.0042e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Y164 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at transformer Y164 2 X 3 amp HV fuse replaced | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000666 | 6.6 | 2017 | 2016-10-09 | C | 2 | 0.000666 | 6.0042e-06
1 | 13954801 | 2016-10-09 08:35 | 2016-10-09 10:50 | 135 | 1 | 135.1667 | 0.00040579 | 0.000396 | 3.0021e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2522T & 2427T | FUSE - ELEMENT/LINK (HV) | Check if OMS 13954862 (2192A Rawhitiroa Road) is related No Faultman found blown fuses at transformers 2522T & 2427T both on same property. 1 X 2 amp HV fuse replaced ( Tfr 2522T ) 2 X 2 amp HV fuses replaced (Tfr 2427T ) | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000396 | 6.6 | 2017 | 2016-10-09 | C | 1 | 0.000396 | 3.0021e-06
1 | 13956309 | 2016-10-09 09:23 | 2016-10-09 12:05 | 161 | 2 | 323.3333 | 0.00097069 | 0.000952 | 6.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X3 | FUSE - ELEMENT/LINK (HV) | poss related to OMS 13954627 - (116 Currie Rd) NO Faultman found blown fuses at transformer X3. 2 X 3 amp HV fuses replaced | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000952 | 11 | 2017 | 2016-10-09 | C | 2 | 0.000952 | 6.0042e-06
1 | 13956394 | 2016-10-09 09:48 | 2016-10-10 13:30 | 1661 | 3 | 4985.15 | 0.014966 | 0.014939 | 9.0063e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | m2155 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Isolated at fuses MA206. Found transformer faulty, replaced, relivened | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.014939 | 11 | 2017 | 2016-10-09 | C | 3 | 0.014939 | 9.0063e-06
1 | 13957837 | 2016-10-09 12:20 | 2016-10-09 14:01 | 101 | 639 | 56512.0167 | 0.16966 | 0.1639 | 0.0019184 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB R41 | UNKNOWN | CB R41 tripped on O/C, line was patrolled and sectionalised and no fault was found, at moment of tripping CB R41 was back feeding a section of CB R21, both feeders have been restored back to normal. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.1639 | 11 | 2017 | 2016-10-09 | C | 639 | 0.1639 | 0.0019184
1 | 13959117 | 2016-10-09 15:35 | 2016-10-09 18:48 | 192 | 3 | 577.85 | 0.0017348 | 0.001707 | 9.0063e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M4305 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 50kVA transformer hit by lightning. Also used: 3mtrs of 16mm cu, backing plate & bolts, 3x 6Amp HV Links | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001707 | 11 | 2017 | 2016-10-09 | C | 3 | 0.001707 | 9.0063e-06
1 | 13959828 | 2016-10-09 21:41 | 2016-10-09 23:33 | 112 | 62 | 5950.35 | 0.017864 | 0.017305 | 0.00018613 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C637 | UNKNOWN | Sec C637 found tripped. Unknown cause. RS 8156 had also Autoclosed. at the same time. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.017305 | 11 | 2017 | 2016-10-09 | C | 62 | 0.017305 | 0.00018613
1 | 13960662 | 2016-10-09 04:18 | 2016-10-09 06:36 | 138 | 2 | 276 | 0.00082859 | 0.00081 | 6.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717838 | FUSE - ELEMENT/LINK (HV) | 3 2amp lightmning | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.00081 | 11 | 2017 | 2016-10-09 | C | 2 | 0.00081 | 6.0042e-06
1 | 13961944 | 2016-10-09 08:20 | 2016-10-09 09:30 | 70 | 4 | 280 | 0.0008406 | 0.000804 | 1.2009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 849432 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp lightning | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000804 | 11 | 2017 | 2016-10-09 | C | 4 | 0.000804 | 1.2009e-05
1 | 13962207 | 2016-10-10 09:28 | 2016-10-10 10:04 | 36 | 1 | 36.4833 | 0.00010953 | 0.0001 | 3.002e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4-074 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Raised as part of NAPA23587 Remove Transformer TC4-074 | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.0001 | 11 | 2017 | 2016-10-10 | C | 1 | 0.0001 | 3.002e-06
1 | 13964061 | 2016-10-10 10:04 | 2016-10-10 12:02 | 118 | 205 | 15386.3833 | 0.046191 | 0.044345 | 0.00061543 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser 9198 L/O No Flags. Sectionalised and found no fault | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.044345 | 11 | 2017 | 2016-10-10 | C | 205 | 0.044345 | 0.00061543
1 | 13966808 | 2016-10-10 11:05 | 2016-10-10 11:59 | 54 | 241 | 13090.3167 | 0.039298 | 0.037127 | 0.0007235 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773971 | CONDUCTOR - REPAIR/REHANG | During the course of planned Live Line works via Permit 24139-01 to remove 11kV temporary links 4100 @ pole 773971 conductor at the work site pulled out of (crimp) sleeve and fell to the ground. Caused Kai Iwi CB 6 to trip to lock out, O/C & E/F. On discussion with recipient, mutually agreed to recover conductor using existing permit and processes. The the line was to remain de-energized until the conductor was recovered and re-terminated and only then re-livened in order to maintain safety to the crew. Recovery work was duly carried out and feeder re-livened at 1158 hrs. Planned works were duly completed and the permit cancelled. Safety Manager 667454 Fi, no request made as crew already onsite. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.037127 | 11 | 2017 | 2016-10-10 | C | 241 | 0.037127 | 0.0007235
1 | 13967391 | 2016-11-01 09:00 | 2016-11-01 12:49 | 229 | 36 | 8244 | 0.024743 | 0.024418 | 0.00010805 | NAPA ID:24292 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 024292 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P45603 | NONE | to change rotton tx pole. Kopikoiko Road, Mangamutu, Mangamaire. W/O 30032597. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.012209 | 5.5 | 2017 | 2016-11-01 | B | 36 | 0.024418 | 0.00010805
1 | 13967629 | 2016-11-01 08:45 | 2016-11-01 10:03 | 78 | 13 | 1014 | 0.0030433 | 0.002926 | 3.9017e-05 | NAPA ID:24621 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 024621 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses 7726 | NONE | replace defected 11kv pin pole. Paierau Road, Akura, Masterton. W/O 30031632. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.001463 | 5.5 | 2017 | 2016-11-01 | B | 13 | 0.002926 | 3.9017e-05
1 | 13968103 | 2016-10-16 01:01 | 2016-10-17 01:00 | 1439 | 205 | 0 | 0 | 0 | 0 | NAPA ID:25430 TP_KINLEITH GXP > TP_KINLEITH > KINLEITH2212-BAIRD RD 33KV | 11 | Planned | 025430 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | KINBRD066 | NONE | To replace pole numbers KINBRD066, KINBRD067 and KINBRD072 so that removed poles can be sent to Busck for testing. PLEASE USE CHIAN HO's LATEST ENGINEERING STUDIES FOR THE BACKFEEDS REQUIRED FOR THIS JOB. SWITCHING REWRITE DUE TO ORIGINAL SWITCHING UNDERTAKEN. REF NAPA 24486. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-10-16 | B | 205 | 0 | 0
1 | 13968147 | 2016-10-10 14:45 | 2016-10-10 16:22 | 96 | 1 | 96.6 | 0.00029 | 0.00028 | 3.002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 849456 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp fuse lightning | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.00028 | 11 | 2017 | 2016-10-10 | C | 1 | 0.00028 | 3.002e-06
1 | 13968191 | 2016-11-01 08:50 | 2016-11-01 14:32 | 342 | 17 | 5814 | 0.017449 | 0.017296 | 5.1022e-05 | NAPA ID:23433 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 023433 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 855089 | NONE | replace defective poles 814232 & 814227. Brandon Street, Featherston, Greytown. W/O 300030519 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.008648 | 5.5 | 2017 | 2016-11-01 | B | 17 | 0.017296 | 5.1022e-05
1 | 13968243 | 2016-10-10 17:55 | 2016-10-10 19:40 | 105 | 5 | 525 | 0.0015761 | 0.001531 | 1.501e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 210807 | NONE | Old comms cable of some sort had blown onto 33kV conductors and was removed after isolating the 33kV and the 11kV beneath. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.001531 | 11 | 2017 | 2016-10-10 | C | 5 | 0.001531 | 1.501e-05
1 | 13968545 | 2016-10-10 18:25 | 2016-10-10 20:35 | 130 | 2 | 260 | 0.00078054 | 0.000762 | 6.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc4003 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Found faulty DDO at TC4003. Isolated at fuses FP1353, replaced DDO & relivened | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000762 | 11 | 2017 | 2016-10-10 | C | 2 | 0.000762 | 6.0041e-06
1 | 13969146 | 2016-10-10 19:19 | 2016-10-11 17:19 | 1320 | 83 | 27476.0167 | 0.082486 | 0.081738 | 0.00044731 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794537 | CONDUCTOR - REPAIR/REHANG | Recloser 4237/2 tripped on E/F flags, line was patrolled and sectionalised and lines down was found from pole 794537, spans down are more than 400 meters long, fault crew will return in morning to repair lines as most of it is on foot.Line is isolated at Fuses 949 for lines to be repaired. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.081738 | 11 | 2017 | 2016-10-10 | C | 83 | 0.081738 | 0.00044731
1 | 13970178 | 2016-10-11 04:26 | 2016-10-11 05:40 | 73 | 21 | 1551.2 | 0.0046568 | 0.004467 | 6.3043e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 5523 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 5523, no fault found suspect bird strike. 2 X 10 amp HV fuses replaced. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.004467 | 11 | 2017 | 2016-10-11 | C | 21 | 0.004467 | 6.3043e-05
1 | 13970215 | 2016-10-11 05:38 | 2016-10-11 13:40 | 481 | 48 | 23127.2 | 0.069429 | 0.068996 | 0.0001441 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Outside 29 Rimu St Hawera. | CABLE - REPLACE LESS THAN 5 METRES | Power Lines arching. Reported by Fire Comms. F2166282 Faultman report that the cable crutch at Fuses 6738 were all burnt and crutch is damaged, line was isolated at Fuses 6738. Replaced all 3 joints, relvened | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.068996 | 11 | 2017 | 2016-10-11 | C | 48 | 0.068996 | 0.0001441
1 | 13970533 | 2016-10-11 08:17 | 2016-10-11 12:25 | 248 | 2 | 397.3833 | 0.001193 | 0.001174 | 6.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842288 | CONDUCTOR - REPAIR/REHANG | Power Restored Repaired conductor Due to birdstrike Nothing else repaired or replaced All surrounding assets up to Powerco standard Isolated section of line from fuses 7144 to repair conductor @ pole 842278 and replaced 2x hv fuses | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.001174 | 11 | 2017 | 2016-10-11 | C | 2 | 0.001174 | 6.0041e-06
1 | 13973181 | 2016-10-11 10:08 | 2016-10-11 14:50 | 282 | 17 | 4798.8167 | 0.014406 | 0.014253 | 5.1035e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc4257 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Found transformer faulty. Isolated at fuses, changed 50kvA transformer & relivened | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.014253 | 11 | 2017 | 2016-10-11 | C | 17 | 0.014253 | 5.1035e-05
1 | 13974104 | 2016-10-11 14:22 | 2016-10-11 15:01 | 39 | 28 | 1092 | 0.0032782 | 0.003026 | 8.4058e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46571 | JUMPER | Repair 1 x jumper on Transformer T7/353 Fuses. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003026 | 11 | 2017 | 2016-10-11 | C | 28 | 0.003026 | 8.4058e-05
1 | 13974133 | 2016-10-11 12:05 | 2016-10-11 15:22 | 196 | 702 | 35766.7 | 0.10737 | 0.10105 | 0.0021074 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 8859/3 | CABLE - REPLACE LESS THAN 5 METRES | CB F11 L/O NO flags Sectionalised and found cable between Sw/Gear 8859/3 & transformer 3878T faulty. Isolated & restored power DNO 161020 | F2 | BROWNE ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.10105 | 11 | 2017 | 2016-10-11 | C | 702 | 0.10105 | 0.0021074
1 | 13975083 | 2016-10-28 09:01 | 2016-10-28 14:38 | 337 | 65 | 21905 | 0.065746 | 0.06516 | 0.00019509 | NAPA ID:23669 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023669 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP 66-67, 9760 | NONE | Replace poles,hardware and conductor. Pukehina Parade, Pongakawa, Te Matai. W/O 30019859. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.03258 | 5.5 | 2017 | 2016-10-28 | B | 65 | 0.06516 | 0.00019509
1 | 13975093 | 2016-10-11 11:20 | 2016-10-11 12:20 | 59 | 17 | 1013.4833 | 0.0030425 | 0.002889 | 5.1035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R48 | FUSE - ELEMENT/LINK (HV) | Replaced 1x 10a HV fuse @ R48 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002889 | 11 | 2017 | 2016-10-11 | C | 17 | 0.002889 | 5.1035e-05
1 | 13977434 | 2016-11-02 10:05 | 2016-11-02 12:29 | 144 | 7 | 1008 | 0.0030253 | 0.002962 | 2.1009e-05 | NAPA ID:24880 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | 024880 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | DDO on T2/563 | NONE | replace 400v xarms on T2/563. Rangitiki Line, Milson, Bunnythorpe. W/O 30031170. | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.001481 | 5.5 | 2017 | 2016-11-02 | B | 7 | 0.002962 | 2.1009e-05
1 | 13977437 | 2016-10-27 09:30 | 2016-10-27 11:29 | 119 | 33 | 3927 | 0.011787 | 0.011489 | 9.9048e-05 | NAPA ID:23624 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11 | Planned | 023624 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P1549 | NONE | TO INSTALL GROUND STAY AND REPLACE TWISTED SPLIT XARM P1549. 729 Waihi Whangamata Road, Waihi , Waikino. W/O 30011828. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.0057445 | 5.5 | 2017 | 2016-10-27 | B | 33 | 0.011489 | 9.9048e-05
1 | 13977478 | 2016-11-02 08:30 | 2016-11-02 12:42 | 252 | 5 | 1260 | 0.0037816 | 0.003736 | 1.5006e-05 | NAPA ID:24941 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 024941 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 1201 | NONE | replace old larch poles 786740 ,786741 and arms ,replace t/f pole x2274 and hard ware. Napier Taihape Road, Springvale Station, Taihape, Mataroa. W/O 30015625. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001868 | 5.5 | 2017 | 2016-11-02 | B | 5 | 0.003736 | 1.5006e-05
1 | 13977804 | 2016-11-02 09:05 | 2016-11-02 10:53 | 108 | 2 | 216 | 0.00064827 | 0.00063 | 6.0024e-06 | NAPA ID:24830 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 024830 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 1256 | NONE | Replace defect 11kv pole 802859. 312 Tutaenui Road, Marton. W/O 10161787. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000315 | 5.5 | 2017 | 2016-11-02 | B | 2 | 0.00063 | 6.0024e-06
1 | 13977826 | 2016-11-02 09:20 | 2016-11-02 14:30 | 310 | 33 | 10230 | 0.030703 | 0.030405 | 9.9041e-05 | NAPA ID:24933 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | 024933 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 780609, 844673 | NONE | Trimming and felling trees between poles 844671 and 844672. 199 Makakaho Road, Ngamatapouri, Wanganui, Waverley. W/O 30026260. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.015203 | 5.5 | 2017 | 2016-11-02 | B | 33 | 0.030405 | 9.9041e-05
1 | 13978177 | 2016-10-11 14:44 | 2016-10-11 19:00 | 256 | 8 | 1734.3333 | 0.0052066 | 0.005134 | 2.4016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 774174 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | called and emailed hub re 999 ETA required by police Car vs possibly pole vs Tx. Event #F2166645. ETA if possible. Fire are enroute. Smoking transformer. Fire comms gave 221 No 2 Line as the closest address. Advised both police and fire comms 10 mins Faultman rtepaired cross arm & replaced all 3 fuses holders & fuses. Full set fuse holders. 3 X 3 amp HV fuses replaced. NDR 41495 | F3 | DURIE HILL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.005134 | 11 | 2017 | 2016-10-11 | C | 8 | 0.005134 | 2.4016e-05
1 | 13978642 | 2016-10-11 18:48 | 2016-10-11 20:05 | 77 | 14 | 1078 | 0.0032362 | 0.00311 | 4.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 804557 | INSULATOR | Faultman found a floating insulator & wire on pole 804557, line was isolated at Fuses 748 to replace the insulator & rebind the conductor in . 1 X 11kV insulator replaced. 1 X binder used. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00311 | 11 | 2017 | 2016-10-11 | C | 14 | 0.00311 | 4.2029e-05
1 | 13978806 | 2016-10-11 18:18 | 2016-10-11 19:15 | 57 | 5 | 285 | 0.00085559 | 0.00081 | 1.501e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 218076 | FUSE - ELEMENT/LINK (HV) | replace 2 x H/V, O/H 3a fuses at fuses SE7 004 ( birds ) | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.00081 | 11 | 2017 | 2016-10-11 | C | 5 | 0.00081 | 1.501e-05
1 | 13979322 | 2016-10-11 22:10 | 2016-10-11 22:50 | 39 | 1413 | 43309.15 | 0.13002 | 0.11729 | 0.0042419 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 9 | UNKNOWN | CB 9 & Sectionalizer 12083/2 tripped on O/C flags, line was sectionalised and patrolled no fault was found, customers on Turuturu Rd said they heard a loud smash but faultman could not find any problems, faultman will do a cursory drive by in morning just to check in day light. | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.11729 | 11 | 2017 | 2016-10-11 | C | 1413 | 0.11729 | 0.0042419
1 | 13981424 | 2016-10-12 05:12 | 2016-10-12 06:00 | 47 | 387 | 17114.8 | 0.051379 | 0.047893 | 0.0011618 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB R | UNKNOWN | CB R41 tripped on O/C flags, at time of tripping CB R41 was feeding a section of CB R21, line was patrolled and sectionalised. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.047893 | 11 | 2017 | 2016-10-12 | C | 387 | 0.047893 | 0.0011618
1 | 13982562 | 2016-10-12 07:13 | 2016-10-12 10:28 | 194 | 387 | 12921.6833 | 0.038791 | 0.035305 | 0.001417 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732150 | LIGHTNING ARRESTOR (HV) | 11kV CB R41 tripped O/C inst E/F to lock out. Loss of supply to Fonterra Bridge street site, commercial team notified (Shirley& Paul) Also affected ANZSCO rennet plant. Sensationalized feeder, Found a blown lightning arrestor at Pole 732150, all three were replaced, note they were the 10kV units, not the older 9kV type. During course of fault NZFS flagged down crew due to meter board fire at 30 Bedford street. 32 Bedford st was also affected with minor damage to the meter board. Both sites checked & tested by electrical inspector. 32 Bedford St required a replacement main switch. Unknown if appliances damaged Note 732150 pole site is directly opposite both the affected properties. It is suspected when the Arrestor failed the 11kV contacted the Earth conductor and thus into the neutral to the two affected houses, causing the damage. NOTE: FM was flagged down by NZFS to urgently disconnect 13989537 as meter board was on fire. FM carried out safety disconnection of 13989537 then carried on to this job. Safety manager report 668105 | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.035305 | 11 | 2017 | 2016-10-12 | C | 387 | 0.035305 | 0.001417
1 | 13989791 | 2016-10-12 08:55 | 2016-10-12 10:58 | 123 | 7 | 861.7 | 0.0025868 | 0.002523 | 2.1014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715022 | FUSE - ELEMENT/LINK (HV) | Advised FM to look at TA787 as there is also no power at Tx 5097 (OMS 13990287) 2 x 10 wind | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002523 | 11 | 2017 | 2016-10-12 | C | 7 | 0.002523 | 2.1014e-05
1 | 13990273 | 2016-10-12 10:06 | 2016-10-12 12:01 | 115 | 2 | 230.1 | 0.00069076 | 0.000672 | 6.004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 356454 | FUSE - ELEMENT/LINK (HV) | 2 x6amp fuse 2630 bird strike | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000672 | 11 | 2017 | 2016-10-12 | C | 2 | 0.000672 | 6.004e-06
1 | 13991083 | 2016-11-03 10:00 | 2016-11-03 13:00 | 180 | 25 | 4500 | 0.013505 | 0.01328 | 7.503e-05 | NAPA ID:24977 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 024977 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX X620 | NONE | Replace broken concrete pole 783729 & replace hardware. 2748 Parapara Road, Ohakune. W/O 30032334. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.00664 | 5.5 | 2017 | 2016-11-03 | B | 25 | 0.01328 | 7.503e-05
1 | 13991666 | 2016-10-12 14:18 | 2016-10-12 14:29 | 11 | 746 | 8206 | 0.024635 | 0.017916 | 0.0022395 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | 263921 | RECLOSER (HV) | Tripped due to protection issues. recloser 13088 install via live line under NAPA 24784. while cutting the jumpers over the new recloser 13088/2 the recloser 13088 tripped on E/F Live L. The E/F protection was disabled so this recloser should not have tripped. the live line crew were not at fault. This needs a protection review as it has safety implications for the live line crews doing this work in the future. This is a commom practice. safety manager 667991 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.017916 | 11 | 2017 | 2016-10-12 | C | 746 | 0.017916 | 0.0022395
1 | 13995750 | 2016-10-12 17:38 | 2016-10-12 20:50 | 192 | 1 | 192.4167 | 0.00057764 | 0.000568 | 3.002e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3527T | JUMPER | Isolated line from fuses 5286 to repair jumper at transformer 3527T | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000568 | 6.6 | 2017 | 2016-10-12 | C | 1 | 0.000568 | 3.002e-06
1 | 13995791 | 2016-10-12 17:52 | 2016-10-13 00:44 | 411 | 1188 | 129513.6 | 0.3888 | 0.3781 | 0.0090631 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 2038 | SWITCH (HV) | CB 7 tripped on IDMT E/F line was sectionalised and patrolled . Switchgear 2038 flashed overe and there was found to be oil coming out . Switchgear isolated and cable disconnected from line at pole 800531 so that the sction from ABS 467 could be backfed switchgear repaired and returned to service and line break is to be restored later using live line procedure | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.3781 | 11 | 2017 | 2016-10-12 | C | 1188 | 0.3781 | 0.0090631
1 | 14000232 | 2016-10-13 06:39 | 2016-10-13 07:57 | 77 | 67 | 5204.7833 | 0.015625 | 0.015021 | 0.00020113 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 753773 | FUSE - ELEMENT/LINK (HV) | 2 x15 amp unknown | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.015021 | 11 | 2017 | 2016-10-13 | C | 67 | 0.015021 | 0.00020113
1 | 14000920 | 2016-10-27 09:15 | 2016-10-27 17:02 | 467 | 37 | 9999 | 0.030012 | 0.029678 | 0.00017108 | NAPA ID:24067 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11 | Planned | 024067 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX TE7-099 | NONE | Pre Switching - isolate 33kV line on 339862 (Off-load 33kV to Pongakawa sub & backfeed 11kV). install 11KV line break at pole 230383. Replace 11kV / 33kV pole 339862. Close line break at pole 230383. 194 Maniatutu Road, Pongakawa, Te Puke, Te Matai. W/O 30031736. Return switching was late as faultman didn't return to site until 16:11. Power should have been restored at 15:00 | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.014839 | 5.5 | 2017 | 2016-10-27 | B | 37 | 0.029678 | 0.00017108
1 | 14007885 | 2016-11-01 09:09 | 2016-11-01 15:30 | 381 | 65 | 24765 | 0.074327 | 0.073741 | 0.00019508 | NAPA ID:23671 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023671 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | Replace poles,hardware and conductor. G&B Connect new conductors to 9760 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.036871 | 5.5 | 2017 | 2016-11-01 | B | 65 | 0.073741 | 0.00019508
1 | 14015371 | 2016-10-13 14:17 | 2016-10-13 14:21 | 3 | 419 | 1571.25 | 0.0047169 | 0 | 0.0012578 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 228298 | CIRCUIT BREAKER (HV) | at 14:17, Pongakawa Sub, CB 3 Rotoehu Feeder, Tripped, O/C, L/O. Downer crews were on site commissioning new Sectionaliser 13103/2. Circuit Break tripped to L/O as safety measures were still applied to CB 3 from the previous live line permit to install the sectionaliser on the pole (Duty NC had not had a chance to remove them after cancelling live line permit). Duty NC contacted field crew to enquire if there had been an incident and crew Advised that a Pukeko had struck the lines at Pole 228298 and caused feeder to trip. This pole is the same pole as their worksite. This tripping happened during SCADA commissioning for Sectionaliser 13103 right after a Close Command was sent to this Sectionaliser (at 14:17). after tripping, sectionaliser 13103 was opened by field crew & then CB 3 closed by NOC at 14:20. Field crew advised SCADA team that commissioning would recommence in a short time. Before commissioning continued, SCADA team noticed that the Source Volts for 13103 failed at 14:27 and then became operational again at 14:35. This would indicate that the links 13103/4 were opened during this time, however Duty NC was not advised of this happening. commissioning continued after 14:35. Duty NC requested evidence of bird strike from field crew (photo of suspect bird) but was told that the bird could not be found. Field Crew - Tom Tanoa Commissioning Tech - Darryn Thomas | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-10-13 | C | 419 | 0 | 0.0012578
1 | 14019049 | 2016-11-02 10:01 | 2016-11-02 11:21 | 80 | 2 | 160 | 0.0004802 | 0.000462 | 6.0024e-06 | NAPA ID:24983 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024983 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Install new pole mid span between pole 211384 & 211385. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000231 | 5.5 | 2017 | 2016-11-02 | B | 2 | 0.000462 | 6.0024e-06
1 | 14019273 | 2016-10-13 17:39 | 2016-10-13 20:15 | 156 | 1 | 156.15 | 0.00046876 | 0.000459 | 3.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217260 | FUSE - ELEMENT/LINK (HV) | 2x5 amp HV fuse blown at S5284. line patrolled no fault found. reloaded & livened. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000459 | 11 | 2017 | 2016-10-13 | C | 1 | 0.000459 | 3.0019e-06
1 | 14019918 | 2016-10-14 08:52 | 2016-10-14 10:05 | 73 | 16 | 1168 | 0.0035063 | 0.003362 | 4.8031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228920 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | at 08:52, Pongakawa Sub, CB 3 Rotoehu Feeder. Found broken HV Fuse Unit at Transformer TF8-023. Isolated lines at Fuses SF7-023. Permit issued & repairs carried out. All Power Restored on Completion. 1x 8A HV Fuse, Base & Holder all replaced (1x complete DDO unit). Mike James Attended. Old / Aged equipment. 07:22 Dennis Ngatai has attended. Found blown jumper at Transformer TF8-023. Needs repair. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.003362 | 11 | 2017 | 2016-10-14 | C | 16 | 0.003362 | 4.8031e-05
1 | 14020211 | 2016-10-14 07:51 | 2016-10-14 12:02 | 251 | 8 | 231.9833 | 0.0006964 | 0.000624 | 3.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 229039 | FUSE - ELEMENT/LINK (HV) | Mike James Attended. Reloaded, Relivened 2x 15A HV Fuses at SF7-024. Suspected bird strike but no bird found. All OK. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000624 | 11 | 2017 | 2016-10-14 | C | 8 | 0.000624 | 3.0019e-06
1 | 14020534 | 2016-10-31 09:15 | 2016-10-31 18:41 | 566 | 129 | 40982 | 0.123 | 0.12184 | 0.00066029 | NAPA ID:25377 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 025377 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole O13726 | NONE | Create break on de-energised Line at pole O019. Replace 11kV P/M Transformer TC3221 with G/M 200kVA. Close break at pole O019 (Line de-energised). 60 Kerepehi Town Road, Kerepehi, Kopu. W/O 30031355. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.060919 | 5.5 | 2017 | 2016-10-31 | B | 129 | 0.12184 | 0.00066029
1 | 14020537 | 2016-11-09 09:00 | 2016-11-09 15:09 | 369 | 4 | 1476 | 0.0044294 | 0.004393 | 1.2004e-05 | NAPA ID:24653 TP_PIAKO GXP | 11 | Planned | 024653 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC682 | NONE | Replace DNO ABS IC682. 1: BACKFEED SWITCHING & OFFLOADING of FC793 & TC2789. 2: Create Line Break on 11kV Lines with 33kV Lines Isolated but not Earthed at same pole structure WHUKER131. 3: Replace 11kV ABS IC682. (11kV & 33kV Isolated and Earthed) 4: Close Line Break on 11kV Line with 33kV Lines Isolated but not Earthed at the same pole structure WHUKER131. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.0021965 | 5.5 | 2017 | 2016-11-09 | B | 4 | 0.004393 | 1.2004e-05
1 | 14020593 | 2016-10-29 09:15 | 2016-10-29 10:50 | 95 | 20 | 1900 | 0.0057026 | 0.005522 | 6.0028e-05 | NAPA ID:24811 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 024811 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 213243 | NONE | Replace broken pole with new 11m. Junction Road, Te Puna, Tauranga. W/O 30033231. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.002761 | 5.5 | 2017 | 2016-10-29 | B | 20 | 0.005522 | 6.0028e-05
1 | 14020934 | 2016-10-14 11:33 | 2016-10-14 12:00 | 27 | 1 | 27 | 8.1052e-05 | 7.2e-05 | 3.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4068 | CONDUCTOR - REPAIR/REHANG | at 11:30, Matatoki Sub, CB 3 Puriri Feeder. While completing planned work to replace earthing for Transformer TC4068, found that the neutral connection was loose. Contacted Control. Permission given for own Isolation & AP for isolate TC4068 and repair neutral connection. All Power Restored on completion. no materials used. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 7.2e-05 | 11 | 2017 | 2016-10-14 | C | 1 | 7.2e-05 | 3.0019e-06
1 | 14020956 | 2016-10-14 11:40 | 2016-10-14 16:58 | 318 | 83 | 21818.4667 | 0.065498 | 0.06475 | 0.00024916 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 794473 | CONDUCTOR - REPAIR/REHANG | Fax received advising of tractor vs main line. Tried to call customer for hazard process - no answer. FM advised. FM delayed in getting to site due to the Targa rally being in progress. NOC advised of road blocks in place at approx 12:20 hrs. ***Note KPI's affected due to Targa Rally***. Faultman delayed in getting to site for between 90-120 minutes. FM found that a tractor was carrying a tree in it's bucket & the tree contacted the lines causing a clash bringing 2x HV lines down. Repaired using 6x16mm cu sleeves & 20mtrs of 16mm cu conductor NDR# 56104 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.06475 | 11 | 2017 | 2016-10-14 | C | 83 | 0.06475 | 0.00024916
1 | 14023157 | 2016-11-01 08:45 | 2016-11-01 15:54 | 429 | 118 | 50622 | 0.15193 | 0.15087 | 0.00035415 | NAPA ID:24566 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 024566 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | RE POLE AND RECON 11KV FEEDER | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.075434 | 5.5 | 2017 | 2016-11-01 | B | 118 | 0.15087 | 0.00035415
1 | 14023173 | 2016-10-18 12:00 | 2016-10-18 12:25 | 25 | 42 | 1050 | 0.0031519 | 0.002773 | 0.00012608 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1283 | NONE | Adam advised that the ground mounted TX need to be taped down - but some one will need to go back when some one is onsite at the water treatment plant - this to be done first thing Monday morning when council guys onsite . Adam will arrange with Neville pope 18/10 emailed SMC for update Transformer T1283 tapped from tap 4 to tap 3 voltages checked and now within tolarances | F2 | WYNDHAM ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.002773 | 11 | 2017 | 2016-10-18 | C | 42 | 0.002773 | 0.00012608
1 | 14023177 | 2016-11-03 08:45 | 2016-11-03 13:41 | 296 | 118 | 34928 | 0.10483 | 0.10376 | 0.00035414 | NAPA ID:24567 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 024567 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | . | NONE | RE POLE AND RECON 11KV FEEDER | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.051881 | 5.5 | 2017 | 2016-11-03 | B | 118 | 0.10376 | 0.00035414
1 | 14023192 | 2016-11-08 08:31 | 2016-11-08 09:35 | 64 | 118 | 7552 | 0.022664 | 0.021601 | 0.00035412 | NAPA ID:24564 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 024564 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | RE POLE AND RECON 11KV FEEDER | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0108 | 5.5 | 2017 | 2016-11-08 | B | 118 | 0.021601 | 0.00035412
1 | 14023311 | 2016-11-03 08:30 | 2016-11-03 15:10 | 400 | 38 | 15200 | 0.045618 | 0.045276 | 0.00011405 | NAPA ID:23436 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 023436 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814341 | NONE | replace defective t/x pole t1619 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.022638 | 5.5 | 2017 | 2016-11-03 | B | 38 | 0.045276 | 0.00011405
1 | 14023339 | 2016-10-14 15:24 | 2016-10-14 15:26 | 2 | 23 | 46 | 0.00013809 | 0 | 6.9045e-05 |  | 11 | Planned | 024785 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | N/A - NOT APPLICABLE | CABLE - REPAIR | NAPA 24785 - test and cut cable for testing both ways to confirm no more faults. Urgent Application. | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-10-14 | B | 23 | 0 | 6.9045e-05
1 | 14023380 | 2016-11-03 09:15 | 2016-11-03 13:35 | 260 | 9 | 2340 | 0.0070228 | 0.006941 | 2.7011e-05 | NAPA ID:24726 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 024726 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | scotts rd | POLE | replace 7 11kv xarms from H137 to the end | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0034705 | 5.5 | 2017 | 2016-11-03 | B | 9 | 0.006941 | 2.7011e-05
1 | 14023434 | 2016-11-03 09:40 | 2016-11-03 14:00 | 260 | 6 | 1560 | 0.0046819 | 0.004627 | 1.8007e-05 | NAPA ID:24418 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 024418 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | t3/373 | NONE | To replace tx pole up grade earths and tx. NOTE: An HT Fuse at T33 broke when reclosing. Required a further outrage to carryout repairs. Refer OMS 14190516. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0023135 | 5.5 | 2017 | 2016-11-03 | B | 6 | 0.004627 | 1.8007e-05
1 | 14026679 | 2016-10-15 07:49 | 2016-10-15 09:25 | 95 | 1 | 95.9833 | 0.00028813 | 0.000279 | 3.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 1189 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8Amp HV Fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000279 | 11 | 2017 | 2016-10-15 | C | 1 | 0.000279 | 3.0019e-06
1 | 14029323 | 2016-10-15 23:21 | 2016-10-15 23:53 | 31 | 1 | 31.6 | 9.486e-05 | 8.5e-05 | 3.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N12514 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Reloaded, Relivened 3x 3A HV Fuses at FC4149 & Replaced Carriers. Carriers were old equipment, however there was lightning in the area earlier in the day and faultman believes this was the real cause. All OK. | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 8.5e-05 | 11 | 2017 | 2016-10-15 | C | 1 | 8.5e-05 | 3.0019e-06
1 | 14029339 | 2016-10-15 22:23 | 2016-10-15 23:55 | 92 | 4 | 369.3333 | 0.0011087 | 0.001072 | 1.2008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D0741 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 3A HV Fuses at FP1600. Unknown Cause. Dandy Trimidal Attended. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.001072 | 11 | 2017 | 2016-10-15 | C | 4 | 0.001072 | 1.2008e-05
1 | 14029684 | 2016-10-16 05:42 | 2016-10-16 07:31 | 109 | 16 | 1749.6 | 0.0052521 | 0.005107 | 4.803e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | B30 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuse at Fuses B30, customer reported to faultman found a dead fresh swan on the road under the lines. 2 X 6 Amp HV fuse replaced | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005107 | 11 | 2017 | 2016-10-16 | C | 16 | 0.005107 | 4.803e-05
1 | 14030069 | 2016-10-16 06:27 | 2016-10-16 08:29 | 122 | 7 | 856.45 | 0.0025709 | 0.002507 | 2.1013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7506 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses Replaced. Suspect Bird Strike. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.002507 | 11 | 2017 | 2016-10-16 | C | 7 | 0.002507 | 2.1013e-05
1 | 14031002 | 2016-10-16 18:25 | 2016-10-16 19:16 | 50 | 4 | 202.1333 | 0.00060678 | 0.00057 | 1.2007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13106 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 10A HV Fuses at FP767. Unknown Cause. James Kennerley Attended. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.00057 | 11 | 2017 | 2016-10-16 | C | 4 | 0.00057 | 1.2007e-05
1 | 14036277 | 2016-10-16 20:10 | 2016-10-16 21:42 | 91 | 1024 | 25627.7333 | 0.076931 | 0.067709 | 0.0030739 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | TD5-130 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | at 20:10, Papamoa Sub, CB 3 Black Stump Feeder, Tripped, A B C O/C, L/O. Faultmen dispatched & investigation began. Backfed supplied from PMA 1. Recloser 9488 Opened, Recloser 9675 Closed at 20:26. Feeder sectionalised. While sectionalising, customer called in to report loud bang from transformer outside property. Faultmen investigated & believes fault was caused by tree branches dropping from large gum tree over hanging lines and falling onto lines. HV Fuses at Transformer TD5-130 were found to be blown (this is where tree was). Could not find any evidence of burning branches, however there were a lot of fallen branches in the area from this tree. Hard to find branches as there is a bamboo bush also around transformer. Also, there were fresh burning and arcing marks on fuse barrels at TD5-130. After transformer isolated, feeder relivened. Short time later Reloaded, Relivened 3x 3A HV Fuses & Holders at Transformer TD5-130. All Power Restored on Completion. Mike James Attended. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.067709 | 11 | 2017 | 2016-10-16 | C | 1024 | 0.067709 | 0.0030739
1 | 14038999 | 2016-10-17 03:20 | 2016-10-17 10:48 | 448 | 337 | 102866.55 | 0.30879 | 0.30575 | 0.0020232 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794738 | INSULATOR | Faultman found Recloser 4217/2 open while attending a customer fault call, line was sectionalised and patrolled and lines down was found at pole 794738 across the gully. Line was isolated at ABS's O30, 1125, transformer X1405 & Fused ABS 4639 to repair the lines. 20 meters 16mm copper conductor. 1 x 11KV insulator replaced. 1 X binder 4 x Sleeves used. Wayne Standford is verifying outage details. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.30575 | 11 | 2017 | 2016-10-17 | C | 337 | 0.30575 | 0.0020232
1 | 14039750 | 2016-10-21 09:22 | 2016-10-21 14:51 | 328 | 8 | 2569.65 | 0.0077133 | 0.007641 | 2.4013e-05 | NAPA ID:24064 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | 024064 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | NONE | 1 - Switching by Downer to Open ABS 1049 & Fuses on TC4729 prior to Live Line 01. 2 - LLP - 01 To Create Line at Pole F1318 & remove 1 span of conductor between Line Break & Pole F13004. 3 - Replace xarms, hardware & conductor plus remove ABS 1049 on spur line while disconnected from the Network. 4 - LLP - 02 To replace xarms & hardware on Pole F1318 plus install new 11kV Fuses FP1843. 5 - AP - 03 To install 1 span of new 11kV conductor from Pole F13004 to F1318 & con to new fuses FP1843 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0038205 | 5.5 | 2017 | 2016-10-21 | B | 8 | 0.007641 | 2.4013e-05
1 | 14039860 | 2016-11-03 08:45 | 2016-11-03 14:33 | 348 | 5 | 1740 | 0.0052221 | 0.005177 | 1.5006e-05 | NAPA ID:24947 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 024947 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 141 | NONE | Replacing 11kv poles and X arms, 11kv reconstruction IR8146 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.0025885 | 5.5 | 2017 | 2016-11-03 | B | 5 | 0.005177 | 1.5006e-05
1 | 14039906 | 2016-11-09 09:00 | 2016-11-09 15:00 | 360 | 5 | 1800 | 0.0054018 | 0.005356 | 1.5005e-05 | NAPA ID:24952 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 024952 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 804635 | NONE | Replacing 11kv poles and X arms, 11kv reconstruction IR8146 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.002678 | 5.5 | 2017 | 2016-11-09 | B | 5 | 0.005356 | 1.5005e-05
1 | 14040114 | 2016-10-17 09:23 | 2016-10-17 11:13 | 109 | 2 | 219.3667 | 0.0006585 | 0.00064 | 6.0036e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373711 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp duck 7757 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.00064 | 11 | 2017 | 2016-10-17 | C | 2 | 0.00064 | 6.0036e-06
1 | 14040135 | 2016-11-18 09:35 | 2016-11-18 15:00 | 325 | 5 | 1625 | 0.004876 | 0.00483 | 1.5003e-05 | NAPA ID:24955 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 024955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 141 | NONE | Replacing 11kv poles and X arms, 11kv reconstruction IR8146 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.002415 | 5.5 | 2017 | 2016-11-18 | B | 5 | 0.00483 | 1.5003e-05
1 | 14040268 | 2016-10-17 09:59 | 2016-10-17 11:38 | 99 | 75 | 7425 | 0.022289 | 0.021613 | 0.00022514 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S0560 | JUMPER | ( MAT 1 ) Emergency switching to repair jumper at pole S0560. Isolations between ABS's IC363, IC258 & Sw/Gear 9645/1 with back feed via sectionaliser 9922/2 Jumper repaired all service restored Materials 1 x Jumper, 1 x H/V sleeve | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.021613 | 11 | 2017 | 2016-10-17 | C | 75 | 0.021613 | 0.00022514
1 | 14040712 | 2016-10-26 07:30 | 2016-10-26 16:15 | 525 | 37 | 15873 | 0.047643 | 0.047309 | 0.00033317 | NAPA ID:24718 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > DOMAIN RD | 11 | Planned | 024718 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX TP491 | NONE | Replace existing SDAF3 Swichgear 9047 with CFC SCADA controller Switchgear with same labelling and liven. SCADA Commission. 116 Oriental Parade - Papamoa Beach - Tauranga. W/O 30019264. | F3 | DOMAIN RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.023654 | 5.5 | 2017 | 2016-10-26 | B | 37 | 0.047309 | 0.00033317
1 | 14041072 | 2016-10-17 12:12 | 2016-10-17 14:15 | 122 | 2 | 245.5333 | 0.00073705 | 0.000719 | 6.0036e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | C3178 | FUSE - ELEMENT/LINK (HV) | Check to see if OMS 14041139 ( as also no power to Council pump shed @ 5722 State Highway 26) Marty advised poss same job poss DDO fuses at 5722 State Highway 26 2 x 15 Fc2129 bird strike | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000719 | 11 | 2017 | 2016-10-17 | C | 2 | 0.000719 | 6.0036e-06
1 | 14042381 | 2016-10-17 14:04 | 2016-10-18 15:55 | 1550 | 1026 | 52407.1833 | 0.15732 | 0.14808 | 0.0031189 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 220427 | POLE | Car v pole 220427 at CNR of Bell Rd and Parton Rd, Papamoa, Fire comms, F2170152. PMA 3 tripped A, B & C Ph O/C, E/F, L/O. Isolations between ABS's SD5 019, SD5 055, SD5 106 & Sw/Gear 9048/2 Back feed via sectionaliser 9675 ( PMA 1 ) Additional isolation required for firemen working near lines with hoses between ABS's SD5 019, SD5 018 SD5 014 with back feed via ABS IP129 CB3 vented its oil & requires magor service. Pole 220427 replaced with back feed via Sw/Gear 9048/2 up to ABS SD5 014 Isolation required to restore service to 2 remaining transformers between CB3 & ABS's SD5 014 SD5 013 NDR No to follow Materials 1 x pole, 1 x H/V arm complete CB3 service completed & returned to service CB3 restored to normal configuration | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.14808 | 11 | 2017 | 2016-10-17 | C | 1026 | 0.14808 | 0.0031189
1 | 14043527 | 2016-10-17 14:36 | 2016-10-17 16:07 | 91 | 8 | 728 | 0.0021853 | 0.002113 | 2.4015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13630 | FUSE - ELEMENT/LINK (HV) | Go to fuses FC2225 as 451 Woodland Rd has come in as well no power Advised Cindy at SMC. 2 x6amp fuse weather | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.002113 | 11 | 2017 | 2016-10-17 | C | 8 | 0.002113 | 2.4015e-05
1 | 14043536 | 2016-10-19 09:03 | 2016-10-19 13:58 | 295 | 5 | 1475 | 0.0044276 | 0.004382 | 1.5009e-05 | NAPA ID:25654 TP_KINLEITH GXP > BAIRD ROAD SUB > PAPANUI ST | 11 | Planned | 025654 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 264430 | NONE | 1: LLP: At 0900 install TEMP 59 at poles KINBRD075 2: AP: Replace Failing PG clamps. | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.002191 | 5.5 | 2017 | 2016-10-19 | B | 5 | 0.004382 | 1.5009e-05
1 | 14043858 | 2016-10-17 15:19 | 2016-10-17 21:52 | 393 | 309 | 4834.2 | 0.014511 | 0.011728 | 5.4033e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 205162 | CONDUCTOR - REPAIR/REHANG | Tree through lines at pole 205162. Tree removed and lines re-strung. Isolation at Fuses SC2-052. Fuse also blown at transformer TC2-166. Relivened at 21:40 Tree outside the notice zone. High Winds | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.011728 | 11 | 2017 | 2016-10-17 | C | 309 | 0.011728 | 5.4033e-05
1 | 14044174 | 2016-11-02 12:15 | 2016-11-02 13:25 | 70 | 3 | 210 | 0.00063026 | 0.000603 | 9.0037e-06 | NAPA ID:24716 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 024716 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Straighten Pole W12859 and Resag HV Conductors | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.0003015 | 5.5 | 2017 | 2016-11-02 | B | 3 | 0.000603 | 9.0037e-06
1 | 14044224 | 2016-11-23 10:07 | 2016-11-23 13:02 | 175 | 12 | 2100 | 0.0063009 | 0.006192 | 3.6005e-05 | NAPA ID:24619 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 024619 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Straighten pole 267208 at IP132 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.003096 | 5.5 | 2017 | 2016-11-23 | B | 12 | 0.006192 | 3.6005e-05
1 | 14044413 | 2016-11-02 09:10 | 2016-11-02 14:40 | 330 | 15 | 4950 | 0.014856 | 0.014721 | 4.5019e-05 | NAPA ID:24022 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024022 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Re-conductor the 2nd 1.5ks of Kumikumi Road. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0073605 | 5.5 | 2017 | 2016-11-02 | B | 15 | 0.014721 | 4.5019e-05
1 | 14044480 | 2016-11-24 10:00 | 2016-11-24 11:00 | 60 | 2 | 120 | 0.00036004 | 0.000342 | 6.0007e-06 | NAPA ID:25612 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025612 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To install a 400V Fuse Disconnector on TP2396 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000171 | 5.5 | 2017 | 2016-11-24 | B | 2 | 0.000342 | 6.0007e-06
1 | 14044511 | 2016-11-24 12:05 | 2016-11-24 13:00 | 55 | 2 | 110 | 0.00033004 | 0.000312 | 6.0007e-06 | NAPA ID:25613 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025613 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To install a 400V fuse unit on TC2712 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000156 | 5.5 | 2017 | 2016-11-24 | B | 2 | 0.000312 | 6.0007e-06
1 | 14047885 | 2016-10-17 17:02 | 2016-10-18 11:10 | 1088 | 1 | 1088 | 0.003266 | 0.003256 | 3.0018e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4947t | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Blown tx , access conditions , will make unsafe to do tonight , customer contact has confirmed this is ok to change tomorrow, his name is Mathew 027 474 1166 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.003256 | 11 | 2017 | 2016-10-17 | C | 1 | 0.003256 | 3.0018e-06
1 | 14047996 | 2016-10-17 17:49 | 2016-10-17 19:14 | 84 | 12 | 1017.6 | 0.0030547 | 0.002946 | 3.6022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789471 | INSULATOR | Customer confirmed is 3km outside of Taihape - SMC informed. Sounds like HV line is smouldering - customer believes is relatively safe at the moment, so long as FM attends soon, but knows to call 111 if the situation gets worse. 4.53pm Bernard called to ask to check the address as TX is for Wanganui and the address is Taihape - customer calling from 381 Otaihape road approx 1km past 381 on RHS - FM was travelling around and will be charging kms for job travelled. Line was isolated at Fuses 981 to replace insulator on pole 789471, pole has also been defected to be replaced, it's an old wooden pole and needs replacing. Replaced 11kV pin & insulator & Ali Binder | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.002946 | 11 | 2017 | 2016-10-17 | C | 12 | 0.002946 | 3.6022e-05
1 | 14048120 | 2016-10-17 17:18 | 2016-10-17 19:41 | 143 | 7 | 1002.5167 | 0.0030094 | 0.002946 | 2.1013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD4-155 | FUSE - ELEMENT/LINK (HV) | LV lines down due to high winds. 3 x 3A HV Fuses replaced. Lines re-hubg. 12 mtrs conductor a Joints used | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.002946 | 11 | 2017 | 2016-10-17 | C | 7 | 0.002946 | 2.1013e-05
1 | 14049159 | 2016-10-18 04:35 | 2016-10-18 07:14 | 158 | 3 | 475.95 | 0.0014287 | 0.001401 | 9.0053e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850073 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp unknown | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001401 | 11 | 2017 | 2016-10-18 | C | 3 | 0.001401 | 9.0053e-06
1 | 14049171 | 2016-10-18 07:10 | 2016-10-18 07:40 | 30 | 4 | 120 | 0.00036022 | 0.000324 | 1.2007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE6 120 | JUMPER | Lance Cook own isolation & AP to repair burnt jumper at Transformer TE6 120 Materials 2 x H/V sleeves | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000324 | 11 | 2017 | 2016-10-18 | C | 4 | 0.000324 | 1.2007e-05
1 | 14058855 | 2016-10-27 09:09 | 2016-10-27 15:35 | 386 | 189 | 72954 | 0.21897 | 0.21727 | 0.00056728 | NAPA ID:24116 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 024116 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC670 | NONE | Change poles and arms. Alexandra Road / Manawaru Road, Mikkelsen Road - Waihou. W/O 30017845. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.10863 | 5.5 | 2017 | 2016-10-27 | B | 189 | 0.21727 | 0.00056728
1 | 14058946 | 2016-11-03 09:57 | 2016-11-03 13:26 | 209 | 29 | 6061 | 0.01819 | 0.017929 | 8.7035e-05 | NAPA ID:24690 TP_BUNNYTHORPE GXP > SANSON SUB > OHAKEA | 11 | Planned | 024690 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | p30689 | NONE | replace 11kv 400v xarms | F1 | SKYHAWK | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0089645 | 5.5 | 2017 | 2016-11-03 | B | 29 | 0.017929 | 8.7035e-05
1 | 14058969 | 2016-11-07 10:15 | 2016-11-07 14:21 | 246 | 12 | 540 | 0.0016206 | 0.001512 | 7.2025e-05 | NAPA ID:25368 TP_KINLEITH GXP > BAIRD ROAD SUB > CAMPBELL ST | 11 | Planned | 025368 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9084 | NONE | 1. Connect Generator (TC893). 2. Replace Cable Box / Base of 9191/1,2,3. 3. Disconnect Generator (TC893). | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000756 | 5.5 | 2017 | 2016-11-07 | B | 12 | 0.001512 | 7.2025e-05
1 | 14059048 | 2016-11-04 09:35 | 2016-11-04 14:41 | 306 | 4 | 1224 | 0.0036734 | 0.003637 | 1.2005e-05 | NAPA ID:24024 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024024 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | se3-068 | NONE | Re-conductor spur line 473mtrs down to House | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0018185 | 5.5 | 2017 | 2016-11-04 | B | 4 | 0.003637 | 1.2005e-05
1 | 14059203 | 2016-11-04 09:20 | 2016-11-04 13:04 | 224 | 21 | 4704 | 0.014117 | 0.013928 | 6.3024e-05 | NAPA ID:24528 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 024528 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | U15 | NONE | To change 11kv x arms install dlb xarms with clamp top insulators | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.006964 | 5.5 | 2017 | 2016-11-04 | B | 21 | 0.013928 | 6.3024e-05
1 | 14059288 | 2016-11-09 09:30 | 2016-11-09 13:45 | 255 | 5 | 1275 | 0.0038262 | 0.003781 | 1.5005e-05 | NAPA ID:24953 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 024953 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 786760 | NONE | replace structure poles 786760 ,786761 Springvale station | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0018905 | 5.5 | 2017 | 2016-11-09 | B | 5 | 0.003781 | 1.5005e-05
1 | 14068848 | 2016-10-18 10:23 | 2016-10-18 12:14 | 111 | 32 | 3552 | 0.010662 | 0.010374 | 9.6057e-05 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 776754 | CROSSARM - WHOLE ASSEMBLY | Line repairs @ pole 776754 Replaced crossarm , Fuse holders and repaired conductor | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.010374 | 11 | 2017 | 2016-10-18 | C | 32 | 0.010374 | 9.6057e-05
1 | 14079206 | 2016-10-18 11:44 | 2016-10-18 15:08 | 204 | 240 | 14035.5833 | 0.042132 | 0.03997 | 0.00072043 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 777081 | CONDUCTOR - REPAIR/REHANG | CB 4232 tripped O/C E/F Lines struck by trees when being felled - Repaired 2x single phase lines 4x sleeves and 45m of conductor under NDR 41861 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.03997 | 11 | 2017 | 2016-10-18 | C | 240 | 0.03997 | 0.00072043
1 | 14079535 | 2016-10-18 10:00 | 2016-10-18 11:45 | 105 | 9 | 945 | 0.0028367 | 0.002755 | 2.7016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3027 | CROSSARM - WHOLE ASSEMBLY | Replaced 1 X 3m Crossarm & 3 X 100 Amp Inline Fuses Came from a defect | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.002755 | 11 | 2017 | 2016-10-18 | C | 9 | 0.002755 | 2.7016e-05
1 | 14080652 | 2016-11-12 09:15 | 2016-11-12 14:42 | 327 | 197 | 64419 | 0.19331 | 0.19154 | 0.00059117 | NAPA ID:25731 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 025731 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | St Auybyn St | NONE | AP/01 - Install Generation to TX 1690N AP/02 - Replace existing poles and hardware for new - poles 702474,702476 & 702478 AP/03 - Un-connect Generation and reinstate supply to TX 1690N | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.095769 | 5.5 | 2017 | 2016-11-12 | B | 197 | 0.19154 | 0.00059117
1 | 14080674 | 2016-10-18 15:50 | 2016-10-18 18:17 | 147 | 60 | 8820 | 0.026476 | 0.025935 | 0.00018011 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P42260 | CONDUCTOR - REPAIR/REHANG | Urgent Shutdown required between ABS D71, D2 & D73 to remove trees that have been uprooted and are about to fall into the lines. Backfeed from KEG11 via ABS D70. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.025935 | 11 | 2017 | 2016-10-18 | C | 60 | 0.025935 | 0.00018011
1 | 14080721 | 2016-10-18 18:45 | 2016-10-18 18:48 | 3 | 1915 | 6862.0833 | 0.020599 | 0 | 0.0057484 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 370941 | CROSSARM - WHOLE ASSEMBLY | * Call from Powerco employee regarding unsafe cross arm requiring immediate inspection at pole 370941. * On inspection found the issue affected the 33kV line from Bidwells structure to Tuhitarata Sub. The site also had under built 11kV. The issue was a missing Kin pin nut, the cross arm had almost slid off the end. Would result in a 11-33kV clash. * Unable to effect repair with the line live. It was unknown as to how secure the cross arm was sitting on the end of king bolt making it impossible to safely secure whilst 'live'. Was made clear the issue could be quickly resolved using live line technique on the line De-energised. * NO option for back feeding TUH or MAB load. Reason: planned works were in process at MAB sub and was out of service for maintenance on SIN 25311. * Escalated to NCTL for discussion on management of issue. Due to urgency, safety and repair process on hand was decided to De-energsie line to effect repairs. Approved to create outage to TUH sub and a large part of (MAB) Martinborough Sub ICP's to effect an immediate repair via live line process on De-energized assets. Power removed at 1844 hrs and re-instated at 1848hrs. Jo/Alicia will require entry to Safety manager please. | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0 | 33 | 2017 | 2016-10-18 | C | 1915 | 0 | 0.0057484
1 | 14083577 | 2016-10-18 18:53 | 2016-10-18 22:29 | 216 | 595 | 58809.9333 | 0.17654 | 0.17118 | 0.0017861 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 839749 | CONDUCTOR - REPAIR/REHANG | 33 mtrs #8 Wire and 8 sleeves used. 1 x 2A HV Fuse and carrier replaced. Tree through lines at Pole 839749. Fault caused 11kV Incomer CB C848 to trip at Sub. Fault found and isolated beyond Fuses 7077 and all feeders restored. NDR # 54311 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.17118 | 11 | 2017 | 2016-10-18 | C | 595 | 0.17118 | 0.0017861
1 | 14084191 | 2016-10-18 20:05 | 2016-10-18 22:01 | 116 | 5 | 580 | 0.001741 | 0.001696 | 1.5009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M4123 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Faultman found a blown fuse & broken fuse holder at transformer M4123. Line was isolated at Fuses 6549 to replace full set of fuse holders. 1 x Full set fuse holders (3). 3 X 3 amp HV fuses replaced. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001696 | 11 | 2017 | 2016-10-18 | C | 5 | 0.001696 | 1.5009e-05
1 | 14085508 | 2016-10-19 02:15 | 2016-10-19 13:54 | 698 | 315 | 48252.5167 | 0.14484 | 0.142 | 0.00094555 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 717209 | POLE | CB TA 8 tripped on O/C & E/F flags, received a call from a lady informing us that a tractor had hit a pole on Oeo Rd, and ask to call her husband as he is in charge of the tractors that are cutting the grass along the side of the roads The husband Chris Carter (027 937 6334) informed me that one of them had hit a pole and brought down lines. Faultman found tractor had hit & broken transformer T5305 pole structure, line was isolated at ABS's TA813 & TA840 & Fuses 6630. Used 1 X Pole 1X H/T Crossam Insulators Etc 1X H/T Fuse arm DDOs etc 1X L/V Arm Insulators 1X 15KVA Transformer NDR Number 100239 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.142 | 11 | 2017 | 2016-10-19 | C | 315 | 0.142 | 0.00094555
1 | 14086630 | 2016-10-19 05:28 | 2016-10-19 08:03 | 154 | 1 | 154.65 | 0.00046422 | 0.000455 | 3.0017e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2630 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a HV fuses @ 2630 suspect caused by geese . | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000455 | 11 | 2017 | 2016-10-19 | C | 1 | 0.000455 | 3.0017e-06
1 | 14091680 | 2016-11-05 08:35 | 2016-11-05 10:07 | 92 | 24 | 2208 | 0.0066265 | 0.00641 | 7.2027e-05 | NAPA ID:24442 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 024442 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To replace transformer T8/25 with lv fuses | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.003205 | 5.5 | 2017 | 2016-11-05 | B | 24 | 0.00641 | 7.2027e-05
1 | 14091684 | 2016-11-04 08:34 | 2016-11-04 12:44 | 250 | 18 | 4500 | 0.013505 | 0.013343 | 5.4021e-05 | NAPA ID:24683 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 024683 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | v12571 | NONE | Replacing Defected Transformer Pole V12571 TC3673 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0066715 | 5.5 | 2017 | 2016-11-04 | B | 18 | 0.013343 | 5.4021e-05
1 | 14092044 | 2016-11-07 08:35 | 2016-11-07 12:09 | 214 | 26 | 5567.4667 | 0.016708 | 0.016474 | 7.8027e-05 | NAPA ID:24752 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 024752 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 788480 | NONE | isolation of 11 kv line for treescape to fell trees at pole 788480 /788478 Paengoroa rd | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.008237 | 5.5 | 2017 | 2016-11-07 | B | 26 | 0.016474 | 7.8027e-05
1 | 14092506 | 2016-11-09 08:45 | 2016-11-09 15:20 | 395 | 114 | 44546 | 0.13368 | 0.13265 | 0.00034211 | NAPA ID:23536 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 023536 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814710 | NONE | replace defective poles 814710, 814704 and 814811 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.066327 | 5.5 | 2017 | 2016-11-09 | B | 114 | 0.13265 | 0.00034211
1 | 14093292 | 2016-10-20 10:15 | 2016-10-20 14:32 | 257 | 8 | 2056 | 0.0061715 | 0.006099 | 2.4014e-05 | NAPA ID:25782 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11 | Planned | 025782 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | n/a | NONE | Cut trees beyond Fuses FC2225 | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.0030495 | 5.5 | 2017 | 2016-10-20 | B | 8 | 0.006099 | 2.4014e-05
1 | 14094342 | 2016-11-09 08:30 | 2016-11-09 16:24 | 474 | 462 | 62370 | 0.18717 | 0.18301 | 0.0027729 | NAPA ID:23837 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 023837 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 702480 | NONE | 1: AP1 Create 11kV Line break at pole 700313. 2: AP2 Install all new cross arms on network pole 700351, replace network pole 702480 for a new 10m Busck pole with all new hardware. 3: AP3 Close 11kV Line Break at pole 700313. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.091506 | 5.5 | 2017 | 2016-11-09 | B | 462 | 0.18301 | 0.0027729
1 | 14095058 | 2016-10-20 00:23 | 2016-10-20 04:19 | 236 | 5 | 1180 | 0.003542 | 0.003497 | 1.5009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | C12873 | POLE | Badly damaged pole C12873 requires imediate replacement ( MIK 5 ) Isolation at fuses FC1458 ( spur no back feed ) Pole replaced all service restored Materials 1 x pole, 1 x H/V arm complete NDR No to follow | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.003497 | 11 | 2017 | 2016-10-20 | C | 5 | 0.003497 | 1.5009e-05
1 | 14095329 | 2016-11-01 09:15 | 2016-11-01 15:15 | 360 | 33 | 11880 | 0.035655 | 0.035358 | 9.9042e-05 | NAPA ID:23319 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023319 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 745136 | NONE | Change 11kv poles and xarms | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.017679 | 5.5 | 2017 | 2016-11-01 | B | 33 | 0.035358 | 9.9042e-05
1 | 14095331 | 2016-11-03 09:15 | 2016-11-03 15:28 | 373 | 33 | 12309 | 0.036942 | 0.036644 | 9.904e-05 | NAPA ID:23320 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023320 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | change 11 kv poles 745156, 745155, 745154, 745153, 745151,745150, 748148, 745146 745145 and xarms 745139 and 745137 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.018322 | 5.5 | 2017 | 2016-11-03 | B | 33 | 0.036644 | 9.904e-05
1 | 14095357 | 2016-11-08 08:30 | 2016-11-08 17:06 | 516 | 70 | 10223 | 0.030679 | 0.030049 | 0.00036612 | NAPA ID:23704 TP_WAIHOU GXP > MIKKELSEN ROAD SUB | 11 | Planned | 023704 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1184 | NONE | Ngarua Feeder Step 7-9b, Shut 5 Specified renewal works on Goodfellow and Rutherford Roads. IC610 replaced with FP1813 Replace ABS 1184 (DNO160332) | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.015024 | 5.5 | 2017 | 2016-11-08 | B | 70 | 0.030049 | 0.00036612
1 | 14096011 | 2016-11-08 09:00 | 2016-11-08 14:51 | 351 | 33 | 11583 | 0.034761 | 0.034463 | 9.9034e-05 | NAPA ID:23321 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023321 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 349 | NONE | change 11kv poles 745144,745143,745142,745141,745140,745136,745135,745134 and 745133 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.017232 | 5.5 | 2017 | 2016-11-08 | B | 33 | 0.034463 | 9.9034e-05
1 | 14096020 | 2016-11-10 09:00 | 2016-11-10 14:47 | 347 | 33 | 11451 | 0.034364 | 0.034066 | 9.9031e-05 | NAPA ID:23322 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023322 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 447343 | NONE | Reconductor 11kv line Between ABS349 and pole 745168 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.017033 | 5.5 | 2017 | 2016-11-10 | B | 33 | 0.034066 | 9.9031e-05
1 | 14096031 | 2016-11-18 09:00 | 2016-11-18 10:50 | 110 | 45 | 4950 | 0.014853 | 0.014447 | 0.00013503 | NAPA ID:23326 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023326 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742986 | NONE | Remove temporary 11kv fuses TEMP79 from pole 742986 and close break in line. add crimp in line at pole 742934 to bring sag back in line | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0072235 | 5.5 | 2017 | 2016-11-18 | B | 45 | 0.014447 | 0.00013503
1 | 14096151 | 2016-11-05 09:14 | 2016-11-05 14:15 | 301 | 2 | 602 | 0.0018067 | 0.001788 | 6.0022e-06 | NAPA ID:24982 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024982 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | se3-066 | NONE | Pole and conductor replacement down to Dam | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000894 | 5.5 | 2017 | 2016-11-05 | B | 2 | 0.001788 | 6.0022e-06
1 | 14097018 | 2016-11-08 09:29 | 2016-11-08 15:33 | 364 | 3 | 1092 | 0.0032771 | 0.00325 | 9.003e-06 | NAPA ID:23381 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 023381 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 216081 | NONE | Re-Conductor between pole 216081 and 216097 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001625 | 5.5 | 2017 | 2016-11-08 | B | 3 | 0.00325 | 9.003e-06
1 | 14097068 | 2016-11-08 08:50 | 2016-11-08 13:46 | 296 | 27 | 7992 | 0.023984 | 0.023741 | 8.1028e-05 | NAPA ID:24006 TP_TAURANGA 33 GXP > OMOKOROA SUB > TE PUNA | 11 | Planned | 024006 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 210369 | NONE | Replace Poles, hardware and conductors between 33kV/11kV poles 210369 & 342810 . | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.011871 | 5.5 | 2017 | 2016-11-08 | B | 27 | 0.023741 | 8.1028e-05
1 | 14097278 | 2016-11-10 09:19 | 2016-11-10 13:36 | 257 | 16 | 4112 | 0.01234 | 0.012195 | 4.8015e-05 | NAPA ID:23384 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 023384 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | se3-060 | NONE | Re-Conductor and change pole in Horse Paddock. No reconductoring due to dispute with landowner. Pole change only. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0060975 | 5.5 | 2017 | 2016-11-10 | B | 16 | 0.012195 | 4.8015e-05
1 | 14097365 | 2016-10-21 10:15 | 2016-10-21 11:20 | 65 | 16 | 1040 | 0.0031218 | 0.002977 | 4.8027e-05 | NAPA ID:25824 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 6.6 | Planned | 025824 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 775915 | NONE | Repair damaged conductor at pole 775915. Motete Road, Raetihi, Ohakune. W/O 30034305. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.0014885 | 3.3 | 2017 | 2016-10-21 | B | 16 | 0.002977 | 4.8027e-05
1 | 14097440 | 2016-11-14 09:00 | 2016-11-14 13:18 | 258 | 2 | 516 | 0.0015484 | 0.00153 | 6.0015e-06 | NAPA ID:24698 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11.00000000 | Planned | 024698 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Raise Transformer on Pole and Reconnductor LV | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000765 | 5.5 | 2017 | 2016-11-14 | B | 2 | 0.00153 | 6.0015e-06
1 | 14097454 | 2016-11-08 09:16 | 2016-11-08 12:31 | 194 | 143 | 27770.6 | 0.08334 | 0.082052 | 0.00042915 | NAPA ID:24885 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | 024885 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/178 | NONE | Replace 11kv DDOs on T3/178 | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.041026 | 5.5 | 2017 | 2016-11-08 | B | 143 | 0.082052 | 0.00042915
1 | 14097639 | 2016-10-30 01:00 | 2016-10-31 14:03 | 2222 | 210 | 8770 | 0.026322 | 0.024431 | 1.5007e-05 | NAPA ID:25729 TP_KINLEITH GXP | 11 | Planned | 025729 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2212 | NONE | To replace pole numbers KINBRD023, KINBRD024 and KINBRD072 so that removed poles can be sent to Busck for testing. PLEASE USE CHIAN HO's LATEST ENGINEERING STUDIES FOR THE BACKFEEDS REQUIRED FOR THIS JOB. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.012216 | 5.5 | 2017 | 2016-10-30 | B | 210 | 0.024431 | 1.5007e-05
1 | 14097696 | 2016-11-10 08:30 | 2016-11-10 13:25 | 295 | 11 | 3245 | 0.009738 | 0.009639 | 3.301e-05 | NAPA ID:24484 TP_KOPU GXP > COROMANDEL SUB > WYUNA BAY | 11 | Planned | 024484 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 320 | NONE | Replace Xarms and Line Hardware | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0048195 | 5.5 | 2017 | 2016-11-10 | B | 11 | 0.009639 | 3.301e-05
1 | 14101279 | 2016-10-21 02:58 | 2016-10-21 10:54 | 476 | 227 | 46355.1 | 0.13914 | 0.1371 | 0.0011526 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C956 | UNKNOWN | KEM CB 956 tripped - Flags A Phase, OC. Feeder sectionalised and patrolled. Fault proved difficult to locate with feeder restoring OK when Fuses 7499 were open.. However, the associated Transformers and lines restored OK with no fault found. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.1371 | 11 | 2017 | 2016-10-21 | C | 227 | 0.1371 | 0.0011526
1 | 14103186 | 2016-10-21 08:29 | 2016-10-21 08:33 | 4 | 79 | 338.3833 | 0.0010157 | 0.000304 | 0.00023713 |  | 11 | Planned | 025210 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Planned switching Napa 25210 Transformer G318 turned off not advertised | F3 | PASCAL ST 6 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0.000152 | 5.5 | 2017 | 2016-10-21 | B | 79 | 0.000304 | 0.00023713
1 | 14103306 | 2016-10-21 08:39 | 2016-10-21 10:53 | 133 | 17 | 2273.4667 | 0.0068242 | 0.006671 | 5.1029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798641 | FUSE - ELEMENT/LINK (HV) | Please check OMS 14103417 and 14103348 when closing 2 x8amp 7292 weather | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.006671 | 11 | 2017 | 2016-10-21 | C | 17 | 0.006671 | 5.1029e-05
1 | 14103413 | 2016-11-10 09:00 | 2016-11-10 13:18 | 258 | 86 | 22188 | 0.066585 | 0.06581 | 0.00025808 | NAPA ID:24936 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 024936 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | p03300 | NONE | Tree cutting and removal, between pole P03300 & P03332 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.032905 | 5.5 | 2017 | 2016-11-10 | B | 86 | 0.06581 | 0.00025808
1 | 14103800 | 2016-11-03 09:01 | 2016-11-03 15:13 | 372 | 109 | 40548 | 0.12169 | 0.12071 | 0.00032713 | NAPA ID:24154 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 024154 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Change ABS1241 and multiple site x-arms replacements within the permitted area. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.060355 | 5.5 | 2017 | 2016-11-03 | B | 109 | 0.12071 | 0.00032713
1 | 14104022 | 2016-11-02 09:42 | 2016-11-02 13:31 | 229 | 46 | 10534 | 0.031615 | 0.0312 | 0.00013806 | NAPA ID:24369 TP_WAIKINO GXP > WHANGAMATA SUB > PORT RD | 11 | Planned | 024369 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3358 | NONE | Switching to de-energise 11kV Transformer TC3358. ON COMPLETION OF THE HV ISOLATION: THE Tx LV BUSHINGS TO BE PROVED DE-ENERGIZED AND LV WORK COMPLETED UNDER AN INTERNAL (DOWNER) PERMIT/CONTROL SYSTEM. Repairs to damaged LV frame & cables. CONFIRMATION THAT LV PROTECTION MEASURES REMOVED & WORK COMPLETED. Re-liven Transformer TC3358. | F2/F3 | PORT RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.0156 | 5.5 | 2017 | 2016-11-02 | B | 46 | 0.0312 | 0.00013806
1 | 14104304 | 2016-10-21 11:28 | 2016-10-21 13:40 | 132 | 1 | 132.1667 | 0.00039672 | 0.000387 | 3.0016e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 4664W | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuse | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000387 | 11 | 2017 | 2016-10-21 | C | 1 | 0.000387 | 3.0016e-06
1 | 14104361 | 2016-10-21 15:25 | 2016-10-21 15:50 | 25 | 5 | 125 | 0.00037521 | 0.00033 | 1.5008e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TD3-174 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 15:25, Bethlehem Sub, CB 2 Wairoa Feeder. Faultman was dispatched to a job and found over voltage at Transformer TD3-174 (250V Ph to N, 433V Ph to Ph). Checked other transformers in the area and found voltage were okay. Isolated TD3-174 at Fuses S5927. Permit Issued and Changed taps on TD3-174 from Tap 4 down to Tap 2. Relivened, checked voltage & all OK. Clint Johnstone Attended. No Materials Used. Unsure if this work comes under 2R. Results after Tap Change: R+N: 234V Y+N: 236V B+N: 236V R+Y: 410V R+B: 410V Y+B: 414V unsure if this is 2R work | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.00033 | 11 | 2017 | 2016-10-21 | C | 5 | 0.00033 | 1.5008e-05
1 | 14104697 | 2016-10-21 15:00 | 2016-10-21 18:10 | 190 | 4 | 760 | 0.0022813 | 0.002245 | 1.2007e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X983 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Defective Transformer X983 replaced / relivened OK. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002245 | 11 | 2017 | 2016-10-21 | C | 4 | 0.002245 | 1.2007e-05
1 | 14104781 | 2016-10-21 13:56 | 2016-10-21 17:52 | 236 | 50 | 3340 | 0.010026 | 0.009575 | 0.00015008 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 834139 | POLE | Power pole on fire - sparking and smoking, just down the road from 814. Hazard process explained to customer - Jason, 0273082084 Called through to SMC ETA Required Fire comms in attendance - F2172697, have advised fire comms eta of 15mins First attended and a reload and reliven at Fuses 7737. Following more calls of no power and a call for a pole on fire another FM was sent and found Fuses 7030 blown. and a pole on fire past Fuses 7737. Suspect that the site was not inspected following the first reload and that the action of reloading 7737 blew 7030 causing a larger outage. Isolation required from Fuses 7737 to replace an 11kV Pole 834193. Fault caused by defective insulator causing conductor to fall on crossarm and start fire. Pole replaced along with all associated hardware, insulators and crossarm. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.009575 | 11 | 2017 | 2016-10-21 | C | 50 | 0.009575 | 0.00015008
1 | 14105090 | 2016-10-21 14:10 | 2016-10-21 15:30 | 80 | 12 | 960 | 0.0028816 | 0.002773 | 3.602e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847842 | CONDUCTOR - REPAIR/REHANG | Outage required past Fuses 6863 to raise height of conductors. No backfeeds available. Line raised, relivened OK | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.002773 | 11 | 2017 | 2016-10-21 | C | 12 | 0.002773 | 3.602e-05
1 | 14105615 | 2016-10-21 17:05 | 2016-10-21 20:40 | 215 | 1332 | 7191 | 0.021585 | 0.00959 | 0.00011406 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40953 | CONDUCTOR - REPAIR/REHANG | Advised by Fire Comms and Police that lines were sparking and now one line down and one dangling. Cindy at hub advised 5:17pm F21742862 and P027117317 Line deenergised and faulty section isolated via ABS A1 , ABS A29 & ABS A2 and backfeed put in place for the duration of repairs . Repaired lines and jumpers @ pole P40953 | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.00959 | 11 | 2017 | 2016-10-21 | C | 1332 | 0.00959 | 0.00011406
1 | 14108106 | 2016-10-22 00:05 | 2016-10-22 00:49 | 44 | 1 | 44 | 0.00013207 | 0.000123 | 3.0016e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209976 | JUMPER | Repair broken jumper at fuses SD2-021. Isolated at fuses SD2-009, no back feeds available. Wire re-terminated in to fuse holder. This Transformer is not in the outage area. I have sent to Kasey to investigate | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000123 | 11 | 2017 | 2016-10-22 | C | 1 | 0.000123 | 3.0016e-06
1 | 14108272 | 2016-10-22 00:05 | 2016-10-22 00:49 | 44 | 109 | 4796 | 0.014396 | 0.013414 | 0.00032718 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 209976 | JUMPER |  | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.013414 | 11 | 2017 | 2016-10-22 | C | 109 | 0.013414 | 0.00032718
1 | 14109078 | 2016-10-22 08:02 | 2016-10-22 09:10 | 68 | 755 | 51152.4667 | 0.15354 | 0.14674 | 0.0022662 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 364163 | NONE | CB TA2 Trip, No Flags. Patrolled with dead bird found at base of Pole 364163. Relivened in two stages. | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.14674 | 11 | 2017 | 2016-10-22 | C | 755 | 0.14674 | 0.0022662
1 | 14110032 | 2016-10-22 09:28 | 2016-10-22 10:05 | 36 | 7 | 258.5333 | 0.00077602 | 0.000712 | 2.1011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 147 PUAWAI ROAD | CROSSARM - COMPONENT(S) ONLY | Isolated HV at Fuses B53 to Straighten HV Crossarm from which King Bolt had loosened off. Nil materials used, | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000712 | 11 | 2017 | 2016-10-22 | C | 7 | 0.000712 | 2.1011e-05
1 | 14110182 | 2016-10-22 09:15 | 2016-10-22 10:55 | 100 | 219 | 15734.35 | 0.047229 | 0.045256 | 0.00065736 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NFF | UNKNOWN | CB R11 Trip, E/F. Sectionalised & Patrolled with no fault found. Suspect Bird Strike | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.045256 | 11 | 2017 | 2016-10-22 | C | 219 | 0.045256 | 0.00065736
1 | 14110977 | 2016-10-22 11:07 | 2016-10-22 11:19 | 12 | 37 | 456.3333 | 0.0013697 | 0.001036 | 0.00011106 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40953 | CONDUCTOR - REPAIR/REHANG | HV Lines had come down the night before and had been repaired that night. FM was out taking 'after' photos next morning & noticed some damage to overhead conductor, bad enough to be considered a red defect. Work area shutdown briefly to make repairs Materials used: 1mtr of 25mm cu & 2x sleeves | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.001036 | 11 | 2017 | 2016-10-22 | C | 37 | 0.001036 | 0.00011106
1 | 14111191 | 2016-10-22 17:10 | 2016-10-22 18:44 | 94 | 19 | 1786 | 0.0053609 | 0.005189 | 5.7031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227109 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | at 17:10, Pongakawa Sub, CB 2 Otamarakau Feeder. Found broken HV Fuse Holder at Transformer TE8-028. Isolated Lines at Fuses SE7-037. Permit Issued & Repairs Carried out. All Power Restored on Completion. Brian Sperling Attended. 1x complete DDO replaced, replaced 3 elements 3 amp. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.005189 | 11 | 2017 | 2016-10-22 | C | 19 | 0.005189 | 5.7031e-05
1 | 14112643 | 2016-10-22 20:07 | 2016-10-22 23:47 | 219 | 882 | 68382.5167 | 0.20526 | 0.19732 | 0.001864 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T1525 | SECTIONALISER (HV) | CB 5 A/R B & C O/C Sectionaliser 9839 Tripped. Line Patrolled & sectionalised. Tree across the line at pole T1525. Isolation at ABS IC380, Links 9235/6 ABS 9235/1. No Back feeds available. Temp line breaks cut at poles T13030 & T1523 supply restored. Asplundh will cut tree on 25/10/16. Temp Line breaks will need to be restored under an advertised shutdown. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.19732 | 11 | 2017 | 2016-10-22 | C | 882 | 0.19732 | 0.001864
1 | 14121394 | 2016-10-23 20:43 | 2016-10-24 00:49 | 245 | 566 | 121867.6333 | 0.3658 | 0.3607 | 0.0016989 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 213758 | POLE | at, 20:43, Omanu Sub, CB 7 Central Parade. Fire Service called into report Car Vs Pole at 472 Maunganui Rd, Pole 213758. Duty NC determined that HV pole had been hit using Google Streetview. CB 7 Opened. Faultmen dispatched. Isolated Lines at Sw/gear 9564/1 & ABS SC4-097. Remainder of Feeder Relivened. Permit issued & repairs carried out. HV Restored at 00:47. Repairs continued on LV circuits. NDR # TBA. Materials: 1x Pole, 4x Crossamrs, 9x Insulators, Binders, 32m of 25mm2 Cu Cable all 3 phases. 00:55 Advised UFB of fibre damaged on pole at 472 Maunganui Rd. Car V Pole - fire comms called in. pole sheared off at bottom only wires holding it up. F2173904 | F3 | CENTRAL PARADE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.3607 | 11 | 2017 | 2016-10-23 | C | 566 | 0.3607 | 0.0016989
1 | 14122475 | 2016-10-24 07:12 | 2016-10-24 08:32 | 79 | 24 | 1908.8 | 0.0057294 | 0.005513 | 7.2038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 495 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 495, line was patrolled and a farmer informed the faultman that birds had hit the lines faultman is going to put a defect in on Spar. 2 X 10 amp HV fuses replaced | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.005513 | 11 | 2017 | 2016-10-24 | C | 24 | 0.005513 | 7.2038e-05
1 | 14125692 | 2016-10-25 13:00 | 2016-10-25 14:03 | 63 | 1 | 63 | 0.0001891 | 0.00018 | 3.0015e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | X5064 | SERVICE BOX COVER - GYRO/PILLAR/POD (LV) | Caller advised TX # was 8981? FM advised was a 11kv switch gear: 8981 that a vehicle has hit NDR: 047502 FM has taken photos, made safe and contacted Blair from sub-electrical to organise repairs Nothing else repaired or replaced and all adjacent assets ok | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00018 | 11 | 2017 | 2016-10-25 | C | 1 | 0.00018 | 3.0015e-06
1 | 14126764 | 2016-11-09 08:30 | 2016-11-09 16:01 | 451 | 233 | 70233 | 0.21077 | 0.20867 | 0.0010113 | NAPA ID:24553 TP_MT MAUNGANUI 33 GXP > OMANU SUB > CENTRAL PARADE | 11 | Planned | 024553 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 213744 | NONE | RE POLE AND RECON 11KV FEEDER | F3 | CENTRAL PARADE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.10433 | 5.5 | 2017 | 2016-11-09 | B | 233 | 0.20867 | 0.0010113
1 | 14127484 | 2016-11-12 09:08 | 2016-11-12 14:55 | 347 | 29 | 10063 | 0.030198 | 0.029936 | 8.7025e-05 | NAPA ID:23706 TP_WAIHOU GXP | 11 | Planned | 023706 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | temp 14 | NONE | Ngarua Feeder Step 12b, Shut 8 Specified renewal works on SH26 Specified distribution renewal works completed between poles C1806 and WHUWTO061. | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.014968 | 5.5 | 2017 | 2016-11-12 | B | 29 | 0.029936 | 8.7025e-05
1 | 14128980 | 2016-10-25 19:17 | 2016-10-25 19:55 | 38 | 1 | 38.3333 | 0.00011506 | 0.000106 | 3.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | X2905 | FUSE - ELEMENT/LINK (HV) | FM reported car hit pole & fuses dropped out. Fuses closed again. Links not replaced. NDR N200056 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.000106 | 11 | 2017 | 2016-10-25 | C | 1 | 0.000106 | 3.0015e-06
1 | 14129243 | 2016-10-25 19:46 | 2016-10-25 21:24 | 98 | 179 | 14181.0833 | 0.042565 | 0.040953 | 0.00053727 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N/A - NOT APPLICABLE | UNKNOWN | RS 2032 Trip, E/F. Sectionalised with No fault found. Suspect Bird Strike | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.040953 | 11 | 2017 | 2016-10-25 | C | 179 | 0.040953 | 0.00053727
1 | 14130128 | 2016-10-26 02:11 | 2016-10-26 03:35 | 84 | 1 | 84.1667 | 0.00025263 | 0.000243 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1067 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000243 | 11 | 2017 | 2016-10-26 | C | 1 | 0.000243 | 3.0014e-06
1 | 14130135 | 2016-10-26 02:23 | 2016-10-26 04:10 | 106 | 1 | 106.9333 | 0.00032096 | 0.000311 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 936 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Links | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000311 | 11 | 2017 | 2016-10-26 | C | 1 | 0.000311 | 3.0014e-06
1 | 14130142 | 2016-10-26 02:25 | 2016-10-26 05:10 | 165 | 3 | 495.7 | 0.0014878 | 0.00146 | 9.0044e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2634T | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Fuses & 1x Fuse Carrier | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.00146 | 6.6 | 2017 | 2016-10-26 | C | 3 | 0.00146 | 9.0044e-06
1 | 14130199 | 2016-10-26 04:34 | 2016-10-26 04:48 | 14 | 1 | 14 | 4.2021e-05 | 3.3e-05 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1928N | FUSE - ELEMENT/LINK (HV) | 2x HV Fuses blown at Transformer. Seen by FM driving past Replaced 2x 3Amp Fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 3.3e-05 | 11 | 2017 | 2016-10-26 | C | 1 | 3.3e-05 | 3.0014e-06
1 | 14130230 | 2016-10-26 05:51 | 2016-10-26 08:14 | 143 | 15 | 2151.75 | 0.0064585 | 0.006323 | 4.5022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N12681 | CIRCUIT BREAKER (HV) | rec 9901 trip line patrolled nothing found | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.006323 | 11 | 2017 | 2016-10-26 | C | 15 | 0.006323 | 4.5022e-05
1 | 14130431 | 2016-10-26 07:44 | 2016-10-26 08:04 | 19 | 630 | 9034.5333 | 0.027117 | 0.021444 | 0.0018909 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 636 | FUSE - ELEMENT/LINK (HV) | C 5 Trip O/C during planned switching for NAPA 25883 - incorrect fuse size at fuses 636 (was 5amp should have been 30amp) | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.021444 | 11 | 2017 | 2016-10-26 | C | 630 | 0.021444 | 0.0018909
1 | 14131208 | 2016-10-26 12:00 | 2016-10-26 15:19 | 199 | 160 | 31840 | 0.095568 | 0.094126 | 0.00048024 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | Transformer T1018 Palliser Bay pole No 797291 | POLE | ###Red Defect### Inspect site, appears to show evidence of burning on the HV. Advise required actions and what is to be replaced. Ring Andrew 027 582 2342 of details. Note, If an outage is required, please make arrange times with NOC so retailers can be informed. Isolated at ABS S561 Complete structure replaced all works are to be charged to the PO 595376 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.094126 | 11 | 2017 | 2016-10-26 | C | 160 | 0.094126 | 0.00048024
1 | 14132434 | 2016-10-26 07:56 | 2016-10-26 09:50 | 113 | 21 | 2387 | 0.0071646 | 0.006975 | 6.3031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8195 & 6542 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a & 1x 3a HV fuses | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.006975 | 11 | 2017 | 2016-10-26 | C | 21 | 0.006975 | 6.3031e-05
1 | 14135491 | 2016-11-11 09:30 | 2016-11-11 14:35 | 305 | 4 | 1220 | 0.0036611 | 0.003625 | 1.2004e-05 | NAPA ID:25778 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | 025778 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 7042P | NONE | Remove transformer from drain and put on new platform. WO 30000862 | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.0018125 | 5.5 | 2017 | 2016-11-11 | B | 4 | 0.003625 | 1.2004e-05
1 | 14135754 | 2016-11-11 09:15 | 2016-11-11 12:43 | 208 | 75 | 15600 | 0.046814 | 0.046138 | 0.00022507 | NAPA ID:24781 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 024781 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP662 | NONE | Replacing existing pole and installing a new aerial stay and stub pole. Works location: Lochhead Rd, Tauranga. WO 30033232 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.023069 | 5.5 | 2017 | 2016-11-11 | B | 75 | 0.046138 | 0.00022507
1 | 14135758 | 2016-10-26 14:22 | 2016-10-28 11:50 | 2728 | 61 | 1158.3667 | 0.0034768 | 0.002927 | 0.00018309 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I13312 | LIGHTNING ARRESTOR (HV) | Fuses open Tagged due to suspected cable fault to be investigated by technician tomorrow 27/10/16 OMS 14135758 Chorus running on generator in the meantime Outage required past Fuses FC2737 to test cable and replace faulty lightening arrestors. Cable tests OK. Short outage required from ABS 596 due to 800m cable length feeding to Transformer TC6155. ABS 638 has a DNO and so could not be used. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.002927 | 11 | 2017 | 2016-10-26 | C | 61 | 0.002927 | 0.00018309
1 | 14136902 | 2016-10-26 19:57 | 2016-10-26 21:12 | 74 | 1 | 74.6167 | 0.00022396 | 0.000214 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 795732 | UNKNOWN | Faultman found that fire was about 50 meters from the lines near pole 795732. Fire services advised Faultman that fire was under control and it started to rain and no more danger to lines. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000214 | 11 | 2017 | 2016-10-26 | C | 1 | 0.000214 | 3.0014e-06
1 | 14137274 | 2016-10-26 20:43 | 2016-10-26 22:25 | 102 | 246 | 25092 | 0.075314 | 0.073098 | 0.00073837 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C639 | UNKNOWN | Sectionaliser C639 Found Tripped. Reclosed OK. Feeder patrolled but no cause found. | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.073098 | 11 | 2017 | 2016-10-26 | C | 246 | 0.073098 | 0.00073837
1 | 14139701 | 2016-10-27 06:18 | 2016-10-27 07:57 | 99 | 1 | 99 | 0.00029714 | 0.000288 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H0466 | FUSE - ELEMENT/LINK (HV) | 2 x6am,p fuse @ fc2113 duck | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000288 | 11 | 2017 | 2016-10-27 | C | 1 | 0.000288 | 3.0014e-06
1 | 14139722 | 2016-11-14 09:02 | 2016-11-14 16:09 | 427 | 237 | 53964 | 0.16193 | 0.1598 | 0.0011343 | NAPA ID:23405 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 023405 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 700534 | NONE | AP/01 - Install LV Generation on TX 234,818 & 441.AP/02 - Install new LV transformer fusing at TX 864, Replace pole 700534,700245. AP/03 - Un-connect generation and restore supply. Cutfield Road, New Plymouth. W/O 30018596. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0799 | 5.5 | 2017 | 2016-11-14 | B | 237 | 0.1598 | 0.0011343
1 | 14139881 | 2016-10-27 07:34 | 2016-10-27 10:12 | 158 | 237 | 17876.05 | 0.053654 | 0.05152 | 0.00071135 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C1808 | CONDUCTOR - REPAIR/REHANG | 11kV CB 7 A/R O/C E/F AND 33kV CB 60 tripped on O/C & E/F also CBs 17 , 18 & 19 had pick ups .. CB 7 dropped due to flaging and proximity to State highway 26 . feeders on same poles . Report received as below OMS 14140815 Check for safety - duck has hit service line. Heard an explosion and seen sparks. No loss of supply. Created as a site inspection due to current feeder fault in the area. Advised SMC of 999 Spoke to customer have advised the ducks have hit the network, not service. Waiting on FM doing line patrol for feeder fault to confirm whether this is one and the same. Line repaired @ pole C1808 | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.05152 | 11 | 2017 | 2016-10-27 | C | 237 | 0.05152 | 0.00071135
1 | 14142241 | 2016-11-18 09:16 | 2016-11-18 15:29 | 373 | 4 | 1492 | 0.0044769 | 0.00444 | 1.2002e-05 | NAPA ID:24836 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 024836 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole D12593 | NONE | To replace a damaged transformer pole. 132 Plantation Road, Maungatautari, Cambridge, Tirau. W/O 30033429. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.00222 | 5.5 | 2017 | 2016-11-18 | B | 4 | 0.00444 | 1.2002e-05
1 | 14142319 | 2016-11-16 08:30 | 2016-11-16 09:12 | 42 | 88 | 3317 | 0.0099533 | 0.009161 | 0.00026406 | NAPA ID:23549 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 023549 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX T1292 | NONE | Replace defective poles 814482 and 814277. Lyon Street Featherston, Greytown. W/O 300030519. Work not completed. it was raining so could not do live line | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.0045805 | 5.5 | 2017 | 2016-11-16 | B | 88 | 0.009161 | 0.00026406
1 | 14142365 | 2016-11-21 09:36 | 2016-11-21 14:23 | 287 | 7 | 2009 | 0.006028 | 0.005964 | 2.1003e-05 | NAPA ID:24111 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024111 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole C13929 | NONE | LLP1: Pole C13929, To remove leads from top of fuses FC2102 (Safety Measure due to clearance from isolated side of fuses). AP: To replace 11kV cross arm on pole C1377 & Install a new set of 11kV Fuses Replacing FC2102 (Use same Number). LLP2: Pole C13929, To remove the old set of fuses and reconnect the line. 1010 Paeroa Tahuna Road, Otway, Te Aroha, Mikkelsen Road. W/O 30031668. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.002982 | 5.5 | 2017 | 2016-11-21 | B | 7 | 0.005964 | 2.1003e-05
1 | 14142581 | 2016-11-01 08:04 | 2016-11-09 12:57 | 11812 | 70 | 36321.8333 | 0.10901 | 0.10838 | 0.00042018 | NAPA ID:21986 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 5 | 11 | Planned | 021986 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/169 | NONE | install and connect temp tx 7427P to switch 100 and liven, demolish old T6/169 tx site and install new tx 7403P and new switch 10313. Carry out jointing on the 11KV, cut over 11KV and 400v cables into new equip liven and commission. | F3 | PASCAL ST 5 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0.054191 | 5.5 | 2017 | 2016-11-01 | B | 70 | 0.10838 | 0.00042018
1 | 14143192 | 2016-10-27 14:15 | 2016-10-27 17:42 | 206 | 2 | 413.6667 | 0.0012416 | 0.001223 | 6.0029e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Unable to Open CB C404 at Kourarau Generation site Require Trusthouse contractor on site Once contractor on site CB C404 could not be opened locally either, Contractor removed plants from service and CB C947 Closed | F4 | KOURARAU | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001223 | 11 | 2017 | 2016-10-27 | C | 2 | 0.001223 | 6.0029e-06
1 | 14143776 | 2016-11-10 08:33 | 2016-11-10 13:02 | 269 | 104 | 27976 | 0.083954 | 0.083017 | 0.0003121 | NAPA ID:24550 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CENTRAL TRITON | 11 | Planned | 024550 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 381950 | NONE | RE POLE AND RECON 11KV FEEDER. Tawa Street, Triton, Maunganui. W/O 30019230. | F2 | CENTRAL TRITON | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.041508 | 5.5 | 2017 | 2016-11-10 | B | 104 | 0.083017 | 0.0003121
1 | 14144703 | 2016-10-27 23:34 | 2016-10-28 00:44 | 69 | 334 | 22604.2667 | 0.067846 | 0.064838 | 0.0010025 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209601 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | ( OMO2 ) Emergency switching to replace burnt fuse holder at Fuses SD2 025 Isolation between ABS SD2 007, ABS SD2 004 & recloser links 9560/6 with back feed via ABS SC2 024 Fuses holder replaced, all service restored Materials 1 x fuse holder 3 x 6A fuses, 6 x H/V sleeves, 2 x metres conductor | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.064838 | 11 | 2017 | 2016-10-27 | C | 334 | 0.064838 | 0.0010025
1 | 14145491 | 2016-11-22 09:30 | 2016-11-22 10:04 | 34 | 77 | 2618 | 0.0078552 | 0.007162 | 0.00023103 | NAPA ID:25128 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 14 | 11 | Planned | 025128 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 1344 | NONE | putting up low voltage 160amp fuses on double trany structure 1344,so we can change low tension pole 753468. Parsons Street, Brooklands, Carrington. W/O 30018430. | F4 | BROOKLANDS 14 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003581 | 5.5 | 2017 | 2016-11-22 | B | 77 | 0.007162 | 0.00023103
1 | 14145699 | 2016-10-31 10:30 | 2016-10-31 11:15 | 45 | 247 | 10779.5333 | 0.032353 | 0.030128 | 0.00074133 | NAPA ID:26093 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 026093 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 380 | NONE | Access Permit to rclose Line Breaks at Poles T13030 and T1523. Works location: Hwy 25, Thames Coast. WO 30024974 | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.015064 | 5.5 | 2017 | 2016-10-31 | B | 247 | 0.030128 | 0.00074133
1 | 14145769 | 2016-11-23 10:00 | 2016-11-23 14:05 | 245 | 2 | 490 | 0.0014702 | 0.001452 | 6.0008e-06 | NAPA ID:25062 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 025062 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 704852 | NONE | Replace Transformer &replace HV Xarm & install New 11KV Transformer Fuses. Stent Road, Warea, Pungarehu. W/O 30030348. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000726 | 5.5 | 2017 | 2016-11-23 | B | 2 | 0.001452 | 6.0008e-06
1 | 14146638 | 2016-10-28 12:39 | 2016-10-28 15:07 | 148 | 1 | 148 | 0.00044421 | 0.000435 | 3.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772396 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp unknown | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000435 | 11 | 2017 | 2016-10-28 | C | 1 | 0.000435 | 3.0014e-06
1 | 14146712 | 2016-11-24 09:30 | 2016-11-24 14:09 | 279 | 37 | 10323 | 0.030973 | 0.030639 | 0.00011101 | NAPA ID:25978 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | 025978 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 721523 | NONE | Replace red defect transformer pole W5225 and associated hardware. South Road, Hawera, Manawapou. W/O 30033364. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.015319 | 5.5 | 2017 | 2016-11-24 | B | 37 | 0.030639 | 0.00011101
1 | 14147513 | 2016-10-28 20:30 | 2016-10-29 09:54 | 804 | 57 | 23300.5 | 0.069935 | 0.069421 | 0.00017108 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11397 | INSULATOR | Reports of part / no power found 2 HT Fuses tripped at both S9 and S11 sites. All fuses open at S11 with Fuses S9 reclosed OK. Patrol carried out from Fuses S11 but unable to find fault during night hours. To be patrolled during daylight hours. Line was patrolled in morning and a floating wire was found at pole P11397 and 2 old insulators were replaced with clamp top insulators. 2 X 11KV Clamp top insulators replaced. 2 X 10 amp HV fuses replaced. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.069421 | 11 | 2017 | 2016-10-28 | C | 57 | 0.069421 | 0.00017108
1 | 14147742 | 2016-10-28 22:20 | 2016-10-29 04:23 | 362 | 703 | 109092.6167 | 0.32743 | 0.3211 | 0.004301 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD5 145 | CABLE - REPAIR | MTP3 tripped E/F, C Ph O/C, L/O. Feeder sectionalised & when Sw/Gear SC5 026, 022, 024 & 020 livened Sw/Gear seemed to be in distress Sw/Gear isolated with back feeds via Sw/Gear SD5 174 & ABS SC5 010 all services restored . Found while switching for isolation Fused/sw 9768/2 fuses blown Sw/Gear 9768/2 isolated & cables tested & faulty cable found between transformer TD5 145 & Fused/sw 9588/4. Faulty section isolated & earthed All Services restored, feeder returned to normal config NOTE Sw/Gear SC5 026,022, 024 & 020 checked out ok by elect | F2 | MOUNT | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.3211 | 11 | 2017 | 2016-10-28 | C | 703 | 0.3211 | 0.004301
1 | 14150990 | 2016-10-29 12:32 | 2016-10-29 16:15 | 223 | 26 | 5458.5667 | 0.016383 | 0.016149 | 7.8036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2713/2 | UNKNOWN | Recloser 2713/2 tripped on B & C phase fault, line was patrooled and sectionalised and no fault was found. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.016149 | 11 | 2017 | 2016-10-29 | C | 26 | 0.016149 | 7.8036e-05
1 | 14152821 | 2016-10-30 08:14 | 2016-10-30 08:15 | 1 | 5 | 5 | 1.5007e-05 | 0 | 1.5007e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TC645 | NONE | Isolated TC645 at 08:14. Tapped transformer up. Believed voltage was low due to backfeed for NAPA 25729. Checked voltage after - was all OK RtoN: 234V, YtoN: 235V & BtoN: 234V. Checked back later once backfeed removed and voltage was still OK. OFF: 08:14 ON: 08:15. | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-10-30 | C | 5 | 0 | 1.5007e-05
1 | 14153199 | 2016-11-28 09:44 | 2016-11-28 11:40 | 116 | 9 | 1044 | 0.0031322 | 0.003051 | 2.7002e-05 | NAPA ID:25134 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025134 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4629 | NONE | To replace the 11kV Fuse arm and install a 400V disconnector on TC4629. Works location: Oreipunga Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0015255 | 5.5 | 2017 | 2016-11-28 | B | 9 | 0.003051 | 2.7002e-05
1 | 14153265 | 2016-11-28 14:00 | 2016-11-28 14:45 | 45 | 2 | 90 | 0.00027002 | 0.000252 | 6.0003e-06 | NAPA ID:25135 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025135 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4632 | NONE | To install a 400V Fuse Disconnector on TC4632. Works location: Oreipunga Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000126 | 5.5 | 2017 | 2016-11-28 | B | 2 | 0.000252 | 6.0003e-06
1 | 14153269 | 2016-11-28 10:00 | 2016-11-28 10:45 | 45 | 4 | 180 | 0.00054003 | 0.000504 | 1.2001e-05 | NAPA ID:25150 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025150 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1599 | NONE | To install a 400V Fuse Disconnector on TC1599. Works location: Hwy 1, Maungatautari. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000252 | 5.5 | 2017 | 2016-11-28 | B | 4 | 0.000504 | 1.2001e-05
1 | 14153293 | 2016-11-28 11:45 | 2016-11-28 12:45 | 60 | 5 | 300 | 0.00090006 | 0.000855 | 1.5001e-05 | NAPA ID:25152 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025152 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2156 | NONE | To install a 400V Fuse disconnector on TC2156. Works location: Hwy 1, Maungatautari. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0004275 | 5.5 | 2017 | 2016-11-28 | B | 5 | 0.000855 | 1.5001e-05
1 | 14153297 | 2016-11-28 13:45 | 2016-11-28 14:45 | 60 | 3 | 180 | 0.00054003 | 0.000513 | 9.0005e-06 | NAPA ID:25153 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025153 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1638 | NONE | To install a 400V Fuse Disconnector on TC1638. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0002565 | 5.5 | 2017 | 2016-11-28 | B | 3 | 0.000513 | 9.0005e-06
1 | 14153303 | 2016-11-30 10:00 | 2016-11-30 11:05 | 65 | 5 | 325 | 0.00097503 | 0.00093 | 1.5e-05 | NAPA ID:25155 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025155 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC349 | NONE | To install a 400V Fuse Disconnector on TC349. Works location: Hill Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000465 | 5.5 | 2017 | 2016-11-30 | B | 5 | 0.00093 | 1.5e-05
1 | 14153318 | 2016-11-30 12:08 | 2016-11-30 12:40 | 32 | 1 | 32 | 9.6003e-05 | 8.7e-05 | 3.0001e-06 | NAPA ID:25157 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025157 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4204 | NONE | To install a 400V Disconnector on TC4204. Works location: Hill Rd, Maungatautari. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 4.35e-05 | 5.5 | 2017 | 2016-11-30 | B | 1 | 8.7e-05 | 3.0001e-06
1 | 14153324 | 2016-11-30 14:15 | 2016-11-30 14:33 | 18 | 5 | 90 | 0.00027001 | 0.000225 | 1.5e-05 | NAPA ID:25159 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025159 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4207 | NONE | To install a 400V Fuse Disconnector on TC4207. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001125 | 5.5 | 2017 | 2016-11-30 | B | 5 | 0.000225 | 1.5e-05
1 | 14153330 | 2016-11-30 13:45 | 2016-11-30 14:20 | 35 | 3 | 105 | 0.00031501 | 0.000288 | 9.0003e-06 | NAPA ID:25141 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025141 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4208 | NONE | To install a 400V Fuse disconnector on TC4208. Works location: Plantation Rd, Cambridge. OW 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000144 | 5.5 | 2017 | 2016-11-30 | B | 3 | 0.000288 | 9.0003e-06
1 | 14153333 | 2016-11-30 14:00 | 2016-11-30 14:25 | 25 | 3 | 75 | 0.00022501 | 0.000198 | 9.0003e-06 | NAPA ID:25138 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025138 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2327 | NONE | To install a 400V Fuse Disconnector on TC2327. Works location: Findlay Rd, Maungatautari. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 9.9e-05 | 5.5 | 2017 | 2016-11-30 | B | 3 | 0.000198 | 9.0003e-06
1 | 14153619 | 2016-11-30 09:30 | 2016-11-30 12:35 | 185 | 3 | 555 | 0.0016651 | 0.001638 | 9.0003e-06 | NAPA ID:25137 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025137 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC614 | NONE | To replace the 11kV pin arm, 11kV fuse Arm & install a 400V Fuse Disconnector on TC614. Works location: Oreipunga Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000819 | 5.5 | 2017 | 2016-11-30 | B | 3 | 0.001638 | 9.0003e-06
1 | 14153714 | 2016-11-24 09:32 | 2016-11-24 12:42 | 189 | 2 | 379.4 | 0.0011383 | 0.00112 | 6.0007e-06 | NAPA ID:25381 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 025381 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2295 | NONE | To replace 11kV Fuse arm, 400V Arm & install a 400V Disconnector. Works location: Puketutu Rd. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.00056 | 5.5 | 2017 | 2016-11-24 | B | 2 | 0.00112 | 6.0007e-06
1 | 14153951 | 2016-11-25 09:15 | 2016-11-25 16:01 | 405 | 9 | 3652.5 | 0.010959 | 0.010877 | 2.7003e-05 | NAPA ID:25033 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025033 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole D1739 | NONE | LLP1: To break the jumpers on pole D1739 to Lewis Rd SW 867. AP: To replace switch 867 with Drop Out Fuses and complete line maint. beyond 867. LLP2: To replace the jumpers on pole D1739 to Lewis Rd SW 867. Works location: Lewis Rd, Okoroire. WO 30019182 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0054385 | 5.5 | 2017 | 2016-11-25 | B | 9 | 0.010877 | 2.7003e-05
1 | 14153994 | 2016-11-29 09:15 | 2016-11-29 09:35 | 20 | 5 | 100 | 0.00030001 | 0.000255 | 1.5001e-05 | NAPA ID:25282 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 025282 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1822 | NONE | AP: to install a LV Isolator on TC1822. LLP: To replace pole K12511. Works location: Quine Rd, Morrinsville. WO 30031125 | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0001275 | 5.5 | 2017 | 2016-11-29 | B | 5 | 0.000255 | 1.5001e-05
1 | 14154057 | 2016-10-30 13:06 | 2016-10-30 14:10 | 64 | 33 | 2120.8 | 0.0063653 | 0.006068 | 9.9045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | E27 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV Fuses | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.006068 | 11 | 2017 | 2016-10-30 | C | 33 | 0.006068 | 9.9045e-05
1 | 14154134 | 2016-10-30 14:45 | 2016-10-30 16:35 | 110 | 6 | 660 | 0.0019809 | 0.001926 | 1.8008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | B13459 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | at 14:45, Coromandel Sub, CB 7 Kapanga Rd Feeder. Faultman called to lines down. Found lines had been brought down by customer cutting trees and branches fell on line and pulled lines down. Isolated lines at Fuses FC1412. Permit issued & repairs carried out. All Power restored on completion. Justin Kerrison Attended. Replaced less than 1 span 1 phase of condcutor, 2x connectors & 1x dead end. NDR 047817. Pole B13459 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.001926 | 11 | 2017 | 2016-10-30 | C | 6 | 0.001926 | 1.8008e-05
1 | 14154957 | 2016-11-30 09:30 | 2016-11-30 12:48 | 198 | 42 | 8316 | 0.024949 | 0.02457 | 0.000126 | NAPA ID:25145 TP_CARRINGTON GXP > OAKURA SUB > INLAND COAST | 11 | Planned | 025145 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 414 | NONE | to replace lightning arrestors at pole 757534. Works location: Upper Pitone Rd. WO 30027581 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.012285 | 5.5 | 2017 | 2016-11-30 | B | 42 | 0.02457 | 0.000126
1 | 14155086 | 2016-10-30 18:03 | 2016-10-30 19:51 | 108 | 179 | 18582.35 | 0.055772 | 0.05416 | 0.00053724 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | Recloser 2032 Tripped E/F Patrolled most of line found nothing Took a long Time (48 minutes to disable A/R ) but once done nothing found | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.05416 | 11 | 2017 | 2016-10-30 | C | 179 | 0.05416 | 0.00053724
1 | 14161269 | 2016-11-15 09:26 | 2016-11-15 15:50 | 384 | 17 | 6528 | 0.019589 | 0.019435 | 5.1013e-05 | NAPA ID:24251 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024251 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 217685 | NONE | Re-conductor and remove Links TEMP85. Kumikumi Road - Kaimai Drive- Tauranga. W/O 30017842. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0097175 | 5.5 | 2017 | 2016-11-15 | B | 17 | 0.019435 | 5.1013e-05
1 | 14161826 | 2016-11-18 09:31 | 2016-11-18 14:20 | 289 | 55 | 15918.8333 | 0.047766 | 0.047271 | 0.00016503 | NAPA ID:24599 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 024599 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P25887 | NONE | Replace old #8 conductor. Nireaha Road, Hukanui, Parkville. W/O 30029313. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.023636 | 5.5 | 2017 | 2016-11-18 | B | 55 | 0.047271 | 0.00016503
1 | 14163263 | 2016-10-31 19:40 | 2016-11-01 02:35 | 414 | 203 | 12168.6167 | 0.036522 | 0.034694 | 0.00071431 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 230386 | POLE | at 19:40, Pongakawa Sub, CB 4 Old Coach Rd Feeder, Tripped, O/C, Auto Reclosed. Faultman was requested to carry out line patrol. While faultman was on way to patrol line, call came in from retailer of Car V Pole on Manaiatutu Rd. NOC Opened CB 4 at 20:08. Faultman arrived on site and found that pole 230386 had been hit by car and had pulled away from the lines - pole on the ground but lines still up in the air and safe. Faultman isolated transformer TP1003 due to LV lines being damaged. NOC Closed CB 4 at 20:38. Line Crew arrived to carryout repairs. Made up Pole for replacement and then at 00:20, Isolated lines at ABS SF7-003 & SE7-007. Permit issued and repairs carried out. All Power then restored on completion. Mike James Attended. Used 1x Pole, 4x Crossarms & Complete with Insulators, 6x Dead ends, 2x 63A HRC LV Fuses, Less than 1 span all 3 phases of conductor. NDR 400222 | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.034694 | 11 | 2017 | 2016-10-31 | C | 203 | 0.034694 | 0.00071431
1 | 14164627 | 2016-11-01 08:10 | 2016-11-01 13:27 | 317 | 13 | 4125.1167 | 0.012381 | 0.012263 | 3.9017e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4973 | FUSE - HOLDER/BASE (LV) | 2 x fuse bases lv lv bus pack mounting boaurd isolated hv for lv work old age | F2 | WILLOUGHBY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.012263 | 11 | 2017 | 2016-11-01 | C | 13 | 0.012263 | 3.9017e-05
1 | 14164781 | 2016-11-17 09:00 | 2016-11-17 14:34 | 334 | 25 | 8350 | 0.025056 | 0.02483 | 7.5016e-05 | NAPA ID:24704 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | 024704 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2327 DDOs | NONE | Replace and move 11KV Pole due to slip. 34 Ohinau Drive - Opito Bay - Whitianga. W/O 30027341. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.012415 | 5.5 | 2017 | 2016-11-17 | B | 25 | 0.02483 | 7.5016e-05
1 | 14164900 | 2016-11-15 09:12 | 2016-11-15 14:46 | 334 | 9 | 3006 | 0.0090202 | 0.008939 | 2.7007e-05 | NAPA ID:24746 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 024746 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 200688 | NONE | Replace Poles, hardware and conductors. Install new ABS IP654. Remove SD3-070. Armstrong Road - Waipuna - Bethlehem. W/O 30019163. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.0044695 | 5.5 | 2017 | 2016-11-15 | B | 9 | 0.008939 | 2.7007e-05
1 | 14165138 | 2016-11-01 09:25 | 2016-11-01 12:01 | 156 | 4 | 624.3333 | 0.0018738 | 0.001837 | 1.2005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228389 | FUSE - ELEMENT/LINK (HV) | Reload reliven 2 x3A at Transformer TF7-025 1 x 6A at fuses SF7-014 & Battell Caused by Line Clash - Shay has seen the same thing before | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001837 | 11 | 2017 | 2016-11-01 | C | 4 | 0.001837 | 1.2005e-05
1 | 14165187 | 2016-11-17 08:55 | 2016-11-17 11:39 | 164 | 9 | 1476 | 0.004429 | 0.004347 | 2.7006e-05 | NAPA ID:24783 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 024783 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 200688 | NONE | Replace Poles, hardware and conductors. Armstrong Road - Waipuna - Bethlehem. W/O 30019163. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.0021735 | 5.5 | 2017 | 2016-11-17 | B | 9 | 0.004347 | 2.7006e-05
1 | 14165502 | 2016-11-16 09:01 | 2016-11-16 16:00 | 419 | 13 | 5447 | 0.016345 | 0.016227 | 3.9009e-05 | NAPA ID:24319 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 024319 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole R13108 | NONE | TO REPLACE XARMS HARDWARE & STAYS AT VARIOUS SITES BETWEEN POLES R13116 & R12888 PENINSULA RD ONEMANA. 162D to 162F Whitipirorua Road (Peninsula Road) - Opourere - Waikino. W/O 30002261. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.0081135 | 5.5 | 2017 | 2016-11-16 | B | 13 | 0.016227 | 3.9009e-05
1 | 14178722 | 2016-11-17 09:55 | 2016-11-17 15:17 | 322 | 5 | 1610 | 0.0048311 | 0.004786 | 1.5003e-05 | NAPA ID:24693 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 024693 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 212236 | NONE | Pole and Hardware replacement. Serrona Park Drive (Private Road Off Omanawa), Keenan Road, Taruranga. W/O 30002588. | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002393 | 5.5 | 2017 | 2016-11-17 | B | 5 | 0.004786 | 1.5003e-05
1 | 14179792 | 2016-11-01 12:15 | 2016-11-01 18:00 | 344 | 11 | 3761.3333 | 0.011289 | 0.011189 | 3.3014e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD3-304 | CABLE - REPAIR | HV Cable Fault past fuses 13010/4. Marc Askin has located. Is going to advise Murray Lipinksi of this as Marc believes cable is going to need to be replaced and re-routed due to property development in this area. Have emailed Murray Lipinksi to advise him of this from NOC. DNO No. 161101 Generators have been applied to Transformers TD3-177 & TD3-304. Times for Power Restored to these transformers: TD3-304: 17:30 TD3-177: 18:00 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.011189 | 11 | 2017 | 2016-11-01 | C | 11 | 0.011189 | 3.3014e-05
1 | 14179931 | 2016-11-18 11:27 | 2016-11-18 15:56 | 269 | 7 | 1883 | 0.0056502 | 0.005587 | 2.1004e-05 | NAPA ID:24685 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | 024685 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE7-026 | NONE | REPLACE SWITCH AND POLE SE7-026. INSTALL / REMOVE LL GAP. Works location: Hwy 2, Te Puke. WO 30027178 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.0027935 | 5.5 | 2017 | 2016-11-18 | B | 7 | 0.005587 | 2.1004e-05
1 | 14180000 | 2016-11-01 20:31 | 2016-11-02 00:31 | 239 | 92 | 749.45 | 0.0022493 | 0.00142 | 0.00027612 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810797 | POLE | at 18:40, Tuhitarata Sub, 33kV CB C932. Faultman was dispatched to broken pole. Found to be 33kV/11kV Pole 810797. Tuhitarata Sub Backfed and 33kV Isolated at ABS S749 & S568. 11kV Isolated at Fuses 7352 - OFF at 21:34 ON at 00:29. Permit issued and repairs carried out. All Power Restored on Completion. Adam Whale Attended. Materials: 1x Pole, 2x Crossarms, 6x Insulators & Binders. Adam advised that he had planned a job for this pole to be replaced in November, however, job was pushed out until December due to SAIDI. This was also a red tag pole. Pole was rotten and had snapped - only thing holding pole up was the O/H Lines. There was no mention in the NAPA application that this was a red tag pole and usual process is for work to be approved by works managers as part of SAIDI management. Please arrange for this pole be attended today by a fault person as it is very low to the ground it may need to be held with a crane truck possibly ? Martinborough Pirinoa Rd , approx. 5 km before Tuhitarata substation heading out of Martinborough. 02.11.2016: This pole was only red tagged this week as part of checks. This was after the application had come in. | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.00142 | 11 | 2017 | 2016-11-01 | C | 92 | 0.00142 | 0.00027612
1 | 14180011 | 2016-11-01 18:09 | 2016-11-01 19:00 | 51 | 2 | 102 | 0.00030613 | 0.000288 | 6.0025e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/432 | JUMPER | Faultman found broken jumper at transformer T1/432 line was isolated at Fuses B62 to repair ther jumper. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000288 | 11 | 2017 | 2016-11-01 | C | 2 | 0.000288 | 6.0025e-06
1 | 14180872 | 2016-11-01 21:22 | 2016-11-01 22:46 | 84 | 9 | 757.5 | 0.0022735 | 0.002192 | 2.7012e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819797 | FUSE - ELEMENT/LINK (HV) | Lucas Grant Attended. Reloaded Relivened 2x 10A HV Fuses at 7609. Unknown Cause. All OK. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.002192 | 11 | 2017 | 2016-11-01 | C | 9 | 0.002192 | 2.7012e-05
1 | 14181699 | 2016-11-02 06:54 | 2016-11-02 07:45 | 51 | 283 | 14447.15 | 0.043359 | 0.040811 | 0.00084935 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 263567 | POLE | Car vs pole. Using nearest pole in relation to location. Gareth - Police comms 09 571 2800. #P027256142 33/11 ( POA 9 Rec RC33 offloaded as a precaution Pole 263567 assessed ( Steve McKinney ) will need replacement in near future 33/11 relivened NDR No 55104 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.040811 | 11 | 2017 | 2016-11-02 | C | 283 | 0.040811 | 0.00084935
1 | 14184175 | 2016-11-02 09:30 | 2016-11-02 11:55 | 144 | 1 | 144.35 | 0.00043323 | 0.000424 | 3.0012e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 849434 | FUSE - ELEMENT/LINK (HV) | 2x 6amp duck @2972 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000424 | 11 | 2017 | 2016-11-02 | C | 1 | 0.000424 | 3.0012e-06
1 | 14184190 | 2016-11-16 08:30 | 2016-11-16 16:32 | 482 | 238 | 113644 | 0.34101 | 0.33887 | 0.00071417 | NAPA ID:24570 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 024570 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 248298 | NONE | RE POLE AND RECON 11KV FEEDER. Works location: Papamoa Beach Rd. WO 30019236 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.16943 | 5.5 | 2017 | 2016-11-16 | B | 238 | 0.33887 | 0.00071417
1 | 14184269 | 2016-11-02 13:10 | 2016-11-02 14:49 | 99 | 1 | 99 | 0.00029712 | 0.000288 | 3.0012e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7/600 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Part power - FM went out yesterday and found internal fault and replaced fuse and holder. Electrician has been out and stated 260 volts coming into house, network fault. 2 R replacing TX as voltage reading are 260 volts and phil can not get the lid of the TX to tap down as pouring with rain. will work through contol for HV permit (only 1 customer affected) power will be off for appox 1 1/2 hours Tranformer T7/66 was isolated at the transformer 11KV Fuses and was replaced. | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000288 | 11 | 2017 | 2016-11-02 | C | 1 | 0.000288 | 3.0012e-06
1 | 14185539 | 2016-11-04 09:00 | 2016-11-04 18:30 | 570 | 81 | 46170 | 0.13856 | 0.13783 | 0.00024309 | NAPA ID:26275 TP_WAIKINO GXP > TP_WAIKINO > WAIKINO312-PAEROA 33KV | 11 | Planned | 026275 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 263567 | NONE | Replace H Structure 263567/263564. Dual 33kV/11kV structure | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.068917 | 5.5 | 2017 | 2016-11-04 | B | 81 | 0.13783 | 0.00024309
1 | 14186507 | 2016-11-18 07:00 | 2016-11-18 17:08 | 607 | 167 | 87502.4333 | 0.26256 | 0.26106 | 0.0010022 | NAPA ID:26223 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > MOUNT | 11 | Planned | 026223 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD5-145 | NONE | Replace cable between transformer TD5-145 and Fuse/Sw 9588-4. Temp cable break made at 11kV linkbox SD5-061. Generator will be connected to the LV bus at TD5-145 after LV has been removed from the Transformer bushings. Works location: Gloucester Rd. WO 30034942. Additional switching due to reverse phasing on transformer TD5-145. | F2 | MOUNT | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.13053 | 5.5 | 2017 | 2016-11-18 | B | 167 | 0.26106 | 0.0010022
1 | 14187059 | 2016-11-03 06:03 | 2016-11-03 07:12 | 68 | 4 | 275.7333 | 0.00082753 | 0.000791 | 1.2005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220489 | FUSE - ELEMENT/LINK (HV) | 2x6amp bird @ sd5-086 712 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000791 | 11 | 2017 | 2016-11-03 | C | 4 | 0.000791 | 1.2005e-05
1 | 14187897 | 2016-11-03 12:30 | 2016-11-03 15:35 | 185 | 1 | 185 | 0.00055522 | 0.000546 | 3.0012e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715505 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Rreplaced transformer T1310 Customer has electric fence wire attached to HV poles and has been nadvised by the faultman to remove it as a serious safety issue | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000546 | 11 | 2017 | 2016-11-03 | C | 1 | 0.000546 | 3.0012e-06
1 | 14188068 | 2016-11-18 09:55 | 2016-11-18 15:29 | 334 | 5 | 1670 | 0.005011 | 0.004966 | 1.5003e-05 | NAPA ID:24748 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 024748 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP664 | NONE | Pole and Hardware replacement (2nd shut). Works location: Serrona Park Dr. WO 30002588 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002483 | 5.5 | 2017 | 2016-11-18 | B | 5 | 0.004966 | 1.5003e-05
1 | 14188351 | 2016-11-22 09:05 | 2016-11-22 15:45 | 400 | 5 | 2000 | 0.0060009 | 0.005955 | 1.5002e-05 | NAPA ID:24754 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 024754 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP664 | NONE | Pole and Hardware replacement (3rd shut). Works location: Serrona Park Dr. WO 30002588 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0029775 | 5.5 | 2017 | 2016-11-22 | B | 5 | 0.005955 | 1.5002e-05
1 | 14189912 | 2016-11-22 08:30 | 2016-11-22 15:47 | 437 | 30 | 13110 | 0.039336 | 0.039065 | 9.0013e-05 | NAPA ID:23553 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 023553 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 814557 | NONE | replace defective poles 814556 and 814557. Works location: Hardie Grove, Featherston. WO 30030519 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.019533 | 5.5 | 2017 | 2016-11-22 | B | 30 | 0.039065 | 9.0013e-05
1 | 14190516 | 2016-11-03 15:16 | 2016-11-03 16:02 | 46 | 22 | 1012 | 0.0030372 | 0.002839 | 6.6027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T33 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Refer to Planned OMS 14023434 / NAPA 24418. Fuses T33 were being reloaded when one DDO broke. An outage was then required where all 3 Fuse and Fuse Carriers were replaced.(Isolation required between ABS T35 and 10272 with backfeed at ABS V19). Relivened OK. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002839 | 11 | 2017 | 2016-11-03 | C | 22 | 0.002839 | 6.6027e-05
1 | 14191227 | 2016-11-03 20:05 | 2016-11-03 21:54 | 108 | 1 | 108.7 | 0.00032623 | 0.000317 | 3.0012e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc4021 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 3amp HT fuses at FC4021 & barrels | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000317 | 11 | 2017 | 2016-11-03 | C | 1 | 0.000317 | 3.0012e-06
1 | 14192497 | 2016-11-04 11:09 | 2016-11-04 14:28 | 199 | 2 | 398.2667 | 0.0011953 | 0.001177 | 6.0023e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719340 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 11:07 Chris reported that the transformer K1025 is blown. Chris reported that it only feed 1 house and that house is empty. 2R request for crew to replace transformer due to faulty TX full power restored to the network all tests completed | F4 | KAPUNI | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.001177 | 11 | 2017 | 2016-11-04 | C | 2 | 0.001177 | 6.0023e-06
1 | 14192923 | 2016-11-22 09:25 | 2016-11-22 14:10 | 285 | 25 | 7125 | 0.021378 | 0.021153 | 7.5011e-05 | NAPA ID:25502 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 025502 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace XARMS and Hardware | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.010577 | 5.5 | 2017 | 2016-11-22 | B | 25 | 0.021153 | 7.5011e-05
1 | 14193462 | 2016-11-04 14:27 | 2016-11-04 15:40 | 73 | 1 | 73.25 | 0.00021984 | 0.00021 | 3.0011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 742427 | FUSE - ELEMENT/LINK (HV) | fuses at out at the entry to farm at cow shed at 89 BERTRAND ROAD (as advised by cusotmer) Retailer put job through on incorret ICP Customer waiting to milk. - Advised shannon atSMC of correct address. Reload at fuses 8463 2 x 3A Bird Strike Jo - Can't make Outage job as no ICP's associated with fuses 8463 at the moment. Ta - mjk | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.00021 | 11 | 2017 | 2016-11-04 | C | 1 | 0.00021 | 3.0011e-06
1 | 14193483 | 2016-11-04 15:39 | 2016-11-04 16:42 | 62 | 29 | 1813.95 | 0.005444 | 0.005182 | 8.7034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 228034 | FUSE - ELEMENT/LINK (HV) | Please check OMS 14193513 - 329 Kaituna Road, Te Puke 2 fuses blown at SP012. line patrolled. tree throught the lines at pole 228034. Tree cut using hotstick cleared from the lines. Succssfully relivened. NDR to follow | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.005182 | 11 | 2017 | 2016-11-04 | C | 29 | 0.005182 | 8.7034e-05
1 | 14193507 | 2016-11-23 15:00 | 2016-11-23 17:32 | 152 | 5 | 760 | 0.0022803 | 0.002235 | 1.5002e-05 | NAPA ID:24772 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 024772 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212251 | NONE | Tap-up and liven new section of 11kV line at pole 212251 (Transformer TF3-031). (Omanawa and Belk Road South NEW Connection). Works location: Serrona Park Dr. WO 30002588 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0011175 | 5.5 | 2017 | 2016-11-23 | B | 5 | 0.002235 | 1.5002e-05
1 | 14198628 | 2016-11-24 08:30 | 2016-11-24 15:55 | 445 | 31 | 13795 | 0.04139 | 0.04111 | 9.3011e-05 | NAPA ID:23556 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 023556 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 814508 | NONE | replace defective poles between 814508 and 814516. Works location: Wooward St, Featherston. WO 30030519 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.020555 | 5.5 | 2017 | 2016-11-24 | B | 31 | 0.04111 | 9.3011e-05
1 | 14198773 | 2016-11-04 15:51 | 2016-11-04 21:30 | 338 | 1 | 338.5667 | 0.0010161 | 0.001007 | 3.0011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N13462 | JOINT - CABLE JOINT | reterminate 11kV cable termination at fuses FP211 Isolation at Fuses FP211 ( spur no back feeds ) Cable repair completed all service restored. Burnt Lug Material 1 x H/V Lug | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001007 | 11 | 2017 | 2016-11-04 | C | 1 | 0.001007 | 3.0011e-06
1 | 14199091 | 2016-11-04 18:47 | 2016-11-04 23:28 | 280 | 918 | 128283.6167 | 0.385 | 0.37673 | 0.0027551 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 231843 | POLE | Car vs Pole 321843 at 236 Kaitemako Road, Welcome Bay F2180967 WBY 4 tripped, L/O ( no flags ) report of car v pole. Isolations between ABS's SD4 349, SD4 348 & IP162 with back feeds via ABS's IP 35 & SD4 075. Pole replaced all service restored NDR No to follow Materials 1 x pole, 1 x double x arm complete | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.37673 | 11 | 2017 | 2016-11-04 | C | 918 | 0.37673 | 0.0027551
1 | 14201235 | 2016-11-05 06:44 | 2016-11-05 08:55 | 131 | 107 | 121.7333 | 0.00036534 | 0 | 3.0011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2630 | FUSE - ELEMENT/LINK (HV) | 1 x A/R on recloser 2680. A,B & C Ph O/C flags. 1 r issued for line patrol 2 x 6 amp fuses replaced at fuses 2630. Bird strike. Would have been cause of A/R Link OMS 14201362 | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-05 | C | 107 | 0 | 3.0011e-06
1 | 14213524 | 2016-11-05 12:53 | 2016-11-05 18:52 | 359 | 91 | 13466.7667 | 0.040415 | 0.039596 | 0.0002731 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 844929 | CONDUCTOR - REPAIR/REHANG | Recloser 693/2 tripped to L/O. E/F & O/C flags. Tree has fallen on lines Mangawhio Road just off Omata road and Lakes road - Have advised Control Customer: Jason, 0274218797 advised of hazards Tree confirmed through line at pole 844929. (Caused by customer felling trees near lines - No CACL held) Line isolated at fuses 874 for repairs. Remainder of feeder restored. All supply restored following repairs. Downer still to provide NDR. Safety manager entry required when it is? 20 metres of conductor and 2 joint sleeves materials used.. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.039596 | 11 | 2017 | 2016-11-05 | C | 91 | 0.039596 | 0.0002731
1 | 14218965 | 2016-11-05 17:58 | 2016-11-05 18:56 | 58 | 37 | 2149.0833 | 0.0064497 | 0.006116 | 0.00011104 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6082 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses found tripped at 6082. Patrolled, nothing found. Reloaded OK. Suspect Bird. (Rating 15A) | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.006116 | 11 | 2017 | 2016-11-05 | C | 37 | 0.006116 | 0.00011104
1 | 14220063 | 2016-11-06 07:16 | 2016-11-06 09:44 | 147 | 424 | 37254.4333 | 0.1118 | 0.10799 | 0.0012725 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | C2070 | NONE | at 07:15, Farmer Rd Sub, CB 6 Tatuanui Feeder, Tripped, A B C Fault, E/F, L/O. Faultmen dispatched & investigation began. Feeder Patrolled & Sectionalised. During Sectionalising Found Dead Bird on lines at Pole C2070 (Transformer TP2136). Faultman removed with hot stick and remainder of feeder relivened. All Power Restored on Completion. Sean Molloy Attended. Also Note: ABS IC633 was found to be seized shut during sectionalising - faultman could not open. DNO 161103 | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.10799 | 11 | 2017 | 2016-11-06 | C | 424 | 0.10799 | 0.0012725
1 | 14221639 | 2016-11-06 08:42 | 2016-11-06 12:47 | 245 | 54 | 4639.1167 | 0.013922 | 0.013436 | 0.00016206 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 795885 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Burnt jumper located on pole 795885. Line isolated at ABS 664 & 1217 for repairs. All 3 DDO fuse bases to fuses 683 also replaced due to deterioration. All supply restored on completion | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.013436 | 11 | 2017 | 2016-11-06 | C | 54 | 0.013436 | 0.00016206
1 | 14221695 | 2016-11-06 11:31 | 2016-11-06 13:14 | 102 | 1 | 102.55 | 0.00030776 | 0.000298 | 3.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | R0994 | FUSE - ELEMENT/LINK (HV) | Customer John Shearer, 0273008087 reported he has brought down three lines in new subdivision with his tractor. Have advised customer of hazard process. Advised FM who was already onsite and had found the lines down. Have passed FM onto customer. Wayne Reloaded Relivened 2x 2A Fuses due to blowing when tractor hit lines at TC5330 Pole: R0994 Power has been restored. FM has made safe, cut back the 400v lines and advised lines will need to be repaired under NDR: TBA. This is a new sub division and FM advised another pole may need to be installed to ensure lines are high enough as new houses will be built. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000298 | 11 | 2017 | 2016-11-06 | C | 1 | 0.000298 | 3.001e-06
1 | 14222002 | 2016-11-06 13:41 | 2016-11-06 17:15 | 214 | 4 | 856.9333 | 0.0025717 | 0.002535 | 1.2004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12922 | JUMPER | at 16:00 Kerepehi Sub, CB 6 Ngatea. Faultman dispatched to No Power. Found 2x Blown Fuses and Broken Jumper at Transformer Pole TC4573. Isolated Lines at Fuses FC4003. Permit issued & repairs carried out. All Power Restored on Completion. Replaced 2x 6A HV Fuses at Transformer TC4573 & Replaced 1x Jumper at TC4573. Pieter Diedericks Attended. Check OMS: 14222117 - 278 BUSH ROAD Switching sheet has been checked for KPI purposes and restoration confirmed as 06/11/2016 17:15. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002535 | 11 | 2017 | 2016-11-06 | C | 4 | 0.002535 | 1.2004e-05
1 | 14263710 | 2016-11-06 18:08 | 2016-11-06 20:58 | 170 | 179 | 15597.6667 | 0.04681 | 0.045198 | 0.0005372 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2032 | UNKNOWN | Recloser 2032 tripped to L/O. E/F flag. Feeder sectionalised / patrolled but nothing found. All restored OK. (Part of this feeder backfeeding Roberts CB6 due to Roberts Sub outage). | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.045198 | 11 | 2017 | 2016-11-06 | C | 179 | 0.045198 | 0.0005372
1 | 14288901 | 2016-11-06 19:48 | 2016-11-06 20:59 | 71 | 3 | 214.1 | 0.00064253 | 0.000615 | 9.0032e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E12653 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace transformer on 7/11. Generator supplied to houses. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000615 | 11 | 2017 | 2016-11-06 | C | 3 | 0.000615 | 9.0032e-06
1 | 14289039 | 2016-11-06 23:14 | 2016-11-07 06:53 | 458 | 69 | 14835.3833 | 0.044522 | 0.043901 | 0.00020708 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 222824 | POLE | CB 4 Trip a O/C, E/F Ground, Neutral O/C Car verus pole at 581 Jellico street Te Puke. Reported by Police P02737533. Transformer TE5-071 damaged as well as the 11kV cable feeding this transformer. Pole replaced HV relivened, Generators installed, Transformer replaced in the morning. replace pole, crossarms complete NDR to follow NOTES: Wayne N called to advise that tx TE5-071 was destoyed and needs to be replaced. They have installed 2x Generators to keep businesses going. 1 property at Collins Lane is still isolated as they suspect there may have been a line clash HV onto LV. Tx need to be built and will possibly be replaced within the next day or so. | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.043901 | 11 | 2017 | 2016-11-06 | C | 69 | 0.043901 | 0.00020708
1 | 14290263 | 2016-11-07 03:57 | 2016-11-07 08:06 | 249 | 1111 | 52106.8 | 0.15638 | 0.14637 | 0.0034242 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | R0695 | CONDUCTOR - REPAIR/REHANG | CB 7 Trip. B & C O/C. Pole R0695 branch on line removed by hot stick | F3 | OTAHU RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.14637 | 11 | 2017 | 2016-11-07 | C | 1111 | 0.14637 | 0.0034242
1 | 14291601 | 2016-11-07 06:15 | 2016-11-07 17:20 | 665 | 637 | 413557.4 | 1.2411 | 1.2354 | 0.0019117 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | R0739 | POLE | at 06:15, Whangamata Sub, CB 3 Opoutere Feeder, CB 9637/3 Tripped, O/C, L/O. Faultmen dispatched & investigation began. Sectionalising began. While sectionalising, found tree on line that had also broken Pole R0739. Isolated Lines at ABS 2576, 254, 2122 & Links IP161. No backfeeds available. Permit issued & repairs carried out. All Power Restored on Completion. Pieter Diedericks Attended. Materials Used: 1x Pole, 2x Crossarms, 6x Insulators 6x Binders 1x Possum Guard, 1x Concrete Donut, 1x Breast Block. NDR: 54502 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 1.2354 | 11 | 2017 | 2016-11-07 | C | 637 | 1.2354 | 0.0019117
1 | 14295281 | 2016-11-07 07:17 | 2016-11-07 10:04 | 167 | 195 | 17353 | 0.052077 | 0.050321 | 0.00058521 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 205740 | CONDUCTOR - REPAIR/REHANG | at 07:16, Aongatete Sub, CB 3 Apata Feeder, Tripped, B+C O/C, L/O. Faultmen dispatched & investigation began. report of lines down on Turntable road. Found tree branch on lines at Pole 205715 - faultman removed this with hotstick. Lines confirmed down caused by trees falling on lines on turntable road at Pole 205740. Isolated at Fuses SC2-117. Remainder of feeder relivened. Permit issued & repairs carried out. All Power Restored on Completion. Less than 1 span not all phases of conductor replaced. Mike James attended. NDR: N400229 90 Turntable hill Road, Apata - trees have brought down lines and trees across the road. - 7.44am advised David control about job Mark Bradley 027 2444 386 - advised hazard process | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.050321 | 11 | 2017 | 2016-11-07 | C | 195 | 0.050321 | 0.00058521
1 | 14296010 | 2016-11-07 07:22 | 2016-11-07 12:45 | 323 | 300 | 65578.9 | 0.19681 | 0.1941 | 0.00090032 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 204066 | CONDUCTOR - REPAIR/REHANG | at 07:02, Kauri Point Sub, CB 1 Lindemann Rd Feeder, Tripped, O/C, Auto Reclosed. OCT Team advised of lines down on KPT CB 1 near Transformer TB2-005. Duty NC dropped part of feeder to de-energise supply near faulted area: Opened Sw/gear 13021/4 at 07:22. Faultmen dispatched & investigation began. Found multiple lines down at Poles 204066, 204047 & 204072 caused by tree branches falling on lines - believe some of the high fault current may have caused other lines to come down. Backfeed supplied from KPT 2: Opened IP415, Closed SA2-052 at 08:56. Carried out repairs in 2 parts. Part 1: Isolated lines at ABS SB2-010 & ABS IP414. Permit issued and repairs carried out. All Power Restored up to ABS IP414 on completion. Part 2: Isolated Lines at ABS IP414 & IP415. Permit issued & repairs carried out. All Power Restored on Completion. Shay Deegan Attended. NDR No. TBA. Materials Used: More than 1 span all 3 phases - conductor links - unsure of how many Powerline has snapped and is lying on top of shelter belt next to kauri point pack house 7.12am advised shannon at svs hub & advised control 7.18am advised Fire Service ETA 35mins 7.27am. advised Shannon at svs hub outage extent has changed to Mainline | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.1941 | 11 | 2017 | 2016-11-07 | C | 300 | 0.1941 | 0.00090032
1 | 14297383 | 2016-11-23 09:01 | 2016-11-23 15:49 | 408 | 304 | 124158.6667 | 0.37253 | 0.36979 | 0.00091212 | NAPA ID:24863 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024863 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD2-026 | NONE | Replace poles,hardware & conductor. Remove line fuses SD2-009 and replace with ABS IP667. Works location: Ross & Whakamarama Roads. WO 30017822 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.1849 | 5.5 | 2017 | 2016-11-23 | B | 304 | 0.36979 | 0.00091212
1 | 14297398 | 2016-11-07 08:03 | 2016-11-07 09:59 | 116 | 71 | 8236 | 0.024717 | 0.024077 | 0.00021307 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213162 | FUSE - ELEMENT/LINK (HV) | Fuses SD3-147 replaced 2 x 15amp fuses. Please check if OMS 14297387 is related part power 655 Minden Road & 14297471. Advised Shannon to ask FM to check fuses SD3-147. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.024077 | 11 | 2017 | 2016-11-07 | C | 71 | 0.024077 | 0.00021307
1 | 14297477 | 2016-11-07 09:50 | 2016-11-07 11:56 | 126 | 8 | 1008 | 0.0030251 | 0.002953 | 2.4008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 230102 | CONDUCTOR - REPAIR/REHANG | at 09:50, Paengaroa Sub, CB 7 Maungarangi Rd Feeder. Faultman dispatched to no power. Found lines down caused by trees at Pole 230102. Isolated lines at fuses SF6-008. Permit issued & Repairs carried out. All Power Restored on Completion. Clint Johnstone Attended. Replaced 1 span of conductor all phases (2 phase line). NDR# TBA | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.002953 | 11 | 2017 | 2016-11-07 | C | 8 | 0.002953 | 2.4008e-05
1 | 14297784 | 2016-11-25 08:58 | 2016-11-25 15:29 | 391 | 110 | 43010 | 0.12904 | 0.12805 | 0.00033003 | NAPA ID:24886 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024886 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP667 | NONE | Replace poles,hardware & conductor. Works location: Ross Rd, Whakamarama. WO 30017822 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.064027 | 5.5 | 2017 | 2016-11-25 | B | 110 | 0.12805 | 0.00033003
1 | 14297887 | 2016-11-29 09:00 | 2016-11-29 15:25 | 385 | 110 | 42350 | 0.12706 | 0.12607 | 0.00033002 | NAPA ID:24888 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024888 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 209989 | NONE | Replace poles,hardware & conductor. Install TEMP66 EDO's on pole 209989. Works location: Ross Rd, Whakamarama. WO 30017822 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.063033 | 5.5 | 2017 | 2016-11-29 | B | 110 | 0.12607 | 0.00033002
1 | 14297991 | 2016-11-22 08:34 | 2016-11-22 18:13 | 579 | 189 | 109431 | 0.32834 | 0.32664 | 0.00056708 | NAPA ID:24706 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024706 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 395594 | NONE | Install temporary ABS TEMP95 to pole 395594. Install temporary ABS TEMP96 to pole 268712. Install temporary ABS TEMP97 to pole 268702. Install temporary ABS TEMP98 to pole 381405. Works location: Wainui South Rd. WO 30019861 ASW to follow up on reasons for the late running of outage. Shut ran over time by five hours with power finally restored at 1935hrs. NCTL requested onsite Downer switcher to make observations and feed back to NOC in writing of why shut ran long. Email received, safety manager to be done | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.16332 | 5.5 | 2017 | 2016-11-22 | B | 189 | 0.32664 | 0.00056708
1 | 14298163 | 2016-11-07 09:14 | 2016-11-07 11:50 | 155 | 6 | 935.4 | 0.0028072 | 0.002753 | 1.8006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 778978 | CROSSARM - WHOLE ASSEMBLY | Faultman alerted to a damaged crossarm by local farmer. Outage required past Fuses 2699 to replace 1 x crossarm & 3 x HV Fuses. Fuses have cracked and burnt through the crossarm. No backfeeds available Isolation via Fuses 2699. Materials used: 2x 11kV Arms, 3x Polymers, 3x Dead Enda, 3x Pin & Insulators, 3x HV Fuses complete | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.002753 | 11 | 2017 | 2016-11-07 | C | 6 | 0.002753 | 1.8006e-05
1 | 14300083 | 2016-11-07 10:24 | 2016-11-07 14:10 | 226 | 45 | 10170 | 0.030521 | 0.030115 | 0.00013505 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 205783 | CONDUCTOR - REPAIR/REHANG | at 10:24, Aongatete Sub, CB 3 Apata Feeder. Fautlmen were returning from previous fault and noticed fuses blown at SC2-017. Faultman drove down road to do quick investigation and found lines down at Pole 205783 caused by trees coming through lines. Isolated Lines at Fuses SC2-017. Permit issued & repairs carried out. All Power Restored on Completion. Here Hiha Attended. Materials. More than 1 span of conductor all 3 phases, 8x jumpers & 18x Conductor links. NDR 51652 10.27am advised Shannon at svs hub | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.030115 | 11 | 2017 | 2016-11-07 | C | 45 | 0.030115 | 0.00013505
1 | 14301708 | 2016-11-24 09:15 | 2016-11-24 15:25 | 370 | 2 | 740 | 0.0022203 | 0.002202 | 6.0007e-06 | NAPA ID:25813 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 025813 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP103 | NONE | Reconductor OH Lines and change pole and Xarms. Works location: Manaia Rd, Coromandel. WO 30016096 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.001101 | 5.5 | 2017 | 2016-11-24 | B | 2 | 0.002202 | 6.0007e-06
1 | 14302035 | 2016-11-24 08:55 | 2016-11-24 14:58 | 363 | 16 | 5808 | 0.017426 | 0.017282 | 4.8006e-05 | NAPA ID:25434 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 025434 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC517 | NONE | Upgrade TC517 at Pole O13548. Extend conductor from Pole O2258 to O2262 and install / liven new P/M Transformer TP3031 at O2262. Works location: Wani Rd, Paeroa. WO 30032230 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.008641 | 5.5 | 2017 | 2016-11-24 | B | 16 | 0.017282 | 4.8006e-05
1 | 14302393 | 2016-11-07 16:37 | 2016-11-07 17:55 | 78 | 1 | 78.1167 | 0.00023443 | 0.000225 | 3.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2640 | FUSE - ELEMENT/LINK (HV) | Check 500 Brunswick Road, OMS 14302464 is related. Attn Super user. Cant close off job. Jump to map not working so can't offline transformer. Replaced 4 x 2 Amp fuse links as one broke when closing in. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000225 | 11 | 2017 | 2016-11-07 | C | 1 | 0.000225 | 3.001e-06
1 | 14302443 | 2016-11-07 16:47 | 2016-11-07 18:05 | 78 | 1 | 78.4333 | 0.00023538 | 0.000226 | 3.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2670 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2Amp HV Links | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000226 | 11 | 2017 | 2016-11-07 | C | 1 | 0.000226 | 3.001e-06
1 | 14302492 | 2016-11-07 17:01 | 2016-11-07 18:00 | 58 | 3 | 175.75 | 0.00052744 | 0.0005 | 9.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2724 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 15Amp HV Links Attn Superuser. Cant close off. Jump to map not working | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0005 | 11 | 2017 | 2016-11-07 | C | 3 | 0.0005 | 9.0031e-06
1 | 14302545 | 2016-11-07 17:09 | 2016-11-07 20:09 | 180 | 4 | 720 | 0.0021608 | 0.002124 | 1.2004e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13469 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Blown Transformer Due to Lightning. To Be Replaced 30kVA 3 Phase. Maurice Doig. Transformer replaced by Les Edwards. Voltages R236, W235, B236 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.002124 | 11 | 2017 | 2016-11-07 | C | 4 | 0.002124 | 1.2004e-05
1 | 14302646 | 2016-11-07 20:15 | 2016-11-08 01:50 | 335 | 197 | 43884.7833 | 0.1317 | 0.12993 | 0.00059121 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 202316 | POLE | Pole replaced after car accident. Isolated at Links SC4-653. No back feeds available. NDR 56003 Materials, 11 concrete pole, set of DDO's, Crossarms, Insulators called and emailed hub re 999 ETA required for Police comms 5 mins - advised police comms passed through to control | F3 | BELLEVUE RD | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.12993 | 11 | 2017 | 2016-11-07 | C | 197 | 0.12993 | 0.00059121
1 | 14302882 | 2016-11-07 18:12 | 2016-11-07 19:26 | 73 | 1 | 73.7333 | 0.00022128 | 0.000212 | 3.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T4/336 | FUSE - ELEMENT/LINK (HV) | Fuses Found Blown At Transformer T4/336 - Cause Lightning Used 2 x 3 Amp Fuses | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000212 | 11 | 2017 | 2016-11-07 | C | 1 | 0.000212 | 3.001e-06
1 | 14302913 | 2016-11-07 17:12 | 2016-11-07 18:00 | 47 | 1 | 47.85 | 0.0001436 | 0.000134 | 3.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2618 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Fuses found Blown at Transformer X2618 - cause Lightning Used 3 x 6 amp fuses livened 18:00 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000134 | 11 | 2017 | 2016-11-07 | C | 1 | 0.000134 | 3.001e-06
1 | 14303619 | 2016-11-07 20:41 | 2016-11-07 23:50 | 189 | 3 | 567 | 0.0017016 | 0.001674 | 9.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716037 | JUMPER | Blown Jumper Found at Transformer T7155 Isolated at Fuses TA998 Used 1 x sleeve & 1 mtr of conductor | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001674 | 11 | 2017 | 2016-11-07 | C | 3 | 0.001674 | 9.0031e-06
1 | 14304294 | 2016-11-07 21:56 | 2016-11-07 23:07 | 71 | 91 | 4477.2 | 0.013436 | 0.012617 | 0.00018907 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 816760 | UNKNOWN | Recloser 8156 A/R B & C O/C Sectionalizer C637 Tripped. Sectionalizer C637 reclosed Sucessfully, Line patrolled Tripped due to weather, strong winds & heavy rain reported by F/M | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.012617 | 11 | 2017 | 2016-11-07 | C | 91 | 0.012617 | 0.00018907
1 | 14304604 | 2016-11-07 23:06 | 2016-11-08 02:22 | 195 | 10 | 1957.8333 | 0.0058756 | 0.005785 | 3.0011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771483 | FUSE - ELEMENT/LINK (HV) | 2x8amp fuses blown at 999 line patrolled reloaded & livened. Unknown cause. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.005785 | 11 | 2017 | 2016-11-07 | C | 10 | 0.005785 | 3.0011e-05
1 | 14304620 | 2016-11-08 01:23 | 2016-11-08 02:48 | 85 | 18 | 1530 | 0.0045916 | 0.004429 | 5.4018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 729739 | CONDUCTOR - REPAIR/REHANG | Lines down found past Pole 729739 in 2 locations Isolated at Fuses WH277 Used 2 x sleeves 2 mtrs of conductor | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.004429 | 11 | 2017 | 2016-11-08 | C | 18 | 0.004429 | 5.4018e-05
1 | 14304629 | 2016-11-07 23:23 | 2016-11-08 08:31 | 547 | 627 | 97696.0667 | 0.29319 | 0.28755 | 0.0021578 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P12554 | CROSSARM - WHOLE ASSEMBLY | Parkville CB 2 Tripped B,C Ph O/C L/OBurnt Crossarm found at Pole P12554 Isolated at ABS U4 CB 1 Tripped on install backfeed from Parkville CB1 (Hukanui) via ABS S12, ABS S12 opened and power restored to CB 1 Insulator replaced at Pole P12554, Branch found in lines over river Isolated at ABS's U4 & U5 Faultman to sort out entry to lines in day light | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.28755 | 11 | 2017 | 2016-11-07 | C | 627 | 0.28755 | 0.0021578
1 | 14305737 | 2016-11-08 00:13 | 2016-11-08 11:51 | 698 | 181 | 19071.9 | 0.057235 | 0.055605 | 0.00054318 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P26154 | CONDUCTOR - REPAIR/REHANG | Faultman found line arcing and branches in lines on way to another fault, Isolated at ABS's S27, S26 & S24 Line left Isolated due to further lines down found Tree branches had come down contacting lines & damaging pole. Temp repairs made to Pole and trees cleared away enough to reliven HV. Wooden pole to be defected by faultman and treescape will need to attend to remove trees. Materials used: 2x Arm Braces, Misc Bolts, 1mtr of No.8 wire & 2x No.8 sleeves NDR# 35340 | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.055605 | 11 | 2017 | 2016-11-08 | C | 181 | 0.055605 | 0.00054318
1 | 14306415 | 2016-11-08 01:11 | 2016-11-08 03:11 | 120 | 258 | 5851.6833 | 0.017561 | 0.015238 | 0.00014705 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9787 | UNKNOWN | Line Patrolled Sectiionaliser 9787 closed. no fault found | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.015238 | 11 | 2017 | 2016-11-08 | C | 258 | 0.015238 | 0.00014705
1 | 14307995 | 2016-11-08 03:08 | 2016-11-08 04:23 | 75 | 1 | 75.2833 | 0.00022593 | 0.000216 | 3.001e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761474 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer 2903T - Cause Lightning Used 2 x 3 amp fuses | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000216 | 6.6 | 2017 | 2016-11-08 | C | 1 | 0.000216 | 3.001e-06
1 | 14309166 | 2016-11-08 04:59 | 2016-11-08 05:54 | 54 | 497 | 26990.9167 | 0.081 | 0.076525 | 0.0014915 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207383 | POLE | Car Vs Pole reported by fire. Recloser 9225 NOC opened. Pole 207383 removed from Line by impact. Feeder relivened while pole is taken to site Replace pole, crossarm & hardware | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.076525 | 11 | 2017 | 2016-11-08 | C | 497 | 0.076525 | 0.0014915
1 | 14309675 | 2016-11-08 06:12 | 2016-11-08 08:28 | 136 | 1 | 136 | 0.00040814 | 0.000399 | 3.001e-06 |  | 0.41499999999999998 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 768058 | CONDUCTOR - REPAIR/REHANG | Please check 14310152 unable to inference because job verified Trees through lines at pole 768058. Repaired - Used 20 m Squirrel Conductor 6 Sleeves 3 x 2 Amp Fuses NDR 30480 | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000399 | 0.415 | 2017 | 2016-11-08 | C | 1 | 0.000399 | 3.001e-06
1 | 14309852 | 2016-11-08 07:37 | 2016-11-08 09:15 | 98 | 11 | 1078 | 0.0032351 | 0.003136 | 3.3011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 729995 | CONDUCTOR - REPAIR/REHANG | Tree Branch through lines at Pole 729995. Caused by Earthquake. Lines isolated at Fuses LI725 and tree removed. NDR N100242 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.003136 | 11 | 2017 | 2016-11-08 | C | 11 | 0.003136 | 3.3011e-05
1 | 14309889 | 2016-11-08 08:48 | 2016-11-08 11:56 | 188 | 52 | 3820 | 0.011464 | 0.010995 | 0.00015605 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208165 | JUMPER | Please check OMS 14313583 - 166 LUND ROAD OMS 14314152 - 280 LUND ROAD OMS 14314318 444 LUND ROAD Repair jumper at TC1-001 | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.010995 | 11 | 2017 | 2016-11-08 | C | 52 | 0.010995 | 0.00015605
1 | 14309924 | 2016-11-08 04:50 | 2016-11-08 10:08 | 318 | 33 | 10506.65 | 0.031531 | 0.031233 | 9.9034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 14309161 | INSULATOR | FM found floating HV conductor caused by wind. Isolated at Fuses E27. Repaired using 1 x 11kV Pin. 21/11/2016: Note the On Site Time was achieved at 08:17 as per ERoad data provided to the Powerco Performance Manager. Response Time has met the Priority 83 KPI for an F3/F4 Feeder. KPI = 90 minutes. Response made 73.24 minutes after Request. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.031233 | 11 | 2017 | 2016-11-08 | C | 33 | 0.031233 | 9.9034e-05
1 | 14310216 | 2016-11-08 07:43 | 2016-11-08 10:00 | 137 | 2 | 274 | 0.00082228 | 0.000804 | 6.002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | O13877 | FUSE - ELEMENT/LINK (HV) | Reolad at fuses FC4005 2 x 6A Fuses Cause Unknown | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000804 | 11 | 2017 | 2016-11-08 | C | 2 | 0.000804 | 6.002e-06
1 | 14310247 | 2016-11-08 07:52 | 2016-11-08 10:45 | 172 | 2 | 345.4667 | 0.0010368 | 0.001018 | 6.002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 805818 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses 2741 2 x 6A Weather | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.001018 | 11 | 2017 | 2016-11-08 | C | 2 | 0.001018 | 6.002e-06
1 | 14310409 | 2016-11-08 08:18 | 2016-11-08 13:01 | 282 | 59 | 16695.0333 | 0.050102 | 0.04957 | 0.00017706 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207383 | POLE |  | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.04957 | 11 | 2017 | 2016-11-08 | C | 59 | 0.04957 | 0.00017706
1 | 14314175 | 2016-11-08 10:54 | 2016-11-08 14:40 | 225 | 15 | 3385.75 | 0.010161 | 0.010025 | 4.5015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 396294 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.010025 | 11 | 2017 | 2016-11-08 | C | 15 | 0.010025 | 4.5015e-05
1 | 14314393 | 2016-11-08 10:53 | 2016-11-08 12:14 | 81 | 577 | 39042.4 | 0.11717 | 0.11197 | 0.0017316 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 249481 | UNKNOWN | CB 1304 tripped on PH A OC & E/F Patrolled no fault found - Suspect trees and high winds | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.11197 | 11 | 2017 | 2016-11-08 | C | 577 | 0.11197 | 0.0017316
1 | 14315136 | 2016-11-08 13:54 | 2016-11-08 19:06 | 312 | 9 | 2808 | 0.0084269 | 0.008345 | 2.7009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | K1754 | CONDUCTOR - REPAIR/REHANG | Please also check OMS 14315391 - 164 MAUKORO LANDING ROAD Customer has advised there are trees that have fallen down on this road, damaged power poles and lines. SMC has advised FM is aware of lines down and he has made safe to be able to attend 999 job Line isolated at fuses FP1320 to repair lines down at pole K1754. 40 metres of squirrel conductor, 3 x HV crossarms and assemblies, 10 metres of binder material required. All supply restored following repairs. NDR to be provided by Downer | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.008345 | 11 | 2017 | 2016-11-08 | C | 9 | 0.008345 | 2.7009e-05
1 | 14315565 | 2016-11-25 09:43 | 2016-11-25 12:03 | 140 | 16 | 2240 | 0.0067207 | 0.006576 | 4.8005e-05 | NAPA ID:24450 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | 024450 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS V85 | NONE | To change 11kv x ams install d/man stay and straigten pole. Works location: Route 52. WO 30029312 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.003288 | 5.5 | 2017 | 2016-11-25 | B | 16 | 0.006576 | 4.8005e-05
1 | 14315925 | 2016-11-08 12:59 | 2016-11-08 13:01 | 2 | 438 | 1007.4 | 0.0030232 | 0 | 0.0013144 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207383 | POLE |  | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-08 | C | 438 | 0 | 0.0013144
1 | 14340431 | 2016-11-08 14:31 | 2016-11-08 15:30 | 59 | 4 | 237.3333 | 0.00071224 | 0.000676 | 1.2004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 204597 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuses at TB1-013 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.000676 | 11 | 2017 | 2016-11-08 | C | 4 | 0.000676 | 1.2004e-05
1 | 14340792 | 2016-11-08 18:25 | 2016-11-08 18:51 | 25 | 320 | 8092.1333 | 0.024285 | 0.021403 | 0.00096033 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 216574 | JUMPER | Blown jumper located on pole 216574. Line isolated at ABS SE4-001 to repair jumper. All supply restored on completion of repairs. 2 x connectors only material required. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.021403 | 11 | 2017 | 2016-11-08 | C | 320 | 0.021403 | 0.00096033
1 | 14340848 | 2016-11-08 14:48 | 2016-11-08 15:52 | 63 | 928 | 59160 | 0.17754 | 0.16919 | 0.0027849 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | t1235 | NONE | CB 4 L/O on O/C Found branch on line on pole T1235. Removed branch and re-livened | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.16919 | 11 | 2017 | 2016-11-08 | C | 928 | 0.16919 | 0.0027849
1 | 14343270 | 2016-11-08 16:06 | 2016-11-08 16:24 | 18 | 7 | 126 | 0.00037813 | 0.000315 | 2.1007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | td4-155 | CONDUCTOR - REPAIR/REHANG | isolated to repair LT, Re-livened | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.000315 | 11 | 2017 | 2016-11-08 | C | 7 | 0.000315 | 2.1007e-05
1 | 14343313 | 2016-11-07 13:40 | 2016-11-07 16:15 | 155 | 2 | 310 | 0.00093033 | 0.000912 | 6.0021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc818 | CONDUCTOR - REPAIR/REHANG | Isolated transformer to repair lines down & install LV isolator. Own SIS & AP | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000912 | 11 | 2017 | 2016-11-07 | C | 2 | 0.000912 | 6.0021e-06
1 | 14344119 | 2016-11-08 17:39 | 2016-11-08 19:40 | 121 | 624 | 36987.0667 | 0.111 | 0.10538 | 0.0018726 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 209669 | CONDUCTOR - REPAIR/REHANG | CB 2 tripped to L/O. E/F & O/C flags. Line sectionalised & patrolled. Lines down reported on Old Highway at pole 209669. Caused by branch over line. Line isolated at ABS SD2-004 & SC2-024 for repairs. Remainder of supply restored. All other supply restored following repairs. 4 metres namu conductor & 2 joint sleeves material required. NDR to be forwarded by Downer. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.10538 | 11 | 2017 | 2016-11-08 | C | 624 | 0.10538 | 0.0018726
1 | 14348610 | 2016-11-08 23:17 | 2016-11-09 05:23 | 365 | 117 | 33250.8 | 0.099786 | 0.098732 | 0.00045015 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837612 | CONDUCTOR - REPAIR/REHANG | CB C936 tripped to L/O. O/C & E/F flags. 2 x 1 r requested Line sectionalised & patrolled. Lines down located at pole 837612. Tree through line. Isolation at ABS S92. All supply restored on completion of repairs. 50 metres mink conductor & 2 x mink joint sleeves material required. NDR 21958 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.098732 | 11 | 2017 | 2016-11-08 | C | 117 | 0.098732 | 0.00045015
1 | 14349894 | 2016-11-09 05:59 | 2016-11-09 07:30 | 91 | 1 | 91.0333 | 0.00027319 | 0.000264 | 3.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ic292 | FUSE - ELEMENT/LINK (HV) | Please Check OMS 14349911 - 110 FERGUS ROAD OMS 14349934 - 62 FERGUS ROAD Replaced 2 x 20amp HT fuses at IC292 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.000264 | 11 | 2017 | 2016-11-09 | C | 1 | 0.000264 | 3.0009e-06
1 | 14349923 | 2016-11-09 08:11 | 2016-11-09 10:55 | 163 | 74 | 4819.3 | 0.014463 | 0.013796 | 0.00022207 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1904 Parewanui Rd | CONDUCTOR - REPAIR/REHANG | Lines down to Cow Shed Brenda on Site 027 681 4197 Found that 1 Fuse at Fuses 2875 would not Open So had to go back to Fuse 4203 open Replace 1 X DDO at Fuses 2875 Then open Fuses 2875 to fix Problem Replaced 30m Conductor as old conductor is rotten James will defect this | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.013796 | 11 | 2017 | 2016-11-09 | C | 74 | 0.013796 | 0.00022207
1 | 14350106 | 2016-11-09 07:23 | 2016-11-09 09:55 | 151 | 5 | 758.9167 | 0.0022775 | 0.002232 | 1.5005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 443178 | FUSE - ELEMENT/LINK (HV) | Reload at fuss 7473 2 x 10A Fried Duck! | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002232 | 11 | 2017 | 2016-11-09 | C | 5 | 0.002232 | 1.5005e-05
1 | 14350169 | 2016-11-25 09:50 | 2016-11-25 13:38 | 228 | 5 | 1103 | 0.0033094 | 0.003264 | 1.5002e-05 | NAPA ID:24787 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV | 11 | Planned | 024787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF3-006 | NONE | Phase out 11kv between feeders and make connection. Works location: Belk Rd South. WO 30002588 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001632 | 5.5 | 2017 | 2016-11-25 | B | 5 | 0.003264 | 1.5002e-05
1 | 14350259 | 2016-11-09 08:06 | 2016-11-09 15:37 | 450 | 3 | 1352.3 | 0.0040582 | 0.004031 | 9.0029e-06 | uire | 11 | Unplanned |  | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TD3-077 | CABLE - REPAIR | Problem looks like it is with generators supplying power or the UG cable, electrical fitters required to come and check generator connections and also the generator Mark Askin and Wendel are onsite with generator rental services now and have found faulty generator feeding transformer TD3-177, generator is without power now so TX is without power, emergency outage put out to retailers. charges to go to Generator rental services if the generator is a fault on their side. Clint advised fuses keep tripping, will need to investigate further. Clint advised that he has located cables, tested cables and meggered cables, swapped one phase over to level out the load. Everything seems to be working ok and generator is not tripping anymore. Full power restored to everyone on generator. Related to OMS 14179792 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.004031 | 11 | 2017 | 2016-11-09 | C | 3 | 0.004031 | 9.0029e-06
1 | 14351068 | 2016-11-09 09:33 | 2016-11-09 10:31 | 58 | 298 | 16192 | 0.048592 | 0.045908 | 0.00089429 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201044 | JUMPER | Jumper repaired at Pole 201044 | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.045908 | 11 | 2017 | 2016-11-09 | C | 298 | 0.045908 | 0.00089429
1 | 14351546 | 2016-11-29 08:30 | 2016-11-29 15:30 | 420 | 3 | 1260 | 0.0037802 | 0.003753 | 9.0004e-06 | NAPA ID:24512 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 024512 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 839112 | NONE | Change arms at pole 839112 and poles from 839108 to 839116. Works location: Kaka Amu Rd. WO 30014082 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0018765 | 5.5 | 2017 | 2016-11-29 | B | 3 | 0.003753 | 9.0004e-06
1 | 14352368 | 2016-11-09 09:15 | 2016-11-09 14:41 | 326 | 67 | 21842 | 0.065547 | 0.064944 | 0.00020107 | NAPA ID:26413 TP_HUIRANGI GXP > INGLEWOOD SUB > RATA ST | 6.6 | Planned | 026413 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 707703 | POLE | to replace old hardwood pole. CREATED TO REWRITE SWITCHING DUE TO FIRST SWITCHING STARTED THE STOPPED DUE TO WEATHER. | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.032472 | 3.3 | 2017 | 2016-11-09 | B | 67 | 0.064944 | 0.00020107
1 | 14353291 | 2016-11-21 09:02 | 2016-11-21 15:34 | 392 | 38 | 14896 | 0.044695 | 0.044353 | 0.00011402 | NAPA ID:26454 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 026454 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 366649 | NONE | Change 10 x poles and 9 x xarms and install ABS TEMP 72 between pole 366649 & P06737 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.022176 | 5.5 | 2017 | 2016-11-21 | B | 38 | 0.044353 | 0.00011402
1 | 14353351 | 2016-12-05 10:15 | 2016-12-05 10:40 | 25 | 6 | 150 | 0.00044998 | 0.000395 | 1.7999e-05 | NAPA ID:26029 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026029 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2296 | NONE | To install a 400V Fuse/Disconnector on TC2296. Works location: Maungatautari Rd, TIrau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001975 | 5.5 | 2017 | 2016-12-05 | B | 6 | 0.000395 | 1.7999e-05
1 | 14353357 | 2016-12-05 12:30 | 2016-12-05 13:30 | 60 | 7 | 420 | 0.00126 | 0.001196 | 2.0999e-05 | NAPA ID:26032 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026032 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1625 | NONE | To install a 400V Fuse/Disconnector on TC1625. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000598 | 5.5 | 2017 | 2016-12-05 | B | 7 | 0.001196 | 2.0999e-05
1 | 14353367 | 2016-12-05 10:00 | 2016-12-05 14:26 | 266 | 1 | 266 | 0.00079797 | 0.000788 | 2.9998e-06 | NAPA ID:25972 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 025972 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5131 | NONE | Replace transformer TC5131 and replace the 11kV crossarms on transformer structure TC5131. Works location: Kereone Rd, Morrinsville. WO 30019176 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000394 | 5.5 | 2017 | 2016-12-05 | B | 1 | 0.000788 | 2.9998e-06
1 | 14354045 | 2016-12-05 14:00 | 2016-12-05 14:55 | 55 | 6 | 330 | 0.00098996 | 0.000935 | 1.7999e-05 | NAPA ID:26034 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026034 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC377 | NONE | To install a 400V Fuse Disconnector on TC377. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0004675 | 5.5 | 2017 | 2016-12-05 | B | 6 | 0.000935 | 1.7999e-05
1 | 14354063 | 2016-12-06 10:05 | 2016-12-06 10:25 | 20 | 9 | 180 | 0.00053997 | 0.000458 | 2.6998e-05 | NAPA ID:26044 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026044 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2158 | NONE | To install a 400V fuse/Disconnector on TC2158. Works location: Maungatautari Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000229 | 5.5 | 2017 | 2016-12-06 | B | 9 | 0.000458 | 2.6998e-05
1 | 14354088 | 2016-11-15 18:00 | 2016-11-15 18:52 | 52 | 2 | 104 | 0.00031208 | 0.000294 | 6.0014e-06 | NAPA ID:26466 TP_MASTERTON GXP > CLAREVILLE SUB > WYNDHAM ST | 11 | Planned | 026466 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7588 | NONE | Replace faulty drop outs 7588. Works location: Kent St, Carterton. WO 30032191 | F2 | WYNDHAM ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000147 | 5.5 | 2017 | 2016-11-15 | B | 2 | 0.000294 | 6.0014e-06
1 | 14354258 | 2016-12-06 12:00 | 2016-12-06 12:40 | 40 | 6 | 240 | 0.00071996 | 0.000665 | 1.7999e-05 | NAPA ID:26046 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026046 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4443 | NONE | To install a 400V Fuse Disconnector on TC4443. Works location: Mangatautari Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0003325 | 5.5 | 2017 | 2016-12-06 | B | 6 | 0.000665 | 1.7999e-05
1 | 14354280 | 2016-12-06 14:00 | 2016-12-06 14:45 | 45 | 4 | 180 | 0.00053997 | 0.000503 | 1.1999e-05 | NAPA ID:26048 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026048 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC335 | NONE | To install a 400V Fuse/Disconnector on TC335. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0002515 | 5.5 | 2017 | 2016-12-06 | B | 4 | 0.000503 | 1.1999e-05
1 | 14354302 | 2016-12-06 09:45 | 2016-12-06 10:00 | 15 | 8 | 120 | 0.00035998 | 0.000287 | 2.3999e-05 | NAPA ID:25296 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 025296 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2357 | NONE | To install an LV Isolator on TC2357. Works location: Ngutumanga Rd, Waihou. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0001435 | 5.5 | 2017 | 2016-12-06 | B | 8 | 0.000287 | 2.3999e-05
1 | 14354463 | 2016-12-07 09:45 | 2016-12-07 10:15 | 30 | 4 | 120 | 0.00035998 | 0.000323 | 1.1999e-05 | NAPA ID:26049 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026049 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2178 | NONE | To install a 400V Fuse Disconnector on TC2178. Works location: Hwy 1, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001615 | 5.5 | 2017 | 2016-12-07 | B | 4 | 0.000323 | 1.1999e-05
1 | 14355401 | 2016-12-07 12:00 | 2016-12-07 12:40 | 40 | 3 | 120 | 0.00035998 | 0.000332 | 8.9993e-06 | NAPA ID:26051 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026051 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6130 | NONE | To install a 30400V Fuse Disconnector on TC6130. Works location: Hwy 1, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000166 | 5.5 | 2017 | 2016-12-07 | B | 3 | 0.000332 | 8.9993e-06
1 | 14356280 | 2016-11-30 08:45 | 2016-11-30 15:12 | 387 | 69 | 26703 | 0.080112 | 0.07949 | 0.00020701 | NAPA ID:26304 TP_MASTERTON GXP > CHAPEL SUB > HIGH ST | 11 | Planned | 026304 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 828561 | NONE | replace red taged 11kv /lv pole. Works location: Solway St, Masterton. WO 30034778 | F3 | HIGH ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.039745 | 5.5 | 2017 | 2016-11-30 | B | 69 | 0.07949 | 0.00020701
1 | 14356323 | 2016-12-07 14:00 | 2016-12-07 14:40 | 40 | 7 | 280 | 0.00083994 | 0.000776 | 2.0998e-05 | NAPA ID:26053 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026053 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6128 | NONE | Install a 400V Fuse Disconnector on TC6128. Works location: Hwy 1, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000388 | 5.5 | 2017 | 2016-12-07 | B | 7 | 0.000776 | 2.0998e-05
1 | 14356338 | 2016-12-12 09:45 | 2016-12-12 11:55 | 130 | 4 | 520 | 0.0015598 | 0.001523 | 1.1998e-05 | NAPA ID:26056 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026056 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1518 | NONE | To install a 400V Fuse Disconnector on TC1518. Works location: Westlea Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0007615 | 5.5 | 2017 | 2016-12-12 | B | 4 | 0.001523 | 1.1998e-05
1 | 14356439 | 2016-11-30 08:19 | 2016-11-30 12:22 | 243 | 1 | 243 | 0.00072902 | 0.00072 | 3.0001e-06 | NAPA ID:24771 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024771 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T9/367 | NONE | Change 3 x poles and 2 x xarms and 1 x TX fitout. Works location: Castlehill Rd. WO 30019072 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00036 | 5.5 | 2017 | 2016-11-30 | B | 1 | 0.00072 | 3.0001e-06
1 | 14356443 | 2016-12-12 13:00 | 2016-12-12 13:11 | 11 | 1 | 11 | 3.2995e-05 | 2.3e-05 | 2.9995e-06 | NAPA ID:26057 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026057 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3568 | NONE | To install a 400V Fuse Disconnector on TC3568. Works location: Westlea Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 1.15e-05 | 5.5 | 2017 | 2016-12-12 | B | 1 | 2.3e-05 | 2.9995e-06
1 | 14356463 | 2016-12-12 14:00 | 2016-12-12 14:40 | 40 | 5 | 200 | 0.00059991 | 0.000554 | 1.4998e-05 | NAPA ID:26058 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026058 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4865 | NONE | To install a 400V Fuse Disconnector on TC4865. Works location: Westlea Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000277 | 5.5 | 2017 | 2016-12-12 | B | 5 | 0.000554 | 1.4998e-05
1 | 14356503 | 2016-12-01 08:32 | 2016-12-01 16:51 | 499 | 19 | 9481 | 0.028444 | 0.028272 | 5.7001e-05 | NAPA ID:24518 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 024518 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2178 | NONE | Upgrade 11Kv conductor from pole 841043 to T2178 in 11kv shutdown. Works location: Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.014136 | 5.5 | 2017 | 2016-12-01 | B | 19 | 0.028272 | 5.7001e-05
1 | 14357480 | 2016-11-09 15:25 | 2016-11-09 22:15 | 409 | 411 | 38360.4167 | 0.11512 | 0.11142 | 0.0012334 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | C634 | POLE | at 15:25, Mikkelsen Rd Sub, CB 5 Maungakawa Rd Feeder. Report came in of Car V Pole at Pole C634. Duty NC Opened CB 5 to de-energise lines until faultman arrived. Isolated lines at ABS 659, IC704 & IC672. Reminder of feeder relivened at 16:18. Permit issued & repairs carried out. All Power Restored on Completion. Replaced 1x Pole, 4x Crossarms, 8x Insulators, Binders, Dead Ends, 3x HV Fuses, Replaced less than 1 span all 3 phases. Les Edwards Attended. NDR: 11735 car vs pole at this address F2184224 ETA required, phoned svs hub. 5mins ETA, fire comms advised. CB 5 was open by NC after receiving a call from Wolf Martin who received a call of a car vs pole on Alexandra Rd. CB 5 had an Auto Reclose at 15:19 on OMS 14356576 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.11142 | 11 | 2017 | 2016-11-09 | C | 411 | 0.11142 | 0.0012334
1 | 14359185 | 2016-11-09 17:11 | 2016-11-09 19:14 | 122 | 15 | 1785.9167 | 0.0053595 | 0.005224 | 4.5015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 396294 | FUSE - ELEMENT/LINK (HV) | reloaded, relivened 2x HV Fuses at IC292 20A. Unknown Cause but has been very windy up there today. Nick Hyland attended. | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.005224 | 11 | 2017 | 2016-11-09 | C | 15 | 0.005224 | 4.5015e-05
1 | 14359480 | 2016-11-09 20:06 | 2016-11-09 20:45 | 38 | 211 | 8144.6 | 0.024442 | 0.022542 | 0.00063321 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 751393 | INSULATOR | HV conductor floating due to faulty insulator. Needs to be attended to before causing a feeder outage. Work area isolated at fuses 8238. Materials used: 1x HV Pin & Insulator, 1x Binder, 3x 30Amp HV Fuse Links Note: Initial FM onsite requested another 1r for safety as job was HV, and to lessen shutdown time. NOC Operator did not request second 1r but stated this may need to be looked at when invoicing. Second faultman Chris Vivier did attend & provide assistance. | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.022542 | 11 | 2017 | 2016-11-09 | C | 211 | 0.022542 | 0.00063321
1 | 14360009 | 2016-11-10 03:15 | 2016-11-10 05:18 | 123 | 12 | 1476 | 0.0044294 | 0.004321 | 3.6011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848485 | JUMPER |  | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.004321 | 11 | 2017 | 2016-11-10 | C | 12 | 0.004321 | 3.6011e-05
1 | 14360364 | 2016-11-10 02:16 | 2016-11-10 02:33 | 17 | 66 | 1122 | 0.0033671 | 0.002772 | 0.00019806 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848485 | JUMPER | at 02:16, Tuhitarata Sub, CB C926 Pirinoa Feeder. Faultman was called to Part Powers / No Powers. Lines patrolled and 3 phase transformers checked. Eventually found a blown jumper at Pole 848485. Isolated Lines at ABS 7197 & Links 7342. Backfeed supplied from TUH C927: ABS S544 Closed. Permit Issued & Repairs carried out. All Power Restored on Completion. | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.002772 | 11 | 2017 | 2016-11-10 | C | 66 | 0.002772 | 0.00019806
1 | 14360586 | 2016-11-10 04:57 | 2016-11-10 06:12 | 74 | 1 | 74.9667 | 0.00022497 | 0.000215 | 3.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8295 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8Amp HV fuses due to bird strike | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000215 | 11 | 2017 | 2016-11-10 | C | 1 | 0.000215 | 3.0009e-06
1 | 14360619 | 2016-11-10 05:26 | 2016-11-10 09:09 | 223 | 316 | 37509.9333 | 0.11257 | 0.10972 | 0.0009483 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 827368 | CONDUCTOR - REPAIR/REHANG | Customer called on emergency line to advise lines down at 183 Morris Rd, Masterton. Bevan Scott 06 377 2928 or 027 321 5836. Repaired downed lines at pole 827368. Used 2m conductor and sleeves | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.10972 | 11 | 2017 | 2016-11-10 | C | 316 | 0.10972 | 0.0009483
1 | 14362096 | 2016-12-13 09:24 | 2016-12-13 13:45 | 261 | 4 | 1044 | 0.0031315 | 0.003095 | 1.1998e-05 | NAPA ID:26076 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026076 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6055 | NONE | To replace arms & Install a 400V Fuse/Disconnector. Works location: Orepunga Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0015475 | 5.5 | 2017 | 2016-12-13 | B | 4 | 0.003095 | 1.1998e-05
1 | 14362105 | 2016-12-13 10:00 | 2016-12-13 10:30 | 30 | 1 | 30 | 8.9986e-05 | 8e-05 | 2.9995e-06 | NAPA ID:26059 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026059 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1528 | NONE | To install a 400V Fuse Disconnector on TP1528. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 4e-05 | 5.5 | 2017 | 2016-12-13 | B | 1 | 8e-05 | 2.9995e-06
1 | 14362130 | 2016-12-13 12:00 | 2016-12-13 12:20 | 20 | 5 | 100 | 0.00029995 | 0.000254 | 1.4998e-05 | NAPA ID:26061 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026061 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2298 | NONE | To install a 400V Fuse Disconnector on TC2298. Works location: Hicks Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000127 | 5.5 | 2017 | 2016-12-13 | B | 5 | 0.000254 | 1.4998e-05
1 | 14362463 | 2016-11-10 08:29 | 2016-11-10 11:05 | 156 | 1214 | 146124 | 0.43851 | 0.42758 | 0.0036431 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 379115 | NONE | Gavin Paget to NCTL - has organised Chopper to fly. Line Patrols Found 3 X Birds at Pole 379115 2 In Bird begone 1 On Ground. | S4 | AWATOITOI 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 0.42758 | 33 | 2017 | 2016-11-10 | C | 1214 | 0.42758 | 0.0036431
1 | 14364034 | 2016-11-10 10:33 | 2016-11-10 11:25 | 52 | 1 | 52 | 0.00015605 | 0.000147 | 3.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L81 | JOINT - CONDUCTOR JOINT | Advised SMC of 999 1 X PG Clamp | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000147 | 11 | 2017 | 2016-11-10 | C | 1 | 0.000147 | 3.0009e-06
1 | 14364066 | 2016-11-10 09:12 | 2016-11-10 13:55 | 283 | 4 | 1132.4 | 0.0033983 | 0.003362 | 1.2004e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12731 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Shane reported that Transformer TC5303 is faulty, need replacing. 2R request for assistance. Replaced transformer TC5303 all service restored Material 1 x transformer , 2 x H/V fuses | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.003362 | 11 | 2017 | 2016-11-10 | C | 4 | 0.003362 | 1.2004e-05
1 | 14364139 | 2016-11-27 08:43 | 2016-11-27 14:15 | 332 | 2 | 662 | 0.0019862 | 0.001968 | 6.0004e-06 | NAPA ID:26393 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE NORTH | 11 | Planned | 026393 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 222835 | NONE | change 11kv pole 222835. Works location: Jellicoe St, Te Puke. WO 30025416 | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.000984 | 5.5 | 2017 | 2016-11-27 | B | 2 | 0.001968 | 6.0004e-06
1 | 14364201 | 2016-12-13 10:05 | 2016-12-13 11:00 | 55 | 7 | 385 | 0.0011548 | 0.001091 | 2.0997e-05 | NAPA ID:26064 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026064 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformr TC1525 | NONE | To install a 400V Fuse Disconnector on TC1525. Works location: Maungatautari Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0005455 | 5.5 | 2017 | 2016-12-13 | B | 7 | 0.001091 | 2.0997e-05
1 | 14364602 | 2016-11-10 10:34 | 2016-11-10 12:00 | 86 | 1 | 86.4667 | 0.00025948 | 0.00025 | 3.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 796330 | FUSE - ELEMENT/LINK (HV) | Reload at Transformer X2613 2 x 2A Bird Strike | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.00025 | 11 | 2017 | 2016-11-10 | C | 1 | 0.00025 | 3.0009e-06
1 | 14364659 | 2016-12-13 12:50 | 2016-12-13 14:55 | 125 | 6 | 750 | 0.0022496 | 0.002195 | 1.7997e-05 | NAPA ID:26065 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026065 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4147 | NONE | To install a 400V Fuse Disconnector on TC4147. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0010975 | 5.5 | 2017 | 2016-12-13 | B | 6 | 0.002195 | 1.7997e-05
1 | 14364767 | 2016-11-10 10:50 | 2016-11-10 12:34 | 104 | 12 | 1248 | 0.0037452 | 0.003637 | 3.6011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848485 | JUMPER |  | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.003637 | 11 | 2017 | 2016-11-10 | C | 12 | 0.003637 | 3.6011e-05
1 | 14364847 | 2016-12-14 09:45 | 2016-12-14 10:10 | 25 | 4 | 100 | 0.00029995 | 0.000263 | 1.1998e-05 | NAPA ID:26079 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026079 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3462 | NONE | To install a 400V Fuse/Disconnector on TC3462. Works location: Stokes Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001315 | 5.5 | 2017 | 2016-12-14 | B | 4 | 0.000263 | 1.1998e-05
1 | 14364861 | 2016-12-14 11:45 | 2016-12-14 12:35 | 50 | 3 | 150 | 0.00044992 | 0.000422 | 8.9984e-06 | NAPA ID:26080 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026080 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2319 | NONE | To install a 400V Fuse/Disconnector on TC2319. Works location: Stokes Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000211 | 5.5 | 2017 | 2016-12-14 | B | 3 | 0.000422 | 8.9984e-06
1 | 14364886 | 2016-12-14 13:45 | 2016-12-14 14:40 | 55 | 5 | 275 | 0.00082486 | 0.000779 | 1.4997e-05 | NAPA ID:26081 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026081 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC999 | NONE | To install a 400V Fuse Disconnector on TC999. Works location: Stokes Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0003895 | 5.5 | 2017 | 2016-12-14 | B | 5 | 0.000779 | 1.4997e-05
1 | 14366558 | 2016-12-15 09:30 | 2016-12-15 10:15 | 45 | 4 | 180 | 0.0005399 | 0.000503 | 1.1998e-05 | NAPA ID:26069 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026069 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2297 | NONE | To install a 400V Fuse Disconnector on TC2297. Works location: Scott Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0002515 | 5.5 | 2017 | 2016-12-15 | B | 4 | 0.000503 | 1.1998e-05
1 | 14366565 | 2016-12-15 11:30 | 2016-12-15 12:25 | 55 | 5 | 275 | 0.00082484 | 0.000779 | 1.4997e-05 | NAPA ID:26070 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026070 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC633 | NONE | To install a 400V Fuse disconnector on TC633. Works location: Maungatautari Rd, Tirau. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0003895 | 5.5 | 2017 | 2016-12-15 | B | 5 | 0.000779 | 1.4997e-05
1 | 14366633 | 2016-12-16 09:15 | 2016-12-16 12:37 | 202 | 4 | 808 | 0.0024235 | 0.002387 | 1.1997e-05 | NAPA ID:22407 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022407 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2322 | NONE | To replace arms, Hardware and relocate the transformers. Works location: Taihoa North Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0011935 | 5.5 | 2017 | 2016-12-16 | B | 4 | 0.002387 | 1.1997e-05
1 | 14366635 | 2016-12-01 09:30 | 2016-12-01 12:30 | 180 | 26 | 4680 | 0.01404 | 0.013806 | 7.8001e-05 | NAPA ID:24435 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 024435 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To replace 11kv pole P11356 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.006903 | 5.5 | 2017 | 2016-12-01 | B | 26 | 0.013806 | 7.8001e-05
1 | 14367514 | 2016-12-16 13:45 | 2016-12-16 14:25 | 40 | 2 | 80 | 0.00023995 | 0.000221 | 5.9987e-06 | NAPA ID:22409 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022409 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP479 | NONE | To install 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0001105 | 5.5 | 2017 | 2016-12-16 | B | 2 | 0.000221 | 5.9987e-06
1 | 14367521 | 2016-11-10 15:31 | 2016-11-10 17:55 | 144 | 51 | 7344 | 0.022039 | 0.021579 | 0.00015305 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/170 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replace 1 X DDO at Transformer T2/170 Other DDOs all OK | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.021579 | 11 | 2017 | 2016-11-10 | C | 51 | 0.021579 | 0.00015305
1 | 14367533 | 2016-12-16 14:00 | 2016-12-16 14:27 | 27 | 17 | 459 | 0.0013767 | 0.001223 | 5.099e-05 | NAPA ID:23024 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 023024 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1957 | NONE | To install a 400V Fuse/Disconnector to TC1957. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0006115 | 5.5 | 2017 | 2016-12-16 | B | 17 | 0.001223 | 5.099e-05
1 | 14367557 | 2016-12-19 09:00 | 2016-12-19 13:32 | 272 | 7 | 1904 | 0.0057106 | 0.005647 | 2.0995e-05 | NAPA ID:25885 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025885 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2134 | NONE | To replace defective arms, Replace pole & install 400V Fuse Dis-connectors on TC2134 & TC1877. Works location: McGill Rd, Maungatautari. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0028235 | 5.5 | 2017 | 2016-12-19 | B | 7 | 0.005647 | 2.0995e-05
1 | 14368233 | 2016-11-10 14:25 | 2016-11-10 16:40 | 135 | 241 | 14940.5167 | 0.044836 | 0.042665 | 0.0010623 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 730223 | CONDUCTOR - REPAIR/REHANG | CB T31 tripped on A phase O/C & E/F flags, line was patrolled and sectionalised and a line was found down at pole 730223, line was isolated at ABS's 5959 & 6000 to repair the line.Line down was caused by a bird strike- magpie 10 M of 16mm copper conductor & 3 X crimp sleeves used. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.042665 | 11 | 2017 | 2016-11-10 | C | 241 | 0.042665 | 0.0010623
1 | 14369122 | 2016-11-10 15:17 | 2016-11-10 19:16 | 238 | 1 | 238.8167 | 0.00071667 | 0.000707 | 3.0009e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/14 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 3ph 30kva transformer & 1x 3Amp fuse after lightning strike | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.000707 | 11 | 2017 | 2016-11-10 | C | 1 | 0.000707 | 3.0009e-06
1 | 14369414 | 2016-12-01 08:55 | 2016-12-01 15:03 | 368 | 10 | 3680 | 0.01104 | 0.01095 | 3e-05 | NAPA ID:25293 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 025293 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P00605 | NONE | install new TX 7423P on pole P00605 to improve power. Kahuterawa Road, Linton, Turitea. W/O 30025838. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.005475 | 5.5 | 2017 | 2016-12-01 | B | 10 | 0.01095 | 3e-05
1 | 14370258 | 2016-11-10 23:20 | 2016-11-11 03:44 | 264 | 485 | 9519 | 0.028566 | 0.024199 | 0.0014555 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217973 | CONDUCTOR - REPAIR/REHANG | CB 1 L/O on O/C Sectionalised and found 3 wires down between ABS SE7-005 & IP515, isolated, repaired & relivened | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.024199 | 11 | 2017 | 2016-11-10 | C | 485 | 0.024199 | 0.0014555
1 | 14374186 | 2016-11-10 23:20 | 2016-11-11 00:31 | 71 | 1 | 71 | 0.00021307 | 0.000204 | 3.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | refer to oms14370258 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000204 | 11 | 2017 | 2016-11-10 | C | 1 | 0.000204 | 3.0009e-06
1 | 14374233 | 2016-11-11 07:03 | 2016-11-11 08:51 | 108 | 10 | 1083.8333 | 0.0032525 | 0.003162 | 3.0009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P01225 | FUSE - ELEMENT/LINK (HV) | Emailed and advised Jo @ SMC **Please check OMS 14374275 also OMS 14374233** set of fuses out at H108 2 x DDO out on 2 phase line - indicates pole could be down. poles and lines through paddocks/river - FM needs to do line patrol and it may take a while due to weather and swollen river./ Will pass information onto control to ascertain if we need more crews for line patrols. Jeff reported that reload reliven was successful and extra operational assisatance was not required - Request rejected Reload reliven at H108 2 x 10A Lightening | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.003162 | 11 | 2017 | 2016-11-11 | C | 10 | 0.003162 | 3.0009e-05
1 | 14375747 | 2016-11-11 10:50 | 2016-11-11 11:36 | 45 | 2 | 91.5667 | 0.00027478 | 0.000256 | 6.0018e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2873 | JUMPER | Transformer outage required (HV fuses) to repair a loose jumper on the HV side which had come out of connector. . Suspect it was due to wind. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000256 | 11 | 2017 | 2016-11-11 | C | 2 | 0.000256 | 6.0018e-06
1 | 14409974 | 2016-12-07 09:29 | 2016-12-07 15:05 | 335 | 20 | 6718 | 0.020153 | 0.019972 | 5.9996e-05 | NAPA ID:25409 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | 025409 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Change 11kv pole 832750 and TX T2078 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.009986 | 5.5 | 2017 | 2016-12-07 | B | 20 | 0.019972 | 5.9996e-05
1 | 14410028 | 2016-12-01 09:30 | 2016-12-01 15:30 | 359 | 11 | 3959.45 | 0.011879 | 0.011779 | 3.3001e-05 | NAPA ID:24606 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 024606 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 787258 | NONE | replace old hardwood pole 787258 and resag 11 kv wires. Moawhonga Valley Road, Taihape, Mataroa. W/O 30020456. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0058895 | 5.5 | 2017 | 2016-12-01 | B | 11 | 0.011779 | 3.3001e-05
1 | 14410216 | 2016-12-02 09:45 | 2016-12-02 11:59 | 134 | 3 | 402 | 0.001206 | 0.001179 | 9e-06 | NAPA ID:26186 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 026186 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | isolation of 11 kv line for tree work from line fuses 2626 . Trees causing 11 kv outages | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0005895 | 5.5 | 2017 | 2016-12-02 | B | 3 | 0.001179 | 9e-06
1 | 14410233 | 2016-12-02 08:45 | 2016-12-02 13:43 | 298 | 1 | 298 | 0.000894 | 0.000885 | 3e-06 | NAPA ID:26268 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 026268 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 826880 | NONE | replace tx structure and pin pole. Westmere Road, Gladstone, Masterton. W/O 30013200. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.0004425 | 5.5 | 2017 | 2016-12-02 | B | 1 | 0.000885 | 3e-06
1 | 14410281 | 2016-11-29 09:30 | 2016-11-29 14:57 | 326 | 40 | 13074.6667 | 0.039226 | 0.038865 | 0.00012001 | NAPA ID:25650 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025650 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-113 | NONE | REPLACE POLES AND ARMS CUT TREES. Te Matai Road - Strange Road, Mangorewa, Te Puke, W/O 30017835. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.019432 | 5.5 | 2017 | 2016-11-29 | B | 40 | 0.038865 | 0.00012001
1 | 14410293 | 2016-12-02 09:00 | 2016-12-02 15:33 | 393 | 26 | 10218 | 0.030654 | 0.03042 | 7.8e-05 | NAPA ID:24774 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024774 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS I18 | NONE | Change 2 x poles and 8 x xarms and 5 x H structures, Install TEMP ABS 80. Castlehill, Alferdton, Mangamaire. W/O 30019072. | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.01521 | 5.5 | 2017 | 2016-12-02 | B | 26 | 0.03042 | 7.8e-05
1 | 14410326 | 2016-11-23 01:00 | 2016-11-25 01:14 | 2894 | 124 | 360 | 0.0010801 | 0 | 0.00018002 | NAPA ID:25717 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | 025717 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | 1: Off load switching to Break before Make. Less than 1min switching 0100hrs 23/11/2016. 2: Create 11kV Line Break at pole B0767. (11kV ABS 1376 & 11kV ABS 1137 Opened Tagged Backfeeds in place)). 3: Install new 11kV Regulator complete with 11kV Bypass ABS, Links & Fuses at pole B0866. 4: Complete installation of reg. (Commissioning will be on NAPA 25752 on the 25th/11/2016). 5: Close 11kV Line Break at pole B0767. 6:Feeder back to normal. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-11-23 | B | 124 | 0 | 0.00018002
1 | 14410335 | 2016-12-05 09:23 | 2016-12-05 15:45 | 382 | 1 | 382 | 0.001146 | 0.001136 | 2.9998e-06 | NAPA ID:25565 TP_STRATFORD GXP | 11 | Planned | 025565 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replacing 33Kv xarm & conductor with 11Kv under pole no 734490 Shut 1 of week starting 05/12/16 to 09/12/16 for this project . Reconfigure the Network for the start of this weeks outages . Refer to proposed switching & methodology . | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000568 | 5.5 | 2017 | 2016-12-05 | B | 1 | 0.001136 | 2.9998e-06
1 | 14422048 | 2016-12-02 09:00 | 2016-12-02 13:30 | 270 | 4 | 1080 | 0.00324 | 0.003204 | 1.2e-05 | NAPA ID:26274 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 026274 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuse T2722 | NONE | replace cross arms. State Highway 2, Masterton, Miro St. Akura. W/O 30030270. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.001602 | 5.5 | 2017 | 2016-12-02 | B | 4 | 0.003204 | 1.2e-05
1 | 14422959 | 2016-12-02 10:00 | 2016-12-02 12:00 | 120 | 54 | 6480 | 0.01944 | 0.018954 | 0.000162 | NAPA ID:25722 TP_MARTON GXP > RATA SUB > PUTORINO | 22 | Planned | 025722 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 806945 | NONE | Replace three 11kv disc on tap off pole number 806945. Rangatira, Hunterville, Putoring, Rata. W/O 10160679. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.009477 | 11 | 2017 | 2016-12-02 | B | 54 | 0.018954 | 0.000162
1 | 14423572 | 2016-11-16 10:32 | 2016-11-16 12:56 | 144 | 3 | 432 | 0.0012963 | 0.001269 | 9.002e-06 | NAPA ID:26564 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 026564 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 745169 | NONE | Replace 11kV Transformer 1538 for a New 30kVA tx. Embedded generation at 385 Wortley RD Inglewood. 397 Wortley Road, Waiongana, Inglewood. W/O 30030730. | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0006345 | 5.5 | 2017 | 2016-11-16 | B | 3 | 0.001269 | 9.002e-06
1 | 14423645 | 2016-11-23 09:01 | 2016-11-23 15:20 | 379 | 35 | 13265 | 0.0398 | 0.039485 | 0.00010501 | NAPA ID:26456 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 026456 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Change 10 x poles and 11 x xarms, and install TEMP 11KV LINKS 28 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.019742 | 5.5 | 2017 | 2016-11-23 | B | 35 | 0.039485 | 0.00010501
1 | 14423677 | 2016-11-19 09:15 | 2016-11-19 15:29 | 374 | 45 | 16830 | 0.0505 | 0.050094 | 0.00013503 | NAPA ID:26449 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 026449 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 58 | NONE | Change 7 x poles and 15 x xarms, and install TEMP ABS 58 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.025047 | 5.5 | 2017 | 2016-11-19 | B | 45 | 0.050094 | 0.00013503
1 | 14424259 | 2016-11-11 17:40 | 2016-11-12 11:42 | 1081 | 168 | 24605.2333 | 0.073838 | 0.072325 | 0.00064219 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O632 | BINDER | ( KPE 1 ) recloser RC22 tripped E/F, ABR scheme at 9668/2 closed and tripped TAH 4 ( RC27 ) Sectionaliser 9668/2 opened & recloser RC27 closed. ABS 520 Opened, customers notified, power left off over night as line is cross country, Floating conductor found at pole O632 Isolated at ABS 520. No Back Feeds available. line rebound in, relivened. Insulators posssibly need to be replaced with Clamp top insulators as area prone to high winds, customer said has happened at this site before. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.072325 | 11 | 2017 | 2016-11-11 | C | 168 | 0.072325 | 0.00064219
1 | 14424429 | 2016-11-11 17:40 | 2016-11-11 17:46 | 5 | 240 | 1412 | 0.0042373 | 0.002076 | 0.00072022 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | RC 27 | UNKNOWN | Recloser RC 27 tripped on C phase O/C flags, after auto backfeed system Recloser 9668/2 between Tahuna CB 4 & Kerepehi CB 1 closed for loss of supply at Recloser RC22 (Kerepehi CB1), Recloser 9668/2 was opened and Recloser RC 27 was closed in to restore supply, fault was on Kerepehi CB 1 past Recloser RC22. Protection check may be needed, Auto Backfeed system should not have operated as KPE CB 1 did not trip, this systems is not to operate if Recloser RC22 trips. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.002076 | 11 | 2017 | 2016-11-11 | C | 240 | 0.002076 | 0.00072022
1 | 14426883 | 2016-11-12 08:05 | 2016-11-12 10:38 | 153 | 7 | 1071 | 0.0032139 | 0.00315 | 2.1006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P2070 | FUSE - ELEMENT/LINK (HV) | Removed tree through the lines at Pole P2070 . Isolation at Fuses FP1261, no back feeds available. 6amp HV Fuse element replaced at Fuses FP1261 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.00315 | 11 | 2017 | 2016-11-12 | C | 7 | 0.00315 | 2.1006e-05
1 | 14427347 | 2016-12-01 09:31 | 2016-12-01 14:59 | 327 | 20 | 6554.3333 | 0.019663 | 0.019483 | 6.0001e-05 | NAPA ID:24448 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 024448 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 12109 | NONE | reconductor 6.6kv lines. Works location: Ngaro Rd. WO 30018291 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.0097415 | 3.3 | 2017 | 2016-12-01 | B | 20 | 0.019483 | 6.0001e-05
1 | 14428840 | 2016-11-12 13:00 | 2016-11-12 15:32 | 152 | 6 | 912 | 0.0027368 | 0.002682 | 1.8005e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/320 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Ongoing problem with low volts on 1 phase. Fault traced to defective transformer T8/320. Transformer changed and Livened OK.Refer linked job for notes (OMS 14428153) - job not forced uop, OMS No. changee | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002682 | 11 | 2017 | 2016-11-12 | C | 6 | 0.002682 | 1.8005e-05
1 | 14429135 | 2016-11-12 17:12 | 2016-11-12 17:58 | 46 | 5 | 231.5833 | 0.00069495 | 0.000649 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718155 | BINDER | 1R Repair broken binder - put paul fitzpatrick on site, Fault found by Jade. Isolation required between ABS TA801 and 8831/1 to repair broken binders (3 replaced at Pole 718155). Relivened OK | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000649 | 11 | 2017 | 2016-11-12 | C | 5 | 0.000649 | 1.5004e-05
1 | 14429400 | 2016-11-12 18:18 | 2016-11-12 18:55 | 37 | 5 | 185 | 0.00055516 | 0.00051 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | NG378 | CONDUCTOR - REPAIR/REHANG | Line down Witiora Road. Isolated at fuses NG378. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00051 | 11 | 2017 | 2016-11-12 | C | 5 | 0.00051 | 1.5004e-05
1 | 14430053 | 2016-11-12 18:34 | 2016-11-13 08:12 | 818 | 4 | 3272.1333 | 0.0098192 | 0.009783 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 712444 | CROSSARM - WHOLE ASSEMBLY | Line goes across country will put in morning as can not see anything @ pole 712444 straightned crossarm and replaced bolts . | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.009783 | 11 | 2017 | 2016-11-12 | C | 4 | 0.009783 | 1.2003e-05
1 | 14431041 | 2016-11-12 18:30 | 2016-11-13 00:27 | 357 | 242 | 26099.2833 | 0.07832 | 0.076141 | 0.00078923 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI109 | CONDUCTOR - REPAIR/REHANG | Rebolted crossarm up pulled conductors up Replace 1 X DDO at LI109 as Broke when opening it Used 3 X HT Insulators 1` X DDO | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.076141 | 11 | 2017 | 2016-11-12 | C | 242 | 0.076141 | 0.00078923
1 | 14431544 | 2016-11-12 18:43 | 2016-11-12 23:41 | 297 | 299 | 21688.2167 | 0.065083 | 0.062391 | 0.0024097 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3221t | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced 3 X DDo at transformer 3221t | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.062391 | 11 | 2017 | 2016-11-12 | C | 299 | 0.062391 | 0.0024097
1 | 14434616 | 2016-11-12 22:42 | 2016-11-13 12:25 | 822 | 768 | 237828.0667 | 0.71369 | 0.70677 | 0.0023047 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 268850 | CONDUCTOR - REPAIR/REHANG | KPT CB1 tripped A, B & C Ph O/C, E/F, L/O recloser 9606/2 opened with back feed via sectionaliser 9223/2. Feeder sectionalised ( Sw/Gear 13021/1 locked up staff called out to repair ) Line down x 1 at pole 268850 Isolation between ABS IP414 & IP 415 back feed via ABS ABS SA2 052 Lines repaired 4 squirrel sleeves, 5m of squirrel conductor, 1x din fuse assembly replaced at transformer TB2-106. Reset LFI flags at sw/Gear 13021. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.70677 | 11 | 2017 | 2016-11-12 | C | 768 | 0.70677 | 0.0023047
1 | 14436447 | 2016-11-13 00:28 | 2016-11-13 15:57 | 929 | 172 | 32168 | 0.09653 | 0.094982 | 0.00092125 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P13269 | CONDUCTOR - REPAIR/REHANG | WHI 2 recloser 9713 tripped A & B Ph O/C L/O. feeder sectionalised Temp Line Break cut at pole P13629. Feeder relivened. Trees throught the lines beyond this point Asplundh required to clear trees.Trees cleared temp line break closed power restored. Recreated on 17018685 | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.094982 | 11 | 2017 | 2016-11-13 | C | 172 | 0.094982 | 0.00092125
1 | 14436970 | 2016-11-13 00:56 | 2016-11-13 05:50 | 294 | 53 | 15601.4333 | 0.046817 | 0.046339 | 0.00015904 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 733794 | POLE | Car V Pole Lines on Road Used 1x Pole 1x Crossarm 3 X Insulaters 3 X 10 amp Fuses 50m 25mm Copper Conductor | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.046339 | 11 | 2017 | 2016-11-13 | C | 53 | 0.046339 | 0.00015904
1 | 14437605 | 2016-11-13 02:28 | 2016-11-13 07:34 | 306 | 21303 | 2708172.5833 | 8.1267 | 7.935 | 0.063927 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2422,2162 | UNKNOWN | Trippings of CB 2422 & 2162 at TGA GXP. E/F Intertrip. Lines patrolled Feeders gradually restored. No Fault found. E/F flag indicating on a trustpower line CB162 Wairoa L1 feeder. This feeder was left off for restoration until patrolled by Trustpower contractor. Will need protection investigation. | S2 | GREERTON202-AONGATETE82 33KV | TAURANGA 31 | Tauranga | GREERTON | Eastern Electricity | POWERCO | 7.935 | 33 | 2017 | 2016-11-13 | C | 21303 | 7.935 | 0.063927
1 | 14460335 | 2016-11-13 19:39 | 2016-11-13 20:37 | 58 | 1 | 58.7 | 0.00017615 | 0.000167 | 3.0008e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2773T | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses blown at Transformer 2733T. Patrolled, Relivened OK. (2A). Unknown | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000167 | 11 | 2017 | 2016-11-13 | C | 1 | 0.000167 | 3.0008e-06
1 | 14460599 | 2016-11-14 00:05 | 2016-11-14 00:08 | 3 | 44 | 147.4 | 0.00044231 | 0 | 0.00013203 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | C929 | UNKNOWN | C929 tripped O/C A & C Phase. Line not patrolled - Earthquake | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-14 | C | 44 | 0 | 0.00013203
1 | 14460645 | 2016-11-14 00:05 | 2016-11-14 00:08 | 3 | 586 | 1963.1 | 0.0058908 | 0 | 0.0017585 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | C928 | UNKNOWN | C928 Tripped O/C A & B Phase. Line not patrolled - earthquake. | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-14 | C | 586 | 0 | 0.0017585
1 | 14461235 | 2016-11-14 00:05 | 2016-11-14 09:48 | 582 | 253 | 86060.6167 | 0.25825 | 0.25597 | 0.0020165 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | T879 | CONDUCTOR - REPAIR/REHANG | CB C955 Tripped - No Flags. Line patrolled.Lines found twisted together and line down between transformers T879 & T1811. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.25597 | 11 | 2017 | 2016-11-14 | C | 253 | 0.25597 | 0.0020165
1 | 14461490 | 2016-11-14 00:05 | 2016-11-14 00:08 | 3 | 228 | 756.2 | 0.0022692 | 0 | 0.00068418 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | C956 tripped during EQ. Closed successfully. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-14 | C | 228 | 0 | 0.00068418
1 | 14461898 | 2016-11-14 00:05 | 2016-11-14 05:06 | 300 | 72 | 21624 | 0.064889 | 0.06424 | 0.00021606 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | WH2 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | 28 and 54 TIWHAITI ROAD - both addresses have pole fuses out and need to be checked once lines down is repaired - OMS 14562013 Check for safety - Lines down between Tawhaiti Road and Tawhiti Musuem. Wires draped on a wooden gateway over someone's gateway Advised SMC of 999 1:18pm - email sent to SMC to escalate | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.06424 | 11 | 2017 | 2016-11-14 | C | 72 | 0.06424 | 0.00021606
1 | 14463941 | 2016-11-14 00:05 | 2016-11-14 06:02 | 356 | 91 | 32467.2833 | 0.097427 | 0.096607 | 0.00027307 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 809518 | UNKNOWN | Earthquake - CB 2842 trip / patrolled / reclosed OK. Flag A Phase OC | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.096607 | 11 | 2017 | 2016-11-14 | C | 91 | 0.096607 | 0.00027307
1 | 14464044 | 2016-11-14 00:05 | 2016-11-14 06:45 | 399 | 693 | 226304.85 | 0.67909 | 0.67285 | 0.0020795 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P33020 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | CB9 Tripped. Network line found down across the driveway. Materials used: 15 metres of 16mm CU and 2 x sleeves. | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.67285 | 11 | 2017 | 2016-11-14 | C | 693 | 0.67285 | 0.0020795
1 | 14464740 | 2016-11-14 00:05 | 2016-11-14 03:32 | 206 | 200 | 38500.2333 | 0.11553 | 0.11373 | 0.00060016 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P41377 | CONDUCTOR - REPAIR/REHANG | CB12 Tripped, CB23 Tripped. Line patrolled and lines found twisted at P41377 and P41376. | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.11373 | 11 | 2017 | 2016-11-14 | C | 200 | 0.11373 | 0.00060016
1 | 14467991 | 2016-11-14 00:05 | 2016-11-14 01:42 | 96 | 212 | 20507.4667 | 0.061538 | 0.059629 | 0.00063616 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Recloser 4261/2 tripped A & B Phase O/C. Line not patrolled - Earthquake | F2 | TAUPO 2 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.059629 | 11 | 2017 | 2016-11-14 | C | 212 | 0.059629 | 0.00063616
1 | 14468206 | 2016-11-14 00:05 | 2016-11-14 01:23 | 77 | 841 | 63259.35 | 0.18983 | 0.18226 | 0.0025237 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Mangamutu Sub, CB 6, 8 & 10 tripped following earthquake Lines patrolled, relivened OK | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.18226 | 11 | 2017 | 2016-11-14 | C | 841 | 0.18226 | 0.0025237
1 | 14470343 | 2016-11-14 00:06 | 2016-11-14 02:22 | 136 | 2515 | 252803.2167 | 0.75861 | 0.73596 | 0.007547 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | CB 5 & CB 9 | UNKNOWN | CB 5 tripped on PH A & B OC CB 9 Tripped on INTT OC, PH B & C OC, & Gnd Fault Line patrolled | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.73596 | 11 | 2017 | 2016-11-14 | C | 2515 | 0.73596 | 0.007547
1 | 14472105 | 2016-11-14 00:06 | 2016-11-14 02:12 | 126 | 386 | 46609.2667 | 0.13986 | 0.13639 | 0.0011583 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB R41 Tripped O/C INST. Sectionalising undertaken to restore. Earthquake occurred at this time. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.13639 | 11 | 2017 | 2016-11-14 | C | 386 | 0.13639 | 0.0011583
1 | 14472852 | 2016-11-14 00:06 | 2016-11-14 03:57 | 231 | 861 | 199364.55 | 0.59825 | 0.5905 | 0.0025837 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | WGN CB 7 | UNKNOWN | 1R - Patrolled by Gary Fisher Trip Flags InvT, Ph A, B , & C OC, Gnd Fault | F2/F3 | WANGANUI EAST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.5905 | 11 | 2017 | 2016-11-14 | C | 861 | 0.5905 | 0.0025837
1 | 14475809 | 2016-11-14 00:06 | 2016-11-14 01:42 | 96 | 791 | 76410.6 | 0.22929 | 0.22217 | 0.0023736 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | CB11 Tripped O/C. Line patrolled - cause of fault unknown. | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.22217 | 11 | 2017 | 2016-11-14 | C | 791 | 0.22217 | 0.0023736
1 | 14476602 | 2016-11-14 00:06 | 2016-11-14 06:13 | 367 | 2678 | 510174.3667 | 1.5309 | 1.5068 | 0.0087893 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P03600 | LIGHTNING ARRESTOR (HV) | Y40 tripped O/C E/F. Line patrolled and lightning arrestor cut away at pole P03600. | S3 | LINTON-TURITEA 33KV | LINTON | Manawatu | TP_LINTON | Western Electricity | POWERCO | 1.5068 | 33 | 2017 | 2016-11-14 | C | 2678 | 1.5068 | 0.0087893
1 | 14479511 | 2016-11-14 00:06 | 2016-11-14 04:18 | 252 | 1935 | 420660.8333 | 1.2623 | 1.2449 | 0.0058065 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 3102 | UNKNOWN | Peat st CB 7, CB 8, CB 4747/3, CB 1092, & CB 3092 tripped. Line patrolled. No fault found. | F3 | ARAMOHO RIVERSIDE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 1.2449 | 11 | 2017 | 2016-11-14 | C | 1935 | 1.2449 | 0.0058065
1 | 14480635 | 2016-11-14 00:06 | 2016-11-14 04:49 | 283 | 602 | 129456.7167 | 0.38847 | 0.38305 | 0.0018065 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 750923 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | CB7 Tripped O/C. Line patrolled. Lines down reported 15 Lorna Street, New Plymouth. (SMC informed 1:26am, NC informed). Council pump station affected also 1 Ocean View Parade Moturoa no power. 2 lines ru-hung and 2 jumpers repaired. | F2 | MOTUROA 7 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.38305 | 11 | 2017 | 2016-11-14 | C | 602 | 0.38305 | 0.0018065
1 | 14481480 | 2016-11-14 00:06 | 2016-11-14 11:00 | 654 | 257 | 116940.7667 | 0.35091 | 0.3486 | 0.0007712 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | 97 Clarke Road - THERE ARE 3X POWER LINES DOWN ON THE GROUND BY THE RD AROUND 200m AWAY FROM THE HOUSE. THE POWER IS OFF. , SMC informed 2:30am | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.3486 | 11 | 2017 | 2016-11-14 | C | 257 | 0.3486 | 0.0007712
1 | 14481739 | 2016-11-14 00:06 | 2016-11-14 06:37 | 390 | 1413 | 448645.1 | 1.3463 | 1.3336 | 0.0034479 |  | 33 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | x20 | UNKNOWN | CB X20 tripped on B & C phase OC due to earth quake. Relivened, OK This was all restored when Dave got to site, no onsite here now | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 1.3336 | 33 | 2017 | 2016-11-14 | C | 1413 | 1.3336 | 0.0034479
1 | 14483757 | 2016-11-14 00:06 | 2016-11-14 03:41 | 215 | 219 | 40475.8167 | 0.12146 | 0.11949 | 0.00065717 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB R11 Tripped O/C. All power restored, Hazards removed | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.11949 | 11 | 2017 | 2016-11-14 | C | 219 | 0.11949 | 0.00065717
1 | 14483979 | 2016-11-14 00:06 | 2016-11-14 01:49 | 103 | 582 | 60304.9 | 0.18096 | 0.17572 | 0.0017465 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | CB R61 | UNKNOWN | 11kV CB R21 tripped to lock out, no flags. | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.17572 | 11 | 2017 | 2016-11-14 | C | 582 | 0.17572 | 0.0017465
1 | 14484563 | 2016-11-14 00:06 | 2016-11-14 04:28 | 262 | 461 | 85044.6 | 0.2552 | 0.25105 | 0.00097225 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 10227 | NONE |  | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.25105 | 11 | 2017 | 2016-11-14 | C | 461 | 0.25105 | 0.00097225
1 | 14485235 | 2016-11-14 00:06 | 2016-11-14 04:11 | 245 | 316 | 74529.9667 | 0.22365 | 0.2208 | 0.00094825 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H15 | FUSE - ELEMENT/LINK (HV) | CB23 Tripped. Line patrolled and HV Fuse replaced at Fuses H15. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.2208 | 11 | 2017 | 2016-11-14 | C | 316 | 0.2208 | 0.00094825
1 | 14487316 | 2016-11-14 00:06 | 2016-11-14 04:00 | 234 | 716 | 167925.8667 | 0.50391 | 0.49746 | 0.0021486 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | WGN CB 7 | UNKNOWN | Trip Flags Inv T OC, Ph A & B OC, Line patrolled. | F3 | IKITARA RD | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.49746 | 11 | 2017 | 2016-11-14 | C | 716 | 0.49746 | 0.0021486
1 | 14489809 | 2016-11-14 00:06 | 2016-11-14 01:46 | 99 | 48 | 4788.8 | 0.01437 | 0.013938 | 0.00014404 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Norfolk CB C881 tripped O/C. Line patrolled and no fault found. Severe earthquake. | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.013938 | 11 | 2017 | 2016-11-14 | C | 48 | 0.013938 | 0.00014404
1 | 14489980 | 2016-11-14 00:06 | 2016-11-14 02:51 | 165 | 2546 | 362045.1333 | 1.0864 | 1.0635 | 0.00764 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | OCB 5 tripped O/C. Line patrolled - cause of fault not found. | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 1.0635 | 11 | 2017 | 2016-11-14 | C | 2546 | 1.0635 | 0.00764
1 | 14492528 | 2016-11-14 00:06 | 2016-11-14 04:41 | 275 | 4 | 1100.6667 | 0.0033029 | 0.003266 | 1.2003e-05 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Stratford GXP CB 2822 | UNKNOWN | 33kV CB 2822 tripped to Lock out. Suspected to be line clash. LOS to Waihapa Sub. NZFS reported flash down Skinner road. Patrolled and re-livened no issues found. No paperwork found. | S4 | WAIHAPA 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.003266 | 33 | 2017 | 2016-11-14 | C | 4 | 0.003266 | 1.2003e-05
1 | 14494796 | 2016-11-14 00:06 | 2016-11-14 02:08 | 121 | 255 | 31029.25 | 0.093112 | 0.090816 | 0.0007652 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | KEG CB 11 | NONE | 1R - Les Patrolled. Trip Flag OC | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.090816 | 11 | 2017 | 2016-11-14 | C | 255 | 0.090816 | 0.0007652
1 | 14497244 | 2016-11-14 00:06 | 2016-11-14 12:12 | 725 | 249 | 103554.7 | 0.31074 | 0.3085 | 0.00096025 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 720426 | CONDUCTOR - REPAIR/REHANG | Escalated to FRM CB KA7 tripped. Line down at Pole 720425. 7 x sleeves, 1 span not all phases, 4 x fuses, 1 x fuse holder. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.3085 | 11 | 2017 | 2016-11-14 | C | 249 | 0.3085 | 0.00096025
1 | 14498588 | 2016-11-14 00:06 | 2016-11-16 15:21 | 3794 | 566 | 215851.9833 | 0.64772 | 0.64263 | 0.0064067 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nil | UNKNOWN | Ohangai Road - further up from where they just were - by the flashing lights near the last job. Left a message for Rhys Job came through from retailer - Lines down on the corner of Allen road and Meremere Road - cusotmers driving over them, advised OCT. Rang customer for hazard process - she advised she waved school bus down and advised as there is a young child who gets on where the line is down. 15/11 11:45 Advise the Hub that Fuses WH270 need crew to close when available | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.64263 | 11 | 2017 | 2016-11-14 | C | 566 | 0.64263 | 0.0064067
1 | 14499404 | 2016-11-14 00:06 | 2016-11-14 09:24 | 558 | 340 | 152934.6667 | 0.45892 | 0.45586 | 0.0010203 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | DDO | FUSE - ELEMENT/LINK (HV) | Lines down 78 Rawhitiroa Road, Eltham - fm has disconnected 78 Rawhitiroa road, Eltham have re entered a job for this property. No materials used, replaced 2x 8a DDO fuses, power restored at 09:08. The abovemementioned works were undertaken during the feeder fault that is reflected within this outage. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.45586 | 11 | 2017 | 2016-11-14 | C | 340 | 0.45586 | 0.0010203
1 | 14499746 | 2016-11-14 00:06 | 2016-11-14 03:01 | 174 | 847 | 148112.0667 | 0.44445 | 0.43683 | 0.0025417 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Part of Kai Iwi tripping. CB3102 tripped during earthquake. | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.43683 | 11 | 2017 | 2016-11-14 | C | 847 | 0.43683 | 0.0025417
1 | 14500595 | 2016-11-14 00:06 | 2016-11-14 03:53 | 226 | 1529 | 346394.95 | 1.0395 | 1.0257 | 0.0045882 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | SIS REQUIRED | UNKNOWN | CB tripped as a result of the earthquake | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 1.0257 | 11 | 2017 | 2016-11-14 | C | 1529 | 1.0257 | 0.0045882
1 | 14503376 | 2016-11-14 00:06 | 2016-11-14 06:30 | 383 | 1173 | 350722.0167 | 1.0524 | 1.0419 | 0.0035199 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 742729 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, ALL PHASES | Outage required between ABS 344 & 350 to repair lines down. No backfeeds available. BBK7 being backfed from BBK8 via ABS 86. Replaced 8 x sleeves 1 x 2A fuse 1 x 63A fuse, conductor | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 1.0419 | 11 | 2017 | 2016-11-14 | C | 1173 | 1.0419 | 0.0035199
1 | 14505588 | 2016-11-14 00:06 | 2016-11-14 14:45 | 878 | 185 | 143386.55 | 0.43027 | 0.42861 | 0.00055514 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | D21 | NONE | Feeder sectionalised and patrolled no fault found. | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.42861 | 11 | 2017 | 2016-11-14 | C | 185 | 0.42861 | 0.00055514
1 | 14505775 | 2016-11-14 00:06 | 2016-11-14 04:23 | 256 | 1 | 256.85 | 0.00077075 | 0.000761 | 3.0007e-06 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | S3 | PEAT ST 33KV | BRUNSWICK | Wanganui | TP_BRUNSWICK | Western Electricity | POWERCO | 0.000761 | 33 | 2017 | 2016-11-14 | C | 1 | 0.000761 | 3.0007e-06
1 | 14505779 | 2016-11-14 00:06 | 2016-11-14 02:40 | 153 | 2244 | 295020.5333 | 0.88529 | 0.86509 | 0.0067337 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | cb 12 | UNKNOWN | CB 12 tripped on Ph A & B Fault | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.86509 | 11 | 2017 | 2016-11-14 | C | 2244 | 0.86509 | 0.0067337
1 | 14508025 | 2016-11-14 00:07 | 2016-11-14 01:29 | 82 | 4075 | 330752.3333 | 0.99251 | 0.95583 | 0.012228 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Casstle cliff CB 3102/1 tripped in earthquake line patrollled and sub relivened | S3 | CASTLECLIFF NORTH 33KV | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.95583 | 33 | 2017 | 2016-11-14 | C | 4075 | 0.95583 | 0.012228
1 | 14512295 | 2016-11-14 00:07 | 2016-11-14 04:31 | 264 | 219 | 57668.7667 | 0.17305 | 0.17108 | 0.00065717 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB7 Tripped All Phases O/C. Line patrolled - no fault found. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.17108 | 11 | 2017 | 2016-11-14 | C | 219 | 0.17108 | 0.00065717
1 | 14512876 | 2016-11-14 00:08 | 2016-11-14 10:52 | 643 | 249 | 100304.4333 | 0.30099 | 0.29875 | 0.00080421 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | C927 | CONDUCTOR - REPAIR/REHANG | C927 tripped A Phase. 8.14am advised LV Lines down at transformer T1054. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.29875 | 11 | 2017 | 2016-11-14 | C | 249 | 0.29875 | 0.00080421
1 | 14513129 | 2016-11-14 00:05 | 2016-11-14 02:30 | 145 | 1280 | 135573.7333 | 0.40683 | 0.3953 | 0.003841 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Clareville C838 tripped due to severe earthquake. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.3953 | 11 | 2017 | 2016-11-14 | C | 1280 | 0.3953 | 0.003841
1 | 14521676 | 2016-11-14 03:52 | 2016-11-14 03:56 | 4 | 64 | 264.5333 | 0.00079381 | 0.000217 | 0.00019205 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | CB955 tripped due to EQ. Closed successfully. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000217 | 11 | 2017 | 2016-11-14 | C | 64 | 0.000217 | 0.00019205
1 | 14522213 | 2016-11-14 00:06 | 2016-11-14 07:29 | 443 | 244 | 87353.3833 | 0.26213 | 0.25993 | 0.0007802 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Mangorei CB 499 tripped due to earthquake. | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.25993 | 11 | 2017 | 2016-11-14 | C | 244 | 0.25993 | 0.0007802
1 | 14522633 | 2016-11-14 05:13 | 2016-11-14 09:40 | 267 | 1 | 267.3 | 0.00080211 | 0.000793 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | C18 | FUSE - ELEMENT/LINK (HV) | Check OMS: 14531233 - 79 DUNCAN ROAD shane advises replaced 2x HV fuses at C18 power restored 9.40 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000793 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000793 | 3.0007e-06
1 | 14522645 | 2016-11-14 05:16 | 2016-11-14 08:26 | 190 | 4 | 761.6667 | 0.0022856 | 0.002249 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P39962 | FUSE - ELEMENT/LINK (HV) | 2x 6amp and candle due to earthquake. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.002249 | 11 | 2017 | 2016-11-14 | C | 4 | 0.002249 | 1.2003e-05
1 | 14523166 | 2016-11-14 05:21 | 2016-11-14 11:28 | 366 | 330 | 48269.8333 | 0.14485 | 0.14188 | 0.00099026 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 71707 | CONDUCTOR - REPAIR/REHANG | TOO C822 tripped A & B Ph O/C, E/F, L/O Lines down at 148 TE ORE ORE ROAD - 2 lines lying across the road, customer has is directing traffic around lines - advised Maurice control Repair LV lines at Pole 71707 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.14188 | 11 | 2017 | 2016-11-14 | C | 330 | 0.14188 | 0.00099026
1 | 14523779 | 2016-11-14 14:10 | 2016-11-14 15:50 | 100 | 954 | 29859 | 0.0896 | 0.081011 | 0.00097225 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 356901 | JUMPER | at 13:39, Cambria Sub, CB 9 Glover Rd West. Calls came in of part powers. Faultmen dispatched & investigation began. Found broken jumper at links 8711 (Pole 356901). Isolated Lines at ABS 8608, CA719, 6947, Sw/gear CA761, Links 12083/4 & 8747. Backfeeds supplied from CAM 8: Closed Sectionaliser 12150/2. Permit issued & repairs carried out. All Power Restored on Completion. Kane McKay attended. 1x Jumper Replaced & 2x Sleeves Used. Unknown cause but could have been line clash from earthquake and fault current caused jumper to blow. **OMS 14524992 - 411 Glover Road also has part power but is behind another fuse - please dispatch if not related. have advised Irene Glynn at downer hub to get Kaine to check links 8247 and 8711 and advise the outcome Used 1 x Jumper 2 x Sleeves | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.081011 | 11 | 2017 | 2016-11-14 | C | 954 | 0.081011 | 0.00097225
1 | 14525227 | 2016-11-14 06:15 | 2016-11-14 09:00 | 165 | 129 | 21340.9 | 0.064039 | 0.062877 | 0.0003871 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 803670 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 30A fuses | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.062877 | 11 | 2017 | 2016-11-14 | C | 129 | 0.062877 | 0.0003871
1 | 14525870 | 2016-11-14 06:25 | 2016-11-14 11:22 | 297 | 13 | 3863.1667 | 0.011593 | 0.011475 | 3.901e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 740093 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 50A fuses Nick attended under OMS 14533286 - crew status was cancelled due to inefrencing. OMS 14533286 ? safety disconnect on tag a15407 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.011475 | 11 | 2017 | 2016-11-14 | C | 13 | 0.011475 | 3.901e-05
1 | 14526005 | 2016-11-14 09:44 | 2016-11-14 10:27 | 43 | 133 | 5719 | 0.017161 | 0.015964 | 0.0003991 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P16274 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Check OMS: 14526238 - 11 CHURCHILL and OMS: 14531104, 14527730 \called line down contact and confirm power is on, line has been dealt with, control completed faultman, not sure whats happened here? Transformer T7/452 fuses blown with damaged holders. Outage required between ABS Q44, T15 & Q37 to replace fuse holders. Backfeed from MAG4 via 10215/2. Replace fuses and holders at Transformer T7/452 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.015964 | 11 | 2017 | 2016-11-14 | C | 133 | 0.015964 | 0.0003991
1 | 14526060 | 2016-11-14 06:33 | 2016-11-14 12:30 | 357 | 14 | 5000.3333 | 0.015005 | 0.014878 | 4.2011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 743611 | FUSE - ELEMENT/LINK (HV) | Replace: 3 x 3A fuses at Transformer 831 & 2 x 10A fuses at Fuses 8277 | F2 | DE HAVILAND NORTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.014878 | 11 | 2017 | 2016-11-14 | C | 14 | 0.014878 | 4.2011e-05
1 | 14526067 | 2016-11-14 06:33 | 2016-11-14 11:01 | 268 | 73 | 19583.4667 | 0.058766 | 0.058108 | 0.00021906 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 378127 | FUSE - ELEMENT/LINK (HV) | Customer service line safety disconnected A13206. FM believes links have gone and will contact control and complete under this OMS Replace: 2 x 15A fuses at 8435 2 x 10A fuses at 8421 2 x 3A fuses at 8471 Tony has returned and 205 Surrey Hill Rd and reconnected after SD | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.058108 | 11 | 2017 | 2016-11-14 | C | 73 | 0.058108 | 0.00021906
1 | 14526757 | 2016-11-14 07:10 | 2016-11-14 16:54 | 584 | 68 | 39713.1333 | 0.11917 | 0.11856 | 0.00020405 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 745799 | FUSE - ELEMENT/LINK (HV) | Replace 1 x 40A fuse at Fuses 8186 and 2 x 15A fuses at 8292 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.11856 | 11 | 2017 | 2016-11-14 | C | 68 | 0.11856 | 0.00020405
1 | 14526799 | 2016-11-14 07:12 | 2016-11-14 13:20 | 367 | 86 | 31610.7333 | 0.094857 | 0.094082 | 0.00025807 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P03343 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 10A fuses | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.094082 | 11 | 2017 | 2016-11-14 | C | 86 | 0.094082 | 0.00025807
1 | 14526813 | 2016-11-14 07:14 | 2016-11-15 18:10 | 2096 | 12 | 25157.4 | 0.075492 | 0.075383 | 3.6009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | NNF | NONE | Check 36 ELSHAM ROAD is related, OMS 14541164 133, 134, 144 all affected confirm with faultman 7am 16/11 emailed svs hub for update 08:15am - cancelled crews with Talia at SMC - rang each customer - power has come back on. Have asked Control to close this job as its sitting at tap extent and as 3 contacts are attached I don't want to force down and have shrapnel jobs. Switching sheet says 2 x 8 amp fuses replaced. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.075383 | 11 | 2017 | 2016-11-14 | C | 12 | 0.075383 | 3.6009e-05
1 | 14526863 | 2016-11-14 07:17 | 2016-11-14 12:06 | 289 | 33 | 9548.55 | 0.028653 | 0.028355 | 9.9026e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 758041 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 20A fuses at Fuses 8494. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.028355 | 11 | 2017 | 2016-11-14 | C | 33 | 0.028355 | 9.9026e-05
1 | 14526869 | 2016-11-14 03:34 | 2016-11-14 11:17 | 463 | 73 | 33831.85 | 0.10152 | 0.10086 | 0.00021906 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 443062 | FUSE - ELEMENT/LINK (HV) | Customer called outside 21 Rosendale Ave to advise there was a blue flash form the TX and the TX is also on a lean. Please link OMS 14524851 when closing - FM onsite verified it is part of this fault Replace 2 x 10A fuse | F3 | MOTUROA 6 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.10086 | 11 | 2017 | 2016-11-14 | C | 73 | 0.10086 | 0.00021906
1 | 14526896 | 2016-11-14 12:29 | 2016-11-16 10:30 | 2760 | 4 | 11043.4667 | 0.033139 | 0.033102 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P43021 | FUSE - ELEMENT/LINK (HV) | 15/11 4.22pm - tried to call customer no answer. e,mail sent to downer 7am 16/11 emailed svs hub for update 3x 6amp HT fuses B51 reloaded at approx 10.30am | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.033102 | 11 | 2017 | 2016-11-14 | C | 4 | 0.033102 | 1.2003e-05
1 | 14527366 | 2016-11-14 07:36 | 2016-11-14 10:39 | 182 | 296 | 19146.1833 | 0.057453 | 0.054788 | 0.00088823 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 702430 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | 11kV Line Down. Replace 4 x sleeves, 15m conductor. Outage recorded on the child job | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.054788 | 11 | 2017 | 2016-11-14 | C | 296 | 0.054788 | 0.00088823
1 | 14527454 | 2016-11-14 07:41 | 2016-11-14 10:14 | 152 | 3 | 458.25 | 0.0013751 | 0.001348 | 9.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 845812 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.001348 | 11 | 2017 | 2016-11-14 | C | 3 | 0.001348 | 9.0023e-06
1 | 14527496 | 2016-11-14 07:45 | 2016-11-14 17:20 | 574 | 25 | 14374.1667 | 0.043134 | 0.042908 | 7.5019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 739665 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuses | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.042908 | 11 | 2017 | 2016-11-14 | C | 25 | 0.042908 | 7.5019e-05
1 | 14527537 | 2016-11-14 00:06 | 2016-11-14 09:56 | 589 | 225 | 108828.6 | 0.32657 | 0.32454 | 0.0017675 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P79409 | JUMPER | CB R12 tripped L/O B Ph O/C. Line patrolled. Jumper repaired at pole P79409. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.32454 | 11 | 2017 | 2016-11-14 | C | 225 | 0.32454 | 0.0017675
1 | 14527924 | 2016-11-14 08:03 | 2016-11-14 12:30 | 266 | 1 | 266.8 | 0.00080061 | 0.000791 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 836421 | FUSE - ELEMENT/LINK (HV) | 2 x 6 amp Fuses replaced at 7719 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000791 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000791 | 3.0007e-06
1 | 14527956 | 2016-11-14 08:05 | 2016-11-14 12:40 | 274 | 95 | 26118.6667 | 0.078376 | 0.077521 | 0.00028507 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 448705 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.077521 | 11 | 2017 | 2016-11-14 | C | 95 | 0.077521 | 0.00028507
1 | 14527965 | 2016-11-14 08:06 | 2016-11-14 12:30 | 264 | 14 | 2012.2667 | 0.0060384 | 0.005912 | 4.2011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20868 | FUSE - ELEMENT/LINK (HV) | replace 2 x 6a fuses replace 1 x 63A HRC Transformer T1/352 and 1 x 63A Transformer at T1/64 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005912 | 11 | 2017 | 2016-11-14 | C | 14 | 0.005912 | 4.2011e-05
1 | 14528516 | 2016-11-14 08:20 | 2016-11-14 15:10 | 410 | 23 | 9440.7333 | 0.02833 | 0.028122 | 6.9018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 851809 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuses | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.028122 | 11 | 2017 | 2016-11-14 | C | 23 | 0.028122 | 6.9018e-05
1 | 14528551 | 2016-11-14 08:21 | 2016-11-14 17:27 | 545 | 4 | 2183.8 | 0.0065531 | 0.006517 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 731037 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuses at Fuses LI727 & 2 x 6A fuses at 8813 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.006517 | 11 | 2017 | 2016-11-14 | C | 4 | 0.006517 | 1.2003e-05
1 | 14528609 | 2016-11-14 08:22 | 2016-11-15 11:40 | 1637 | 1 | 1637.8833 | 0.0049149 | 0.004905 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | Had been linked to 14526724 - was NNF - will check with customer at 5am confirmed with customer power is on | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.004905 | 11 | 2017 | 2016-11-14 | C | 1 | 0.004905 | 3.0007e-06
1 | 14528620 | 2016-11-14 08:23 | 2016-11-15 20:00 | 2136 | 8 | 17095.8667 | 0.051301 | 0.051228 | 2.4006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 723253 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses CA426 2 x 6A EQ | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.051228 | 11 | 2017 | 2016-11-14 | C | 8 | 0.051228 | 2.4006e-05
1 | 14530404 | 2016-11-14 08:35 | 2016-11-14 14:55 | 380 | 3 | 1140.55 | 0.0034225 | 0.003395 | 9.0023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P20740 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuses | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.003395 | 11 | 2017 | 2016-11-14 | C | 3 | 0.003395 | 9.0023e-06
1 | 14530529 | 2016-11-29 08:30 | 2016-11-29 17:03 | 513 | 100 | 4700 | 0.014101 | 0.0132 | 0.00060003 | NAPA ID:25124 TP_KOPU GXP > THAMES SUB > QUEEN ST | 11 | Planned | 025124 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1818 | NONE | Open fuses FP1005 to offload TP1818 & TC5230 & install generation on LV side of TP1818 & TC5230, install temp break on 11kV at T12709 live line, access permit from temp break to FP1005 to replace pole T0450 & install new solid links IP671, close temp line break live line at T12709, uninstall generators at TP1818 & TC5230, close FP1005. Works location: Mt Pleasant Rd, Thames. WO 30002509 | F2/F3 | QUEEN ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.0066 | 5.5 | 2017 | 2016-11-29 | B | 100 | 0.0132 | 0.00060003
1 | 14530642 | 2016-11-14 18:48 | 2016-11-14 19:24 | 36 | 105 | 3780 | 0.011343 | 0.010397 | 0.00031508 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Check OMS: 14536269 - 229 Kellow Road Jeff called control to close off job - | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.010397 | 11 | 2017 | 2016-11-14 | C | 105 | 0.010397 | 0.00031508
1 | 14530701 | 2016-11-14 08:47 | 2016-11-14 14:50 | 362 | 17 | 6167.6 | 0.018508 | 0.018354 | 5.1013e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758960 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 20A DDO fuse links | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.018354 | 6.6 | 2017 | 2016-11-14 | C | 17 | 0.018354 | 5.1013e-05
1 | 14530716 | 2016-11-14 07:20 | 2016-11-14 12:00 | 279 | 43 | 12021.3667 | 0.036073 | 0.035686 | 0.00012903 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P19919 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.035686 | 11 | 2017 | 2016-11-14 | C | 43 | 0.035686 | 0.00012903
1 | 14531076 | 2016-11-14 08:51 | 2016-11-14 16:55 | 484 | 7 | 1453.0167 | 0.0043602 | 0.004297 | 2.1005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 745644 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 3A fuses | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.004297 | 11 | 2017 | 2016-11-14 | C | 7 | 0.004297 | 2.1005e-05
1 | 14531089 | 2016-11-14 18:15 | 2016-11-14 19:10 | 55 | 9 | 495 | 0.0014854 | 0.001404 | 2.7007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 860726 | CONDUCTOR - REPAIR/REHANG | Pls check same as 14540842 (432 and 459 Upland Rd) called customer to confirm power is on, she also advised line down was repaired. email sent to SMC 16/11 Own isolation and permit process on the HV to repair LV lines down. Lines repaired, relivened OK Outage recorded on the child job. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.001404 | 11 | 2017 | 2016-11-14 | C | 9 | 0.001404 | 2.7007e-05
1 | 14531110 | 2016-11-14 08:52 | 2016-11-14 14:11 | 318 | 7 | 2230.7833 | 0.0066941 | 0.006631 | 2.1005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 774847 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.006631 | 11 | 2017 | 2016-11-14 | C | 7 | 0.006631 | 2.1005e-05
1 | 14531150 | 2016-11-14 08:31 | 2016-11-14 10:20 | 109 | 18 | 1970.4 | 0.0059127 | 0.00575 | 5.4014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 836196 | FUSE - ELEMENT/LINK (HV) | called and emailed hub re 999 please check 14531717 and 14530243 also if related - spoke to both customers. Replaced 2 x 10amp HV fuses @ 7702 reloaded at 10:20am | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.00575 | 11 | 2017 | 2016-11-14 | C | 18 | 0.00575 | 5.4014e-05
1 | 14531279 | 2016-11-14 08:59 | 2016-11-15 09:51 | 1492 | 48 | 71619.2 | 0.21491 | 0.21448 | 0.00014404 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P20330 | FUSE - ELEMENT/LINK (HV) | replaced 2x 10a hv fuse links yesterday, closed off with control. End time taken from crew complete time. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.21448 | 11 | 2017 | 2016-11-14 | C | 48 | 0.21448 | 0.00014404
1 | 14532539 | 2016-11-14 09:14 | 2016-11-14 21:37 | 742 | 1 | 742.5833 | 0.0022283 | 0.002219 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 743703 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuses | F2 | DE HAVILAND NORTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002219 | 11 | 2017 | 2016-11-14 | C | 1 | 0.002219 | 3.0007e-06
1 | 14532731 | 2016-11-14 09:23 | 2016-11-15 10:01 | 1477 | 2 | 2954.8333 | 0.0088668 | 0.008848 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | Nothing replaced onsite, power was already restored by someone else | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.008848 | 11 | 2017 | 2016-11-14 | C | 2 | 0.008848 | 6.0015e-06
1 | 14532752 | 2016-11-14 09:24 | 2016-11-14 14:20 | 295 | 1 | 295.95 | 0.00088808 | 0.000879 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P21617 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuses | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000879 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000879 | 3.0007e-06
1 | 14532781 | 2016-11-14 09:24 | 2016-11-14 18:05 | 520 | 4 | 2082.0667 | 0.0062478 | 0.006211 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740659 | FUSE - ELEMENT/LINK (HV) | Advised NP SMC that this is now a lines down outside 57 Kaiapo Road Replace 2 x 3A fuse | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006211 | 11 | 2017 | 2016-11-14 | C | 4 | 0.006211 | 1.2003e-05
1 | 14532801 | 2016-11-14 09:25 | 2016-11-15 13:45 | 1700 | 21 | 35701.4 | 0.10713 | 0.10694 | 6.3016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 747156 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 10A fuse at Fuses 8195 & 3 x 2A fuses at Fuses 8159 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.10694 | 11 | 2017 | 2016-11-14 | C | 21 | 0.10694 | 6.3016e-05
1 | 14533096 | 2016-11-14 10:22 | 2016-11-14 12:04 | 101 | 1044 | 106087.8 | 0.31835 | 0.30895 | 0.0031328 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | NA | NONE | NOC opened CB U30 due to reports of lines down. Line patrolled and no lines found down in the area. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.30895 | 11 | 2017 | 2016-11-14 | C | 1044 | 0.30895 | 0.0031328
1 | 14533498 | 2016-11-14 09:03 | 2016-11-14 13:30 | 267 | 455 | 46347.9 | 0.13908 | 0.13498 | 0.0014104 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB11 opened by NOC. to repair lines down at P432176. ABS R44 defect 167-10510 | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.13498 | 11 | 2017 | 2016-11-14 | C | 455 | 0.13498 | 0.0014104
1 | 14533507 | 2016-11-14 09:47 | 2016-11-14 11:44 | 116 | 1 | 116.1833 | 0.00034864 | 0.000339 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | Replace fuses at transformer 1635. No paperwork found. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000339 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000339 | 3.0007e-06
1 | 14533523 | 2016-11-14 09:48 | 2016-11-14 13:30 | 221 | 9 | 1997.4 | 0.0059938 | 0.005912 | 2.7007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 824292 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.005912 | 11 | 2017 | 2016-11-14 | C | 9 | 0.005912 | 2.7007e-05
1 | 14533532 | 2016-11-14 09:48 | 2016-11-15 12:29 | 1601 | 2 | 1642.2167 | 0.0049279 | 0.004909 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P31653 | JUMPER | Anjay advises he has cleared this with control, replaced hv jumper isolated L35 fuses and also replaced 20a hv fuse, 12.34pm | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.004909 | 11 | 2017 | 2016-11-14 | C | 2 | 0.004909 | 6.0015e-06
1 | 14534396 | 2016-11-14 10:37 | 2016-11-14 17:25 | 408 | 1528 | 159898.25 | 0.47982 | 0.46606 | 0.0058515 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 766077 | UNKNOWN | Peat St CB7. tripped on O/C. Pothead blown at pole 766077 | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.46606 | 11 | 2017 | 2016-11-14 | C | 1528 | 0.46606 | 0.0058515
1 | 14534486 | 2016-11-14 21:56 | 2016-11-14 23:04 | 68 | 1 | 68.5 | 0.00020555 | 0.000196 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 743693 | FUSE - ELEMENT/LINK (HV) | Outage recorded on the child job. Suspect incorrect ICP data Replace 2 x fuses | F2 | DE HAVILAND NORTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000196 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000196 | 3.0007e-06
1 | 14534518 | 2016-11-30 07:51 | 2016-11-30 15:37 | 465 | 2 | 931.9667 | 0.002796 | 0.002777 | 6.0002e-06 | NAPA ID:23749 TP_MT MAUNGANUI 33 GXP > TRITON SUB > SOUTH | 11 | Planned | 023749 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9323 | NONE | Replace ABB series 1 RMU with ABB Safe link CFCF. Works location: Seeka Cold St, Mt Maunganui. WO 30019232 | F1 | SOUTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.0013885 | 5.5 | 2017 | 2016-11-30 | B | 2 | 0.002777 | 6.0002e-06
1 | 14536290 | 2016-11-14 04:29 | 2016-11-14 14:39 | 610 | 297 | 32004.2 | 0.096037 | 0.093363 | 0.00089123 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N/A - NOT APPLICABLE | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | Feeder de-energised due to lines down. Line was patrolled and no lines down located in the area. Further job located (which had been rolled up into this job and cancelled. This is shown as second step in outage information). LV Lines down. Own Isolation and AP taken by attending faultman at transformer 4084T. Materials Used: 4 x 80A, 30 x 60A, 3 x 3A HV Fuses and 3 phases 1 span and 1 x 1 span single phase. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.093363 | 11 | 2017 | 2016-11-14 | C | 297 | 0.093363 | 0.00089123
1 | 14539695 | 2016-11-14 10:45 | 2016-11-14 11:10 | 25 | 2 | 50 | 0.00015004 | 0.000132 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | K6 | FUSE - ELEMENT/LINK (HV) | 2x blown DDO fuses davw whale 660 power off last night during earth quake fuses reloaded at Replace 2 x 10A fuse | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000132 | 11 | 2017 | 2016-11-14 | C | 2 | 0.000132 | 6.0015e-06
1 | 14539760 | 2016-11-14 08:50 | 2016-11-15 09:21 | 1471 | 1 | 1471.2833 | 0.004415 | 0.004405 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Replaced 11kv through joint and termination. Power Restored Due to deterioration Nothing else repaired or replaced All surrounding assets up to Powerco standard Dispatch entered above info - FM advised he called control with this info last night. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.004405 | 11 | 2017 | 2016-11-14 | C | 1 | 0.004405 | 3.0007e-06
1 | 14540318 | 2016-11-14 11:06 | 2016-11-14 17:11 | 365 | 1 | 365.0833 | 0.0010955 | 0.001086 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T2/47 | UNKNOWN | no fault on the network fm believes may have been part of a feeder fault earlier in the day | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.001086 | 11 | 2017 | 2016-11-14 | C | 1 | 0.001086 | 3.0007e-06
1 | 14540848 | 2016-12-02 10:00 | 2016-12-02 11:05 | 65 | 35 | 2275 | 0.006825 | 0.00651 | 0.000105 | NAPA ID:25318 TP_HUIRANGI GXP > WAITARA EAST SUB > PRINCESS ST | 11 | Planned | 025318 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 764190 | NONE | to replace hv insulators on pole 764190. Works location: Turangi Rd. WO 30019382 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003255 | 5.5 | 2017 | 2016-12-02 | B | 35 | 0.00651 | 0.000105
1 | 14540902 | 2016-11-14 11:30 | 2016-11-14 13:23 | 113 | 6 | 680.2 | 0.0020411 | 0.001987 | 1.8005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 799864 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.001987 | 11 | 2017 | 2016-11-14 | C | 6 | 0.001987 | 1.8005e-05
1 | 14541003 | 2016-11-14 11:33 | 2016-11-15 10:07 | 1354 | 1 | 1354.3667 | 0.0040642 | 0.004055 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | mnn | UNKNOWN | this is related to OMS 14591988 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.004055 | 11 | 2017 | 2016-11-14 | C | 1 | 0.004055 | 3.0007e-06
1 | 14541649 | 2016-11-14 11:52 | 2016-11-14 15:16 | 203 | 282 | 36464.7 | 0.10942 | 0.10688 | 0.00084622 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 715765 | INSULATOR | CB TA1 tripped L/O, E/F. Broken insulator at Pole 715765. All repairs complete. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.10688 | 11 | 2017 | 2016-11-14 | C | 282 | 0.10688 | 0.00084622
1 | 14542003 | 2016-11-14 11:55 | 2016-11-14 16:00 | 245 | 19 | 4658.1667 | 0.013978 | 0.013807 | 5.7015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 739472 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses at 4973. Check 143 BREDOW ROAD OMS 14547478 is related 4:56pm SMC advise need FM taken from site as can't progress him to another fault | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.013807 | 11 | 2017 | 2016-11-14 | C | 19 | 0.013807 | 5.7015e-05
1 | 14542580 | 2016-11-14 16:04 | 2016-11-14 17:40 | 95 | 5 | 477.5833 | 0.0014331 | 0.001388 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 5197E | FUSE - ELEMENT/LINK (HV) | Ray Linepower - 0272431702 1 HV fuse out Replace 2 x 3A fuse | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001388 | 11 | 2017 | 2016-11-14 | C | 5 | 0.001388 | 1.5004e-05
1 | 14542711 | 2016-11-14 12:21 | 2016-11-14 14:21 | 119 | 2 | 239.4333 | 0.00071849 | 0.0007 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TP985 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse at Transformer TP985 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.0007 | 11 | 2017 | 2016-11-14 | C | 2 | 0.0007 | 6.0015e-06
1 | 14543053 | 2016-11-16 09:05 | 2016-11-16 10:50 | 105 | 16 | 1680 | 0.0050412 | 0.004897 | 4.8011e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 764189 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | John robbinson advising that there is a fault with this property but are unable to access property due to high winds and the pole being on a cliff edge, bucket required to complete this work, advise someone will attend tomorrow, customer advised. 6.57pm Robo called and advised that they have checked with bucket truck, they have found that tx needs to be replaced - they will replace the tx 3989T tomorrow 16/11 - customer to have part power overnight TX possibly feeds 10-12 people have put out emergency outage to retailers advising tx needs to be replaced tomorrow 16/11 Replaced 1x transformer and associated hardware replaced Replaced Stay wire and pineapple insulator and associated hardware 63amp fuse at pillar box - 123 Turangi Road. Cause: high winds Same transformer number kept. | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.004897 | 11 | 2017 | 2016-11-16 | C | 16 | 0.004897 | 4.8011e-05
1 | 14543213 | 2016-11-14 12:36 | 2016-11-16 11:18 | 2801 | 4 | 2778.7833 | 0.0083385 | 0.008302 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 738167 | FUSE - ELEMENT/LINK (HV) | 15/11 called customer still have no power from 14/11 @ 13:37 called through to SMC to Escalate to FRM - (Joanne) blown pole fuse outside ppty 16/11 emailed svs hub for update Reload at Fuses 4975 - 2 x 10 Amp due to earthquake. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.008302 | 11 | 2017 | 2016-11-14 | C | 4 | 0.008302 | 3.0007e-06
1 | 14544202 | 2016-11-14 09:32 | 2016-11-14 12:05 | 153 | 42 | 6435.8 | 0.019312 | 0.018934 | 0.00012603 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746737 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuse due to earthquake | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.018934 | 11 | 2017 | 2016-11-14 | C | 42 | 0.018934 | 0.00012603
1 | 14544499 | 2016-11-14 06:41 | 2016-11-14 20:30 | 829 | 17 | 14095.2667 | 0.042297 | 0.042143 | 5.1013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P42320 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.042143 | 11 | 2017 | 2016-11-14 | C | 17 | 0.042143 | 5.1013e-05
1 | 14545135 | 2016-12-01 09:45 | 2016-12-01 13:33 | 228 | 5 | 1141.25 | 0.0034238 | 0.003378 | 1.5e-05 | NAPA ID:25433 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 025433 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole D0818 | NONE | INSTALL TEMP LINE BREAK LIVE LINE AT POLE D0818, ACCESS PERMIT FROM TEMP BREAK TO REPLACE XARMS AT POLE D0819, CLOSE TEMP LINE BREAK AT POLE D0818. Works location: Tirau Rd, Maungatautari. WO 30002692 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.001689 | 5.5 | 2017 | 2016-12-01 | B | 5 | 0.003378 | 1.5e-05
1 | 14545381 | 2016-11-14 13:32 | 2016-11-16 00:10 | 2077 | 2 | 4155.1 | 0.012469 | 0.01245 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C4120 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses @ C4120 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.01245 | 11 | 2017 | 2016-11-14 | C | 2 | 0.01245 | 6.0015e-06
1 | 14547231 | 2016-11-14 13:39 | 2016-11-14 13:47 | 7 | 56 | 430.2667 | 0.0012911 | 0.000787 | 0.00016804 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000787 | 11 | 2017 | 2016-11-14 | C | 56 | 0.000787 | 0.00016804
1 | 14547618 | 2016-11-14 13:49 | 2016-11-14 15:38 | 109 | 94 | 10314.9333 | 0.030953 | 0.030106 | 0.00028207 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.030106 | 11 | 2017 | 2016-11-14 | C | 94 | 0.030106 | 0.00028207
1 | 14548126 | 2016-11-15 19:05 | 2016-11-15 20:10 | 65 | 18 | 1170 | 0.0035109 | 0.003348 | 5.4013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 746552 | JUMPER | Update : no attendance - still surging - switched everything off. Own AP At Transformer 651 Off 19:05 OFF 20:10 Replaced broken LV Jumper at T651. Materials used: LV sanger, 10A HV Fuse and Candle, 70cu Jumper. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.003348 | 11 | 2017 | 2016-11-15 | C | 18 | 0.003348 | 5.4013e-05
1 | 14548146 | 2016-12-06 13:20 | 2016-12-06 14:45 | 85 | 29 | 2465 | 0.0073946 | 0.007133 | 8.6995e-05 | NAPA ID:25280 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 025280 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5866 | NONE | Replace 11kV X arm & DDo fuses at TC5866. Works location: Tahuroa Rd, Morrinsville. WO 30027522 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0035665 | 5.5 | 2017 | 2016-12-06 | B | 29 | 0.007133 | 8.6995e-05
1 | 14551065 | 2016-11-14 05:21 | 2016-11-14 13:37 | 495 | 5 | 2479.5 | 0.0074404 | 0.007395 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 845693 | FUSE - ELEMENT/LINK (HV) | Joe found fuses blown and replaced 2 x 10A fuses. See OMS 14523166 for start time as there was a fault on feeder. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.007395 | 11 | 2017 | 2016-11-14 | C | 5 | 0.007395 | 1.5004e-05
1 | 14551191 | 2016-11-14 14:28 | 2016-11-14 15:54 | 85 | 1 | 85.9 | 0.00025777 | 0.000248 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 824036 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000248 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000248 | 3.0007e-06
1 | 14552649 | 2016-11-14 15:03 | 2016-11-14 19:14 | 250 | 1 | 250.85 | 0.00075274 | 0.000743 | 3.0007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6487 | FUSE - ELEMENT/LINK (HV) | 4679T off Fuses 6487 - 2x 6Amp Fuses, Clash due to Quake Fiona, 1x 1R, could not onsite Paul as SMC too busy, thought easier to cancel to keep things rolling, AW | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000743 | 6.6 | 2017 | 2016-11-14 | C | 1 | 0.000743 | 3.0007e-06
1 | 14552708 | 2016-12-06 10:00 | 2016-12-06 15:30 | 330 | 33 | 10890 | 0.032668 | 0.032371 | 9.8995e-05 | NAPA ID:26038 TP_HAWERA GXP > MANAIA SUB > MANAIA | 11 | Planned | 026038 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M3475 | NONE | Replace all cross arms and transformer on t.x pole M3475. Works location: South Rd, Manaia. WO 30018721 | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.016185 | 5.5 | 2017 | 2016-12-06 | B | 33 | 0.032371 | 9.8995e-05
1 | 14553079 | 2016-11-14 06:09 | 2016-11-14 15:00 | 531 | 2 | 1062.5 | 0.0031883 | 0.00317 | 6.0015e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 758742 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses and barrels. Disconnect house LV and advise to get service line repaired | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00317 | 6.6 | 2017 | 2016-11-14 | C | 2 | 0.00317 | 6.0015e-06
1 | 14553124 | 2016-11-14 15:18 | 2016-11-15 11:43 | 1225 | 1 | 1225.4667 | 0.0036774 | 0.003668 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | check all jobs on pohangina feeder before signing this off, possible fault at F20 restored power yesterday, replaced fuse at transformer | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.003668 | 11 | 2017 | 2016-11-14 | C | 1 | 0.003668 | 3.0007e-06
1 | 14553689 | 2016-11-14 15:40 | 2016-11-16 13:15 | 2734 | 1 | 2734.8167 | 0.0082066 | 0.008197 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 4260T | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | 15/11 - 3pm could not contact customer to check if power back on 16/11 7.37am called customer to see if their power is restored? customer still has no power - on pole opposite neighbours house on the pole by the tx - pole fuses have popped out 2 hanging down. 16/11 emailed svs hub for update Customer called to say that their power has been restored as they got a private contractor. They left approx 13:30 16/11/16. Not sure if Scott has attended this job. Closing off as power restored. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.008197 | 11 | 2017 | 2016-11-14 | C | 1 | 0.008197 | 3.0007e-06
1 | 14553880 | 2016-11-14 15:45 | 2016-11-15 20:58 | 1753 | 1 | 1753.35 | 0.0052614 | 0.005252 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | X107 | UNKNOWN | Contractor stated this was part of an earlier feeder fault on NO 3 LINE. Closing as NFF, HV. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.005252 | 11 | 2017 | 2016-11-14 | C | 1 | 0.005252 | 3.0007e-06
1 | 14555504 | 2016-11-14 16:52 | 2016-11-16 16:44 | 2872 | 1 | 2872.4833 | 0.0086197 | 0.00861 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733909 | FUSE - ELEMENT/LINK (HV) | check oms 14555037 Have isolated at tx, made safe will require re-visit with bucket truck to re-sleeve and re-hang conductor due to earthquake damage Email sent to Steve Oldfield follow up to have repaired no power to farm, mother at house in wheel chair needs heating, Adam from obertech confirmed LV has been repaired. Used 10 Sleeves 5m x 10mm Reloaded Relivened at 3426T 3 x 3A Fuses Caused by LV Fault | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.00861 | 11 | 2017 | 2016-11-14 | C | 1 | 0.00861 | 3.0007e-06
1 | 14555947 | 2016-11-14 17:01 | 2016-11-16 20:21 | 3080 | 1 | 3080.0333 | 0.0092425 | 0.009233 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6073 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a hv fuses @ 6073 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.009233 | 11 | 2017 | 2016-11-14 | C | 1 | 0.009233 | 3.0007e-06
1 | 14556971 | 2016-11-14 17:05 | 2016-11-14 20:00 | 175 | 236 | 24133.95 | 0.072421 | 0.070296 | 0.00070818 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Cardiff Q11. Feeder restored. Replaced 1 11kV centre phase insulator. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.070296 | 11 | 2017 | 2016-11-14 | C | 236 | 0.070296 | 0.00070818
1 | 14561829 | 2016-11-14 18:01 | 2016-11-15 20:36 | 1595 | 1 | 1595.3333 | 0.0047872 | 0.004778 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NNF | UNKNOWN | 15/11 3:35pm could not contact customer to check if power back on No fault - FM has attended and full power was restored as part of earlier outage. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.004778 | 11 | 2017 | 2016-11-14 | C | 1 | 0.004778 | 3.0007e-06
1 | 14561941 | 2016-11-14 18:09 | 2016-11-14 18:36 | 26 | 82 | 2183.9333 | 0.0065535 | 0.005815 | 0.00024606 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005815 | 11 | 2017 | 2016-11-14 | C | 82 | 0.005815 | 0.00024606
1 | 14563191 | 2016-11-14 06:45 | 2016-11-14 18:40 | 714 | 24 | 17152.4 | 0.051471 | 0.051254 | 7.2019e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 5402 | FUSE - ELEMENT/LINK (HV) | 2x 20 6.6kV Fuses blown due to clash due to Earth Quake | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.051254 | 6.6 | 2017 | 2016-11-14 | C | 24 | 0.051254 | 7.2019e-05
1 | 14563783 | 2016-11-14 19:03 | 2016-11-15 20:27 | 1524 | 512 | 110898.4167 | 0.33278 | 0.32817 | 0.0031628 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715569 & 715909 | CONDUCTOR - REPAIR/REHANG | Lines repaired @ Pole 715569 & 715909 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.32817 | 11 | 2017 | 2016-11-14 | C | 512 | 0.32817 | 0.0031628
1 | 14564708 | 2016-11-14 19:08 | 2016-11-15 19:27 | 1459 | 241 | 125496.5667 | 0.37659 | 0.37442 | 0.0011703 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 730302 | CONDUCTOR - REPAIR/REHANG | CB T31 tripped to lock out, multiple issues on the feeder as per below. alled and emailed hub re 999 OMS 14567210 Lines down 2172 Opunake road near Auroa Road Multiple works carried out on this job. 1. Poles 730302 to 303, 2x HV line down, one span, rehang 2. Pole 730305 2 x LV Pin insulators replaced. 3. Pole 730306 2 x complete HV fuse holders and bases replaced. 4. 730308 to 309. 3x LV lines down, 30m conductor, 6 links, 4x pin insulators. 5. 730309 2x LV pins replaced 6. 730310 Rebind 2x LV insulators Fiona, all 2R works. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.37442 | 11 | 2017 | 2016-11-14 | C | 241 | 0.37442 | 0.0011703
1 | 14564722 | 2016-11-14 19:20 | 2016-11-16 12:29 | 2469 | 596 | 262858.5667 | 0.78878 | 0.78341 | 0.0024546 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | CONDUCTOR - REPAIR/REHANG | OMS 14566165 2020 Opunake road Opunake - near Mangawhero road lines down due to trees across road, Fire serivce attending at 19.26 Shane from 2808 Skeet Road near intersection of Nopera Road has advised there is a line hanging and another piece of wire near the top of the pole. 2816 Skeet - has a line that has dropped and looks like it will come down. 2808 Skeet - line has come down outside property - customer advised it was made safe by some of our FM last night but wanting update on when we will be back 15/11 9.45pm - retailer called in on behalf of a customer for an ETR, advised no ETR at this stage 16/11 9:45 am retailer called again for an ETR. Advised 2 x faultman are around the area 16/11 5.40pm Lucy at hub asked for Rhys to be taken offsite as he has called control earlier with sign off details. Took him offsite | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.78341 | 11 | 2017 | 2016-11-14 | C | 596 | 0.78341 | 0.0024546
1 | 14565086 | 2016-11-14 19:22 | 2016-11-16 18:22 | 2819 | 33 | 12726.6667 | 0.03819 | 0.037892 | 9.9026e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 716846 | FUSE - ELEMENT/LINK (HV) | Bonita from Faults Line called to advise that the person has said its is popped pole fuses and for that to be looked at. check OMS 14599084 - 208B Mangawhero Road Check OMS: 14619642 - 172 MANGAWHERO email sent to SMC for update 1719 - Advised SMC this need to be upgraded LV to HV as multiple properties affected past MA117 and trees on the lines at Pole 716846 Reload at MA117 after trees removed from lines using hot sticks | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.037892 | 11 | 2017 | 2016-11-14 | C | 33 | 0.037892 | 9.9026e-05
1 | 14565326 | 2016-11-14 11:14 | 2016-11-15 10:15 | 1380 | 9 | 4202.7833 | 0.012612 | 0.01253 | 2.7007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P32023 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse and holders, 4 x 60A LV fuses | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.01253 | 11 | 2017 | 2016-11-14 | C | 9 | 0.01253 | 2.7007e-05
1 | 14565641 | 2016-11-14 19:24 | 2016-11-15 17:35 | 1330 | 298 | 169300.85 | 0.50803 | 0.50535 | 0.0012363 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733151 | CONDUCTOR - REPAIR/REHANG | OMS 14569355 - 758 SKeet Road POWER POLE VERY LOW , NEARY ON ROAD, IN DANGER OF BEING HIT trees in line at pole 733151 | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.50535 | 11 | 2017 | 2016-11-14 | C | 298 | 0.50535 | 0.0012363
1 | 14566895 | 2016-11-14 19:26 | 2016-11-15 14:56 | 1169 | 307 | 148121.1333 | 0.44448 | 0.44171 | 0.00092124 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 710500 | POLE | Multiple faults across the feeder Replaced binders, pole, blocks 2 x 3A fuses | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.44171 | 11 | 2017 | 2016-11-14 | C | 307 | 0.44171 | 0.00092124
1 | 14567212 | 2016-11-14 00:06 | 2016-11-16 17:02 | 3896 | 417 | 322424.8333 | 0.96753 | 0.96377 | 0.0024246 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 734881 | CONDUCTOR - REPAIR/REHANG | Lines down, hanging low close to ground a car can easily hit it with a car. Located half way down Maata Road. Customer cannot get past it. - Advised Irene - Chris Katene attending this as at 1201 15/11 Shed through lines. Lines repaired | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.96377 | 11 | 2017 | 2016-11-14 | C | 417 | 0.96377 | 0.0024246
1 | 14567541 | 2016-11-14 19:35 | 2016-11-14 21:20 | 104 | 305 | 25542.5333 | 0.076647 | 0.073901 | 0.00091524 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 6561 tripped B & C Phase Feeder sectionalised, no fault found | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.073901 | 11 | 2017 | 2016-11-14 | C | 305 | 0.073901 | 0.00091524
1 | 14567869 | 2016-11-14 19:36 | 2016-11-14 20:27 | 50 | 1 | 50.7667 | 0.00015234 | 0.000143 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 47 A TE NGAIO ROAD, MOUNT MAUNGANUI | UNKNOWN | Contractor has turned up and this is incorrect address. Caller is moving to new address which is not this property. Caller asked contractor to go to other property, FM advised caller that he must ring through retailer and log a job. | F3 | TAWA ST | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.000143 | 11 | 2017 | 2016-11-14 | C | 1 | 0.000143 | 3.0007e-06
1 | 14568493 | 2016-11-14 20:07 | 2016-11-15 20:00 | 1433 | 334 | 92686 | 0.27813 | 0.27512 | 0.0010023 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733630 | CONDUCTOR - REPAIR/REHANG | Customer at 403 Dalziell Road advising trees through lines appears: Lines down 3 poles damaged with damaged cross arms main line with tx/fuses? is leaning and mangled. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.27512 | 11 | 2017 | 2016-11-14 | C | 334 | 0.27512 | 0.0010023
1 | 14568810 | 2016-11-14 19:49 | 2016-11-14 22:05 | 135 | 535 | 55461.8667 | 0.16643 | 0.16161 | 0.0016054 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 772133 | CONDUCTOR - REPAIR/REHANG | CB 262 tripped Outage required between ABS 098 & 499 to repair lines bought down by trees in high winds. no backfeeds available. Repair 2 x lines down, reliven OK | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.16161 | 11 | 2017 | 2016-11-14 | C | 535 | 0.16161 | 0.0016054
1 | 14569854 | 2016-11-14 19:59 | 2016-11-15 18:40 | 1360 | 249 | 50556.6833 | 0.15171 | 0.14947 | 0.0007802 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 719912 | POLE | Low hanging lines, pole leaning. 200M east of address. caller advised that a truck would hit the lines if it came through. Tried to advise of hazard process, no answer on number given. OMs 14571615 - 834 Skeet road Lines down on corner skeet & little Tempskey OMS 14569355 758 Skeet Road - power pole very low, nearly on road in danger of being hit. Clear of job pole 719912 - straightened pole with crane. put stay on. dead ends, anchor etc. replaced 2 x LV insulators. worked through control for accessing HV | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.14947 | 11 | 2017 | 2016-11-14 | C | 249 | 0.14947 | 0.0007802
1 | 14572275 | 2016-11-14 20:40 | 2016-11-15 13:40 | 1019 | 7 | 7138.7167 | 0.021422 | 0.021358 | 2.1005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P43063 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 25A fuses | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.021358 | 11 | 2017 | 2016-11-14 | C | 7 | 0.021358 | 2.1005e-05
1 | 14572298 | 2016-11-17 16:33 | 2016-11-17 17:20 | 47 | 1 | 47 | 0.00014103 | 0.000132 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718171 | CONDUCTOR - REPAIR/REHANG | Line down - in paddock 10.40pm emailed svs hub Lines on ground - LV - conductor that feeds dead end - not going to do isolation because is still on by double pin insulator - is made safe. Rolled conductor up and put at base of pole Faultman isolated transformer 5004E to repair LV conductor from thr transformer structure. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000132 | 11 | 2017 | 2016-11-17 | C | 1 | 0.000132 | 3.0006e-06
1 | 14572368 | 2016-11-14 20:00 | 2016-11-14 21:18 | 78 | 100 | 7800 | 0.023406 | 0.022505 | 0.00030008 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G255T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | INvestigate noisy transformer G255. 14552718 11 Goodwyn Cres also affected same tx 14551231 30A surrey Cres also affected same tx 14563137 6 surrey cres also affected same tx 14561306 4 Swansea St also affected same tx | F3 | KEITH ST 24 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.022505 | 11 | 2017 | 2016-11-14 | C | 100 | 0.022505 | 0.00030008
1 | 14574121 | 2016-11-14 21:11 | 2016-11-15 15:47 | 1116 | 91 | 36603.7833 | 0.10984 | 0.10902 | 0.00044111 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 773302 | POLE | Waverley CB 693 tripped on Ph C O/C, E/F. Numerous faults on feeder beyond Fuses 2732 including pole down among others. Replace pole 773302, straighten crossarm at Pole 773324 & repair lines at pole 773285. Relivened OK | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.10902 | 11 | 2017 | 2016-11-14 | C | 91 | 0.10902 | 0.00044111
1 | 14575227 | 2016-11-14 21:23 | 2016-11-15 17:05 | 1182 | 2 | 2364.2 | 0.0070944 | 0.007076 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 731422 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuses | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.007076 | 11 | 2017 | 2016-11-14 | C | 2 | 0.007076 | 6.0015e-06
1 | 14575470 | 2016-11-14 21:27 | 2016-11-15 12:50 | 922 | 152 | 37216.5 | 0.11168 | 0.11031 | 0.00045612 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712461 | CONDUCTOR - REPAIR/REHANG | ng4 trip e/f floating conductor at pole 712461 | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.11031 | 11 | 2017 | 2016-11-14 | C | 152 | 0.11031 | 0.00045612
1 | 14577144 | 2016-11-14 22:46 | 2016-11-17 15:13 | 3866 | 2 | 7733.8 | 0.023207 | 0.023189 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704854 | CROSSARM - WHOLE ASSEMBLY | 10.47pm emailed svs hub 16/11 emailed svs hub for update 16/11 9.30pm added to spreadsheet to be sent to SMC 17/11 Retailer phoned for update and ETR. Still no power 17/11 9.55am customer called directly - advised that there is a line down since fire at pole and that this is a commercial premise requesting 2R broken x arm (HV) - FM leaving site **** customer called to advise pole is on an awful lean so will it be defected, please check with FM***** Faultman isolated lines at Fuses PU205 to replace broken cross arm on pole 704854. 1 X cross arm with all hardware. 1 X 6 amp HV fuse replaced Outage start time amended to reflect 1st call from customer. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.023189 | 11 | 2017 | 2016-11-14 | C | 2 | 0.023189 | 6.0015e-06
1 | 14577354 | 2016-11-14 22:53 | 2016-11-15 15:25 | 992 | 197 | 175315.9167 | 0.52608 | 0.52431 | 0.00094524 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 846291 | CONDUCTOR - REPAIR/REHANG | Kai Iwi CB 2032 tripped on A & B ph, O/C HV lines down at pole 846291 due to trees. 15 metres sq conductor, 6 x sleeves. NDR N200061. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.52431 | 11 | 2017 | 2016-11-14 | C | 197 | 0.52431 | 0.00094524
1 | 14578626 | 2016-11-14 19:48 | 2016-11-15 18:47 | 1379 | 275 | 47606.0333 | 0.14286 | 0.14038 | 0.0017645 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715782 | CONDUCTOR - REPAIR/REHANG | 2R works: Repairs to two sets of lines down between ABS TA127, TA126. Pole 715782. 1R works In addition due to issues at water treatment plant, fault crew also checked fuses TA141, found 2 fuses blown, reloaded. Urgent work as council were to issue a 'boil water notice' if the site could not be brought back online. Sorting blown fuses prevented this aspect from occurring. Fiona, note the two work types please, essentially two separate jobs. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.14038 | 11 | 2017 | 2016-11-14 | C | 275 | 0.14038 | 0.0017645
1 | 14579865 | 2016-11-15 | 2016-11-15 09:20 | 560 | 214 | 66688.1667 | 0.20012 | 0.19819 | 0.0003961 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 788053 | UNKNOWN | A/R A & B O/C Sectionaliser 4705 Tripped Found trees that had been in the lines but had blown clear. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.19819 | 11 | 2017 | 2016-11-14 | C | 214 | 0.19819 | 0.0003961
1 | 14580083 | 2016-11-14 20:59 | 2016-11-15 13:32 | 992 | 98 | 80932.3333 | 0.24286 | 0.24198 | 0.00057015 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755682 | CONDUCTOR - REPAIR/REHANG | New contact contact - 0273591251 blown lighten arrestor at pole 755682 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.24198 | 11 | 2017 | 2016-11-14 | C | 98 | 0.24198 | 0.00057015
1 | 14580748 | 2016-11-15 00:32 | 2016-11-15 14:31 | 839 | 412 | 133937.4 | 0.40191 | 0.3982 | 0.0014824 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731470 | CONDUCTOR - REPAIR/REHANG | lines down on Hastings Road, Mangatoki Bridge called by police officer en-route to another job, could not stay, no one to attend.Police notified council who were going to do safety measures. Caller would not leave details. P027414513. Police called 09:00 15/11/16 09:05 - Customer advised line down close to 855 Hastings Road 16:43 Bruce called to get completed off site. Advised Jared is still onsite working with control. NDR#38870 repaired using 20M conductor and 15 sleeves 16/11/2016: The following ICP has been removed from Step 5 of the Putge Steps as it is recorded under OMS 14575227 which commenced at 14/11/2016 21:22 - 15/11/2016 17:34. 0081648702PCE1B | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.3982 | 11 | 2017 | 2016-11-15 | C | 412 | 0.3982 | 0.0014824
1 | 14581204 | 2016-11-15 00:37 | 2016-11-15 19:34 | 1137 | 376 | 170668.8333 | 0.51213 | 0.50875 | 0.0013743 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 732236 - 732239 | CONDUCTOR - REPAIR/REHANG | Advised NC of sparking lines at 49 Conway Road, Eltham - informed NC 1:22am - Chris Katene on way Have spoken to ONC regarding this job. They are going to talk to Andrew regarding this. It looks like the job was rolled up to something. It is a service cable sparking that has yet to be attended, notes above indicate it was being looked at. Still needs to be attended. Owner of 44 Conway Road is Karen 020 4099 6316. Please call with findings as she is the property owner. Advised by fire service that line is down outside 51 Conway Street, Eltham Dennis Embling and Phil Webby onsite at 8.53pm Trees removed by tree crew btween poles 732236 - 732239 | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.50875 | 11 | 2017 | 2016-11-15 | C | 376 | 0.50875 | 0.0013743
1 | 14582656 | 2016-11-15 01:23 | 2016-11-15 19:01 | 1057 | 234 | 65379.5833 | 0.19619 | 0.19408 | 0.00070217 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790854 | CONDUCTOR - REPAIR/REHANG | CB 10 tripped on Ph A OC, Deft EF Lines down at pole 790854 Paul Osbourne and Tony Sinclair | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.19408 | 11 | 2017 | 2016-11-15 | C | 234 | 0.19408 | 0.00070217
1 | 14582897 | 2016-11-15 01:29 | 2016-11-15 16:11 | 881 | 1730 | 702363.9167 | 2.1076 | 2.092 | 0.0051913 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720608 | CONDUCTOR - REPAIR/REHANG | Line patrolled floating conductor found at pole 720608. line rebound in, and repaired binders @ poles 720543 , 720575 & 847246 | S4 | WAIMATE 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 2.092 | 33 | 2017 | 2016-11-15 | C | 1730 | 2.092 | 0.0051913
1 | 14585139 | 2016-11-15 01:41 | 2016-11-16 18:11 | 2429 | 26 | 63161.3667 | 0.18953 | 0.1893 | 7.8019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 844122 | CONDUCTOR - REPAIR/REHANG | trees on LINES. TREES CLEARED BY TREESCAPE. DAMAGED LINES REPAIRED AT Pole 844122 - 783160 Used 3 x Squirrell joints Note all 2R works completed under 1R Request | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.1893 | 11 | 2017 | 2016-11-15 | C | 26 | 0.1893 | 7.8019e-05
1 | 14585169 | 2016-11-15 01:43 | 2016-11-15 16:20 | 876 | 66 | 46869 | 0.14064 | 0.14005 | 0.00019805 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783651 | CONDUCTOR - REPAIR/REHANG | Police comms called through lines down at X610, opposite Kakatahi School, SH 4, P027413540 7.09am Fire service calling through advising pole is down - 04 801 0812 F2188184 - Called Tallia at SVS hub asking for eta.... SVS hub to call back with eta. 7.24am SVS hub advised eta 40mins - called fire service and advised eta. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.14005 | 11 | 2017 | 2016-11-15 | C | 66 | 0.14005 | 0.00019805
1 | 14585557 | 2016-11-15 02:11 | 2016-11-17 13:00 | 3529 | 82 | 103234.5167 | 0.30978 | 0.30904 | 0.00024906 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 794289 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | check OMS 14618312, is it related to feeder fault? Tree cleared from lines Pole 794433. Blown Transformer X1442 replaced. Used 15KVA 3 phase transformer. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.30904 | 11 | 2017 | 2016-11-15 | C | 82 | 0.30904 | 0.00024906
1 | 14585669 | 2016-11-15 00:26 | 2016-11-15 02:48 | 142 | 61 | 8675.2167 | 0.026032 | 0.025482 | 0.00018305 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB T41 tripped on A & C O/C. Possible mid span clash at poles 733111 and 733109. Residual job to be created. | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.025482 | 11 | 2017 | 2016-11-15 | C | 61 | 0.025482 | 0.00018305
1 | 14586268 | 2016-11-15 03:04 | 2016-11-15 06:23 | 198 | 440 | 55614.3333 | 0.16688 | 0.16292 | 0.0013203 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 790685 | CONDUCTOR - REPAIR/REHANG | CB 9 tripped on A & B OC. Feeder sectionalised and tree branch found on the lines, removed with hotsticks. Relivened OK Outage recorded on the child job | F3 | KIWI ST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.16292 | 11 | 2017 | 2016-11-15 | C | 440 | 0.16292 | 0.0013203
1 | 14587928 | 2016-11-15 03:38 | 2016-11-16 11:47 | 1929 | 4 | 7717.3333 | 0.023158 | 0.023121 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727174 | FUSE - ELEMENT/LINK (HV) | Reload at fuses LI148. 2 x 6A Fuses. 1 x 60A HRC at 5560E due to Weather | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.023121 | 11 | 2017 | 2016-11-15 | C | 4 | 0.023121 | 1.2003e-05
1 | 14587941 | 2016-11-15 03:47 | 2016-11-15 03:50 | 3 | 84 | 252 | 0.00075619 | 0 | 0.00025206 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | OCB R41 tripped O/C. Not patrolled. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-15 | C | 84 | 0 | 0.00025206
1 | 14589374 | 2016-11-15 04:45 | 2016-11-15 11:25 | 399 | 10 | 3996 | 0.011991 | 0.0119 | 3.0007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 771483 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuse, 1 x holder at Fuses 999 & 1 x 6A Fuse at 4139 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0119 | 11 | 2017 | 2016-11-15 | C | 10 | 0.0119 | 3.0007e-05
1 | 14589398 | 2016-11-15 04:59 | 2016-11-15 16:50 | 710 | 27 | 19184.85 | 0.057569 | 0.057325 | 8.102e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 734505 | FUSE - ELEMENT/LINK (HV) | FM called to advise that he has replaced 2x 10amp HV Fuses Switch number 5621 - reloaded at 16.50pm | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.057325 | 11 | 2017 | 2016-11-15 | C | 27 | 0.057325 | 8.102e-05
1 | 14589508 | 2016-11-15 05:16 | 2016-11-16 14:40 | 2004 | 5 | 10020 | 0.030067 | 0.030022 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 715888 715891 | CONDUCTOR - REPAIR/REHANG | will need replacing under 2R - broken cross arm,HV pin arm,broken lv conductor, binders TX 7115 Fm is isolating just now and tagging. Needs to leave site to isolate at another job. made safe for now. Found isolated TX Full power restored Replaced 5m conductor, 2x sleeves, 2x binders 4x connectors, 1 pg clamp, 3x 100A fuses, 1x 3A DDO fuse element and 1 candle Due to earthquake/wind Nothing else repaired or replaced All surrounding assets up to Powerco standard 715909 - 11kv crossarm was replaced last night | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.030022 | 11 | 2017 | 2016-11-15 | C | 5 | 0.030022 | 1.5004e-05
1 | 14589615 | 2016-11-14 16:31 | 2016-11-15 15:54 | 1403 | 2 | 1406.2167 | 0.0042197 | 0.004201 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 740012 | FUSE - ELEMENT/LINK (HV) | UPDATE, TREE THROUGH LINE, LINE DOWN - GENESIS HAS ADVISED OF SAFETY FM has advised this is part of oms 14604634 which has been closed off by control. Signed off with the same details. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.004201 | 11 | 2017 | 2016-11-14 | C | 2 | 0.004201 | 6.0015e-06
1 | 14589624 | 2016-11-17 10:50 | 2016-11-17 11:00 | 10 | 3 | 30 | 9.002e-05 | 6.3e-05 | 9.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735228 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at transformer 2762T on pole 735228 and a damaged lightning arrestor, transformer was isolated to cut lightning arrestor away. 1 X 2 amp HV fuse replaced. | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 6.3e-05 | 11 | 2017 | 2016-11-17 | C | 3 | 6.3e-05 | 9.0019e-06
1 | 14589728 | 2016-11-15 06:24 | 2016-11-16 17:15 | 2090 | 5 | 10454.25 | 0.03137 | 0.031325 | 1.5004e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | - | CONDUCTOR - REPAIR/REHANG | 12.03pm received email from retailer advising customer now has no power.. Brent Morrati has advised (he will advise his hub and get job escalated) - Asplundh called him direct and are on site, trees are connecting with lines causing them to clash, HV isolation needs to be done to safely cut trees Replaced 2x3A HV & 3x 80Amp LV fuses. Due to trees & weather Attended by Neil Woodhead. Livened 17:15 hrs on 16/11/16 17/11 10.38am Neil called to make sure he is offsite. I completed him, left job open as HV No Paperwork | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.031325 | 6.6 | 2017 | 2016-11-15 | C | 5 | 0.031325 | 1.5004e-05
1 | 14589736 | 2016-11-15 06:25 | 2016-11-15 17:05 | 640 | 191 | 81852.3667 | 0.24562 | 0.2439 | 0.00077419 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 376130 | CONDUCTOR - REPAIR/REHANG | check fuses 200 Remove trees from lines at multiple sites. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.2439 | 11 | 2017 | 2016-11-15 | C | 191 | 0.2439 | 0.00077419
1 | 14589967 | 2016-11-14 17:05 | 2016-11-14 18:09 | 64 | 102 | 6528 | 0.019589 | 0.01867 | 0.00030608 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | N/A - NOT APPLICABLE | UNKNOWN | ABS A56 opened for repairs to be made. | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.01867 | 11 | 2017 | 2016-11-14 | C | 102 | 0.01867 | 0.00030608
1 | 14590145 | 2016-12-07 10:00 | 2016-12-07 12:02 | 122 | 7 | 854 | 0.0025618 | 0.002498 | 2.0998e-05 | NAPA ID:26122 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 026122 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 904 | NONE | We are installing a new pole in between TX 904 and 11kv pole 752193 to stop wires from clashing. Works location: Maude Rd, Egmont Village. WO 30033176 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.001249 | 5.5 | 2017 | 2016-12-07 | B | 7 | 0.002498 | 2.0998e-05
1 | 14590331 | 2016-11-15 07:18 | 2016-11-15 14:00 | 402 | 8 | 3220 | 0.0096624 | 0.00959 | 2.4006e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 762052 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00959 | 6.6 | 2017 | 2016-11-15 | C | 8 | 0.00959 | 2.4006e-05
1 | 14590628 | 2016-12-01 09:21 | 2016-12-01 13:27 | 245 | 25 | 6149.5833 | 0.018449 | 0.018224 | 7.5001e-05 | NAPA ID:24979 TP_KOPU GXP > COROMANDEL SUB > KAPANGA ROAD | 11 | Planned | 024979 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole V13196 | NONE | Replace defected old wooden pole and Xarms. Pole V13196. Works location: Buffalo Heights Rd, Coromandel. WO 30025798 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.009112 | 5.5 | 2017 | 2016-12-01 | B | 25 | 0.018224 | 7.5001e-05
1 | 14590638 | 2016-11-15 16:52 | 2016-11-17 13:52 | 2699 | 5 | 13498.3333 | 0.040505 | 0.040459 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 710226 | BINDER | Replaced lv insulator 710226 hv/conductor still clashing - isolate earth at PU331 - passed through to control for HV - requesting 2R Ray rang to advise 1 conductor is sitting on the crossarm at pole 710226. He has opened Fuses PU331 for safety and another crew will be assigned to make repairs 2 X 3 amp HV fuses replace. 1 X fuse holder replaced. 1 X Binder used. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.040459 | 11 | 2017 | 2016-11-15 | C | 5 | 0.040459 | 1.5004e-05
1 | 14590725 | 2016-12-08 10:38 | 2016-12-08 11:59 | 81 | 4 | 324 | 0.00097192 | 0.000935 | 1.1999e-05 | NAPA ID:25367 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11 | Planned | 025367 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole K12394 | NONE | Replace 11KV DDO Fuse xarm liveline. Works location: Horrell Rd, Morrinsville. WO 30026234 | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0004675 | 5.5 | 2017 | 2016-12-08 | B | 4 | 0.000935 | 1.1999e-05
1 | 14590731 | 2016-11-15 07:41 | 2016-11-16 23:28 | 2387 | 1 | 2387.2333 | 0.0071635 | 0.007154 | 3.0007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3486T | FUSE - ELEMENT/LINK (HV) | 10:50am 16/11/2016 - customer called for update - reports "is only a pole fuse out, please attend asap and pop the fuses back in" Has had no power since 7:40am 15/11/2016 Emailed SMC 10:53am 16/11/2016 16/11/16 Retailer called and wanted an update still no further action taken have again re-escalated replaced 3x 3a hv fuses @ 3486T Job wont restore | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.007154 | 6.6 | 2017 | 2016-11-15 | C | 1 | 0.007154 | 3.0007e-06
1 | 14590958 | 2016-11-15 14:06 | 2016-11-15 14:09 | 3 | 52 | 164.6667 | 0.00049412 | 0 | 0.00015604 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 721393 | BINDER | CB 7 - Line patrol. CB 7 tripped when relivening the sub after a 33kV fault caused the loss of supply to the entire sub. Outage stages from 07:43 to 12:45 will be recorded on 33kV fault. Outages from 14:06 recorded on child job. Replace 1 x binder at Pole 721393. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-15 | C | 52 | 0 | 0.00015604
1 | 14591110 | 2016-11-16 10:35 | 2016-11-16 12:15 | 100 | 1 | 100 | 0.00030007 | 0.000291 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 717238 | CONDUCTOR - REPAIR/REHANG | Disconnect for safety tag A1729. Advised FM to call Control as HV line has been affected Tamie worked through control and replaced x3 3amp HV fuses ( they have the paper work for this. At the HV pole there was x1 phse down on 1 span, used 50 meters of 16ml bare conductor rehung and resagged the HV line the LV pole down due to the wind blowing the farmers shed into both HV and LV lines replaced LV pole used: 9.5 m pole, 2 LV cross arms, 12 meters of Bear conductor, also repaired x2 LV u/g cables used x4 core boots, x10 meters of 16ml sleeves, 24meters of PVC 16ml conductor at the base of the pole installed a round block and 900 block also installed a new stay and anchor old pole # 717238 new pole # 450407 at another pole 717237 installed a 900 block at the bottom of the pole and replaced x2 LV crossarms NDR # N100248 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000291 | 11 | 2017 | 2016-11-16 | C | 1 | 0.000291 | 3.0006e-06
1 | 14591186 | 2016-12-01 09:35 | 2016-12-01 14:42 | 307 | 65 | 19955 | 0.059866 | 0.059281 | 0.000195 | NAPA ID:25608 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 025608 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC2052 | NONE | Replace ABS IC2502 Change Xarms Various Sites also change Delta Insulators 32 sites. Works location: Back Miranda Rd. WO 3033365 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.029641 | 5.5 | 2017 | 2016-12-01 | B | 65 | 0.059281 | 0.000195
1 | 14591191 | 2016-11-15 08:01 | 2016-11-15 10:11 | 130 | 62 | 8070.3333 | 0.024217 | 0.023658 | 0.00018605 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 836859 | NONE | Branch removed from lines using hot sticks, relivened OK | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.023658 | 11 | 2017 | 2016-11-15 | C | 62 | 0.023658 | 0.00018605
1 | 14591317 | 2016-11-15 08:05 | 2016-11-16 14:50 | 1844 | 2 | 3689.5333 | 0.011071 | 0.011053 | 6.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 759358 | FUSE - ELEMENT/LINK (HV) | Reload at 5707 2 x 3A EQ | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.011053 | 11 | 2017 | 2016-11-15 | C | 2 | 0.011053 | 6.0014e-06
1 | 14591386 | 2016-11-15 11:56 | 2016-11-15 13:00 | 64 | 3 | 192 | 0.00057614 | 0.000549 | 9.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 810213 | NONE | Outage required past fuses 1209 to remove trees from lines using hot sticks. Outage recorded on child job, possible incorrect ICP data. Outage step has been removed from this job as the correct transformer shown under child job 14604213. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.000549 | 11 | 2017 | 2016-11-15 | C | 3 | 0.000549 | 9.0022e-06
1 | 14592438 | 2016-11-15 08:30 | 2016-11-16 02:21 | 1070 | 1 | 1070.6667 | 0.0032128 | 0.003203 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8203 & 8808 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 20a @ 8203 & 2x 6a @ 8808 | F2 | KATERE 11 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.003203 | 11 | 2017 | 2016-11-15 | C | 1 | 0.003203 | 3.0007e-06
1 | 14593335 | 2016-11-15 08:47 | 2016-11-15 16:05 | 438 | 190 | 83280.1667 | 0.2499 | 0.24819 | 0.00057014 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | line patrolled by bryan stevens nothing found | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.24819 | 6.6 | 2017 | 2016-11-15 | C | 190 | 0.24819 | 0.00057014
1 | 14594349 | 2016-11-19 09:30 | 2016-11-19 11:15 | 104 | 46 | 4813.9 | 0.014444 | 0.01403 | 0.00013803 | NAPA ID:26610 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 026610 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS R42 | NONE | Replace DNO ABS R42, shutdown needed due to unsafe to do live line. Resag lines while power is off. Works location: Halls Rd, Pahiatua. WO 30035465 Only the insulators were replaced and not the ABS due to vehicle access issues. Safety Manager 681630 - Switching error | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.007015 | 5.5 | 2017 | 2016-11-19 | B | 46 | 0.01403 | 0.00013803
1 | 14594581 | 2016-11-15 09:21 | 2016-11-16 12:00 | 1598 | 4 | 6395.2667 | 0.019191 | 0.019154 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 739405 | FUSE - ELEMENT/LINK (HV) | Customer at 1765 advises fuse hanging at tx. Advised by Mercury at 16.19. 7.57pm 15/11 emailed svs hub for update -= retailer calling for update customer has no water and young children onsite 9.10 pm 15/11 - retailer called through again for customer wanting any updates. 2x 3amp hv loads at fuses 3738T reloaded 12pm Weather | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.019154 | 11 | 2017 | 2016-11-15 | C | 4 | 0.019154 | 1.2003e-05
1 | 14594668 | 2016-11-15 09:25 | 2016-11-16 02:38 | 1032 | 1 | 1032.6 | 0.0030986 | 0.003089 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 846435 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV fuses at Fuses 6769 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.003089 | 11 | 2017 | 2016-11-15 | C | 1 | 0.003089 | 3.0007e-06
1 | 14594768 | 2016-12-09 09:30 | 2016-12-09 17:21 | 471 | 174 | 21921 | 0.065757 | 0.06419 | 0.00074693 | NAPA ID:25129 TP_HINUERA GXP > BROWNE STREET SUB > TAINUI ST | 11 | Planned | 025129 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3709 | NONE | Disconnect HV Cables from TC3709 to TC3792 & TC3711. Generate TC3792 & TC3711.Re-Liven cable from IC1897 to TC3709. Terminate Cable from TC3792 onto 13143/1. Terminate cable from TC3711 onto 13143/3. Remove Generation. Works location: Rawhiti Ave, Matamata. WO 30019206 | F3 | TAINUI ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.032095 | 5.5 | 2017 | 2016-12-09 | B | 174 | 0.06419 | 0.00074693
1 | 14594989 | 2016-11-15 11:20 | 2016-11-15 13:02 | 102 | 6 | 612 | 0.0018365 | 0.001782 | 1.8004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 855128 | CROSSARM - WHOLE ASSEMBLY | Outage required past Fuses 7776 to repair lines. No backfeeds available. Lines repaired, relivened OK Replaced bolts, crossarm, braces, 3 x binders, 2 x 10A fuses | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.001782 | 11 | 2017 | 2016-11-15 | C | 6 | 0.001782 | 1.8004e-05
1 | 14595064 | 2016-11-15 09:43 | 2016-11-16 13:05 | 1642 | 3 | 4927.3 | 0.014786 | 0.014758 | 9.0022e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 762365 | FUSE - ELEMENT/LINK (HV) | Reload at 4122T 2 x 5A EQ | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.014758 | 6.6 | 2017 | 2016-11-15 | C | 3 | 0.014758 | 9.0022e-06
1 | 14595198 | 2016-12-13 09:41 | 2016-12-13 11:48 | 127 | 40 | 5080 | 0.015238 | 0.014877 | 0.00011998 | NAPA ID:25142 TP_HINUERA GXP > BROWNE STREET SUB > TAINUI ST | 11 | Planned | 025142 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3709 | NONE | Disconnect HV Cable from IC1897-TC3709 at TC3709 & re-terminate at 13143/4. Works location: Rawhiti Ave, Matamata. WO 30019206 | F3 | TAINUI ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0074385 | 5.5 | 2017 | 2016-12-13 | B | 40 | 0.014877 | 0.00011998
1 | 14596070 | 2016-11-15 10:06 | 2016-11-15 14:57 | 290 | 1 | 290.4333 | 0.00087152 | 0.000862 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | UNKNOWN | Power restored on earlier HV job 14595006. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000862 | 11 | 2017 | 2016-11-15 | C | 1 | 0.000862 | 3.0007e-06
1 | 14596656 | 2016-11-15 10:27 | 2016-11-15 21:59 | 692 | 1 | 692.6833 | 0.0020786 | 0.002069 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6742 | FUSE - ELEMENT/LINK (HV) | job came in @ 11:27am no power at cow shed - Retailer calling for an update - called /emailed SMC to follow up with FRM - sammy replaced 2x 6a HV fuses @ 6742 | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.002069 | 11 | 2017 | 2016-11-15 | C | 1 | 0.002069 | 3.0007e-06
1 | 14596814 | 2016-11-15 10:31 | 2016-11-15 10:33 | 1 | 1 | 1.6667 | 5.0012e-06 | 0 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P21586 | FUSE - ELEMENT/LINK (HV) | Found Fuses C31 open. Replace 3 x 6A fuses. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-15 | C | 1 | 0 | 3.0007e-06
1 | 14596977 | 2016-11-15 10:37 | 2016-11-15 10:45 | 8 | 2 | 16.4333 | 4.9312e-05 | 3.1e-05 | 6.0014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | P43027 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 3.1e-05 | 11 | 2017 | 2016-11-15 | C | 2 | 3.1e-05 | 6.0014e-06
1 | 14597704 | 2016-11-15 11:06 | 2016-11-16 10:52 | 1426 | 4 | 1367.4833 | 0.0041035 | 0.004067 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 778628 | FUSE - ELEMENT/LINK (HV) | Leighton did Reload at 1490. 2 x 10A due to weather. Leighton to confirm X1339 restored also. | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.004067 | 11 | 2017 | 2016-11-15 | C | 4 | 0.004067 | 1.2003e-05
1 | 14597753 | 2016-12-01 09:01 | 2016-12-01 15:21 | 380 | 79 | 30020 | 0.090062 | 0.08935 | 0.000237 | NAPA ID:24892 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024892 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses SD2-033 | NONE | Replace poles,hardware & conductor. Works location: Ross Rd, Whakamarama. WO 30017822. F Feeder auto reclosed when restoring Safety Manager 685148 due to flash over at temp links. DNO 161201 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.044675 | 5.5 | 2017 | 2016-12-01 | B | 79 | 0.08935 | 0.000237
1 | 14597876 | 2016-12-05 08:30 | 2016-12-05 10:07 | 97 | 1 | 97 | 0.00029099 | 0.000281 | 2.9998e-06 | NAPA ID:26562 TP_BUNNYTHORPE GXP > FEILDING SUB > CROWN | 11 | Planned | 026562 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/276 | NONE | Replacing T3/276. Works location: Kawakawa Rd. WO 30008316 | F2 | CROWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.0001405 | 5.5 | 2017 | 2016-12-05 | B | 1 | 0.000281 | 2.9998e-06
1 | 14597972 | 2016-11-15 11:19 | 2016-11-15 17:58 | 399 | 1 | 399.2833 | 0.0011981 | 0.001189 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 764514 | FUSE - LV ELEMENT/LINK - HRC (LV) | cut branches away from the LV and HV lines, replaced 60 amp HRC fuse at TX 4099T cause due to tree= Robo is going to talk to Irene to get Asplundh to attend and get the trees trimmed away from both the HV and LV lines as this will require a shut down to clear the trees from the lines , unsure who owners the trees. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001189 | 11 | 2017 | 2016-11-15 | C | 1 | 0.001189 | 3.0007e-06
1 | 14598081 | 2016-12-04 09:00 | 2016-12-04 15:11 | 371 | 18 | 6678 | 0.020033 | 0.019871 | 5.3999e-05 | NAPA ID:24779 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024779 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS I21 | NONE | Change 1 x H structure xarms, and 8 x xarms and 1 x H structures. Works location: Castlehill Rd. WO 30019072 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0099355 | 5.5 | 2017 | 2016-12-04 | B | 18 | 0.019871 | 5.3999e-05
1 | 14598173 | 2016-12-05 08:37 | 2016-12-05 15:42 | 425 | 5 | 2125.25 | 0.0063755 | 0.00633 | 1.4999e-05 | NAPA ID:24788 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024788 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T9/373 | NONE | Change 15 poles, Access not good, hill country. Works location: Castlehill Rd. WO 30019072 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003165 | 5.5 | 2017 | 2016-12-05 | B | 5 | 0.00633 | 1.4999e-05
1 | 14598283 | 2016-12-05 10:31 | 2016-12-05 15:37 | 306 | 4 | 1224 | 0.0036719 | 0.003635 | 1.1999e-05 | NAPA ID:25995 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | 025995 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/469 | NONE | Replace 11Kv Tranny Fuses arms & Tranny T2/469. Works location: Harts Rd, Palmerston North. WO 30031865 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0018175 | 5.5 | 2017 | 2016-12-05 | B | 4 | 0.003635 | 1.1999e-05
1 | 14599385 | 2016-11-15 12:32 | 2016-11-15 14:13 | 101 | 572 | 45555.15 | 0.1367 | 0.13155 | 0.0017164 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213743 | JUMPER | CB 7 tripped to L/O. Line sectionalised & patrolled. Jumper located in contact with crossarm at pole 213743. Removed/cleared with hot stick. All supply restored. | F3 | CENTRAL PARADE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.13155 | 11 | 2017 | 2016-11-15 | C | 572 | 0.13155 | 0.0017164
1 | 14601055 | 2016-12-08 09:15 | 2016-12-08 12:42 | 207 | 5 | 1035 | 0.0031047 | 0.003059 | 1.4999e-05 | NAPA ID:26074 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 026074 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 1433 | NONE | We are replacing TX 1433 and cross arms and upgrading earths. Works location: Upland Rd, New Plymouth. WO 30031328 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0015295 | 5.5 | 2017 | 2016-12-08 | B | 5 | 0.003059 | 1.4999e-05
1 | 14601058 | 2016-12-08 08:45 | 2016-12-08 14:20 | 335 | 39 | 13065 | 0.039192 | 0.03884 | 0.00011699 | NAPA ID:24900 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024900 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD2-101 | NONE | Replace poles,hardware & conductor. Works location: Ross Rd, Whakamarama. WO 30017822 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.01942 | 5.5 | 2017 | 2016-12-08 | B | 39 | 0.03884 | 0.00011699
1 | 14601809 | 2016-12-05 09:58 | 2016-12-05 13:13 | 195 | 47 | 9165 | 0.027494 | 0.02707 | 0.00014099 | NAPA ID:25943 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | 025943 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S333 | NONE | Replace defected 11kv strain arms. Works location: Admiral Rd, Carterton. WO 30033179 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.013535 | 5.5 | 2017 | 2016-12-05 | B | 47 | 0.02707 | 0.00014099
1 | 14601960 | 2016-12-08 10:00 | 2016-12-08 14:31 | 270 | 138 | 37363.5 | 0.11208 | 0.11084 | 0.00041397 | NAPA ID:25281 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 025281 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC1347 | NONE | Replace ABS IC1347 & 11 x X arms at various locations. Works location: Scotsman Valley Rd, Morrinsville. WO 30027522 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.055419 | 5.5 | 2017 | 2016-12-08 | B | 138 | 0.11084 | 0.00041397
1 | 14602656 | 2016-12-05 09:45 | 2016-12-05 11:43 | 118 | 15 | 1770 | 0.0053098 | 0.005174 | 4.4998e-05 | NAPA ID:26023 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | 026023 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P34430 | NONE | Replace 11KV crossarms P34430 to P34425. Works location: Rongotea Rd, Palmerston North. WO 30019117 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.002587 | 5.5 | 2017 | 2016-12-05 | B | 15 | 0.005174 | 4.4998e-05
1 | 14603036 | 2016-12-03 09:30 | 2016-12-03 11:25 | 115 | 7 | 805 | 0.002415 | 0.002351 | 2.1e-05 | NAPA ID:24917 TP_MANGAMAIRE GXP > TP_MANGAMAIRE > MANGAMUTU 1 33KV | 11 | Planned | 024917 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses R45 | NONE | To change 33kx pins and insulators and rebind in. Works location: Ridge Rd Central. WO 30033287 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0011755 | 5.5 | 2017 | 2016-12-03 | B | 7 | 0.002351 | 2.1e-05
1 | 14604370 | 2016-11-23 08:40 | 2016-11-23 16:45 | 485 | 128 | 62080 | 0.18627 | 0.18511 | 0.00038405 | NAPA ID:26643 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | 026643 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T0392 | NONE | Replace 11kV pole T0392 with new pole. Existing Fuses FP1682 to be replaced with Links IP672 (Tee-off). Connect new cable to links IP672 and Liven through to new CFC Sw/gear 13071/1. Connect existing G/M Transformer TC5227 to new Fuse/Sw 13071/2. Sw/gear 13071/3 is future OPEN point (MOTORISED). No current connection. WORKS LOCATION: Hape Rd, Thames. WO 30002509 | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.092556 | 5.5 | 2017 | 2016-11-23 | B | 128 | 0.18511 | 0.00038405
1 | 14604634 | 2016-11-15 15:39 | 2016-11-15 15:42 | 2 | 5 | 14.6667 | 4.4011e-05 | 0 | 1.5004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 740012 | FUSE - ELEMENT/LINK (HV) | Fuses 6243 found tripped on way to another job. Replace 2 x 20A fuses. Transformer 2507T was already off under a LV fault. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-15 | C | 5 | 0 | 1.5004e-05
1 | 14605302 | 2016-11-15 12:11 | 2016-11-15 18:11 | 359 | 149 | 53630.0667 | 0.16093 | 0.15959 | 0.00044711 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 284 | UNKNOWN | Neville Ashton was passing and closed on his way to another fault. No comms to site - faultman alerted to tripping by the public. Recloser 284 closed. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.15959 | 11 | 2017 | 2016-11-15 | C | 149 | 0.15959 | 0.00044711
1 | 14605380 | 2016-11-15 16:26 | 2016-11-16 11:17 | 1130 | 1 | 1130.6167 | 0.0033927 | 0.003383 | 3.0007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | Part of 14593335 power restored as part of feeder | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.003383 | 6.6 | 2017 | 2016-11-15 | C | 1 | 0.003383 | 3.0007e-06
1 | 14607347 | 2016-11-15 17:02 | 2016-11-15 19:23 | 141 | 129 | 10913.8667 | 0.03275 | 0.031588 | 0.0003871 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 735197 | CONDUCTOR - REPAIR/REHANG | 11kV CB Q31 tripped Lock out. Line Down at pole 735197 due to high winds. All works complete. | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.031588 | 11 | 2017 | 2016-11-15 | C | 129 | 0.031588 | 0.0003871
1 | 14607654 | 2016-11-15 16:57 | 2016-11-15 19:40 | 162 | 25 | 4072.0833 | 0.012219 | 0.011994 | 7.5019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.011994 | 11 | 2017 | 2016-11-15 | C | 25 | 0.011994 | 7.5019e-05
1 | 14608914 | 2016-11-15 17:20 | 2016-11-15 19:15 | 115 | 36 | 4140 | 0.012423 | 0.012098 | 0.00010803 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | MA112 | FUSE - ELEMENT/LINK (HV) | 8.19pm Hamish called to advise that they cleared this job earlier with control - Pull up one phase used approx 10m of squirrel conductor & replace 1x 10amp hv fuse reloaded 19.15pm MA112 Advised Markus of the above he advised ok for me to complete job. Part of 14596054 but was not linked when job was closed - HV fuse replaced at MA112. Signed off with the same details. | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.012098 | 11 | 2017 | 2016-11-15 | C | 36 | 0.012098 | 0.00010803
1 | 14609331 | 2016-11-15 17:58 | 2016-11-15 20:30 | 152 | 234 | 14257.4667 | 0.042783 | 0.040676 | 0.00070217 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711397 | CONDUCTOR - REPAIR/REHANG | 11kV Cb NG 2 tripped to lock out. Reported line down, Isolated via Fuses NG270. All repairs complete, rehang only | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.040676 | 11 | 2017 | 2016-11-15 | C | 234 | 0.040676 | 0.00070217
1 | 14610616 | 2016-11-15 18:39 | 2016-11-15 19:44 | 65 | 3 | 195.8 | 0.00058755 | 0.00056 | 9.0022e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V13017 | FUSE - ELEMENT/LINK (HV) | 2x2amp HV fuses blown at transformer TC1503 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.00056 | 11 | 2017 | 2016-11-15 | C | 3 | 0.00056 | 9.0022e-06
1 | 14611909 | 2016-11-15 19:37 | 2016-11-16 07:03 | 686 | 113 | 77529.3 | 0.23265 | 0.23163 | 0.00033908 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | 1x amp fuse blown at transformer TC1744. Reloaded & livened. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.23163 | 11 | 2017 | 2016-11-15 | C | 113 | 0.23163 | 0.00033908
1 | 14613049 | 2016-11-15 23:18 | 2016-11-16 01:04 | 105 | 12 | 1264.2 | 0.0037935 | 0.003685 | 3.6009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845816 | CONDUCTOR - REPAIR/REHANG | Customer has reported that the bolt is half-way out of one of the crossarms on the Tx pole (T2872 or T3145). The braces are still holding it up and he believes it is currently safe, but he is concerned that a gust of wind or a strong aftershock could bring the crossarm down. He is at the second house on the left when driving up Parera Road, past Boggy Lagoon. (06) 307 7863. Crossarm straightend, bolt replaced at pole 845816, branch removed from following pole. NDR for tree branch to follow | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.003685 | 11 | 2017 | 2016-11-15 | C | 12 | 0.003685 | 3.6009e-05
1 | 14613117 | 2016-11-15 21:31 | 2016-11-16 21:48 | 1457 | 1 | 1457.3 | 0.004373 | 0.004363 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734487 | CONDUCTOR - REPAIR/REHANG | Repaired lines beyond Pole 734487 with +/- 60m conductor and some sleeves | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.004363 | 11 | 2017 | 2016-11-15 | C | 1 | 0.004363 | 3.0007e-06
1 | 14614142 | 2016-11-15 23:47 | 2016-11-16 16:55 | 1028 | 453 | 15428.7833 | 0.046298 | 0.042219 | 0.0010893 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 79050 | CONDUCTOR - REPAIR/REHANG | TJ handed his HV permits back to Control @ 5:30 to 6pm - took him off site 16.11.16 HAVE CALLED AND LEFT MESSAGE ON ANSWER PHONE , THIS IS RELATED TO A FEEDER FAULT, CREW ENROUTE ( 01.30PM) HUGE SPAN DOWN, CONTRACTOR HOPES TO HAVE RESTORED THIS EVENING, DEPENDENT ON TERRAIN AND WEATHER CONDITIONS. ALSO CALLED NOVA FOR ALTERNATIVE NUMBER, NONE GIVEN BY CUSTOMER. Whangamomona Hotel returned my call, | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.042219 | 11 | 2017 | 2016-11-15 | C | 453 | 0.042219 | 0.0010893
1 | 14615651 | 2016-11-16 00:34 | 2016-11-16 11:40 | 666 | 1 | 666.2333 | 0.0019992 | 0.00199 | 3.0006e-06 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711032 | CONDUCTOR - REPAIR/REHANG | Section from fuses PU363 isolated due to lines down in paddock farmer has a generator running and will guide repair crew in in daylight to execute repairs | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00199 | 11 | 2017 | 2016-11-16 | C | 1 | 0.00199 | 3.0006e-06
1 | 14615908 | 2016-11-16 02:19 | 2016-11-16 05:57 | 217 | 9 | 1960.8 | 0.0058838 | 0.005802 | 2.7006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B40 | FUSE - ELEMENT/LINK (HV) | Replaced 2x20amp HV fuses blown at B40 reloaded & livened | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005802 | 11 | 2017 | 2016-11-16 | C | 9 | 0.005802 | 2.7006e-05
1 | 14616003 | 2016-11-15 21:45 | 2016-11-16 00:50 | 185 | 47 | 8695 | 0.026091 | 0.025668 | 0.00014103 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5464 | FUSE - ELEMENT/LINK (HV) | 11kV Blown Fuses at Sw/gear 5464 Isolated and cleaned LV cables and replaced HV fuses | F4 | CLOTON RD CENTRAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.025668 | 11 | 2017 | 2016-11-15 | C | 47 | 0.025668 | 0.00014103
1 | 14616122 | 2016-11-16 03:29 | 2016-11-16 06:13 | 163 | 2 | 315.8 | 0.00094762 | 0.000929 | 6.0013e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8195 & 6524 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a fuses @ 8195 & 2x 5a fuses @ 6524 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.000929 | 11 | 2017 | 2016-11-16 | C | 2 | 0.000929 | 6.0013e-06
1 | 14618300 | 2016-11-16 18:50 | 2016-11-17 11:10 | 980 | 4 | 3920 | 0.011763 | 0.011726 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 1105 | UNKNOWN | Found LV lines twisted and after repairing attempted close on 2x HV fuses . Failed due to faulty transformer bushing. Transformer 1105 was replaced. | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.011726 | 11 | 2017 | 2016-11-16 | C | 4 | 0.011726 | 1.2003e-05
1 | 14618569 | 2016-11-16 08:32 | 2016-11-16 11:18 | 166 | 1 | 166.3333 | 0.00049912 | 0.00049 | 3.0006e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | UNKNOWN | related to HV outage OMS 14593335. Not related to 14593335 as this is a different day from the history. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00049 | 6.6 | 2017 | 2016-11-16 | C | 1 | 0.00049 | 3.0006e-06
1 | 14618656 | 2016-11-16 08:42 | 2016-11-16 09:30 | 48 | 20 | 962 | 0.0028867 | 0.002706 | 6.0014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 815076 | FUSE - ELEMENT/LINK (HV) | Darrell Rothery attended. Reload at 7205 2 x 20A due to Bird Strike. Invoicing notes: Contacted Denis Rose to advise of what occurred. Denis to get JDE record raised for Downer, Poltech to submit invoice to Downer, Poco to pay via the EFSA contract | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.002706 | 11 | 2017 | 2016-11-16 | C | 20 | 0.002706 | 6.0014e-05
1 | 14618779 | 2016-11-16 08:49 | 2016-11-16 11:00 | 130 | 2 | 261.4333 | 0.00078448 | 0.000766 | 6.0013e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 823627 | FUSE - ELEMENT/LINK (HV) | LV lines down at pole 823627. Transformer was isolated to repair LV lines and install LV disconnects. Power restored @ 11:00 LV repaired using 20m x 16mm and 3 x 63A HRC fuses and carriers Reload 1 x 3A Fuses at T1547 Caused by LV Fault | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000766 | 11 | 2017 | 2016-11-16 | C | 2 | 0.000766 | 6.0013e-06
1 | 14618814 | 2016-11-30 08:45 | 2016-11-30 14:33 | 348 | 14 | 4872 | 0.014616 | 0.01449 | 4.2001e-05 | NAPA ID:26647 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 026647 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7074 | NONE | red tag poles GP. POLES TO CHANGE UNDER RED TAG.839818,839822,839823,839825,839826 4X4 ACCES ONLY NEEDS TO BE DONE WHILE GROUND CONDITIONS ALLOW. Works location: Bute Rd. WO 30033228 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.007245 | 5.5 | 2017 | 2016-11-30 | B | 14 | 0.01449 | 4.2001e-05
1 | 14619868 | 2016-11-14 20:28 | 2016-11-16 09:41 | 2233 | 1 | 2233.0167 | 0.0067008 | 0.006691 | 3.0007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715782 | CONDUCTOR - REPAIR/REHANG | Part of TAS 1 feeder fault. TA 1 tripped L/O. Lines down as per data on 14578626. Lines down - moving in the wind. No sparking. 0274946160 10.34am called Shan at hub to advise to please call customer when on way so he can show where the issue is. Customer called to advise there is another lines down near his property - advised Marc Askin to check on same property HT fault - Marc spoke to control about this and cleared it with them. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.006691 | 11 | 2017 | 2016-11-14 | C | 1 | 0.006691 | 3.0007e-06
1 | 14619935 | 2016-12-06 09:15 | 2016-12-06 14:55 | 340 | 5 | 1700 | 0.0050997 | 0.005054 | 1.4999e-05 | NAPA ID:25235 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 025235 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7456 | NONE | Replace 11kv poles and crossarms. Works location: Lennies Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002527 | 5.5 | 2017 | 2016-12-06 | B | 5 | 0.005054 | 1.4999e-05
1 | 14620376 | 2016-12-02 08:30 | 2016-12-02 14:50 | 380 | 3 | 1140 | 0.00342 | 0.003393 | 9e-06 | NAPA ID:26649 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 026649 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7076 | NONE | RED TAG POLES GP. RED TAG POLE CHANGE 839847. Works location: Bute Rd. WO 30033228 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.0016965 | 5.5 | 2017 | 2016-12-02 | B | 3 | 0.003393 | 9e-06
1 | 14620447 | 2016-11-16 09:57 | 2016-11-16 15:00 | 303 | 4 | 1212.5333 | 0.0036384 | 0.003602 | 1.2003e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2806 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Terry advise transformer T2806 is blown - Transformer T3664 is on the same property with the owners ICP 2R - To replace Transformer T2806 Used 50 KVa 2 x 6A HV Fuses | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.003602 | 11 | 2017 | 2016-11-16 | C | 4 | 0.003602 | 1.2003e-05
1 | 14620757 | 2016-12-06 09:45 | 2016-12-06 14:38 | 293 | 2 | 586 | 0.0017579 | 0.001739 | 5.9996e-06 | NAPA ID:25686 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11 | Planned | 025686 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 816074 | NONE | tree removal between poles 816074 and 816073 blue rock road martinborough. Works location: Blue Rock Rd. WO 30026281 | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.0008695 | 5.5 | 2017 | 2016-12-06 | B | 2 | 0.001739 | 5.9996e-06
1 | 14621395 | 2016-11-16 08:20 | 2016-11-16 11:38 | 198 | 67 | 11754.5167 | 0.035272 | 0.034668 | 0.00020105 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 0 | JUMPER | FM looking for fault found that there was a phase missing on the HV (16/11/2016 05.32.36AM) and requested another faultman to help locate it. Broken jumper found at ABS S531. Blown Jumper located at ABS S531. Replaced HV Fuse Links at Fuses 7283 (This was not the cause of the feeder fault). Materials Used: 1 metre of Mink Conductor and 1 x conductor joint use to repair jumper at ABS S531. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.034668 | 11 | 2017 | 2016-11-16 | C | 67 | 0.034668 | 0.00020105
1 | 14622311 | 2016-11-16 10:35 | 2016-11-16 19:39 | 543 | 1 | 543.8167 | 0.0016318 | 0.001622 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6523 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses @ 6523. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001622 | 11 | 2017 | 2016-11-16 | C | 1 | 0.001622 | 3.0006e-06
1 | 14622568 | 2016-11-16 18:15 | 2016-11-16 18:16 | 1 | 2 | 3.1667 | 9.5022e-06 | 0 | 6.0013e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | GRANT ROAD | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer is faulty C4112 - needs replacing. Craig Brogden knows about this. Hi Steph David has brought me out the paperwork for this one. It appears this tx is not used, the fuses have been out for years. Please cancel the job to have the transformer replaced until we get more info. Thanks Jo Transformer will be replaced as a planned job through the NAPA system. Steph has emailed Irene to ask her to follow up for transformer change. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-16 | C | 2 | 0 | 6.0013e-06
1 | 14623556 | 2016-12-03 08:00 | 2016-12-03 12:25 | 265 | 42 | 11130 | 0.03339 | 0.033011 | 0.000126 | NAPA ID:25597 TP_MATAROA GXP > TAIHAPE SUB > TAIHAPE TOWN NORTH | 11 | Planned | 025597 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | change xarms at pole 789319 24 huia street taihape | F2 | TAIHAPE TOWN NORTH | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.016505 | 5.5 | 2017 | 2016-12-03 | B | 42 | 0.033011 | 0.000126
1 | 14623716 | 2016-12-12 09:18 | 2016-12-12 11:40 | 142 | 1 | 142 | 0.00042594 | 0.000416 | 2.9995e-06 | NAPA ID:25657 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025657 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | REPLACE ARMS AT TE6-139 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000208 | 5.5 | 2017 | 2016-12-12 | B | 1 | 0.000416 | 2.9995e-06
1 | 14624105 | 2016-12-20 09:15 | 2016-12-20 13:37 | 262 | 14 | 3668 | 0.011001 | 0.010875 | 4.1989e-05 | NAPA ID:25666 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025666 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE6-084 | NONE | REPLACE HV ARMS. Works location: Karner Dr, Te Puke. WO 30017835 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0054375 | 5.5 | 2017 | 2016-12-20 | B | 14 | 0.010875 | 4.1989e-05
1 | 14624172 | 2016-11-16 17:50 | 2016-11-16 17:53 | 3 | 31 | 93 | 0.00027906 | 0 | 9.3021e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 841125 | NONE | Sw/Gear 8974/1 opened to remove trees from lines at pole 841125 using hot sticks. | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-11-16 | C | 31 | 0 | 9.3021e-05
1 | 14624294 | 2016-11-16 11:59 | 2016-11-16 13:11 | 72 | 301 | 12281.85 | 0.036854 | 0.034144 | 0.00090321 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 23281 | BINDER | Floating conductor replace binder at pole 23281 1 x Ali Binder | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.034144 | 11 | 2017 | 2016-11-16 | C | 301 | 0.034144 | 0.00090321
1 | 14625238 | 2016-11-16 12:03 | 2016-11-16 16:52 | 288 | 1 | 288.7667 | 0.0008665 | 0.000857 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | Reloaded relivened WH270 - no fuses used as fuses were not blown - were opened during fault sectionalising. part of HV, closing as per A. Wilson | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000857 | 11 | 2017 | 2016-11-16 | C | 1 | 0.000857 | 3.0006e-06
1 | 14625284 | 2016-11-16 12:06 | 2016-11-16 15:02 | 176 | 439 | 29813.1333 | 0.08946 | 0.085508 | 0.0013173 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36447 | CONDUCTOR - REPAIR/REHANG | CB 9 tripped on Ph A, B, & C OC Lines down between Poles P36447 & P36442 due to Bird strike Used 10m x 25mm Copper, 8 x Sleeves, & 12m of binding wire | F2 | OHAKEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.085508 | 11 | 2017 | 2016-11-16 | C | 439 | 0.085508 | 0.0013173
1 | 14625725 | 2016-11-14 18:15 | 2016-11-14 19:10 | 55 | 2 | 110 | 0.00033009 | 0.000312 | 6.0015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 745696 | CONDUCTOR - REPAIR/REHANG | LV lines down. Own isolation and AP. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000312 | 11 | 2017 | 2016-11-14 | C | 2 | 0.000312 | 6.0015e-06
1 | 14626268 | 2016-11-16 12:09 | 2016-11-16 14:55 | 166 | 1 | 166.3333 | 0.00049912 | 0.00049 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P23580 | FUSE - ELEMENT/LINK (HV) | Reload at T3/49 2 x 3A Fuses Wind | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00049 | 11 | 2017 | 2016-11-16 | C | 1 | 0.00049 | 3.0006e-06
1 | 14626458 | 2016-11-16 14:02 | 2016-11-17 10:22 | 1220 | 5 | 6100 | 0.018304 | 0.018259 | 1.5003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 733828 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 3.18pm FM called to advise that they have replaced HV lines and have worked through control. Tx 2230T will need to be replaced tomorrow. Customer at this address has been advised of this Transformer 2230T on pole 733828 was replaced, cause was when line fell down it pulled the 11KV bushing out of the transformer. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.018259 | 11 | 2017 | 2016-11-16 | C | 5 | 0.018259 | 1.5003e-05
1 | 14626566 | 2016-12-07 09:23 | 2016-12-07 15:11 | 348 | 17 | 5858 | 0.017573 | 0.017419 | 5.0996e-05 | NAPA ID:25271 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 025271 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P00058 | NONE | To cut live line gap at pole P00078 and replace 11kv pole p00058 and close live line gap. Works location: Akaroa St, Pongaroa. WO 30024619 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0087095 | 5.5 | 2017 | 2016-12-07 | B | 17 | 0.017419 | 5.0996e-05
1 | 14626988 | 2016-12-13 13:48 | 2016-12-13 14:43 | 55 | 2 | 110 | 0.00032995 | 0.000311 | 5.999e-06 | NAPA ID:26644 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026644 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4288 | NONE | To install a 400V Fuse Disconnector on TC4288. Works location: Maungatautari Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001555 | 5.5 | 2017 | 2016-12-13 | B | 2 | 0.000311 | 5.999e-06
1 | 14627015 | 2016-11-16 12:54 | 2016-11-16 16:56 | 242 | 79 | 13640.3833 | 0.040931 | 0.040219 | 0.00023705 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 10300 | CROSSARM - WHOLE ASSEMBLY | Recloser 10300 tripped on PH a OC, & E/F. Replace HV Crossarm at pole P02418 due to faulty insulator burning it. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.040219 | 11 | 2017 | 2016-11-16 | C | 79 | 0.040219 | 0.00023705
1 | 14627685 | 2016-12-07 08:49 | 2016-12-07 14:50 | 361 | 45 | 16245 | 0.048732 | 0.048326 | 0.00013499 | NAPA ID:25364 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11 | Planned | 025364 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X1756 | NONE | Replace two 11kv poles Transformer pole X1756 and links pole 838 (843711). Works location: Rangitatau East Rd, Wanganui. WO 30024971 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.024163 | 5.5 | 2017 | 2016-12-07 | B | 45 | 0.048326 | 0.00013499
1 | 14628136 | 2016-12-05 09:20 | 2016-12-05 14:13 | 293 | 7 | 2051 | 0.0061528 | 0.006089 | 2.0999e-05 | NAPA ID:26248 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 026248 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O4024 | NONE | TO REPLACE XARMS & HARDWARE AT POLES, O4024, O4023, O4022, O4021, O4020, O4019, O4018, O4017, O4016, O14378, O4014. Works location: Baigent Rd, Miranda. WO 30002293 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0030445 | 5.5 | 2017 | 2016-12-05 | B | 7 | 0.006089 | 2.0999e-05
1 | 14628145 | 2016-11-16 13:57 | 2016-11-16 16:06 | 129 | 91 | 8228.0667 | 0.02469 | 0.02387 | 0.00027306 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 443421 | UNKNOWN | Recloser 693 Flags. Found branch on line at pole 443421. Removed with hot sticks. Ph A & B & C OC roger advised this is complete | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.02387 | 11 | 2017 | 2016-11-16 | C | 91 | 0.02387 | 0.00027306
1 | 14629060 | 2016-12-05 09:00 | 2016-12-05 15:35 | 395 | 63 | 24885 | 0.074652 | 0.074085 | 0.00018899 | NAPA ID:24620 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 024620 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC409 | NONE | change ABS pole IC409, and TX structure TC3949 and change poles O1674, O1672, O1671, O1670 and 1669. Works location: Wani Rd, Kerepehi. WO 30019843 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.037042 | 5.5 | 2017 | 2016-12-05 | B | 63 | 0.074085 | 0.00018899
1 | 14629651 | 2016-11-16 14:30 | 2016-11-16 17:27 | 177 | 97 | 10688.2333 | 0.032072 | 0.031198 | 0.00029107 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 823497 | UNKNOWN | Recloser C421 tripped Ph A & C OC Patrolled & sectionalised by A Whale & L Grant. No fault found | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.031198 | 11 | 2017 | 2016-11-16 | C | 97 | 0.031198 | 0.00029107
1 | 14629842 | 2016-11-16 15:05 | 2016-11-16 17:46 | 161 | 2 | 322 | 0.00096622 | 0.000948 | 6.0013e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 441319 | POLE | Car vs Pole 441319. Used 1 x 10m Pole 3 x Pin Insulators NDR - N600011 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000948 | 11 | 2017 | 2016-11-16 | C | 2 | 0.000948 | 6.0013e-06
1 | 14631226 | 2016-12-07 09:47 | 2016-12-07 14:54 | 307 | 12 | 3688.6 | 0.011065 | 0.010957 | 3.5998e-05 | NAPA ID:26192 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 026192 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 786288 | NONE | replace rotten red tag hardwood pole 786288 moawhonga valley rd. Works location: Moawhonga Valley Rd. WO 30034759 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0054785 | 5.5 | 2017 | 2016-12-07 | B | 12 | 0.010957 | 3.5998e-05
1 | 14631247 | 2016-12-06 09:00 | 2016-12-06 15:02 | 362 | 4 | 1448 | 0.0043438 | 0.004307 | 1.1999e-05 | NAPA ID:24625 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 024625 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O1666 | NONE | change poles O1666, O1665, O1664, O1663, O1662, O1661, O1658, O1656, O1654, O1653, O1652, and O1651. Works location: Wani Rd, Kerepehi. WO 30019843 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0021535 | 5.5 | 2017 | 2016-12-06 | B | 4 | 0.004307 | 1.1999e-05
1 | 14632704 | 2016-12-07 09:00 | 2016-12-07 14:55 | 355 | 6 | 2130 | 0.0063896 | 0.006335 | 1.7999e-05 | NAPA ID:24626 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 024626 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole O1650 | NONE | change poles O1650, O1649, O1648, O1647, O1646, O1645, O13395, O1643, O1642, O1641, O1640, O1639, and O1638. Works location: Wani Rd, Kerepehi. WO 30019843 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0031675 | 5.5 | 2017 | 2016-12-07 | B | 6 | 0.006335 | 1.7999e-05
1 | 14632750 | 2016-12-02 09:12 | 2016-12-02 15:16 | 363 | 47 | 17076.6667 | 0.05123 | 0.050807 | 0.000141 | NAPA ID:25040 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 025040 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC566 | NONE | Shutdown 1 on Tainui road to replace hardware and install 2 new HV fuses. Works location: Tainui Rd, Tahuna. WO 30017834 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.025403 | 5.5 | 2017 | 2016-12-02 | B | 47 | 0.050807 | 0.000141
1 | 14633164 | 2016-12-08 09:08 | 2016-12-08 13:12 | 244 | 9 | 2196 | 0.0065875 | 0.006506 | 2.6998e-05 | NAPA ID:25044 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 025044 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1848 | NONE | Shutdown 4 on Kiwi road to replace hardware. Works location: Kiwi Rd, Morrinsville. WO 30017834 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.003253 | 5.5 | 2017 | 2016-12-08 | B | 9 | 0.006506 | 2.6998e-05
1 | 14634451 | 2016-12-09 09:21 | 2016-12-09 14:15 | 294 | 7 | 2058 | 0.0061734 | 0.00611 | 2.0998e-05 | NAPA ID:25046 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 025046 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1847 | NONE | Shutdown 5 on Tainui road to replace hardware. Works location: Tainui Rd, Morrinsville. WO 30017834 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.003055 | 5.5 | 2017 | 2016-12-09 | B | 7 | 0.00611 | 2.0998e-05
1 | 14634487 | 2016-11-17 14:50 | 2016-11-17 16:06 | 76 | 12 | 912 | 0.0027366 | 0.002628 | 3.6008e-05 | NAPA ID:26682 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 026682 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | URGENT: Storm Repairs. Replace Tx pole 614 & pole 783654. Repair Lv lines & reinstate line break at pole 783651 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001314 | 5.5 | 2017 | 2016-11-17 | B | 12 | 0.002628 | 3.6008e-05
1 | 14634636 | 2016-12-08 09:00 | 2016-12-08 14:45 | 345 | 6 | 2070 | 0.0062095 | 0.006155 | 1.7999e-05 | NAPA ID:24627 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 024627 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC409 | NONE | Run new conductor from ABS pole IC409 to pole O1663. Works location: Wani Rd, Kerepehi. WO 30019843 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0030775 | 5.5 | 2017 | 2016-12-08 | B | 6 | 0.006155 | 1.7999e-05
1 | 14634710 | 2016-11-16 15:44 | 2016-11-16 17:28 | 103 | 4 | 414.9333 | 0.0012451 | 0.001209 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716299 | FUSE - ELEMENT/LINK (HV) | Reload at T7280 2 x 3A due to LV line clash. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001209 | 11 | 2017 | 2016-11-16 | C | 4 | 0.001209 | 1.2003e-05
1 | 14635628 | 2016-11-15 08:16 | 2016-11-16 17:47 | 2011 | 11 | 22123.9333 | 0.066388 | 0.066289 | 3.3008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 733525 | POLE | Marc Askin has attended under OMS 14591667. Worked through control, HT fuse reloaded. Cross arm still needs to be replaced. Craig advised pole & crossarm needs to be defected,He has advised that it is safe and he will Amber 1 defect pole 733525 & crossarm to be replaced deterioration - all customers fed from this pole have full power | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.066289 | 11 | 2017 | 2016-11-15 | C | 11 | 0.066289 | 3.3008e-05
1 | 14635636 | 2016-11-17 10:19 | 2016-11-17 13:37 | 198 | 2 | 396 | 0.0011883 | 0.00117 | 6.0013e-06 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I12762 | CROSSARM - WHOLE ASSEMBLY | 3m rotten cross arm to be replaced at pole Pole I12762. Faultman replaced rotten cross arm holding up transformer TC750. from a wooden one to steel cross arm . 1 X cross arm replaced | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.00117 | 11 | 2017 | 2016-11-17 | C | 2 | 0.00117 | 6.0013e-06
1 | 14636321 | 2016-11-16 16:42 | 2016-11-16 18:07 | 85 | 5 | 421.0667 | 0.0012635 | 0.001218 | 1.5003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725022 | CONDUCTOR - REPAIR/REHANG | Lines down at Pole 725022 Used 3 x 10A HV Fuses 1 Span of conductor - All 3 Phases 12 x Sleeves | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001218 | 11 | 2017 | 2016-11-16 | C | 5 | 0.001218 | 1.5003e-05
1 | 14636887 | 2016-11-16 16:55 | 2016-11-16 20:00 | 185 | 1 | 185.0333 | 0.00055523 | 0.000546 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a HV Fuses @ I26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.000546 | 11 | 2017 | 2016-11-16 | C | 1 | 0.000546 | 3.0006e-06
1 | 14637104 | 2016-11-16 17:06 | 2016-11-16 21:00 | 234 | 501 | 17402.1333 | 0.052219 | 0.047708 | 0.0022685 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 393882 | UNKNOWN | Line sectionalised & patrolled. Became apparent during sectionalising there was two separate faults beyond recloser RP09. This fault was identified to be a faulty lightning arrestor on pole 220296. Line isolated at ABS SD4-066 & links 9462/4 to cut faulty arrestor away from line. All supply restored following repairs. Other fault beyond sectionaliser 9876/2 reported on OMS 14643193 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.047708 | 11 | 2017 | 2016-11-16 | C | 501 | 0.047708 | 0.0022685
1 | 14638084 | 2016-11-16 17:27 | 2016-11-17 12:05 | 1117 | 4 | 4470.9333 | 0.013416 | 0.013379 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 731981 | FUSE - ELEMENT/LINK (HV) | Rhys unable to gain access through horse paddocks and gates that he couldn't open. Tried calling customer but no response. Crew replacement in for AM. FM confirmed no pole down in this area Reload at Fuses 5768 2 x 3A Weather | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.013379 | 11 | 2017 | 2016-11-16 | C | 4 | 0.013379 | 1.2003e-05
1 | 14638114 | 2016-11-16 17:29 | 2016-11-16 23:10 | 341 | 323 | 72803.6 | 0.21846 | 0.21555 | 0.00096922 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9274/2 | RECLOSER (HV) | 16/11 9.50pm - Contractor called in to Control with this and were told too busy and to call Dispatch. Have created a new OMS for work needing done tomorrow OMS 14643193: 11kV line down 2 people needed huge span across a gulley with 33 kV above it. Cant repair tonight - needs everybody on it tomorrow. Put Lance and Hayden onsite 17/11 Not sure if notes above are attached to correct OMS?? Recloser 9274/2 tripped to L/O. Following line sectionalising and patrolling, it was identified the fault was within the recloser itself. Recloser isolated by opening links 9274/6 and creating line break on other side of it. All supply restored following isolation via by pass ABS 9274/1. DNO created to have recloser removed/replaced. | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.21555 | 11 | 2017 | 2016-11-16 | C | 323 | 0.21555 | 0.00096922
1 | 14638957 | 2016-11-16 17:38 | 2016-11-16 21:10 | 211 | 2 | 423.2 | 0.0012699 | 0.001251 | 6.0013e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7873 | FUSE - ELEMENT/LINK (HV) | 7873 2 x 10 amp fuses replaced at fuses 7873 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.001251 | 11 | 2017 | 2016-11-16 | C | 2 | 0.001251 | 6.0013e-06
1 | 14640631 | 2016-11-16 19:47 | 2016-11-17 12:33 | 1006 | 91 | 24756.7 | 0.074287 | 0.073468 | 0.00018904 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 816988 | CONDUCTOR - REPAIR/REHANG | FM to head to sectionalizer C637 on Hinakura Road - SMC advised 2 x A/R on recloser 8156/2. Sectionaliser C637/2 found open. Line sectionalised & patrolled. Line down located beyond ABS s1204. Unable to carry out repairs due to terrain etc. Supply left off overnight to all customers beyond ABS S1204. 2 r requested to completed repairs 17/11/16 Remove trees from lines and repair 1 x deadend NDR 34895 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.073468 | 11 | 2017 | 2016-11-16 | C | 91 | 0.073468 | 0.00018904
1 | 14641065 | 2016-11-16 20:25 | 2016-11-16 21:21 | 56 | 2 | 112.0667 | 0.00033628 | 0.000318 | 6.0013e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6942 | UNKNOWN | CB 6942 trippeed on B phase O/C & E/F and clearance received from cheal to close . suspect tripped due to a problem @ cheal site | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000318 | 11 | 2017 | 2016-11-16 | C | 2 | 0.000318 | 6.0013e-06
1 | 14641103 | 2016-11-16 20:31 | 2016-11-17 16:47 | 1215 | 167 | 46950.6 | 0.14088 | 0.13938 | 0.00078918 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 765278 | CONDUCTOR - REPAIR/REHANG | Sectionalised and patrolled found tree over lines & transformer 3168T tree crew required to remove trees and traffic management required also transformer to be replaced jumpers disconnected @ pole 765278 Line was isolated at Fuses 5214 to make a line break to transformer 3168T line was relivened, faultman returned to replace transformer 3168T & the pole, line was isolated again at Fuses 5214 to close the line break to transformer 3168T. 1 x transformer replaced. 1 X pole with all hardware. 200 meters of 16mm copper conductor used. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.13938 | 11 | 2017 | 2016-11-16 | C | 167 | 0.13938 | 0.00078918
1 | 14642679 | 2016-11-16 21:49 | 2016-11-17 11:15 | 805 | 495 | 96557 | 0.28974 | 0.28528 | 0.0014853 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835351 | CONDUCTOR - REPAIR/REHANG | CB C850 tripped to L/O. E/F flag. Line sectionalised & patrolled. Tree through line located at pole 835352. Unable to carry out repairs tonight due to damage caused. Line left isolated at fuses 7125, supply to transformer T529 to be left off overnight (1 customer only) 2 r requested for repairs 17/11/16. NDR to be submitted by Downers | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.28528 | 11 | 2017 | 2016-11-16 | C | 495 | 0.28528 | 0.0014853
1 | 14643193 | 2016-11-17 11:39 | 2016-11-17 12:26 | 47 | 25 | 1177.9167 | 0.0035345 | 0.003309 | 7.5016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 341685 | CONDUCTOR - REPAIR/REHANG | 11kV line down 2 people needed huge span across a gully with 33 kV above it. Cant repair tonight - needs everybody on it tomorrow. Put Lance and Hayden onsite 17/11 Following trip on recloser RP09, (OMS 14634770) second fault was identified on line beyond it. This one was beyond sectionasliser 9876/2. Broken conductor located at pole 341685 across large gully. Temp line breaks created at pole's 344726 & 341685 leaving faulted span isolated overnight with all other supply restored. Unable to carry out repairs tonight due to terrain and 33kV line above. Isolation's to create line breaks were at links 9954/4 & links SE5-030. 2 r requested to complete repairs 17/11/16 PLEASE CHECK OMS: 14649892 - 455 ROCKY CUTTING | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.003309 | 11 | 2017 | 2016-11-17 | C | 25 | 0.003309 | 7.5016e-05
1 | 14646230 | 2016-11-17 03:02 | 2016-11-17 06:30 | 208 | 26 | 4942.5667 | 0.014831 | 0.014596 | 7.8017e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 844137 | CONDUCTOR - REPAIR/REHANG | Recloser 2713 ARC & tripped O/C sectionalised and found branch on line @ pole 844137 and removed using hot sticks | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.014596 | 11 | 2017 | 2016-11-17 | C | 26 | 0.014596 | 7.8017e-05
1 | 14646354 | 2016-11-17 04:02 | 2016-11-17 06:03 | 121 | 209 | 13142.0667 | 0.039435 | 0.037553 | 0.00062714 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 645 | FUSE - ELEMENT/LINK (HV) | Opened CB 4566 to Replace 2x hv fuses @ 645 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.037553 | 11 | 2017 | 2016-11-17 | C | 209 | 0.037553 | 0.00062714
1 | 14646391 | 2016-11-17 04:41 | 2016-11-17 07:25 | 164 | 21 | 3446.45 | 0.010342 | 0.010152 | 6.3014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 737151 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 4980 2 x 8A Weather | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.010152 | 11 | 2017 | 2016-11-17 | C | 21 | 0.010152 | 6.3014e-05
1 | 14646405 | 2016-11-17 04:42 | 2016-11-17 06:58 | 135 | 31 | 4206.7 | 0.012623 | 0.012343 | 9.302e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 764777 | FUSE - ELEMENT/LINK (HV) | TJ confirmed other contacts restored Reload at fuses 5301 2 x 10A Lightning | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.012343 | 11 | 2017 | 2016-11-17 | C | 31 | 0.012343 | 9.302e-05
1 | 14647257 | 2016-12-09 09:00 | 2016-12-09 15:25 | 385 | 36 | 3960 | 0.011879 | 0.011554 | 0.00010799 | NAPA ID:24662 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 024662 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O1663 | NONE | Run new conductor from pole O1663 to pole O13393. Works location: Wani Rd, Kerepehi. WO 30019843 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.005777 | 5.5 | 2017 | 2016-12-09 | B | 36 | 0.011554 | 0.00010799
1 | 14647476 | 2016-11-17 08:35 | 2016-11-17 11:55 | 199 | 1 | 199.55 | 0.00059878 | 0.000589 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T21616 | FUSE - ELEMENT/LINK (HV) | Reload at fuses M83 3 x 3A caused by line clash. Jeff roberts reported that Pole T21616 is on a lean causing Lines to hang low and clash in the wind. Jeff has defected this leaning pole | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000589 | 11 | 2017 | 2016-11-17 | C | 1 | 0.000589 | 3.0006e-06
1 | 14647578 | 2016-12-06 08:58 | 2016-12-06 14:42 | 344 | 115 | 39560 | 0.11867 | 0.11764 | 0.00034498 | NAPA ID:25633 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | 025633 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 222870 | NONE | REPOLE AND RECON FEEDER. Works location: Te Puke Quarry Rd. WO 30019857 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.058819 | 5.5 | 2017 | 2016-12-06 | B | 115 | 0.11764 | 0.00034498
1 | 14647856 | 2016-11-16 12:00 | 2016-11-16 21:00 | 540 | 8 | 4320 | 0.012963 | 0.01289 | 2.4005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5483 | FUSE - ELEMENT/LINK (HV) | reload reliven 2x fuses 6 Amps, cause due to wind. Jo, will need to change SAIDI times as was off for unknown time???? but relivened at approx 2100 Hrs on the 16th. Off time is only an estimate | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.01289 | 11 | 2017 | 2016-11-16 | C | 8 | 0.01289 | 2.4005e-05
1 | 14648078 | 2016-11-17 11:04 | 2016-11-17 12:43 | 99 | 34 | 3366 | 0.0101 | 0.009794 | 0.00010202 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P07988 | CONDUCTOR - REPAIR/REHANG | Conductor down at Pole P07988. 1m 25mm Cu and 2 sleeves. ABS R27 and R29 opened for isolation. Check 252 Arapata Rd OMS 14648380 is related. 1M 25mm Copper 2x Sleeves | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.009794 | 11 | 2017 | 2016-11-17 | C | 34 | 0.009794 | 0.00010202
1 | 14648317 | 2016-11-17 09:52 | 2016-11-18 12:36 | 1604 | 3 | 4812.05 | 0.014439 | 0.014412 | 9.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 739352 | CONDUCTOR - REPAIR/REHANG | Jade reports there is a tree through the lines and will need tree contractors to remove. He has isolated at Fuses 8834 for safety until repairs can be made. Faultman removed tree away from lines at pole 739352. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.014412 | 11 | 2017 | 2016-11-17 | C | 3 | 0.014412 | 9.0019e-06
1 | 14648343 | 2016-11-17 09:55 | 2016-11-17 12:09 | 134 | 284 | 11731.3 | 0.035202 | 0.032645 | 0.00085219 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V13629 | JUMPER | Jumper replaced at pole V13629 (TC1164) | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.032645 | 11 | 2017 | 2016-11-17 | C | 284 | 0.032645 | 0.00085219
1 | 14648372 | 2016-12-06 10:00 | 2016-12-06 11:00 | 60 | 54 | 3240 | 0.0097195 | 0.009233 | 0.00016199 | NAPA ID:25632 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > GLOUCESTER RD | 11 | Planned | 025632 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S4582 | NONE | clean repair hv lv connectitions. Works location: Grabella Place, Tauranga. OW 10162937 | F3 | GLOUCESTER RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.0046165 | 5.5 | 2017 | 2016-12-06 | B | 54 | 0.009233 | 0.00016199
1 | 14648744 | 2016-12-08 07:45 | 2016-12-08 07:48 | 3 | 49 | 147 | 0.00044096 | 0 | 0.00014699 | NAPA ID:26151 TP_KINLEITH GXP > BAIRD ROAD SUB > DALMENY ST | 11 | Planned | 026151 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Safelink 9896 | NONE | retrofit scada automation to rmu abb safelink 9896. install temporary generation at transformer tc4241 Early due to school and remove late due to school. Works location: Bridge St. WO 30019211 Power off at Transformer 07:45 to install generator, Generator in service at 07:48 | F2/F3 | DALMENY ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-12-08 | B | 49 | 0 | 0.00014699
1 | 14648852 | 2016-12-06 08:30 | 2016-12-06 16:57 | 507 | 5 | 2535 | 0.0076046 | 0.007559 | 1.4999e-05 | NAPA ID:24793 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV I19 | NONE | Change 15 poles, Access not good, hill country. Works location: Castlehill Rd. WO 30019072 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0037795 | 5.5 | 2017 | 2016-12-06 | B | 5 | 0.007559 | 1.4999e-05
1 | 14649093 | 2016-12-07 08:48 | 2016-12-07 16:08 | 439 | 5 | 2198.4167 | 0.0065948 | 0.006549 | 1.4999e-05 | NAPA ID:24796 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024796 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV I19 | NONE | Change 15 poles, Access not good, hill country. Works location: Castlehill Rd. WO 30019072 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0032745 | 5.5 | 2017 | 2016-12-07 | B | 5 | 0.006549 | 1.4999e-05
1 | 14649317 | 2016-12-01 10:15 | 2016-12-01 13:40 | 205 | 1 | 205 | 0.00061501 | 0.000606 | 3e-06 | NAPA ID:26027 TP_BUNNYTHORPE GXP > SANSON SUB > OHAKEA | 11 | Planned | 026027 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Felling the tree on this spur line | F2 | OHAKEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000303 | 5.5 | 2017 | 2016-12-01 | B | 1 | 0.000606 | 3e-06
1 | 14649608 | 2016-12-05 09:35 | 2016-12-05 13:50 | 255 | 1 | 255 | 0.00076497 | 0.000755 | 2.9998e-06 | NAPA ID:26658 TP_TAURANGA 33 GXP > KAURI POINT > LINDERMANN RD | 11 | Planned | 026658 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 204492 | NONE | REPLACE ARMS ON SPUR AND INSTALL SPUR FUSES FP1854 AT POLE 204492. Works location: Willoughby Rd, Katikati. WO 30034938 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.0003775 | 5.5 | 2017 | 2016-12-05 | B | 1 | 0.000755 | 2.9998e-06
1 | 14649806 | 2016-11-17 11:49 | 2016-11-17 13:39 | 109 | 8 | 876.1333 | 0.002629 | 0.002556 | 2.4005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B12450 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.002556 | 11 | 2017 | 2016-11-17 | C | 8 | 0.002556 | 2.4005e-05
1 | 14650028 | 2016-12-06 09:00 | 2016-12-06 14:50 | 350 | 79 | 27650 | 0.082946 | 0.082234 | 0.00023699 | NAPA ID:24897 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | 024897 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace poles,hardware & conductor plus install Links TEMP67 at Pole 210017. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.041117 | 5.5 | 2017 | 2016-12-06 | B | 79 | 0.082234 | 0.00023699
1 | 14650226 | 2016-11-17 14:30 | 2016-11-17 14:50 | 20 | 3 | 60 | 0.00018004 | 0.000153 | 9.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716051 | BINDER | Repair 1 x binder past fuses 12149. Pole 716051. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000153 | 11 | 2017 | 2016-11-17 | C | 3 | 0.000153 | 9.0019e-06
1 | 14652871 | 2016-12-02 08:45 | 2016-12-02 17:00 | 495 | 12 | 5940 | 0.01782 | 0.017712 | 3.6e-05 | NAPA ID:24909 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024909 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 268722 | NONE | Crossarm Replacement: Pole 268722. Reconductor 381405 to 268728. Conductor connection for TEMP98 ABS & SC2-120. Works location: Esdaile Rd. WO 30019861 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.008856 | 5.5 | 2017 | 2016-12-02 | B | 12 | 0.017712 | 3.6e-05
1 | 14655418 | 2016-11-17 18:05 | 2016-11-17 19:25 | 80 | 23 | 1840 | 0.0055212 | 0.005314 | 6.9015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1477 | JUMPER | Faultman found broken jumper at Fuses FC1477 & a damaged fuse holder, line was isolated at ABS's 829, 2505 & 2649 to make the repairs. Jumper repaired and 1 x HV fuse base replaced. All supply restored. Materials required - 1 x HV fuse base & carrier, 1 x 3 amp fuse, 1 x ABS padlock also required for ABS 829 (had to be cut off) | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.005314 | 11 | 2017 | 2016-11-17 | C | 23 | 0.005314 | 6.9015e-05
1 | 14655591 | 2016-12-09 12:45 | 2016-12-09 15:05 | 140 | 7 | 980 | 0.0029397 | 0.002876 | 2.0998e-05 | NAPA ID:26651 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 026651 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 839754 | NONE | red tag poles gp. change red tag pole 839656 on same day as pole 839754 but at different times for isolation as they have sepperate isolation points. Works location: Adams Peak Rd. WO 30033228 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.001438 | 5.5 | 2017 | 2016-12-09 | B | 7 | 0.002876 | 2.0998e-05
1 | 14655672 | 2016-12-09 08:45 | 2016-12-09 14:50 | 365 | 3 | 1095 | 0.0032847 | 0.003257 | 8.9991e-06 | NAPA ID:26650 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 026650 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 839744 | NONE | RED TAG POLES GP pin poles 839744 839745. RED TAG POLE CHANGE OF 839754 TX 77. Works location: Masterton Castlepoint Rd. WO 30033228 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.0016285 | 5.5 | 2017 | 2016-12-09 | B | 3 | 0.003257 | 8.9991e-06
1 | 14655675 | 2016-12-09 08:07 | 2016-12-09 15:19 | 432 | 25 | 3393 | 0.010178 | 0.009953 | 7.4993e-05 | NAPA ID:25638 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | 025638 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 222957 | NONE | REPOLE AND RECON FEEDER INSTALL ABS TEMP21 AT POLE 222957 DURING SHUTDOWN. Works location: Te Puke Quarry Rd. WO 30019857 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.0049765 | 5.5 | 2017 | 2016-12-09 | B | 25 | 0.009953 | 7.4993e-05
1 | 14655788 | 2016-12-08 01:00 | 2016-12-08 01:01 | 1 | 2 | 2 | 5.9995e-06 | 0 | 5.9995e-06 | NAPA ID:26018 TP_WANGANUI GXP > HATRICKS WHARF SUB > OPERA HOUSE | 11 | Planned | 026018 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 4627 | NONE | Non Resin DGS Mtce. Works location: St Hill St. WO 30021058 | F2 | OPERA HOUSE | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-12-08 | B | 2 | 0 | 5.9995e-06
1 | 14655843 | 2016-12-08 02:00 | 2016-12-08 03:46 | 106 | 3 | 318 | 0.00095392 | 0.000926 | 8.9992e-06 | NAPA ID:26025 TP_WANGANUI GXP > HATRICKS WHARF SUB > OPERA HOUSE | 11 | Planned | 026025 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 4175 | NONE | Non Resin DGS Mtce and guroflexing of bus connection. Works location: St Hill St. WO 30021058 | F2 | OPERA HOUSE | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.000463 | 5.5 | 2017 | 2016-12-08 | B | 3 | 0.000926 | 8.9992e-06
1 | 14655853 | 2016-12-09 10:27 | 2016-12-09 13:27 | 180 | 1 | 180 | 0.00053995 | 0.00053 | 2.9997e-06 | NAPA ID:26033 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 026033 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 4632W | NONE | Replace transformer and X arms on 4632W. Works location: Rangikura Rd, Waverley. WO 30027080 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000265 | 5.5 | 2017 | 2016-12-09 | B | 1 | 0.00053 | 2.9997e-06
1 | 14655914 | 2016-12-06 09:19 | 2016-12-06 17:15 | 476 | 37 | 17612 | 0.052833 | 0.0525 | 0.00011099 | NAPA ID:24920 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024920 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 268715 | NONE | Crossarm replacement: 268715, 268720. Reconductor: 268712 to 381405. Connect conductor to TEMP96 ABS & TEMP98 ABS. Works location: Esdaile Rd. WO 30019861 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.02625 | 5.5 | 2017 | 2016-12-06 | B | 37 | 0.0525 | 0.00011099
1 | 14657854 | 2016-11-17 15:44 | 2016-11-17 16:40 | 56 | 29 | 1625.45 | 0.0048774 | 0.004616 | 8.7019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735977 | JUMPER | Faultman received a report of a broken jumper on pole 735977, line was isolated at ABS's 5693 & 4833 and Links 4813 to repair the jumper. 1 X line connector used. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.004616 | 11 | 2017 | 2016-11-17 | C | 29 | 0.004616 | 8.7019e-05
1 | 14658524 | 2016-11-17 18:02 | 2016-11-17 20:10 | 128 | 1 | 128 | 0.00038408 | 0.000375 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 265 CAVES ROAD, MASTERTON | CONDUCTOR - REPAIR/REHANG | Lines down because of trees - unknown if this is network line of service cable Paul not on site so unable to complete hazard process Advised SMC of 999 Transformer T521 isolated to repair LV lines. Restored at completion | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000375 | 11 | 2017 | 2016-11-17 | C | 1 | 0.000375 | 3.0006e-06
1 | 14658817 | 2016-11-17 17:10 | 2016-11-17 17:28 | 18 | 5 | 90 | 0.00027006 | 0.000225 | 1.5003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5295 | JUMPER | Faultman isolated transformer T5295 to repair 11KV jumper & reterminate LV line. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000225 | 11 | 2017 | 2016-11-17 | C | 5 | 0.000225 | 1.5003e-05
1 | 14660222 | 2016-11-17 19:02 | 2016-11-17 20:15 | 72 | 8 | 579.2 | 0.001738 | 0.001665 | 2.4005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773682 | BINDER | FM working in the area noticed a floating HV conductor at Pole 773682. Work area isolated at Fuses 2584 & conductor & the one next to it rebound in. Materials used: 4mtrs of Ali Binder | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001665 | 11 | 2017 | 2016-11-17 | C | 8 | 0.001665 | 2.4005e-05
1 | 14660235 | 2016-11-17 19:03 | 2016-11-17 22:55 | 231 | 307 | 23007.9833 | 0.069039 | 0.066275 | 0.0009242 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 4 A/R, E/F, O/C. Feeder auto reclosed again so faultman was requested to patrol feeder. Feeder split in half and backfed via ABS PU203. Feeder stopped auto reclosing, probably only due to the drop off in wind speed. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.066275 | 11 | 2017 | 2016-11-17 | C | 307 | 0.066275 | 0.0009242
1 | 14661437 | 2016-11-17 20:48 | 2016-11-17 23:39 | 170 | 3 | 511.3 | 0.0015342 | 0.001507 | 9.0019e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP894 | FUSE - ELEMENT/LINK (HV) | 2 x 8 amp HV fuses replaced at fuses FP894 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001507 | 11 | 2017 | 2016-11-17 | C | 3 | 0.001507 | 9.0019e-06
1 | 14663125 | 2016-11-17 21:25 | 2016-11-18 13:01 | 936 | 4 | 3744 | 0.011234 | 0.011198 | 1.2003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 2552 | FUSE - ELEMENT/LINK (HV) | FM attended & reported to control that 2x HV fuses at Fuses 2552 were blown due to trees on the lines. The other fuse was removed to make the area safe. On discussion with tree contractor he decided it was not safe to attend during darkness. FM notified customer that power would be left off overnight as per NC instruction. Note: Trees owned by customer & affects transformers on his farm. Trees removed CACD 47889. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.011198 | 11 | 2017 | 2016-11-17 | C | 4 | 0.011198 | 1.2003e-05
1 | 14663209 | 2016-11-17 21:57 | 2016-11-17 23:00 | 62 | 1 | 62.5833 | 0.00018779 | 0.000178 | 3.0006e-06 |  | 0.41499999999999998 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2642 | FUSE - ELEMENT/LINK (HV) | Check for safety - No power - heard a loud bang and believe it has come from the TX located on the corner of their property Advised SMC of 999 Replaced 2x 3 Amp HV Fuse Links Lines are very close to large poplar trees which need cutting that possibly contacted lines. Home owner says a tree contractor has been notified & is awaiting Powerco go ahead.. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000178 | 0.415 | 2017 | 2016-11-17 | C | 1 | 0.000178 | 3.0006e-06
1 | 14663566 | 2016-11-17 23:18 | 2016-11-18 02:35 | 197 | 1939 | 127856.9333 | 0.38366 | 0.3662 | 0.0058183 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 818365 | CONDUCTOR - REPAIR/REHANG | CB C957 tripped. A, B & C Ph O/C flags. Report of lines down received from Fire service at 32 Udy St. Site checked and tree branch had come through line at pole 446688. pole number is a new pole no asbuilts at time of fault NOTE: LOS to KEM Sub. Feeder fault not cleared by feeder CB C953 and tripped incomer 11kV C957. SCADA events indicated initially CB C953 protection operated, CB tripped but was found closed when faultman arrived on site? Maybe auto reclosed then tripping incomer? SCADA info/control/comms to 11kV feeder CB's was lost to sub following tripping. All feeder CB,s opened on site by faultman, CB C957 closed by NOC. SCADA comms restored when L/S supply restored (This by design?) CB's C956, C955 and C954 then closed by NOC. Faulted section of line isolated at ABS S359, CB C953 then reclosed. Protection review required to investigate failure of CB C953 to clear fault. Bus Zone protection on all feeder CB's were noticed to be disabled following tripping. Possibly due to ongoing SCADA & protection upgades at sub? Gavin Paget requested to down load relays and investigate loss of comms issue as well. NCTL. Transformer T1712 isolated before HV restored due to obvious HI/LO contact when wires brought down. Inspector being arranged to check installations for damage before restoring LV supply. All other supply restored. 1 metre of Mink conductor & 2 joint sleeves materials required. NDR to be provided by Downer | S2 | KEMPTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.3662 | 11 | 2017 | 2016-11-17 | C | 1939 | 0.3662 | 0.0058183
1 | 14666840 | 2016-11-18 05:14 | 2016-11-18 06:29 | 75 | 43 | 3240.05 | 0.0097221 | 0.009335 | 0.00012903 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2984 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV Fuse Links | F2 | TAUPO 2 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.009335 | 11 | 2017 | 2016-11-18 | C | 43 | 0.009335 | 0.00012903
1 | 14666931 | 2016-11-18 06:30 | 2016-11-18 07:22 | 52 | 1355 | 65819.5 | 0.1975 | 0.1853 | 0.0040658 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2862 | UNKNOWN | frm informed CB 2862 tripped on O/C flags causing LOS to Cardiff and Kaponga Substations. Line was patrolled and sectionalised and no fault was found, suspect bird strike. | S4 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.1853 | 33 | 2017 | 2016-11-18 | C | 1355 | 0.1853 | 0.0040658
1 | 14674869 | 2016-12-14 10:20 | 2016-12-14 13:40 | 200 | 2 | 400 | 0.0011998 | 0.001181 | 5.9989e-06 | NAPA ID:26245 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 026245 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6531 | NONE | To replace the 11kV fuse arm, Install a new crucifix bracket with Lightning Arrestors on the 11kV Cable. Note Transformer & 11kV Cable to be isolated for the length of the job. Works location: Wairere Rd, Matamata. WO 30034939 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0005905 | 5.5 | 2017 | 2016-12-14 | B | 2 | 0.001181 | 5.9989e-06
1 | 14674890 | 2016-12-15 10:05 | 2016-12-15 13:35 | 210 | 2 | 420 | 0.0012598 | 0.001241 | 5.9988e-06 | NAPA ID:26246 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 026246 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6531 | NONE | To replace TC6531 with a 200KVA Transformer. Works location: Wairere Rd, Matamata. WO 30034939 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0006205 | 5.5 | 2017 | 2016-12-15 | B | 2 | 0.001241 | 5.9988e-06
1 | 14674950 | 2016-11-18 07:33 | 2016-11-18 10:13 | 159 | 1 | 159.6833 | 0.00047915 | 0.00047 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 837953 | FUSE - ELEMENT/LINK (HV) | Reload at T7 2 x 3A Weather | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.00047 | 11 | 2017 | 2016-11-18 | C | 1 | 0.00047 | 3.0006e-06
1 | 14674981 | 2016-12-08 09:00 | 2016-12-08 11:40 | 160 | 57 | 9120 | 0.027358 | 0.026844 | 0.00017099 | NAPA ID:25188 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | 025188 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P35350 | NONE | Replace 11KV crossarms P35350 & P35364. Works location: Oroua Rd, Palmerston North. OW 30019767 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.013422 | 5.5 | 2017 | 2016-12-08 | B | 57 | 0.026844 | 0.00017099
1 | 14675053 | 2016-12-08 09:15 | 2016-12-08 15:45 | 390 | 4 | 1560 | 0.0046796 | 0.004643 | 1.1999e-05 | NAPA ID:25742 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 025742 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 831975 | NONE | tree work around over head line at poles 831975 831976. Works location: Hwy 2, Opaki Rd. WO 30026281 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0023215 | 5.5 | 2017 | 2016-12-08 | B | 4 | 0.004643 | 1.1999e-05
1 | 14675763 | 2016-12-05 09:32 | 2016-12-05 12:41 | 189 | 27 | 5103 | 0.015308 | 0.015065 | 8.0997e-05 | NAPA ID:25653 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025653 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE6-008 | NONE | REPLACE HV ARMS. Works location: Rangiuru Rd, Te Puke. WO 30017835 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0075325 | 5.5 | 2017 | 2016-12-05 | B | 27 | 0.015065 | 8.0997e-05
1 | 14676101 | 2016-11-18 15:45 | 2016-11-18 18:04 | 139 | 25 | 3475 | 0.010427 | 0.010202 | 7.5015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810052 | CROSSARM - WHOLE ASSEMBLY | Have spoken and advised customer of hazard process. Lines are only sagging slightly, in a paddock. SMC sending a text to call in Saturday 07.30 am. Update sent to SMC 1 X Crossarms 3 X HT Insulators replaced HRC | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.010202 | 11 | 2017 | 2016-11-18 | C | 25 | 0.010202 | 7.5015e-05
1 | 14679489 | 2016-11-18 12:23 | 2016-11-18 13:10 | 46 | 13 | 606.45 | 0.0018197 | 0.001702 | 3.9008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | P11454 | FUSE - ELEMENT/LINK (HV) | Check 14679645 Reload at Fuses F21 2 x 6A Unknown | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001702 | 11 | 2017 | 2016-11-18 | C | 13 | 0.001702 | 3.9008e-05
1 | 14680384 | 2016-12-15 10:00 | 2016-12-15 14:14 | 254 | 5 | 1270 | 0.0038093 | 0.003764 | 1.4997e-05 | NAPA ID:25503 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | 025503 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1851 | NONE | INSTALL TEMP LIVE LINE BREAK AND NEW FUSES FP1851 AT POLE M1509, ACCESS PERMIT FROM FP1851 TO REMOVE FC2189 & CHANGE STRAIN XARMS POLE M12362. Works location: Dukeson Rd, Putaruru. WO 30013417 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001882 | 5.5 | 2017 | 2016-12-15 | B | 5 | 0.003764 | 1.4997e-05
1 | 14680605 | 2016-11-18 15:50 | 2016-11-18 18:15 | 145 | 54 | 7830 | 0.023495 | 0.023008 | 0.00016203 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Western Lake Road, Wairarapa 798048 | POLE | Broken Pole 798048 Gavin Gray called this in, he has guys on the way now as it is an HV pole Advised SMC and Control - have sent out emergency outage to retailers 14.30 - 18.30 ******please check if OMS 14682879 is related (3935B WESTERN LAKE ROAD)***** 1 X Pole 1 X Crossarm 3 X HT Insulators | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.023008 | 11 | 2017 | 2016-11-18 | C | 54 | 0.023008 | 0.00016203
1 | 14682072 | 2016-12-19 09:45 | 2016-12-19 13:22 | 217 | 108 | 23436 | 0.070291 | 0.069318 | 0.00032392 | NAPA ID:24492 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11 | Planned | 024492 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5702 | NONE | Replace ABS 5702 & xarms. Works location: Broadway St, Stratford. WO 30017990 | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.034659 | 5.5 | 2017 | 2016-12-19 | B | 108 | 0.069318 | 0.00032392
1 | 14682213 | 2016-12-07 09:02 | 2016-12-07 14:23 | 321 | 3 | 963 | 0.0028888 | 0.002861 | 8.9993e-06 | NAPA ID:25041 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 025041 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole K1826 | NONE | Shutdown 2 spur line - Change hardware between K1826 and K12885. Works location: Tainui Rd, Morrinsville. WO 30017834 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0014305 | 5.5 | 2017 | 2016-12-07 | B | 3 | 0.002861 | 8.9993e-06
1 | 14682228 | 2016-12-11 03:18 | 2016-12-11 04:30 | 72 | 29 | 2088 | 0.0062632 | 0.006002 | 8.6989e-05 | NAPA ID:25131 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11 | Planned | 025131 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2680 | NONE | Drain and replace oil (failed tests) on T2680. Works location: Kuripuni Car Park. WO 30007513 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.003001 | 5.5 | 2017 | 2016-12-11 | B | 29 | 0.006002 | 8.6989e-05
1 | 14682248 | 2016-12-15 08:45 | 2016-12-15 12:33 | 228 | 12 | 2691 | 0.0080715 | 0.007963 | 3.5993e-05 | NAPA ID:26127 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11 | Planned | 026127 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 743429 | NONE | We are relocating 11kv pole 743429 to take away the sharpe angle as the pole is pulling over. We have to resag the HV and LV wires. 1: LLP create 11kV Line break at pole 743420. 2: AP relocate Pole 743429. Resag lHV & LV Lines. 3: LLP Close 11kV Line break at pole 743420. Works location: Henwood Rd, New Plymouth. WO 30034571 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.0039815 | 5.5 | 2017 | 2016-12-15 | B | 12 | 0.007963 | 3.5993e-05
1 | 14682258 | 2016-12-12 08:33 | 2016-12-12 15:24 | 411 | 86 | 35346 | 0.10602 | 0.10525 | 0.00025796 | NAPA ID:26535 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 026535 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 814265 | NONE | replace defective poles 814265, 814381 and 814383. Works location: Daniel St, Featherston. WO 30030519 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.052624 | 5.5 | 2017 | 2016-12-12 | B | 86 | 0.10525 | 0.00025796
1 | 14682282 | 2016-11-19 13:15 | 2016-11-19 17:16 | 241 | 13 | 3133 | 0.0094008 | 0.009283 | 3.9007e-05 | NAPA ID:26750 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 4 | 11 | Planned | 026750 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 444 | AIR BREAK SWITCH - ABS (HV) | Carry out urgent repairs on DNO ( 161116 ) ABS 444 . | F1 | DE HAVILLAND SOUTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0046415 | 5.5 | 2017 | 2016-11-19 | B | 13 | 0.009283 | 3.9007e-05
1 | 14682351 | 2016-12-11 08:30 | 2016-12-11 08:58 | 28 | 30 | 840 | 0.0025197 | 0.002249 | 8.9988e-05 | NAPA ID:25933 TP_WANGANUI GXP > HATRICKS WHARF SUB > OPERA HOUSE | 11 | Planned | 025933 | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 7 | NONE | Non Resin DGS Mtce and inspect bus connection and guroflex if needed. Works location: Taupo Quay. WO 30021058 | F2 | OPERA HOUSE | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.0011245 | 5.5 | 2017 | 2016-12-11 | B | 30 | 0.002249 | 8.9988e-05
1 | 14682392 | 2016-12-07 19:00 | 2016-12-07 22:53 | 233 | 7 | 1631 | 0.0048927 | 0.004829 | 2.0998e-05 | NAPA ID:26163 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11 | Planned | 026163 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 213296 | NONE | REPLACE 11KV POLES 213296 213301. Works location: TOtara St. WO 30017839 | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.0024145 | 5.5 | 2017 | 2016-12-07 | B | 7 | 0.004829 | 2.0998e-05
1 | 14683066 | 2016-11-18 17:29 | 2016-11-18 18:30 | 61 | 367 | 8485.1 | 0.025461 | 0.022156 | 0.0011012 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 5020E | CONDUCTOR - REPAIR/REHANG | Truck vs pole. Please get FM to contact Control. Advised SMC of 999 and asked for ETA Received a call from Cambell 027 434 0357 of Line Power,he received a call from one of his electricians that a truck had hit the lines at transformer 5020E, electrician informed the drive to remain in the vehicle, NC opened CB 5 at substation intial made safe, Fuses 4826 were Opened and then CB 5 was restored. 2 X 10 amp HV fuses replaced. NDR: N100254 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.022156 | 11 | 2017 | 2016-11-18 | C | 367 | 0.022156 | 0.0011012
1 | 14684218 | 2016-11-18 19:15 | 2016-11-19 08:20 | 785 | 1 | 785 | 0.0023555 | 0.002346 | 3.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2458T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Blown 15kva/3ph/11kv Transformer 2458T requires replacement. Not being done until next morning. Only customer affected is happy according to FM. | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.002346 | 11 | 2017 | 2016-11-18 | C | 1 | 0.002346 | 3.0006e-06
1 | 14684303 | 2016-11-18 19:55 | 2016-11-18 20:35 | 40 | 15 | 600 | 0.0018004 | 0.001665 | 4.5009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 2326 TE HOPAI ROAD | NONE | Advised SMC of 999 Found branch on line. Isolated at fuses 7298, removed branch & re-livened | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.001665 | 11 | 2017 | 2016-11-18 | C | 15 | 0.001665 | 4.5009e-05
1 | 14684637 | 2016-11-18 22:45 | 2016-11-19 18:05 | 1160 | 257 | 41794.2333 | 0.12541 | 0.12309 | 0.00085818 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 820 | CONDUCTOR - REPAIR/REHANG | RS 6610/2 A/R, L/O, E/F, O/C A Phase, faultman found trees had fallen and broken transformer structure and transformer 820 and lines, 2 line breaks were made at transformer 1761N & pole 746390 to carry out the repairs and replace transformer & structure. ALL material will be in invoice. Replaced transformer 820. Transformer structure Cross arms NDR: N100256 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.12309 | 11 | 2017 | 2016-11-18 | C | 257 | 0.12309 | 0.00085818
1 | 14685290 | 2016-11-19 05:33 | 2016-11-19 06:37 | 63 | 1 | 63.9 | 0.00019174 | 0.000182 | 3.0005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc2147 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 15amp ht fuse | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000182 | 11 | 2017 | 2016-11-19 | C | 1 | 0.000182 | 3.0005e-06
1 | 14685308 | 2016-11-19 06:24 | 2016-11-19 08:06 | 101 | 1047 | 79795.3667 | 0.23943 | 0.23001 | 0.0047139 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2034 | INSULATOR | CB 8 tripped on C phase E/F flags, line was patrolled and sectionalised and a broken 11KV insulator was found at transformer X2034, line was isolated at transformer X2034. 1 X 11KV insulator replaced | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.23001 | 11 | 2017 | 2016-11-19 | C | 1047 | 0.23001 | 0.0047139
1 | 14686917 | 2016-11-19 07:27 | 2016-11-19 09:15 | 107 | 19 | 2046.9333 | 0.006142 | 0.00597 | 5.7011e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8169 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuses at Fuses 8169, line was patrolled and no fault was found. 2 X 8 amp HV fuses replaced. | F1 | PARAITE RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.00597 | 11 | 2017 | 2016-11-19 | C | 19 | 0.00597 | 5.7011e-05
1 | 14687280 | 2016-11-19 08:13 | 2016-11-19 11:48 | 215 | 2334 | 85691.55 | 0.25712 | 0.23611 | 0.0033096 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 6334 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | 85 and 86 Cordelia Street - Big rumbling sound then a flash with smoke. Over the river - Council was working there yesterday. No wind. 87 Ariel Street - CB 2842 at SFD GXP tripped on O/C flags, CB 3 tripped on C phase Fault, faultman found blown fuses and broken drop outs at Fuses 6334 caused by a bird that flered up into the 33KV lines, line was isolated at ABS's 5788, 5803, 5833 & 5855 to replace the full set of drop out links & fuses. 1 X Full set of drop out links replaced. 3 X 25 amp fuses replaced. 2 X sleeves & 1 X binder used. This job maybe a 2 R job due to nature of job. | F4 | CLOTON RD CENTRAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.23611 | 11 | 2017 | 2016-11-19 | C | 2334 | 0.23611 | 0.0033096
1 | 14688870 | 2016-11-19 08:47 | 2016-11-19 10:05 | 77 | 3 | 232.5 | 0.00069763 | 0.00067 | 9.0017e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | FC922/1 | FUSE - ELEMENT/LINK (HV) | Defect No 10161992 trees in line replace 2 x 2A H/V, O/H fuses at fuses FC922/1 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.00067 | 11 | 2017 | 2016-11-19 | C | 3 | 0.00067 | 9.0017e-06
1 | 14693995 | 2016-11-19 17:12 | 2016-11-19 19:56 | 164 | 237 | 18030.7333 | 0.054102 | 0.051969 | 0.00071114 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27743 | BINDER | Floating Conductor at Pole P27743 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.051969 | 11 | 2017 | 2016-11-19 | C | 237 | 0.051969 | 0.00071114
1 | 14694968 | 2016-11-19 21:40 | 2016-11-19 22:48 | 68 | 1528 | 87301.2 | 0.26195 | 0.2482 | 0.0069823 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1136 | JUMPER | CB 7 tripped on O/C flags, line was sectionalised and patrolled and a blown jumper was found at ABS 1136, the jumper on ABS 1136 was repaired under a Live Line Permit. | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.2482 | 11 | 2017 | 2016-11-19 | C | 1528 | 0.2482 | 0.0069823
1 | 14697245 | 2016-11-19 22:04 | 2016-11-19 23:53 | 108 | 62 | 4907.6 | 0.014726 | 0.014167 | 0.00018604 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C267/2 | UNKNOWN | Recloser C267 tripped on A,B,C Ph Fault Sectionalised and found NO fault | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.014167 | 11 | 2017 | 2016-11-19 | C | 62 | 0.014167 | 0.00018604
1 | 14699683 | 2016-11-20 01:27 | 2016-11-20 17:38 | 970 | 589 | 82275.2667 | 0.24687 | 0.24157 | 0.0039907 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Two conductors down at Pole 783358. Used 30 metres of conductor and 6 x sleeves. 3 X Generators at transformer X596 so Everyone has power at 18:30. this outage has duplicated steps so i have sent to Praksha to check. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.24157 | 11 | 2017 | 2016-11-20 | C | 589 | 0.24157 | 0.0039907
1 | 14701896 | 2016-11-20 09:31 | 2016-11-20 10:08 | 36 | 41 | 1511.5333 | 0.0045354 | 0.004166 | 0.00012302 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851696 | JUMPER | Faultman found a burnt of jumper at pole 851696, line was isolated at ABS's 982 & 1418 to repair the jumper. 1 X line connector used | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.004166 | 11 | 2017 | 2016-11-20 | C | 41 | 0.004166 | 0.00012302
1 | 14702406 | 2016-11-20 06:04 | 2016-11-20 08:36 | 151 | 190 | 22727.2167 | 0.068194 | 0.066483 | 0.0005701 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB H11 | UNKNOWN | CB H11 tripped on no flags, line was sectionalised and patrolled and no fault was found. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.066483 | 6.6 | 2017 | 2016-11-20 | C | 190 | 0.066483 | 0.0005701
1 | 14703015 | 2016-11-20 11:15 | 2016-11-20 12:45 | 90 | 12 | 1080 | 0.0032406 | 0.003132 | 3.6006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 519 | CONDUCTOR - REPAIR/REHANG | Faultman found a tree had gone through LV lines, transformer 519 was isolated for safety to repair the LV lines. 8 X 25mm copper conductor was used. 8 X sleeves used. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.003132 | 11 | 2017 | 2016-11-20 | C | 12 | 0.003132 | 3.6006e-05
1 | 14703751 | 2016-11-20 08:01 | 2016-11-21 08:41 | 1479 | 1 | 1479.7833 | 0.0044401 | 0.004431 | 3.0005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Transformer TP1718 already turned off some time ago. This Transformer will be permanently disconnected. NO SadI SR 116937 | F1 | CHAPEL ST | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 0.004431 | 11 | 2017 | 2016-11-20 | C | 1 | 0.004431 | 3.0005e-06
1 | 14707669 | 2016-11-20 08:44 | 2016-11-20 10:25 | 101 | 15 | 1515.5 | 0.0045473 | 0.004412 | 4.5008e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 207179 | FUSE - ELEMENT/LINK (HV) | 2x8amp HV Fuses blown at Fuses SA2-033. Line patrolled Reloaded & Livened. Probably bird strike. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.004412 | 11 | 2017 | 2016-11-20 | C | 15 | 0.004412 | 4.5008e-05
1 | 14708343 | 2016-11-20 09:26 | 2016-11-20 12:25 | 179 | 2 | 358.3 | 0.0010751 | 0.001057 | 6.001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782742 | CONDUCTOR - REPAIR/REHANG | Faultman isolated transformer X2563 for safety to repair LV cable on pole 782742. 1meter of 10mm copper conductor used. 2 X 10mm sleeves used. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001057 | 11 | 2017 | 2016-11-20 | C | 2 | 0.001057 | 6.001e-06
1 | 14709088 | 2016-11-20 10:51 | 2016-11-20 14:17 | 206 | 424 | 27115.05 | 0.08136 | 0.077542 | 0.0018243 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | C1989 | CONDUCTOR - REPAIR/REHANG | CB 6 Trip C Fault E/F Ground. Tree Through line at pole C989. line broken at same pole from branch. Isolation at ABS IC626, IC633 & Links 9707/6. Back feeds from ABS 617 MIK CB 7 and ABS IC646. Line repaired & relivened. Transformer TC4165 isolated due to 11kV/400V Clash, inspector inspaecting properties. 1 burnt out meter box at 239 No2 road off pole C1991. 2 Fuse assemblies replaced at this property as well. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.077542 | 11 | 2017 | 2016-11-20 | C | 424 | 0.077542 | 0.0018243
1 | 14711337 | 2016-11-20 14:05 | 2016-11-20 16:11 | 125 | 27 | 3396.15 | 0.01019 | 0.009947 | 8.1014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5193 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 5193, line was patrolled and no fault was found. 2 X 15 amp HV fuses replaced | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.009947 | 11 | 2017 | 2016-11-20 | C | 27 | 0.009947 | 8.1014e-05
1 | 14712144 | 2016-11-20 21:27 | 2016-11-20 22:40 | 72 | 17 | 1237.8833 | 0.0037143 | 0.003561 | 5.1009e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 0792 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A H/V, O/H fuses ( unknown ) | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003561 | 11 | 2017 | 2016-11-20 | C | 17 | 0.003561 | 5.1009e-05
1 | 14712276 | 2016-11-21 06:00 | 2016-11-21 07:12 | 71 | 1528 | 60656.65 | 0.182 | 0.16825 | 0.0045847 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | CB 7 Tripped E/F L/O Feeder currently supporting most of ROB Ave Sub Feeders sectionlised with no fault found Feeder back feeds changed to spread feeders more | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.16825 | 11 | 2017 | 2016-11-21 | C | 1528 | 0.16825 | 0.0045847
1 | 14714569 | 2016-11-21 06:33 | 2016-11-21 09:15 | 161 | 27 | 4361.85 | 0.013088 | 0.012844 | 8.1013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 204509 | FUSE - ELEMENT/LINK (HV) | 2x15amp HV fuses blown at SB1-047. line patrolled, fuses reloaded & livened. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.012844 | 11 | 2017 | 2016-11-21 | C | 27 | 0.012844 | 8.1013e-05
1 | 14714827 | 2016-12-01 09:04 | 2016-12-01 11:57 | 173 | 95 | 16435 | 0.049306 | 0.04845 | 0.00028501 | NAPA ID:25287 TP_HAWERA GXP > WHAREROA SUB > MANUTAHI | 11 | Planned | 025287 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 728158 | NONE | Replace defect pole 728158 with new 11m Busck pole. Works location: South Rd, Patea. WO 30033747 | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.024225 | 5.5 | 2017 | 2016-12-01 | B | 95 | 0.04845 | 0.00028501
1 | 14719738 | 2016-11-21 09:33 | 2016-11-21 13:39 | 245 | 27 | 6638.4 | 0.019918 | 0.019675 | 8.1013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 317084 | CONDUCTOR - REPAIR/REHANG | at 12:45, Pungarehu Sub, CB PU4 Parihaka Rd Feeder. Found floating HV conductor at Pole 317084. Isolated Lines at Fuses 6435. Permit Issued & Repairs Carried out. All Power Restored on Completion. Tony Jullian Attended. 1x Binder Replaced. May have been left over fault from last weeks storm. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.019675 | 11 | 2017 | 2016-11-21 | C | 27 | 0.019675 | 8.1013e-05
1 | 14720513 | 2016-11-21 11:00 | 2016-11-21 14:45 | 225 | 1 | 225.45 | 0.00067646 | 0.000667 | 3.0004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | 827646 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses From the quake but didn't ring in because it only feeds a pump shed | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000667 | 11 | 2017 | 2016-11-21 | C | 1 | 0.000667 | 3.0004e-06
1 | 14720596 | 2016-12-05 10:11 | 2016-12-05 15:22 | 311 | 15 | 4665 | 0.013994 | 0.013859 | 4.4998e-05 | NAPA ID:26271 TP_GREYTOWN GXP > FEATHERSTON SUB > DAIRY FACTORY | 11 | Planned | 026271 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 799902 | NONE | replace poles 799902 and 799932. Works location: Hwy 53, Featherston. WO 30000172 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.0069295 | 5.5 | 2017 | 2016-12-05 | B | 15 | 0.013859 | 4.4998e-05
1 | 14721225 | 2016-12-08 19:00 | 2016-12-08 21:00 | 120 | 25 | 3000 | 0.0089993 | 0.008774 | 7.4994e-05 | NAPA ID:26164 TP_MT MAUNGANUI 33 GXP > TRITON SUB | 11 | Planned | 026164 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 213267 | NONE | This job ran over time due to 110V DC Battery Bank fault at triton sub which occured during switching for this job. CB 7 would not close into circuit earth so switching and isolations had to be changed. (see OMS 15031101) REPLACE 11KV POLE # 213267 | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.004387 | 5.5 | 2017 | 2016-12-08 | B | 25 | 0.008774 | 7.4994e-05
1 | 14721578 | 2016-12-13 09:15 | 2016-12-13 14:58 | 343 | 62 | 21266 | 0.063788 | 0.06323 | 0.00018597 | NAPA ID:26748 TP_MASTERTON GXP > GLADSTONE SUB > PUKETIRO | 11 | Planned | 026748 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 822526 | NONE | red tag pole gp. change pole 822526 ,replace conductor from tx1746 to links 7636 with squirrel. Works location: Te Kopi Rd. WO 30013138 | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.031615 | 5.5 | 2017 | 2016-12-13 | B | 62 | 0.06323 | 0.00018597
1 | 14721901 | 2016-11-21 15:55 | 2016-11-21 16:29 | 34 | 7 | 238 | 0.00071412 | 0.000651 | 2.1003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847176 | JUMPER | Broken Jumper found at Pole 847176 Isolated at Fuses 4248 Jumper repaired Used no Materials | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000651 | 11 | 2017 | 2016-11-21 | C | 7 | 0.000651 | 2.1003e-05
1 | 14722529 | 2016-11-21 15:28 | 2016-11-21 17:19 | 111 | 20 | 2088.1 | 0.0062653 | 0.006085 | 6.001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P00522 | FUSE - ELEMENT/LINK (HV) | Check 85 NGAHERE PARK, oms 14722538,and 333 NGAHERE PARK ROAD, oms 14722556 are related. Fuses found blown at H34 - cause possible bird strike Used 2 x 15 amp fuses | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.006085 | 11 | 2017 | 2016-11-21 | C | 20 | 0.006085 | 6.001e-05
1 | 14722953 | 2016-11-21 17:09 | 2016-11-21 19:05 | 116 | 1 | 116.2167 | 0.00034871 | 0.000339 | 3.0004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | M83 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuse at Fuses M83, suspect duck strike as ducks flying around area. 2 X 6 amp HV fuses repalced. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000339 | 11 | 2017 | 2016-11-21 | C | 1 | 0.000339 | 3.0004e-06
1 | 14723680 | 2016-11-21 20:47 | 2016-11-21 21:19 | 32 | 15 | 480 | 0.0014402 | 0.001305 | 4.5007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q0279 | FUSE - ELEMENT/LINK (HV) | ( WBH 1 ) Emergency switching to restrain low H/V line clashing at pole Q0279 during high wind Isolation at Fused ABS IC292 ( spur no back feed ) Line re strained all service restored Materials 2 x 20 H/V O/H fuses replaced at fusd ABS IC292 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.001305 | 11 | 2017 | 2016-11-21 | C | 15 | 0.001305 | 4.5007e-05
1 | 14724095 | 2016-11-22 04:16 | 2016-11-22 15:27 | 670 | 1130 | 143063.1667 | 0.42925 | 0.41908 | 0.0033905 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 707665 | POLE | Recloser 4775/2 tripped on B phase O/C flags, received a call from fire services of car vs pole at 160 Mosston Rd. (Pole 707665) Isolated 33kV at CB's 3042, 3102/2 and 11kV at ABS's 483, 1185, 678, 720 with Fuses 2652 & for Transformer X3077 due to inbedded generation. Generators installed at effected schools Temp Line break installaed at Pole 707664 and backfeed install via ABS 1356 Pole 707665 Replaced NDR # N200070 Faultman to provide materials list tomorrow | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.41908 | 11 | 2017 | 2016-11-22 | C | 1130 | 0.41908 | 0.0033905
1 | 14727150 | 2016-11-22 07:42 | 2016-11-22 09:23 | 101 | 30 | 3030 | 0.0090913 | 0.008821 | 9.0013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 785874 | FUSE - ELEMENT/LINK (HV) | Mark went to transfortmer X1154 and confirmed that all power was on. It was found that Fuses 2611 were open Reload 2 x 10A Bird strike | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.008821 | 11 | 2017 | 2016-11-22 | C | 30 | 0.008821 | 9.0013e-05
1 | 14729163 | 2016-11-16 10:00 | 2016-11-16 12:00 | 120 | 6 | 720 | 0.0021605 | 0.002106 | 1.8004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Repair LV network from Tx 5109E Own Isolation and AP | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.002106 | 11 | 2017 | 2016-11-16 | C | 6 | 0.002106 | 1.8004e-05
1 | 14731660 | 2016-12-01 08:45 | 2016-12-01 15:10 | 385 | 12 | 4620 | 0.01386 | 0.013752 | 3.6001e-05 | NAPA ID:26690 TP_TAURANGA 33 GXP | 11 | Planned | 026690 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV poel 268724 | NONE | AP1 Pole replacement: 268724, 263420. Crossarm replacement: 209370, 383691. LLP1 & 2 Replace pole 268703 & 268719. NOTE: Backfeed must be made before, and stay in place, until Live Line work is completed (ie TEMP98 must remain OPEN). Works location: Esdaile Rd. WO 30019861 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.006876 | 5.5 | 2017 | 2016-12-01 | B | 12 | 0.013752 | 3.6001e-05
1 | 14736496 | 2016-11-22 14:20 | 2016-11-22 18:16 | 236 | 41 | 9676 | 0.029032 | 0.028663 | 0.00012302 | Fuses were found blown | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207139 | POLE | Report of car v pole. Broken pole 207139 replaced. Isolation at fuses FP1781. Fuses were found blown on site arrival by faultman. Pole replaced. All supply restored NDR 53908. Material required - 1 x 11m busck pole & 3 ph crossarm, pin & ins assembly - 3 x 6amp fuses | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.028663 | 11 | 2017 | 2016-11-22 | C | 41 | 0.028663 | 0.00012302
1 | 14738160 | 2016-11-22 16:16 | 2016-11-22 20:58 | 282 | 228 | 11780.5 | 0.035347 | 0.033294 | 0.0006841 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 815753 | POLE | Car vs pole - pole snapped in half, lines down. F2193520 ETA required. 04 801 0812 Pole # Called in by Wayne Watt, Power Related Services, 027 439 7239 Pole replaced. Isolation at ABS S577, S556, S515. Transformer T903 Material, 1x11m concrete Pole, 2.7m LV Crossarm C/W insulators, 1x 2.0m HV Crossarms C/W Insulators. NDR to follow protection review on CB C956 micheal allpress investigating | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.033294 | 11 | 2017 | 2016-11-22 | C | 228 | 0.033294 | 0.0006841
1 | 14740740 | 2016-11-23 12:20 | 2016-11-23 13:45 | 85 | 6 | 510 | 0.0015302 | 0.001476 | 1.8002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22914 | BINDER | Faultman found a blown fuse at Fuses V56, line was patrolled and a floating wire at pole P22914 was found, line was isolate at Fuses V56 to repair the floater. 1 X Binder used. 2 X 10 amp HV fuses replaced | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.001476 | 11 | 2017 | 2016-11-23 | C | 6 | 0.001476 | 1.8002e-05
1 | 14740781 | 2016-12-08 08:30 | 2016-12-08 09:53 | 83 | 4 | 332 | 0.00099592 | 0.000959 | 1.1999e-05 | NAPA ID:26786 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 026786 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 834972 | POLE | replace red tag pole 834972.RED TAG POLE 10 day shutdown notice G.P. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0004795 | 5.5 | 2017 | 2016-12-08 | B | 4 | 0.000959 | 1.1999e-05
1 | 14740861 | 2016-12-07 10:00 | 2016-12-07 12:44 | 163 | 15 | 2450.75 | 0.0073517 | 0.007216 | 4.4997e-05 | NAPA ID:26768 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11 | Planned | 026768 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 820334 | POLE | replace red tag pole 820334. RED TAG POLE 10 day shutdown notice G.P. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.003608 | 5.5 | 2017 | 2016-12-07 | B | 15 | 0.007216 | 4.4997e-05
1 | 14740979 | 2016-12-08 12:00 | 2016-12-08 15:11 | 191 | 7 | 1337 | 0.0040107 | 0.003947 | 2.0998e-05 | NAPA ID:26787 TP_MASTERTON GXP > CLAREVILLE SUB > CHESTER RD | 11 | Planned | 026787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 817766 | POLE | replace red tagged poles 817766 and 817767. RED TAG POLES 10 day shutdown notice G.P. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0019735 | 5.5 | 2017 | 2016-12-08 | B | 7 | 0.003947 | 2.0998e-05
1 | 14741702 | 2016-11-23 09:41 | 2016-11-23 13:44 | 242 | 2 | 484.7667 | 0.0014545 | 0.001436 | 6.0008e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837632 | FUSE - ELEMENT/LINK (HV) | 2 x 10 unknown | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.001436 | 11 | 2017 | 2016-11-23 | C | 2 | 0.001436 | 6.0008e-06
1 | 14753774 | 2016-12-09 11:35 | 2016-12-09 12:50 | 75 | 8 | 600 | 0.0017998 | 0.001727 | 2.3998e-05 | NAPA ID:25825 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11 | Planned | 025825 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP2985 | NONE | LLP1: Connect drop-out fuses for new transformer TP2985 and commission transformer AP1: Remove transformer TC683 and replace LV crossarm on pole O12992. After LV crossarm is replaced the LV reticulation formally supplied from TC683 can be supplied from new transformer TP2985. Liven LV reticulation via the LV fuses on TP2985. LLP2: Permanently remove the 11kV drop-out fuses TC683, from pole O12992. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0008635 | 5.5 | 2017 | 2016-12-09 | B | 8 | 0.001727 | 2.3998e-05
1 | 14753886 | 2016-12-08 09:52 | 2016-12-08 10:44 | 52 | 92 | 4784 | 0.014351 | 0.013522 | 0.00027598 | NAPA ID:25568 TP_STRATFORD GXP | 11 | Planned | 025568 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Install two 11Kv line breaks at poles 734448 & 441345. Replace 33Kv poles & conductors over isolated 11Kv line. Close 11Kv break next week. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006761 | 5.5 | 2017 | 2016-12-08 | B | 92 | 0.013522 | 0.00027598
1 | 14754538 | 2016-11-23 11:55 | 2016-11-23 14:32 | 157 | 186 | 19925.8667 | 0.059786 | 0.058111 | 0.00055808 |  | 22 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1133 | UNKNOWN | Retailer has advised that a caller is stating there is a broken down truck blocking most of the road. CB 1133 tripped on A & B phase OC & E/F flags, line was sectionalised and patrolled and no fault was found. Faultman did report quiet windy in area. Can not close job off. | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.058111 | 22 | 2017 | 2016-11-23 | C | 186 | 0.058111 | 0.00055808
1 | 14755468 | 2016-12-07 09:00 | 2016-12-07 14:37 | 337 | 12 | 4044 | 0.012131 | 0.012023 | 3.5998e-05 | NAPA ID:26886 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 026886 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 268706 | NONE | Pole replacements: 268706, 209396. Crossarm replacements: 268708, 268709, 268711. Works location: Esdaile Rd, Whakamarama. WO 30019861 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.0060115 | 5.5 | 2017 | 2016-12-07 | B | 12 | 0.012023 | 3.5998e-05
1 | 14756321 | 2016-12-07 12:00 | 2016-12-07 14:14 | 134 | 32 | 4288 | 0.012863 | 0.012575 | 9.5993e-05 | NAPA ID:26772 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11 | Planned | 026772 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 821071 | POLE | replace red tag pole 821071.RED TAG POLE 10 day shutdown notice G.P. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0062875 | 5.5 | 2017 | 2016-12-07 | B | 32 | 0.012575 | 9.5993e-05
1 | 14756457 | 2016-11-29 08:48 | 2016-11-29 16:20 | 452 | 37 | 16724 | 0.050174 | 0.049841 | 0.00011101 | NAPA ID:26684 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 026684 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 268728 | POLE | Replace pole 268728 day 1 (install pole) & replace pole 268713, 268714, 268717 & 209381. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.024921 | 5.5 | 2017 | 2016-11-29 | B | 37 | 0.049841 | 0.00011101
1 | 14757070 | 2016-11-23 21:30 | 2016-11-23 22:32 | 62 | 109 | 6336.5833 | 0.019012 | 0.018031 | 0.00032704 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9480 | UNKNOWN | Recloser 9480 Trip. No Flags. Line patrolled. No Fault found. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.018031 | 11 | 2017 | 2016-11-23 | C | 109 | 0.018031 | 0.00032704
1 | 14757618 | 2016-11-24 09:30 | 2016-11-24 13:15 | 225 | 3 | 669 | 0.0020072 | 0.00198 | 1.8002e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851229 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | tx N2060 found blown replaced with new. Self issue permit 1 x 50kVA 3ph tx, 1 x backing plate, 2 bolts and 3 x 6amp HV links | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00198 | 11 | 2017 | 2016-11-24 | C | 3 | 0.00198 | 1.8002e-05
1 | 14757732 | 2016-11-30 08:58 | 2016-11-30 15:45 | 407 | 37 | 15059 | 0.045179 | 0.044845 | 0.000111 | NAPA ID:26685 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 026685 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 268728 | NONE | Replace pole 268728 day 2 (transfer hardware) & Replace 11kV Poles 268716, 268718, 209380 & 209378. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.022423 | 5.5 | 2017 | 2016-11-30 | B | 37 | 0.044845 | 0.000111
1 | 14758222 | 2016-12-16 08:08 | 2016-12-16 14:34 | 386 | 96 | 37056 | 0.11115 | 0.11028 | 0.00028794 | NAPA ID:26679 TP_WAIKINO GXP > WHANGAMATA SUB > OTAHU RD | 11 | Planned | 026679 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1068 | NONE | Disconnect TP1068 from FP722, Connect new RMU 13130/ onto cable from FP722, Connect TP1068 onto 13130/2 & new TP3034 onto 13130/4. Leave 13130/3 in earthed. Confirmed that Fuses FP722 will be up-rated. | F3 | OTAHU RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.055141 | 5.5 | 2017 | 2016-12-16 | B | 96 | 0.11028 | 0.00028794
1 | 14758611 | 2016-11-24 09:18 | 2016-11-24 09:47 | 28 | 1210 | 15277.5667 | 0.045838 | 0.034946 | 0.0036304 |  | 11 | Unplanned |  | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | mangamutu CB 18 | NONE | During planned switching NAPA 26859 operator error closed into bus earth instead of circuit earth tripping CB18 bus coupler. | S1 | MANGAMUTU 2 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0.034946 | 11 | 2017 | 2016-11-24 | C | 1210 | 0.034946 | 0.0036304
1 | 14759824 | 2016-12-13 09:00 | 2016-12-13 12:24 | 204 | 54 | 11016 | 0.033043 | 0.032556 | 0.00016197 | NAPA ID:25192 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | 025192 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P05447 | NONE | Replace 11KV pole P05447 & install new Trani 7422P. Works location: Oroua Valley Rd, Apiti. WO 30033480 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.016278 | 5.5 | 2017 | 2016-12-13 | B | 54 | 0.032556 | 0.00016197
1 | 14759854 | 2016-12-09 08:36 | 2016-12-09 13:34 | 298 | 187 | 966 | 0.0028977 | 0.001214 | 0.00056094 | NAPA ID:26405 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 026405 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5378 | NONE | Replace defective Single Phase GM transformer TC5378. ABS 2703 opened on restoration because of ferro resonance & damage to the 11kV cable past fuses FC4134. This cable is 700M long & cause quite an arc when opened at the start of the shutdown. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000607 | 5.5 | 2017 | 2016-12-09 | B | 187 | 0.001214 | 0.00056094
1 | 14759993 | 2016-12-13 08:45 | 2016-12-13 11:35 | 170 | 3 | 510 | 0.0015298 | 0.001502 | 8.9985e-06 | NAPA ID:26763 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11 | Planned | 026763 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 828980 | NONE | replace red tag pole 828980 and defective pole 828977. RED TAG POLE10 day shutdown notice G.P. Works location: Solway Cres, Masterton. WO 30020281 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.000751 | 5.5 | 2017 | 2016-12-13 | B | 3 | 0.001502 | 8.9985e-06
1 | 14760049 | 2016-12-12 21:02 | 2016-12-12 22:45 | 103 | 26 | 2678 | 0.0080329 | 0.007798 | 7.7989e-05 | NAPA ID:25427 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 025427 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Ngatea | NONE | Disconnect HV & LV cables from Tx lift & re-level. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003899 | 5.5 | 2017 | 2016-12-12 | B | 26 | 0.007798 | 7.7989e-05
1 | 14760061 | 2016-12-13 09:48 | 2016-12-13 14:34 | 286 | 41 | 11755.3833 | 0.035261 | 0.034891 | 0.00012298 | NAPA ID:26835 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11 | Planned | 026835 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 797565 | NONE | Replace red tag pole, defective cross arms and ABS out on Lake Ferry Road. Works location: Lake Ferry Rd. WO 30017992 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.017445 | 5.5 | 2017 | 2016-12-13 | B | 41 | 0.034891 | 0.00012298
1 | 14760258 | 2016-12-10 13:11 | 2016-12-10 15:08 | 117 | 1 | 117.5167 | 0.00035251 | 0.000343 | 2.9996e-06 | NAPA ID:26760 TP_HUIRANGI GXP > WAITARA WEST SUB > AFFCO-QUEEN ST | 11 | Planned | 026760 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | F51 | NONE | 3Yearly 11kV CB F51 maintenance incl. protection testing | F1 | AFFCO-QUEEN ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.0001715 | 5.5 | 2017 | 2016-12-10 | B | 1 | 0.000343 | 2.9996e-06
1 | 14760794 | 2016-11-24 09:55 | 2016-11-24 15:20 | 325 | 1 | 325 | 0.00097512 | 0.000966 | 3.0003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21354 | BINDER | Urgent short notice job to repair broken binders on North Range Rd affecting the Airways Rada System, while carrying out the repairs the faultman also found a broken double cross arm that was broken. 3 X Binders replaced on pole P21354. 1 X Double cross arm & all hardware was replaced on pole P21355. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.000966 | 11 | 2017 | 2016-11-24 | C | 1 | 0.000966 | 3.0003e-06
1 | 14761039 | 2016-12-11 21:30 | 2016-12-11 22:17 | 47 | 422 | 19847.9 | 0.059536 | 0.055738 | 0.0012658 | NAPA ID:26857 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 026857 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 814892 | NONE | make temp line break at pole 814892 to be used as isolation point for shutdown on 12/12/16 to replace RED TAG POLE. 10 day shutdown notice G.P. Works location: East St, Greytown. WO 30034641 | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.027869 | 5.5 | 2017 | 2016-12-11 | B | 422 | 0.055738 | 0.0012658
1 | 14761069 | 2016-12-21 09:00 | 2016-12-21 13:53 | 293 | 46 | 13478 | 0.040423 | 0.040008 | 0.00013796 | NAPA ID:25656 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 025656 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726547 | NONE | Replace defect poles 726547 & 726545 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.020004 | 5.5 | 2017 | 2016-12-21 | B | 46 | 0.040008 | 0.00013796
1 | 14761169 | 2016-12-12 08:45 | 2016-12-12 11:25 | 160 | 7 | 1120.0333 | 0.0033596 | 0.003296 | 2.0997e-05 | NAPA ID:26866 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 026866 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 818080 | NONE | replace red tag pole 818080. RED TAG POLE 10 day shutdown notice G.P. Works location: East St, Greytown. WO 30034641 | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.001648 | 5.5 | 2017 | 2016-12-12 | B | 7 | 0.003296 | 2.0997e-05
1 | 14761172 | 2016-12-06 09:30 | 2016-12-06 12:45 | 195 | 37 | 7215 | 0.021644 | 0.02131 | 0.00011099 | NAPA ID:25279 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 025279 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole I13390 | NONE | Replace 11 kV X arms at various locations. WORKSITE CONFIRMED BY PAUL BETWEEN POLES I13390 & I1645. Works location: Bell Rd, Morrinsville. WO 30027522 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.010655 | 5.5 | 2017 | 2016-12-06 | B | 37 | 0.02131 | 0.00011099
1 | 14761234 | 2016-12-20 10:00 | 2016-12-20 14:45 | 285 | 8 | 2280 | 0.0068382 | 0.006766 | 2.3994e-05 | NAPA ID:22028 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 022028 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2122 | NONE | To replace arms and install 400V Disconnectors to TC3287 & TC2122. Works location: Gunn Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.003383 | 5.5 | 2017 | 2016-12-20 | B | 8 | 0.006766 | 2.3994e-05
1 | 14761289 | 2016-12-14 08:30 | 2016-12-14 16:10 | 460 | 30 | 13800 | 0.041393 | 0.041122 | 8.9984e-05 | NAPA ID:25670 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 025670 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Nannestads Road | NONE | This is a Powerco tender, with 33kv xarms and poles, and 11kv xarms and hardware | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.020561 | 5.5 | 2017 | 2016-12-14 | B | 30 | 0.041122 | 8.9984e-05
1 | 14761371 | 2016-12-15 08:24 | 2016-12-15 15:48 | 444 | 30 | 13320 | 0.039952 | 0.039682 | 8.9983e-05 | NAPA ID:25677 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 025677 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Nannestads Road | NONE | This is a Powerco tender, with 33kv xarms and poles, and 11kv xarms and hardware | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.019841 | 5.5 | 2017 | 2016-12-15 | B | 30 | 0.039682 | 8.9983e-05
1 | 14761376 | 2016-12-22 09:30 | 2016-12-22 12:30 | 180 | 8 | 1440 | 0.0043187 | 0.004246 | 2.3993e-05 | NAPA ID:26253 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 026253 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4670 | NONE | To Relocate the 11kV Fuses and Transformer TC4670. Works location: Wairere Rd, Matamata. WO 30034939 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.002123 | 5.5 | 2017 | 2016-12-22 | B | 8 | 0.004246 | 2.3993e-05
1 | 14761534 | 2016-12-13 08:16 | 2016-12-13 12:57 | 281 | 5 | 1405 | 0.0042143 | 0.004169 | 1.4998e-05 | NAPA ID:25641 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | 025641 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-029 | NONE | REPOLE AND RECON FEEDER. Works location: Te Puke Quarry Rd. WO 30019857 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.0020845 | 5.5 | 2017 | 2016-12-13 | B | 5 | 0.004169 | 1.4998e-05
1 | 14762069 | 2016-12-09 08:53 | 2016-12-09 16:10 | 437 | 56 | 24472 | 0.073409 | 0.072904 | 0.00016798 | NAPA ID:26892 TP_TAURANGA 33 GXP | 11 | Planned | 026892 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 209404 | NONE | Pole replacement at 209404, 268701. X-arm replacement at 209403. Reconductor between 395594 & 268702. Live Line connection of new conductor to ABS TEMP95 & ABS TEMP97. Works location: Wainui South Rd. WO 30019861 TO BE PLACED IN SAFETY MANAGER DUE TO RUNNING LATE | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.036452 | 5.5 | 2017 | 2016-12-09 | B | 56 | 0.072904 | 0.00016798
1 | 14762135 | 2016-12-20 09:02 | 2016-12-20 16:18 | 436 | 11 | 4798.0167 | 0.01439 | 0.014291 | 3.2991e-05 | NAPA ID:25927 TP_BUNNYTHORPE GXP | 11 | Planned | 025927 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P32397 | NONE | This is a Powerco tender, to replace 33kv xarms and poles, and 11kv xarms and hardware between 4 pole structure P32397/P32396/P32395/P32398 and P38742. Note: Per switching will need to be done on 33kV prior to 9am to ensure AP can be issued at 9am | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.0071455 | 5.5 | 2017 | 2016-12-20 | B | 11 | 0.014291 | 3.2991e-05
1 | 14762166 | 2016-12-22 09:02 | 2016-12-22 14:22 | 320 | 1 | 320.1667 | 0.00096022 | 0.000951 | 2.9991e-06 | NAPA ID:25925 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 025925 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P38743 | NONE | This is a Powerco tender, to replace 33kv xarms and poles, and 11kv xarms and hardware between Pole P38743 (Temp ABS 87) and P38760 (ABS E6). Note: Per switching will need to be done on 33kV prior to 9am to ensure AP can be issued at 9am | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.0004755 | 5.5 | 2017 | 2016-12-22 | B | 1 | 0.000951 | 2.9991e-06
1 | 14762215 | 2016-12-21 09:00 | 2016-12-21 15:00 | 360 | 3 | 1080 | 0.0032391 | 0.003212 | 8.9974e-06 | NAPA ID:22029 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 022029 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2170 | NONE | LLP1: Cut the leads supplying FC2170 & install LL covers to the supply conductors. AP: To replace arms & Hardware on Transformer pole & install new fuse arm & fuses (FC2170). LLP2: To reconnect Fuses FC2170. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.001606 | 5.5 | 2017 | 2016-12-21 | B | 3 | 0.003212 | 8.9974e-06
1 | 14762305 | 2016-12-14 14:48 | 2016-12-14 15:19 | 31 | 2 | 62 | 0.00018597 | 0.000167 | 5.9989e-06 | NAPA ID:25344 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ROBERTS LINE | 11 | Planned | 025344 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P02196 | NONE | LLP to Create 11kV line break at H structure pole P02196. AP to replace H structure P45151/P45152. To be completed next day NAPA 25346 and line break closed | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 8.35e-05 | 5.5 | 2017 | 2016-12-14 | B | 2 | 0.000167 | 5.9989e-06
1 | 14762360 | 2016-12-15 09:00 | 2016-12-15 17:02 | 482 | 2 | 964 | 0.0028915 | 0.002873 | 5.9988e-06 | NAPA ID:25346 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ROBERTS LINE | 11 | Planned | 025346 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | AP to Complete new H structure. LLP to close line break at pole P02196/P02197 | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0014365 | 5.5 | 2017 | 2016-12-15 | B | 2 | 0.002873 | 5.9988e-06
1 | 14762585 | 2016-12-14 09:49 | 2016-12-14 11:30 | 101 | 71 | 7171 | 0.021509 | 0.02087 | 0.00021296 | NAPA ID:25605 TP_MANGAMAIRE GXP > PONGAROA SUB > COAST ROAD | 11 | Planned | 025605 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V68 | NONE | To straighten 11kv pole and replace 11kv fuses V68 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.010435 | 5.5 | 2017 | 2016-12-14 | B | 71 | 0.02087 | 0.00021296
1 | 14762663 | 2016-11-24 16:12 | 2016-11-24 18:03 | 111 | 1 | 111.3333 | 0.00033404 | 0.000325 | 3.0003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780879 | FUSE - ELEMENT/LINK (HV) | Reports of arcing effecting TV's and Radios in the area All 3 fuses replaced and connections all checked and tightened Used 3 x 2amp fuses Unable to close sr118751 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000325 | 11 | 2017 | 2016-11-24 | C | 1 | 0.000325 | 3.0003e-06
1 | 14763075 | 2016-11-24 12:32 | 2016-11-24 13:02 | 30 | 55 | 1650 | 0.0049506 | 0.004455 | 0.00016502 | Referral | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-180 | CABLE - REPLACE 5 METRES OR MORE | CR, thump cable. Locate and repair cable. replace U/G cable between fault & transformer TD4 180 Isolation at fused sw 9635/2, generator in service Fault repaired all service restored Materials 1 x termination kit, 1 x through joint kit , 5 x meters 11kV U/G cable | F3 | CENTRAL OTUMOETAI | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.004455 | 11 | 2017 | 2016-11-24 | C | 55 | 0.004455 | 0.00016502
1 | 14765801 | 2016-11-24 21:16 | 2016-11-24 22:08 | 51 | 79 | 4076.4 | 0.012231 | 0.011519 | 0.00023703 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 326084 | JUMPER |  | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.011519 | 11 | 2017 | 2016-11-24 | C | 79 | 0.011519 | 0.00023703
1 | 14765899 | 2016-11-24 21:29 | 2016-11-24 23:47 | 138 | 868 | 37427.85 | 0.1123 | 0.10448 | 0.0026043 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 326084 | JUMPER |  | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.10448 | 11 | 2017 | 2016-11-24 | C | 868 | 0.10448 | 0.0026043
1 | 14766800 | 2016-11-24 21:51 | 2016-11-24 23:32 | 100 | 85 | 8549.5833 | 0.025652 | 0.024886 | 0.00025503 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815702 | INSULATOR | Following auto reclose, Fire Service reported scrub fire at 70 Bidwells Crossing caused by exploded insulator. Fire was under control, no conductors on ground. Area was under 1352 circuit Inspection by Downer staff identified faulty 33kV insulator at pole 815702 requiring replacing. Kempton sub was off loaded via 11kV t/fers, 33kV line isolated at ABS S719 & S59 and CB C956 11kV circuit (on same pole) was isolated at CB C956 & ABS S380 to replace insulator. During restoration, CB C956 was noticed to be discharging arc related noise and evidence of heating by faultman on site. CB opened, removed from service and DNO'd for further investigation. Feeder left backfed. DNO 161120 All supply restored following repairs etc. Bird contact (magpie) on line possibly caused flashover damaging insulator. All 33kV insulators replaced. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.024886 | 11 | 2017 | 2016-11-24 | C | 85 | 0.024886 | 0.00025503
1 | 14767859 | 2016-11-25 05:06 | 2016-11-25 06:59 | 112 | 30 | 3371.5 | 0.010116 | 0.009845 | 9.001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 215886 | FUSE - ELEMENT/LINK (HV) | 2 x 25a mp fuse unknown | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.009845 | 11 | 2017 | 2016-11-25 | C | 30 | 0.009845 | 9.001e-05
1 | 14768813 | 2016-11-25 06:59 | 2016-11-25 09:36 | 157 | 1 | 157.25 | 0.0004718 | 0.000462 | 3.0003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C2837 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp unknown fp129 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000462 | 11 | 2017 | 2016-11-25 | C | 1 | 0.000462 | 3.0003e-06
1 | 14768883 | 2016-11-25 07:10 | 2016-11-25 11:57 | 287 | 334 | 3821 | 0.011464 | 0.008457 | 0.0010021 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 390 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace blown tx 390. Cause auto reclose & trip on rec 8667 when original relivening of tx. Transformer replaced with self issued AP | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.008457 | 11 | 2017 | 2016-11-25 | C | 334 | 0.008457 | 0.0010021
1 | 14768995 | 2016-11-25 07:51 | 2016-11-25 09:44 | 112 | 635 | 56464.8167 | 0.16941 | 0.1637 | 0.0019052 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 3 Tripped E/F Line sectionalised nothing found | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.1637 | 11 | 2017 | 2016-11-25 | C | 635 | 0.1637 | 0.0019052
1 | 14769637 | 2016-11-25 07:51 | 2016-11-25 10:01 | 130 | 2 | 260.1 | 0.00078038 | 0.000762 | 6.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Opunake Hydro REC 6942 tripped e/f . Recloser trips when any fault on sub may need investigation | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000762 | 11 | 2017 | 2016-11-25 | C | 2 | 0.000762 | 6.0006e-06
1 | 14770522 | 2016-12-10 09:00 | 2016-12-10 12:45 | 225 | 5 | 1125 | 0.0033746 | 0.003329 | 1.4998e-05 | NAPA ID:26888 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 026888 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Reading St, Greytown | NONE | Replace red tag 11kv poles issued by GP to be done before christmas | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.0016645 | 5.5 | 2017 | 2016-12-10 | B | 5 | 0.003329 | 1.4998e-05
1 | 14770567 | 2016-11-25 08:23 | 2016-11-25 15:30 | 426 | 91 | 11780.8833 | 0.035346 | 0.034527 | 0.00043505 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773254 | CONDUCTOR - REPAIR/REHANG | Rec 693 tripped on B ph E/F. 1 X Connector. 2m Conductor at pole 773254. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.034527 | 11 | 2017 | 2016-11-25 | C | 91 | 0.034527 | 0.00043505
1 | 14771734 | 2016-11-25 08:56 | 2016-11-25 09:48 | 51 | 21 | 1089.9 | 0.00327 | 0.003081 | 6.3007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I12592 | FUSE - ELEMENT/LINK (HV) | 3 fuses at FC2249 faulty needed replacing Isolated at ABS 782 257413075/1790 materials 3 x fuses complete 3 6amp fuse links | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.003081 | 11 | 2017 | 2016-11-25 | C | 21 | 0.003081 | 6.3007e-05
1 | 14771983 | 2016-11-25 09:21 | 2016-11-25 11:15 | 114 | 1047 | 71521.1833 | 0.21459 | 0.20516 | 0.0031413 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 765563 | INSULATOR | CB 8 Trip O/C E/F line sectionalised found blown insulator at pole 765563 Isolated at ABS 1274 1268 16 Raupo Street - big bang before power went out 1 X Polymer 1 X Deadend Used at ABS 1296 Pole 765563 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.20516 | 11 | 2017 | 2016-11-25 | C | 1047 | 0.20516 | 0.0031413
1 | 14773324 | 2016-11-25 09:31 | 2016-11-25 09:50 | 19 | 3080 | 56364.2667 | 0.16911 | 0.14139 | 0.009241 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | W10 | CIRCUIT BREAKER (HV) | CB W10 TRIP e/f LOS entire sub MAGPIE FOUND ON 33kV STRUCTURE RELIVENED OK removed by hotstick comment made lots of magpies on structure may need bird be gone | S4 | FEILDING-SANSON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.14139 | 33 | 2017 | 2016-11-25 | C | 3080 | 0.14139 | 0.009241
1 | 14776458 | 2016-11-25 09:30 | 2016-11-25 11:09 | 99 | 11 | 1089 | 0.0032673 | 0.003168 | 3.3003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 787258 | POLE | REPLACE POLE 787258 ISOLATED AT ABS244 &1320 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.003168 | 11 | 2017 | 2016-11-25 | C | 11 | 0.003168 | 3.3003e-05
1 | 14777083 | 2016-11-25 12:11 | 2016-11-25 12:34 | 22 | 148 | 3339.8667 | 0.010021 | 0.008688 | 0.00044405 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 358471 | CROSSARM - WHOLE ASSEMBLY |  | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.008688 | 11 | 2017 | 2016-11-25 | C | 148 | 0.008688 | 0.00044405
1 | 14777232 | 2016-11-25 10:24 | 2016-11-25 12:02 | 97 | 3 | 293.05 | 0.00087924 | 0.000852 | 9.0009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 821729 | FUSE - ELEMENT/LINK (HV) | 7583 2 x 8 amp unkown | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000852 | 11 | 2017 | 2016-11-25 | C | 3 | 0.000852 | 9.0009e-06
1 | 14777343 | 2016-11-25 10:38 | 2016-11-25 15:06 | 267 | 329 | 10596.9333 | 0.031794 | 0.028832 | 0.00027303 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | i2979 | CONDUCTOR - REPAIR/REHANG | REC 13080 A/R then Trip O/C E/F LINE PATROLLED fOUND FLOATING WIRE AT POLE I2979 iSOLATED AT abs 2630 9718 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.028832 | 11 | 2017 | 2016-11-25 | C | 329 | 0.028832 | 0.00027303
1 | 14778059 | 2016-12-15 08:25 | 2016-12-15 14:00 | 335 | 3 | 1005 | 0.0030144 | 0.002987 | 8.9983e-06 | NAPA ID:26807 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 026807 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1600 | NONE | Replace poles and reconductor line from links 7458 to T1600. Works location: Southeys Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0014935 | 5.5 | 2017 | 2016-12-15 | B | 3 | 0.002987 | 8.9983e-06
1 | 14778431 | 2016-12-15 08:30 | 2016-12-15 15:35 | 425 | 8 | 3400 | 0.010198 | 0.010126 | 2.3995e-05 | NAPA ID:26791 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11 | Planned | 026791 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1921 | NONE | Replace red tag poles t1921 and 820383. RED TAG POLES 10 day shutdown notice G.P. Works location: Railway Rd, Carterton. WO 30020281 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.005063 | 5.5 | 2017 | 2016-12-15 | B | 8 | 0.010126 | 2.3995e-05
1 | 14778460 | 2016-12-13 09:27 | 2016-12-13 20:44 | 677 | 23 | 1351.6167 | 0.0040542 | 0.003847 | 6.8989e-05 | NAPA ID:25314 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | 025314 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | te6-282 | NONE | install lv frame and jean muller unit [600amp] in low voltage side of te6-282 as cables are connected hard on to transformer bushings | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0019235 | 5.5 | 2017 | 2016-12-13 | B | 23 | 0.003847 | 6.8989e-05
1 | 14779119 | 2016-12-15 10:15 | 2016-12-15 14:25 | 250 | 31 | 7750 | 0.023246 | 0.022966 | 9.2983e-05 | NAPA ID:26656 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 026656 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 839847 | NONE | red tag poles gp. Works location: Masterton Castlepoint Rd. WO 30033228 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.011483 | 5.5 | 2017 | 2016-12-15 | B | 31 | 0.022966 | 9.2983e-05
1 | 14779488 | 2016-12-15 09:18 | 2016-12-15 12:28 | 190 | 48 | 9120 | 0.027355 | 0.026922 | 0.00014397 | NAPA ID:25820 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | 025820 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P04564 | NONE | To repacle 11kv pole p04564 and 11kv fuses V83. Works location: Route 52, Tiraumea. WO 30028904 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.013461 | 5.5 | 2017 | 2016-12-15 | B | 48 | 0.026922 | 0.00014397
1 | 14779797 | 2016-11-25 12:23 | 2016-11-25 12:37 | 14 | 37 | 537.7333 | 0.0016134 | 0.00128 | 0.00011101 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Patrolled Nothing Found | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.00128 | 11 | 2017 | 2016-11-25 | C | 37 | 0.00128 | 0.00011101
1 | 14779975 | 2016-12-15 09:15 | 2016-12-15 13:22 | 247 | 8 | 1976 | 0.0059269 | 0.005854 | 2.3995e-05 | NAPA ID:25275 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 025275 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 7424P | NONE | Istall new TX 7424P on pole P01209 for improve power. Works location: Greens Rd. WO 30025838 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.002927 | 5.5 | 2017 | 2016-12-15 | B | 8 | 0.005854 | 2.3995e-05
1 | 14779997 | 2016-11-25 12:43 | 2016-11-25 13:02 | 19 | 149 | 2835.9667 | 0.0085088 | 0.007167 | 0.00044705 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 783721 | NONE | Trees at Pole 783721 Maybe Cause | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.007167 | 11 | 2017 | 2016-11-25 | C | 149 | 0.007167 | 0.00044705
1 | 14781356 | 2016-12-22 10:00 | 2016-12-22 12:59 | 179 | 4 | 716 | 0.0021474 | 0.002111 | 1.1996e-05 | NAPA ID:25308 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 025308 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5811 | NONE | To replace 11kV Fuse arm & install LV Fuses TC5811. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0010555 | 5.5 | 2017 | 2016-12-22 | B | 4 | 0.002111 | 1.1996e-05
1 | 14781371 | 2016-11-25 14:48 | 2016-11-25 15:52 | 64 | 1 | 64 | 0.00019202 | 0.000183 | 3.0003e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1208 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer T1208. 1R customer had a power outage this morning. Power has been restored but they are still a phase down. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000183 | 11 | 2017 | 2016-11-25 | C | 1 | 0.000183 | 3.0003e-06
1 | 14782130 | 2016-11-25 14:00 | 2016-11-25 18:56 | 296 | 661 | 44571.8167 | 0.13373 | 0.12778 | 0.0039664 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 752492 | CONDUCTOR - REPAIR/REHANG | CB 6777/5 A/R, L/O, E/F, O/C A & B Phase. Sectionalised & partial patrolled with no fault found. Feeder held in for 8 minutes after being fully relivened & then tripped again. Feeder sectionalising restarted & cause was found to be trees in the lines at Pole 752492. Remainder of feeder backfed. Asplundh called in to cut trees. Line was isolated at CB 6777/5 & ABS 208 so tree branches could be cut away from lines. | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.12778 | 11 | 2017 | 2016-11-25 | C | 661 | 0.12778 | 0.0039664
1 | 14783870 | 2016-11-25 14:43 | 2016-11-25 16:11 | 87 | 2 | 174.9333 | 0.00052486 | 0.000506 | 6.0006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771312 | FUSE - ELEMENT/LINK (HV) | 2 X 8AMP FUSE LV TANGELED | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.000506 | 11 | 2017 | 2016-11-25 | C | 2 | 0.000506 | 6.0006e-06
1 | 14783949 | 2016-12-20 08:30 | 2016-12-20 17:15 | 525 | 212 | 25016 | 0.075028 | 0.07312 | 0.0012717 | NAPA ID:25529 TP_CARRINGTON GXP > CITY SUB > CITY 10 | 11 | Planned | 025529 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754070 | NONE | Remove pothead at pole 754070 reterminate existing 11kv cable. 1: AP1 Create 11kV Line break. 2: AP2 Repair pot head. 3: TP: Phasing test. 4: AP3 Close line break. | F3 | CITY 10 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.03656 | 5.5 | 2017 | 2016-12-20 | B | 212 | 0.07312 | 0.0012717
1 | 14784676 | 2016-12-14 08:21 | 2016-12-14 13:46 | 325 | 20 | 6500 | 0.019497 | 0.019316 | 5.999e-05 | NAPA ID:25644 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | 025644 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Quarry Rd, Te Puke | NONE | RE-POLE AND RECON FEEDER | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.009658 | 5.5 | 2017 | 2016-12-14 | B | 20 | 0.019316 | 5.999e-05
1 | 14785434 | 2016-11-25 16:10 | 2016-11-25 19:22 | 191 | 30 | 2465.6833 | 0.0073978 | 0.007127 | 9.001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792691 | INSULATOR | Faultman found a floating wire at pole 792691, line was isolated at Fuses 496 and faultman replaced the insulator pin. 1 X Insulator pin used. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.007127 | 11 | 2017 | 2016-11-25 | C | 30 | 0.007127 | 9.001e-05
1 | 14785590 | 2016-11-25 18:28 | 2016-11-25 19:55 | 86 | 76 | 6567.6667 | 0.019705 | 0.019021 | 0.00022802 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 251 | JUMPER | Faultman found a blown jumper at ABS 251, line was isolated at ABS 906 to repair the jumper. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.019021 | 11 | 2017 | 2016-11-25 | C | 76 | 0.019021 | 0.00022802
1 | 14785926 | 2016-11-25 19:42 | 2016-11-25 22:48 | 186 | 5 | 931 | 0.0027933 | 0.002748 | 1.5002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T589 | CONDUCTOR - REPAIR/REHANG | Has found 2 lines down on the ground. Has requested another fault man, and road traffic management. NDR # TBA. LV conductors clashed blowing HV fuses on transformer T589. LV conductors repaired. 3 x 3 amp HV fuses replaced. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.002748 | 11 | 2017 | 2016-11-25 | C | 5 | 0.002748 | 1.5002e-05
1 | 14786305 | 2016-11-25 22:43 | 2016-11-26 00:49 | 125 | 382 | 35833.15 | 0.10751 | 0.10407 | 0.0011461 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4812/2 | FUSE - ELEMENT/LINK (HV) | Recloser 4812/2 tripped on E/F flags, line was patrolled and sectionalised and no fault was found. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.10407 | 11 | 2017 | 2016-11-25 | C | 382 | 0.10407 | 0.0011461
1 | 14787668 | 2016-11-26 00:30 | 2016-11-26 04:55 | 265 | 171 | 21897.4333 | 0.065698 | 0.064159 | 0.00094209 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 811361 | CONDUCTOR - REPAIR/REHANG | Recloser C604 tripped to L/O. E/F flag. Line sectionalised & patrolled. Lines down (tree through line) at pole 811361. Isolated at fuses 8158. Lines repaired. All supply restored. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.064159 | 11 | 2017 | 2016-11-26 | C | 171 | 0.064159 | 0.00094209
1 | 14788458 | 2016-11-26 03:12 | 2016-11-26 07:30 | 257 | 8 | 2058.1333 | 0.006175 | 0.006102 | 2.4002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 230101 | CONDUCTOR - REPAIR/REHANG | (PGA7) Lines x 2 down at pole 230102. Isolation at Fuses SF6 008 (spur no back feed). Lines repaired all service restored. Materials Used:18 meters conductor, 4 x H/V sleeves. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.006102 | 11 | 2017 | 2016-11-26 | C | 8 | 0.006102 | 2.4002e-05
1 | 14788702 | 2016-11-26 07:52 | 2016-11-26 12:08 | 256 | 24 | 1164.4833 | 0.0034938 | 0.003277 | 7.5007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717070 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replace 1 X DDO at Tranformer T5170 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.003277 | 11 | 2017 | 2016-11-26 | C | 24 | 0.003277 | 7.5007e-05
1 | 14789042 | 2016-11-26 09:20 | 2016-11-26 10:50 | 90 | 2 | 180 | 0.00054005 | 0.000522 | 6.0005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6231 | FUSE - ELEMENT/LINK (HV) | 2 X 2amp Wind | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000522 | 11 | 2017 | 2016-11-26 | C | 2 | 0.000522 | 6.0005e-06
1 | 14789113 | 2016-11-26 21:02 | 2016-11-26 23:10 | 128 | 246 | 31561.8 | 0.094694 | 0.092479 | 0.00073807 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797165 | POLE | Pole on lean, no known accident in area to cause this. Pole is on top of hill and in dense gorse so may be awkward to access. Pole 797165. Replaced pole complete. | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.092479 | 11 | 2017 | 2016-11-26 | C | 246 | 0.092479 | 0.00073807
1 | 14789488 | 2016-11-26 12:15 | 2016-11-26 13:45 | 89 | 726 | 49509.75 | 0.14854 | 0.14201 | 0.0021782 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P34307 | CONDUCTOR - REPAIR/REHANG | Banches on Line at Pole P34307 Removed with Hotsticks | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.14201 | 11 | 2017 | 2016-11-26 | C | 726 | 0.14201 | 0.0021782
1 | 14790914 | 2016-11-26 12:25 | 2016-11-26 15:10 | 164 | 2 | 329.9667 | 0.00098999 | 0.000971 | 6.0005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 2704 | CONDUCTOR - REPAIR/REHANG | Trees in line 2 Fuses Blown when got there removed last one to remove trees. 2 x 6Amp Fuses. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000971 | 11 | 2017 | 2016-11-26 | C | 2 | 0.000971 | 6.0005e-06
1 | 14792400 | 2016-11-26 14:47 | 2016-11-26 20:22 | 335 | 1041 | 27448.1333 | 0.082352 | 0.072982 | 0.0031233 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 220874 | CONDUCTOR - REPAIR/REHANG | PMA 3 tripped A, B & C Ph O/C, E/F, L/O. Report from tree fellers ( CAC 33680) tree contacted line Isolation at ABS SD5 182 ( spur no back feeds ) Remainder of feeder returned to service NDR to come 1 x pole 2 spans of wire 4 x crossarms | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.072982 | 11 | 2017 | 2016-11-26 | C | 1041 | 0.072982 | 0.0031233
1 | 14794735 | 2016-11-26 18:30 | 2016-11-26 19:25 | 55 | 1 | 55 | 0.00016501 | 0.000156 | 3.0002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B34 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuse at Fuses B34 and a broken jumper at Fuses B34 this caused the fuse to blown. Fuses B34 were isolated to repair the jumper. 1 X 10 amp HV fuse replaced. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000156 | 11 | 2017 | 2016-11-26 | C | 1 | 0.000156 | 3.0002e-06
1 | 14795223 | 2016-11-26 19:08 | 2016-11-26 22:29 | 201 | 316 | 25925.4 | 0.077783 | 0.074939 | 0.00094809 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | P42910 | CONDUCTOR - REPAIR/REHANG | CB 23 tripped on A, B & C phase O/C & E/F flags, received a call from retailer of lines down on Healy Rd, line was isolated at ABS's B1, B2, B3 & B4 & transformer T2/334 to repair the line at pole P42910 that was broken by a falling branch. 10 meters squirrel conductor used. 3 X compression sleeves used. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.074939 | 11 | 2017 | 2016-11-26 | C | 316 | 0.074939 | 0.00094809
1 | 14797722 | 2016-11-27 05:07 | 2016-11-27 10:06 | 299 | 2 | 598.7333 | 0.0017963 | 0.001778 | 6.0004e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1310 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faulty transformer replaced. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.001778 | 11 | 2017 | 2016-11-27 | C | 2 | 0.001778 | 6.0004e-06
1 | 14797829 | 2016-11-27 05:15 | 2016-11-27 08:13 | 178 | 94 | 12415.8667 | 0.03725 | 0.036404 | 0.00028202 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P23699 | CONDUCTOR - REPAIR/REHANG | Tripping on Parkvile CB4 on EF. Patrol found floating conductor at Pole P23699. Isolation required from ABS U36 to end. One jointer required, relivened OK. High winds | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.036404 | 11 | 2017 | 2016-11-27 | C | 94 | 0.036404 | 0.00028202
1 | 14798676 | 2016-11-27 05:20 | 2016-11-27 11:10 | 350 | 586 | 118755.1667 | 0.35629 | 0.35102 | 0.0017581 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797445 | CONDUCTOR - REPAIR/REHANG | TUH C928 tripped A & B Ph O/C, L/O Feeder sectionalised with floating conductors found at pole 797445 Isolation at ABS S562 with remainder of feeder returned to service Conductors repaired all service restored | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.35102 | 11 | 2017 | 2016-11-27 | C | 586 | 0.35102 | 0.0017581
1 | 14800216 | 2016-11-27 05:36 | 2016-11-27 10:42 | 306 | 109 | 25227.7833 | 0.075689 | 0.074708 | 0.00040803 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 14800216 | CONDUCTOR - REPAIR/REHANG | FEA C916 recloser C634 tripped E/F, L/O Feeder sectionalised with broken conductor found at pole 798579. Isolation at fuses 7261 ( spur ) rest of feeder returned to service Conductor repaired all service restored | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.074708 | 11 | 2017 | 2016-11-27 | C | 109 | 0.074708 | 0.00040803
1 | 14800609 | 2016-11-27 05:38 | 2016-11-27 12:19 | 400 | 97 | 21704.6333 | 0.065119 | 0.064245 | 0.00050404 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 798862 | CONDUCTOR - REPAIR/REHANG | Outage required past Fuses 7298 & ABS S565 for multiple faults with trees through lines and lines down. No backfeeds available. Removed trees, replaced 6m conductor, 6 joints | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.064245 | 11 | 2017 | 2016-11-27 | C | 97 | 0.064245 | 0.00050404
1 | 14801573 | 2016-11-27 05:52 | 2016-11-27 10:17 | 264 | 12 | 2994.4 | 0.0089839 | 0.008875 | 3.6003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 799275 | CONDUCTOR - REPAIR/REHANG | Recloser C640 tripped and locked out. Branch found on the line at pole 799275. NDR 600018 | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.008875 | 11 | 2017 | 2016-11-27 | C | 12 | 0.008875 | 3.6003e-05
1 | 14802554 | 2016-11-27 06:13 | 2016-11-27 08:07 | 114 | 298 | 34091.2 | 0.10228 | 0.099599 | 0.00089407 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | ALF-PON 33kV | UNKNOWN | Tripping on Parkville 33kV CB XT40 (B Phase E/F) causing loss of supply Alfredton. ABS XT56 Open at Alfredton and supply restored from Parkville. Crew replacement in place for full patrol. (Delay in restoration due to loss of comms at Parkville - ongoing problem). Hele patrol organised between NCTL and Gavin Paget due to remote area. Helicptor patrol carried out but nothing found. All restored to normal. | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.099599 | 33 | 2017 | 2016-11-27 | C | 298 | 0.099599 | 0.00089407
1 | 14804313 | 2016-11-27 06:11 | 2016-11-27 07:54 | 103 | 2 | 206.5667 | 0.00061975 | 0.000601 | 6.0004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 390173 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A H/V O/H fuses at FP48 ( line clash ) | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000601 | 11 | 2017 | 2016-11-27 | C | 2 | 0.000601 | 6.0004e-06
1 | 14804334 | 2016-11-27 06:14 | 2016-11-27 12:34 | 380 | 237 | 66895.6 | 0.2007 | 0.19857 | 0.00071105 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 849964 | CONDUCTOR - REPAIR/REHANG |  | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.19857 | 11 | 2017 | 2016-11-27 | C | 237 | 0.19857 | 0.00071105
1 | 14805179 | 2016-11-27 06:42 | 2016-11-27 14:55 | 492 | 20 | 9856.6667 | 0.029572 | 0.029392 | 6.0004e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 834757 | FUSE - ELEMENT/LINK (HV) | Upgraded to HV extent - please check other jobs when closing 2 x 10 amp weather | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.029392 | 11 | 2017 | 2016-11-27 | C | 20 | 0.029392 | 6.0004e-05
1 | 14805652 | 2016-11-27 07:27 | 2016-11-27 16:53 | 566 | 63 | 22589.4833 | 0.067774 | 0.067206 | 0.00018901 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 816286 | CONDUCTOR - REPAIR/REHANG | Outage required past ABS S541 to repair floating conductor. No backfeeds available. Live rebound, relivened OK | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.067206 | 11 | 2017 | 2016-11-27 | C | 63 | 0.067206 | 0.00018901
1 | 14805684 | 2016-11-27 07:34 | 2016-11-27 10:38 | 184 | 28 | 5165.5333 | 0.015498 | 0.015245 | 8.4006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V16 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses tripped at V16. Reloaded OK. (10A Rating). High winds | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.015245 | 11 | 2017 | 2016-11-27 | C | 28 | 0.015245 | 8.4006e-05
1 | 14806764 | 2016-11-27 09:12 | 2016-11-27 14:05 | 293 | 1456 | 140931 | 0.42283 | 0.40972 | 0.0043683 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 821133 | CONDUCTOR - REPAIR/REHANG | CLV CB C838 tripped O/C, L/O Perrys Road and Taumata Island Road reports of lines down NDR - tree through line HV repaired broken cross arm and one span of conductor | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.40972 | 11 | 2017 | 2016-11-27 | C | 1456 | 0.40972 | 0.0043683
1 | 14809709 | 2016-11-30 16:04 | 2016-11-30 16:57 | 53 | 10 | 530 | 0.0015901 | 0.0015 | 3.0001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10792 | POLE | 2 HT Fuses found tripped at I26. Faultl had also tripped CB I23 at Alfredton Sub, reclosed OK.Problem traced to broken Transformer Pole T9/386. Isolation required from Fuses I23. Generators installed at Transformers T9/386, T9/387, T9/391 &, T9/394 Pole broke due conductor breaking due to age and twisting pole Full list of Equipment to be provided at a later date used 1 x pole, 1 x 30 kVA 3ph transformer, approx 120 mtrs conductor, 4 x anchors, 2 x sleeves, | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0015 | 11 | 2017 | 2016-11-30 | C | 10 | 0.0015 | 3.0001e-05
1 | 14809901 | 2016-11-27 09:59 | 2016-11-27 15:40 | 341 | 9 | 3069.75 | 0.0092099 | 0.009128 | 2.7002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 826205 | FUSE - ELEMENT/LINK (HV) | BRANCH ON LINE at pole 826205 | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.009128 | 11 | 2017 | 2016-11-27 | C | 9 | 0.009128 | 2.7002e-05
1 | 14810094 | 2016-11-27 10:05 | 2016-11-27 16:33 | 388 | 78 | 25167.3333 | 0.075508 | 0.074805 | 0.00023402 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 832169 | CONDUCTOR - REPAIR/REHANG | Initial tripping on recloser CB7417 on A Phase OC, EF. Fire called in 2 lines down on Craigie Lea Road - isolation required from fuses 7993. Repairs carried out following day with 6 metres No.8 conductor used with 3 sleeves. Relivened OK. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.074805 | 11 | 2017 | 2016-11-27 | C | 78 | 0.074805 | 0.00023402
1 | 14810829 | 2016-11-27 10:21 | 2016-11-28 14:47 | 1706 | 316 | 61517.0667 | 0.18457 | 0.18172 | 0.00094807 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 827915 | POLE | Advised SMC and Control Isolated for fire, pole 827893. 7133 on C3830 with control Initial reports of Fire, line down. CB C830 open from NOC. (Later found that Sectioanliser 213/2 had tripped). Isolation made from fuses 7113. Work completed next day with a Pole and double pin arm replaced. Relivened OK and CB 213/3 reclosed. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.18172 | 11 | 2017 | 2016-11-27 | C | 316 | 0.18172 | 0.00094807
1 | 14812003 | 2016-11-27 10:42 | 2016-11-27 12:21 | 98 | 31 | 3045.75 | 0.0091379 | 0.008858 | 9.3007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 5301 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses found tripped at 5301. Patrolled, recllosed OK. (10A Rating) | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.008858 | 11 | 2017 | 2016-11-27 | C | 31 | 0.008858 | 9.3007e-05
1 | 14814087 | 2016-11-27 11:43 | 2016-11-27 13:27 | 103 | 360 | 37320 | 0.11197 | 0.10873 | 0.0010801 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 367312 | CONDUCTOR - REPAIR/REHANG | Branch on line at Pole 367312. Fire brigade on site. Adam confirmed he has left site and closed this job off with Control. Progressed him to complete so I can sign off 14819992 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.10873 | 11 | 2017 | 2016-11-27 | C | 360 | 0.10873 | 0.0010801
1 | 14814498 | 2016-11-27 11:51 | 2016-11-27 13:10 | 78 | 8 | 629.2 | 0.0018877 | 0.001815 | 2.4002e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 737919 | NONE | Tripping on Recloser CB 6551 on Phase B, OC. Patrol carried out up to Mountain house. Evidence of burnt branch that had fallen down through lines. Reclosed OK. Mountain House checked out OK. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.001815 | 6.6 | 2017 | 2016-11-27 | C | 8 | 0.001815 | 2.4002e-05
1 | 14814918 | 2016-11-27 12:43 | 2016-11-27 13:23 | 40 | 218 | 8720 | 0.026162 | 0.024199 | 0.00065405 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 357781 | CROSSARM - WHOLE ASSEMBLY | Replace king bolt at xarm on pole 357781 | F3 | NAPLES ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.024199 | 11 | 2017 | 2016-11-27 | C | 218 | 0.024199 | 0.00065405
1 | 14816070 | 2016-11-27 14:07 | 2016-11-27 20:08 | 361 | 1 | 361.1 | 0.0010834 | 0.001074 | 3.0002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t1192 | FUSE - ELEMENT/LINK (HV) | replace 3 x 2amp ht fuses LT still to be repaired chased hub Transformer replaced on 14827225. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.001074 | 11 | 2017 | 2016-11-27 | C | 1 | 0.001074 | 3.0002e-06
1 | 14816077 | 2016-11-27 14:52 | 2016-11-27 17:33 | 161 | 15 | 2415 | 0.0072456 | 0.00711 | 4.5003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838336 | CONDUCTOR - REPAIR/REHANG | Lines down x 1 at pole 838336. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.00711 | 11 | 2017 | 2016-11-27 | C | 15 | 0.00711 | 4.5003e-05
1 | 14816529 | 2016-11-27 14:22 | 2016-11-27 16:55 | 153 | 373 | 13349.0333 | 0.04005 | 0.036692 | 0.0011191 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O278 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | WHI CB2 tripped E/F, L/O Feeder sectionalsed with lines down found at pole 0278 & king bolt faulted Isolation at Fuses FC2235 ( spur no back feed ) rest of feeder returned to service Lines & king bolt repaired all service restored Material 8 x H/V Sleeves, 10 Meters conductor | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.036692 | 11 | 2017 | 2016-11-27 | C | 373 | 0.036692 | 0.0011191
1 | 14817837 | 2016-11-28 00:31 | 2016-11-28 01:39 | 68 | 29 | 1972 | 0.0059164 | 0.005655 | 8.7006e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T6/575 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer voltage on 2 phase - Fuses all checked OK. faullty transformer to be replaced (Staff shortage due to storm event). Will be carried out when staff available - job now 2R. 1 X 30kVA Transformer 3 X 3 Amp Fuses Hardware Etc | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.005655 | 11 | 2017 | 2016-11-28 | C | 29 | 0.005655 | 8.7006e-05
1 | 14817881 | 2016-11-27 16:14 | 2016-11-27 17:04 | 50 | 24 | 1202 | 0.0036063 | 0.00339 | 7.2005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/266 | JUMPER | Patrol found a blown jumper at Transformer T9/266. Outage required from fuses V66 to repair jumper. Relivened OK. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.00339 | 11 | 2017 | 2016-11-27 | C | 24 | 0.00339 | 7.2005e-05
1 | 14818084 | 2016-11-27 15:25 | 2016-11-27 22:16 | 411 | 1 | 411.15 | 0.0012335 | 0.001224 | 3.0002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7497 | FUSE - ELEMENT/LINK (HV) | replaced 2 x amp ht fuses | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.001224 | 11 | 2017 | 2016-11-27 | C | 1 | 0.001224 | 3.0002e-06
1 | 14818324 | 2016-11-27 15:44 | 2016-11-27 20:42 | 297 | 342 | 66704.4333 | 0.20013 | 0.19705 | 0.0010261 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9876/2 | LIGHTNING ARRESTOR (HV) | Sectionalised and found lightning arrestor faulty at 9876/2 Isolated betweem ABS sd5-001, IP119, sd4-372, 9876/1 & 9876/6 Disconnected & relivened | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.19705 | 11 | 2017 | 2016-11-27 | C | 342 | 0.19705 | 0.0010261
1 | 14818673 | 2016-11-27 15:46 | 2016-11-28 10:08 | 1102 | 1 | 1102.25 | 0.003307 | 0.003298 | 3.0002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21616 | FUSE - ELEMENT/LINK (HV) | replaced 2 x HV fuses - 3 amp fuses M83 - due to line clash Got permission to access HV Cam and Nev Morris leaving site now. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.003298 | 11 | 2017 | 2016-11-27 | C | 1 | 0.003298 | 3.0002e-06
1 | 14819181 | 2016-11-27 07:36 | 2016-11-28 13:59 | 1823 | 29 | 47660.1167 | 0.14299 | 0.14273 | 8.7007e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 371784 | CONDUCTOR - REPAIR/REHANG | 11kV NON-SCADA-ised Sectionaliser tripped at unknown time on the 27th. Due to remote area and time, left off over night. Hele-patrolled and found a line down at pole 371784, iso from sectionaliser. All power restored at 1242hrs on the 28th. Hele patrol organised between NCTL and Gavin Paget due to remote area. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.14273 | 11 | 2017 | 2016-11-27 | C | 29 | 0.14273 | 8.7007e-05
1 | 14820048 | 2016-11-27 16:17 | 2016-11-27 19:47 | 210 | 2 | 420.3667 | 0.0012612 | 0.001243 | 6.0004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784412 | FUSE - ELEMENT/LINK (HV) | 2 X6 Amp Trees | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001243 | 11 | 2017 | 2016-11-27 | C | 2 | 0.001243 | 6.0004e-06
1 | 14820105 | 2016-11-27 16:24 | 2016-11-27 19:12 | 167 | 1 | 167.6167 | 0.00050289 | 0.000493 | 3.0002e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | - | UNKNOWN | Part of 14820142 Is fed from TD3-290 - NI Admins to be informed Customer confirmed full power restored 15 mins ago Mike did go to site | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000493 | 11 | 2017 | 2016-11-27 | C | 1 | 0.000493 | 3.0002e-06
1 | 14820113 | 2016-11-27 15:58 | 2016-11-27 18:16 | 138 | 83 | 11495.5 | 0.034489 | 0.033742 | 0.00024902 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 230772 | CONDUCTOR - REPAIR/REHANG | Sec 9875 tripped E/F O/C A and C ph. 10m conductor and 4 x sleeves. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.033742 | 11 | 2017 | 2016-11-27 | C | 83 | 0.033742 | 0.00024902
1 | 14821098 | 2016-11-27 16:57 | 2016-11-28 00:05 | 428 | 91 | 3578.3667 | 0.010736 | 0.009916 | 0.00027302 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc1026 | JUMPER | SMC advised Kyle is on stand down - Terry is assigned to attend after sorting out Kohutara Road. Found jumper broken at TC1026. Isolated between ABS S513 & S525, repaired & relivened. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.009916 | 11 | 2017 | 2016-11-27 | C | 91 | 0.009916 | 0.00027302
1 | 14821410 | 2016-11-27 17:07 | 2016-11-27 22:22 | 315 | 106 | 30156.2 | 0.090475 | 0.089521 | 0.00031802 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PO4808 | INSULATOR | 6 X Clamp Top Insulators At Pole Po4808 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.089521 | 11 | 2017 | 2016-11-27 | C | 106 | 0.089521 | 0.00031802
1 | 14822463 | 2016-11-27 19:01 | 2016-11-27 19:10 | 9 | 93 | 888.15 | 0.0026647 | 0.001827 | 0.00027902 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | A & C Phase OC Closed atfer 10 mins | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.001827 | 11 | 2017 | 2016-11-27 | C | 93 | 0.001827 | 0.00027902
1 | 14822644 | 2016-11-27 19:00 | 2016-11-27 22:49 | 229 | 204 | 2059 | 0.0061775 | 0.004341 | 0.00021302 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fp1816 | JUMPER | Found jumper broken at FP1816, isolated between SD5-008 & SD5-009, repaired & relivened. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.004341 | 11 | 2017 | 2016-11-27 | C | 204 | 0.004341 | 0.00021302
1 | 14824716 | 2016-11-27 15:47 | 2016-11-27 22:43 | 416 | 54 | 22474.8 | 0.06743 | 0.066943 | 0.00016201 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7316 | JUMPER | Found jumper broken at 7316. Isolated between S525 & S1201, repaired jumper & relivened. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.066943 | 11 | 2017 | 2016-11-27 | C | 54 | 0.066943 | 0.00016201
1 | 14825005 | 2016-11-27 22:27 | 2016-11-28 02:12 | 224 | 480 | 50985.8333 | 0.15297 | 0.14865 | 0.0014401 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | I1226 | CONDUCTOR - REPAIR/REHANG | Found tree in line . isolated between ABS ic2579, ic2524 & IP496. Removed tree & relivened | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.14865 | 11 | 2017 | 2016-11-27 | C | 480 | 0.14865 | 0.0014401
1 | 14827225 | 2016-11-28 13:40 | 2016-11-28 15:45 | 125 | 4 | 500 | 0.0015001 | 0.001464 | 1.2001e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1192 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Defective transformer T1192 replaced & livened / tested OK. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.001464 | 11 | 2017 | 2016-11-28 | C | 4 | 0.001464 | 1.2001e-05
1 | 14827237 | 2016-11-28 07:33 | 2016-11-28 10:38 | 185 | 347 | 19701.1833 | 0.059107 | 0.055984 | 0.00081005 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 832052 | CONDUCTOR - REPAIR/REHANG | Tripping on CB C948 on B Phase, EF to lock out. Fault caused by Contractor (Harvard logging) bringing down a conductor with their digger). Isolation required from ABS C420/1 to end. Repaired and relivened. 10m conductor required, 3 sleeves. Awating NDR. NOTE: CB 946 opened from NOC due to SCADA Link error. (That OMS linked to this job). Reclosed within a minute. Safety Manager number 683282. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.055984 | 11 | 2017 | 2016-11-28 | C | 347 | 0.055984 | 0.00081005
1 | 14827578 | 2016-11-28 07:37 | 2016-11-28 12:36 | 299 | 1120 | 65986.1333 | 0.19797 | 0.18789 | 0.0033602 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 790084 | CONDUCTOR - REPAIR/REHANG | PST CB 4747-3 tripped B phase EF. Tree broke 1 conductor and damaged another. Feeder backfeeding ROB7 & ROB4 Outage required on ROB4 past Fuses 705. No backfeeds available. Replaced 50m conductor, 6 x sleeves. relivened OK | F3 | ARAMOHO RIVERSIDE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.18789 | 11 | 2017 | 2016-11-28 | C | 1120 | 0.18789 | 0.0033602
1 | 14828619 | 2016-11-25 08:20 | 2016-11-25 10:35 | 135 | 19 | 2565 | 0.0076958 | 0.007524 | 5.7006e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2621 | FUSE - ELEMENT/LINK (HV) | RECREATION OF 14788733 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.007524 | 11 | 2017 | 2016-11-25 | C | 19 | 0.007524 | 5.7006e-05
1 | 14828874 | 2016-12-14 09:18 | 2016-12-14 14:30 | 312 | 1 | 312 | 0.00093584 | 0.000926 | 2.9994e-06 | NAPA ID:25475 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 025475 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 207499 | NONE | Install New Xarms at pole 207499 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.000463 | 5.5 | 2017 | 2016-12-14 | B | 1 | 0.000926 | 2.9994e-06
1 | 14829347 | 2016-11-28 08:29 | 2016-11-28 12:27 | 237 | 1 | 237.8667 | 0.00071365 | 0.000704 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837953 | FUSE - ELEMENT/LINK (HV) | 2 X3AMP UNKNOWN | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.000704 | 11 | 2017 | 2016-11-28 | C | 1 | 0.000704 | 3.0001e-06
1 | 14829647 | 2016-12-16 08:35 | 2016-12-16 14:40 | 365 | 4 | 1460 | 0.0043791 | 0.004343 | 1.1997e-05 | NAPA ID:26762 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 026762 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7462 to t1883 | NONE | replace crossarms and reconductor from links 7462 to t1883 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0021715 | 5.5 | 2017 | 2016-12-16 | B | 4 | 0.004343 | 1.1997e-05
1 | 14829657 | 2016-11-28 08:47 | 2016-11-28 09:59 | 72 | 7 | 504.1167 | 0.0015124 | 0.001449 | 2.1001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 785894 | FUSE - ELEMENT/LINK (HV) | 2 X 6AMP 2954 WIND | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001449 | 11 | 2017 | 2016-11-28 | C | 7 | 0.001449 | 2.1001e-05
1 | 14829744 | 2016-12-21 09:31 | 2016-12-21 14:28 | 297 | 6 | 1782.2 | 0.0053451 | 0.005291 | 1.7995e-05 | NAPA ID:26861 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 026861 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P16151 | NONE | To replace red tagged pole P16151 (GP) | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0026455 | 5.5 | 2017 | 2016-12-21 | B | 6 | 0.005291 | 1.7995e-05
1 | 14832805 | 2016-11-28 11:00 | 2016-11-28 14:10 | 189 | 2 | 365.7667 | 0.0010974 | 0.001079 | 6.0003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 827192 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuses wind tx t 954 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.001079 | 11 | 2017 | 2016-11-28 | C | 2 | 0.001079 | 6.0003e-06
1 | 14832876 | 2016-11-28 11:36 | 2016-11-28 15:15 | 218 | 771 | 72788.3333 | 0.21838 | 0.21144 | 0.0023131 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P05132 | CONDUCTOR - REPAIR/REHANG | Tripping on Kimbolton CB7 on Phase B-B OC. Feeder patrolled and sectionalised with the fault found beyond Recloser K45 (Recloser faulty, to be defected). 2 Conductors found wrapped up together due to the high wind. Unwrapped OK and relivened. . 9/12 completed by Alf Downs and relivened. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.21144 | 11 | 2017 | 2016-11-28 | C | 771 | 0.21144 | 0.0023131
1 | 14832986 | 2016-11-28 11:21 | 2016-11-28 17:51 | 389 | 2 | 778.9333 | 0.0023369 | 0.002318 | 6.0003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 2704 | NONE | Tripping on fuses 2704. Ongoing tree issue, opportunity taken to cut away branches (Tree contractors called out). Vegetation cleared, relivened. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.002318 | 11 | 2017 | 2016-11-28 | C | 2 | 0.002318 | 6.0003e-06
1 | 14833065 | 2016-11-28 11:29 | 2016-11-28 13:42 | 132 | 1 | 132.35 | 0.00039708 | 0.000388 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06080 | FUSE - ELEMENT/LINK (HV) | 2 sectional T41 P06080 2 x 15 amp HV fuses | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000388 | 11 | 2017 | 2016-11-28 | C | 1 | 0.000388 | 3.0001e-06
1 | 14833155 | 2016-11-28 11:35 | 2016-11-28 13:03 | 88 | 688 | 52115.4833 | 0.15636 | 0.15016 | 0.0020641 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 793690 | CONDUCTOR - REPAIR/REHANG | PUK4 tripped O/C branch removed from line at pole 793690 | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.15016 | 11 | 2017 | 2016-11-28 | C | 688 | 0.15016 | 0.0020641
1 | 14834749 | 2016-11-28 11:54 | 2016-11-28 13:31 | 96 | 41 | 3970.1667 | 0.011911 | 0.011542 | 0.00012301 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217325 | FUSE - ELEMENT/LINK (HV) | 2 x 15 amp se2-001 1331 line clash due to wind te2-001 no materials just placed back fuse | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.011542 | 11 | 2017 | 2016-11-28 | C | 41 | 0.011542 | 0.00012301
1 | 14836476 | 2016-12-14 09:00 | 2016-12-14 15:07 | 367 | 20 | 7340 | 0.022016 | 0.021836 | 5.999e-05 | NAPA ID:25446 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | 025446 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CFC 13145 | NONE | Replace poles, hardware and conductor. Commission new CFC 13145 and associated 11kV Cables | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.010918 | 5.5 | 2017 | 2016-12-14 | B | 20 | 0.021836 | 5.999e-05
1 | 14836590 | 2016-12-16 08:45 | 2016-12-16 13:43 | 298 | 11 | 3278 | 0.009832 | 0.009733 | 3.2993e-05 | NAPA ID:25466 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | 025466 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 580 No 4 Rd Te Puke | NONE | Replace poles, hardware and conductor. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.0048665 | 5.5 | 2017 | 2016-12-16 | B | 11 | 0.009733 | 3.2993e-05
1 | 14836628 | 2016-12-01 10:00 | 2016-12-01 14:26 | 265 | 41 | 10902.5833 | 0.032708 | 0.032339 | 0.000123 | NAPA ID:26330 TP_STRATFORD GXP | 11 | Planned | 026330 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Remove Temp Recloser 12153 on pole 734729 close Mid span line break + Replace DNO Abs 5833 with new Sectos switch | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.016169 | 5.5 | 2017 | 2016-12-01 | B | 41 | 0.032339 | 0.000123
1 | 14837445 | 2016-11-28 13:22 | 2016-11-28 13:49 | 27 | 527 | 13145.2 | 0.039438 | 0.034694 | 0.0015811 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | D12545 | UNKNOWN | Recloser 9773/2 Trip B O/C line patrolled, Suspected line clash as line crosses waikato river pole D12545 Line Patrolled NO fault found | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.034694 | 11 | 2017 | 2016-11-28 | C | 527 | 0.034694 | 0.0015811
1 | 14838038 | 2016-12-20 08:45 | 2016-12-20 13:15 | 270 | 20 | 5400 | 0.016196 | 0.016015 | 5.9984e-05 | NAPA ID:25468 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | 025468 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 580 No 4 Rd Te Puke | NONE | Replace poles, hardware and conductor. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.0080075 | 5.5 | 2017 | 2016-12-20 | B | 20 | 0.016015 | 5.9984e-05
1 | 14841744 | 2016-11-28 14:22 | 2016-11-28 15:15 | 53 | 49 | 2597 | 0.0077915 | 0.00735 | 0.00014701 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 229059 | NONE | Faultman found a branch between poles 229058 & 229059 that was hanging very close to the lines, line was isolated at ABS 9833/1 & links 9833/6 to remove the branch using Live Line Procedures. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.00735 | 11 | 2017 | 2016-11-28 | C | 49 | 0.00735 | 0.00014701
1 | 14841808 | 2016-11-28 17:15 | 2016-11-28 20:15 | 180 | 2 | 360 | 0.0010801 | 0.001062 | 6.0003e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/493 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | REPLACE 1 X 15kVA TX DEFECTIVE UNKNOWN REASON | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.001062 | 11 | 2017 | 2016-11-28 | C | 2 | 0.001062 | 6.0003e-06
1 | 14841850 | 2016-12-14 08:45 | 2016-12-14 14:15 | 330 | 20 | 6600 | 0.019797 | 0.019616 | 5.999e-05 | NAPA ID:26803 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 026803 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Ngaro Road | NONE | Replace various poles and xarms in work area | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.009808 | 3.3 | 2017 | 2016-12-14 | B | 20 | 0.019616 | 5.999e-05
1 | 14841944 | 2016-12-16 09:50 | 2016-12-16 15:25 | 335 | 20 | 6700 | 0.020096 | 0.019915 | 5.9988e-05 | NAPA ID:26805 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 026805 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Ngaro Road | NONE | reconductor 6.6kv lines | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.0099575 | 3.3 | 2017 | 2016-12-16 | B | 20 | 0.019915 | 5.9988e-05
1 | 14842053 | 2016-11-28 14:37 | 2016-11-28 16:31 | 114 | 8 | 918.8 | 0.0027566 | 0.002684 | 2.4002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 817434 | FUSE - ELEMENT/LINK (HV) | 7919 wind 2 x 10 amp | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.002684 | 11 | 2017 | 2016-11-28 | C | 8 | 0.002684 | 2.4002e-05
1 | 14842447 | 2016-12-20 09:33 | 2016-12-20 14:02 | 269 | 93 | 25037.15 | 0.075092 | 0.074254 | 0.00027893 | NAPA ID:26862 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 026862 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P16136 | NONE | To replace red tagged poles P16136, P16113, P15193 & P12301 in Eketahuna township (GP) | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.037127 | 5.5 | 2017 | 2016-12-20 | B | 93 | 0.074254 | 0.00027893
1 | 14842481 | 2016-11-28 14:48 | 2016-11-28 14:56 | 8 | 48 | 384 | 0.0011521 | 0.00072 | 0.00014401 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738122 | UNKNOWN | Switching to restore power past ABS 6167. Jumper broken at ABS 6167. Feed back feed from ABS 6034. DNO Created 161123 | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.00072 | 11 | 2017 | 2016-11-28 | C | 48 | 0.00072 | 0.00014401
1 | 14843176 | 2016-11-28 15:16 | 2016-11-28 20:02 | 286 | 93 | 14808.1167 | 0.044427 | 0.04359 | 0.00039303 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n21 | UNKNOWN | cb n21 TRIP e/f LINE PATROLLED NOTHING FOUND | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.04359 | 11 | 2017 | 2016-11-28 | C | 93 | 0.04359 | 0.00039303
1 | 14846710 | 2016-11-28 17:20 | 2016-11-28 19:10 | 109 | 1 | 109.5833 | 0.00032877 | 0.000319 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P29 | FUSE - ELEMENT/LINK (HV) | 2 X3 amp Bird | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000319 | 11 | 2017 | 2016-11-28 | C | 1 | 0.000319 | 3.0001e-06
1 | 14847178 | 2016-11-28 17:38 | 2016-11-28 20:40 | 182 | 9 | 1639.8 | 0.0049197 | 0.004838 | 2.7002e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 816496 | FUSE - ELEMENT/LINK (HV) | Replace 2 x H/V O/H fuses at fuses 7387 ( line clash ) | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.004838 | 11 | 2017 | 2016-11-28 | C | 9 | 0.004838 | 2.7002e-05
1 | 14847700 | 2016-11-28 14:34 | 2016-11-28 19:07 | 273 | 1 | 273.1167 | 0.0008194 | 0.00081 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | 2 X 3 Amp Wind | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00081 | 11 | 2017 | 2016-11-28 | C | 1 | 0.00081 | 3.0001e-06
1 | 14848090 | 2016-11-28 20:22 | 2016-11-29 09:05 | 763 | 1 | 763 | 0.0022891 | 0.00228 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K13129 | FUSE - ELEMENT/LINK (HV) | No Power at Environmental Monitoring site very small shed/house at end of road since 8pm 23/11/16. Off SH27 - turn right, at very end of road next to river. Cane Lynn 07 859 0754 / 021 683 455 10.34pm Debs at svs hub called customer and advised that they have contacted the customer and the customer is ok for FM to attend tomorrow during day light hours as no one lives onsite 3x6 amp HV fuses blown at FC2203 Line Patrolled & reloaded & Livened outage on child | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.00228 | 11 | 2017 | 2016-11-28 | C | 1 | 0.00228 | 3.0001e-06
1 | 14848100 | 2016-11-28 20:58 | 2016-11-28 21:21 | 23 | 546 | 5543.5 | 0.016632 | 0.011717 | 0.0016381 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219758 | AIR BREAK SWITCH - ABS (HV) | 8.30pm advised Debs at svs hub of job ABS D5-8 pole 219758 - Michael Mcdonald called job through advising the middle phase is about to blow - called and advised Sam of update - advised Stu in control fire service called to advise of this job and that the fuse is on fire - advised Sam 9.10pm fire service advised they are leaving site. CB8 offloaded due to fire service report Back feed in place up to recloser RP09 via sectionaliser 9954 until ABS checked out ABS SD5 008 opened with CB 8 returned to service all service restored Live line team to check ABS in morning looks like centre phase contact has hot spot DNO No 161125 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.011717 | 11 | 2017 | 2016-11-28 | C | 546 | 0.011717 | 0.0016381
1 | 14849528 | 2016-12-13 05:30 | 2016-12-13 16:57 | 687 | 146 | 17296.1333 | 0.05188 | 0.050566 | 0.00087586 | NAPA ID:24386 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11 | Planned | 024386 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-281-L1 AP2 | NONE | AP1. Open Fuses TD4-281-L1 AP2. Install cable break at HV link-box TD4-666 & install generators at transformers TD4-281 & TD4-SV2. AP3. Joint into disconnected cable (TD4-666 & TD4-281) to 13114/3. Connect new cable at TD4-281 to 13114/4, and TD4-SV2 to 13114/2. Remove CFC 9759 4. Test cables AP4. Reconnect cable at HV link-box TD4-666 & remove generators from transformers TD4-281 & TD4-SV2 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.025283 | 5.5 | 2017 | 2016-12-13 | B | 146 | 0.050566 | 0.00087586
1 | 14849537 | 2016-12-14 09:15 | 2016-12-14 14:34 | 319 | 5 | 1595 | 0.0047842 | 0.004739 | 1.4997e-05 | NAPA ID:25169 TP_MASTERTON GXP > CLAREVILLE SUB > CHESTER RD | 11 | Planned | 025169 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Francis Line, Carterton | CABLE - REPLACE 5 METRES OR MORE | replacing 11kv conductor | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0023695 | 5.5 | 2017 | 2016-12-14 | B | 5 | 0.004739 | 1.4997e-05
1 | 14851214 | 2016-11-29 09:31 | 2016-11-29 15:11 | 339 | 223 | 21144.8167 | 0.063438 | 0.06143 | 0.00066903 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 358888 | CONDUCTOR - REPAIR/REHANG | R/S R12 Tripped E/F L/O Tree through lines found at Pole 358888 duing sectionlising Isolated at Fuses R19 - lines repaired Used 12 mtrs of conductor 6 x sleeves, 4 mtrs binder NDR # 35346 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.06143 | 11 | 2017 | 2016-11-29 | C | 223 | 0.06143 | 0.00066903
1 | 14851976 | 2016-12-15 11:00 | 2016-12-15 18:50 | 470 | 43 | 20210 | 0.060619 | 0.060231 | 0.00012898 | NAPA ID:26851 TP_MASTERTON GXP > CHAPEL SUB > HIGH ST | 11 | Planned | 026851 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2408 | NONE | De-energize LV off T2408, change pole and ABS S159, then remove live line breaks. RED TAG POLE | F3 | HIGH ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.030115 | 5.5 | 2017 | 2016-12-15 | B | 43 | 0.060231 | 0.00012898
1 | 14852559 | 2016-12-12 21:36 | 2016-12-12 22:40 | 64 | 422 | 22120 | 0.066351 | 0.062553 | 0.0012658 | NAPA ID:26867 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 026867 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814892 | NONE | close temp line break at pole 814892 and make a new temp line break at the same pole on the opposite side for a new shutdown the 14/12/16 | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.031276 | 5.5 | 2017 | 2016-12-12 | B | 422 | 0.062553 | 0.0012658
1 | 14852576 | 2016-12-01 10:14 | 2016-12-01 14:05 | 231 | 26 | 6019 | 0.018057 | 0.017823 | 7.8001e-05 | NAPA ID:27061 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 027061 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Emergency shutdown requested to fell trees at Poles W1239-W12555 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.0089115 | 5.5 | 2017 | 2016-12-01 | B | 26 | 0.017823 | 7.8001e-05
1 | 14853257 | 2016-11-29 12:49 | 2016-11-29 15:26 | 156 | 3 | 470.9 | 0.0014128 | 0.001385 | 9.0004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741104 | FUSE - ELEMENT/LINK (HV) | 2 x 2a 1507 bird | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001385 | 11 | 2017 | 2016-11-29 | C | 3 | 0.001385 | 9.0004e-06
1 | 14853355 | 2016-12-15 09:00 | 2016-12-15 15:12 | 372 | 43 | 8358.4 | 0.02507 | 0.024683 | 0.00012898 | NAPA ID:25647 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | 025647 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP21 | NONE | RE-POLE AND RECON FEEDER, REMOVE TEMP21 & TEMP23 FROM 1430 TO 1500. | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.012342 | 5.5 | 2017 | 2016-12-15 | B | 43 | 0.024683 | 0.00012898
1 | 14853551 | 2016-11-29 14:03 | 2016-11-29 19:56 | 353 | 93 | 13897.75 | 0.041695 | 0.040858 | 0.00055803 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10188 P10193 | INSULATOR | RS N21 Tripped B Ph E/F. Ongoing fault. Fuses N30 Opened due to faults from night before - line patrolled Faulty Insulator found at Pole P10188 - Used 1 x HV Insiulator and pin. CB N21 tripped on reclose. Isolation from N31 again where a broken DDO (2A Rating) replaced at Transformer T5/199 (Pole P10193). Relivened OK. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.040858 | 11 | 2017 | 2016-11-29 | C | 93 | 0.040858 | 0.00055803
1 | 14857003 | 2016-11-29 14:35 | 2016-11-29 16:12 | 96 | 1 | 96.9833 | 0.00029096 | 0.000281 | 3.0001e-06 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805197 | FUSE - ELEMENT/LINK (HV) | 2x 8 2962 1605 | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000281 | 22 | 2017 | 2016-11-29 | C | 1 | 0.000281 | 3.0001e-06
1 | 14857901 | 2016-11-29 15:00 | 2016-11-29 15:39 | 39 | 21 | 819 | 0.0024571 | 0.002268 | 6.3003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736803 | INSULATOR | Repair FABS 5279, badly broken insulator on FABS possibly causing feeder to trip. Isolation at ABS's 5761, 5732, 8996/1 & Links 8996/4. Back feed from Douglas D31 via 6298 And Offload CLO CB3 Close ABS 5643 Open 5557. DNO161119 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.002268 | 11 | 2017 | 2016-11-29 | C | 21 | 0.002268 | 6.3003e-05
1 | 14858034 | 2016-11-29 15:20 | 2016-11-29 19:30 | 250 | 1 | 250.4 | 0.00075124 | 0.000742 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | 2HT Fuses replaced at M83. High winds (6A rating) | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000742 | 11 | 2017 | 2016-11-29 | C | 1 | 0.000742 | 3.0001e-06
1 | 14858086 | 2016-12-04 13:01 | 2016-12-04 16:00 | 179 | 19 | 3403.85 | 0.010211 | 0.01004 | 5.6998e-05 | NAPA ID:27002 TP_CARRINGTON GXP > KATERE SUB > KATERE 7 | 11 | Planned | 027002 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | We are installing a new 11kv pole mid span of TX 475 complete with New 11kv fuse 8158 to put a new 11kv vertical ABS 12174 that will be feeding a new 11kv cable to Olex to be installed and connected at a later date with a separate NAPA application. | F2 | KATERE 7 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.00502 | 5.5 | 2017 | 2016-12-04 | B | 19 | 0.01004 | 5.6998e-05
1 | 14858827 | 2016-11-29 16:06 | 2016-11-29 18:43 | 157 | 351 | 2352.25 | 0.0070571 | 0.003897 | 0.0010531 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P590322 | JUMPER | Blown Jumper found at Pole P590322 Isolated at Links 10227/4, ABS's 10227/1, ABS B3, ABS B43, ABS A91 , & ABS 10200. Back Feeds installed via VS 10041 and ABS 10194. Isolation required from ABS 10200, A91, B3, Links 10227/6, ABS 10227/1 & ABS B43 with backfeeds at CB 10041 and ABS 10194. Repaired / relivened. (NOTE: D.Thompsons original OMS No. 14856842). | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.003897 | 11 | 2017 | 2016-11-29 | C | 351 | 0.003897 | 0.0010531
1 | 14863543 | 2016-11-29 17:27 | 2016-11-29 21:00 | 213 | 110 | 11475.2167 | 0.034427 | 0.033437 | 0.00033002 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22954 | CONDUCTOR - REPAIR/REHANG | Tripping on Recloser T42 on EF. Feeder patrlled / sectionalised with a burnt off termination arm (plus broken conductor) found at Pole P22954. Isolation required from fuses T32. Conductor repaired / rehung. New Insulator bolt attached with new binder. Temporary repair made, to be defected by Contractor. Relivened OK. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.033437 | 11 | 2017 | 2016-11-29 | C | 110 | 0.033437 | 0.00033002
1 | 14864868 | 2016-11-30 08:24 | 2016-11-30 09:23 | 59 | 28 | 1651 | 0.0049532 | 0.004701 | 8.4003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46565 | JUMPER | Blown Jumper Found at Transformer T7/365 Isolated at ABS's T35 & 10272 with backfeed installed via ABS V19 Jumper Repaired temperary to get school back on ASAP - Cause age Used 1 x Live Line Connector | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.004701 | 11 | 2017 | 2016-11-30 | C | 28 | 0.004701 | 8.4003e-05
1 | 14864885 | 2016-11-30 10:45 | 2016-11-30 16:28 | 342 | 6 | 2056.9 | 0.0061709 | 0.006116 | 1.8001e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W2265 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Line trucks don't have enough lift to reach the tx from where they park. Need a different truck that isn't available until tomorrow. Will take winching equipment down with the new TX but if this is not adequate to get TX installed they will install a generator as the farmer has 300 sheep penned to be shorn. Spoke to KG to approve the use of the generator. Pole 725884 FM has advised unable to complete TX replacement today but they are going back to install a generator now. Owner Graham Dixon 06 278 6641 has agreed to a generator until the TX is replaced Please close job and create follow up with the 2R TX replacement once FM has advised customers supply has been restored via the generator. Also this is an HV TX so please confirm what time the generator was connected for SAIDI Paul advised the generators have been dropped to site, he is now leaving site. petrol powered generators left onsite so that customer can operate woolshed, These are not hooked up to network so SAIDI should still be ticking on this job 06/12 - Emailed SMC requesting update 06/12 Transformer replaced by Paul Fitzpatrick, Isolated at fuses WH208 so that crane could access the lines. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.006116 | 11 | 2017 | 2016-11-30 | C | 6 | 0.006116 | 1.8001e-05
1 | 14865198 | 2016-11-30 07:43 | 2016-11-30 13:04 | 320 | 5 | 1604.75 | 0.0048144 | 0.004769 | 1.5e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03174 | FUSE - ELEMENT/LINK (HV) | i19 1304 wind 2 x6amp | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.004769 | 11 | 2017 | 2016-11-30 | C | 5 | 0.004769 | 1.5e-05
1 | 14865309 | 2016-12-05 09:46 | 2016-12-05 17:00 | 434 | 69 | 14292.3 | 0.042875 | 0.042254 | 0.00020699 | NAPA ID:25955 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 025955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Commission and Liven new regulator 12171/2. Refer attached methodology. Advertising amended to advise customers of longer outages. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.021127 | 5.5 | 2017 | 2016-12-05 | B | 69 | 0.042254 | 0.00020699
1 | 14865320 | 2016-11-30 08:15 | 2016-11-30 09:22 | 67 | 1 | 67.25 | 0.00020176 | 0.000192 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 831404 | CONDUCTOR - REPAIR/REHANG | loose terminations on lv isolated hv to repair | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000192 | 11 | 2017 | 2016-11-30 | C | 1 | 0.000192 | 3.0001e-06
1 | 14865651 | 2016-12-20 09:15 | 2016-12-20 13:44 | 269 | 74 | 19906 | 0.059702 | 0.059036 | 0.00022194 | NAPA ID:25787 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 025787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Waihekau, Mikkelsen Road | NONE | Change 11KV x-arms on network | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.029518 | 5.5 | 2017 | 2016-12-20 | B | 74 | 0.059036 | 0.00022194
1 | 14866287 | 2016-12-20 09:30 | 2016-12-20 13:36 | 245 | 12 | 2949.4 | 0.0088459 | 0.008737 | 3.5991e-05 | NAPA ID:26030 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | 026030 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P03576 | NONE | Replace 11KV crossarms P03576 P08163 straighten 11KV pole P08161 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.0043685 | 5.5 | 2017 | 2016-12-20 | B | 12 | 0.008737 | 3.5991e-05
1 | 14866427 | 2016-12-01 10:06 | 2016-12-01 22:52 | 766 | 33 | 25286.8 | 0.075862 | 0.075564 | 9.9002e-05 | NAPA ID:27163 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11 | Planned | 026478 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | SWITCHING REWRITE FOR NAPA 26509: Provide Backfeed to 9558/3 Connect Generator to TC1129 Create Line Break at pole W0456 Shift Safelink 9558 and associated HV cables West into Easement for Construction Works Remove Generator and Close Line Break. | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.037782 | 5.5 | 2017 | 2016-12-01 | B | 33 | 0.075564 | 9.9002e-05
1 | 14866650 | 2016-12-21 08:31 | 2016-12-21 16:06 | 454 | 109 | 8896.2167 | 0.026681 | 0.0257 | 0.00065382 | NAPA ID:26889 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11 | Planned | 026889 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 820951 | NONE | create a line break at pole 820951 (HV Issuer Earths one set to be applied at isolated jumpers source side Refer tile), replace red tag t/x pole t1534, close line break at pole 820951. RED TAG POLE 10 days shutdown notice G.P. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.01285 | 5.5 | 2017 | 2016-12-21 | B | 109 | 0.0257 | 0.00065382
1 | 14866748 | 2016-11-30 12:38 | 2016-11-30 14:27 | 108 | 8 | 871.2 | 0.0026137 | 0.002541 | 2.4001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P48701 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp wind | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002541 | 11 | 2017 | 2016-11-30 | C | 8 | 0.002541 | 2.4001e-05
1 | 14867025 | 2016-12-21 09:34 | 2016-12-21 15:03 | 329 | 9 | 2967 | 0.0088985 | 0.008817 | 2.6992e-05 | NAPA ID:26260 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 026260 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Western Lake Road, Featherston | NONE | replace 11kv poles and hardware | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.0044085 | 5.5 | 2017 | 2016-12-21 | B | 9 | 0.008817 | 2.6992e-05
1 | 14868403 | 2016-12-14 11:00 | 2016-12-14 12:25 | 85 | 40 | 3400 | 0.010198 | 0.009838 | 0.00011998 | NAPA ID:26976 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 026976 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 834315 | NONE | replace 11kv red tagged pole 834315 from GP | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.004919 | 5.5 | 2017 | 2016-12-14 | B | 40 | 0.009838 | 0.00011998
1 | 14869091 | 2016-11-30 13:34 | 2016-11-30 16:11 | 156 | 7 | 1097.95 | 0.003294 | 0.00323 | 2.1001e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 444809 | FUSE - ELEMENT/LINK (HV) | fuses 6635 blown at 6635 | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00323 | 11 | 2017 | 2016-11-30 | C | 7 | 0.00323 | 2.1001e-05
1 | 14869501 | 2016-11-30 16:17 | 2016-11-30 18:14 | 117 | 1 | 117.3333 | 0.00035201 | 0.000343 | 3.0001e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | I12809 | CONDUCTOR - REPAIR/REHANG | 4.19pm advised Sammy at svs hub, emailed hub and advised control Conductor has historical damage. Fault man has deemed it safe for the time being. Has put an amber defect in to do a mid span repair in January due to customer not wanting a bucket truck on his new lawn. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000343 | 11 | 2017 | 2016-11-30 | C | 1 | 0.000343 | 3.0001e-06
1 | 14869937 | 2016-11-30 18:34 | 2016-11-30 19:48 | 73 | 25 | 1848.75 | 0.0055464 | 0.005321 | 7.5003e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | V13249 | UNKNOWN | at 19:48, Coromandel Sub, CB 1 Colville Feeder. Faultman dispatched to no power calls. Found Recloser 9927 had tripped. Patrolled what could be easily patrolled from road (difficult terrain). Asked control for permission to try a reclose. Permission granted. Recloser 9927 Closed at 19:48 and held in. Unknown Cause. No Materials Used. Justin Kerrison Attended. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.005321 | 11 | 2017 | 2016-11-30 | C | 25 | 0.005321 | 7.5003e-05
1 | 14872205 | 2016-12-01 07:01 | 2016-12-01 08:59 | 118 | 6 | 709.5 | 0.0021285 | 0.002074 | 1.8e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201631 | FUSE - ELEMENT/LINK (HV) | 2 x6 @ sc2-031 859 bird | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.002074 | 11 | 2017 | 2016-12-01 | C | 6 | 0.002074 | 1.8e-05
1 | 14873886 | 2016-12-22 11:09 | 2016-12-22 14:30 | 201 | 2 | 402.5 | 0.0012071 | 0.001189 | 5.9982e-06 | NAPA ID:21955 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2772 | NONE | To rebuild the transformer structure. Work location: Bowelrs Road, Matamata. W/O 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0005945 | 5.5 | 2017 | 2016-12-22 | B | 2 | 0.001189 | 5.9982e-06
1 | 14874057 | 2016-12-19 09:35 | 2016-12-19 14:08 | 273 | 32 | 8736 | 0.026202 | 0.025913 | 9.5976e-05 | NAPA ID:26149 TP_KOPU GXP > TAIRUA SUB > PAUANUI | 11 | Planned | 026149 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4112 | NONE | Replace MVD Transformer TC4112 | F3 | PAUANUI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.012956 | 5.5 | 2017 | 2016-12-19 | B | 32 | 0.025913 | 9.5976e-05
1 | 14874553 | 2016-12-15 12:30 | 2016-12-15 15:55 | 205 | 65 | 13325 | 0.039967 | 0.039382 | 0.00019496 | NAPA ID:27223 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | 027223 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P45161 | NONE | Removing several trees from 11kV lines and staywire between poles P45161 & P45162. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.019691 | 5.5 | 2017 | 2016-12-15 | B | 65 | 0.039382 | 0.00019496
1 | 14874947 | 2016-12-21 09:08 | 2016-12-21 16:07 | 418 | 20 | 8370.3333 | 0.025104 | 0.024923 | 5.9983e-05 | NAPA ID:25893 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 025893 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Falloon Settlement Road, Masterton | NONE | 11kv pole and cross arm changes , 2 x TX structures | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.012462 | 5.5 | 2017 | 2016-12-21 | B | 20 | 0.024923 | 5.9983e-05
1 | 14876893 | 2016-12-01 20:20 | 2016-12-01 21:05 | 45 | 3064 | 107300.4833 | 0.32191 | 0.29433 | 0.0091922 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | At 20:19, Waikino GXP, 33kV CB 302, Tripped, O/C Time, L/O. At 20:19 Waihi Sub, 33kV CB 50, Tripped, Ph B + C O/C, E/F, L/O. Loss of supply to Waihi Beach Sub. Faultmen dispatched & investigation began. Backfed sub via 11kV from Waihi CB 2. All Power Restored at 21:05. 33kV Lines Patrolled as Much as Possible. Sectionalised Also. No Fault was Found. Unknown Cause. Ferdie De Lange Attended. No Materials Used. Majority of the 33kV Line from Waihi CB 50 up to ABS 182 & CB 22 at Waihi Beach was patrolled and nothing found. Need to do a more thorough patrol from ABS 182 to CB 302 at Waikino GXP. Difficult to patrol in dark as most of this line is cross country. CB 22 DNO 161202, as could not open/close this CB from SCADA. Worked fine with faultman using panel inside the sub. | S2 | WAIKINO302-CREANS 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 0.29433 | 33 | 2017 | 2016-12-01 | C | 3064 | 0.29433 | 0.0091922
1 | 14880176 | 2016-12-01 22:01 | 2016-12-02 12:50 | 889 | 182 | 29217.9833 | 0.087656 | 0.086017 | 0.00054601 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 8341 - 8354 | FAULT INDICATOR | Large tree in line - unsure of pole number but Adam Whale advised it was about 500m South from Transformer T2693 and is near the rail way line. Treescape not able to attend tonight - faultman advised that they believe they know about this tree. Will be attended to first thing in the morning. Lines Isolated between ABS S123 & S94 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.086017 | 11 | 2017 | 2016-12-01 | C | 182 | 0.086017 | 0.00054601
1 | 14885587 | 2016-12-05 08:20 | 2016-12-05 14:19 | 359 | 7 | 2513 | 0.0075387 | 0.007475 | 2.0999e-05 | NAPA ID:27270 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 027270 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 914 | NONE | isolation of 11 kv line to allow for tree work , trees overhanging 11 k line causing outages on windy days , behind line fuses 914 Waka rd | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0037375 | 5.5 | 2017 | 2016-12-05 | B | 7 | 0.007475 | 2.0999e-05
1 | 14885872 | 2016-12-02 16:16 | 2016-12-02 17:22 | 66 | 3 | 198 | 0.000594 | 0.000567 | 9e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 833989 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Rplaced 2X HV drop out holders @ pole 833989 | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.000567 | 11 | 2017 | 2016-12-02 | C | 3 | 0.000567 | 9e-06
1 | 14885933 | 2016-12-20 09:24 | 2016-12-20 14:59 | 335 | 12 | 4024.6 | 0.012071 | 0.011962 | 3.5991e-05 | NAPA ID:25450 TP_MASTERTON GXP | 11 | Planned | 025450 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 833930 | NONE | replace 11kv pole 833930, replace x/arms on pole 833930 and straighten 33kv pole 441812. | S5 | TINUI 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 0.005981 | 5.5 | 2017 | 2016-12-20 | B | 12 | 0.011962 | 3.5991e-05
1 | 14886691 | 2016-12-16 10:00 | 2016-12-16 11:57 | 117 | 3 | 351 | 0.0010528 | 0.001025 | 8.9981e-06 | NAPA ID:25960 TP_GREYTOWN GXP > TUHITARATA SUB > OTARAIA | 11 | Planned | 025960 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Lake Ferry Road, Martinborough | NONE | replace 11kv pole | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.0005125 | 5.5 | 2017 | 2016-12-16 | B | 3 | 0.001025 | 8.9981e-06
1 | 14887096 | 2016-12-09 15:17 | 2016-12-09 15:36 | 19 | 1 | 19 | 5.6994e-05 | 4.7e-05 | 2.9997e-06 | NAPA ID:25919 TP_MARTON GXP > ARAHINA SUB > MARTON | 11 | Planned | 025919 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Operational checks on SW/Gear 4451, Switching only open /close . | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2.35e-05 | 5.5 | 2017 | 2016-12-09 | B | 1 | 4.7e-05 | 2.9997e-06
1 | 14887138 | 2016-12-17 09:00 | 2016-12-17 14:50 | 350 | 17 | 5950 | 0.017846 | 0.017693 | 5.0989e-05 | NAPA ID:26918 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 026918 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp85 | NONE | Re-conductor and remove Links TEMP85 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0088465 | 5.5 | 2017 | 2016-12-17 | B | 17 | 0.017693 | 5.0989e-05
1 | 14890841 | 2016-12-03 10:00 | 2016-12-03 14:01 | 241 | 1 | 241 | 0.00072299 | 0.000713 | 2.9999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 117 Peaks Road | CONDUCTOR - REPAIR/REHANG | limb on line FM requesting 2R to get tree cutters out to site. Asked what damage - won't know full extent until the tree limb is lifted NDR 52868 Isolated at fuses 7867 to remove branch | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.000713 | 11 | 2017 | 2016-12-03 | C | 1 | 0.000713 | 2.9999e-06
1 | 14891419 | 2016-12-03 08:14 | 2016-12-03 10:05 | 111 | 2 | 222 | 0.00066599 | 0.000647 | 5.9999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc5806 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 3amp ht fuse | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000647 | 11 | 2017 | 2016-12-03 | C | 2 | 0.000647 | 5.9999e-06
1 | 14892248 | 2016-12-03 13:18 | 2016-12-03 14:15 | 56 | 45 | 2550.75 | 0.0076522 | 0.007247 | 0.000135 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 14892188 Recloser I15 | UNKNOWN | Alfredton I15 tripped. Patrolled and nothing found | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.007247 | 11 | 2017 | 2016-12-03 | C | 45 | 0.007247 | 0.000135
1 | 14893758 | 2016-12-03 19:34 | 2016-12-03 22:53 | 199 | 2 | 398 | 0.001194 | 0.001175 | 5.9999e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3794T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Found 3 fuses blown checked line and all ok tried close and first fuse blew replaced transformer 3794T 15KVA 3 Phase | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001175 | 11 | 2017 | 2016-12-03 | C | 2 | 0.001175 | 5.9999e-06
1 | 14893903 | 2016-12-03 22:03 | 2016-12-04 00:10 | 127 | 2 | 254.2 | 0.00076259 | 0.000744 | 5.9999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N13196 | FUSE - ELEMENT/LINK (HV) | 2 X 6 amp HV fuses replaced on pole N13196 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000744 | 11 | 2017 | 2016-12-03 | C | 2 | 0.000744 | 5.9999e-06
1 | 14908053 | 2016-12-04 18:04 | 2016-12-04 22:49 | 285 | 1 | 285.35 | 0.00085603 | 0.000847 | 2.9999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | WH157 | UNKNOWN | Sectionalised and restored supply with no apparent cause found Replaced 3X HV fuses @ WH157 | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.000847 | 11 | 2017 | 2016-12-04 | C | 1 | 0.000847 | 2.9999e-06
1 | 14910375 | 2016-12-04 20:54 | 2016-12-04 23:19 | 145 | 149 | 15281.45 | 0.045843 | 0.044502 | 0.00044699 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NFF | UNKNOWN | cb 284 Trip O/C Line sectionalised and patrolled supply restored with no apparent fault found | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.044502 | 11 | 2017 | 2016-12-04 | C | 149 | 0.044502 | 0.00044699
1 | 14926972 | 2016-12-05 12:00 | 2016-12-05 14:01 | 120 | 17 | 2053.0333 | 0.0061589 | 0.006005 | 5.0998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810032 | FUSE - ELEMENT/LINK (HV) | 057 2 x10 amp birdstrike 1401 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.006005 | 11 | 2017 | 2016-12-05 | C | 17 | 0.006005 | 5.0998e-05
1 | 14927513 | 2016-12-05 14:40 | 2016-12-05 16:08 | 87 | 1 | 87.5333 | 0.00026259 | 0.000253 | 2.9998e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1142 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses replaced at Transformer 1142, 2A Rating, lightning | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000253 | 11 | 2017 | 2016-12-05 | C | 1 | 0.000253 | 2.9998e-06
1 | 14927805 | 2016-12-12 09:15 | 2016-12-12 12:55 | 220 | 26 | 5720 | 0.017158 | 0.016923 | 7.7989e-05 | NAPA ID:27335 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11 | Planned | 027335 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To change two red tagged poles | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0084615 | 5.5 | 2017 | 2016-12-12 | B | 26 | 0.016923 | 7.7989e-05
1 | 14971058 | 2016-12-19 21:30 | 2016-12-19 22:02 | 32 | 422 | 13504 | 0.040502 | 0.036704 | 0.0012657 | NAPA ID:27098 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 027098 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814892 | NONE | close temp line break at pole 814892 which was made on 12/12/16 NAPA #26867 | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.018352 | 5.5 | 2017 | 2016-12-19 | B | 422 | 0.036704 | 0.0012657
1 | 14971257 | 2016-12-14 08:31 | 2016-12-14 08:43 | 12 | 61 | 732 | 0.0021956 | 0.001646 | 0.00018297 | NAPA ID:27058 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11 | Planned | 027058 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 818149 | POLE | replace red tag pole 818149. RED TAG POLE 10 day shutdown notice G.P. | F3 | EAST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000823 | 5.5 | 2017 | 2016-12-14 | B | 61 | 0.001646 | 0.00018297
1 | 14971840 | 2016-12-06 09:17 | 2016-12-06 10:38 | 81 | 2 | 162.7667 | 0.00048827 | 0.00047 | 5.9996e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 769247 | FUSE - ELEMENT/LINK (HV) | 3 x3amp and holder bird | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.00047 | 11 | 2017 | 2016-12-06 | C | 2 | 0.00047 | 5.9996e-06
1 | 14972391 | 2016-12-20 06:00 | 2016-12-20 15:08 | 548 | 106 | 58088 | 0.17422 | 0.17326 | 0.00031792 | NAPA ID:25423 TP_KAITIMAKO GXP > WELCOME BAY SUB > POIKE | 11 | Planned | 025423 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | 1. Install 500 kva generator at transformer TP553 (AP1 0600>0630) 2. Remove existing SDAF3 and install automated CFC, liven & SCADA checks (AP2 0630>1500) 3. Remove generator at transformer TP553 (AP3 1500>1530) | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.086632 | 5.5 | 2017 | 2016-12-20 | B | 106 | 0.17326 | 0.00031792
1 | 14972675 | 2016-12-07 09:03 | 2016-12-07 16:08 | 425 | 184 | 78200 | 0.23458 | 0.23293 | 0.00055196 | NAPA ID:27359 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027359 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp 05 | NONE | Poles and Hardware Replacement Install ABS TEMP05 & Links TEMP32 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.11646 | 5.5 | 2017 | 2016-12-07 | B | 184 | 0.23293 | 0.00055196
1 | 14973784 | 2016-12-10 09:39 | 2016-12-10 12:49 | 190 | 3 | 570 | 0.0017098 | 0.001682 | 8.9989e-06 | NAPA ID:27273 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 027273 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 212207 | NONE | REPLACE RED TAG POLE 212207. Works location: Omanawa Rd, Tauranga. WO 30035621 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000841 | 5.5 | 2017 | 2016-12-10 | B | 3 | 0.001682 | 8.9989e-06
1 | 14975216 | 2016-12-07 00:55 | 2016-12-07 03:41 | 166 | 547 | 34201.4833 | 0.1026 | 0.097674 | 0.0016409 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | na | UNKNOWN | PMA8 tripped O/C, L/O report of explosion around 750 Welcome Bay Rd ( Downer road crew ) Back feed via Sectionaliser 9954 ( ATU6 ) to Sectionaliser 9876. & CB 8 Closed up to ABS SD5 007, Sectionaliser 9876 closed up to recloser RP09 after cursory patrol Operational patrol between ABS SD5 007 & recloser RP09 No fault found all service restored ( suspect tree branch ) | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.097674 | 11 | 2017 | 2016-12-07 | C | 547 | 0.097674 | 0.0016409
1 | 14978048 | 2016-12-07 07:41 | 2016-12-07 08:46 | 64 | 5 | 324 | 0.00097193 | 0.000926 | 1.4999e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K12454 | FUSE - ELEMENT/LINK (HV) | 2 x 30 amp swan | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000926 | 11 | 2017 | 2016-12-07 | C | 5 | 0.000926 | 1.4999e-05
1 | 14979123 | 2016-12-08 09:15 | 2016-12-08 15:03 | 348 | 12 | 4176 | 0.012527 | 0.012418 | 3.5997e-05 | NAPA ID:27406 TP_TAURANGA 33 GXP | 11 | Planned | 027406 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Install Backfeed from AON 3 Removal of ABS TEMP98 from pole 381405. Crossarm replacement: 268704 & 268707. Reconductor: 268702 to 268712. Connect conductor to ABS TEMP96 ABS & ABS TEMP97. Removal of ABS 98 didn't occur due to wet weather, could not live line | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.006209 | 5.5 | 2017 | 2016-12-08 | B | 12 | 0.012418 | 3.5997e-05
1 | 14979540 | 2016-12-07 10:44 | 2016-12-07 15:33 | 289 | 176 | 38492.1667 | 0.11547 | 0.11388 | 0.00052796 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 829720 | POLE | Fire called to report car v pole at 11:10. Notified HUB as had no access to OMS. Established was part of feeder fault. Notified Fire of ETA 10mins at 11:15. F2203356. 12:40 - Terry Moyes Completed off Site so he can attend other Faults - AP already underway for pole Replacemant. CB C948 tripped on A, B & C phase fault, received a call of a car vs pole, line was isolated at ABS C420/1 to replace the pole 829720 hit by car. This job is now a 2 R job. 1 X pole & all hardware replaced. NDR: 52869 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.11388 | 11 | 2017 | 2016-12-07 | C | 176 | 0.11388 | 0.00052796
1 | 14980393 | 2016-12-07 11:37 | 2016-12-07 13:00 | 83 | 25 | 2075 | 0.0062246 | 0.005999 | 7.4995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717428 | CONDUCTOR - REPAIR/REHANG | Lines down found at Pole 717428 Isolated at Fuses TA857 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.005999 | 11 | 2017 | 2016-12-07 | C | 25 | 0.005999 | 7.4995e-05
1 | 14980608 | 2016-12-09 09:30 | 2016-12-09 15:59 | 389 | 45 | 17505 | 0.05251 | 0.052104 | 0.00013499 | NAPA ID:27409 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027409 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ip63 | NONE | Poles and Hardware Replacements LLP's required to apply & remove Line cover-ups at TEMP32 (CLOSED) and TEMP05 (OPEN) prior to, and after the Outage. attention Paul Jumper applied to Emap as there is a break in the line at poleT1506 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.026052 | 5.5 | 2017 | 2016-12-09 | B | 45 | 0.052104 | 0.00013499
1 | 14982335 | 2016-12-07 17:22 | 2016-12-07 18:38 | 76 | 19 | 1444 | 0.0043317 | 0.00416 | 5.6996e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06972 | JUMPER | Faultman found a blown jumper at transformer T9/430 on pole P06972 and damaged fuse holders, line was isolated at Fuses I37 to repair the jumper and replace the fuse holders to transformer T9/430 3 X DDO's Replaced. 3 X jumpers replaced | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00416 | 11 | 2017 | 2016-12-07 | C | 19 | 0.00416 | 5.6996e-05
1 | 14982396 | 2016-12-09 09:30 | 2016-12-09 12:32 | 182 | 4 | 728 | 0.0021838 | 0.002147 | 1.1999e-05 | NAPA ID:27415 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | 027415 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X34 | CROSSARM - WHOLE ASSEMBLY | Replace rotten transformer X arm, transformer pole X34 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.0010735 | 5.5 | 2017 | 2016-12-09 | B | 4 | 0.002147 | 1.1999e-05
1 | 14982574 | 2016-12-07 15:31 | 2016-12-07 21:04 | 332 | 265 | 25129.8333 | 0.075384 | 0.072999 | 0.00079495 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 225010 | POLE | Pole down by Fused ABS SF6-022 CNR Bonny Dale Lane & Old Coach Road - tree trimmer has hit pole and brought high tension lines down and started a scrub fire F2203575 eta 09 4867948 - eta 30-35mins- advised fire service of eta CB 5 tripped B & C Ph O/C, L/O, car v pole 225010 isolation between sectionaliser 9408 & ABS SF6 013 with back feed via recloser 9463 & CB 5 closed all repairs completed all service restored Materials 1 x pole, 1 x double arm complete NDR to follow | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.072999 | 11 | 2017 | 2016-12-07 | C | 265 | 0.072999 | 0.00079495
1 | 14982868 | 2016-12-07 15:33 | 2016-12-07 18:00 | 147 | 9 | 1326.6 | 0.0039795 | 0.003898 | 2.6998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7156 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 7156, line was patrolled and suspect line clashes caused fault. 2 X 10 amp HV fuses replaced. 1 X fuse holder replaced. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.003898 | 11 | 2017 | 2016-12-07 | C | 9 | 0.003898 | 2.6998e-05
1 | 14984079 | 2016-12-07 19:02 | 2016-12-07 19:45 | 43 | 29 | 1247 | 0.0037407 | 0.003479 | 8.6994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 811672 | CIRCUIT BREAKER (HV) | 6.08pm advised Sammy at svs hub & emailed 6.10pm called customer to advise hazard process small branch has fallen on the high voltage line - hooked on one and not touching the other, there was an arc between the lines Advised Sammy of update for fm to check C633 CB 633/2 has tripped. Branch removed from pole 811672 CB C633/2 closed, all service restored | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.003479 | 11 | 2017 | 2016-12-07 | C | 29 | 0.003479 | 8.6994e-05
1 | 14984155 | 2016-12-07 18:23 | 2016-12-07 19:05 | 41 | 138 | 5784.5 | 0.017352 | 0.01611 | 0.00041397 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | B12345 | STREET LIGHT CIRCUIT (LV) | 6.20pm advised Sammy at svs hub & emailed & advised control ETA: 35mins - have advised fire comms. Hub called new eta of 10mins. Report of car v pole beyond recloser 13024 recloser offloaded as precaution faultman report car v street light pole feeder restored FM has completed a safety disconnection to the streetlight Pole: B12345 | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.01611 | 11 | 2017 | 2016-12-07 | C | 138 | 0.01611 | 0.00041397
1 | 14984939 | 2016-12-07 23:56 | 2016-12-08 14:20 | 864 | 161 | 137572.5167 | 0.41269 | 0.41124 | 0.00048297 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 762055 | CONDUCTOR - REPAIR/REHANG | Tripping on CB H41 on EF, OC. Feeder patrolled with a broken conductor repaired at Pole 762058. Isolation required from The Substation.CB Tripped on reclose. A further patrol found another conductor down at Pole 762055, also on the main line. Isolation carried out again from the Sub with repairs carried out. Used for second repair 1 x HV Cross Arm Complete, 250 mtrs of conductor, 2 x arm braces, 12 sleeves Faultman still to provide materials list for first repair | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.41124 | 6.6 | 2017 | 2016-12-07 | C | 161 | 0.41124 | 0.00048297
1 | 14986217 | 2016-12-08 03:12 | 2016-12-08 04:14 | 61 | 440 | 19121.1333 | 0.057359 | 0.053398 | 0.0014219 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 768358 | NONE | Tripping on CB9 onn Phase A-B OC. Feeder patrolled / sectionalised. Backfeed initially put in at ABS 039 up to ABS 1352. Tree branch removed (sitting across all 3 phases). Relivened OK. (Overhainging tree, to be defected by Contractor). | F3 | KIWI ST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.053398 | 11 | 2017 | 2016-12-08 | C | 440 | 0.053398 | 0.0014219
1 | 14987346 | 2016-12-08 09:56 | 2016-12-08 12:55 | 179 | 7 | 1253 | 0.0037587 | 0.003695 | 2.0998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12473 | JUMPER | 2 R to replace 30 KVA TX Platform # T1436 on pole # O12473. Tranformer Isolated, HV lead found to be touching pole causing fuse to blown. rerouted lead & relivened 12:55 | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003695 | 11 | 2017 | 2016-12-08 | C | 7 | 0.003695 | 2.0998e-05
1 | 14989298 | 2017-01-09 14:00 | 2017-01-09 14:50 | 50 | 5 | 250 | 0.00074957 | 0.000704 | 1.4991e-05 | NAPA ID:27110 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 027110 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 192 Waharoa East Rd, Matamata | NONE | To install a 400V Fuse Disconnector | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000352 | 5.5 | 2017 | 2017-01-09 | B | 5 | 0.000704 | 1.4991e-05
1 | 14989688 | 2017-01-10 09:45 | 2017-01-10 13:45 | 240 | 4 | 960 | 0.0028783 | 0.002842 | 1.1993e-05 | NAPA ID:26927 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 026927 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 47 Rangipai Rd, Okoroire, Tirau | NONE | To replace the 11kV arms and install a 400v Fuse Unit | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001421 | 5.5 | 2017 | 2017-01-10 | B | 4 | 0.002842 | 1.1993e-05
1 | 14989925 | 2017-01-10 09:30 | 2017-01-10 10:00 | 30 | 4 | 120 | 0.00035979 | 0.000323 | 1.1993e-05 | NAPA ID:25658 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 025658 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 150A Pond Road, Matamata | NONE | To install a 400V Disconnector | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0001615 | 5.5 | 2017 | 2017-01-10 | B | 4 | 0.000323 | 1.1993e-05
1 | 14989983 | 2017-01-12 08:31 | 2017-01-12 15:20 | 409 | 6 | 2454 | 0.0073575 | 0.007303 | 1.7989e-05 | NAPA ID:24800 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024800 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Castlehill | NONE | Change 6 x poles and 6 x xarms | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0036515 | 5.5 | 2017 | 2017-01-12 | B | 6 | 0.007303 | 1.7989e-05
1 | 14989989 | 2017-01-10 11:40 | 2017-01-10 12:04 | 24 | 5 | 120 | 0.00035979 | 0.000314 | 1.4991e-05 | NAPA ID:25733 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 025733 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC 4417 | NONE | To install a 400V Fuse Disconnector on TC 4417 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000157 | 5.5 | 2017 | 2017-01-10 | B | 5 | 0.000314 | 1.4991e-05
1 | 14990002 | 2017-01-14 08:37 | 2017-01-14 13:48 | 311 | 6 | 1866 | 0.0055944 | 0.00554 | 1.7988e-05 | NAPA ID:24801 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11.00000000 | Planned | 024801 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Castlehill | NONE | Change 6 x poles and 5 x xarms | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00277 | 5.5 | 2017 | 2017-01-14 | B | 6 | 0.00554 | 1.7988e-05
1 | 14990018 | 2016-12-08 11:35 | 2016-12-08 12:11 | 36 | 2 | 72.5667 | 0.00021768 | 0.000199 | 5.9995e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 802677 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000199 | 11 | 2017 | 2016-12-08 | C | 2 | 0.000199 | 5.9995e-06
1 | 14990057 | 2017-01-11 08:46 | 2017-01-11 15:10 | 384 | 133 | 51072 | 0.15312 | 0.15193 | 0.00039876 | NAPA ID:27234 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 027234 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809547 | NONE | Replace poles 809547 & 809548 with new DDO?s | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.075964 | 5.5 | 2017 | 2017-01-11 | B | 133 | 0.15193 | 0.00039876
1 | 14990065 | 2017-01-10 13:55 | 2017-01-10 14:06 | 11 | 7 | 77 | 0.00023087 | 0.000167 | 2.0988e-05 | NAPA ID:25664 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 025664 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1590 | NONE | To install a 400V Fuse Disconnector on TC1590 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 8.35e-05 | 5.5 | 2017 | 2017-01-10 | B | 7 | 0.000167 | 2.0988e-05
1 | 14990074 | 2016-12-08 11:45 | 2016-12-08 13:45 | 120 | 1 | 120.0667 | 0.00036017 | 0.000351 | 2.9997e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809083 | FUSE - ELEMENT/LINK (HV) | 2 x 8amp 2969 biird | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.000351 | 11 | 2017 | 2016-12-08 | C | 1 | 0.000351 | 2.9997e-06
1 | 14990156 | 2016-12-17 08:46 | 2016-12-17 10:45 | 119 | 10 | 1194.1667 | 0.0035817 | 0.003491 | 2.9993e-05 | NAPA ID:27416 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 027416 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829054 | NONE | to make safe 11kv cross arms between pole 829054 and 829078 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.0017455 | 5.5 | 2017 | 2016-12-17 | B | 10 | 0.003491 | 2.9993e-05
1 | 14990403 | 2017-01-10 09:15 | 2017-01-10 14:28 | 313 | 15 | 4539 | 0.013609 | 0.013474 | 4.4974e-05 | NAPA ID:26382 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | 026382 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 725408 | NONE | Run three new phases of 35cu from 725408 and 725421 and close line breaks at both structures to restore feeder | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.006737 | 5.5 | 2017 | 2017-01-10 | B | 15 | 0.013474 | 4.4974e-05
1 | 14990423 | 2017-01-12 08:54 | 2017-01-12 14:46 | 352 | 24 | 8448 | 0.025329 | 0.025112 | 7.1956e-05 | NAPA ID:27244 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 027244 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Replace poles between 809548 & 809645 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012556 | 5.5 | 2017 | 2017-01-12 | B | 24 | 0.025112 | 7.1956e-05
1 | 14990432 | 2017-01-17 09:15 | 2017-01-17 15:15 | 360 | 24 | 8640 | 0.025902 | 0.025686 | 7.1951e-05 | NAPA ID:27247 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 027247 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Reconductor between poles 809548 & 809645 with Iodine conductor | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012843 | 5.5 | 2017 | 2017-01-17 | B | 24 | 0.025686 | 7.1951e-05
1 | 14990457 | 2017-01-18 09:07 | 2017-01-18 14:54 | 347 | 24 | 8335.2 | 0.024988 | 0.024772 | 7.195e-05 | NAPA ID:27248 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 027248 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Reconductor between poles 809548 & 809645 with Iodine conductor | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012386 | 5.5 | 2017 | 2017-01-18 | B | 24 | 0.024772 | 7.195e-05
1 | 14990469 | 2017-01-11 09:30 | 2017-01-11 10:29 | 59 | 1 | 59 | 0.00017689 | 0.000167 | 2.9982e-06 | NAPA ID:26932 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | 026932 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Halcombe Rd, Feilding | NONE | Pull back 11KV pole restrain line | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 8.35e-05 | 5.5 | 2017 | 2017-01-11 | B | 1 | 0.000167 | 2.9982e-06
1 | 14990596 | 2017-01-11 10:00 | 2017-01-11 15:00 | 300 | 8 | 2400 | 0.0071957 | 0.007123 | 2.3986e-05 | NAPA ID:26937 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 026937 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5643 State Highway 29, Hinuera, Matamata | NONE | To replace arms and install 400V Fuse/Disconnector | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0035615 | 5.5 | 2017 | 2017-01-11 | B | 8 | 0.007123 | 2.3986e-05
1 | 14990654 | 2017-01-12 09:15 | 2017-01-12 13:04 | 229 | 17 | 3893 | 0.011672 | 0.011518 | 5.0969e-05 | NAPA ID:26297 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | 026297 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 141 Wilford Rd, Patea | NONE | Replace poles on Wilford rd that are leaning over | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.005759 | 5.5 | 2017 | 2017-01-12 | B | 17 | 0.011518 | 5.0969e-05
1 | 14990705 | 2017-01-11 21:45 | 2017-01-11 22:45 | 60 | 1 | 60 | 0.00017989 | 0.00017 | 2.9982e-06 | NAPA ID:26347 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH EAST | 11 | Planned | 026347 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3/50 Juliet St, Stratford | NONE | Replace fiberglass Tx cover with new Ally Tx cover | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 8.5e-05 | 5.5 | 2017 | 2017-01-11 | B | 1 | 0.00017 | 2.9982e-06
1 | 14990792 | 2017-01-12 11:30 | 2017-01-12 13:45 | 135 | 3 | 405 | 0.0012143 | 0.001187 | 8.9945e-06 | NAPA ID:26936 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 026936 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 383 Totman Rdm, Tirau | NONE | To replace the 400V arm & install a 400V Disconnector | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0005935 | 5.5 | 2017 | 2017-01-12 | B | 3 | 0.001187 | 8.9945e-06
1 | 14990880 | 2017-01-12 09:30 | 2017-01-12 15:00 | 330 | 1 | 330 | 0.0009894 | 0.00098 | 2.9981e-06 | NAPA ID:26730 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | 026730 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 180 Gravesons Rd, Waharoa | NONE | To replace the existing pole (TP610) with a double 11M Pole. To upgrade the pole mount transformer to a 100kVA | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.00049 | 5.5 | 2017 | 2017-01-12 | B | 1 | 0.00098 | 2.9981e-06
1 | 14991280 | 2017-01-12 09:00 | 2017-01-12 13:18 | 258 | 46 | 11868 | 0.035582 | 0.035168 | 0.00013792 | NAPA ID:25667 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 025667 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726526 | NONE | Replace defect network poles 726526, 726527,726528 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.017584 | 5.5 | 2017 | 2017-01-12 | B | 46 | 0.035168 | 0.00013792
1 | 14991298 | 2017-01-12 09:31 | 2017-01-12 12:24 | 173 | 47 | 8131 | 0.024378 | 0.023955 | 0.00014091 | NAPA ID:26668 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 026668 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Halls Rd, Mauriceville | NONE | To replace red tagged poles | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.011978 | 5.5 | 2017 | 2017-01-12 | B | 47 | 0.023955 | 0.00014091
1 | 14992304 | 2016-12-08 18:20 | 2016-12-08 19:46 | 85 | 8 | 686.4 | 0.002059 | 0.001987 | 2.3998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728432 | CROSSARM - WHOLE ASSEMBLY | Fuse found blown at Fuses WH157, Burnt Crossarm found at Pole 728420 Isolated at Fuses WH157. Crossarm assembly replaced, relivened OK. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.001987 | 11 | 2017 | 2016-12-08 | C | 8 | 0.001987 | 2.3998e-05
1 | 15029893 | 2016-12-08 19:20 | 2016-12-08 22:58 | 217 | 408 | 34262.6 | 0.10278 | 0.099107 | 0.0018838 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730048 | INSULATOR | Tripping on CB LI7 on EF. Feeder patrolled, sectionalised with a blown insulator found at Pole 730048. Backfeeds at ABS LI790 and LI702 with isolation required between ABS LI742 and LI729. Insulator replaced, relivened OK. 7.22pm advised Cindy svs hub. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.099107 | 11 | 2017 | 2016-12-08 | C | 408 | 0.099107 | 0.0018838
1 | 15039887 | 2016-12-08 21:08 | 2016-12-08 23:26 | 137 | 180 | 10899 | 0.032694 | 0.031074 | 0.00053996 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 2032 | UNKNOWN | Tripping on Recloser 2032 on EF. feeder patrolled / sectionalised but nothing found. Restored to servicve. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.031074 | 11 | 2017 | 2016-12-08 | C | 180 | 0.031074 | 0.00053996
1 | 15058566 | 2017-01-23 09:10 | 2017-01-23 11:40 | 150 | 11 | 1650 | 0.0049462 | 0.004847 | 3.2975e-05 | NAPA ID:26524 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > THOMAS ROAD | 11 | Planned | 026524 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1813 | NONE | Replace IC610 with Fuses FP1813 | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0024235 | 5.5 | 2017 | 2017-01-23 | B | 11 | 0.004847 | 3.2975e-05
1 | 15058610 | 2017-01-24 12:30 | 2017-01-24 16:00 | 210 | 2 | 420 | 0.001259 | 0.001241 | 5.9952e-06 | NAPA ID:26526 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > THOMAS ROAD | 11 | Planned | 026526 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3915 | NONE | Replace TC3915 support Arm | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0006205 | 5.5 | 2017 | 2017-01-24 | B | 2 | 0.001241 | 5.9952e-06
1 | 15058786 | 2017-01-13 14:01 | 2017-01-13 14:55 | 54 | 2 | 108 | 0.0003238 | 0.000305 | 5.9962e-06 | NAPA ID:26481 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 026481 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12 Oreipunga Rd, Maungatautari, Cambridge | NONE | To install a 400V Fuse Disconnector | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001525 | 5.5 | 2017 | 2017-01-13 | B | 2 | 0.000305 | 5.9962e-06
1 | 15059580 | 2016-12-09 09:04 | 2016-12-09 10:52 | 108 | 742 | 59108.2167 | 0.17731 | 0.17063 | 0.0022258 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 218490 | CONDUCTOR - REPAIR/REHANG | CB 3 Trip A,B,C O/C line patrolled & sectionaliser fault found to be tree branch across ABS IP. Branch removed by Hot Stick. NDR N400266 | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.17063 | 11 | 2017 | 2016-12-09 | C | 742 | 0.17063 | 0.0022258
1 | 15061000 | 2016-12-09 09:19 | 2016-12-09 09:33 | 14 | 422 | 5966.5 | 0.017898 | 0.0141 | 0.0012659 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2742 | UNKNOWN | CB 2742 Tripped at Stratford GXP Neutral Time O/C Sub transferred to Huirangi GXP to restore power Line Patrolled with no Fault Found Sub to be transferred back to Stratford GXP once generation stopped 12/12/16 19:45 clearance received from NGOC for GXP parallel and network returned to normal configuration | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.0141 | 33 | 2017 | 2016-12-09 | C | 422 | 0.0141 | 0.0012659
1 | 15062377 | 2017-01-13 09:30 | 2017-01-13 11:35 | 124 | 1 | 124.9167 | 0.00037452 | 0.000365 | 2.9981e-06 | NAPA ID:26478 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 026478 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1513 | NONE | LLP: lift the transformer off the pole AP: Replace arms & Install a 400V Fuse Disconnector on TC1513, Reinstall transformer at lowered height. | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001825 | 5.5 | 2017 | 2017-01-13 | B | 1 | 0.000365 | 2.9981e-06
1 | 15063045 | 2016-12-09 10:06 | 2016-12-09 11:28 | 81 | 874 | 56665.8667 | 0.16998 | 0.16212 | 0.0026217 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 130 | INSULATOR | CB 10 tripped E/F during sectionalising found blown insulator on ABS 130 and cut jumper away using hot sticks .. Section of line from ABS 2603 being backfed via ABS 969 and section from ABS 130 from ABS 1140 for duration until repairs can be effected DNO 161307 applied | F3 | BELL ST | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.16212 | 11 | 2017 | 2016-12-09 | C | 874 | 0.16212 | 0.0026217
1 | 15064175 | 2017-01-16 09:24 | 2017-01-16 14:15 | 291 | 3 | 873 | 0.0026173 | 0.00259 | 8.9939e-06 | NAPA ID:25227 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 025227 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12902 | NONE | To replace the 11kV Fuse Arm, 400V Pin Arm, install 400V Disconnector. TC2722 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.001295 | 5.5 | 2017 | 2017-01-16 | B | 3 | 0.00259 | 8.9939e-06
1 | 15065240 | 2017-01-16 09:45 | 2017-01-16 10:30 | 45 | 3 | 135 | 0.00040473 | 0.000377 | 8.9939e-06 | NAPA ID:27107 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 027107 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2043 | NONE | To install a 400V Fuse Disconnector on TC2043 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001885 | 5.5 | 2017 | 2017-01-16 | B | 3 | 0.000377 | 8.9939e-06
1 | 15065286 | 2017-01-10 08:34 | 2017-01-10 14:49 | 375 | 10 | 3750 | 0.011243 | 0.011153 | 2.9982e-05 | NAPA ID:24798 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | 024798 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Castlehill | NONE | Change 5 x poles and 3 x xarms | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.0055765 | 5.5 | 2017 | 2017-01-10 | B | 10 | 0.011153 | 2.9982e-05
1 | 15065298 | 2017-01-16 12:00 | 2017-01-16 13:30 | 90 | 5 | 450 | 0.0013491 | 0.001304 | 1.499e-05 | NAPA ID:27108 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 027108 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4706 | NONE | To install a 400V Fuse disconnector on TC4706 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000652 | 5.5 | 2017 | 2017-01-16 | B | 5 | 0.001304 | 1.499e-05
1 | 15065405 | 2016-12-09 13:53 | 2016-12-09 14:43 | 49 | 50 | 2483.3 | 0.0074492 | 0.006999 | 0.00014999 |  | 11 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1 | NONE | Transformer T1 tripped during testing on T2 under TP 24274-2 Protection DIff , TRP relay & SOTF during restoration CB C879 failed to close due to spring not rewinding .Technician investigated and found nothing aparrent that would have caused the spring not to rewind and on restoring to sevice position breaker opperated correctly and supply was restored | S1 | NORFOLK 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 0.006999 | 11 | 2017 | 2016-12-09 | C | 50 | 0.006999 | 0.00014999
1 | 15065676 | 2017-01-16 15:00 | 2017-01-16 16:00 | 60 | 8 | 480 | 0.001439 | 0.001367 | 2.3984e-05 | NAPA ID:27109 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 027109 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC969 | NONE | To install a 400V fuse disconnector on TC969 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0006835 | 5.5 | 2017 | 2017-01-16 | B | 8 | 0.001367 | 2.3984e-05
1 | 15065732 | 2017-01-16 15:05 | 2017-01-16 15:25 | 20 | 1 | 20 | 5.996e-05 | 5e-05 | 2.9979e-06 | NAPA ID:25265 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 025265 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP289 | NONE | To install a 400V Fuse Disconnector on TP289 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2.5e-05 | 5.5 | 2017 | 2017-01-16 | B | 1 | 5e-05 | 2.9979e-06
1 | 15065828 | 2017-01-12 11:00 | 2017-01-12 11:20 | 20 | 26 | 520 | 0.001559 | 0.001325 | 7.7952e-05 | NAPA ID:25981 TP_PIAKO GXP > PIAKO SUB > MVILLE NORTH | 11 | Planned | 025981 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2005 | NONE | Replace earthing connections onto transformer TC2005 | F3 | MVILLE NORTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0006625 | 5.5 | 2017 | 2017-01-12 | B | 26 | 0.001325 | 7.7952e-05
1 | 15066060 | 2017-01-14 09:19 | 2017-01-14 11:06 | 107 | 143 | 15312.9167 | 0.045909 | 0.044623 | 0.00042873 | NAPA ID:27027 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11 | Planned | 027027 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5572 | NONE | Fused ABS 5572 is Faulty and is being replaced with a HV fuse Xarm and HV fuses | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.022312 | 5.5 | 2017 | 2017-01-14 | B | 143 | 0.044623 | 0.00042873
1 | 15067439 | 2016-12-10 06:22 | 2016-12-10 11:32 | 310 | 3 | 930 | 0.0027897 | 0.002762 | 8.9989e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/38 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found blown fuses at transformer T7/381 after testing found transformer T7/381to be damaged, transformer was isolated so it can be replaced. replaced with 1 phase 15 kva transformer | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002762 | 11 | 2017 | 2016-12-10 | C | 3 | 0.002762 | 8.9989e-06
1 | 15067598 | 2016-12-15 10:46 | 2016-12-15 15:05 | 258 | 57 | 14749.7 | 0.044241 | 0.043727 | 0.00017097 | NAPA ID:26893 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 026893 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Western Lake Rd and Viles Rd, Featherston | NONE | Replace red tagged poles and hardware | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.021864 | 5.5 | 2017 | 2016-12-15 | B | 57 | 0.043727 | 0.00017097
1 | 15067636 | 2017-01-17 10:20 | 2017-01-17 14:50 | 270 | 12 | 3240 | 0.0097134 | 0.009605 | 3.5975e-05 | NAPA ID:26443 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 026443 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 776642 | NONE | Replace Iron rail poles. Pole numbers 776642 to 776644. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.0048025 | 5.5 | 2017 | 2017-01-17 | B | 12 | 0.009605 | 3.5975e-05
1 | 15068029 | 2017-01-18 09:00 | 2017-01-18 14:08 | 308 | 5 | 1540 | 0.0046168 | 0.004571 | 1.4989e-05 | NAPA ID:27198 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 027198 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 804659 | NONE | Replacing 11kv poles 804659, 804657, 804656, 804655, X arms on pole 804658 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.0022855 | 5.5 | 2017 | 2017-01-18 | B | 5 | 0.004571 | 1.4989e-05
1 | 15068458 | 2016-12-10 10:20 | 2016-12-10 11:31 | 71 | 3 | 213 | 0.00063893 | 0.000611 | 8.9989e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 408 HUTCHINSON ROAD | STAY WIRE | called and emailed SMC - could not contact customer Found stay wire touching 11kV at transformer TC729. Isolated tc729 and repaired stay wire, relivened .Own SIS & AP | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000611 | 11 | 2017 | 2016-12-10 | C | 3 | 0.000611 | 8.9989e-06
1 | 15068486 | 2017-01-19 09:30 | 2017-01-19 12:25 | 174 | 26 | 4534.4 | 0.013594 | 0.013359 | 7.7944e-05 | NAPA ID:26369 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 026369 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 844108 | NONE | REPLACE CRACKED 11KV CONCRETE POLE 844108 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0066795 | 5.5 | 2017 | 2017-01-19 | B | 26 | 0.013359 | 7.7944e-05
1 | 15068561 | 2016-12-10 10:02 | 2016-12-10 12:59 | 176 | 17 | 3001.9167 | 0.0090047 | 0.008851 | 5.0994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 057 | FUSE - ELEMENT/LINK (HV) | Check to see if OMS 15068744 (1017 MANGAHOE ROAD HUNTERVILLE,) is related Replaced 2x 10a HV Fuses @ 057 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.008851 | 11 | 2017 | 2016-12-10 | C | 17 | 0.008851 | 5.0994e-05
1 | 15068642 | 2017-01-20 09:03 | 2017-01-20 14:35 | 332 | 11 | 3652 | 0.010948 | 0.010849 | 3.2976e-05 | NAPA ID:24691 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024691 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C13701 | NONE | replace poles C13701, C738 and xarms C13702, C13703 C13704 and reconductor between C738 and C13704 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0054245 | 5.5 | 2017 | 2017-01-20 | B | 11 | 0.010849 | 3.2976e-05
1 | 15068682 | 2017-01-21 09:00 | 2017-01-21 12:46 | 226 | 27 | 6102 | 0.018292 | 0.018049 | 8.094e-05 | NAPA ID:24780 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024780 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C922 | NONE | change pole C922, and xarms C13637, C13639, C901, CC13640, C612399, C917, C923, C925, C927 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0090245 | 5.5 | 2017 | 2017-01-21 | B | 27 | 0.018049 | 8.094e-05
1 | 15069017 | 2016-12-10 15:07 | 2016-12-10 17:17 | 129 | 1418 | 51606.4333 | 0.1548 | 0.14204 | 0.0042535 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 721696 | CROSSARM - WHOLE ASSEMBLY | CB CAM9 tripped on B&C phase O/C & E/F , during sectionalising found a crossarm twisted on pole 721696 Section of line between ABS CA710 & CA781 isolated to Repair crossarm Section from CA 710 backfed from Recloser 8820 for duration of repairs | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.14204 | 11 | 2017 | 2016-12-10 | C | 1418 | 0.14204 | 0.0042535
1 | 15071108 | 2016-12-10 19:59 | 2016-12-10 20:49 | 50 | 22 | 1100 | 0.0032996 | 0.003101 | 6.5992e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730475 | FUSE - ELEMENT/LINK (HV) | Faultman found a burnt out drop out fuse on transformer 2221T, line was isolated at ABS 5960 & Fuses 5933 to rerplace the drop out fuse. 1 X DDO fuse holder replaced. 1 X 6 amp HV fuse replaced. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.003101 | 11 | 2017 | 2016-12-10 | C | 22 | 0.003101 | 6.5992e-05
1 | 15071683 | 2016-12-11 00:40 | 2016-12-11 07:12 | 392 | 149 | 17743.8333 | 0.053225 | 0.051883 | 0.0010169 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 783721 | CONDUCTOR - REPAIR/REHANG | Recloser 284 tripped on B & C phase O/C flags, line was patrolled and sectionalised, found tree branches touching lines, will return in morning to cut them as entry is on foot and too dangerous in the dark, line was isolated at ABS's 509 &596. Tree Branch from on lines at Pole 783721 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.051883 | 11 | 2017 | 2016-12-11 | C | 149 | 0.051883 | 0.0010169
1 | 15072611 | 2016-12-11 09:57 | 2016-12-11 14:38 | 280 | 178 | 49899.3333 | 0.14968 | 0.14808 | 0.00053393 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 221793 | POLE | Car V Pole Isolated between SF6-009, SE6-042, IP125, 9834/6. Replaced pole & relivened | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.14808 | 11 | 2017 | 2016-12-11 | C | 178 | 0.14808 | 0.00053393
1 | 15072670 | 2016-12-11 08:05 | 2016-12-11 09:15 | 70 | 2 | 126.1667 | 0.00037845 | 0.00036 | 5.9992e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7547 | FUSE - ELEMENT/LINK (HV) | check if OMS 15072862 - 17 Riversdale Rd related - will get f/man to check links 7547 emailed SMC about LV to HV replaced 2 x 10amp ht fuses at 7547 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.00036 | 11 | 2017 | 2016-12-11 | C | 2 | 0.00036 | 5.9992e-06
1 | 15072679 | 2016-12-11 08:10 | 2016-12-11 08:57 | 47 | 158 | 5184.4167 | 0.015551 | 0.014129 | 0.00047394 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 222991 | NONE | Recloser 9274 L/O on O/C Sectionalised & found branch on line at pole 222991, removed & relivened | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.014129 | 11 | 2017 | 2016-12-11 | C | 158 | 0.014129 | 0.00047394
1 | 15073721 | 2016-12-11 16:15 | 2016-12-11 17:11 | 56 | 74 | 4144 | 0.01243 | 0.011764 | 0.00022197 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2344 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | check to see if OMS 15074499 (231 Landlyst rd is related part power) poss fault @ fuses FC2344 -1:50pm - left msg on Ryans cell to call NOC either dispatch or control emailed SMC about LV to HV as Ryan confirmed DDO out Isolated between IC243 & IC213. Replaced DDO & relivened | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.011764 | 11 | 2017 | 2016-12-11 | C | 74 | 0.011764 | 0.00022197
1 | 15074620 | 2016-12-11 13:56 | 2016-12-11 16:27 | 151 | 213 | 13482.45 | 0.040442 | 0.038525 | 0.00063892 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | X1022 | INSULATOR | A Phase OC EF. 1 X HT Insulator Bird Hit It | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.038525 | 11 | 2017 | 2016-12-11 | C | 213 | 0.038525 | 0.00063892
1 | 15075304 | 2016-12-11 16:22 | 2016-12-11 17:42 | 80 | 49 | 424 | 0.0012718 | 0.00083 | 0.00014698 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc771 | JUMPER | Found jumper at TC771 broken. Isolated between CB3, 1196 & 915. Repaired jumper and relivened | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.00083 | 11 | 2017 | 2016-12-11 | C | 49 | 0.00083 | 0.00014698
1 | 15075602 | 2016-12-11 15:08 | 2016-12-11 16:28 | 79 | 1 | 79.95 | 0.00023982 | 0.00023 | 2.9996e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X122 | FUSE - ELEMENT/LINK (HV) | 2 X 3 Amp Fuses | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.00023 | 11 | 2017 | 2016-12-11 | C | 1 | 0.00023 | 2.9996e-06
1 | 15076107 | 2016-12-11 18:40 | 2016-12-11 20:45 | 125 | 56 | 7000 | 0.020997 | 0.020493 | 0.00016798 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809346 | JUMPER | Section of line between Recloser 717 and Links 181 Isolated to repair jumper @ pole 809346 on fuses 742 Section backfed from Switch 912 for duration of repairs | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.020493 | 11 | 2017 | 2016-12-11 | C | 56 | 0.020493 | 0.00016798
1 | 15076190 | 2016-12-11 17:36 | 2016-12-11 20:54 | 198 | 1 | 198.0167 | 0.00059397 | 0.000584 | 2.9996e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5643 | NONE | Line being backfed for planned work resulting in low voltage to cow sheds . Reconfigured backfeeds to provide improved voltages | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000584 | 6.6 | 2017 | 2016-12-11 | C | 1 | 0.000584 | 2.9996e-06
1 | 15078094 | 2016-12-11 21:41 | 2016-12-12 00:30 | 169 | 117 | 15743.15 | 0.047223 | 0.04617 | 0.00044994 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837527 | NONE | CB C936 Trip A,B O/C Line patrolled fault found to be twisted wires at pole 837527. Feeder successfully relivened | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.04617 | 11 | 2017 | 2016-12-11 | C | 117 | 0.04617 | 0.00044994
1 | 15079406 | 2016-12-12 07:10 | 2016-12-12 09:12 | 121 | 1 | 121.6833 | 0.000365 | 0.000355 | 2.9995e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X3078 | FUSE - ELEMENT/LINK (HV) | 2 X 25A UNKNOWN | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000355 | 11 | 2017 | 2016-12-12 | C | 1 | 0.000355 | 2.9995e-06
1 | 15079860 | 2017-01-17 09:50 | 2017-01-17 11:45 | 115 | 4 | 460 | 0.0013791 | 0.001343 | 1.1992e-05 | NAPA ID:25480 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 025480 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3288 | NONE | To replace the 400V Spreader arm & install a 400V Disconnector. | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0006715 | 5.5 | 2017 | 2017-01-17 | B | 4 | 0.001343 | 1.1992e-05
1 | 15080988 | 2016-12-12 09:28 | 2016-12-12 10:30 | 62 | 2 | 124 | 0.00037195 | 0.000353 | 5.9991e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208490 | JUMPER | FM attending part power fault found jumper burnt off from main line to top of HV fuses at Fuses SB1-078. Work area isolated at ABS S5626 to replace jumper. Materials used: 1mtr of 16mm cu & 1x conductor joint | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.000353 | 11 | 2017 | 2016-12-12 | C | 2 | 0.000353 | 5.9991e-06
1 | 15081030 | 2016-12-15 09:48 | 2016-12-15 11:21 | 93 | 92 | 8233.3833 | 0.024696 | 0.023867 | 0.00027595 | NAPA ID:27572 TP_STRATFORD GXP | 11 | Planned | 027572 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | UNKNOWN | Close two 11Kv line breaks at poles 734448 & 441345.Carry on replacing 33Kv poles & conductors in afternoon. Note: This NAPA replaces 25743 - Rewrite switching due to Network being reconfigured to remedy voltage issues . This outage has ben advertised as 25743 . | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.011933 | 5.5 | 2017 | 2016-12-15 | B | 92 | 0.023867 | 0.00027595
1 | 15081067 | 2016-12-12 09:37 | 2016-12-12 11:49 | 132 | 4 | 530.6 | 0.0015916 | 0.001555 | 1.1998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718082 | FUSE - ELEMENT/LINK (HV) | 2 X 6AMP WIND | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001555 | 11 | 2017 | 2016-12-12 | C | 4 | 0.001555 | 1.1998e-05
1 | 15081081 | 2016-12-09 12:47 | 2016-12-09 14:00 | 73 | 2 | 146 | 0.00043796 | 0.000419 | 5.9994e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 388736 | CROSSARM - WHOLE ASSEMBLY | REPLACE LV CROSSARM ISOLATEDHV FOR WORK | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.000419 | 11 | 2017 | 2016-12-09 | C | 2 | 0.000419 | 5.9994e-06
1 | 15081104 | 2016-12-09 12:32 | 2016-12-09 12:53 | 21 | 3 | 63 | 0.00018898 | 0.000161 | 8.9991e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | p49867 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | OFFLOAD TO CORRECT PHASING ISSUE | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.000161 | 11 | 2017 | 2016-12-09 | C | 3 | 0.000161 | 8.9991e-06
1 | 15081424 | 2016-12-14 08:30 | 2016-12-14 17:23 | 533 | 248 | 73460 | 0.22034 | 0.21811 | 0.00089085 | NAPA ID:27582 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027582 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ic380 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | SYNC on 11kV Generation. Re-conductor between IC380 and 9235. Remove TEMP05 and TEMP32. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.10905 | 5.5 | 2017 | 2016-12-14 | B | 248 | 0.21811 | 0.00089085
1 | 15081439 | 2017-01-17 14:02 | 2017-01-17 15:53 | 111 | 7 | 777 | 0.0023294 | 0.002266 | 2.0986e-05 | NAPA ID:26689 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 026689 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Ngutumanga Rd, Waihou | NONE | Physically disconnect 11kV leads from main line using live-line techniques and then replace 11kV drop-out fuses and install LV disconnector on the transformer. Reconnect leads to main line using live-line techniques. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.001133 | 5.5 | 2017 | 2017-01-17 | B | 7 | 0.002266 | 2.0986e-05
1 | 15081779 | 2017-01-17 10:00 | 2017-01-17 13:06 | 186 | 2 | 372 | 0.0011152 | 0.001097 | 5.9959e-06 | NAPA ID:26691 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 026691 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C1218 | NONE | To replace 11kV Pin arm on pole C1218 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0005485 | 5.5 | 2017 | 2017-01-17 | B | 2 | 0.001097 | 5.9959e-06
1 | 15082031 | 2016-12-29 09:03 | 2016-12-29 15:01 | 358 | 29 | 2669.1333 | 0.0080041 | 0.007743 | 0.00016493 | NAPA ID:27274 TP_TE MATAI GXP > TE PUKE SUB > KAITUNA | 11 | Planned | 027274 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228086 | NONE | REPLACE RED TAG POLE 228086 TE6-056 | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0038715 | 5.5 | 2017 | 2016-12-29 | B | 29 | 0.007743 | 0.00016493
1 | 15082329 | 2016-12-12 14:19 | 2016-12-12 17:50 | 211 | 765 | 23613 | 0.070829 | 0.063944 | 0.0022947 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3813 | JOINT - CONDUCTOR JOINT | Faultman called to low voltage at transformer TC3813 Suspect faulty 11kV cables at Sw/Gear 9455. During putting in back feed via Sw/Gear 9455/3 CB6 tripped Sw/Gear cables at 9455 to be tested Generators in service at remaining transformers TP957 & TC3813 overnight Removed generators & restored to normal Repaired 6 joints at TC3813 | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.063944 | 11 | 2017 | 2016-12-12 | C | 765 | 0.063944 | 0.0022947
1 | 15082581 | 2017-01-31 09:01 | 2017-01-31 14:23 | 322 | 2 | 645.3 | 0.0019342 | 0.001916 | 5.9947e-06 | NAPA ID:26040 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 026040 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7705 | NONE | Change 11kv poles & crossarms on Spur line 7705 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000958 | 5.5 | 2017 | 2017-01-31 | B | 2 | 0.001916 | 5.9947e-06
1 | 15082676 | 2017-01-19 10:00 | 2017-01-19 10:17 | 17 | 1 | 17 | 5.0964e-05 | 4.1e-05 | 2.9978e-06 | NAPA ID:26692 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 026692 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3049 | NONE | To install 400V Fuses on TC3049 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2.05e-05 | 5.5 | 2017 | 2017-01-19 | B | 1 | 4.1e-05 | 2.9978e-06
1 | 15085122 | 2017-01-20 09:53 | 2017-01-20 11:24 | 91 | 5 | 455 | 0.001364 | 0.001319 | 1.4989e-05 | NAPA ID:26680 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 026680 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Larsons Road | NONE | To replace red tagged poles | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0006595 | 5.5 | 2017 | 2017-01-20 | B | 5 | 0.001319 | 1.4989e-05
1 | 15085220 | 2016-12-12 14:21 | 2016-12-12 18:51 | 269 | 93 | 13159.2333 | 0.039472 | 0.038635 | 0.0006689 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P08442 | INSULATOR | Rec N21 trip O/C E/F Isolated at ABS N29 Replaced 2x 11kv pins & insulators on pole P08442 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.038635 | 11 | 2017 | 2016-12-12 | C | 93 | 0.038635 | 0.0006689
1 | 15085503 | 2017-01-10 09:30 | 2017-01-10 14:14 | 284 | 2 | 568 | 0.001703 | 0.001685 | 5.9964e-06 | NAPA ID:26955 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11 | Planned | 026955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N2864 | NONE | TO REPLACE LIVE LINE XARMS AT POLES N2864,N1360,N1358. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.0008425 | 5.5 | 2017 | 2017-01-10 | B | 2 | 0.001685 | 5.9964e-06
1 | 15085530 | 2016-12-12 14:34 | 2016-12-12 18:03 | 208 | 92 | 9019.2833 | 0.027054 | 0.026226 | 0.00027596 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224458 | CROSSARM - WHOLE ASSEMBLY | SS 9781/2 Trip, E/F, O/C A & B Phase. Sectionalised & Patrolled with broken crossarm found at Pole 224458. Due to rot. Materials used: 1x 3 Pin HV Crossarm with associated bolts, arm braces etc | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.026226 | 11 | 2017 | 2016-12-12 | C | 92 | 0.026226 | 0.00027596
1 | 15086126 | 2017-01-24 10:11 | 2017-01-24 14:00 | 229 | 46 | 10534 | 0.031577 | 0.031163 | 0.00013789 | NAPA ID:26394 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 026394 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 794509 | NONE | replace rotten 11kv xarms at poles 794509 and 794506 , turikina vly | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.015581 | 5.5 | 2017 | 2017-01-24 | B | 46 | 0.031163 | 0.00013789
1 | 15086194 | 2016-12-12 14:52 | 2016-12-12 21:20 | 388 | 76 | 7031.0167 | 0.02109 | 0.020406 | 0.00032695 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780567 | CONDUCTOR - REPAIR/REHANG | Paul Clutterbuck also attending. Bring out equipment to FM Found conductor brought down by trees and repaired 1 span @ pole 780567 used 10m Squirel conductor and 2 x sleves | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.020406 | 11 | 2017 | 2016-12-12 | C | 76 | 0.020406 | 0.00032695
1 | 15086273 | 2017-01-25 09:29 | 2017-01-25 12:40 | 191 | 3 | 573 | 0.0017176 | 0.00169 | 8.9928e-06 | NAPA ID:26749 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 026749 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 794665 | NONE | Replace defect 11kv pole number 794665 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000845 | 5.5 | 2017 | 2017-01-25 | B | 3 | 0.00169 | 8.9928e-06
1 | 15086477 | 2016-12-12 14:58 | 2016-12-12 17:46 | 167 | 1 | 167.9167 | 0.00050368 | 0.000494 | 2.9995e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | t388 | FUSE - ELEMENT/LINK (HV) | 2 X 2 amp Fuses at Transformer T388 | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000494 | 11 | 2017 | 2016-12-12 | C | 1 | 0.000494 | 2.9995e-06
1 | 15086579 | 2017-01-18 09:32 | 2017-01-18 13:40 | 247 | 211 | 52190.85 | 0.15646 | 0.15457 | 0.00063256 | NAPA ID:25833 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 025833 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P00049 | NONE | To replace poles P00049,P00072,P00044 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.077283 | 5.5 | 2017 | 2017-01-18 | B | 211 | 0.15457 | 0.00063256
1 | 15086650 | 2017-01-25 09:50 | 2017-01-25 16:30 | 400 | 17 | 6800 | 0.020384 | 0.02023 | 5.0959e-05 | NAPA ID:26806 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 026806 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 607 Finnis Rd | NONE | Cutting tree close to 11KV on Ridge Rd. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.010115 | 5.5 | 2017 | 2017-01-25 | B | 17 | 0.02023 | 5.0959e-05
1 | 15086716 | 2016-12-12 15:56 | 2016-12-12 19:27 | 210 | 566 | 55179.5167 | 0.16551 | 0.16042 | 0.0025136 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 729624 | CONDUCTOR - REPAIR/REHANG | Pole# 728479. Wire sitting on cross arm, insulator gone completely. Wire is touching power pole. 7kms sth of Hawera on main Sth road. Southern side of Tangahoe bridge. - 839 South Road - tried calling customer re hazard process - advised control. above refers to L/V fault WHR1 tripped A,B & C Ph O/C L/O feeder sectionalised with WHR1 returned to service WHR 1 backfeeding WHR2 & lines down found at pole 729624 ( 1 span all phases ) Isolation between ABS's WH210 & WH293 with rest of feeder returned to service NDR Number N100273 | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.16042 | 11 | 2017 | 2016-12-12 | C | 566 | 0.16042 | 0.0025136
1 | 15087294 | 2017-01-25 09:35 | 2017-01-25 14:50 | 315 | 43 | 13545 | 0.040603 | 0.040215 | 0.0001289 | NAPA ID:26727 TP_MANGAMAIRE GXP > MANGAMUTU SUB | 11 | Planned | 026727 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P16665 | NONE | To replace red tagged poles P16665 and P16632 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.020108 | 5.5 | 2017 | 2017-01-25 | B | 43 | 0.040215 | 0.0001289
1 | 15090648 | 2017-01-25 09:50 | 2017-01-25 16:13 | 383 | 17 | 6511 | 0.019517 | 0.019364 | 5.0959e-05 | NAPA ID:25962 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 025962 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 836189 | NONE | Change 11kv poles and crossarms , 2x TX poles , Fit DDOs at Pole 836189 DDO#11098 for spur line | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.009682 | 5.5 | 2017 | 2017-01-25 | B | 17 | 0.019364 | 5.0959e-05
1 | 15090719 | 2016-12-12 16:25 | 2016-12-12 19:10 | 165 | 1 | 165.25 | 0.00049568 | 0.000486 | 2.9995e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1616 | FUSE - ELEMENT/LINK (HV) | 15091268 POSSIBLE LINKED replace 2 x 3 amp ht fuses LT fault caused ht fuses to operate | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000486 | 11 | 2017 | 2016-12-12 | C | 1 | 0.000486 | 2.9995e-06
1 | 15091523 | 2016-12-12 18:26 | 2016-12-12 22:00 | 213 | 1 | 213.6167 | 0.00064076 | 0.000631 | 2.9995e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741104 | FUSE - ELEMENT/LINK (HV) | NDR N100274 Trees in line . HV links down . repaired LV lines and replaced 2x 3amp HV fuses @ pole 741104 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000631 | 11 | 2017 | 2016-12-12 | C | 1 | 0.000631 | 2.9995e-06
1 | 15091962 | 2016-12-12 19:17 | 2016-12-12 22:41 | 204 | 293 | 45311.0333 | 0.13591 | 0.13328 | 0.0020307 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3942 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Recloser C225 L/O on E/F & O/C. Sectionalised & found transformer T3942 faulty. Left off over night to replace next day | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.13328 | 11 | 2017 | 2016-12-12 | C | 293 | 0.13328 | 0.0020307
1 | 15094133 | 2016-12-12 23:06 | 2016-12-13 00:48 | 101 | 185 | 13262.2667 | 0.039781 | 0.038116 | 0.00055492 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | D21 | UNKNOWN | Line sectionalised and patrolled (cursorary) Suppply restored with nothing obvious found | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.038116 | 11 | 2017 | 2016-12-12 | C | 185 | 0.038116 | 0.00055492
1 | 15094753 | 2016-12-12 23:21 | 2016-12-13 05:48 | 386 | 1120 | 78094.6667 | 0.23425 | 0.22417 | 0.0037945 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784718 | CONDUCTOR - REPAIR/REHANG | CB 575 tripped and also CB 3 @ Peat street as a result of backfeeds in place for work @ Roberts ave caused outage to part of Roberts Ave 4 Roberts Ave 7 and Peat Street 3 Report received of lines down @ pole 784718 Contractor tried to locate tree contractors to no avail so repaired lines only to find they were still burning in the trees so line isolated again and finally managed to arrange tree contractor .trees cut and supply restored beyond CB 575 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.22417 | 11 | 2017 | 2016-12-12 | C | 1120 | 0.22417 | 0.0037945
1 | 15095888 | 2016-12-12 19:17 | 2016-12-13 10:50 | 933 | 2 | 1866 | 0.0055972 | 0.005579 | 5.9991e-06 | Referral | 11.00000000 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3942 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace faulty transformer T3942 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.005579 | 11 | 2017 | 2016-12-12 | C | 2 | 0.005579 | 5.9991e-06
1 | 15096247 | 2016-12-13 02:59 | 2016-12-13 03:28 | 28 | 180 | 3195 | 0.0095835 | 0.007963 | 0.0010798 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2032 | NONE | When reseting flags CB 2032 tripped for no apparent reason CB manually closed but whilst investigating due to backfeeds in place it appeared that closing the breaker created a parallel with Kai Iwi and Peat street so reopened the breaker. Closer inspection carried out . Checked the backfeeding switching and found the open point and Closed the breaker back on load | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.007963 | 11 | 2017 | 2016-12-13 | C | 180 | 0.007963 | 0.0010798
1 | 15096984 | 2016-12-13 06:07 | 2016-12-13 07:31 | 84 | 3 | 252.85 | 0.00075843 | 0.000731 | 8.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C3352 | FUSE - ELEMENT/LINK (HV) | 2 x 25amp swan | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000731 | 11 | 2017 | 2016-12-13 | C | 3 | 0.000731 | 8.9985e-06
1 | 15099002 | 2017-01-16 09:00 | 2017-01-16 15:00 | 360 | 33 | 11880 | 0.035616 | 0.035319 | 9.8934e-05 | NAPA ID:24677 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024677 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C370 | NONE | Replace poles C370, C371, and xarm C365, C13175, C13179, C382, and install LV fusing on TX structures C13170, C13172, C13174, C13176, C13179, C13184, C13146 and C13149 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.01766 | 5.5 | 2017 | 2017-01-16 | B | 33 | 0.035319 | 9.8934e-05
1 | 15099099 | 2017-01-17 09:00 | 2017-01-17 16:15 | 434 | 66 | 28690.2 | 0.086012 | 0.085418 | 0.00019786 | NAPA ID:24681 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024681 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C2383 | NONE | replace poles C2383, and replace xarms C2386, C971, C970, C984, C983, C978, C13630, C13635, and C13655 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.042709 | 5.5 | 2017 | 2017-01-17 | B | 66 | 0.085418 | 0.00019786
1 | 15099296 | 2016-12-13 10:57 | 2016-12-14 14:21 | 1643 | 1604 | 80567.4667 | 0.24166 | 0.22723 | 0.0073158 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738863 | JUMPER | 33kV CB 2782 tripped O/C B & C Phase to lock out. LOS to Cardiff and Kaponga Subs. Line fully patrolled, no fault found. Report of flash reported from section of line past ABS 364, Both line fault indicators flashing at ABS's 353 and 364, nil operated at Chiselhurst site, backed public report of flash location. Patrol found no evidence of fault found. All re livened OK. NOTE: the other Kaponga/Cardiff was out of service for planned project works to re-pole. Required crew to stand down and make line ready for service, due to 'fluidity' of situation was not required as power restored prior to requirement. Managed to get project crew back to work on second AP. relevant Downer and Powerco project managers and FRM's informed of situation throughout. A short while after restoration it was observed tapchangers, loading's and voltages not as per expectation at Kaponga, Cloten, Eltham and Cardiff Substations. Crews again mobilized to inspect. Further inspection raised the possibility of a either a lost phase or a partial phase loss. Due to CLO and ELT sub's having other 33kV feeder supply's suspected these were back feeding into faulted feeder due to tied 11kV BUS's at each sub. Due to loading and voltage issues at ELT sub, NOC opened CB's RO9 and 402 to resolve issue, brought ELT voltage back to correct levels. KAP sub voltage now very low, used CLO sub tap-changer to support voltage to KAP sub. NOC requested feeder patrol focus to first part of SFD 2782 feeder and IRT camera sort by NOC to assist process. Found ABS 352 had a failed centre phase, causing low voltage (on that phase). project crews work completed and SFD 2862 circuit brought back to service with both Cardiff and Kaponga changed to this circuit. Affected section of circuit isolated earthed up to effect temp repair of ABS 352 with the centre phase jumpered through. Has been DNO 161208. To effect repairs of 33kV ABS, required sections of CLO CB 8 between ABS's 5846, 5828 and 5793. As well as CLO CB 3 Isolated between ABS's 5776 and 5793(open point between CLO 3 & 8) Note: 33kV network to be restored to 33kv re-pole project configuration to allow works to continue on the 14th Fiona: quite a few crews onsite for this fault and will involve considerable time and mileage. 2R request time does not reflect actual time job changed to 2R, this was a number of hours earlier, NCTL | S1 | CLOTON ROAD SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.22723 | 33 | 2017 | 2016-12-13 | C | 1604 | 0.22723 | 0.0073158
1 | 15105196 | 2016-12-29 08:30 | 2016-12-29 12:59 | 269 | 14 | 3766 | 0.011293 | 0.011167 | 4.1983e-05 | NAPA ID:27453 TP_MASTERTON GXP > AWATOITOI SUB > MANGAPAKEHA | 11 | Planned | 027453 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 839818 | NONE | red tag poles.Change 2 poles under red tag pole situation | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.0055835 | 5.5 | 2017 | 2016-12-29 | B | 14 | 0.011167 | 4.1983e-05
1 | 15105463 | 2017-01-19 09:00 | 2017-01-19 15:12 | 372 | 35 | 13020 | 0.039032 | 0.038717 | 0.00010493 | NAPA ID:24689 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024689 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C13666 | NONE | replace xarms C13666, C13667, C13668, C869, C865, C13662, C836, C13664, C832, C612501, C13683, C809, C13689 and install LV fusing on TX structures C13681, C819, C13686, C13676 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.019359 | 5.5 | 2017 | 2017-01-19 | B | 35 | 0.038717 | 0.00010493
1 | 15105501 | 2017-01-11 09:08 | 2017-01-11 11:08 | 119 | 59 | 7060.3333 | 0.021168 | 0.020637 | 0.00017689 | NAPA ID:25789 TP_STRATFORD GXP | 11 | Planned | 025789 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | N/A - NOT APPLICABLE | UNKNOWN | Install 11Kv line breaks at poles 372414 & 737603. Liven 11Kv Feeder. Carry on with Cardiff 33Kv Line reconstruction over isolated 11Kv lines. Shut 2 of week starting 10/1/17 to 13/1/17 for this project . . | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.010318 | 5.5 | 2017 | 2017-01-11 | B | 59 | 0.020637 | 0.00017689
1 | 15105538 | 2017-01-18 09:01 | 2017-01-18 15:24 | 383 | 37 | 14171 | 0.042483 | 0.04215 | 0.00011092 | NAPA ID:24687 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024687 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C13446 | NONE | Replace xarms C13446, CC770, C769, C786, C787, C13722, C13466, C13467, C797, C775, C13715, C780 and replace pole C13725 and install LV fusing on TX Structures C13447, C13717 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.021075 | 5.5 | 2017 | 2017-01-18 | B | 37 | 0.04215 | 0.00011092
1 | 15105588 | 2017-01-23 09:04 | 2017-01-23 15:23 | 379 | 11 | 4169 | 0.012497 | 0.012398 | 3.2975e-05 | NAPA ID:24692 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024692 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C13694 | NONE | reconductor line between poles C13694 and pole C13700 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.006199 | 5.5 | 2017 | 2017-01-23 | B | 11 | 0.012398 | 3.2975e-05
1 | 15105685 | 2017-01-24 09:00 | 2017-01-24 14:29 | 329 | 12 | 3948 | 0.011835 | 0.011726 | 3.5972e-05 | NAPA ID:24699 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024699 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C2894 | NONE | replace poles C2894, C2361, and xarms C2893, C2892, C2889, C2888, C13590, C2362, C2366, C2367, C2370, C2372, C2373, C2375, C2376, C2377, C23778 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.005863 | 5.5 | 2017 | 2017-01-24 | B | 12 | 0.011726 | 3.5972e-05
1 | 15123186 | 2017-01-25 09:00 | 2017-01-25 13:25 | 265 | 23 | 6095 | 0.01827 | 0.018063 | 6.8945e-05 | NAPA ID:24738 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 024738 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C654 | NONE | Replace pole C654, and xarms C658, C659, C660, C663, C13201 C651 and install LV fusing on TX Structures C13201, C13205, C13191, C13194 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0090315 | 5.5 | 2017 | 2017-01-25 | B | 23 | 0.018063 | 6.8945e-05
1 | 15126348 | 2016-12-14 00:03 | 2016-12-14 01:26 | 82 | 12 | 992.8 | 0.0029779 | 0.002869 | 3.5994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 799275 | NONE | Recloser C640 L/O on E/F Remove twig from pole 799275 & relivened | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.002869 | 11 | 2017 | 2016-12-14 | C | 12 | 0.002869 | 3.5994e-05
1 | 15128242 | 2017-01-25 09:15 | 2017-01-25 13:56 | 281 | 32 | 8992 | 0.026954 | 0.026666 | 9.5923e-05 | NAPA ID:24740 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > LOVEGROVE RD | 11 | Planned | 024740 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C363 | NONE | replace xarms C363, C362, C348, C13159 and install LV fusing on TX structures C13161, C13164 | F2/F4 | LOVEGROVE RD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.013333 | 5.5 | 2017 | 2017-01-25 | B | 32 | 0.026666 | 9.5923e-05
1 | 15131570 | 2017-01-12 08:31 | 2017-01-12 14:11 | 340 | 4 | 1337 | 0.0040086 | 0.003972 | 1.1993e-05 | NAPA ID:25678 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025678 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rangiuru Rd, Penderel Rd | NONE | REPLACE HV ARMS 2 SITES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001986 | 5.5 | 2017 | 2017-01-12 | B | 4 | 0.003972 | 1.1993e-05
1 | 15131661 | 2016-12-14 08:47 | 2016-12-14 12:46 | 238 | 1433 | 166 | 0.00049791 | 0 | 2.9994e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 746015 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | 9:22am - followed up with SMC - still trying to find FM to attend 9:28 ETA is 7 mins. BBK 8 tripped A,B & C Ph O/C, E/F, A/R ( feeding BBK 7 sub upgrade ) Report of truck v pole 746015 Fuses 8162 blown ( spur 1 transformer off ) 1 span x 3 phases down Lines repaired, all service restored Materials 3 x H/V polymers, 1 x H/V arm complete, 10 x H/V sleeves, 130 meters conductor NDR N100275 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-12-14 | C | 1433 | 0 | 2.9994e-06
1 | 15132315 | 2016-12-14 08:55 | 2016-12-14 14:17 | 321 | 324 | 44251.1 | 0.13273 | 0.12981 | 0.0023186 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 749459 | JUMPER | Hazard process complete with customer at 527 Rapanui - advised this is a side line that comes off the main HV line and has been down for a while - power went off well after this. Possibly not cause of feeder fault. 15134136 created Branch found at Pole 749459 during sectionlising pushing Jumper onto crossarm feeder. Cleared using hot sticks NDR # 749459 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.12981 | 11 | 2017 | 2016-12-14 | C | 324 | 0.12981 | 0.0023186
1 | 15134270 | 2017-01-16 08:50 | 2017-01-16 12:38 | 228 | 13 | 2964 | 0.0088861 | 0.008769 | 3.8974e-05 | NAPA ID:26323 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 026323 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W13390 | POLE | REPLACE 11KV POLES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0043845 | 5.5 | 2017 | 2017-01-16 | B | 13 | 0.008769 | 3.8974e-05
1 | 15151847 | 2017-01-18 08:00 | 2017-01-18 15:15 | 435 | 1 | 435 | 0.0013041 | 0.001295 | 2.9979e-06 | NAPA ID:27575 TP_MASTERTON GXP > CHAPEL SUB > CORNWALL ST | 11 | Planned | 027575 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 2608 | NONE | replace existing tx 2608 due to acidic smell coming from tx 3 days work to complete .day one remove tx and do ground work install new earths and new fencing day 2-3 to install new tx and joint cable hope full to do with 2 days | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.0006475 | 5.5 | 2017 | 2017-01-18 | B | 1 | 0.001295 | 2.9979e-06
1 | 15152275 | 2017-01-29 08:45 | 2017-01-29 14:52 | 367 | 47 | 7062.5833 | 0.02117 | 0.020746 | 0.00028176 | NAPA ID:25964 TP_HUIRANGI GXP > BELL BLOCK SUB > MANGATI RD | 11 | Planned | 025964 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12166 | NONE | We are Installing new 11kv fuses 12166 to feed 11kv cable to new 11kv ground mount transformer 1102. We are installing a 11kv line break for saidi impact. | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.010373 | 5.5 | 2017 | 2017-01-29 | B | 47 | 0.020746 | 0.00028176
1 | 15152659 | 2016-12-18 08:15 | 2016-12-18 11:18 | 183 | 1 | 183 | 0.00054887 | 0.000539 | 2.9993e-06 | NAPA ID:27649 TP_HUIRANGI GXP > BELL BLOCK SUB > DE HAVILLAND SOUTH | 11 | Planned | 027649 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 413/2 | NONE | Nexans being isolated to do switchgear maintenance and connect new cable from 413/2 to O/H line via ABS 12174. After completion switching to be done to liven new cable from Links 551 through 413/1 7 413/2 to phase at ABS 12174. If correct to close ABS 12174 and open 413/2 as NO till BBK job completion. CAble not connected to switch 413/2 due to no cable jointer being available | F1 | DE HAVILLAND SOUTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0002695 | 5.5 | 2017 | 2016-12-18 | B | 1 | 0.000539 | 2.9993e-06
1 | 15157121 | 2017-01-16 09:20 | 2017-01-16 15:40 | 380 | 6 | 2280 | 0.0068354 | 0.006781 | 1.7988e-05 | NAPA ID:25498 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 025498 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13004 | POLE | Replace poles,hardware and conductor. Remove TEMP64 in Outage | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0033905 | 5.5 | 2017 | 2017-01-16 | B | 6 | 0.006781 | 1.7988e-05
1 | 15159601 | 2017-01-24 09:08 | 2017-01-24 16:14 | 426 | 34 | 14484 | 0.043418 | 0.043112 | 0.00010192 | NAPA ID:25730 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 025730 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP670 | NONE | Replace poles,hardware and conductor. Install new ABS IP670 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.021556 | 5.5 | 2017 | 2017-01-24 | B | 34 | 0.043112 | 0.00010192
1 | 15159903 | 2016-12-14 16:23 | 2016-12-14 17:15 | 52 | 3 | 156.05 | 0.00046807 | 0.000441 | 8.9984e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 228063 | FUSE - ELEMENT/LINK (HV) | Bird strike causing 2x6amp fuse to blown at fuses FP896. reloaded & livened. Bird sited by F/M | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000441 | 11 | 2017 | 2016-12-14 | C | 3 | 0.000441 | 8.9984e-06
1 | 15160996 | 2016-12-15 06:55 | 2016-12-15 09:40 | 164 | 6 | 987.8 | 0.0029628 | 0.002908 | 1.7997e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373430 | FUSE - ELEMENT/LINK (HV) |  | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002908 | 11 | 2017 | 2016-12-15 | C | 6 | 0.002908 | 1.7997e-05
1 | 15161526 | 2017-01-25 09:11 | 2017-01-25 17:00 | 469 | 128 | 59352.6667 | 0.17792 | 0.17676 | 0.00038369 | NAPA ID:24701 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | 024701 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS S589 | NONE | make a live line cut and replace 9 defective 11kv poles. ABS S589-T1548-T1291-814642-814113--814111-814459 814460-845245 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.088382 | 5.5 | 2017 | 2017-01-25 | B | 128 | 0.17676 | 0.00038369
1 | 15161903 | 2016-12-15 10:15 | 2016-12-15 14:19 | 244 | 283 | 25438.9833 | 0.076303 | 0.073756 | 0.0015387 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847879 | CROSSARM - WHOLE ASSEMBLY | CB KA & Tripped O/C L/O Cross arm found at Pole 847879 during Sectionlising, Isolated at ABS's KA737 & CA413 Crossarm straightened. This also affected 34 ICPs on Tawhiti feeder as isolation could not be made at open point 8726. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.073756 | 11 | 2017 | 2016-12-15 | C | 283 | 0.073756 | 0.0015387
1 | 15162169 | 2016-12-15 12:02 | 2016-12-15 13:24 | 82 | 3 | 246 | 0.00073786 | 0.00071 | 8.9983e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3127 | CONDUCTOR - REPAIR/REHANG | Faultman isolated transformer T3127 for safety to repair LV lines | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.00071 | 11 | 2017 | 2016-12-15 | C | 3 | 0.00071 | 8.9983e-06
1 | 15162929 | 2016-12-15 16:36 | 2016-12-15 21:21 | 284 | 1609 | 6460.3667 | 0.019377 | 0.004899 | 0.0048261 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | waitara CB702 To Pohukura | UNKNOWN | feeder fault CB 702 Tripped on C Phase EF. Auto Changeover activated at Pohokura. No fault found on vissial inspection, 33kV line isolated between CB 3180/1 and ABS 704 & 3179 WAW F21 tripped during switching due to ABS 5104 being faulty (DNO 161209). 11kV isolation required (to access Cable terminations) between ABSs 5104, 5115 and 5073 with backfeeds at 5007 and 5021. 33kV Cables tested between CB 3180/1 and overhead - all OK. 11kV restored to service followed by 33kV. Restored OK, suspect bird strike. | F1 | BLAKE ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.004899 | 11 | 2017 | 2016-12-15 | C | 1609 | 0.004899 | 0.0048261
1 | 15162941 | 2016-12-15 13:30 | 2016-12-15 15:58 | 148 | 3 | 444 | 0.0013317 | 0.001304 | 8.9983e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 824525 | CONDUCTOR - REPAIR/REHANG | Transformer T1241 was isolated for so faultman could repair LV cable crutch. | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001304 | 11 | 2017 | 2016-12-15 | C | 3 | 0.001304 | 8.9983e-06
1 | 15164375 | 2017-01-17 10:26 | 2017-01-17 11:43 | 77 | 3 | 231 | 0.00069253 | 0.000665 | 8.9938e-06 | NAPA ID:26395 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 026395 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220005 | NONE | change pole 220005 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0003325 | 5.5 | 2017 | 2017-01-17 | B | 3 | 0.000665 | 8.9938e-06
1 | 15164610 | 2017-01-24 09:40 | 2017-01-24 15:00 | 320 | 3 | 960 | 0.0028777 | 0.00285 | 8.9929e-06 | NAPA ID:26584 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 026584 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13081 | NONE | Install new reg site 13081. Note: Work for the Install spread over 2 days 24 & 25/01/2017. Commissioning to take place at a later date. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.001425 | 5.5 | 2017 | 2017-01-24 | B | 3 | 0.00285 | 8.9929e-06
1 | 15164686 | 2017-01-17 08:52 | 2017-01-17 12:17 | 205 | 22 | 4510 | 0.013521 | 0.013322 | 6.5955e-05 | NAPA ID:26655 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 026655 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 338 | NONE | Replace ABS 338 and various sites XARMS | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.006661 | 5.5 | 2017 | 2017-01-17 | B | 22 | 0.013322 | 6.5955e-05
1 | 15164748 | 2017-01-25 09:36 | 2017-01-25 14:51 | 315 | 3 | 945 | 0.0028327 | 0.002805 | 8.9928e-06 | NAPA ID:26585 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 026585 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13081 | NONE | Install new Regulator 13081. Note all equipment will be installed by-pass ABS left closed & Links /4 & /6 will be left open. Regulator will be commissioned at a later date. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0014025 | 5.5 | 2017 | 2017-01-25 | B | 3 | 0.002805 | 8.9928e-06
1 | 15168878 | 2016-12-15 14:13 | 2016-12-15 16:50 | 156 | 1379 | 93573.5333 | 0.28067 | 0.26826 | 0.0041362 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P31602 | INSULATOR | Recloser 10083 & Recloser 10082 tripped on E/F flags, line was patrolled and sectionalised and a broken insulator was found at pole P 31602, line was isolated at Fused ABS F89 to replace the insulator. At the time of tripping KEG CB 10 was back feeding a section of Turitea CB 4 on NAPA 27223, this section of line was restored to service when CB 4 was restored after work was completed at 15:54. 1 X 11KV insulator replaced | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.26826 | 11 | 2017 | 2016-12-15 | C | 1379 | 0.26826 | 0.0041362
1 | 15170993 | 2016-12-15 14:45 | 2016-12-15 17:53 | 187 | 9 | 1320.35 | 0.0039603 | 0.003879 | 2.6995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 776435 | FUSE - ELEMENT/LINK (HV) | possibly 15171354 linked Faultman found blown fuses at Fuses 4205, line was patrolled and a magpie was found at pole 776435, magpie was removed supply restored.. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.003879 | 11 | 2017 | 2016-12-15 | C | 9 | 0.003879 | 2.6995e-05
1 | 15171021 | 2017-01-17 10:00 | 2017-01-17 13:00 | 180 | 3 | 540 | 0.0016189 | 0.001591 | 8.9938e-06 | NAPA ID:27040 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 027040 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | tc437 | NONE | Replace pole mount transformer TC437 and the associated hanger crossarm. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0007955 | 5.5 | 2017 | 2017-01-17 | B | 3 | 0.001591 | 8.9938e-06
1 | 15171235 | 2017-01-24 09:15 | 2017-01-24 16:33 | 438 | 145 | 62808 | 0.18828 | 0.18697 | 0.00043466 | NAPA ID:26968 TP_GREYTOWN GXP | 11 | Planned | 026968 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS S525 | NONE | Remove ABS S525 & jumper through with Iodine conductor Replace pole 799021 & install new recloser 11095 Commissioning of comms and recloser 11095 will be done at a later date, bypass and Links to be left opened with a The recloser and bypass to be the new open point as per Network Reconfiguration notice attached. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.093486 | 5.5 | 2017 | 2017-01-24 | B | 145 | 0.18697 | 0.00043466
1 | 15171296 | 2016-12-15 18:18 | 2016-12-15 19:50 | 92 | 4 | 368 | 0.0011038 | 0.001067 | 1.1998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781680 | BINDER | 2 HT Fuses found tripped at 2726. Patrol found a floating conductor at Pole 781680. Isolation from fuses 2726 to rebind in. Relivened. (2 HT fuses replaced at 5A rating). | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001067 | 11 | 2017 | 2016-12-15 | C | 4 | 0.001067 | 1.1998e-05
1 | 15171405 | 2017-01-13 09:00 | 2017-01-13 12:47 | 227 | 11 | 2497 | 0.0074863 | 0.007387 | 3.2979e-05 | NAPA ID:25681 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025681 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP346 | NONE | REPLACE HV ARMS | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0036935 | 5.5 | 2017 | 2017-01-13 | B | 11 | 0.007387 | 3.2979e-05
1 | 15171462 | 2017-01-13 11:10 | 2017-01-13 13:56 | 166 | 2 | 332 | 0.00099538 | 0.000977 | 5.9962e-06 | NAPA ID:25680 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025680 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP347 | NONE | REPLACE HV ARMS TRIM TREES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0004885 | 5.5 | 2017 | 2017-01-13 | B | 2 | 0.000977 | 5.9962e-06
1 | 15173902 | 2016-12-15 16:54 | 2016-12-15 19:41 | 167 | 93 | 10596.9667 | 0.031785 | 0.030948 | 0.00027895 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N21 | UNKNOWN | Tripping on Recloser N21 on B Phase EF. Feeder patrolled, sectionalised but nothing found. Restored OK. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.030948 | 11 | 2017 | 2016-12-15 | C | 93 | 0.030948 | 0.00027895
1 | 15174674 | 2016-12-15 18:39 | 2016-12-15 21:03 | 144 | 1 | 144.05 | 0.00043207 | 0.000423 | 2.9994e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | M83 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses tripped at M83. Reloaded OK (3A Rating) - suspect bird | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000423 | 11 | 2017 | 2016-12-15 | C | 1 | 0.000423 | 2.9994e-06
1 | 15174685 | 2016-12-15 18:40 | 2016-12-15 19:38 | 58 | 3 | 175.45 | 0.00052625 | 0.000499 | 8.9983e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SE5-282 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Fuses | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.000499 | 11 | 2017 | 2016-12-15 | C | 3 | 0.000499 | 8.9983e-06
1 | 15174705 | 2016-12-15 18:43 | 2016-12-16 14:05 | 1162 | 2 | 2324.9333 | 0.0069735 | 0.006955 | 5.9988e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 212644 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 HV fuses blown at transformer TE4-202. Single phase transformer. Transformer in bad condition, rusty & leaking oil down pole. Transformer replaced & relivened 14:05 | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.006955 | 11 | 2017 | 2016-12-15 | C | 2 | 0.006955 | 5.9988e-06
1 | 15174825 | 2016-12-15 19:15 | 2016-12-15 19:52 | 37 | 271 | 10112.8167 | 0.030333 | 0.027894 | 0.00081285 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | 832788 | NONE | Numerous faults started coming in on feeder beyond RS C201. FM sent to check status of RS C201 found it tripped. Also had a report of someone cutting trees at 151 Skeets Rd that may have caused the fault. FM reported that a tree branch had fallen through the lines but was now clear. RS C201 livened successfully. FM went to talk to the tree cutters & ordered them off site & will arrange for Powerco approved contractors to look at the site to get rest of trees removed. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.027894 | 11 | 2017 | 2016-12-15 | C | 271 | 0.027894 | 0.00081285
1 | 15174844 | 2016-12-15 19:23 | 2016-12-16 02:07 | 404 | 1070 | 229487.2667 | 0.68833 | 0.6787 | 0.0032094 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | N/A - NOT APPLICABLE | POLE | RS 9629 A/R, L/O & CB 8 Trip O/C A & B Phase. Report came in of car v pole. Work area isolated & CB 8 relivened up to RS 9629. 11m Busck Pole replaced NDR# 44724 Property at 366 Fraser St not connected as service line has been pulled away from the house. Awaiting repair before re connection | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.6787 | 11 | 2017 | 2016-12-15 | C | 1070 | 0.6787 | 0.0032094
1 | 15176831 | 2016-12-15 22:51 | 2016-12-16 00:55 | 123 | 360 | 43317.85 | 0.12993 | 0.12669 | 0.0010798 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | See OMS 15176814 | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.12669 | 11 | 2017 | 2016-12-15 | C | 360 | 0.12669 | 0.0010798
1 | 15177564 | 2016-12-15 23:05 | 2016-12-16 01:45 | 160 | 230 | 34183.6833 | 0.10253 | 0.10046 | 0.00068987 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P26466 | CROSSARM - WHOLE ASSEMBLY | Reports of no power found CB1 had tripped at Parkvile Sub (No Comms). Earth Fault protection operated. Burnt crossarm reported by Fire Service Nireaha Hall. Isolation required from ABS S5, S12 & S13. CB1 then closed locally. Temp Repairs carried out with a new insulator fitted (high winds, unable to change crossarm safely - will be defected by Robin). Feeder livened OK. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.10046 | 11 | 2017 | 2016-12-15 | C | 230 | 0.10046 | 0.00068987
1 | 15178069 | 2017-01-17 09:04 | 2017-01-17 11:40 | 156 | 62 | 9690.6 | 0.029052 | 0.028494 | 0.00018587 | NAPA ID:26390 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 026390 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 802286 | NONE | replace cracked insulators at pole 802286 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.014247 | 5.5 | 2017 | 2017-01-17 | B | 62 | 0.028494 | 0.00018587
1 | 15178091 | 2016-12-21 11:04 | 2016-12-21 14:45 | 221 | 78 | 5238 | 0.01571 | 0.015007 | 0.00045887 | NAPA ID:27323 TP_MASTERTON GXP > AKURA SUB > NGAUMUTAWA RD | 11 | Planned | 027323 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | red tag poles gp replace red tag pole 831450 | F2 | NGAUMUTAWA RD | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0075035 | 5.5 | 2017 | 2016-12-21 | B | 78 | 0.015007 | 0.00045887
1 | 15178778 | 2016-12-16 09:33 | 2016-12-16 14:46 | 312 | 26 | 8117.2 | 0.024347 | 0.024112 | 7.7984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 844155 | NONE | 1R - changed to 2R - Treescape required for Tree removal 12:03 mjk. Recloser 2713/2 tripped on A & B phase O/C flags, line was patrolled and broken branches was found on the lines at pole 844155, line was isolated at ABS 2846 & Links 2536 to get treescape to cut away the branches. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.024112 | 11 | 2017 | 2016-12-16 | C | 26 | 0.024112 | 7.7984e-05
1 | 15179436 | 2016-12-16 12:16 | 2016-12-16 13:48 | 92 | 1 | 92 | 0.00027594 | 0.000266 | 2.9993e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826912 | FUSE - ELEMENT/LINK (HV) | sent to ONC for follow up 17/01 2 x 2 amp magpie | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000266 | 11 | 2017 | 2016-12-16 | C | 1 | 0.000266 | 2.9993e-06
1 | 15180033 | 2016-12-16 16:26 | 2016-12-16 17:18 | 52 | 84 | 3641.3 | 0.010922 | 0.010165 | 0.00025195 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220072 | CROSSARM - WHOLE ASSEMBLY | PMA CB 8 RED Defect insulator needs replacing. Crossarm replaced at pole 220072. isolation at ABS IP598, 9876/1,Links 9876/6 Back feed from ATU 6 via sectionaliser 9954. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.010165 | 11 | 2017 | 2016-12-16 | C | 84 | 0.010165 | 0.00025195
1 | 15180047 | 2016-12-16 13:53 | 2016-12-16 14:18 | 24 | 195 | 4845.75 | 0.014534 | 0.012779 | 0.00058488 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213873 | JUMPER | Cable screen earths repaired at pole 213873. isolated at ABS IP75 & IP596. 2 connectors used | F3 | TAWA ST | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.012779 | 11 | 2017 | 2016-12-16 | C | 195 | 0.012779 | 0.00058488
1 | 15180348 | 2017-01-26 10:02 | 2017-01-26 14:45 | 283 | 15 | 4245 | 0.012725 | 0.012589 | 4.4963e-05 | NAPA ID:27229 TP_HUIRANGI GXP > INGLEWOOD SUB > KAIMATA | 6.6 | Planned | 027229 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 760526 | NONE | We are installing a 12.5m pole with a new 6.6kv ABS 12177 on it so CB I21 and CB I51 can be tied together via a 6.6kv U/G cable. Tarata Road, Inglewood, Huirangi. W/O 30036545. | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.0062945 | 3.3 | 2017 | 2017-01-26 | B | 15 | 0.012589 | 4.4963e-05
1 | 15180493 | 2016-12-16 16:40 | 2016-12-16 19:22 | 162 | 17 | 2754 | 0.0082603 | 0.008107 | 5.099e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771567 | CONDUCTOR - REPAIR/REHANG | Report of no power found a Broken 11kV conductor at Pole 771567. Isolation required from ABS 663. (NOTE: No tripping at Recloser 1112). Repairs made with 3m conductor used, 1 binder and 2 sleeves. Relivened OK. (Deterioration). | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.008107 | 11 | 2017 | 2016-12-16 | C | 17 | 0.008107 | 5.099e-05
1 | 15180528 | 2017-01-30 09:30 | 2017-01-30 14:39 | 308 | 18 | 5556.9 | 0.016656 | 0.016494 | 5.3953e-05 | NAPA ID:27230 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 6.6 | Planned | 027230 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 33kV 447993 | NONE | We are installing a new 11.5m pole to be able to tie CB I51 and CB I21 via a 6.6kv cable through a new vertical ABS 12177. Note the ABS will be on the 12.5m pole that will come under NAPA 27229. Tarata Road, Inglewood, Huirangi. W/O 30036545. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.008247 | 3.3 | 2017 | 2017-01-30 | B | 18 | 0.016494 | 5.3953e-05
1 | 15180635 | 2017-01-16 08:45 | 2017-01-16 15:00 | 375 | 101 | 37875 | 0.11355 | 0.11264 | 0.0003028 | NAPA ID:25226 TP_MASTERTON GXP > NORFOLK SUB > HOLDSWORTH | 11 | Planned | 025226 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX T2865 | NONE | Install new recloser and x5 sets of fuses. Norfolk Road, Carterton, Norfolk. W/O 30031186. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.05632 | 5.5 | 2017 | 2017-01-16 | B | 101 | 0.11264 | 0.0003028
1 | 15181527 | 2016-12-16 23:28 | 2016-12-16 23:29 | 1 | 36 | 36 | 0.00010798 | 0 | 0.00010798 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218818 | AIR BREAK SWITCH - ABS (HV) | Found ABS SE7-019 burning up. Backfeeds put in and ABS opened. Will need to be repaired or replaced. DNO 161210 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-12-16 | C | 36 | 0 | 0.00010798
1 | 15181609 | 2016-12-17 04:16 | 2016-12-17 06:24 | 128 | 20 | 2563.6667 | 0.0076893 | 0.007509 | 5.9987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7205 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses tripped at 7205. Reloaded OK (15A). Cause unknown | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.007509 | 11 | 2017 | 2016-12-17 | C | 20 | 0.007509 | 5.9987e-05
1 | 15181641 | 2016-12-17 07:35 | 2016-12-17 09:03 | 88 | 42 | 3696.1 | 0.011086 | 0.010707 | 0.00012597 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 209649 | FUSE - ELEMENT/LINK (HV) | Goose through the lines causing 2 fuses to blow at TD2-008L2. Truck needed to lift concrete lid off and replace fuses. Relivened & tested Isolated at Fuses SD2-017 to lift concrete lid & replace the fuses. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.010707 | 11 | 2017 | 2016-12-17 | C | 42 | 0.010707 | 0.00012597
1 | 15182257 | 2016-12-17 06:51 | 2016-12-17 08:53 | 121 | 47 | 5729.3 | 0.017184 | 0.016761 | 0.00014097 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q68 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.016761 | 11 | 2017 | 2016-12-17 | C | 47 | 0.016761 | 0.00014097
1 | 15183187 | 2017-01-26 09:15 | 2017-01-26 15:24 | 369 | 22 | 8118 | 0.024334 | 0.024136 | 6.5946e-05 | NAPA ID:26842 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 026842 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 778129 | NONE | Pole replacement & TX upgrades. 778129 - 778179. 47 in Total. Install Temp links 46 at pole 778154. Oruakukuru Road, Parapara, Ohakune. W/O 30018751. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.012068 | 5.5 | 2017 | 2017-01-26 | B | 22 | 0.024136 | 6.5946e-05
1 | 15184603 | 2016-12-17 12:48 | 2016-12-17 16:17 | 209 | 360 | 29896.1667 | 0.089669 | 0.086429 | 0.0010798 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835690 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Recloser 8097/2 Trip A,B O/C Faulty fuses at transformer T3283. Isolated at ABS S384. Replaced fuses relivened, Isolated Transformer T3283 at own fuses. Relivened at 1919 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.086429 | 11 | 2017 | 2016-12-17 | C | 360 | 0.086429 | 0.0010798
1 | 15187521 | 2016-12-17 19:06 | 2016-12-17 20:40 | 94 | 1 | 94.1167 | 0.00028229 | 0.000273 | 2.9993e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6993 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 6993, line was patrolled and no fault was found. 2 X 3 amp HV fuses replaced. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000273 | 11 | 2017 | 2016-12-17 | C | 1 | 0.000273 | 2.9993e-06
1 | 15187636 | 2016-12-17 21:00 | 2016-12-17 21:40 | 40 | 7 | 282.1 | 0.00084612 | 0.000783 | 2.0995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TA787 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses TA787 after a report of ducks that had hit the lines. 2 X 8 amp HV fuses replaced | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000783 | 11 | 2017 | 2016-12-17 | C | 7 | 0.000783 | 2.0995e-05
1 | 15188389 | 2016-12-18 09:45 | 2016-12-18 12:27 | 162 | 21 | 3402 | 0.010204 | 0.010014 | 6.2985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 727912 | POLE | Car hit a pole, reported by Mr Hollingsworth 06 273 6008. Faultman found pole 727912 to be damaged that was hit by car, pole safe for now but will need to be replaced at day light. NDR: 43445. Replaced 1x 11m pole complete with hv & lv crossarms complete | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.010014 | 11 | 2017 | 2016-12-18 | C | 21 | 0.010014 | 6.2985e-05
1 | 15188409 | 2016-12-18 06:57 | 2016-12-18 09:18 | 140 | 3 | 369.1333 | 0.0011071 | 0.00108 | 8.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sd3-088 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 6amp ht fuses at sd3-088 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.00108 | 11 | 2017 | 2016-12-18 | C | 3 | 0.00108 | 8.9979e-06
1 | 15188668 | 2016-12-18 12:08 | 2016-12-18 14:49 | 161 | 9 | 1449 | 0.004346 | 0.004265 | 2.6994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 7768 | NONE | Replaced 2 x amp ht fuses at 7768 which re operated. Checked line & found branch on line. Got tree cutters in to remove branch from tree. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.004265 | 11 | 2017 | 2016-12-18 | C | 9 | 0.004265 | 2.6994e-05
1 | 15188803 | 2016-12-18 10:26 | 2016-12-18 11:30 | 63 | 365 | 18909.1167 | 0.056714 | 0.053429 | 0.0010947 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 391384 | NONE | CB 4 LO on E/F Backfeed to Recloser RC25 via 9705. Reported branch on line at 153 Waghorn Rd. Removed branch & relivened | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.053429 | 11 | 2017 | 2016-12-18 | C | 365 | 0.053429 | 0.0010947
1 | 15189225 | 2016-12-18 11:10 | 2016-12-18 12:00 | 49 | 1 | 49.2833 | 0.00014782 | 0.000138 | 2.9993e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB4 | UNKNOWN | Part of CB 4 feeder fault. Cow shed at the back of the farm different to main address that was not part of the fault | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000138 | 11 | 2017 | 2016-12-18 | C | 1 | 0.000138 | 2.9993e-06
1 | 15190889 | 2016-12-18 22:59 | 2016-12-18 23:04 | 5 | 17 | 90.95 | 0.00027279 | 0.000119 | 5.0988e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7292 | FUSE - ELEMENT/LINK (HV) | 2x8amp HV fuses blown at 7292. line patrolled & reloaded & livened. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000119 | 11 | 2017 | 2016-12-18 | C | 17 | 0.000119 | 5.0988e-05
1 | 15190954 | 2016-12-18 21:55 | 2016-12-19 00:11 | 136 | 164 | 19063.9333 | 0.057178 | 0.055702 | 0.00049189 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C642 | UNKNOWN | CB C642 Trip B & C O/C line patrolled. No fault found | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.055702 | 11 | 2017 | 2016-12-18 | C | 164 | 0.055702 | 0.00049189
1 | 15191460 | 2016-12-19 06:49 | 2016-12-19 09:45 | 176 | 1 | 176 | 0.00052787 | 0.000518 | 2.9992e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/111 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced Transformer Due to leaking Oil | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000518 | 11 | 2017 | 2016-12-19 | C | 1 | 0.000518 | 2.9992e-06
1 | 15191585 | 2016-12-19 07:13 | 2016-12-19 09:56 | 163 | 2002 | 242774.95 | 0.72814 | 0.71013 | 0.0060045 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB C905 Trip CB 903 Trip LOS to entire sub | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.71013 | 33 | 2017 | 2016-12-19 | C | 2002 | 0.71013 | 0.0060045
1 | 15193598 | 2016-12-19 07:17 | 2016-12-19 09:36 | 139 | 678 | 54934 | 0.16476 | 0.15866 | 0.0020335 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB7 | UNKNOWN | 11kV CB 7 tripped B & C Phase. L/O. Fully patrolled nothing found. Issues with (comms) state on Sw/gear 10275/3 causing emap issues, will cause larger than actual SAIDI count, will need to be corrected, NCTL. OMS 15236684 created to resolve, had to apply temp jumper to switchgear to get power restored. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.15866 | 11 | 2017 | 2016-12-19 | C | 678 | 0.15866 | 0.0020335
1 | 15234603 | 2016-12-19 07:13 | 2016-12-19 08:59 | 106 | 109 | 10982.2167 | 0.032938 | 0.031957 | 0.00032692 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Rec 409 Trip O/C Line patrolled and sectionalised. Nothing found. Tripped again after 5 mins. Sectionalised and patrolled nothing found | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.031957 | 11 | 2017 | 2016-12-19 | C | 109 | 0.031957 | 0.00032692
1 | 15235020 | 2016-12-19 07:46 | 2016-12-19 09:35 | 108 | 2 | 217.3 | 0.00065174 | 0.000633 | 5.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09611 | FUSE - ELEMENT/LINK (HV) | 2 x 6a mainline clash P09611 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000633 | 11 | 2017 | 2016-12-19 | C | 2 | 0.000633 | 5.9985e-06
1 | 15235597 | 2016-12-19 09:10 | 2016-12-19 10:44 | 94 | 109 | 5450.35 | 0.016347 | 0.015366 | 0.00050987 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Rec 409 Trip O/C Line patrolled and sectionalised. Nothing found. Tripped again after 5 mins. Sectionalised and patrolled nothing found | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.015366 | 11 | 2017 | 2016-12-19 | C | 109 | 0.015366 | 0.00050987
1 | 15236047 | 2016-12-20 09:03 | 2016-12-20 13:34 | 271 | 79 | 21409 | 0.06421 | 0.063499 | 0.00023694 | NAPA ID:27793 TP_STRATFORD GXP | 11 | Planned | 027793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Cardiff 33Kv Line reconstruction poles & conductor Over 11Kv lines ( pole 737287 ). Liven 11Kv. New Ap to work on 33Kv in afternoon . Shut 2 of week starting 19/12/16 to 21/12/16 for this project . Reconfigure the Network for the start of this weeks outages . Rewrite of NAPA 25777 . This outage has been advertised as 2577 . | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.031749 | 5.5 | 2017 | 2016-12-20 | B | 79 | 0.063499 | 0.00023694
1 | 15237529 | 2016-12-19 10:16 | 2016-12-19 11:43 | 86 | 241 | 17555.45 | 0.052653 | 0.050484 | 0.00072282 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB6 | UNKNOWN | CB 6 Tripped B Phase OC EF | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.050484 | 11 | 2017 | 2016-12-19 | C | 241 | 0.050484 | 0.00072282
1 | 15238674 | 2017-01-18 08:15 | 2017-01-18 14:57 | 402 | 40 | 16080 | 0.048206 | 0.047846 | 0.00011992 | NAPA ID:27759 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 027759 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole O448 | NONE | Move TC474 to 0446 install New pole install new TP3091 at pole 0450 replace HV Xarms. 1547 Kaihere Road, Ngatea, Kerepehi. W/O 30036210. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.023923 | 5.5 | 2017 | 2017-01-18 | B | 40 | 0.047846 | 0.00011992
1 | 15238707 | 2017-01-17 08:34 | 2017-01-17 14:39 | 365 | 2 | 730 | 0.0021885 | 0.00217 | 5.9959e-06 | NAPA ID:26604 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11 | Planned | 026604 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuse 421 | NONE | Replace t/f pole 796470 / x515 and hardware. 1358 Kawhatau Valley Road, Mangaweke, Taihape. W/O 30032330. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001085 | 5.5 | 2017 | 2017-01-17 | B | 2 | 0.00217 | 5.9959e-06
1 | 15238743 | 2017-01-13 09:30 | 2017-01-13 11:53 | 143 | 1 | 143 | 0.00042873 | 0.000419 | 2.9981e-06 | NAPA ID:27757 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | 027757 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W13441 | NONE | Replace Red Tag pole W13441. Whitianga Road, Tairua. W/O 30035655. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.0002095 | 5.5 | 2017 | 2017-01-13 | B | 1 | 0.000419 | 2.9981e-06
1 | 15239106 | 2017-01-16 09:52 | 2017-01-16 12:37 | 165 | 30 | 4950 | 0.01484 | 0.01457 | 8.994e-05 | NAPA ID:27758 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | 027758 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 323 | NONE | Replace Red Tag pole W13390. Boat Harbour Road, Whenuakite, Tairua. W/O 30035653. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.007285 | 5.5 | 2017 | 2017-01-16 | B | 30 | 0.01457 | 8.994e-05
1 | 15239158 | 2016-12-19 14:00 | 2016-12-19 18:55 | 295 | 39 | 11505 | 0.034506 | 0.034155 | 0.00011697 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 732689 | POLE | Advised SMC and control of 999 ( ELT R21 ) Emergency switching to replace pole 732689 ( car v pole ) Isolations between ABS's 6176, 6193 & 6041 with back feeds via ABS's 6169 & 6125. Pole replaced, used 1 x complete pole structure NDR # 38871 | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.034155 | 11 | 2017 | 2016-12-19 | C | 39 | 0.034155 | 0.00011697
1 | 15240726 | 2016-12-19 14:54 | 2016-12-19 15:52 | 58 | 55 | 3190 | 0.0095676 | 0.009072 | 0.00016496 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS S536 | JUMPER | Blown Jumper at ABS S536 Used 1 X ABS Jumper isolated at ABS S522& cb912 | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.009072 | 11 | 2017 | 2016-12-19 | C | 55 | 0.009072 | 0.00016496
1 | 15245152 | 2016-12-19 14:15 | 2016-12-19 20:06 | 350 | 1 | 350.9333 | 0.0010525 | 0.001043 | 2.9992e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | - | UNKNOWN |  | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.001043 | 11 | 2017 | 2016-12-19 | C | 1 | 0.001043 | 2.9992e-06
1 | 15245697 | 2016-12-19 14:21 | 2016-12-19 17:33 | 192 | 182 | 31787.35 | 0.095338 | 0.0937 | 0.00054586 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 15245152 | UNKNOWN | Recloser F55 Tripped A, B Ph O/C L/O No Fault found during sectionlising | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0937 | 11 | 2017 | 2016-12-19 | C | 182 | 0.0937 | 0.00054586
1 | 15245739 | 2017-01-09 13:00 | 2017-01-09 13:30 | 30 | 2 | 60 | 0.0001799 | 0.000161 | 5.9965e-06 | NAPA ID:27801 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ROBERTS LINE | 11 | Planned | 027801 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX T2/813 | NONE | Close 11KV Gap P02196. Staces Road, Palmerston North, Roberts Line. W/O 30032359. | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 8.05e-05 | 5.5 | 2017 | 2017-01-09 | B | 2 | 0.000161 | 5.9965e-06
1 | 15245923 | 2017-01-17 09:01 | 2017-01-17 14:58 | 357 | 11 | 3927 | 0.011773 | 0.011674 | 3.2977e-05 | NAPA ID:25683 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025683 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rangiuru Road | NONE | REPLACE HV ARMS AND POLES BEYOND FUSES SF5-064 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.005837 | 5.5 | 2017 | 2017-01-17 | B | 11 | 0.011674 | 3.2977e-05
1 | 15248354 | 2016-12-19 19:18 | 2016-12-19 20:10 | 51 | 1 | 51.8667 | 0.00015556 | 0.000146 | 2.9992e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21616 | FUSE - ELEMENT/LINK (HV) | Fuse found Blown at Fuses M83 - Cause Wind Used 2 x 3amp | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000146 | 11 | 2017 | 2016-12-19 | C | 1 | 0.000146 | 2.9992e-06
1 | 15249200 | 2016-12-20 05:54 | 2016-12-20 07:15 | 81 | 6 | 486.1 | 0.0014579 | 0.001403 | 1.7995e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 757801 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 5482 2 x 10A Bird strike | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001403 | 6.6 | 2017 | 2016-12-20 | C | 6 | 0.001403 | 1.7995e-05
1 | 15249900 | 2017-01-18 09:00 | 2017-01-18 12:40 | 220 | 5 | 1100 | 0.0032977 | 0.003252 | 1.4989e-05 | NAPA ID:25684 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025684 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Oak Drive | NONE | REPLACE HV ARMS AND POLES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001626 | 5.5 | 2017 | 2017-01-18 | B | 5 | 0.003252 | 1.4989e-05
1 | 15249946 | 2017-01-19 08:30 | 2017-01-19 14:53 | 383 | 10 | 3830 | 0.011482 | 0.011391 | 2.9979e-05 | NAPA ID:25704 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025704 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rangiuru Road | NONE | REPLACE HV ARMS AND POLES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0056955 | 5.5 | 2017 | 2017-01-19 | B | 10 | 0.011391 | 2.9979e-05
1 | 15250145 | 2016-12-20 08:59 | 2016-12-20 12:04 | 184 | 1 | 184.7833 | 0.0005542 | 0.000545 | 2.9992e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 848262 | FUSE - ELEMENT/LINK (HV) | 2x HV fuses 10Amp, due to Goose | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000545 | 11 | 2017 | 2016-12-20 | C | 1 | 0.000545 | 2.9992e-06
1 | 15250152 | 2017-01-13 08:45 | 2017-01-13 16:29 | 464 | 13 | 6032 | 0.018085 | 0.017967 | 3.8976e-05 | NAPA ID:27186 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 027186 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | UNKNOWN | Replace poles, crossarms and connect 11kv cable to newly installed fused ABS 11097 at pole 451460 and connect at T3434 then remove two span of overhead 11kv line between poles 834699 and 834658(7464) | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0089835 | 5.5 | 2017 | 2017-01-13 | B | 13 | 0.017967 | 3.8976e-05
1 | 15251915 | 2016-12-20 09:53 | 2016-12-20 11:02 | 69 | 40 | 2760 | 0.0082778 | 0.007917 | 0.00011997 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 804280 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | fuses 081 opened to replace fuses and fix missing bolts at Fuses 2510 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.007917 | 11 | 2017 | 2016-12-20 | C | 40 | 0.007917 | 0.00011997
1 | 15258207 | 2016-12-21 10:45 | 2016-12-21 14:31 | 225 | 12 | 2710.2 | 0.0081283 | 0.00802 | 3.599e-05 | NAPA ID:27709 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 027709 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | relocation pole pole due to slipping | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.00401 | 5.5 | 2017 | 2016-12-21 | B | 12 | 0.00802 | 3.599e-05
1 | 15259079 | 2017-01-06 20:01 | 2017-01-20 23:28 | 20367 | 57 | 2385.8 | 0.0071537 | 0.00664 | 0.00017991 | NAPA ID:27175 TP_BUNNYTHORPE GXP > KEITH ST SUB > KEITH ST 23 | 11 | Planned | 027175 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G190 | NONE | make line break at TB103, isolate G190, demolish TX site G190, install new TX and SW at G190 site, liven switch 10311/4 and 10311/2, isolate TB103, carry out through joints on the 2 11KV legs then liven each leg, remove TB103. | F3 | KEITH ST 23 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.00332 | 5.5 | 2017 | 2017-01-06 | B | 57 | 0.00664 | 0.00017991
1 | 15259533 | 2017-01-27 09:45 | 2017-01-27 14:30 | 285 | 3 | 855 | 0.0025629 | 0.002535 | 8.9925e-06 | NAPA ID:26596 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 026596 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4786 | NONE | To replace 11kV Arms, 400V arms & Install 400V Fuse Disc. TC4786 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0012675 | 5.5 | 2017 | 2017-01-27 | B | 3 | 0.002535 | 8.9925e-06
1 | 15259616 | 2017-01-18 09:55 | 2017-01-18 13:00 | 185 | 3 | 555 | 0.0016638 | 0.001636 | 8.9937e-06 | NAPA ID:27829 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 027829 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1061 | NONE | De Energise TC1061 to install DIN fusing and raise LV Xarm for road crossing being hit by construction trucks on council site. Xing too low | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000818 | 5.5 | 2017 | 2017-01-18 | B | 3 | 0.001636 | 8.9937e-06
1 | 15260138 | 2017-01-18 10:35 | 2017-01-18 12:00 | 85 | 2 | 170 | 0.00050964 | 0.000491 | 5.9958e-06 | NAPA ID:27830 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 027830 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3381 | NONE | Change 11kV P/M defect Transformer TC3381 under Own Isolation & AP. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.0002455 | 5.5 | 2017 | 2017-01-18 | B | 2 | 0.000491 | 5.9958e-06
1 | 15260352 | 2017-01-24 09:00 | 2017-01-24 14:28 | 328 | 7 | 2296 | 0.0068826 | 0.006819 | 2.0983e-05 | NAPA ID:25706 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025706 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rangiuru Road | NONE | REPLACE HV ARMS AND POLES | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0034095 | 5.5 | 2017 | 2017-01-24 | B | 7 | 0.006819 | 2.0983e-05
1 | 15260894 | 2016-12-22 09:16 | 2016-12-22 10:13 | 56 | 28 | 1590.8667 | 0.0047712 | 0.004519 | 8.3975e-05 | NAPA ID:27827 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | 027827 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | IO439 | POLE | Replace pole I0440 hit by truck to maintain legal ground clearance | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0022595 | 5.5 | 2017 | 2016-12-22 | B | 28 | 0.004519 | 8.3975e-05
1 | 15261982 | 2016-12-20 23:20 | 2016-12-21 00:30 | 70 | 11 | 770 | 0.0023094 | 0.00221 | 3.2991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | 769185 | CONDUCTOR - REPAIR/REHANG | SMC advised 8:29pm. No answer on phone number provided for hazard process Tractor with pole rammer hit lines between Poles 769185 & 367014 Used 55 metres 25 mm PVC copper & 4 sleeves. NDR 56356 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.00221 | 11 | 2017 | 2016-12-20 | C | 11 | 0.00221 | 3.2991e-05
1 | 15263895 | 2017-01-20 08:55 | 2017-01-20 14:35 | 340 | 3 | 1020 | 0.0030578 | 0.00303 | 8.9934e-06 | NAPA ID:26372 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 026372 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pahioa Road | NONE | change poles and x arms and recon | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.001515 | 5.5 | 2017 | 2017-01-20 | B | 3 | 0.00303 | 8.9934e-06
1 | 15264004 | 2017-01-13 08:46 | 2017-01-13 13:00 | 254 | 37 | 9398 | 0.028176 | 0.027843 | 0.00011093 | NAPA ID:27818 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 027818 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K1575 | NONE | TO REMEDY RED TAG WORKS ON POLES K1575 & K13382, SET POLES IN GROUND TO CORRECT DEPTH AND CHANGE ROTTEN A2/P. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.013921 | 5.5 | 2017 | 2017-01-13 | B | 37 | 0.027843 | 0.00011093
1 | 15265240 | 2016-12-21 08:17 | 2016-12-21 10:12 | 115 | 1 | 115.3 | 0.0003458 | 0.000336 | 2.9991e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 264453 | FUSE - ELEMENT/LINK (HV) | 2 x6amp unknown 682 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000336 | 11 | 2017 | 2016-12-21 | C | 1 | 0.000336 | 2.9991e-06
1 | 15265510 | 2016-12-21 12:05 | 2016-12-22 03:30 | 925 | 14 | 11630 | 0.03488 | 0.034754 | 4.1988e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 221119 | CABLE - REPAIR | at 12:05, Te Puke Sub, CB 2 Mangorewa Feeder. Faultman dispatched to job of low voltages/part powers. found HV Fuse blown at Fuses SE6-084. Patrolled line and looked OK. Found terminations in bad condition and believed this could be cause of fault. Isolated lines at Fuses SE6-084, Permit issued & repairs carried out. When trying to reliven fuses blew again. Permits then issued to isolate / test each section of cable. Found cable fault on 11kV cable connected to fuses SE6-084. Permit issued & repairs carried out. All power restored on completion. Clint Johnstone Attended. Materials: Generators connected to TE6-088 at 00:30 Generators connected to TE6-092 at 01:00 Sectionalised & found fault on cable at SE6-084 Generators connected to TE6-088 at 00:30 & TE6-092 at 01:00 Repaired cable & relivened | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.034754 | 11 | 2017 | 2016-12-21 | C | 14 | 0.034754 | 4.1988e-05
1 | 15265831 | 2017-01-19 10:15 | 2017-01-19 15:12 | 297 | 226 | 67122 | 0.20122 | 0.19919 | 0.00067752 | NAPA ID:27832 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11 | Planned | 027832 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P40746 | NONE | Replace 11KV redtagged pole P40746 | F2 | FAIRS RD | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.099595 | 5.5 | 2017 | 2017-01-19 | B | 226 | 0.19919 | 0.00067752
1 | 15266321 | 2017-01-31 09:34 | 2017-01-31 14:38 | 303 | 19 | 5775.05 | 0.01731 | 0.017138 | 5.695e-05 | NAPA ID:26984 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | 026984 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Magone Valley Road | NONE | To replace red tagged poles (GP) | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.008569 | 5.5 | 2017 | 2017-01-31 | B | 19 | 0.017138 | 5.695e-05
1 | 15266372 | 2017-01-17 09:50 | 2017-01-17 16:10 | 380 | 5 | 1900 | 0.0056961 | 0.005651 | 1.499e-05 | NAPA ID:27835 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11 | Planned | 027835 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 392574 | NONE | Replace pole 392574 and upgrade Tx to 100kVA using Live Line Techniques. Disconnect existing drop-out fuses on transformer structure TC3-032 using Live-line techniques and then replace drop-out fuses, transformer and LV crossarm. Reconnect drop-out fuses using live-line techniques and commission replacement transformer. | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.0028255 | 5.5 | 2017 | 2017-01-17 | B | 5 | 0.005651 | 1.499e-05
1 | 15267333 | 2016-12-21 15:09 | 2016-12-21 16:36 | 86 | 101 | 8743.2333 | 0.026222 | 0.025313 | 0.00030291 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 386103 | FUSE - ELEMENT/LINK (HV) | 2 x 15 amp line patrolled nothing found | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.025313 | 11 | 2017 | 2016-12-21 | C | 101 | 0.025313 | 0.00030291
1 | 15283124 | 2016-12-21 18:31 | 2016-12-21 21:05 | 154 | 4 | 616 | 0.0018475 | 0.001811 | 1.1997e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717552 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | SMC advised 7:33pm 760 Fire comms requesting ETA F2212760 - advised 10mins Transformer M2015 found to be faulty - isolated at fuses for transformer Transformer replaced used 1 x 30 kVA Transformer 3 x fuse carriers, 3 x 3amp fuses | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001811 | 11 | 2017 | 2016-12-21 | C | 4 | 0.001811 | 1.1997e-05
1 | 15283495 | 2016-12-21 21:31 | 2016-12-21 22:54 | 83 | 43 | 3579.0333 | 0.010734 | 0.010347 | 0.00012896 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784444 | FUSE - ELEMENT/LINK (HV) | Also affecting 43 Waireka Road - X1161 @ Fuses found blown at Fuses 586, line patrolled with no fault found Used 2 x 20 amp fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.010347 | 11 | 2017 | 2016-12-21 | C | 43 | 0.010347 | 0.00012896
1 | 15283924 | 2016-12-21 19:05 | 2016-12-22 00:25 | 320 | 28 | 8960 | 0.026872 | 0.02662 | 8.3976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | R12958 | CONDUCTOR - REPAIR/REHANG | Isolated at fuses FC4128, cut tress & relivened oms 15268458 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.02662 | 11 | 2017 | 2016-12-21 | C | 28 | 0.02662 | 8.3976e-05
1 | 15284221 | 2017-01-25 08:30 | 2017-01-25 10:07 | 97 | 72 | 6984 | 0.020935 | 0.020287 | 0.00021583 | NAPA ID:27087 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 027087 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Welcome Bay Rd | NONE | Change double HV xarm , | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.010143 | 5.5 | 2017 | 2017-01-25 | B | 72 | 0.020287 | 0.00021583
1 | 15284269 | 2017-01-17 05:30 | 2017-01-17 15:30 | 600 | 226 | 16752 | 0.050222 | 0.048189 | 0.0010193 | NAPA ID:23915 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > PAPAMOA BEACH WEST | 11 | Planned | 023915 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | PMA7 | NONE | 1. Install Backfeed from PMA7 2. Create Isolations SD5-067 /L1 & L2. (AP1) 3. Cable-break at link-box SD5-085 and install generators at transformers TD5-143 & TD5-159. (AP2) 4. Terminate cable from SD5-289 at new RMU 13098/3, cable from TD5-143 at fuse-switch 13098/2, & cable from TD5-159 at fuse-switch 13098/4. (AP3) 5. Test cables (TP) & liven new Sw/gear 13098 6. Remove generators at TD5-143 & TD5-159 (AP4) & liven from new Fuse /Sw 13098/2 & 13098/4. | F3 | PAPAMOA BEACH WEST | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.024095 | 5.5 | 2017 | 2017-01-17 | B | 226 | 0.048189 | 0.0010193
1 | 15284276 | 2016-12-22 08:09 | 2016-12-22 11:47 | 217 | 1 | 217.9667 | 0.00065371 | 0.000644 | 2.9991e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3340 | FUSE - ELEMENT/LINK (HV) | 2 x 3A Fuses replaced at Fuses FC1412. Caused by faulty single phase 15kVA Transformer TC3340. TC3340 replaced. 1 x 2A HV Fuses replaced at TC3340 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000644 | 11 | 2017 | 2016-12-22 | C | 1 | 0.000644 | 2.9991e-06
1 | 15284324 | 2017-01-25 09:30 | 2017-01-25 13:33 | 243 | 10 | 2430 | 0.0072842 | 0.007194 | 2.9976e-05 | NAPA ID:26711 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | 026711 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4730 | NONE | Remove TC4730 (relocate to new pole) Replace pole O13415 with new transformer structure and upgrade transformer with new 50KVA | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003597 | 5.5 | 2017 | 2017-01-25 | B | 10 | 0.007194 | 2.9976e-05
1 | 15284359 | 2017-01-20 08:45 | 2017-01-20 15:19 | 394 | 58 | 22852 | 0.068506 | 0.067984 | 0.00017387 | NAPA ID:27189 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | 027189 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T12553 | NONE | Thames additional Feeder Pre-works Replace Pole T12553 in preparation for it to become a cable pole. Reconductor from T0206 to FC4111 | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.033992 | 5.5 | 2017 | 2017-01-20 | B | 58 | 0.067984 | 0.00017387
1 | 15284537 | 2017-01-23 09:45 | 2017-01-23 12:20 | 155 | 7 | 1085 | 0.0032525 | 0.003189 | 2.0984e-05 | NAPA ID:27039 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 027039 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | tc2404 | NONE | Replace pole mount transformer TC2404 and the associated hanger crossarm. While the transformer is isolated LV crossarm to be replaced on poles O3896, O3988, O3989 and O3993. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0015945 | 5.5 | 2017 | 2017-01-23 | B | 7 | 0.003189 | 2.0984e-05
1 | 15284597 | 2017-01-24 08:30 | 2017-01-24 15:10 | 400 | 18 | 6826 | 0.020462 | 0.0203 | 5.3958e-05 | NAPA ID:27204 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027204 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4911 | NONE | PQI Upgrade TC4911 and reconductor between Poles V0266 and V0276 Upgrade 11KV Hardware | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.01015 | 5.5 | 2017 | 2017-01-24 | B | 18 | 0.0203 | 5.3958e-05
1 | 15284786 | 2017-01-26 08:45 | 2017-01-26 16:00 | 435 | 17 | 7251 | 0.021735 | 0.021582 | 5.0959e-05 | NAPA ID:27212 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027212 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V0266 | NONE | PQI Reconductor between Poles V0266 and V0276 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.010791 | 5.5 | 2017 | 2017-01-26 | B | 17 | 0.021582 | 5.0959e-05
1 | 15284824 | 2016-12-22 10:22 | 2016-12-22 11:31 | 69 | 59 | 4071 | 0.012209 | 0.011678 | 0.00017695 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 791184 | CONDUCTOR - REPAIR/REHANG | FM found HV line down at Pole 791184 due to bird strike. Isolated at ABS 251 and repaired using 2mtrs of 16mm conductor & two conductor joints | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.011678 | 11 | 2017 | 2016-12-22 | C | 59 | 0.011678 | 0.00017695
1 | 15285665 | 2017-01-18 14:30 | 2017-01-18 15:23 | 53 | 112 | 5936 | 0.017796 | 0.016788 | 0.00033577 | NAPA ID:23931 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > PAPAMOA BEACH WEST | 11 | Planned | 023931 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-085 | NONE | Terminate cable from SD5-085 at new RMU 13098-1 (livened day prior NAPA 23915) . Test, liven & phase check | F3 | PAPAMOA BEACH WEST | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.008394 | 5.5 | 2017 | 2017-01-18 | B | 112 | 0.016788 | 0.00033577
1 | 15285672 | 2016-12-22 12:32 | 2016-12-22 13:03 | 30 | 18 | 556.8 | 0.0016699 | 0.001507 | 5.3984e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M1692 - NEED PAPERWORK | SWITCH (HV) | Sw/Gear 1352 (DNO 161211) hit by car again. Required cable disconnected at Pole M1692 for safety. Isolation required between Sw/Gear 1352, Links IP499 and ABS 917. (NOTE: outage area extended due to faulty recloser RC36 (DNO 161212). Sw/Gear damaged and to be replaced | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001507 | 11 | 2017 | 2016-12-22 | C | 18 | 0.001507 | 5.3984e-05
1 | 15285785 | 2017-01-20 10:40 | 2017-01-20 12:15 | 95 | 5 | 475 | 0.001424 | 0.001379 | 1.4989e-05 | NAPA ID:27038 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 027038 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace pole mount transformer TC464 and the associated hanger crossarm. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0006895 | 5.5 | 2017 | 2017-01-20 | B | 5 | 0.001379 | 1.4989e-05
1 | 15285897 | 2017-01-24 08:45 | 2017-01-24 16:15 | 450 | 79 | 3269 | 0.0097993 | 0.009088 | 0.00024281 | NAPA ID:27219 TP_HINUERA GXP > TIRAU SUB > PROSPECT ST | 11 | Planned | 027219 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 13105 | NONE | Install new RMU 13105, Install new TX TP3008, Connect to IC3069 and TC 4855 | F4 | PROSPECT ST | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.004544 | 5.5 | 2017 | 2017-01-24 | B | 79 | 0.009088 | 0.00024281
1 | 15285900 | 2016-12-22 13:27 | 2016-12-22 16:34 | 187 | 358 | 47049.1167 | 0.14111 | 0.13788 | 0.0010737 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722888 | CROSSARM - WHOLE ASSEMBLY | Tripping on recloser 6728 on EF Phase B. Fault caused by broken crossarm at Pole 722888. Isolation required between ABS 6875, Links 8948/6 ans ABS 6620 with backfeed at ABS WH855. Full crossarm assembly replaced, relivened OK. | F1 | GLOVER RD EAST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.13788 | 11 | 2017 | 2016-12-22 | C | 358 | 0.13788 | 0.0010737
1 | 15286303 | 2016-12-22 13:48 | 2016-12-22 15:13 | 84 | 1 | 84.5667 | 0.00025362 | 0.000244 | 2.9991e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M1476 | CABLE - REPLACE LESS THAN 5 METRES | 28/12/16 - Operational Control Transferred to Mike Jefferies Downer to repair 11kV Cable Fault beyond Fuses 1322. Own Isolation, Earthing and Permit Issued - All Repairs Competed. Closed Fuses 1322 at 14:30. 1x HV Joint Kit & 3x 55A HV Fuses Replaced. Digger has exposed the underground 11kv line, has tripped three DDO fuses , quarry has no power. Damaged Cable to be repaired over Xmas break. (Signed authorisation from Quarry to leave power off until repairs made). Job to be completed under DNO 161213 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000244 | 11 | 2017 | 2016-12-22 | C | 1 | 0.000244 | 2.9991e-06
1 | 15286721 | 2016-12-22 13:19 | 2016-12-22 15:20 | 120 | 25 | 3021.6667 | 0.0090623 | 0.008837 | 7.4978e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 717395 | CONDUCTOR - REPAIR/REHANG | Fuses TA857 found tripped on Omuturangi Rd. Patrol found 2 11kV conductors broken caused by bird strike (Seagull). Isolation required from Fuses TA857. 6 sleeves used along with 3 HV fuses at 9A rating. Relivened OK. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.008837 | 11 | 2017 | 2016-12-22 | C | 25 | 0.008837 | 7.4978e-05
1 | 15286851 | 2017-01-23 09:15 | 2017-01-23 14:03 | 288 | 16 | 4608 | 0.013813 | 0.013669 | 4.7963e-05 | NAPA ID:27839 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV | 11.00000000 | Planned | 027839 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 216529 | NONE | Replace pole 216529 and upgrade Tx to 100kVA using Live Line Techniques. Disconnect existing drop-out fuses on transformer structure TC4-005 using Live-line techniques and then replace drop-out fuses, transformer and LV crossarm. Reconnect drop-out fuses using live-line techniques and commission replacement transformer. This outage went to 15:26 but there was an unplanned outage starting at 1404 that affected these same customers. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0068345 | 5.5 | 2017 | 2017-01-23 | B | 16 | 0.013669 | 4.7963e-05
1 | 15286885 | 2016-12-31 14:12 | 2016-12-31 16:32 | 140 | 4 | 560 | 0.0016793 | 0.001643 | 1.1995e-05 | NAPA ID:26561 TP_MASTERTON GXP > NORFOLK SUB > WAINGAWA RD | 11 | Planned | 026561 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C881 | NONE | Install underground cable and replace CB881. NOTE: Gavin Grey (027 234 3206) will be the recipient of the LLP's. | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.0008215 | 5.5 | 2017 | 2016-12-31 | B | 4 | 0.001643 | 1.1995e-05
1 | 15287066 | 2016-12-23 09:46 | 2016-12-23 10:54 | 68 | 38 | 2592.8667 | 0.0077762 | 0.007434 | 0.00011396 | NAPA ID:27886 TP_GREYTOWN GXP > FEATHERSTON SUB > DAIRY FACTORY | 11 | Planned | 027886 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace red tag pole 799805,dug below ground level and found signs of rot,pole is next to SH53 and very visual to the public,Talking to Powerco area manager Gavin Paget replace tomorrow | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.003717 | 5.5 | 2017 | 2016-12-23 | B | 38 | 0.007434 | 0.00011396
1 | 15287768 | 2016-12-22 17:20 | 2016-12-22 18:58 | 97 | 145 | 6232.3 | 0.018691 | 0.017386 | 0.00043487 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser 575 Tripped O/C L/O Line patrolled while sectionlising with no fault found | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.017386 | 11 | 2017 | 2016-12-22 | C | 145 | 0.017386 | 0.00043487
1 | 15288017 | 2016-12-22 17:54 | 2016-12-22 19:16 | 81 | 2 | 163.2667 | 0.00048965 | 0.000471 | 5.9982e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4096 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 3x 3A HV Fuses at Transformer TC4096. Unknown Cause | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000471 | 11 | 2017 | 2016-12-22 | C | 2 | 0.000471 | 5.9982e-06
1 | 15288661 | 2016-12-23 | 2016-12-23 05:15 | 314 | 241 | 45301.2 | 0.13586 | 0.13369 | 0.0014605 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773600 | INSULATOR | Line Down found at Pole 773600 during sectionlising Isolated at ABS 249, ABS 1221 and Links 4050 Cause blown HV Insulator Used 1 x HV Insulator, 5 metres Conductor, 2 x Sleeves, 1 x Distribution Tie | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.13369 | 11 | 2017 | 2016-12-23 | C | 241 | 0.13369 | 0.0014605
1 | 15289764 | 2016-12-23 02:40 | 2016-12-23 06:45 | 244 | 93 | 14617.3833 | 0.043839 | 0.043001 | 0.00039288 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10061 | INSULATOR | Recloser N21 Tripped B Ph E/F Fault found to be past Fuses N31 during sectionlising Isolated at Fuses N31 to replace insulator on pole P10061. 1 X 11KV insulator replaced. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.043001 | 11 | 2017 | 2016-12-23 | C | 93 | 0.043001 | 0.00039288
1 | 15291400 | 2016-12-23 02:49 | 2016-12-23 09:45 | 415 | 120 | 38127.3333 | 0.11435 | 0.11327 | 0.00059981 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04775 | INSULATOR | Recloser V27 Tripped B Ph E/F, line was patrolled and 2 faults were found, broken insulators on pole P04775 and floating wire on pole P04958, line was isolated at ABS V35 to replace & repair the faults. 6 X 11kV clamp top insulators replaced - Pole P04775. 1 X binder replaced. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.11327 | 11 | 2017 | 2016-12-23 | C | 120 | 0.11327 | 0.00059981
1 | 15292050 | 2016-12-23 06:54 | 2016-12-23 10:42 | 227 | 8 | 1656.95 | 0.0049693 | 0.004897 | 2.3993e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | FP1208 | FUSE - ELEMENT/LINK (HV) | 2HT Fuses at FP1208 found tripped. Line patrolled OK. Fuses tripped agin on relivening. Each transformer isolated and livened one at a time. All restored OK. Cause unknown. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.004897 | 11 | 2017 | 2016-12-23 | C | 8 | 0.004897 | 2.3993e-05
1 | 15292092 | 2016-12-23 07:10 | 2016-12-23 09:38 | 147 | 16 | 2364.8 | 0.0070922 | 0.006948 | 4.7985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792455 | FUSE - ELEMENT/LINK (HV) | 2 x 15amp 2951 unknown | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.006948 | 11 | 2017 | 2016-12-23 | C | 16 | 0.006948 | 4.7985e-05
1 | 15292214 | 2016-12-23 07:51 | 2016-12-23 09:33 | 101 | 14 | 1420.5333 | 0.0042603 | 0.004134 | 4.1987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1948 | FUSE - ELEMENT/LINK (HV) | 15292542 - could be poss linked to HV fuses FP1214 called and advised mike ( left message on cell phone emailed SMC LV to HV fp1214 2 x 10amp unknown | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.004134 | 11 | 2017 | 2016-12-23 | C | 14 | 0.004134 | 4.1987e-05
1 | 15292344 | 2017-02-02 10:00 | 2017-02-02 13:20 | 200 | 1 | 200 | 0.00059945 | 0.00059 | 2.9972e-06 | NAPA ID:27856 TP_HUIRANGI GXP > BELL BLOCK SUB > LEPPERTON | 11 | Planned | 027856 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 485 RIchmond Road, Lepperton | NONE | 10 Yearly 11kV metering for mayor customer. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000295 | 5.5 | 2017 | 2017-02-02 | B | 1 | 0.00059 | 2.9972e-06
1 | 15292379 | 2017-02-02 18:09 | 2017-02-02 19:49 | 100 | 1 | 100 | 0.00029973 | 0.00029 | 2.9972e-06 | NAPA ID:27857 TP_CARRINGTON GXP > CITY SUB > CITY 4 | 11 | Planned | 027857 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WITT Campus, Bell Street, New Plymouth | NONE | 10 Yearly 11kV metering for mayor customer. | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.000145 | 5.5 | 2017 | 2017-02-02 | B | 1 | 0.00029 | 2.9972e-06
1 | 15292616 | 2016-12-23 12:26 | 2016-12-23 13:25 | 58 | 6 | 353.3 | 0.0010596 | 0.001005 | 1.7994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I1846 | CROSSARM - WHOLE ASSEMBLY | Report of low hanging line found broken cross arm at Pole I1846. Isolation required from Piako Sub CB5 to ABS IC2529 with backfeed at ABS IC2524. Crossarm Assembly replaced, relivened. Stuck in restored will not allow job to be signed of in one site. Note - outage reflected under OMS 15295674 - this OMS should have been raised as a Site Inspection. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.001005 | 11 | 2017 | 2016-12-23 | C | 6 | 0.001005 | 1.7994e-05
1 | 15294354 | 2016-12-23 11:34 | 2016-12-23 14:22 | 168 | 1 | 168 | 0.00050384 | 0.000494 | 2.999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4623 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV and 2 x100A LV Fuses replaced | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.000494 | 11 | 2017 | 2016-12-23 | C | 1 | 0.000494 | 2.999e-06
1 | 15294909 | 2017-01-26 09:20 | 2017-01-26 10:40 | 79 | 38 | 3027.9667 | 0.0090765 | 0.008734 | 0.00011391 | NAPA ID:26969 TP_GREYTOWN GXP > TUHITARATA SUB > OTARAIA | 11 | Planned | 026969 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 810726 | NONE | Disconnect jumpers at pole 810726 to create linebreak Open dropout fuses 7178 & 7179 & ABS S388 at Temp REG T3810 Commence construction of new regulator site 11093 Note: when this outage is completed work on Regulator site will stop the AP will be handed back, another AP will be issued under NAPA 24988 with isolations at S388, 7179, 7178 and line break at pole 810276 . Outage to Close TLB will be under diff OMS | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.004367 | 5.5 | 2017 | 2017-01-26 | B | 38 | 0.008734 | 0.00011391
1 | 15294944 | 2016-12-23 13:10 | 2016-12-23 16:00 | 170 | 1 | 170.2833 | 0.00051069 | 0.000501 | 2.999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5/66 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuses at transformer T5/66 due to lightning. 2 X 3 amp HV fuses replaced | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000501 | 11 | 2017 | 2016-12-23 | C | 1 | 0.000501 | 2.999e-06
1 | 15294951 | 2016-12-23 13:10 | 2016-12-23 14:59 | 108 | 223 | 18950.7833 | 0.056835 | 0.054828 | 0.00066879 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | R12/2 | UNKNOWN | Recloser R12 tripped open on E/F flags, line was patrolled and sectionalised and no fault was found, farmer did inform faultman that at time of tripping that there had been lightning in the area. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.054828 | 11 | 2017 | 2016-12-23 | C | 223 | 0.054828 | 0.00066879
1 | 15295917 | 2016-12-23 14:29 | 2016-12-23 18:05 | 216 | 250 | 1730.6667 | 0.0051904 | 0.002941 | 2.3993e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C721 | CROSSARM - WHOLE ASSEMBLY | 1 x burnt cross arm at pole C721. Replaced 1 x HV Crossarm and associated gear. 4 x 10A HV Fuses replaced. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.002941 | 11 | 2017 | 2016-12-23 | C | 250 | 0.002941 | 2.3993e-05
1 | 15298909 | 2016-12-23 16:12 | 2016-12-23 17:42 | 90 | 2 | 180.3667 | 0.00054093 | 0.000522 | 5.9981e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3596 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Broken DDO replaced at pole S12707. Isolated at Fuses FC4047. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000522 | 11 | 2017 | 2016-12-23 | C | 2 | 0.000522 | 5.9981e-06
1 | 15298936 | 2016-12-23 17:16 | 2016-12-23 19:35 | 138 | 1 | 138.7167 | 0.00041602 | 0.000407 | 2.999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T4/49 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Fuses | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000407 | 11 | 2017 | 2016-12-23 | C | 1 | 0.000407 | 2.999e-06
1 | 15299004 | 2016-12-23 17:09 | 2016-12-23 18:34 | 84 | 95 | 8052.8333 | 0.024151 | 0.023296 | 0.00028491 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 7368 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at Fuses 7368 due to lightning. 2 X 10 amp HV fuse replaced | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.023296 | 11 | 2017 | 2016-12-23 | C | 95 | 0.023296 | 0.00028491
1 | 15299598 | 2016-12-23 20:43 | 2016-12-23 21:58 | 74 | 62 | 4636.5667 | 0.013905 | 0.013347 | 0.00018594 |  | 6.6 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 707707 | POLE | Car hit pole knocking out HV fuses at FABS 5526. Fuse links closed again. Nil materials used. Pole is safe but will most likely need to be replaced. NDR #N100279 - Outage reflected under OMS 15299645. | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.013347 | 6.6 | 2017 | 2016-12-23 | C | 62 | 0.013347 | 0.00018594
1 | 15299783 | 2016-12-23 22:10 | 2016-12-24 04:31 | 381 | 228 | 31731.8333 | 0.095166 | 0.093114 | 0.00083074 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12935 | CROSSARM - WHOLE ASSEMBLY | LV at Transformer TC2463 is still off as believe HV Lines have clashed with the LV - Downer to organise inspector to investigate. at 22:09, Putaruru Sub, CB 6 Horahora Feeder, Recloser 9636, Tripped, No Flags, L/O. Faultmen dispatched & investigation began. Feeder patrolled & sectionalised. Found 2x broken crossarms at Pole M12935. Isolated Lines at ABS 1271 & 1187. Permit issued & repairs carried out. All Power Restored on Completion. Replaced 2x Crossarms, 3x HV Fuses & Fuse Carriers. Cause: Aged equipment. Mike Jeffrey Attended. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.093114 | 11 | 2017 | 2016-12-23 | C | 228 | 0.093114 | 0.00083074
1 | 15301019 | 2016-12-24 05:54 | 2016-12-24 07:32 | 98 | 17 | 1667.1333 | 0.0049998 | 0.004846 | 5.0983e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 743971 | INSULATOR | Faultman found blown fuses at Fuses 8267 due to suspected bird strike after a liune patrol faultman also found a broken insulator on pole 743971. 1 X 11KV insulator replaced. 2 X 6 amp HV fuses replaced. | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.004846 | 11 | 2017 | 2016-12-24 | C | 17 | 0.004846 | 5.0983e-05
1 | 15303284 | 2016-12-24 10:15 | 2016-12-24 10:50 | 35 | 3 | 105 | 0.0003149 | 0.000287 | 8.997e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC437 | JUMPER | Problem was at transformer TC437. Transformer isolated at HV fuses to repair burnt LV jumper on transformer structure due to proximity issues. 1 metre 25Cu conductor and 2 x 25mm sleeves materials required. All supply restored. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000287 | 11 | 2017 | 2016-12-24 | C | 3 | 0.000287 | 8.997e-06
1 | 15303590 | 2016-12-24 10:12 | 2016-12-24 12:10 | 118 | 95 | 9754.4167 | 0.029254 | 0.028398 | 0.00028491 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | FUSE - ELEMENT/LINK (HV) | 2 x blown 10 amp fuses at 7368 replaced. 2 x blown 10 amp fuses at 7607 replaced with 8 amp fuses. Both sets loaded with same size probable cause of blowing both sets. All fuses at 7607 opened and removed at 11:10, 7368 reloaded and livened. Line patrolled past 7607 with no apparent cause found (possible tree contact?) Fuses 7607 reloaded & livened at 12:10. All supply restored. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.028398 | 11 | 2017 | 2016-12-24 | C | 95 | 0.028398 | 0.00028491
1 | 15306821 | 2016-12-24 20:25 | 2016-12-24 21:40 | 75 | 6 | 450 | 0.0013496 | 0.001295 | 1.7994e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 875 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8A HV Fuse Links | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.001295 | 22 | 2017 | 2016-12-24 | C | 6 | 0.001295 | 1.7994e-05
1 | 15306846 | 2016-12-24 21:33 | 2016-12-24 22:55 | 81 | 105 | 8561 | 0.025675 | 0.024729 | 0.0003149 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SA2-053 | FUSE - ELEMENT/LINK (HV) | 2 x 30A HV Fuses at SA2-053 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.024729 | 11 | 2017 | 2016-12-24 | C | 105 | 0.024729 | 0.0003149
1 | 15306898 | 2016-12-24 22:37 | 2016-12-25 00:33 | 116 | 6 | 116.85 | 0.00035043 | 0.000296 | 2.999e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | TC3-199 - no paperwork | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses at TC3-199 Opossum at base of pole. *JO to check | F4 | PLUMMERS POINT | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000296 | 11 | 2017 | 2016-12-24 | C | 6 | 0.000296 | 2.999e-06
1 | 15308232 | 2016-12-25 06:29 | 2016-12-25 08:05 | 96 | 34 | 2990.8667 | 0.0089695 | 0.008663 | 0.00010196 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7383 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8 a HV fuses @ 7379 & 2x 10a @ 7383 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.008663 | 11 | 2017 | 2016-12-25 | C | 34 | 0.008663 | 0.00010196
1 | 15312139 | 2016-12-26 08:00 | 2016-12-26 11:20 | 200 | 42 | 7112.6667 | 0.02133 | 0.020952 | 0.00012595 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | I23 | UNKNOWN | Likne sectionalised and patrolled with no apparent cause found supply restored | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.020952 | 11 | 2017 | 2016-12-26 | C | 42 | 0.020952 | 0.00012595
1 | 15313396 | 2016-12-26 21:18 | 2016-12-27 01:01 | 223 | 174 | 17996.5333 | 0.05397 | 0.052404 | 0.00052181 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 811274 | CONDUCTOR - REPAIR/REHANG | Recloser C604 on Martinbourgh CB C894 feeder tripped to L/O. B & C Ph O/C flags. Lines down & scrub fire reported by fire service on White Rock Rd past intersection on Ruakokopatuna Rd. Lines down located between poles 811274 & 845025. Isolation at ABS S543. Conductors had clashed caused by bird strike. All supply restored following completion of repairs. 140 metres on 16mm Cu conductor & 8 sleeves materials required. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.052404 | 11 | 2017 | 2016-12-26 | C | 174 | 0.052404 | 0.00052181
1 | 15314517 | 2016-12-27 10:10 | 2016-12-27 11:50 | 100 | 3 | 300 | 0.00089966 | 0.000872 | 8.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837234 | CONDUCTOR - REPAIR/REHANG | called and emailed hub re 999. LV Lines down at pole 837234. Isolated transformer T508 for safety while working on the LV conductors. 15m 10mm PC conducter, 6 sleeves | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000872 | 11 | 2017 | 2016-12-27 | C | 3 | 0.000872 | 8.9966e-06
1 | 15314572 | 2016-12-27 10:14 | 2016-12-27 13:45 | 210 | 202 | 8450.7 | 0.025343 | 0.023525 | 0.00038686 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 231050 | CONDUCTOR - REPAIR/REHANG | SEC 9875 Trip A,B,C O/C. E/F Line bought down by logging crew working on CAC31835. Jason Notified NOC of the tree going through the lines. Faultman dispatched to site. Isolated at Fuses SG7-001, sectionaliser 9875 Closed. Lines repaired 15meters Aluminium conducter, 4 sleeves. NDR to follow | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.023525 | 11 | 2017 | 2016-12-27 | C | 202 | 0.023525 | 0.00038686
1 | 15316226 | 2016-12-27 11:42 | 2016-12-27 13:30 | 108 | 1 | 108.15 | 0.00032433 | 0.000315 | 2.9988e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 375777 | FUSE - ELEMENT/LINK (HV) | 2x3 amp HV Fuses blown at Transformer T2970. Reloaded & Livened | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000315 | 11 | 2017 | 2016-12-27 | C | 1 | 0.000315 | 2.9988e-06
1 | 15316299 | 2016-12-27 12:24 | 2016-12-27 14:50 | 146 | 42 | 4793.45 | 0.014375 | 0.013997 | 0.00012895 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R19 | FUSE - ELEMENT/LINK (HV) | Fuse R19 - 5X 8 Amp Fuses. Tried Reload & Liven No Good. Found conductors Twisted at Pole P44794. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.013997 | 11 | 2017 | 2016-12-27 | C | 42 | 0.013997 | 0.00012895
1 | 15316319 | 2016-12-27 12:31 | 2016-12-27 17:11 | 280 | 93 | 15703.5833 | 0.047093 | 0.046256 | 0.0002789 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | N53 | CONDUCTOR - REPAIR/REHANG | 3 or 4 Poles will need replacing, lots of crossarms and maybe ABS N53. Les Robinson to arrange this under NDR number. 2 Temp Line Breaks in place (1 at Pole P17623 and the other at Pole P11577). NDR Number to follow. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.046256 | 11 | 2017 | 2016-12-27 | C | 93 | 0.046256 | 0.0002789
1 | 15317916 | 2016-12-27 14:14 | 2016-12-27 15:55 | 101 | 3 | 303.25 | 0.00090941 | 0.000882 | 8.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826477 | FUSE - ELEMENT/LINK (HV) | 2x3amp HV fuses blown at Transformer T812, Reloaded & relivened. possible line clash due to wind | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.000882 | 11 | 2017 | 2016-12-27 | C | 3 | 0.000882 | 8.9966e-06
1 | 15317986 | 2016-12-27 14:44 | 2016-12-27 20:44 | 360 | 1 | 360.4 | 0.0010808 | 0.001071 | 2.9988e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8164 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses 8164. All supply restored. Outage time has been reduced from 2045 to 2044 to reflect the outage was restored by the faultman in 360.6 minutes (not 361). The faultman was on site and was called away to attend a Feeder Fault (OMS 15319343). He retuned to this job and power was restore within 360.6 minutes from initial Crew Request. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.001071 | 11 | 2017 | 2016-12-27 | C | 1 | 0.001071 | 2.9988e-06
1 | 15318014 | 2016-12-27 14:52 | 2016-12-27 20:25 | 333 | 439 | 39958.1333 | 0.11983 | 0.11588 | 0.0013165 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208963 | JUMPER | Jumper off at pole 208963. isolation at 9695/6, 9695/1 9764/1 & 9764/6 Jumper repaired. All supply restored. 1 x 16mm connector only material required. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.11588 | 11 | 2017 | 2016-12-27 | C | 439 | 0.11588 | 0.0013165
1 | 15318036 | 2016-12-28 10:10 | 2016-12-28 12:57 | 167 | 5 | 835 | 0.002504 | 0.002459 | 1.4994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | V1108 | CONDUCTOR - REPAIR/REHANG | at 10:10, Coromandel Sub, CB 7 Kapanga Rd Feeder. Lines isolated at Fuses FC2471 for Asplundh to cut trees near lines. All Power Restored on Completion at 12:57. Dean Brett Attended for Switching/Recipient of Permit. No Materials Used. Asplundh arranged to cut trees on 28/12/16. | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.002459 | 11 | 2017 | 2016-12-28 | C | 5 | 0.002459 | 1.4994e-05
1 | 15318057 | 2016-12-27 15:05 | 2016-12-27 16:14 | 69 | 10 | 690 | 0.0020692 | 0.001979 | 2.9989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | 2 X 6 Amp at Fuse I26 Due to wind | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001979 | 11 | 2017 | 2016-12-27 | C | 10 | 0.001979 | 2.9989e-05
1 | 15319343 | 2016-12-27 16:27 | 2016-12-27 18:46 | 139 | 81 | 8209.2 | 0.024618 | 0.023889 | 0.00024291 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 845840 | CONDUCTOR - REPAIR/REHANG | CB C935 tripped to L/O. A & B Ph O/C flags. Tree branch located over line at pole 845840. Line isolated at ABS S161, backfeed established via ABS S176. Line left de energised between CB C935 & ABS S161 while branch removed from line with hotstick. All supply restored. Backfeed restored. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.023889 | 11 | 2017 | 2016-12-27 | C | 81 | 0.023889 | 0.00024291
1 | 15319744 | 2016-12-27 17:10 | 2016-12-27 19:07 | 116 | 223 | 3406.2333 | 0.010215 | 0.008208 | 0.00066875 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R29 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a hv fuses | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.008208 | 11 | 2017 | 2016-12-27 | C | 223 | 0.008208 | 0.00066875
1 | 15319751 | 2016-12-27 17:11 | 2016-12-27 20:26 | 195 | 1 | 195.1167 | 0.00058513 | 0.000576 | 2.9988e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | U32 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 15a HV fuses | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000576 | 11 | 2017 | 2016-12-27 | C | 1 | 0.000576 | 2.9988e-06
1 | 15319838 | 2016-12-27 17:37 | 2016-12-27 19:53 | 136 | 20 | 2722 | 0.0081629 | 0.007983 | 5.9977e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | 363162 | CONDUCTOR - REPAIR/REHANG | Line down due to coming out of sleeve. Reconducting work recently carried out past ABS S115. Isolated at ABS S115. ABS S115 had private lock on it from replacement a couple of weeks ago Gavin had to cut it off with his hacksaw, this took time to isolate. Quite windy Gavin requires EWP & assistance. Told to contact HUB & it will be sorted out at invoicing Line repaired. All supply restored. NDR to be submitted due to suspect workmanship. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.007983 | 11 | 2017 | 2016-12-27 | C | 20 | 0.007983 | 5.9977e-05
1 | 15320146 | 2016-12-27 17:53 | 2016-12-27 20:30 | 157 | 120 | 16644.6 | 0.049915 | 0.048835 | 0.00035987 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | V27 | UNKNOWN | Line sectionalised and patrolled. Supply restored with no apparent cause found. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.048835 | 11 | 2017 | 2016-12-27 | C | 120 | 0.048835 | 0.00035987
1 | 15321506 | 2016-12-27 18:32 | 2016-12-27 19:13 | 41 | 157 | 6520.7333 | 0.019555 | 0.018142 | 0.00047082 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P27770 | CONDUCTOR - REPAIR/REHANG | Removed branch from line @ pole P27770 using hot stick line de-energised for safety from ABS V54 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.018142 | 11 | 2017 | 2016-12-27 | C | 157 | 0.018142 | 0.00047082
1 | 15321996 | 2016-12-27 20:26 | 2016-12-27 21:43 | 76 | 1 | 76.9333 | 0.00023071 | 0.000221 | 2.9988e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 - No Paperwork | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a fuses & carrier | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000221 | 11 | 2017 | 2016-12-27 | C | 1 | 0.000221 | 2.9988e-06
1 | 15322405 | 2016-12-27 23:25 | 2016-12-28 03:54 | 269 | 167 | 44860.15 | 0.13453 | 0.13303 | 0.0010886 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 708126 | NONE | during patrol found opossum on pole 708126 and removed using hot stick | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.13303 | 11 | 2017 | 2016-12-27 | C | 167 | 0.13303 | 0.0010886
1 | 15322865 | 2016-12-28 05:42 | 2016-12-28 07:11 | 89 | 23 | 620.9333 | 0.0018621 | 0.001655 | 6.8973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 840585 | CONDUCTOR - REPAIR/REHANG | Conductor down due to bird strike at pole 840585. Used 2 X 6 Amp Fuses, 600mm Conductor and 3 x Sleeves. | F4 | WAITARA EAST TOWN | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001655 | 11 | 2017 | 2016-12-28 | C | 23 | 0.001655 | 6.8973e-05
1 | 15323008 | 2016-12-28 07:21 | 2016-12-28 09:04 | 103 | 197 | 17283.5167 | 0.05183 | 0.050058 | 0.00059077 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 824330 | NONE | at 07:23, Clareville Sub, CB C839 Park Rd Feeder, Recloser C422, Tripped, Ph B Fault, E/F, L/O. Faultmen dispatched & investigation began. Feeder patrolled & sectionalised. No Fault was Found. All Relivened OK. Ben Taylor Attended. Unknown Cause - weather conditions were good at the time. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.050058 | 11 | 2017 | 2016-12-28 | C | 197 | 0.050058 | 0.00059077
1 | 15324736 | 2016-12-28 12:21 | 2016-12-28 13:34 | 72 | 2 | 64.0667 | 0.00019213 | 0.000174 | 2.9988e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 366211 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Reloaded, Relivened 2x 10A HV Fuses at Fuses 8162. Also replaced 1x HV Fuse Carrier. Cause was birds - a lot of ducks/geese right in this area. Faultman didn't find evidence but was very certain this was the cause. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000174 | 11 | 2017 | 2016-12-28 | C | 2 | 0.000174 | 2.9988e-06
1 | 15324807 | 2016-12-28 11:40 | 2016-12-28 12:36 | 56 | 2 | 112 | 0.00033587 | 0.000317 | 5.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208490 | JUMPER | Note: OMS was not rolling up correctly for this job. Actual work was carried out under OMS 15323789 at 11:40, Katikati Sub, CB 4 Wharawhara Feeder. Faultman dispatched to part power/no power calls. Found broken jumper at Pole 208490. Isolated Lines at an ABS that is not on SCADA or GIS. ABS at Pole 208488. Permit issued & repairs carried out. All Power Restored on Completion. No Materials Used - Jumper just repaired only. Pieter Diedericks Attended. | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.000317 | 11 | 2017 | 2016-12-28 | C | 2 | 0.000317 | 5.9976e-06
1 | 15325156 | 2016-12-28 18:30 | 2016-12-28 19:50 | 79 | 41 | 3276.5833 | 0.0098259 | 0.009457 | 0.00012295 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217327 | JUMPER | Broken Jumper at Pole 217327. Isolation at fuses SE2-001 jumper repaired. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.009457 | 11 | 2017 | 2016-12-28 | C | 41 | 0.009457 | 0.00012295
1 | 15325172 | 2016-12-28 17:43 | 2016-12-28 17:49 | 5 | 17 | 98.3167 | 0.00029484 | 0.000141 | 5.098e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 220245 | CONDUCTOR - REPAIR/REHANG | at 17:44, Papamoa Sub, CB 8 Reid Rd Feeder. Faultman called to Kaiwha rd of bamboo in lines that was smoking. Isolated lines at Fuses SD4-130 and removed bamboo with hot stick. All Power Restored at 17:49. No Materials Used. Between Poles 220245 & 220246. Advised SMC of 999 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000141 | 11 | 2017 | 2016-12-28 | C | 17 | 0.000141 | 5.098e-05
1 | 15325542 | 2016-12-29 06:35 | 2016-12-29 08:20 | 105 | 4 | 420 | 0.0012595 | 0.001223 | 1.1995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 390 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2Amp HV Fuses at Transformer 390 which is not on the Makirikiri feeder, and is not fed from Roberts Ave Sub outage shown on child | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.001223 | 11 | 2017 | 2016-12-29 | C | 4 | 0.001223 | 1.1995e-05
1 | 15325682 | 2016-12-29 08:39 | 2016-12-29 10:45 | 125 | 20 | 2511 | 0.0075299 | 0.00735 | 5.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 207009 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Reloaded, Relivened 2x 20A HV Fuses & Holders at Fuses SA2-019. Cause - tree branch found below lines. looks as if it blew off a tree and hit 2 phases of the line. poss - LV to HV extent emailed SMC | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.00735 | 11 | 2017 | 2016-12-29 | C | 20 | 0.00735 | 5.9976e-05
1 | 15326756 | 2016-12-29 13:24 | 2016-12-29 15:04 | 99 | 2 | 199.1 | 0.00059706 | 0.000579 | 5.9975e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2923 | FUSE - ELEMENT/LINK (HV) | Arama Campbell Attended. Reloaded, Relivened 3x 10A HV Fuses at Transformer TP2923. Faultman believes it is caused by birdstrike as there are a lot of ducks around and this is transformer is next to sewage ponds. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000579 | 11 | 2017 | 2016-12-29 | C | 2 | 0.000579 | 5.9975e-06
1 | 15327357 | 2016-12-29 16:04 | 2016-12-29 17:16 | 71 | 22 | 1572.2667 | 0.0047149 | 0.004516 | 6.5973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | OUTAGE ON CHILD 1 X 10AMP UNKNOWN CAUSE | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.004516 | 11 | 2017 | 2016-12-29 | C | 22 | 0.004516 | 6.5973e-05
1 | 15328575 | 2016-12-29 20:27 | 2016-12-29 22:50 | 142 | 688 | 46735.1333 | 0.14015 | 0.13396 | 0.0041263 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P23610 | CONDUCTOR - REPAIR/REHANG | Wire Down at Pole P23610 1 X Sleeve 1 X Connector | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.13396 | 11 | 2017 | 2016-12-29 | C | 688 | 0.13396 | 0.0041263
1 | 15330484 | 2016-12-29 21:51 | 2016-12-30 01:43 | 232 | 186 | 20545.2 | 0.061611 | 0.059937 | 0.00055777 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 80522 | CONDUCTOR - REPAIR/REHANG | Pukepapa 11kV CB 1133 tripped on B ph, O/C and E/F. Conductor down at pole 805202. 10 M Conductor 2 X Sleeves | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.059937 | 22 | 2017 | 2016-12-29 | C | 186 | 0.059937 | 0.00055777
1 | 15332344 | 2016-12-30 07:30 | 2016-12-30 10:13 | 162 | 79 | 4569.1333 | 0.013702 | 0.01299 | 0.0002369 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P05261 | JOINT - CONDUCTOR JOINT | HV Line down at Pole P05261 still live. NOC Operator opened RS 10300 & work area isolated. Backfeed installed via ABS M72. Fault caused by deteriorated O/H connection at tap off supplying transformer T3/35 which also broke one HV fuse holder supplying that transformer. Materials used: 5mtrs of squirrel conductor, 2mtrs of 25mm cu conductor, 1x squirrel conductor joint, 1x 2Amp HV Fuse, & 1x HV Fuse holder | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.01299 | 11 | 2017 | 2016-12-30 | C | 79 | 0.01299 | 0.0002369
1 | 15332351 | 2016-12-30 06:26 | 2016-12-30 07:50 | 84 | 4 | 338.2 | 0.0010142 | 0.000978 | 1.1995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7980 | FUSE - ELEMENT/LINK (HV) | 2 x 40A HV Fuses and 1 x Fuse Carrier. Caused by Bird Strike. Found at base off pole | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000978 | 11 | 2017 | 2016-12-30 | C | 4 | 0.000978 | 1.1995e-05
1 | 15333378 | 2016-12-30 15:38 | 2016-12-30 17:20 | 102 | 1 | 102.45 | 0.00030722 | 0.000298 | 2.9987e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | T1/525 | NONE | Note: Transformer feeding property is T1/525, not T1/94 as per OMS. Low Voltage at property. Transformer had been recently installed. Tap Changer raised two taps to correct Voltage. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000298 | 11 | 2017 | 2016-12-30 | C | 1 | 0.000298 | 2.9987e-06
1 | 15333403 | 2016-12-30 15:14 | 2016-12-30 15:20 | 5 | 2 | 11.5 | 3.4485e-05 | 1.6e-05 | 5.9974e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4801W | NONE | Voltage complaints at property. Transformer briefly shut down to change Tap Setting to Tap 2. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 1.6e-05 | 11 | 2017 | 2016-12-30 | C | 2 | 1.6e-05 | 5.9974e-06
1 | 15333740 | 2016-12-30 17:05 | 2016-12-30 20:09 | 184 | 7 | 1288 | 0.0038624 | 0.003799 | 2.0991e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4808T | FUSE - ELEMENT/LINK (HV) | 1 X 30kvA Transformer 2X 3 Amp HT Fuses Off at 17:05 On at 20:09 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003799 | 11 | 2017 | 2016-12-30 | C | 7 | 0.003799 | 2.0991e-05
1 | 15333937 | 2016-12-30 21:14 | 2016-12-30 22:11 | 57 | 970 | 43232.8833 | 0.12964 | 0.12092 | 0.0029088 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 370934 | NONE | at 21:14, Greytown GXP, Bidswell Switching Station, 33kV Recloser 3139 Tripped, E/F, Ph B O/C, L/O. 33kV Recloser 3141 Tripped, E/F, Ph B O/C, L/O. Loss of Supply to Tuhitarata Sub. Faultmen dispatched & investigation began. Substation backfed via MAB CB C894 & FEA C916. All Power Restored by 22:11. 33kV Line was patrolled at road crossings & areas close to public access (this line goes cross country for a large portion of it) Faultman checked Bidswell switching station and found at Pole 370934 2x Dead Magpies at bottom of pole. 33kV Line Relivened. Substation restored back into service. No Materials Used. | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.12092 | 33 | 2017 | 2016-12-30 | C | 970 | 0.12092 | 0.0029088
1 | 15337006 | 2016-12-30 22:47 | 2016-12-31 00:09 | 82 | 563 | 46541.3333 | 0.13957 | 0.1345 | 0.0016883 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T1 | UNKNOWN | at 22:46, Chapel St Sub, CB C856 Cornwall St Feeder, Tripped, E/F, Ph A O/C, L/O. Faultmen dispatched & investigation began. Proved Feeder cable OK: Opened ABS S82, Closed C856. Remainder of feeder patrolled - no fault found. Relivened - all OK at 00:09. Unknown Cause - nothing found during patrol. Warren Madembo Attended. | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.1345 | 11 | 2017 | 2016-12-30 | C | 563 | 0.1345 | 0.0016883
1 | 15339027 | 2016-12-31 05:01 | 2016-12-31 06:37 | 96 | 5 | 480.9167 | 0.0014421 | 0.001397 | 1.4993e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7-004 | FUSE - ELEMENT/LINK (HV) | 2 x 6A HV Fuses. Bird Strike. Pukeko | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001397 | 11 | 2017 | 2016-12-31 | C | 5 | 0.001397 | 1.4993e-05
1 | 15339314 | 2016-12-31 10:50 | 2016-12-31 16:51 | 361 | 11 | 2072.45 | 0.0062146 | 0.006115 | 3.2985e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764353 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 X10 AMP FUSES TRANSFORMER BLOWN AT TC 5262. Tx replaced. Times taken from child job. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.006115 | 11 | 2017 | 2016-12-31 | C | 11 | 0.006115 | 3.2985e-05
1 | 15339452 | 2016-12-31 12:37 | 2016-12-31 17:18 | 280 | 4 | 1122.9333 | 0.0033673 | 0.003331 | 1.1995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1666 | FUSE - ELEMENT/LINK (HV) | This customer is allocated to the wrong transformer. Should be TC6249 2 x 10A Fuses blown at FP1666. and 2 x 6A Fuses at TC6249 Pole P13193. Caused by Bird Strike | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.003331 | 11 | 2017 | 2016-12-31 | C | 4 | 0.003331 | 1.1995e-05
1 | 15339614 | 2016-12-31 14:58 | 2016-12-31 15:57 | 59 | 174 | 10297.9 | 0.03088 | 0.029314 | 0.00052177 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 808697 | JUMPER | Emergency Isolation to repair broken Jumper on top of Links 7330 (Pole 808697) | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.029314 | 11 | 2017 | 2016-12-31 | C | 174 | 0.029314 | 0.00052177
1 | 15339928 | 2016-12-31 16:32 | 2016-12-31 16:38 | 5 | 52 | 297.2667 | 0.00089141 | 0.000423 | 0.00015593 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C875 | UNKNOWN | Feeder tripped when restoring switching at Norfolk Sub. HLT was still on after LLP carried out just before switching. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.000423 | 11 | 2017 | 2016-12-31 | C | 52 | 0.000423 | 0.00015593
1 | 15340057 | 2016-12-31 18:30 | 2016-12-31 20:24 | 113 | 41 | 4660.3333 | 0.013975 | 0.013606 | 0.00012295 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44504 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Shutdown at Fuses H21 to replace HV fuse complete with 3Amp fuse link. Also replaced jumper using 1mtr of 25mm cu | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.013606 | 11 | 2017 | 2016-12-31 | C | 41 | 0.013606 | 0.00012295
1 | 15345126 | 2017-01-01 00:33 | 2017-01-01 06:28 | 355 | 418 | 34494.8167 | 0.10344 | 0.099677 | 0.00029087 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 228427 | POLE | at 00:32, Pongakawa Sub, CB 3 Rotuehu Feeder, Tripped, E/F O/C, Auto Reclosed. Sectionaliser 13103 Tripped, E/F O/C, L/O. Faultmen dispatched & investigation began. Fire comms called in Car V Pole on Pongakawa Bush Rd. Isolated Lines at Links 13103/4 & ABS 13103/1. Permit Issued & Repairs carried out. All Power Restored on Completion. Materials: 1x Pole 2x Crossarms, 6x Insulators, 6x Binders, 2x Links, less than 1 span not all phases of conductor replaced. NDR: TBA Pole 228427 Fire comms reported Car V Pole on Pongakawa Bush Rd | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.099677 | 11 | 2017 | 2017-01-01 | C | 418 | 0.099677 | 0.00029087
1 | 15347133 | 2017-01-01 07:28 | 2017-01-01 08:58 | 89 | 7 | 629.7667 | 0.0018884 | 0.001825 | 2.099e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O55 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses O55. 2 X 10 amp HV fuses replaced. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001825 | 11 | 2017 | 2017-01-01 | C | 7 | 0.001825 | 2.099e-05
1 | 15347317 | 2017-01-01 08:12 | 2017-01-01 08:45 | 33 | 4 | 132 | 0.00039582 | 0.000359 | 1.1995e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 973N | JUMPER | Faultman found a burnt jumper on transformer 973N & blown fuse & broken holder.Transformer was isolated to repair the 11KV jumper. 1 X 100 amp HRC LV fuse & holder replace. | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000359 | 11 | 2017 | 2017-01-01 | C | 4 | 0.000359 | 1.1995e-05
1 | 15347583 | 2017-01-01 12:27 | 2017-01-01 16:12 | 225 | 213 | 23587.8 | 0.070731 | 0.068815 | 0.00039582 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4705/2 | UNKNOWN | CB 7 auto reclosed due to fault past Sectionalizer 4705/2 that tripped on B & C phase O/C flags, line was sectionalised and patrolled and no fault was found. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.068815 | 11 | 2017 | 2017-01-01 | C | 213 | 0.068815 | 0.00039582
1 | 15348268 | 2017-01-01 16:45 | 2017-01-01 18:52 | 126 | 15 | 1897.5 | 0.0056899 | 0.005554 | 4.498e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 2829 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 15Amp HV Fuse Links | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.005554 | 11 | 2017 | 2017-01-01 | C | 15 | 0.005554 | 4.498e-05
1 | 15349212 | 2017-01-01 19:23 | 2017-01-01 23:24 | 241 | 299 | 39232.5167 | 0.11764 | 0.11495 | 0.00096556 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764353 | INSULATOR | RS 6224/2 A/R, L/O, E/F. Sectionalised & patrolled. Backfeed installed via Gas Sw 8801. Fault was due to a broken insulator at Pole 764353 which also caused some damage to the line.. Materials used: 2x HV Pins & Insulators, 4x 16mm sleeves, 1mtr of 16mm cu wire, 2x cu binders | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.11495 | 11 | 2017 | 2017-01-01 | C | 299 | 0.11495 | 0.00096556
1 | 15350211 | 2017-01-01 22:07 | 2017-01-02 05:11 | 423 | 289 | 52326.1833 | 0.15691 | 0.15431 | 0.00086661 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 799831 | POLE | CB C917 Trip. E/F. O/C. L/O. Car V Pole. Corner of #1 Rd and SH53. Fire Comms Event # F2219098 Pole Replaced. 1 x 11 Pole. 1 x 2mtr HV Crossarm. 1 x 2mtr LV Crossarm 11kV has touched the LV on Transformer T2353 and melted lines. House and LV will need inspection. Gavin Grey organising house to be supplied generator until repaired No generator connected due to too much danage on meterboard inspector would not allow 02/01/17 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.15431 | 11 | 2017 | 2017-01-01 | C | 289 | 0.15431 | 0.00086661
1 | 15350619 | 2017-01-01 22:22 | 2017-01-02 00:09 | 106 | 44 | 4676.4667 | 0.014023 | 0.013627 | 0.00013194 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7570 | FUSE - ELEMENT/LINK (HV) | 2 x 20A HV Fuses. High Winds. Linbe Clash | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.013627 | 11 | 2017 | 2017-01-01 | C | 44 | 0.013627 | 0.00013194
1 | 15351545 | 2017-01-02 01:48 | 2017-01-02 04:59 | 190 | 762 | 39755.0667 | 0.11921 | 0.11235 | 0.0018891 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 741735 | INSULATOR | CB 7 A/R, L/O, E/F C Phase. Sectionalised & patrolled with fault being due to 2x broken insulators at Pole 741735. Materials used: 2x HV pins & Insulators, 4x 16mm sleeves, 2mtrs of 16mm cu conductor, 2x cu binders | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.11235 | 11 | 2017 | 2017-01-02 | C | 762 | 0.11235 | 0.0018891
1 | 15353018 | 2017-01-02 02:35 | 2017-01-02 12:12 | 576 | 674 | 92814.0667 | 0.27831 | 0.27225 | 0.0020211 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | N12626 | POLE | 1 x A/R on CB 3 (O/C flag) was followed by call from emergency services of car v pole on Puke Rd. CB 3 opened by NOC. Damaged pole (N12626 carrying ABS 1237) isolated at sw/gear 9544/3, ABS 503, ABS 9761/1, Links 9761/4 & ABS 386 to to replace pole. Backfeed established from ABS IC1093 to 386 during repairs. All supply restored following repairs/pole replacement. Material required - 11m busck pole, new ABS earthing, 8 x eye bolts, 1 x disc strain. Existing crossarms & ABS recovered from damaged pole, all in good condition. pieter offsite just after 6:30am FRM: Sean. sean sent pieter home - so completed Pieter from site and Arama Campbell is still onsite replacing the pole - transferred through to Maurice Control to chat about job | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.27225 | 11 | 2017 | 2017-01-02 | C | 674 | 0.27225 | 0.0020211
1 | 15353710 | 2017-01-02 02:46 | 2017-01-02 06:23 | 216 | 3 | 650.6 | 0.0019509 | 0.001923 | 8.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/21 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2Amp HV Fuses | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001923 | 11 | 2017 | 2017-01-02 | C | 3 | 0.001923 | 8.9957e-06
1 | 15353880 | 2017-01-02 05:27 | 2017-01-02 06:36 | 68 | 288 | 16128.7167 | 0.048364 | 0.045772 | 0.0008636 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | RC01 | UNKNOWN | Recloser RC01 Trip. E/F. L/O. Feeder Sectionalised. No Fault found. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.045772 | 11 | 2017 | 2017-01-02 | C | 288 | 0.045772 | 0.0008636
1 | 15354216 | 2017-01-02 05:56 | 2017-01-02 10:35 | 278 | 295 | 27269.3333 | 0.08177 | 0.079116 | 0.0012804 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783267 | CONDUCTOR - REPAIR/REHANG | RS 1011 A/R, L/O, O/C B & C Phase. Materials Used: 25M Conductor, 4 x Tension Sleeves at Pole 783267. NDR To Follow | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.079116 | 11 | 2017 | 2017-01-02 | C | 295 | 0.079116 | 0.0012804
1 | 15357034 | 2017-01-02 10:57 | 2017-01-02 14:45 | 228 | 1 | 228 | 0.00068368 | 0.000674 | 2.9985e-06 |  | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2515T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 1 X 30kVA At 2515T | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000674 | 6.6 | 2017 | 2017-01-02 | C | 1 | 0.000674 | 2.9985e-06
1 | 15359030 | 2017-01-02 14:38 | 2017-01-02 16:01 | 82 | 4807 | 386800.95 | 1.1599 | 1.1166 | 0.014414 |  | 66 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KPUTHS001 | INSULATOR | Supply lost to Thames sub at 14:38 when CB 1072 at Kopu GXP tripped to L/O. INV time O/C flag. T3 & T4 Y & B Ph O/C relays also picked up at Kopu GXP. Several other system disturbance alarms over various sites from Kopu & Waikino GXP's also operated indicating very heavy fault. Any delay experienced in supply restoration was while faultman were dispatched to Thames sub and Kaimarama switching station. Initial inspection carried out on incoming side of CB QC72 and cable terminations between ABS QC165 & QC169 proving negative. CB 1072 was left out of service to be patrolled after restoration attempt from CB 1092 due to unknown location and severity of fault. Whitianga & Coromandel subs were transferred to CB 1132 via Tairua sub leaving CB 1092 load free to pressure test line/cable cable to Thames sub. This was successful with all supply restored to Thames sub at 16:00. Methodology in doing this was erring on side of caution and not risking loss of supply to Whitianga & Coromandel should the fault have been on the cable to CB QC72. Line patrol was then commenced on the 1072 line with a helicopter being requested to patrol section of line over rougher terrain. Blown insulator was located on pole KPUTHA001, 1 span out from Kopu sub and on a double circuit structure with the 1092 line. Sutdown was arranged with Transpower/Downer for both circuits for 02:30 on 3/01/17. This was completed successfully and 66kV network was restored to normal. No further outages were required to carry out these repairs as minimal loads allowed all supply to be maintained via 1132 line. | S3 | KOPU1072-PARAWAI 66KV | KOPU | Valley | TP_KOPU | Eastern Electricity | POWERCO | 1.1166 | 66 | 2017 | 2017-01-02 | C | 4807 | 1.1166 | 0.014414
1 | 15363893 | 2017-01-02 13:12 | 2017-01-02 14:52 | 100 | 1 | 100 | 0.00029986 | 0.00029 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P49997 | INSULATOR | Floating conductor at pole P49997. Fuse S43 opened and 3 clamp top insulators replaced. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.00029 | 11 | 2017 | 2017-01-02 | C | 1 | 0.00029 | 2.9985e-06
1 | 15364059 | 2017-01-02 13:49 | 2017-01-02 16:19 | 149 | 1 | 149.8167 | 0.00044924 | 0.00044 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 11001 | FUSE - ELEMENT/LINK (HV) | This aapeared after Closing off 15358880 | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.00044 | 11 | 2017 | 2017-01-02 | C | 1 | 0.00044 | 2.9985e-06
1 | 15364198 | 2017-01-02 15:31 | 2017-01-02 17:27 | 116 | 1 | 116.3833 | 0.00034899 | 0.000339 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 378467 | FUSE - ELEMENT/LINK (HV) | 2 X 10 AMP BIRD STRIKE | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000339 | 11 | 2017 | 2017-01-02 | C | 1 | 0.000339 | 2.9985e-06
1 | 15364617 | 2017-01-02 19:07 | 2017-01-02 19:23 | 15 | 27 | 422.55 | 0.0012671 | 0.001024 | 8.0962e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P33371 | CONDUCTOR - REPAIR/REHANG | Tree on lines caused fire. F2219517 - SMC advised of 999, ETA 6.50pm. Faultman found an old tree that had died,broke off at bottom and fell against the lines at pole P33371, line was isolated at ABS's L20 & L22 and the tree was pushed off with hot line sticks. NDR: N300267. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001024 | 11 | 2017 | 2017-01-02 | C | 27 | 0.001024 | 8.0962e-05
1 | 15364703 | 2017-01-02 19:00 | 2017-01-03 00:21 | 320 | 50 | 16023.3333 | 0.048048 | 0.047597 | 0.00014993 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 216696 | CONDUCTOR - REPAIR/REHANG | Tree removed from lines and power restored. Materials Used: 3 x 15 A HV Fuses. NDR 17995 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.047597 | 11 | 2017 | 2017-01-02 | C | 50 | 0.047597 | 0.00014993
1 | 15364847 | 2017-01-02 19:21 | 2017-01-02 21:21 | 120 | 1 | 120.3333 | 0.00036083 | 0.000351 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/225 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer T5/225. 3 X 3 amp HV fuses replaced | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000351 | 11 | 2017 | 2017-01-02 | C | 1 | 0.000351 | 2.9985e-06
1 | 15365162 | 2017-01-02 22:13 | 2017-01-03 14:00 | 947 | 500 | 56545.55 | 0.16956 | 0.16506 | 0.0016492 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M2199 | POLE | Car V Pole. 100mtrs past Railway Line on Main Rd. Police Event # P028007077. 11kV untangled and cut away from damaged pole. Damaged LV cut away and feeder relivened. One customer still off on Transformer TC1926. This will be fixed Tues morning. Pole to be replaced Tuesday. Pole replaced, Isolated at ABS 927. All HV work completed & relivened. LV isolated at transformer TC1926 400V Fuses to allow work to continue on the 400V wires. 1 concrete pole, 3 crossarms, 11kV pin insulators, 6x LV bobbins | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.16506 | 11 | 2017 | 2017-01-02 | C | 500 | 0.16506 | 0.0016492
1 | 15365682 | 2017-01-02 22:22 | 2017-01-03 11:16 | 773 | 4 | 3094.1333 | 0.0092781 | 0.009242 | 1.1994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P590359 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a HV fuses @ R56 suspect caused by tree branch | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.009242 | 11 | 2017 | 2017-01-02 | C | 4 | 0.009242 | 1.1994e-05
1 | 15365742 | 2017-01-02 23:24 | 2017-01-03 01:28 | 123 | 1 | 123.3 | 0.00036973 | 0.00036 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | SD5-064 | NONE | Handle has come loose from ABS. Handle has been strapped to pole to make it safe. DNO 170101 | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.00036 | 11 | 2017 | 2017-01-02 | C | 1 | 0.00036 | 2.9985e-06
1 | 15365942 | 2017-01-03 05:49 | 2017-01-03 08:41 | 171 | 5 | 166.8667 | 0.00050036 | 0.000455 | 1.4993e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K2125 | CROSSARM - WHOLE ASSEMBLY | Replaced crossarm at pole K2125. Transformer TC1825 isolated so that the work could be carried out safely. 1xdouble crossarm used | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000455 | 11 | 2017 | 2017-01-03 | C | 5 | 0.000455 | 1.4993e-05
1 | 15366301 | 2017-01-03 10:44 | 2017-01-03 13:22 | 158 | 2 | 317 | 0.00095054 | 0.000932 | 5.9971e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 097 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a hv fuses @ 097 | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000932 | 11 | 2017 | 2017-01-03 | C | 2 | 0.000932 | 5.9971e-06
1 | 15366313 | 2017-01-03 11:05 | 2017-01-03 12:46 | 101 | 301 | 9734.65 | 0.02919 | 0.026482 | 0.00090256 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P35332 | CONDUCTOR - REPAIR/REHANG | called and emailed hub re 999 advised fire comms 15-20 mins ETA Isolated section of line between ABS C24 and Switch 10182 to remove tree branches and checked crossarm on pole P35332 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.026482 | 11 | 2017 | 2017-01-03 | C | 301 | 0.026482 | 0.00090256
1 | 15367529 | 2017-01-03 13:12 | 2017-01-03 20:18 | 426 | 313 | 133421.4667 | 0.40007 | 0.39726 | 0.00093855 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T6/270 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | SMC advised of 999. Car vs GM transformer T6/270, feeder was isolated at Sw/Gear 228 & ABS A81 to replace the ground mounted transformer, all the 11kV & 400v cables had to be reterminated and the 400V board redone. NDR: N300268. | F3 | PASCAL ST 9 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0.39726 | 11 | 2017 | 2017-01-03 | C | 313 | 0.39726 | 0.00093855
1 | 15367651 | 2017-01-03 12:46 | 2017-01-03 14:15 | 88 | 1 | 88.6833 | 0.00026592 | 0.000256 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 15366313 | CONDUCTOR - REPAIR/REHANG | Closed with same notes as OMS 15366313 - not linked properly 'Isolated section of line between ABS C24 and Switch 10182 to remove tree branches and checked crossarm on pole P35332' | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.000256 | 11 | 2017 | 2017-01-03 | C | 1 | 0.000256 | 2.9985e-06
1 | 15369144 | 2017-01-03 16:40 | 2017-01-03 19:25 | 164 | 3 | 494.15 | 0.0014817 | 0.001454 | 8.9956e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found a damaged transformer C6707after attending a customer fault, transformer was isolated and replaced. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001454 | 11 | 2017 | 2017-01-03 | C | 3 | 0.001454 | 8.9956e-06
1 | 15370489 | 2017-01-04 10:14 | 2017-01-04 11:09 | 55 | 164 | 9102 | 0.027292 | 0.025817 | 0.00049176 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P 372791 | POLE | Recloser D 79 Tripped, Sectionliser 10249 opened and Recloser reclosed Flags A ph O/C E/F Car V Pole Reported on Rangatiki Line ABS D81 opened to isolate area, ABS's D89 & C12 checked open Tagged NDR 35251 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.025817 | 11 | 2017 | 2017-01-04 | C | 164 | 0.025817 | 0.00049176
1 | 15371210 | 2017-01-04 11:26 | 2017-01-04 14:28 | 181 | 50 | 9089.1667 | 0.027254 | 0.026804 | 0.00014993 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 216697 | CONDUCTOR - REPAIR/REHANG | Isolation for tree cutters to remove branch from over the lines, can not be done live. Tree branch already been tied to another branch to stop it falling on to the lines. This is following on from OMS 15364703 which is an NDR 17995. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.026804 | 11 | 2017 | 2017-01-04 | C | 50 | 0.026804 | 0.00014993
1 | 15372173 | 2017-01-04 13:04 | 2017-01-04 14:34 | 90 | 1 | 90 | 0.00026987 | 0.00026 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 799945 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer Offlined to alllow repairs to the LV lines to 2 customers after car accident on the 1/1/17 OMS15350211 work completed by Warren Madenbo | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.00026 | 11 | 2017 | 2017-01-04 | C | 1 | 0.00026 | 2.9985e-06
1 | 15372411 | 2017-01-04 16:50 | 2017-01-04 18:20 | 89 | 7 | 626.5 | 0.0018786 | 0.001815 | 2.0989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826570 | FUSE - ELEMENT/LINK (HV) | 2x amp HV fuses blown at Transformer T1661 possibly due to wind 2 LV Conducters tangled together. LV line patrolled fuses reloaded & livened. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.001815 | 11 | 2017 | 2017-01-04 | C | 7 | 0.001815 | 2.0989e-05
1 | 15372536 | 2017-01-04 17:26 | 2017-01-04 20:03 | 157 | 1 | 157.4167 | 0.00047202 | 0.000463 | 2.9985e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a hv fuses - cause unknown. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000463 | 11 | 2017 | 2017-01-04 | C | 1 | 0.000463 | 2.9985e-06
1 | 15372770 | 2017-01-04 16:40 | 2017-01-04 18:05 | 84 | 68 | 5758.4667 | 0.017267 | 0.016655 | 0.0002039 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 819988 | FUSE - ELEMENT/LINK (HV) | 2x 15 amp HV fuses blown at Fuses 7607 possibly due to wind blown debris. Line patrolled fuses reloaded & livened. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.016655 | 11 | 2017 | 2017-01-04 | C | 68 | 0.016655 | 0.0002039
1 | 15373484 | 2017-01-04 18:17 | 2017-01-04 22:22 | 244 | 4 | 978.6 | 0.0029343 | 0.002898 | 1.1994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 359924 | INSULATOR | Repaired floating conductor @ pole 359924 and replaced 2x 6a HV fuses @R56 Materials used 2x clamp top insulators | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002898 | 11 | 2017 | 2017-01-04 | C | 4 | 0.002898 | 1.1994e-05
1 | 15373996 | 2017-01-05 00:02 | 2017-01-05 12:38 | 756 | 29 | 15104 | 0.045289 | 0.045027 | 8.6955e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 811672 | CONDUCTOR - REPAIR/REHANG | at 00:02, Hau Nui Sub, CB C642 Tuturumuri Feeder, Sectionaliser C633 - found tripped by faultman. Investigation began. Found tree down on lines at Pole 811672. Isolated Lines at ABS S1203. Permit issued & repairs carried out. All Power Restored on Completion. Frank Martin Attended. 2x Sleeves & 1 phase less than 1 span of conductor used. NDR: TBA Sectionaliser C633/2 found tripped. Line sectionalised and patrolled. Tree located through line beyond ABS S1203. Repairs unable to be completed in darkness due to terrain etc. 2 r requested to complete after daylight. NDR: & pole number to be supplied. pulled up 2 x 11kv wires | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.045027 | 11 | 2017 | 2017-01-05 | C | 29 | 0.045027 | 8.6955e-05
1 | 15374101 | 2017-01-05 05:47 | 2017-01-05 08:37 | 169 | 250 | 31720.3 | 0.095112 | 0.092863 | 0.00074962 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | n/a | UNKNOWN | at 05:47, Farmer Rd Sub, CB 4 Township Feeder, Tripped, B + C Ph O/C, L/O. Faultmen dispatched & investigation began. Feeder Patrolled / Sectionalised. No Fault was Found. All Power Restored on Completion. Mike Cornelius Attended. CB 4 tripped to L/O. B & C Ph O/C flags | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.092863 | 11 | 2017 | 2017-01-05 | C | 250 | 0.092863 | 0.00074962
1 | 15377398 | 2017-01-05 05:59 | 2017-01-05 11:02 | 303 | 420 | 79738.2333 | 0.23909 | 0.23531 | 0.0015352 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | n/a | UNKNOWN | at 05:59, Tinui Sub, CB C937 Castlepoint Feeder, Tripped, B + C Phase O/C, L/O. Faultmen dispatched & investigation began. Line Patrolled & Sectionalised - No Fault Found. All Power Restored on Completion. CB C937 tripped to L/O. A & B Ph O/C flags. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.23531 | 11 | 2017 | 2017-01-05 | C | 420 | 0.23531 | 0.0015352
1 | 15379586 | 2017-01-05 11:19 | 2017-01-05 12:08 | 48 | 14 | 685.7667 | 0.0020562 | 0.00193 | 4.1978e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | T71 | NONE | Warren Madembo Attended. Found Branch on Line at Transformer T71 - Removed with hot stick. Reloaded, Relivened 2x 10A HV Fuses at 7074. All OK. 1129 - Hub advises that Warren ETA 15mins. Check 208 Bute Road, OMS 154379699 is related | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.00193 | 11 | 2017 | 2017-01-05 | C | 14 | 0.00193 | 4.1978e-05
1 | 15379717 | 2017-01-05 09:47 | 2017-01-05 13:05 | 198 | 95 | 17251.9167 | 0.051729 | 0.050874 | 0.00028485 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 448705 | FUSE - ELEMENT/LINK (HV) | Ben Taylor Attended. Unknown cause - Reloaded Relivened 2x 10A HV Fuses at 7368, and Reloaded, Relivened 2x 8A Fuses at 7607. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.050874 | 11 | 2017 | 2017-01-05 | C | 95 | 0.050874 | 0.00028485
1 | 15380114 | 2017-01-05 14:10 | 2017-01-05 15:13 | 62 | 1 | 62.9667 | 0.0001888 | 0.000179 | 2.9984e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826688 | FUSE - ELEMENT/LINK (HV) | Ben Taylor Attended. Reloaded, Relivened 2x 8A HV Fuses at 7160. Unknown Cause. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.000179 | 11 | 2017 | 2017-01-05 | C | 1 | 0.000179 | 2.9984e-06
1 | 15380327 | 2017-01-05 15:28 | 2017-01-05 17:08 | 99 | 17 | 1632 | 0.0048935 | 0.00474 | 5.0974e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P28771 | BINDER | Floating conductor found at pole P28771 as part of OMS 15379944 I4 dressed incorrectly ( wrong time) caused second OMS job ignore Work site Isolated at ABS I7 & ABS I6 and Links I5. Back feed installed via ABS 10169 Binders found to be all broken - replaced all HV insolators with clamp tops | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00474 | 11 | 2017 | 2017-01-05 | C | 17 | 0.00474 | 5.0974e-05
1 | 15380379 | 2017-01-05 15:53 | 2017-01-05 19:55 | 241 | 422 | 12299.1333 | 0.036879 | 0.033082 | 0.0013133 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13551 | CROSSARM - WHOLE ASSEMBLY | Feeder CB opened for safety after reports of a low hanging line. Broken crossarms at Pole O13551. isolation at ABS IC1139. 2x Termination crossarms, 6xpolymer strain insulators, 2xpin insulators | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.033082 | 11 | 2017 | 2017-01-05 | C | 422 | 0.033082 | 0.0013133
1 | 15381750 | 2017-01-05 17:29 | 2017-01-05 19:41 | 132 | 2 | 264.6667 | 0.00079359 | 0.000775 | 5.9969e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760386 - Need paperwork email sent to Paul | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV fuses and 2x 80a LV fuses *Jo to check | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000775 | 6.6 | 2017 | 2017-01-05 | C | 2 | 0.000775 | 5.9969e-06
1 | 15381930 | 2017-01-05 19:05 | 2017-01-05 19:35 | 29 | 44 | 1300.2 | 0.0038986 | 0.003502 | 0.00013193 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728203 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | section of line Isolated from fuses WH 140 in order to replace fuse holder @ WH 120 which broke on closing | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.003502 | 11 | 2017 | 2017-01-05 | C | 44 | 0.003502 | 0.00013193
1 | 15382229 | 2017-01-05 22:08 | 2017-01-06 00:45 | 157 | 6 | 942 | 0.0028246 | 0.00277 | 1.7991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 224927 | CONDUCTOR - REPAIR/REHANG | Isolation for tree cutting. Reported by Mark from Asplundh 027 4433255 Tree Head across the lines at Pole 224927.Isolated at SE6-135 & SE6-137. Tree cut & removed. NDR to follow | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.00277 | 11 | 2017 | 2017-01-05 | C | 6 | 0.00277 | 1.7991e-05
1 | 15382807 | 2017-01-06 07:24 | 2017-01-06 09:34 | 129 | 4 | 519.6 | 0.001558 | 0.001522 | 1.1994e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | R21 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuse Links | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001522 | 11 | 2017 | 2017-01-06 | C | 4 | 0.001522 | 1.1994e-05
1 | 15383743 | 2017-01-06 12:18 | 2017-01-06 16:52 | 273 | 1142 | 79050.6667 | 0.23703 | 0.22676 | 0.0034242 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798561 | CONDUCTOR - REPAIR/REHANG | at 13:13, Featherston Sub, CB C916 Revans St Feeder. Faultman contacted NOC and requested NOC Open CB C916 at Featherston Sub due to line down at Pole 798561 which was still sparking and had caused a fire. CB Opened, then isolated lines at Fuses 7261. Remainder of feeder then all relivened at 13:25. Permit issued & repairs carried out. All Power Restored on Completion. Warren Madembo Attended. 2x 10A HV Fuses, 3x Sleeves & 1 Span, 1 Phase of 16mm2 Cu Conductor replaced. Safety Manager: 693099 called and emailed hub re 999 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.22676 | 11 | 2017 | 2017-01-06 | C | 1142 | 0.22676 | 0.0034242
1 | 15384989 | 2017-01-06 13:14 | 2017-01-06 14:15 | 60 | 2 | 121.6667 | 0.00036481 | 0.000346 | 5.9968e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 823850 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | at 14:00, Gladstone Sub, CB C945 Longbush Feeder. Found branch on line at Pole 823850. Isolated line at Fuses 7086 & removed branch with hotstick. All Power Restored on Completion. Lee Wilton Attended. 1x 10A HV Fuse Replaced. | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000346 | 11 | 2017 | 2017-01-06 | C | 2 | 0.000346 | 5.9968e-06
1 | 15386065 | 2017-01-06 19:46 | 2017-01-06 21:40 | 114 | 241 | 11833.0167 | 0.03548 | 0.033312 | 0.00072262 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 730240 | CONDUCTOR - REPAIR/REHANG | Lines down reported while sectionlising, confirmed at Pole 730240 Isolated at ABS's 6000 & 5959 with backfeed via ABS 5960 3 lines down used 25 mtrs conductor and 9 sleeves | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.033312 | 11 | 2017 | 2017-01-06 | C | 241 | 0.033312 | 0.00072262
1 | 15386833 | 2017-01-06 21:50 | 2017-01-06 23:30 | 100 | 7 | 703.3833 | 0.002109 | 0.002046 | 2.0989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715022 | FUSE - ELEMENT/LINK (HV) | 2 Fuses found blown at Fuses TA 787 - cause unknown Used 2 x 10 amp fuses | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002046 | 11 | 2017 | 2017-01-06 | C | 7 | 0.002046 | 2.0989e-05
1 | 15389548 | 2017-01-07 06:58 | 2017-01-07 07:42 | 44 | 19 | 836 | 0.0025066 | 0.002335 | 5.6969e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L12452 | JUMPER | Blown Jumper found at ABS IC677, Pole L12452. Backfeeds put in place via ABS IC 2116 and ABS 681. Isolation between ABS IC635, IC1194, IC646 & IC612. Jumper Re-joined. See OMS 15389156 | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.002335 | 11 | 2017 | 2017-01-07 | C | 19 | 0.002335 | 5.6969e-05
1 | 15389578 | 2017-01-07 09:50 | 2017-01-07 11:25 | 94 | 1 | 94.8333 | 0.00028435 | 0.000275 | 2.9983e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 583 FITZHERBERT EAST ROAD | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | FM attending part power fault found 1x blown transformer fuse. Tried reload reliven which blew fuse again & caused Recloser 10050/2 to trip & auto reclose. Replaced transformer T2/710. Materials used: 1x 15kVA Transformer, 2x 2Amp HV Fuses, 2x Arm braces, & misc bolts & nuts | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.000275 | 11 | 2017 | 2017-01-07 | C | 1 | 0.000275 | 2.9983e-06
1 | 15425639 | 2017-01-07 11:54 | 2017-01-07 13:20 | 85 | 7 | 600.4833 | 0.0018005 | 0.001737 | 2.0989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2315 | FUSE - ELEMENT/LINK (HV) | 2 x 6A HV Fuses. Caused by twisted LV Wires between Poles 841249 & 822280 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001737 | 11 | 2017 | 2017-01-07 | C | 7 | 0.001737 | 2.0989e-05
1 | 15426690 | 2017-01-07 17:57 | 2017-01-07 19:20 | 82 | 9 | 745.2 | 0.0022344 | 0.002153 | 2.6985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 834806 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 10A HV Fuses at 7153. Line Patrolled - nothing found - unknown cause. Ben Taylor Attended. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002153 | 11 | 2017 | 2017-01-07 | C | 9 | 0.002153 | 2.6985e-05
1 | 15427182 | 2017-01-08 02:01 | 2017-01-08 03:11 | 69 | 954 | 57509.1 | 0.17243 | 0.16385 | 0.0028604 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | O2970 | STAY WIRE | at 02:00, Kerepehi Sub, CB 6 Ngatea Feeder, Tripped, A B C Ph O/C, E/F, L/O. Faultmen dispatched & investigation began. Partial backfeed from KPE 3: Opened RC04, Closed 9724. Faultman found a Car V Pole at Pole O2970. Stay wire was broken and was lying across lines. Removed with hot stick. All Power Restored on Completion. James Kennerley Attended. Still need to replace stay wire. NDR: 55011 - will replace stay wire under NDR. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.16385 | 11 | 2017 | 2017-01-08 | C | 954 | 0.16385 | 0.0028604
1 | 15429364 | 2017-01-08 09:50 | 2017-01-08 13:05 | 195 | 1 | 195 | 0.00058468 | 0.000575 | 2.9983e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1813N | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced faulty transformer 30kvA On time 1305 neighbours auto roller door not working. getting elect to look at it | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000575 | 11 | 2017 | 2017-01-08 | C | 1 | 0.000575 | 2.9983e-06
1 | 15430016 | 2017-01-08 17:29 | 2017-01-08 19:10 | 101 | 21 | 2121 | 0.0063595 | 0.00617 | 6.2965e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 218786 | POLE | at 17:29, Pongakawa Sub, CB 2 Otamrakau Feeder. Report came in of Car V Pole. Car had hit pole 218786. Isolated lines at ABS SE7-018, ABS SE7-019 & ABS SE7-035. Backfeed supplied from PKW 3: Closed ABS SE7-025. Permit issued & repairs carried out. All Power restored on Completion. Mike James Attended. 1x Pole, 1x Crossarm 3x Insulators, 3x binders, 2x blocks. NDR: TBA Fire Comms reported car v pole F2222252, outside Bill and Rosie Garage. Require eta SMC and Control advised ETA: 30mins - have advised fire comms Pole replaced. Isolation between ABS SE&-018, SE7-035 & SE7-019. Backfeed via SE7-025 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.00617 | 11 | 2017 | 2017-01-08 | C | 21 | 0.00617 | 6.2965e-05
1 | 15430731 | 2017-01-08 19:56 | 2017-01-08 20:53 | 56 | 1 | 56.65 | 0.00016986 | 0.00016 | 2.9983e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | M83 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuse Links | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00016 | 11 | 2017 | 2017-01-08 | C | 1 | 0.00016 | 2.9983e-06
1 | 15431388 | 2017-01-08 22:36 | 2017-01-09 01:03 | 147 | 297 | 37329.5667 | 0.11193 | 0.10926 | 0.00089051 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 363187 | JUMPER | at 21:47, Tinui Sub, CB C937 Castlepoint Feeder, Recloser C225 Tripped, B + C Ph O/C, Auto Reclosed. at 22:35, call came in of sparking line at the castlepoint campground. NOC Opened C225 at 22:35. Faultman dispatched & investigation began. Found blown jumper at Transformer T1821. Isolated lines at ABS S168. Permit issued & repairs carried out. All Power Restored on Completion. Lee Wilton Attended. 1x Connector used. Aged Equipment | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.10926 | 11 | 2017 | 2017-01-08 | C | 297 | 0.10926 | 0.00089051
1 | 15432262 | 2017-01-09 03:46 | 2017-01-09 05:15 | 88 | 135 | 8509.9667 | 0.025515 | 0.024301 | 0.00080954 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 724749 | NONE | RS 6560 A/R, L/O, E/F B Phase. Sectionalised & patrolled with an Opossum found on lines at Pole 724749. Removed using hot stick. No damage to Network | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.024301 | 11 | 2017 | 2017-01-09 | C | 135 | 0.024301 | 0.00080954
1 | 15432856 | 2017-01-09 05:29 | 2017-01-09 06:53 | 83 | 11 | 919.2333 | 0.0027561 | 0.002657 | 3.2981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 0770 | FUSE - ELEMENT/LINK (HV) | 2 x 8amp @ fc823 birds | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002657 | 11 | 2017 | 2017-01-09 | C | 11 | 0.002657 | 3.2981e-05
1 | 15433240 | 2017-01-19 10:15 | 2017-01-19 11:40 | 85 | 43 | 3655 | 0.010957 | 0.01057 | 0.00012891 | NAPA ID:26896 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 026896 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K0105 | NONE | AP: To replace 2 x 11kV Pin arms. Pole K0105 & K0106. LLP: to install a set if Temp Fuses (TEMP59) Between Pole K0106 & K0105. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.005285 | 5.5 | 2017 | 2017-01-19 | B | 43 | 0.01057 | 0.00012891
1 | 15433277 | 2017-01-26 08:45 | 2017-01-26 14:57 | 372 | 3 | 1116 | 0.0033453 | 0.003318 | 8.9926e-06 | NAPA ID:27881 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11 | Planned | 027881 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3347 | NONE | Up Grade TC3347 to 3/30kVA | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.001659 | 5.5 | 2017 | 2017-01-26 | B | 3 | 0.003318 | 8.9926e-06
1 | 15433416 | 2017-02-01 09:03 | 2017-02-01 15:15 | 372 | 39 | 14508 | 0.043485 | 0.043134 | 0.00011689 | NAPA ID:26784 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 026784 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 245 Waiti Rdm Tahuna, Morrinsville | NONE | Shutdown 1 replacing poles and x-arms on Waiti Rd, Tahuna | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.021567 | 5.5 | 2017 | 2017-02-01 | B | 39 | 0.043134 | 0.00011689
1 | 15433686 | 2017-01-25 09:00 | 2017-01-25 14:10 | 310 | 7 | 2170 | 0.0065048 | 0.006441 | 2.0983e-05 | NAPA ID:25708 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 025708 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rangiuru Road | NONE | REPLACE HV ARMS AND POLES . INSTALL TEMP LINKS 26 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0032205 | 5.5 | 2017 | 2017-01-25 | B | 7 | 0.006441 | 2.0983e-05
1 | 15433739 | 2017-02-03 09:30 | 2017-02-03 16:15 | 405 | 5 | 2025 | 0.0060694 | 0.006024 | 1.4986e-05 | NAPA ID:26789 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11.00000000 | Planned | 026789 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP 1858 | NONE | Changing poles and x-arms on Waiti Rd, beyond new fuses FP 1858 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.003012 | 5.5 | 2017 | 2017-02-03 | B | 5 | 0.006024 | 1.4986e-05
1 | 15433899 | 2017-01-24 10:20 | 2017-01-24 12:35 | 135 | 109 | 14715 | 0.04411 | 0.04313 | 0.00032674 | NAPA ID:27876 TP_HUIRANGI GXP > BELL BLOCK SUB > MANGATI RD | 11 | Planned | 027876 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1264 | NONE | Replace leaking tx 1264 | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.021565 | 5.5 | 2017 | 2017-01-24 | B | 109 | 0.04313 | 0.00032674
1 | 15434225 | 2017-02-08 11:48 | 2017-02-08 14:30 | 162 | 5 | 810 | 0.0024276 | 0.002382 | 1.4985e-05 | NAPA ID:27703 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027703 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 1067 | NONE | replacing tx 1067 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.001191 | 5.5 | 2017 | 2017-02-08 | B | 5 | 0.002382 | 1.4985e-05
1 | 15434276 | 2017-02-08 09:00 | 2017-02-08 11:45 | 165 | 3 | 495 | 0.0014835 | 0.001456 | 8.991e-06 | NAPA ID:27694 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11.00000000 | Planned | 027694 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 941 | NONE | Replacing tx 941 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000728 | 5.5 | 2017 | 2017-02-08 | B | 3 | 0.001456 | 8.991e-06
1 | 15434532 | 2017-01-09 10:30 | 2017-01-09 11:55 | 85 | 106 | 6860 | 0.020568 | 0.019614 | 0.00031782 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p41307 | LIGHTNING ARRESTOR (HV) | was created under 15434030. | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.019614 | 11 | 2017 | 2017-01-09 | C | 106 | 0.019614 | 0.00031782
1 | 15434695 | 2017-02-08 08:45 | 2017-02-08 11:30 | 165 | 2 | 330 | 0.00098901 | 0.000971 | 5.994e-06 | NAPA ID:27697 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11.00000000 | Planned | 027697 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 934 | NONE | replacing tx 934 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0004855 | 5.5 | 2017 | 2017-02-08 | B | 2 | 0.000971 | 5.994e-06
1 | 15434751 | 2017-02-08 12:25 | 2017-02-08 14:45 | 140 | 7 | 980 | 0.0029371 | 0.002874 | 2.0979e-05 | NAPA ID:27705 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11.00000000 | Planned | 027705 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 926 | NONE | replacing tx 926 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.001437 | 5.5 | 2017 | 2017-02-08 | B | 7 | 0.002874 | 2.0979e-05
1 | 15434785 | 2017-02-09 09:00 | 2017-02-09 11:30 | 150 | 4 | 600 | 0.0017982 | 0.001762 | 1.1988e-05 | NAPA ID:27708 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027708 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 929 | NONE | replacing tx 929 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000881 | 5.5 | 2017 | 2017-02-09 | B | 4 | 0.001762 | 1.1988e-05
1 | 15434802 | 2017-02-09 12:15 | 2017-02-09 14:30 | 135 | 2 | 270 | 0.00080918 | 0.000791 | 5.9939e-06 | NAPA ID:27711 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027711 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 1597 | NONE | replacing tx 1597 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0003955 | 5.5 | 2017 | 2017-02-09 | B | 2 | 0.000791 | 5.9939e-06
1 | 15434848 | 2017-02-09 12:39 | 2017-02-09 14:45 | 126 | 5 | 630 | 0.0018881 | 0.001843 | 1.4985e-05 | NAPA ID:27710 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027710 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 1183 | NONE | replacing tx 1183 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0009215 | 5.5 | 2017 | 2017-02-09 | B | 5 | 0.001843 | 1.4985e-05
1 | 15434890 | 2017-02-09 08:45 | 2017-02-09 11:30 | 165 | 2 | 330 | 0.000989 | 0.000971 | 5.9939e-06 | NAPA ID:27706 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027706 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer 998 | NONE | replacing tx 998 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0004855 | 5.5 | 2017 | 2017-02-09 | B | 2 | 0.000971 | 5.9939e-06
1 | 15434932 | 2017-01-09 11:37 | 2017-01-09 13:25 | 108 | 1 | 108.0333 | 0.00032392 | 0.000314 | 2.9982e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 808781 | FUSE - ELEMENT/LINK (HV) | 2X 8 unknown cause | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000314 | 11 | 2017 | 2017-01-09 | C | 1 | 0.000314 | 2.9982e-06
1 | 15434937 | 2017-02-10 12:30 | 2017-02-10 13:45 | 75 | 3 | 225 | 0.00067431 | 0.000647 | 8.9907e-06 | NAPA ID:27815 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027815 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 981 | NONE | replacing tx 981 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0003235 | 5.5 | 2017 | 2017-02-10 | B | 3 | 0.000647 | 8.9907e-06
1 | 15435157 | 2017-02-10 09:30 | 2017-02-10 11:30 | 120 | 3 | 360 | 0.0010789 | 0.001051 | 8.9907e-06 | NAPA ID:27813 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027813 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 1000 | NONE | replacing tx 1000 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0005255 | 5.5 | 2017 | 2017-02-10 | B | 3 | 0.001051 | 8.9907e-06
1 | 15435242 | 2017-02-10 09:20 | 2017-02-10 11:55 | 155 | 3 | 465 | 0.0013936 | 0.001366 | 8.9907e-06 | NAPA ID:27712 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027712 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 935 | NONE | replacing tx 935 as has an internal tap changer. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000683 | 5.5 | 2017 | 2017-02-10 | B | 3 | 0.001366 | 8.9907e-06
1 | 15435374 | 2017-01-09 12:37 | 2017-01-09 14:00 | 83 | 11 | 917.7667 | 0.0027517 | 0.002652 | 3.2981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220138 | FUSE - ELEMENT/LINK (HV) | Check 51 GARRETT RD, OMS 15435430 is related 30 Garrett Rd, OMS 15435993 se5-284 2 x 10amp wind 1445 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002652 | 11 | 2017 | 2017-01-09 | C | 11 | 0.002652 | 3.2981e-05
1 | 15435547 | 2017-02-09 09:19 | 2017-02-09 12:42 | 202 | 21 | 4262.3 | 0.012774 | 0.012585 | 6.2936e-05 | NAPA ID:27601 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 027601 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 727849 | NONE | Replace pole 727849 with new 11m busck pole , replace double cross arms pole 726533 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.0062925 | 5.5 | 2017 | 2017-02-09 | B | 21 | 0.012585 | 6.2936e-05
1 | 15435640 | 2017-02-14 09:30 | 2017-02-14 12:07 | 157 | 64 | 8166 | 0.024471 | 0.023896 | 0.00019179 | NAPA ID:27681 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027681 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12171/2 | NONE | Day 1: Commission new regulator 12171/2. Refer attached methodology. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.011948 | 5.5 | 2017 | 2017-02-14 | B | 64 | 0.023896 | 0.00019179
1 | 15435834 | 2017-01-09 13:48 | 2017-01-09 16:05 | 136 | 6 | 820.9 | 0.0024613 | 0.002407 | 1.799e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712772 | CONDUCTOR - REPAIR/REHANG | Check for safety - Lines down, hanging in bamboo. Across from this address, look like broken from joint. Advised control and SMC of 999 Brett called to advise he is leaving site now. They have a team out there - talked to control? Line down between poles 712772 & 712773 repaired. Isolation at ABS NG425 & TA101. No protection operation as conductor still in air suspended from bamboo tree. 500 metres 35mm Cu conductor & 2 x 35mm sleeves material required. Lines down suspected to hav been caused by conductor clash | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002407 | 11 | 2017 | 2017-01-09 | C | 6 | 0.002407 | 1.799e-05
1 | 15435859 | 2017-02-15 08:46 | 2017-02-15 13:38 | 292 | 74 | 16601 | 0.049748 | 0.049083 | 0.00022176 | NAPA ID:27683 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027683 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12171/2 | NONE | Day 2: Commission new regulator 12171/2. Refer attached methodology. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.024542 | 5.5 | 2017 | 2017-02-15 | B | 74 | 0.049083 | 0.00022176
1 | 15435971 | 2017-02-16 09:00 | 2017-02-16 11:30 | 150 | 33 | 4207 | 0.012607 | 0.01231 | 9.889e-05 | NAPA ID:27685 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 027685 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12171/2 | NONE | Day Three Commission new regulator 12171/2 Refer to methodology attached | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.006155 | 5.5 | 2017 | 2017-02-16 | B | 33 | 0.01231 | 9.889e-05
1 | 15436002 | 2017-02-08 08:19 | 2017-02-08 15:33 | 434 | 11 | 4774 | 0.014308 | 0.014208 | 3.2967e-05 | NAPA ID:26902 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 026902 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2688 | NONE | To replace poles, Install 2 new transformers, Install a set of 11kV fuses, Connect new 11kV Spur line, Replace arms & Hardware, Remove redundant LV Lines. Works location: Cameron Rd, Morrinsville. WO 30035792 | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.007104 | 5.5 | 2017 | 2017-02-08 | B | 11 | 0.014208 | 3.2967e-05
1 | 15436057 | 2017-01-10 10:30 | 2017-01-10 12:20 | 110 | 62 | 6820 | 0.020448 | 0.01989 | 0.00018589 | NAPA ID:27969 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | 027969 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 840017 | NONE | Replace broken 11kv pole. Works location: Pack Spur Rd. WO 30024973 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.009945 | 5.5 | 2017 | 2017-01-10 | B | 62 | 0.01989 | 0.00018589
1 | 15436099 | 2017-01-09 14:36 | 2017-01-09 17:50 | 194 | 25 | 4850 | 0.014542 | 0.014316 | 7.4957e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 851734 | CONDUCTOR - REPAIR/REHANG | Fuses 4957 found to be all blown when faultman arrived on site. Contractor had driven a digger through line at pole 851734. Fuses removed & tagged. Lines repaired. All supply restored on completion. NDR number N100280. Safety manager job to be created when its received. 1 x crossarm, 20 metres no8 Cu conductor, 2 x sleeves materials required. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.014316 | 11 | 2017 | 2017-01-09 | C | 25 | 0.014316 | 7.4957e-05
1 | 15436186 | 2017-02-14 10:00 | 2017-02-14 10:45 | 45 | 2 | 90 | 0.00026971 | 0.000251 | 5.9934e-06 | NAPA ID:27246 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 027246 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4062 | NONE | To install a 400V Fuse Disconnector on TC4062 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0001255 | 5.5 | 2017 | 2017-02-14 | B | 2 | 0.000251 | 5.9934e-06
1 | 15436361 | 2017-01-09 15:04 | 2017-01-09 20:14 | 309 | 83 | 13049.4333 | 0.039126 | 0.038379 | 0.00036879 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 739304 | CONDUCTOR - REPAIR/REHANG | CB 7121 A/R, L/O, E/F, O/C. Sectionalised & patrolled. Line down found at Pole 739304 due to the top breaking off of a tree & falling on lines. Repaired using 2x conductor joints. NDR # N100281 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.038379 | 11 | 2017 | 2017-01-09 | C | 83 | 0.038379 | 0.00036879
1 | 15436814 | 2017-02-15 10:05 | 2017-02-15 13:40 | 215 | 3 | 645 | 0.0019329 | 0.001905 | 8.9901e-06 | NAPA ID:27337 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 027337 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 532 Luck at Last Rd, Maungatautari, Cambridge | NONE | To replace 400V Arm & install a 400V Disconnector | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0009525 | 5.5 | 2017 | 2017-02-15 | B | 3 | 0.001905 | 8.9901e-06
1 | 15436830 | 2017-01-09 17:39 | 2017-01-09 18:22 | 43 | 247 | 10621 | 0.031845 | 0.029623 | 0.00074058 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21132 | JUMPER | Jumper broken at T3/329 Isolated between O6, J22, M100 & M50, repaired jumper and relivened | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.029623 | 11 | 2017 | 2017-01-09 | C | 247 | 0.029623 | 0.00074058
1 | 15436846 | 2017-02-09 09:00 | 2017-02-09 15:02 | 362 | 20 | 7240 | 0.021698 | 0.021518 | 5.9939e-05 | NAPA ID:26801 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | 026801 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3198 | NONE | Remove old double pole transformer structure and Transformer. Install new single pole and pole mount 100kVA Transformer TC3198. Remove old ABS IP508. (DNO160923) Install new 11kV Fuses FP1855 connected to new Transformer TC3198. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.010759 | 5.5 | 2017 | 2017-02-09 | B | 20 | 0.021518 | 5.9939e-05
1 | 15438919 | 2017-01-09 18:09 | 2017-01-09 21:20 | 191 | 1 | 191.1333 | 0.00057307 | 0.000564 | 2.9982e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV links. This appears to be a re occurring problem whenever it is windy. FM stated the lines beyond Fuses M83 are on Iron Rail type poles and the sag of the lines is bad. FM thinks there may be an up coming job to straighten pole & remedy this. Unknown if the poles are Powerco owned or privately owned. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000564 | 11 | 2017 | 2017-01-09 | C | 1 | 0.000564 | 2.9982e-06
1 | 15439519 | 2017-01-09 22:35 | 2017-01-10 00:46 | 131 | 661 | 21565.7333 | 0.06466 | 0.058714 | 0.0031452 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745785 | INSULATOR | CB 6777/5 A/R, L/O, E/F, O/C C Phase. Sectionalised & Patrolled with fault being due to a broken insulator at Pole 745785 Repaired using: 1x 11kV pin & Insulator, 1mtr of conductor, 2x conductor joints, & 1x binder NOTE: ABS 115 was incorrectly dressed closed & ABS 180 incorrectly dressed open. There was no outage on Mangorei CB 6 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.058714 | 11 | 2017 | 2017-01-09 | C | 661 | 0.058714 | 0.0031452
1 | 15442761 | 2017-01-10 06:36 | 2017-01-10 12:18 | 342 | 688 | 74655.7833 | 0.22384 | 0.21765 | 0.0020628 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793786 | INSULATOR | Section of line between CB4 ABS 1226, ABS 1289 recloser 4236 and recloser 4242 isolated to replace insulator @ pole 793786 balance of line backfed via switch 4661 for the duration of repairs | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.21765 | 11 | 2017 | 2017-01-10 | C | 688 | 0.21765 | 0.0020628
1 | 15445859 | 2017-01-10 07:14 | 2017-01-11 19:50 | 2196 | 2 | 4224 | 0.012665 | 0.012646 | 1.1993e-05 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P26086 | INSULATOR | CB 2552 tripped on Bph O/C. Outage only to Tararua Wind Farm North. Locate fault beyond CB 10060. Tripped due to HLT being applied for NAPA 26355-01. Switching canned due to fault. Replaced insulator at Pole P26086. | S1 | BUNNYTHORPE-KELVIN GV 33KV | BUNNYTHORPE | Manawatu | TP_BUNNYTHORPE | Western Electricity | POWERCO | 0.012646 | 33 | 2017 | 2017-01-10 | C | 2 | 0.012646 | 1.1993e-05
1 | 15447939 | 2017-02-15 09:33 | 2017-02-15 12:37 | 183 | 2 | 366.9333 | 0.0010996 | 0.001081 | 5.9934e-06 | NAPA ID:27339 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 027339 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Orepunga Rd, Tirau | NONE | To replace arms & install a 400V Fuse/Disconnector | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0005405 | 5.5 | 2017 | 2017-02-15 | B | 2 | 0.001081 | 5.9934e-06
1 | 15448468 | 2017-02-15 14:00 | 2017-02-15 14:30 | 30 | 6 | 180 | 0.00053941 | 0.000485 | 1.798e-05 | NAPA ID:27340 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 027340 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC314 | NONE | Install a 400V Fuse/Disconnector on TC314 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0002425 | 5.5 | 2017 | 2017-02-15 | B | 6 | 0.000485 | 1.798e-05
1 | 15448664 | 2017-01-26 09:39 | 2017-01-26 14:00 | 261 | 4 | 1044 | 0.0031295 | 0.003093 | 1.199e-05 | NAPA ID:27042 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 027042 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4360 | NONE | Replace pole O3232 using G&B techniques and install new transformer to replace TC4360. Disconnect and remove existing transformer from pole 383697. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0015465 | 5.5 | 2017 | 2017-01-26 | B | 4 | 0.003093 | 1.199e-05
1 | 15448674 | 2017-02-22 10:30 | 2017-02-22 14:05 | 215 | 6 | 1290 | 0.0038654 | 0.003811 | 1.7978e-05 | NAPA ID:27544 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 027544 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4247 | NONE | To replace 400V Arms & install a 400V Fuse Disconnector on TC4247 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0019055 | 5.5 | 2017 | 2017-02-22 | B | 6 | 0.003811 | 1.7978e-05
1 | 15449056 | 2017-01-10 09:29 | 2017-01-10 11:51 | 142 | 1 | 142.05 | 0.0004259 | 0.000416 | 2.9982e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 371826 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.000416 | 11 | 2017 | 2017-01-10 | C | 1 | 0.000416 | 2.9982e-06
1 | 15449180 | 2017-01-10 09:47 | 2017-01-10 12:04 | 136 | 2 | 273.6333 | 0.00082042 | 0.000802 | 5.9964e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798102 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000802 | 11 | 2017 | 2017-01-10 | C | 2 | 0.000802 | 5.9964e-06
1 | 15449329 | 2017-02-12 08:58 | 2017-02-12 13:20 | 262 | 1 | 262 | 0.00078517 | 0.000776 | 2.9968e-06 | NAPA ID:27305 TP_PIAKO GXP > PIAKO SUB > MVILLE SOUTH | 11 | Planned | 027305 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP120 | NONE | Level up Transformer TP120 at 75 Snell Street, Morrinsville. DFT244-10375 | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000388 | 5.5 | 2017 | 2017-02-12 | B | 1 | 0.000776 | 2.9968e-06
1 | 15452186 | 2017-02-15 09:48 | 2017-02-15 15:15 | 326 | 16 | 5228.5333 | 0.015668 | 0.015524 | 4.7947e-05 | NAPA ID:27656 TP_STRATFORD GXP > ELTHAM SUB > RAWHITIROA | 11 | Planned | 027656 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 736469 | NONE | Replace network pole 736469 and 736470 Live line break created at pole 736468 to reduce SAIDI impact Links 4943 Open from 0830 - 1430 advertising required | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.007762 | 5.5 | 2017 | 2017-02-15 | B | 16 | 0.015524 | 4.7947e-05
1 | 15452446 | 2017-01-10 11:25 | 2017-01-10 12:13 | 47 | 128 | 6122.6667 | 0.018357 | 0.017205 | 0.00038378 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 204571 | JUMPER | ( KPT1 ) recloser 9606/2 tripped O/C, A/R Part powers beyond ABS SB1 002 blown jumper x 1 at pole 204571 Isolations between links 9606/6 & ABS SB1 079 with back feed via sectionaliser 9223/2 jumper repaired all service restored Materials 1 x jumper , 1 x clamp | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.017205 | 11 | 2017 | 2017-01-10 | C | 128 | 0.017205 | 0.00038378
1 | 15452842 | 2017-01-10 12:30 | 2017-01-10 18:52 | 382 | 761 | 35467.3333 | 0.10634 | 0.099494 | 0.0023566 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 756169 | POLE | Using nearest ICP Car vs pole, lines wrapped around car. #F2223163 ETA required CB 7 Oakura sub tripped by NOC on receipt of OMS job appearing with advise of HV lines down as per above. Line isolated at fuses 8435 to replace pole. All supply restored on completion of repairs etc. NDR to be provided by Downer. 11m busck pole, 1 x donut, 2 x crossarms, 30 metres namu cond, 4 sleeves, materials required. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.099494 | 11 | 2017 | 2017-01-10 | C | 761 | 0.099494 | 0.0023566
1 | 15454214 | 2017-01-31 09:16 | 2017-02-03 11:38 | 4462 | 60 | 15507.2833 | 0.046481 | 0.045941 | 0.00035069 | NAPA ID:27461 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 027461 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220481 | NONE | Create two 11kV line gaps at poles 220481 and 385553 to allow pile driving work to take place by civil contractor for the new Powerco Wairakei Substation. Close breaks on 3rd February 2017. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.022971 | 5.5 | 2017 | 2017-01-31 | B | 60 | 0.045941 | 0.00035069
1 | 15454291 | 2017-02-13 09:23 | 2017-02-13 14:00 | 277 | 8 | 2216 | 0.0066409 | 0.006568 | 2.3974e-05 | NAPA ID:27210 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 027210 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2357 | NONE | LLP: To disconnect TC2357 & Remove 11kV Fuses. AP: To relocate the transformer from Site TC2357 to new site at TP3060. To install a new transformer at Site TP3061. To Create a LV break between the two transformers. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.003284 | 5.5 | 2017 | 2017-02-13 | B | 8 | 0.006568 | 2.3974e-05
1 | 15454564 | 2017-01-10 14:32 | 2017-01-10 15:16 | 44 | 38 | 1640.2 | 0.0049177 | 0.004575 | 0.00011393 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | UNKNOWN | Replace line break at P11577 and P17623 as part of planned work NAPA 27910 to replace poles and xarms broken by tree. Planned work being undertaken and customers not meant to have been affected so were not notified. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.004575 | 11 | 2017 | 2017-01-10 | C | 38 | 0.004575 | 0.00011393
1 | 15459302 | 2017-01-10 18:17 | 2017-01-10 20:55 | 158 | 83 | 9451 | 0.028336 | 0.027589 | 0.00024885 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794431 | CONDUCTOR - REPAIR/REHANG | Recloser 4237 L/O on O/C & E/F found lines down beyound fuses O58. isolated at O58 repaired lines & relivened 15 m of wire 2 tension sleeves | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.027589 | 11 | 2017 | 2017-01-10 | C | 83 | 0.027589 | 0.00024885
1 | 15459855 | 2017-01-10 21:23 | 2017-01-10 22:50 | 87 | 43 | 3741 | 0.011216 | 0.010829 | 0.00012892 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 586 | FUSE - ELEMENT/LINK (HV) | LV to HV please check Fuse 586 on way to this job emailed SMC LV to HV Replaced 2 x 20amp fuse HT | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.010829 | 11 | 2017 | 2017-01-10 | C | 43 | 0.010829 | 0.00012892
1 | 15460358 | 2017-01-11 06:15 | 2017-01-11 11:15 | 300 | 7 | 2100 | 0.0062962 | 0.006233 | 2.0987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t4/318 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace 1 x 10amp fuse at FP19 Replaced faulty transformer t4/318 self issue ap emailed SMC for an update to get F/man to call if still working onsite hub called to say Cameron closed this off with control earlier this morning.Have completed him from site outage on child | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.006233 | 11 | 2017 | 2017-01-11 | C | 7 | 0.006233 | 2.0987e-05
1 | 15462005 | 2017-02-01 09:48 | 2017-02-01 11:05 | 77 | 39 | 3003 | 0.0090009 | 0.00865 | 0.00011689 | NAPA ID:27574 TP_HAWERA GXP > MANAIA SUB > OTAKEHO | 11 | Planned | 027574 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 719033 | NONE | Replace Lighting arrestors on pole 719033 and install new earthing | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.004325 | 5.5 | 2017 | 2017-02-01 | B | 39 | 0.00865 | 0.00011689
1 | 15462028 | 2017-01-11 08:48 | 2017-01-11 08:51 | 3 | 858 | 2602.6 | 0.0078031 | 0 | 0.0025725 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | REC 9488 Tripped and L/O when doing planned maintenance NAPA 27459 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2017-01-11 | C | 858 | 0 | 0.0025725
1 | 15463105 | 2017-02-07 09:30 | 2017-02-07 10:25 | 55 | 35 | 1925 | 0.0057693 | 0.005454 | 0.0001049 | NAPA ID:27111 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | 027111 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 70 Puketutu Road, Matamata | NONE | To replace arms & install a 400V Fuse Disconnector | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.002727 | 5.5 | 2017 | 2017-02-07 | B | 35 | 0.005454 | 0.0001049
1 | 15463219 | 2017-02-14 09:11 | 2017-02-14 10:51 | 100 | 91 | 9125.7833 | 0.027348 | 0.026529 | 0.0002727 | NAPA ID:25671 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 025671 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726650 | NONE | Replace cross arm network pole 726650 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.013265 | 5.5 | 2017 | 2017-02-14 | B | 91 | 0.026529 | 0.0002727
1 | 15463310 | 2017-01-11 09:54 | 2017-01-11 12:16 | 141 | 310 | 682.1833 | 0.0020453 | 0 | 0.00092945 |  | 11 | Unplanned |  | OVERHEAD LINE | OUTAGE RESTORED | OUTAGE RESTORED | T1/437 | NONE | Customer is experiencing low voltage due to Transpower working on the lines. NAPA 2743. FM spoke to control and changed switching around to increase supply to the customer, as this is a non outage and customers are on a generator. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2017-01-11 | C | 310 | 0 | 0.00092945
1 | 15463333 | 2017-01-30 08:30 | 2017-01-30 15:24 | 414 | 26 | 10764 | 0.032264 | 0.03203 | 7.7932e-05 | NAPA ID:26756 TP_MASTERTON GXP | 11 | Planned | 026756 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 828592 | NONE | replacing 5 double circuit poles pole Nos 828592,828594,828596 ,828598 and 828600 red tag poles. NOTE 11kV TEMP58 BETWEEN POLES 376113 & 371240. | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.016015 | 5.5 | 2017 | 2017-01-30 | B | 26 | 0.03203 | 7.7932e-05
1 | 15463765 | 2017-01-11 12:00 | 2017-01-11 13:15 | 75 | 35 | 2625 | 0.0078703 | 0.007555 | 0.00010494 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | 380408 | CABLE - REPLACE LESS THAN 5 METRES | at 12:00, Otumoetai Sub, CB 5 Sherwood St. Contractor hit 11kV Cable feeding Transformer TD4-547. Isolated Cable at Fuses SD4-142. Generator connected to TD4-547. Permit issued & repairs carried out. All Power Restored on Completion. Dennis Ngatai Attended. NDR: TBA Materials: 4m of XLPE 35mm2 Al Cable, 2x 35mm2 Al Joint Kits, 2x 6A HV Fuses Check for safety - Contractors have hit UG cable. WH Kelly Drainlayers Advised control and SMC of 999 FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE 12:22 - 1R upgraded to 2R - Generator on the way to cover transformer TD4-547 13:15 - LV Generator on-line to supply TD4-547 Customers NDR - | F3/F4 | SHERWOOD ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.007555 | 11 | 2017 | 2017-01-11 | C | 35 | 0.007555 | 0.00010494
1 | 15465625 | 2017-02-02 08:55 | 2017-02-02 15:30 | 395 | 2 | 790 | 0.0023678 | 0.002349 | 5.9945e-06 | NAPA ID:26047 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 026047 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11098 | NONE | Change 11kv poles and crossarms on spur line 11098 DDOs 11098 installed in shutdown prior NAPA 25962 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0011745 | 5.5 | 2017 | 2017-02-02 | B | 2 | 0.002349 | 5.9945e-06
1 | 15465660 | 2017-01-11 13:36 | 2017-01-11 16:20 | 164 | 1 | 164 | 0.00049171 | 0.000482 | 2.9982e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K13129 | FUSE - ELEMENT/LINK (HV) | 2x 6amp[ fp2203 bird outage on child | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000482 | 11 | 2017 | 2017-01-11 | C | 1 | 0.000482 | 2.9982e-06
1 | 15469769 | 2017-01-11 16:29 | 2017-01-11 18:32 | 122 | 225 | 11658.45 | 0.034955 | 0.03293 | 0.00098641 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04709 | JUMPER | Repaired jumper @ pole P04709 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.03293 | 11 | 2017 | 2017-01-11 | C | 225 | 0.03293 | 0.00098641
1 | 15471212 | 2017-01-11 17:57 | 2017-01-11 21:31 | 214 | 175 | 11178.3333 | 0.033515 | 0.03194 | 0.00023086 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 448371 | BINDER | ( GLA C948 ) CB C948 tripped, A/R recloser 7417/2 tripped O/C, E/F, L/O feeder sectionalised. Floating conductor found at pole 448371 Isolation at Fuses 7148 ( spur no back feeds ) Conductor re bound all service restored | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.03194 | 11 | 2017 | 2017-01-11 | C | 175 | 0.03194 | 0.00023086
1 | 15473627 | 2017-01-11 20:05 | 2017-01-11 22:00 | 115 | 6 | 690.2 | 0.0020694 | 0.002015 | 1.7989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 373430 | FUSE - ELEMENT/LINK (HV) | replace 2 x 10A H/V, O/H fuses at 7101 ( wind ) | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002015 | 11 | 2017 | 2017-01-11 | C | 6 | 0.002015 | 1.7989e-05
1 | 15474470 | 2017-01-12 07:30 | 2017-01-12 12:22 | 292 | 15 | 2340 | 0.0070157 | 0.00688 | 0.00013492 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736144 | BINDER | Check 14 Hu Road, OMS 15474679 is related Used 4 X 10 Amp H/t Fuses 5 X 15 Amp H/T Fuses 3 X 8 Amp H/T Fuses 1 X Fuse Box 1 X 125 HRC Fuse L/V *Jo to check | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.00688 | 11 | 2017 | 2017-01-12 | C | 15 | 0.00688 | 0.00013492
1 | 15474577 | 2017-01-12 05:24 | 2017-01-12 07:47 | 142 | 6 | 853.3 | 0.0025583 | 0.002504 | 1.7989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 389426 | FUSE - ELEMENT/LINK (HV) | OMS 15474589 will need to be linked/sucked into this job 2X15amp bird @ Sd6-006 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002504 | 11 | 2017 | 2017-01-12 | C | 6 | 0.002504 | 1.7989e-05
1 | 15474871 | 2017-01-12 07:57 | 2017-01-12 12:51 | 293 | 104 | 7244.1333 | 0.021719 | 0.020783 | 0.00031181 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815338 | CONDUCTOR - REPAIR/REHANG | 33kV line fault between Graytown GXP and Martinborough Sub cb Lines down reported by Public MAB C893 offload as fire also in area Once faultman on site, 33 kV lines found down, 11 kv lines in area isolated at Fuses 7041 33kV line Isolated at ABS's 1336, S594 &, S774 lines repaired and returned to service Used 1 xbinder, 2 x sleeves &, 1 metre of conductor | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.020783 | 11 | 2017 | 2017-01-12 | C | 104 | 0.020783 | 0.00031181
1 | 15475032 | 2017-01-12 09:08 | 2017-01-12 12:14 | 186 | 4 | 745.2667 | 0.0022344 | 0.002198 | 1.1993e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1219N | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Check with fault man that this address is fed from the correct transformer. Suspect 1219 not 1204. 1 X 30 kVA Transformer 3 X 10 Fuses HT 3 X 6 Amp Ht Fuses | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.002198 | 11 | 2017 | 2017-01-12 | C | 4 | 0.002198 | 1.1993e-05
1 | 15477010 | 2017-02-19 09:00 | 2017-02-19 13:12 | 252 | 46 | 11592 | 0.034736 | 0.034322 | 0.00013784 | NAPA ID:25661 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 025661 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726531 | NONE | Replace defect poles 726531 & 726524 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.017161 | 5.5 | 2017 | 2017-02-19 | B | 46 | 0.034322 | 0.00013784
1 | 15479180 | 2017-01-12 13:54 | 2017-01-16 18:51 | 6057 | 98 | 9516.2167 | 0.028531 | 0.027649 | 0.00085448 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TL4-003 | CABLE - REPAIR | 12/01/17 at 13:40, Hamilton St Sub, CB 3 Spring St. Report of part power came in. Found fuses at Fuse/Sw SL3-135 had blown. Faultmen dispatched & investigation began. Generator connected to Transformer TL4-003. Cable Tested - found blown termination. Permit issued & repairs carried out. All Power Restored on Completion. Dennis Ngatai Attended. 1x Termination Kit, 3x Lugs, 2m of Earth cable replaced. Aged Equipment Report of part power found 1 HT fuse tripped in Fuse/Sw SL3-135. (Old reyrolle oil immersed Sw/Gear). Outage required from Sw/Gear 9956/1 to SL4-074 with backfeed at Sw/gear SL4-014. Generator connected to L/V of transformer TL3 003 transformer L/V links open, removed tagged | F2 | SPRING ST | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 0.027649 | 11 | 2017 | 2017-01-12 | C | 98 | 0.027649 | 0.00085448
1 | 15479488 | 2017-01-12 14:55 | 2017-01-12 19:16 | 260 | 1 | 260.5167 | 0.00078107 | 0.000772 | 2.9981e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU363 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 5a hv fuses | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000772 | 11 | 2017 | 2017-01-12 | C | 1 | 0.000772 | 2.9981e-06
1 | 15479870 | 2017-01-12 16:37 | 2017-01-12 19:37 | 180 | 1 | 180.2 | 0.00054027 | 0.000531 | 2.9981e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T452 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a hv fuses | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000531 | 11 | 2017 | 2017-01-12 | C | 1 | 0.000531 | 2.9981e-06
1 | 15480109 | 2017-01-12 17:38 | 2017-01-12 18:54 | 76 | 42 | 3201.1 | 0.0095974 | 0.009219 | 0.00012592 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4135 | FUSE - ELEMENT/LINK (HV) | Lv to HV check fuses 4135 Fuses found blown at Fuses 4135 - cause unknown Used 2 x 10a HV Fuses | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.009219 | 6.6 | 2017 | 2017-01-12 | C | 42 | 0.009219 | 0.00012592
1 | 15481063 | 2017-01-12 19:45 | 2017-01-13 13:55 | 1090 | 62 | 10170.3833 | 0.030493 | 0.029934 | 0.00018589 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 765100 | CONDUCTOR - REPAIR/REHANG | Found line down beyond pole 765100 across a river with trees over line on the river bank. Trees appear to be unstable tree crews required. Unsafe to continue in darkness faultman to return in daylight to further assess and repair. Section from fuses 4959 isolated for repairs. Used 20m no8 conductor | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.029934 | 11 | 2017 | 2017-01-12 | C | 62 | 0.029934 | 0.00018589
1 | 15482233 | 2017-01-12 21:15 | 2017-01-12 23:44 | 149 | 58 | 8002 | 0.023991 | 0.023469 | 0.00017389 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S9 & S11 | FUSE - ELEMENT/LINK (HV) | LV to HV to check fuse S9 on way to this fault Replaced 2x 10a fuses @ S9 and 2x 10a @ S11 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.023469 | 11 | 2017 | 2017-01-12 | C | 58 | 0.023469 | 0.00017389
1 | 15483682 | 2017-01-13 07:00 | 2017-01-13 08:25 | 85 | 42 | 3570 | 0.010703 | 0.010325 | 0.00012592 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8462 | FUSE - ELEMENT/LINK (HV) | Found both Fuses 8462 have 1 x20 1x 30 1x40 Amp fuses in & 8410 have 20 Amp so after talking to Andrew Wilson We put 25 Amp Fuses in 8462 After Backfeeding so no lost of power to do this 1 Fuse at 8462 was out And 2 at 8410 Patrolled nothing found Reliven Ok | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.010325 | 11 | 2017 | 2017-01-13 | C | 42 | 0.010325 | 0.00012592
1 | 15484345 | 2017-01-14 09:15 | 2017-01-14 14:11 | 296 | 5 | 1480 | 0.0044372 | 0.004392 | 1.499e-05 | NAPA ID:28064 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV | 11 | Planned | 028064 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | n/a | NONE | Install new span of wire & remove fuses SF3-011. Live line cut in line break at pole 346138 to de-energize including TF3-037. Hot Line Tag required on TGA REC13004 (Pyes Pa) to enable connection of conductor to ABS IP664. (Feeder OPEN point) | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002196 | 5.5 | 2017 | 2017-01-14 | B | 5 | 0.004392 | 1.499e-05
1 | 15484625 | 2017-01-13 09:16 | 2017-01-13 12:28 | 192 | 124 | 10707.8 | 0.032103 | 0.030988 | 0.00037177 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793486 | CROSSARM - WHOLE ASSEMBLY | Recloser 4236 tripped C Ph O/C E/F Crossarms at Pole 793486 known as failing Isolated at ABS's 434 & 709 with transformers X145 & X146 isolated as well Complete crossarms replaced on Both HV and LV lines | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.030988 | 11 | 2017 | 2017-01-13 | C | 124 | 0.030988 | 0.00037177
1 | 15485135 | 2017-01-13 09:35 | 2017-01-13 12:05 | 150 | 1 | 150.0833 | 0.00044997 | 0.00044 | 2.9981e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Relay Plant Palmerston North | LOAD CONTROL - PLANT (HV) | Fault with the ripple relay system in an area of Palmerston North | F3 | KEITH ST 21 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.00044 | 11 | 2017 | 2017-01-13 | C | 1 | 0.00044 | 2.9981e-06
1 | 15485490 | 2017-01-13 10:46 | 2017-01-13 16:30 | 344 | 586 | 30069 | 0.090151 | 0.084879 | 0.00085746 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217021 | CONDUCTOR - REPAIR/REHANG | Large 11kV Span down past Pole 217021. Transformer TF3-024 only transformer effected - generator connected Job restored but Transformer TF3-032 is still off. Transformer has no ICP's connected, may need a site check to correct GIS information. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.084879 | 11 | 2017 | 2017-01-13 | C | 586 | 0.084879 | 0.00085746
1 | 15486965 | 2017-01-13 15:52 | 2017-01-13 16:38 | 46 | 2 | 92.4 | 0.00027703 | 0.000259 | 5.9962e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P14306 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Damaged carrier found at Transformer T4/185 Faultman didn't have replacement and was called off job due to KPI of another job (13:16) Back feed installed Via ABS F38 - Isolations at ABS'S F58 & F57 with Links F56 open as well Fuse carrier replaced - used 1 x carrier & Base 1 x 2 amp fuse | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000259 | 11 | 2017 | 2017-01-13 | C | 2 | 0.000259 | 5.9962e-06
1 | 15487089 | 2017-01-13 12:51 | 2017-01-13 17:32 | 281 | 3 | 843 | 0.0025274 | 0.0025 | 8.9943e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P03952 | CONDUCTOR - REPAIR/REHANG | Check for safety - Digger taken out 11kv OH lines between two poles Hazards process complete Advised control and SMC of 999 Isolated at Fuses H116 lines repaired Used 9 HV sleeves 72 mtrs of HV conductor 3 x 10 amp fuses 6x LV sleeves 15 mtrs LV Conduxctor 2 x 60 amp HRC fuses 2x coach bolts NDR # N300274 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0025 | 11 | 2017 | 2017-01-13 | C | 3 | 0.0025 | 8.9943e-06
1 | 15487275 | 2017-02-14 09:30 | 2017-02-14 14:42 | 312 | 90 | 28080 | 0.084148 | 0.083339 | 0.00026971 | NAPA ID:27021 TP_KINLEITH GXP > MARAETAI ROAD SUB > LOMOND AVE | 11 | Planned | 027021 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1658 | NONE | To disconnect the old transformer TC1658 and commission new transformer TC1658 | F1/F3 | LOMOND AVE | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.041669 | 5.5 | 2017 | 2017-02-14 | B | 90 | 0.083339 | 0.00026971
1 | 15487490 | 2017-02-02 09:00 | 2017-02-02 13:49 | 289 | 6 | 1734 | 0.0051972 | 0.005143 | 1.7984e-05 | NAPA ID:26838 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 026838 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Mahuta Rd, Paeroa | NONE | To replace the existing Transformer pole. To extend the 11kV Lines to a new transformer pole, To complete line Maintenance. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0025715 | 5.5 | 2017 | 2017-02-02 | B | 6 | 0.005143 | 1.7984e-05
1 | 15487667 | 2017-02-02 08:30 | 2017-02-02 13:43 | 313 | 6 | 1878 | 0.0056289 | 0.005574 | 1.7984e-05 | NAPA ID:27036 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 027036 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Knights Rd, Masterton | NONE | replace 11kv poles and hardware | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002787 | 5.5 | 2017 | 2017-02-02 | B | 6 | 0.005574 | 1.7984e-05
1 | 15488572 | 2017-01-13 18:06 | 2017-01-13 18:08 | 1 | 102 | 185.3 | 0.00055555 | 0 | 0.00030581 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N/A - NOT APPLICABLE | UNKNOWN | Outage required during switching for NAPA 27430. Isolation and Earthing for 220kV reconductoring work. Switching due to loading issues. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2017-01-13 | C | 102 | 0 | 0.00030581
1 | 15489155 | 2017-01-13 20:14 | 2017-01-13 22:04 | 110 | 25 | 2757.0833 | 0.0082661 | 0.008041 | 7.4953e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4957 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a hv fuses | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.008041 | 11 | 2017 | 2017-01-13 | C | 25 | 0.008041 | 7.4953e-05
1 | 15491036 | 2017-01-14 12:33 | 2017-01-14 12:39 | 6 | 1 | 6.4 | 1.9188e-05 | 1e-05 | 2.998e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Retailer cancelled job. Power has come back on. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 1e-05 | 11 | 2017 | 2017-01-14 | C | 1 | 1e-05 | 2.998e-06
1 | 15491279 | 2017-01-14 16:08 | 2017-01-14 16:52 | 44 | 23 | 1012 | 0.0030341 | 0.002827 | 6.8956e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | te6-012 | FUSE - ELEMENT/LINK (HV) | at 16:05, Te Puke Sub, CB 8 Te Matai Rd Feeder. Faultman found 1x HV fuse blown at Fuse/Sw SE6-133. Patrolled O/H line and no fault found. To reload fuse had to isolate at Sw/gear 9608/3 & SE6-137 (due to oil insulated fuse switch). Fuse reloaded, and area relivened - All OK. Unknown cause but suspect possible bird strike. Josh Reid Attended. 1x 20A HV Fuse Replaced. 19/01/2017: Crew Times have been amended to reflect the original OMS Crew Times (OMS 12491094) for Request / En Route / Arrived. (axk) | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.002827 | 11 | 2017 | 2017-01-14 | C | 23 | 0.002827 | 6.8956e-05
1 | 15491450 | 2017-01-14 20:48 | 2017-01-14 23:21 | 152 | 202 | 11896.3667 | 0.035666 | 0.033849 | 0.00060561 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 481532 | CONDUCTOR - REPAIR/REHANG | RP 10 L/O on E/F sectionalised and found line down between 13145/3 & se5-279. repaired line & relivened | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.033849 | 11 | 2017 | 2017-01-14 | C | 202 | 0.033849 | 0.00060561
1 | 15493650 | 2017-01-14 23:08 | 2017-01-15 12:17 | 788 | 1 | 770.6833 | 0.0023106 | 0.002301 | 5.9961e-06 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Y10 | UNKNOWN | CB Y10 Trip O/C B & C Phase. Sectionalised & Patrolled, No fault found. Relivened ok. Suspect Bird Strike | F2 | LINTON EXPRESSWAY | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.002301 | 33 | 2017 | 2017-01-14 | C | 1 | 0.002301 | 5.9961e-06
1 | 15494425 | 2017-01-15 09:21 | 2017-01-15 10:28 | 66 | 15 | 994.6667 | 0.002982 | 0.002847 | 4.497e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835245 | JUMPER | Broken Jumper at Pole 835245 and Floating Conductor at Pole 835246 Isolation between CB C850 and ABS S152. Backfeed via ABS S154. 1mtr 25mm Copper conductor 1 x Line Tap and 1 x Binder | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.002847 | 11 | 2017 | 2017-01-15 | C | 15 | 0.002847 | 4.497e-05
1 | 15494430 | 2017-02-01 08:30 | 2017-02-01 15:09 | 399 | 275 | 109725 | 0.32888 | 0.32641 | 0.00082426 | NAPA ID:24708 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 024708 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Featherston | NONE | replace 6 defective 11kv poles | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.1632 | 5.5 | 2017 | 2017-02-01 | B | 275 | 0.32641 | 0.00082426
1 | 15494454 | 2017-02-08 08:36 | 2017-02-08 14:57 | 381 | 166 | 63367.7333 | 0.18991 | 0.18842 | 0.0004975 | NAPA ID:24717 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 024717 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Featherston | NONE | Replace 6 defective 11kv poles. WO 30032258 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.09421 | 5.5 | 2017 | 2017-02-08 | B | 166 | 0.18842 | 0.0004975
1 | 15494492 | 2017-02-07 09:00 | 2017-02-07 14:45 | 344 | 18 | 6202.2 | 0.018588 | 0.018426 | 5.3947e-05 | NAPA ID:27773 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027773 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Burnetts Road, Masterston | NONE | Replace 11kv poles and hardware | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.009213 | 5.5 | 2017 | 2017-02-07 | B | 18 | 0.018426 | 5.3947e-05
1 | 15494505 | 2017-02-28 08:45 | 2017-02-28 13:55 | 310 | 18 | 5580 | 0.016718 | 0.016556 | 5.393e-05 | NAPA ID:27774 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027774 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7702 | POLE | Replace 11kv poles and hardware at different sites | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.008278 | 5.5 | 2017 | 2017-02-28 | B | 18 | 0.016556 | 5.393e-05
1 | 15495985 | 2017-01-15 09:08 | 2017-01-15 14:41 | 332 | 2686 | 107729.1 | 0.32298 | 0.29882 | 0.0080497 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 442951 | POLE | RS H131 A/R, L/O, O/C B & C Phase. TUR CB 8 A/R. TP Linton CB 1182 Trip Car V Pole Corner of SH57 and Kendalls Line. Fire Comms # F2226117 Caused complete outage of Turitea Sub FM determined no 33kV on broken pole, so CB 1182 closed & power restored to Turitea Sub except CB 8. Work area isolated & feeder relivened with a back feed also put in via RS10041. Pole Replaced using 1x 11m busck pole, 2x 11kV Crossarms, 6x Pins & Insulators NDR #52611. Outage should not have affected 33kV line. Protection review initiated - refer safety manager incident 695225. | S3 | LINTON-TURITEA 33KV | LINTON | Manawatu | TP_LINTON | Western Electricity | POWERCO | 0.29882 | 33 | 2017 | 2017-01-15 | C | 2686 | 0.29882 | 0.0080497
1 | 15498499 | 2017-02-07 10:00 | 2017-02-07 14:10 | 249 | 3 | 748.85 | 0.0022443 | 0.002217 | 8.9911e-06 | NAPA ID:28086 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | 028086 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X122 | NONE | Replace Transformer X 122 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.0011085 | 5.5 | 2017 | 2017-02-07 | B | 3 | 0.002217 | 8.9911e-06
1 | 15498689 | 2017-01-15 12:18 | 2017-01-15 12:28 | 9 | 51 | 468.35 | 0.0014041 | 0.000945 | 0.0001529 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 839685 | CONDUCTOR - REPAIR/REHANG | Hub advises ETA 30 minutes, advised NZ Fire Service Tree branch touching line. Feeder de-energised and branch knocked off with fuse stick from Bucket Truck | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.000945 | 11 | 2017 | 2017-01-15 | C | 51 | 0.000945 | 0.0001529
1 | 15498865 | 2017-01-15 12:28 | 2017-01-15 13:15 | 46 | 85 | 3961 | 0.011875 | 0.01111 | 0.00025483 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | See OMS 15498850 Jobs are left over after main fault closed out. Made invalid due to outage recorded on 15498850 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.01111 | 11 | 2017 | 2017-01-15 | C | 85 | 0.01111 | 0.00025483
1 | 15499606 | 2017-01-15 13:12 | 2017-01-15 15:31 | 138 | 213 | 13634.1333 | 0.040876 | 0.038959 | 0.00063858 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850153 | CONDUCTOR - REPAIR/REHANG | CB 7 A/R, O/C B & C Phase. Continued to Auto Reclose so A/R disabled & feeder tripped. Sectionalised & patrolled with fault found to be due to a floating conductor. Repaired by refitting Insulator to cross arm and replacing the nut. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.038959 | 11 | 2017 | 2017-01-15 | C | 213 | 0.038959 | 0.00063858
1 | 15503636 | 2017-01-15 12:58 | 2017-01-15 13:15 | 16 | 1 | 16.95 | 5.0817e-05 | 4.1e-05 | 2.998e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Power already restored. See OMS 15498850 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 4.1e-05 | 11 | 2017 | 2017-01-15 | C | 1 | 4.1e-05 | 2.998e-06
1 | 15504241 | 2017-01-15 19:23 | 2017-01-15 20:16 | 53 | 1038 | 55149.8667 | 0.16534 | 0.15601 | 0.003112 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 764090 | BINDER | CB U30 Tripped No Flags Bird found at Pole 764090 during sectionlising All power restored | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.15601 | 11 | 2017 | 2017-01-15 | C | 1038 | 0.15601 | 0.003112
1 | 15507621 | 2017-01-15 22:41 | 2017-01-16 00:55 | 134 | 181 | 24254 | 0.072714 | 0.071086 | 0.00054264 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TE4-168 | POLE | at 20:50, Welcome Bay Sub, CB 1 Waimapu Feeder, Recloser 9182, Tripped, E/F, Auto Reclosed. Downer Faultman TJ Tanoa lives close by and saw the lines whip from fault current. Drove down road to find Car V Pole at Transformer Pole TE4-168. Lines Isolated at ABS SE4-031, SE4-005 & Fuses SE4-020. Backfeed supplied from WBY 7: Closed Sectionaliser 9507. Permit issued & repairs carried out. All Power Restored on Completion. TJ Tanoa & Dennis Ngatai Attended. 1x Pole & 3x Binders Replaced. NDR: TBA. See 15506841. A/R on 15506841 | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.071086 | 11 | 2017 | 2017-01-15 | C | 181 | 0.071086 | 0.00054264
1 | 15507934 | 2017-01-15 23:13 | 2017-01-16 00:45 | 91 | 10 | 918.6667 | 0.0027542 | 0.002664 | 2.998e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09331 | FUSE - ELEMENT/LINK (HV) | Refer OMS 15507864. Replace 2 x 15amp fuses at I26. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.002664 | 11 | 2017 | 2017-01-15 | C | 10 | 0.002664 | 2.998e-05
1 | 15508227 | 2017-02-02 08:45 | 2017-02-02 14:57 | 372 | 21 | 3982 | 0.011935 | 0.011746 | 0.00010191 | NAPA ID:27316 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027316 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP448-IC368 | NONE | Install TEMP09 Hardware and Pole changes IP448-IC368 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.005873 | 5.5 | 2017 | 2017-02-02 | B | 21 | 0.011746 | 0.00010191
1 | 15508264 | 2017-01-14 08:24 | 2017-01-14 09:43 | 79 | 1 | 79.45 | 0.0002382 | 0.000229 | 2.998e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805832 | FUSE - ELEMENT/LINK (HV) | Reload at Fuss 4746 2 x 6A Cause unknown | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.000229 | 11 | 2017 | 2017-01-14 | C | 1 | 0.000229 | 2.998e-06
1 | 15508942 | 2017-01-15 23:20 | 2017-01-16 01:42 | 142 | 4 | 568.5333 | 0.0017045 | 0.001668 | 1.1992e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 816719 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 7374 2 x 10A Cause wind | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001668 | 11 | 2017 | 2017-01-15 | C | 4 | 0.001668 | 1.1992e-05
1 | 15515355 | 2017-01-16 10:41 | 2017-01-16 14:55 | 254 | 5605 | 340745.6167 | 1.0216 | 0.97114 | 0.01681 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Te Mati Rd | CABLE - REPLACE LESS THAN 5 METRES | CB 2252 CB W50 ,W40 & RECLOSER 10060 ALL TRIPPED AT 10:41 This tripped Kelvin Grove Sub off due to Hot Line Tag on CB2252 & CB W50( CAC 28077-01) After Removing Hot Line Tag & Patrolling Line we Liven up Kelvin Grove Sub Once this was done Patrolled line to Wind Farm Found that to be ok up To 33kV ABS Z44 Liven that section up Patrolled line to CB Z200 found Insulator that may have been Problem Replaced that tryed to liven but no Good This tripped CB W40 Which took Wind Farm off Again Close CB W40 back in windfarm started up Again Tested Cable From ABS 44 to Keith St Sub found that the blue Phase was faulty DNO Number 170105 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.97114 | 11 | 2017 | 2017-01-16 | C | 5605 | 0.97114 | 0.01681
1 | 15519791 | 2017-01-16 10:42 | 2017-01-16 11:55 | 72 | 111 | 8054.9 | 0.024149 | 0.02315 | 0.00033278 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 802916 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 645 2 x 20A Cause unknown | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.02315 | 11 | 2017 | 2017-01-16 | C | 111 | 0.02315 | 0.00033278
1 | 15523168 | 2017-01-16 11:18 | 2017-01-16 14:32 | 194 | 1 | 194.3333 | 0.00058261 | 0.000573 | 2.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Kelvin Grove Sub | UNKNOWN | NNF - FM has confirmed customer has full power as this was part of the Kelvin Grove Sub fault earlier on today | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000573 | 11 | 2017 | 2017-01-16 | C | 1 | 0.000573 | 2.9979e-06
1 | 15523740 | 2017-01-16 11:45 | 2017-01-16 16:00 | 254 | 1 | 254.5833 | 0.00076324 | 0.000754 | 2.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P11842 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000754 | 11 | 2017 | 2017-01-16 | C | 1 | 0.000754 | 2.9979e-06
1 | 15525567 | 2017-01-28 09:00 | 2017-01-28 14:24 | 324 | 45 | 14235.3333 | 0.04267 | 0.042265 | 0.00020683 | NAPA ID:27673 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 027673 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T7/451 | NONE | install poles and equip for the cut over from the OH to UG to remove red defected poles. Works location: Halls Rd. WO 10160544 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.021132 | 5.5 | 2017 | 2017-01-28 | B | 45 | 0.042265 | 0.00020683
1 | 15525584 | 2017-01-27 09:06 | 2017-01-27 12:30 | 204 | 7 | 1394 | 0.0041785 | 0.004115 | 2.0983e-05 | NAPA ID:28024 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 028024 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-001 | NONE | 1. LLP create break at pole 221187 2. AP change xarms 3. LLP Close break at pole 221187. 4. LLP Remove ABS TEMP20. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0020575 | 5.5 | 2017 | 2017-01-27 | B | 7 | 0.004115 | 2.0983e-05
1 | 15525757 | 2017-01-16 15:41 | 2017-01-16 15:55 | 13 | 1 | 13.9167 | 4.1722e-05 | 3.2e-05 | 2.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 849434 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuses at 2972. Very windy | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 3.2e-05 | 11 | 2017 | 2017-01-16 | C | 1 | 3.2e-05 | 2.9979e-06
1 | 15525830 | 2017-02-03 09:24 | 2017-02-03 11:26 | 122 | 38 | 4665.7667 | 0.013984 | 0.013642 | 0.00011389 | NAPA ID:26972 TP_GREYTOWN GXP > TUHITARATA SUB > OTARAIA | 11 | Planned | 026972 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 810726 | NONE | Reconnect jumpers at pole 810726 to close line break. NOTE:: late switching due to flooding (Road closures). | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.006821 | 5.5 | 2017 | 2017-02-03 | B | 38 | 0.013642 | 0.00011389
1 | 15528871 | 2017-01-17 02:18 | 2017-01-17 04:04 | 105 | 288 | 20892.6 | 0.062635 | 0.060044 | 0.00086341 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 381794 | UNKNOWN | at 02:18, Tower Rd Sub, CB 1 Gordon Feeder, Recloser RC01 Tripped, E/F, L/O. Faultmen dispatched & investigation began. Feeder patrolled / sectionalised. No fault was found. Unknown Cause. All Power Restored on Completion. Perry Hicks Attended. No Materials Used. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.060044 | 11 | 2017 | 2017-01-17 | C | 288 | 0.060044 | 0.00086341
1 | 15530128 | 2017-01-17 06:20 | 2017-01-17 07:36 | 76 | 453 | 33920 | 0.10169 | 0.097616 | 0.0013581 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | BHM2 - needs recreating | UNKNOWN | BHM CB 2 tripped on B Ph OC. Line patrolled and no fault found. FM reported. Suspect trees to be defected | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.097616 | 11 | 2017 | 2017-01-17 | C | 453 | 0.097616 | 0.0013581
1 | 15531356 | 2017-01-17 07:19 | 2017-01-17 09:18 | 118 | 10 | 1187.3333 | 0.0035596 | 0.003469 | 2.9979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 264477 | FUSE - ELEMENT/LINK (HV) | Reload at fuses FP703 2 x 10A Bird strike .Stuck in verified SR126781 17/01/17 mjk | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.003469 | 11 | 2017 | 2017-01-17 | C | 10 | 0.003469 | 2.9979e-05
1 | 15533570 | 2017-01-17 13:36 | 2017-01-17 14:36 | 60 | 1 | 60.7833 | 0.00018223 | 0.000173 | 2.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | - | NONE | Is part of Part B of the outage - is within the line break of the worksite (Tx / GIS information is correct) - power should be restored within 20 minutes. | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.000173 | 11 | 2017 | 2017-01-17 | C | 1 | 0.000173 | 2.9979e-06
1 | 15535936 | 2017-01-17 08:30 | 2017-01-17 15:45 | 435 | 111 | 21375 | 0.064081 | 0.063082 | 0.00033277 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | SCADA dressing, no outage | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.063082 | 11 | 2017 | 2017-01-17 | C | 111 | 0.063082 | 0.00033277
1 | 15536670 | 2017-01-17 20:17 | 2017-01-17 21:28 | 71 | 4 | 284.2667 | 0.00085222 | 0.000816 | 1.1992e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | T1670 | FUSE - ELEMENT/LINK (HV) | 1 x 3A HV Fuse Replaced. Transformer Offloaded to remove trees from LV Lines. NDR 600038 | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000816 | 11 | 2017 | 2017-01-17 | C | 4 | 0.000816 | 1.1992e-05
1 | 15538803 | 2017-01-17 22:36 | 2017-01-17 23:34 | 58 | 10 | 582.1667 | 0.0017453 | 0.001655 | 2.9979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | I26 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuses at I26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001655 | 11 | 2017 | 2017-01-17 | C | 10 | 0.001655 | 2.9979e-05
1 | 15539223 | 2017-01-18 06:06 | 2017-01-18 07:50 | 103 | 1 | 103.2 | 0.00030938 | 0.0003 | 2.9979e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845906 | FUSE - ELEMENT/LINK (HV) | 7946 2 x 8 amp wind | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0003 | 11 | 2017 | 2017-01-18 | C | 1 | 0.0003 | 2.9979e-06
1 | 15539681 | 2017-02-03 08:50 | 2017-02-03 10:46 | 116 | 4 | 464 | 0.0013907 | 0.001354 | 1.1989e-05 | NAPA ID:27693 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | 027693 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 144 Frankton Road, Waihi | NONE | REPLACE WITH XARM AR WKOWHI055 WITH 3M XARMS | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000677 | 5.5 | 2017 | 2017-02-03 | B | 4 | 0.001354 | 1.1989e-05
1 | 15541156 | 2017-02-03 10:00 | 2017-02-03 11:24 | 84 | 3 | 252 | 0.0007553 | 0.000728 | 8.9916e-06 | NAPA ID:27690 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11 | Planned | 027690 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1795 | NONE | LLP TO MAKE TEMP BREAK TC1795, AP TO RECONFIGURE TRANSF STRUCTURE & LV XARMS, LLP TO CLOSE TEMP GAP TC1795. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000364 | 5.5 | 2017 | 2017-02-03 | B | 3 | 0.000728 | 8.9916e-06
1 | 15541211 | 2017-01-18 10:24 | 2017-01-18 11:36 | 72 | 2 | 144 | 0.0004317 | 0.000413 | 5.9958e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228044 | FUSE - ELEMENT/LINK (HV) | fuses Fp5-88 2 x 25 poss bird outage on child | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000413 | 11 | 2017 | 2017-01-18 | C | 2 | 0.000413 | 5.9958e-06
1 | 15541277 | 2017-01-18 10:50 | 2017-01-18 12:35 | 104 | 2 | 209.4333 | 0.00062786 | 0.000609 | 5.9958e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 799997 | FUSE - ELEMENT/LINK (HV) | 2 x 10amp fuses Wind | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000609 | 11 | 2017 | 2017-01-18 | C | 2 | 0.000609 | 5.9958e-06
1 | 15542008 | 2017-01-18 12:57 | 2017-01-18 13:17 | 20 | 55 | 1100 | 0.0032977 | 0.002803 | 0.00016488 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2596 | JUMPER | Outage required on HV side of Transformer T2596 to repair a broken LV neutral (2 LV jointers required) | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002803 | 11 | 2017 | 2017-01-18 | C | 55 | 0.002803 | 0.00016488
1 | 15542721 | 2017-01-18 15:02 | 2017-01-18 17:02 | 120 | 6 | 721.7 | 0.0021636 | 0.002109 | 1.7987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2894 | FUSE - ELEMENT/LINK (HV) | This is related to 15543484 - fuses 2894 reloaded. This ICP is showing on the incorrect sub and feeder. Information has been sent to BI to be corrected. 2 HT fuses tripped at 2894. (10A rating). Suspect wind. | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.002109 | 11 | 2017 | 2017-01-18 | C | 6 | 0.002109 | 1.7987e-05
1 | 15544321 | 2017-01-19 05:48 | 2017-01-19 07:43 | 114 | 5 | 573.25 | 0.0017185 | 0.001673 | 1.4989e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 804914 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp 864 trees | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.001673 | 22 | 2017 | 2017-01-19 | C | 5 | 0.001673 | 1.4989e-05
1 | 15544384 | 2017-01-19 06:35 | 2017-01-19 13:54 | 439 | 1139 | 45395.5 | 0.13609 | 0.12585 | 0.0034146 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848864 | CONDUCTOR - REPAIR/REHANG | NOTE: This OMS incorporates 2 seperate HV faults over 2 feeders. Initially recloser CB C634/2 tripped on Phase B OC. This recloser failed to close (locally or remote) when sectionslising. Began sectionalising from end of feeder via Gas/Sw 11035. This caused recloser C630/2 to trip (Tuhitarata CB C927 feeder) due to a fault between AB S526 and the Gas/Sw 11035. Area isolated with a broken conductor rejointed at pole 848864. (Large tree branch blown across conductor). When liveneing area, CB C630/2 tripped again. This area then sectiobailesed but all restored. (Suspect pick up load on recloser). Further sectionalising to ABS S505 found another conductor broken (2 spans). Isolation between ABS S505 and S526 with 3 metres conductor and 3 jointers required (Pole 798319). Feeder livened to ABS S505 with another patrol carried out to CB C634/2. Looked Ok and CB C634/2 then closed successfully on site. Feeders then restored to normal configurations. (Storm conditions in place). | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.12585 | 11 | 2017 | 2017-01-19 | C | 1139 | 0.12585 | 0.0034146
1 | 15544905 | 2017-01-19 07:14 | 2017-01-19 09:30 | 136 | 6 | 816.3 | 0.0024472 | 0.002393 | 1.7987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373430 | FUSE - ELEMENT/LINK (HV) | 7101 2 x10 wind | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002393 | 11 | 2017 | 2017-01-19 | C | 6 | 0.002393 | 1.7987e-05
1 | 15545120 | 2017-02-07 08:22 | 2017-02-07 13:24 | 302 | 24 | 7258.4 | 0.021754 | 0.021537 | 7.1929e-05 | NAPA ID:28084 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028084 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Replace poles between 809548 & 809645 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.010769 | 5.5 | 2017 | 2017-02-07 | B | 24 | 0.021537 | 7.1929e-05
1 | 15545557 | 2017-01-19 09:13 | 2017-01-19 10:03 | 49 | 174 | 8572.4 | 0.025699 | 0.024133 | 0.00052163 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 354362 | BINDER | Outage required past Recloser C604/2 to repair floating conductor. No backfeeds available. Rebind in 3 x conductors | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.024133 | 11 | 2017 | 2017-01-19 | C | 174 | 0.024133 | 0.00052163
1 | 15545612 | 2017-02-07 09:00 | 2017-02-07 13:55 | 294 | 7 | 2063.6 | 0.0061847 | 0.006121 | 2.0979e-05 | NAPA ID:26159 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | 026159 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rotoehu Road | NONE | Replace poles, hardware and conductor | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.0030605 | 5.5 | 2017 | 2017-02-07 | B | 7 | 0.006121 | 2.0979e-05
1 | 15545667 | 2017-01-19 08:11 | 2017-01-19 10:11 | 119 | 4 | 478.0667 | 0.0014332 | 0.001397 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI148 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 5a hv fuses | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.001397 | 11 | 2017 | 2017-01-19 | C | 4 | 0.001397 | 1.1991e-05
1 | 15546740 | 2017-01-19 08:14 | 2017-01-19 18:45 | 630 | 7 | 4413.6167 | 0.013231 | 0.013168 | 2.0985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 811718 | POLE | NOVA called for update at 3pm, rung SMC who were looking into it. ( HAU C642 ) Broken pole 811718 Isolation at Fuses 7166 ( spur no back feeds ) Pole replaced all service restored Materials 1 x pole, 1 x arm complete | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.013168 | 11 | 2017 | 2017-01-19 | C | 7 | 0.013168 | 2.0985e-05
1 | 15546788 | 2017-01-19 08:19 | 2017-01-19 14:39 | 380 | 4 | 1159 | 0.0034745 | 0.003438 | 2.0985e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731316 | CONDUCTOR - REPAIR/REHANG | Replaced 1x hv fuse and found transfromer 4214T faulty and replaced same on completion also found fuse blown @ 6014 on checking the line found line down @ pole 731316 and repaired | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.003438 | 11 | 2017 | 2017-01-19 | C | 4 | 0.003438 | 2.0985e-05
1 | 15546889 | 2017-01-19 08:31 | 2017-01-19 10:21 | 110 | 149 | 9157.6833 | 0.027453 | 0.026113 | 0.00044668 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Rec 284 O/C Trip Line patrolled & sectionalised nothing found | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.026113 | 11 | 2017 | 2017-01-19 | C | 149 | 0.026113 | 0.00044668
1 | 15547535 | 2017-01-19 08:51 | 2017-01-19 11:31 | 159 | 5 | 799.1667 | 0.0023958 | 0.00235 | 1.4989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811131 | FUSE - ELEMENT/LINK (HV) | 2 x 10 fuses 7317 wind | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.00235 | 11 | 2017 | 2017-01-19 | C | 5 | 0.00235 | 1.4989e-05
1 | 15548614 | 2017-01-19 08:59 | 2017-01-19 15:41 | 402 | 100 | 21240.3333 | 0.063676 | 0.062776 | 0.00029979 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 836104 | CONDUCTOR - REPAIR/REHANG | Check 32 DAGGS ROAD, OMS 15548622 is related. Reports of no powers found recloser C268 had tripped (Non SCADA). Feeder sectionalised with a broken conductor found between ABS TEMP84 and S116. (Backfeed at ABS S114). 30m conductor required aand 3 sleeves. (Tree branch involved). Relivened OK. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.062776 | 11 | 2017 | 2017-01-19 | C | 100 | 0.062776 | 0.00029979
1 | 15548780 | 2017-01-19 09:01 | 2017-01-19 10:46 | 105 | 129 | 13264.65 | 0.039766 | 0.038605 | 0.00044968 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 840053 | CONDUCTOR - REPAIR/REHANG | rec 4200 Trip O/C E/F line patrolled found branch on line at pole 840053 Removed by hot stick NDR 30487 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.038605 | 11 | 2017 | 2017-01-19 | C | 129 | 0.038605 | 0.00044968
1 | 15548936 | 2017-01-19 09:03 | 2017-01-19 13:14 | 250 | 3 | 751.05 | 0.0022515 | 0.002224 | 8.9935e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756173 | FUSE - ELEMENT/LINK (HV) | 2 x3 8471 wind | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.002224 | 11 | 2017 | 2017-01-19 | C | 3 | 0.002224 | 8.9935e-06
1 | 15550026 | 2017-01-19 09:47 | 2017-01-19 15:15 | 327 | 3 | 982.25 | 0.0029447 | 0.002917 | 8.9935e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 791542 | FUSE - ELEMENT/LINK (HV) | Check 1022 KAUNGAROA ROAD, OMS 15556944 is related 2 x 10 2539 wind @1508 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.002917 | 11 | 2017 | 2017-01-19 | C | 3 | 0.002917 | 8.9935e-06
1 | 15550215 | 2017-01-19 13:11 | 2017-01-19 14:25 | 74 | 5 | 370 | 0.0011092 | 0.001064 | 1.4989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781932 | INSULATOR | HV Insulator replaced at pole 781932 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001064 | 11 | 2017 | 2017-01-19 | C | 5 | 0.001064 | 1.4989e-05
1 | 15550725 | 2017-01-19 11:20 | 2017-01-19 11:45 | 25 | 56 | 1400 | 0.004197 | 0.003693 | 0.00016788 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 664 | NONE | Contractor working on CB 4227 in Mangweka. Assumed a tripping during storm conditions and ABS 664 was open (in error) to sectionalise before mistake noticed. Reclosed. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.003693 | 11 | 2017 | 2017-01-19 | C | 56 | 0.003693 | 0.00016788
1 | 15551308 | 2017-01-19 10:44 | 2017-01-19 11:32 | 48 | 6 | 288 | 0.00086338 | 0.000809 | 1.7987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 53 ADMIRAL ROAD | FUSE - ELEMENT/LINK (HV) | Advised ETA 15 mins 3 x 10 7101 1250 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000809 | 11 | 2017 | 2017-01-19 | C | 6 | 0.000809 | 1.7987e-05
1 | 15551476 | 2017-01-19 10:56 | 2017-01-19 14:21 | 204 | 230 | 34773.4 | 0.10425 | 0.10218 | 0.00094133 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733896 | JUMPER | On investigation found jumper blown on ABS 6056 section between ABS 6133 , 5985 & 6087 isolated for repairs and section from ABS 6087 backfed via ABS 5983 for duration of repairs | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.10218 | 11 | 2017 | 2017-01-19 | C | 230 | 0.10218 | 0.00094133
1 | 15552019 | 2017-01-19 20:44 | 2017-01-20 00:35 | 231 | 10 | 2310 | 0.0069251 | 0.006835 | 2.9979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 817503 - DONT TOUCH | CONDUCTOR - REPAIR/REHANG | DONT TOUCH. Check for safety - lines Down (We have been advised this is a lines down, near the Pahaoa Station Homestea) Advised SMC of 999 ( MAB C890 ) line down beyond fuses 7360 ( spur no back feed ) L Grant own isolation & AP to repair 1 x line down at pole 817503. line repaired all service restored Material 4 x meters conductor, 2 x H/V sleeves Times taken from history. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.006835 | 11 | 2017 | 2017-01-19 | C | 10 | 0.006835 | 2.9979e-05
1 | 15552149 | 2017-01-19 11:27 | 2017-01-19 14:12 | 165 | 737 | 91727.1333 | 0.27499 | 0.26836 | 0.0040981 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13536 | INSULATOR | Recloser 9226 Trip. Line patrolled & sectionalised. No Back feed from Sw/Gear 9495/1 due to not working vai SCADA. Resources put into fixing fault. Fault repaired, Fault past sectionaliser 9219, 9219 will need to be DNO'd as it doesn't open DNO 170106. Broken strain insultor at ABS 381 Pole W13536. Strain Insultor replaced. Feeder Relivened. 1 polymer strain insulator used | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.26836 | 11 | 2017 | 2017-01-19 | C | 737 | 0.26836 | 0.0040981
1 | 15552909 | 2017-01-19 11:25 | 2017-01-19 12:02 | 37 | 31 | 1147 | 0.0034385 | 0.003159 | 9.2934e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 721393 | CONDUCTOR - REPAIR/REHANG | During line patrol found floating conductor @ pole 721393 section of line between ABS MA 411 & ABS MA 408 isolated to execute repairs | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003159 | 11 | 2017 | 2017-01-19 | C | 31 | 0.003159 | 9.2934e-05
1 | 15557435 | 2017-01-19 12:18 | 2017-01-19 15:20 | 182 | 6 | 1092 | 0.0032737 | 0.003219 | 1.7987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811104 | CONDUCTOR - REPAIR/REHANG | Isolation required from Fuses 7318 to repair a broken conductor over 2 spans (Storm conditions). 40m Conductor and with 2 sleeves required. Relivened OK. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.003219 | 11 | 2017 | 2017-01-19 | C | 6 | 0.003219 | 1.7987e-05
1 | 15557458 | 2017-01-19 12:20 | 2017-01-19 15:05 | 164 | 2 | 329.5333 | 0.0009879 | 0.000969 | 5.9957e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782936 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp 1 x63amp fuse wind | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000969 | 6.6 | 2017 | 2017-01-19 | C | 2 | 0.000969 | 5.9957e-06
1 | 15559417 | 2017-01-19 13:47 | 2017-01-19 17:25 | 217 | 52 | 11131.0833 | 0.033369 | 0.032901 | 0.00015589 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T12922 | FUSE - ELEMENT/LINK (HV) | 2x25amp HV fuse blown at Transformer TC1900. Fuse reloaded & livened. Unknown cause | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.032901 | 11 | 2017 | 2017-01-19 | C | 52 | 0.032901 | 0.00015589
1 | 15559512 | 2017-01-19 13:52 | 2017-01-19 15:16 | 83 | 117 | 9810.45 | 0.02941 | 0.028358 | 0.00035075 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837614 | NONE | Tripping on CB C936 on Phase A-B OC. (Storm conditions). Line patrlled with a wind blown branch removed from lines at Pole 837614. Relivened OK. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.028358 | 11 | 2017 | 2017-01-19 | C | 117 | 0.028358 | 0.00035075
1 | 15560696 | 2017-01-19 15:16 | 2017-01-19 17:50 | 154 | 7 | 1078 | 0.0032317 | 0.003168 | 2.0985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7241 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses reloade at Fuses 7241. (10A rating). Tree problem in storm | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.003168 | 11 | 2017 | 2017-01-19 | C | 7 | 0.003168 | 2.0985e-05
1 | 15561038 | 2017-01-19 15:48 | 2017-01-19 21:18 | 330 | 186 | 25389.2167 | 0.076113 | 0.07444 | 0.0005576 |  | 22 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 805204 | POLE | Pukepapa CB 1133 tripped on Ph C OC & E/F. Advised control of car vs pole at address: 44146 Porewa, Marton Spoke to Boshia (021 390 228) who advised of car vs pole and her husband advised the pole has broken off at the base and has fallen into the paddock. The car has been pulled off the road but and the driver has been taken to hospital by her husband. Used 1 X Pole 1 X Crossarm 3 X Insulators Etc NDR Number N200080 | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.07444 | 22 | 2017 | 2017-01-19 | C | 186 | 0.07444 | 0.0005576
1 | 15561255 | 2017-01-19 15:51 | 2017-01-20 13:05 | 1274 | 1 | 1274.2667 | 0.0038201 | 0.003811 | 2.9978e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797902 | JUMPER | TUH C926 transformer T2914 has 2 x leads burnt at top of H/V fuses farmer happy for repaires to be carried out in morning. requires back feeding , transformer T2914 H/V fuses open, removed, tag. OMS ref 15563740 | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.003811 | 11 | 2017 | 2017-01-19 | C | 1 | 0.003811 | 2.9978e-06
1 | 15562645 | 2017-01-19 18:00 | 2017-01-19 18:50 | 50 | 27 | 1350 | 0.0040471 | 0.003804 | 8.0942e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 357414 | BINDER | Used 2 X H/T Insulators & Rebound at Pole 357414 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003804 | 11 | 2017 | 2017-01-19 | C | 27 | 0.003804 | 8.0942e-05
1 | 15562671 | 2017-01-19 17:45 | 2017-01-19 18:33 | 48 | 93 | 4464 | 0.013382 | 0.012546 | 0.0002788 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27263 | CROSSARM - WHOLE ASSEMBLY | 1 X H/T Crossarm Complete Insulators Etc | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.012546 | 11 | 2017 | 2017-01-19 | C | 93 | 0.012546 | 0.0002788
1 | 15563042 | 2017-01-19 19:47 | 2017-01-19 21:29 | 101 | 9 | 915 | 0.002743 | 0.002662 | 2.6981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 826205 | FUSE - ELEMENT/LINK (HV) | Check for safety - Tree has fallen and taken down lines, caused a small brush fire. F2229237 - ETA required Advised SMC of 999. ( CLV C834 ) tree in lines at pole 826205, isolation at fuses 7156 ( spur no back feed ) Lines re sagged all service restored Materials 2 x meters conductor, 2 x line clamps NDR No 56601 | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.002662 | 11 | 2017 | 2017-01-19 | C | 9 | 0.002662 | 2.6981e-05
1 | 15563740 | 2017-01-20 10:33 | 2017-01-20 12:27 | 114 | 11 | 1254 | 0.0037593 | 0.00366 | 3.2976e-05 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | transformer T2914 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | ( TUH C926 ) Farmer happy for repair to transformer T2914 to be carried out in morning ( top of H/V fuses burnt off x 2 ) requires back feeds isolation & AP Isolated at ABS 7197 and Links 7342 with a backfeed installed via ABS S544 HV fuse units replaced Used 3 x DDO units complete & 3 x 2 amp fuses | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.00366 | 11 | 2017 | 2017-01-20 | C | 11 | 0.00366 | 3.2976e-05
1 | 15563813 | 2017-01-19 21:50 | 2017-01-20 09:54 | 724 | 76 | 17080.7333 | 0.051206 | 0.050522 | 0.00060557 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838091 | JUMPER | ( AWA C850 ) recloser C281 tripped E/F, L/O, feeder sectionalised with fault isolated to beyond ABS S174. Section of line patrolled beyond ABS S174 with no luck will attend at first light. Difficult area to patrol, off road & bush Line Patroled and blown jumper found at Pole 838091 - Isolated at ABS S174 Jumper repaired no equipment used | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.050522 | 11 | 2017 | 2017-01-19 | C | 76 | 0.050522 | 0.00060557
1 | 15564320 | 2017-01-19 23:15 | 2017-01-20 01:20 | 124 | 20 | 2495 | 0.0074797 | 0.007299 | 5.9957e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 270042 | FUSE - ELEMENT/LINK (HV) | ( PGA 3 ) replace 2 x 10A fuses at fuses SE7 032 & 1 x 3A at fuses SE7 064 Found dead possum at pole 218335 & duck at pole 218324 all service restored | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.007299 | 11 | 2017 | 2017-01-19 | C | 20 | 0.007299 | 5.9957e-05
1 | 15564342 | 2017-01-19 23:36 | 2017-01-20 06:22 | 405 | 1047 | 231044 | 0.69264 | 0.68322 | 0.0031388 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 765626 | POLE | CB 8 Tripped B C Ph O/C Car V Pole Isolated at ABS's 1296, 1268, & 1274 with back feed via VS4771 Pole 765626 replaced, the poles on each side will need replacing on planned shutdown at later date Used 1 x Pole ,1 x HV Cross arm complete, 1 x LV crossarm complete, 1 x double termination arm complete, dead ends and binders for all cross arms Faultman to supply NDR number at later date NDR 30488 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.68322 | 11 | 2017 | 2017-01-19 | C | 1047 | 0.68322 | 0.0031388
1 | 15565979 | 2017-01-19 03:37 | 2017-01-19 04:51 | 74 | 2 | 148 | 0.00044368 | 0.000425 | 5.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 1115 | FUSE - ELEMENT/LINK (HV) | 2 X 3 Amp Fuses Smoking Opossum at Transformer 1115 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000425 | 11 | 2017 | 2017-01-19 | C | 2 | 0.000425 | 5.9957e-06
1 | 15566007 | 2017-01-20 05:03 | 2017-01-20 08:20 | 197 | 420 | 77922 | 0.2336 | 0.22982 | 0.0025182 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 838503 | CONDUCTOR - REPAIR/REHANG | ( TIN CB C937 ) tripped A & B Ph O/C, L/O Branch across the lines at pole 838503, removed by hotstick feeder relivened. Recloser C225 needs protection review. I don't think cold load pick up is enabled, when relivening feeder C225 auto recloses due to inrush. Flag on screen says must have A/R enabled to reliven. Didn't open for fault past this recloser a few minutes later Feeder tripped again A & B Ph O/C, line patrolled before recloser Branch found on lines at pole 838539 cleared using hot sticks Protection review will be done. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.22982 | 11 | 2017 | 2017-01-20 | C | 420 | 0.22982 | 0.0025182
1 | 15568488 | 2017-01-19 16:33 | 2017-01-19 19:10 | 157 | 4 | 628 | 0.0018827 | 0.001846 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | recreation | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.001846 | 11 | 2017 | 2017-01-19 | C | 4 | 0.001846 | 1.1991e-05
1 | 15568773 | 2017-01-20 12:05 | 2017-01-20 12:46 | 41 | 43 | 1763 | 0.0052852 | 0.004898 | 0.00012891 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797459 | JUMPER | Blown Jumper found at Transformer T1503 - cause age Isolated at ABS S562 Used 2 joiners | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.004898 | 11 | 2017 | 2017-01-20 | C | 43 | 0.004898 | 0.00012891
1 | 15569100 | 2017-01-20 09:07 | 2017-01-20 12:59 | 231 | 9 | 2080.2 | 0.0062361 | 0.006155 | 2.698e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 443395 - paper work required | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fusses 7779 - caused by branch contacting lines at Pole 443395 Branch cleared using hot sticks used 2 x 10 amp fuses | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.006155 | 11 | 2017 | 2017-01-20 | C | 9 | 0.006155 | 2.698e-05
1 | 15576761 | 2017-02-09 09:02 | 2017-02-09 12:45 | 223 | 7 | 1561 | 0.0046782 | 0.004615 | 2.0979e-05 | NAPA ID:26162 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | 026162 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228283 | NONE | Replace poles, hardware and conductor. Install TEMP62 Links on pole 228283 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.0023075 | 5.5 | 2017 | 2017-02-09 | B | 7 | 0.004615 | 2.0979e-05
1 | 15577107 | 2017-02-14 09:08 | 2017-02-14 15:12 | 364 | 4 | 1456 | 0.0043633 | 0.004327 | 1.1987e-05 | NAPA ID:24845 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024845 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 2730 | POLE | replace poles 781821, 781823, 781825, 781826, 781827 and remove poles 781822, 781824 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0021635 | 5.5 | 2017 | 2017-02-14 | B | 4 | 0.004327 | 1.1987e-05
1 | 15577134 | 2017-02-10 09:10 | 2017-02-10 15:05 | 355 | 4 | 1420 | 0.0042556 | 0.004219 | 1.1988e-05 | NAPA ID:24843 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024843 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 2730 | NONE | replace poles 781809, 781811, 781812, 781814, 781816, 781817, 781818, 781820, and remove poles 781819 and 781813 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0021095 | 5.5 | 2017 | 2017-02-10 | B | 4 | 0.004219 | 1.1988e-05
1 | 15577160 | 2017-02-15 09:04 | 2017-02-15 15:15 | 371 | 15 | 5565 | 0.016677 | 0.016541 | 4.4951e-05 | NAPA ID:24853 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024853 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace poles 781702, 781704, 781706, 781708, 781712 and replace xarms 781697, 781698, 781699, 781700, 781705, 781707 and 781710 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0082705 | 5.5 | 2017 | 2017-02-15 | B | 15 | 0.016541 | 4.4951e-05
1 | 15577730 | 2017-01-20 18:45 | 2017-01-20 19:38 | 53 | 755 | 40317 | 0.12086 | 0.11407 | 0.0022634 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 713884 | NONE | Car vs pole - opposite Holiday Park, Beach Road. Police onsite #P028217736. Tripping on CB TA2. ABS TA232 Pole hit by car, inspection found no damage. Relivened OK. (Suspect lines clashed due to impact). Awaiting NDR from D.Embling. | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.11407 | 11 | 2017 | 2017-01-20 | C | 755 | 0.11407 | 0.0022634
1 | 15578620 | 2017-01-20 20:45 | 2017-01-20 21:29 | 44 | 357 | 15910.3 | 0.047696 | 0.044485 | 0.0010702 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722886 | DEAD-ENDS | Urgent outage required on South Rd Hawera to replace a broken Dead End (35mm) at ABS 6875. (Noticed by Faultman when travelling past). Isolation from ABS WH297, WH855, Links 8948/6 and Links 6728/6. Dead end replaced and relivened OK. | F1 | GLOVER RD EAST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.044485 | 11 | 2017 | 2017-01-20 | C | 357 | 0.044485 | 0.0010702
1 | 15579181 | 2017-01-20 22:50 | 2017-01-21 01:54 | 184 | 3 | 552 | 0.0016548 | 0.001627 | 8.9934e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5331E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | This is the correct Transformer (OMS 15578498 incorrect location). Transformer 5331E defective, to be changed. Replaced & tested OK. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.001627 | 11 | 2017 | 2017-01-20 | C | 3 | 0.001627 | 8.9934e-06
1 | 15579249 | 2017-01-21 00:53 | 2017-01-21 03:18 | 145 | 334 | 19955.3333 | 0.059822 | 0.056817 | 0.0010013 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 | UNKNOWN | PUT 5 tripped E/F, L/O. Recloser 9665/2 opened & back feed via sectionaliser 9702/2 ( PUT 6 ) Feeder sectionalised with no fault found suspect possum | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.056817 | 11 | 2017 | 2017-01-21 | C | 334 | 0.056817 | 0.0010013
1 | 15581693 | 2017-01-21 15:55 | 2017-01-21 19:35 | 220 | 1 | 220 | 0.00065951 | 0.00065 | 2.9977e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5713 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faulty transformer TC5713 replaced. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.00065 | 11 | 2017 | 2017-01-21 | C | 1 | 0.00065 | 2.9977e-06
1 | 15581725 | 2017-01-21 15:00 | 2017-01-21 18:43 | 223 | 34 | 7591.6333 | 0.022758 | 0.022452 | 0.00010192 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5370 paperwork required | FUSE - ELEMENT/LINK (HV) | **Check to see if OMS 15581808 (356 Tahora Road, Whangamomona) is related ** 2 x 10A HV Fuses at Fuses 5370. Unknown Cause | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.022452 | 11 | 2017 | 2017-01-21 | C | 34 | 0.022452 | 0.00010192
1 | 15581956 | 2017-01-21 20:44 | 2017-01-21 23:25 | 161 | 20 | 3220 | 0.0096529 | 0.009472 | 5.9956e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 839 STATE HIGHWAY 53 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Broken HV fuse base located at pole All fuses require replacing. 2 r requested. Isolations at ABS S509 & S552/1. All supply restored following fuse replacements. | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.009472 | 11 | 2017 | 2017-01-21 | C | 20 | 0.009472 | 5.9956e-05
1 | 15583162 | 2017-01-21 21:40 | 2017-01-22 05:25 | 465 | 15 | 6977 | 0.020916 | 0.02078 | 4.4967e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8421 | FUSE - ELEMENT/LINK (HV) | chased hub 2 x 2A Fuses 8471 and 2 x 10 HV Fuses 8421 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.02078 | 11 | 2017 | 2017-01-21 | C | 15 | 0.02078 | 4.4967e-05
1 | 15583725 | 2017-01-21 22:26 | 2017-01-21 23:07 | 40 | 11613 | 397077.45 | 1.1904 | 1.0859 | 0.034813 |  | 66 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | S12971 | INSULATOR | CB 1092 Kopu tripped. E/F & R Ph zone 1 flags. Supply lost to Whitianga & Coromandel subs. Foot patrolls carried out as much as possible, no issue located. Andrew Wilson approved use of helicopterpatrol once wind and dense cloud clears. Hele patrol located a blown insulator on H structure S12971-S12972. Foot access only due to remote location. All repairs complete. Supply to both restored via 1132 circuit. 1092 left out for line patrol at first light. Fiona, note use of Hele patrol due to remote location of lines | S3 | KOPU1092-KAUAERANGA 66KV | KOPU | Valley | TP_KOPU | Eastern Electricity | POWERCO | 1.0859 | 66 | 2017 | 2017-01-21 | C | 11613 | 1.0859 | 0.034813
1 | 15595397 | 2017-01-21 22:29 | 2017-01-22 02:36 | 246 | 400 | 86012.4667 | 0.25785 | 0.25425 | 0.0011991 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | S12571 | NONE | CB 1 Matatoki tripped to L/O. A & B Ph O/C flags. Line sectionalised & patrolled. Tree branch removed from line at pole S12571 with fuse stick. High winds. All supply restored. | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.25425 | 11 | 2017 | 2017-01-21 | C | 400 | 0.25425 | 0.0011991
1 | 15595867 | 2017-01-22 02:06 | 2017-01-22 04:42 | 156 | 171 | 26676 | 0.079968 | 0.078429 | 0.00051261 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 364 | JUMPER | Sparking Lines. Kerry 0272851025 Fire Comms report that Transformer on Fire but now out. F2230711 Blown jumper repaired at ABS 364 (Load side) Isolation at ABS 364, ABS 9235/1, Links 9235/1 | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.078429 | 11 | 2017 | 2017-01-22 | C | 171 | 0.078429 | 0.00051261
1 | 15595902 | 2017-01-21 23:07 | 2017-01-22 00:23 | 76 | 894 | 36343.9 | 0.10895 | 0.10091 | 0.00268 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | V13147 | NONE | CB 7 tripped to L/O. A & B Ph O/C flags. Line sectionalised & patrolled. Tree branch removed from line at pole V13147. All supply restored. | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.10091 | 11 | 2017 | 2017-01-21 | C | 894 | 0.10091 | 0.00268
1 | 15597700 | 2017-01-21 23:37 | 2017-01-22 00:57 | 79 | 841 | 45241.7 | 0.13562 | 0.12806 | 0.0025211 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB 5 | NONE | CB 5 Coromandel tripped to L/O. A & B Ph O/C flags. Line sectionalised & patrolled. No apparent fault found. All supply restored. High winds. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.12806 | 11 | 2017 | 2017-01-21 | C | 841 | 0.12806 | 0.0025211
1 | 15598873 | 2017-01-21 23:56 | 2017-01-22 06:23 | 387 | 113 | 43791.2667 | 0.13128 | 0.13026 | 0.00033875 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nil | UNKNOWN | RS 513 tripped E/F and L/O. No fault found. Referral job created to X1540 for inspection and testing. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.13026 | 11 | 2017 | 2017-01-21 | C | 113 | 0.13026 | 0.00033875
1 | 15599044 | 2017-01-22 00:29 | 2017-01-22 03:52 | 203 | 13 | 2643.55 | 0.0079247 | 0.007807 | 3.8971e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 778880 | CROSSARM - WHOLE ASSEMBLY | Cb 5 tripped. Damage at FUses ABD 4478 with broken cross arm and suspocted cable damage. Have DNO cable 170109 to get repairs done. Camp on generation, ASW notified Jayson Vinson of issue, Army happy, Shirley to be notified of issue by Jayson. DNO is highest priority. Paul and JO, note temp jumpers installed to get OMS to close out | F1 | CAMP RD | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.007807 | 11 | 2017 | 2017-01-22 | C | 13 | 0.007807 | 3.8971e-05
1 | 15599482 | 2017-01-22 01:05 | 2017-01-22 11:45 | 639 | 240 | 34307.8833 | 0.10285 | 0.10069 | 0.0014149 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 777028 | UNKNOWN | 11kV RS 4232 tripped E/F O/C. Temp line break made at pole 777028. NO customers off. No access to site to ascertain fault cause, made refferal for remainder. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.10069 | 11 | 2017 | 2017-01-22 | C | 240 | 0.10069 | 0.0014149
1 | 15600588 | 2017-01-22 01:41 | 2017-01-22 05:09 | 208 | 772 | 159516.3167 | 0.47819 | 0.47125 | 0.0023143 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 744865 | CONDUCTOR - REPAIR/REHANG | CB U40 tripped and L/O. No flags. Tree branch found on line at pole 744865 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.47125 | 11 | 2017 | 2017-01-22 | C | 772 | 0.47125 | 0.0023143
1 | 15601365 | 2017-01-22 01:45 | 2017-01-22 14:05 | 739 | 874 | 52990.7167 | 0.15885 | 0.15099 | 0.00043467 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | nil | UNKNOWN | 11kV recloser tripped to lock out due to adverse weather. Full patrol carried out, found fuses 2650, 2 x blown fuses. Fuses 405 1x fuse blown, no damage anywhere. Also found automated switch open, loss of comms, Unable to close via SCADA. Closed onsite OK, all power restored. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.15099 | 11 | 2017 | 2017-01-22 | C | 874 | 0.15099 | 0.00043467
1 | 15603368 | 2017-01-22 01:51 | 2017-01-22 12:28 | 636 | 87 | 49255.65 | 0.14766 | 0.14687 | 0.0002608 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 763899 | RECLOSER (HV) | Recloser 5329 Triped O/C L/O. Line patrolled. Trees through line?? | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.14687 | 11 | 2017 | 2017-01-22 | C | 87 | 0.14687 | 0.0002608
1 | 15603883 | 2017-01-22 02:01 | 2017-01-23 12:43 | 2082 | 208 | 139813.7833 | 0.41912 | 0.41725 | 0.00062353 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712418 | CROSSARM - WHOLE ASSEMBLY | 319 Kina Road - shed has blown away pulling line with it. Unsure if customer level or reason for area fault - details passed to Paul | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.41725 | 11 | 2017 | 2017-01-22 | C | 208 | 0.41725 | 0.00062353
1 | 15604533 | 2017-01-22 02:09 | 2017-01-22 07:56 | 346 | 119 | 20797.2167 | 0.062345 | 0.061274 | 0.0006595 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 731173 | CONDUCTOR - REPAIR/REHANG | Recloser 6722 tripped L/O. Line patrolled. Line down located at pole 731172. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.061274 | 11 | 2017 | 2017-01-22 | C | 119 | 0.061274 | 0.0006595
1 | 15605072 | 2017-01-22 02:23 | 2017-01-22 16:11 | 827 | 213 | 127903.9333 | 0.38342 | 0.38151 | 0.00067449 |  | 22 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 843749 | UNKNOWN | 22kV RS 4137 tripped O/C L/O. Nothing found, however dead bird found at pole 843749 which is past Recloser 4251. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.38151 | 22 | 2017 | 2017-01-22 | C | 213 | 0.38151 | 0.00067449
1 | 15606314 | 2017-01-22 01:18 | 2017-01-22 06:44 | 326 | 812 | 124799.6167 | 0.37412 | 0.36681 | 0.0027759 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB7 Tripped. Find Fault. NO FAULT FOUND | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.36681 | 11 | 2017 | 2017-01-22 | C | 812 | 0.36681 | 0.0027759
1 | 15608931 | 2017-01-22 16:13 | 2017-01-22 20:50 | 276 | 3 | 829.65 | 0.0024871 | 0.00246 | 8.9932e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 377093 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse | F1 | AIRPORT DRIVE | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.00246 | 11 | 2017 | 2017-01-22 | C | 3 | 0.00246 | 8.9932e-06
1 | 15609565 | 2017-01-22 07:01 | 2017-01-22 14:33 | 452 | 14 | 6328 | 0.01897 | 0.018843 | 4.1968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704681 | CONDUCTOR - REPAIR/REHANG | Customer called to advise there are actually lines down from pole to house SMC advised of 999. 31/01/2017: ERoad data provided by Downer shows the attending faultman arrived at site: 22/01/2017 06:30. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.018843 | 11 | 2017 | 2017-01-22 | C | 14 | 0.018843 | 4.1968e-05
1 | 15609583 | 2017-01-22 04:10 | 2017-01-22 04:26 | 16 | 159 | 2583.75 | 0.0077454 | 0.006315 | 0.00047664 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006315 | 11 | 2017 | 2017-01-22 | C | 159 | 0.006315 | 0.00047664
1 | 15609749 | 2017-01-22 04:13 | 2017-01-22 15:33 | 680 | 241 | 87271.4667 | 0.26162 | 0.25945 | 0.0020714 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | CB t31 | CONDUCTOR - REPAIR/REHANG | CB T31 tripped. 969 Mangawhero road - pole has been taken out by tree. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.25945 | 11 | 2017 | 2017-01-22 | C | 241 | 0.25945 | 0.0020714
1 | 15609767 | 2017-01-22 04:17 | 2017-01-22 10:47 | 390 | 2 | 780.2667 | 0.002339 | 0.002321 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 800112 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp wind | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.002321 | 11 | 2017 | 2017-01-22 | C | 2 | 0.002321 | 5.9954e-06
1 | 15609782 | 2017-01-22 04:27 | 2017-01-22 10:36 | 369 | 1462 | 336710.1 | 1.0094 | 0.99622 | 0.0043827 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 392028 | NONE | CB8 tripped E/F. Line patrolled and trees located through line at pole 392028. | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.99622 | 11 | 2017 | 2017-01-22 | C | 1462 | 0.99622 | 0.0043827
1 | 15611992 | 2017-01-22 04:29 | 2017-01-22 13:00 | 511 | 307 | 141195.1167 | 0.42327 | 0.4205 | 0.00092031 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 705029 | CONDUCTOR - REPAIR/REHANG | CB PU4 tripped A/B Ph E/F O/C. Line patrolled and floating conductor located at pole 705029. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.4205 | 11 | 2017 | 2017-01-22 | C | 307 | 0.4205 | 0.00092031
1 | 15612301 | 2017-01-22 04:29 | 2017-01-22 13:30 | 540 | 161 | 77606.6 | 0.23264 | 0.2312 | 0.00068648 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 759974 | NONE | 6.6kV CB tripped to lockout. Branch on pole 759974, removed OK. Unable to reclose CB H41, have back fed to H21 circuit. CB H41 DNO 170111 as unable to resolve closing issue. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.2312 | 6.6 | 2017 | 2017-01-22 | C | 161 | 0.2312 | 0.00068648
1 | 15612882 | 2017-01-22 04:36 | 2017-01-22 10:04 | 327 | 271 | 79417.2167 | 0.23807 | 0.23563 | 0.00081239 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P05846 | NONE | Recloser 10002 Tripped L/O O/C A& B Phase. Line patrolled and sectionalised. Branch located on line at pole P05846. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.23563 | 11 | 2017 | 2017-01-22 | C | 271 | 0.23563 | 0.00081239
1 | 15613655 | 2017-01-22 04:49 | 2017-01-22 07:45 | 175 | 4 | 703.8667 | 0.00211 | 0.002074 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12917 | FUSE - ELEMENT/LINK (HV) | 2 x 8 amp wind | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002074 | 11 | 2017 | 2017-01-22 | C | 4 | 0.002074 | 1.1991e-05
1 | 15614167 | 2017-01-22 05:25 | 2017-01-22 10:55 | 329 | 685 | 196646.4167 | 0.58949 | 0.58333 | 0.0020534 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB3 Tripped OC INVT Ground Fault A/B Ph. ONC advised of lines down issue 9:10am. Job complete 10:55 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.58333 | 11 | 2017 | 2017-01-22 | C | 685 | 0.58333 | 0.0020534
1 | 15618083 | 2017-01-22 06:01 | 2017-01-22 11:28 | 326 | 2 | 653.2 | 0.0019581 | 0.00194 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12973 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp outage on child. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.00194 | 11 | 2017 | 2017-01-22 | C | 2 | 0.00194 | 5.9954e-06
1 | 15618517 | 2017-01-22 06:12 | 2017-01-23 13:38 | 1885 | 42 | 27524.1 | 0.08251 | 0.082132 | 0.0001259 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 709454 | CONDUCTOR - REPAIR/REHANG | Trees through lines at multiple sites. Poles 709454, 55 & 56. Pole 709464 NDR Issued N100289 X-arm replaced at Pole 709454 | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.082132 | 11 | 2017 | 2017-01-22 | C | 42 | 0.082132 | 0.0001259
1 | 15618740 | 2017-01-22 06:14 | 2017-01-22 12:13 | 358 | 2 | 717.4667 | 0.0021508 | 0.002132 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H1700 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp Fuses at FP580 due to wind | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.002132 | 11 | 2017 | 2017-01-22 | C | 2 | 0.002132 | 5.9954e-06
1 | 15619725 | 2017-01-22 07:52 | 2017-01-22 12:04 | 252 | 42 | 10584 | 0.031728 | 0.03135 | 0.0001259 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8410 | CONDUCTOR - REPAIR/REHANG | Advised SMC and control of 999 when closing please check OMS 15614106 15622381 and 15608169 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.03135 | 11 | 2017 | 2017-01-22 | C | 42 | 0.03135 | 0.0001259
1 | 15619759 | 2017-01-22 02:56 | 2017-01-22 20:08 | 1032 | 21 | 21676.5333 | 0.064981 | 0.064791 | 6.2952e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 791796 | CROSSARM - WHOLE ASSEMBLY | Fuses 1611 open as part of earlier fault (paperwork missing Jo) Replaced x-arm at pole 791796, NDR 047310 as was done by owners tree. Note also found 2x fuses 2691 blown, replaced those as well | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.064791 | 11 | 2017 | 2017-01-22 | C | 21 | 0.064791 | 6.2952e-05
1 | 15620594 | 2017-01-22 07:10 | 2017-01-22 08:10 | 59 | 741 | 39434.5833 | 0.11821 | 0.11155 | 0.0022213 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 389425 | CONDUCTOR - REPAIR/REHANG | at 07:10, Atuaroa Sub, CB 2 No. 3 Rd Feeder, Tripped, A B C O/C, E/F, L/O. Faultmen dispatched & investigation began. Feeder patrolled / sectionalised. Found branch on line at Pole 389425. Removed with hot stick. All Power Restored on Completion. Dennis Ngatai Attended. No Materials Used. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.11155 | 11 | 2017 | 2017-01-22 | C | 741 | 0.11155 | 0.0022213
1 | 15622215 | 2017-01-22 07:18 | 2017-01-23 13:00 | 1782 | 3 | 5346 | 0.016026 | 0.015998 | 8.9932e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712483 | FUSE - ELEMENT/LINK (HV) | 23/1 12.25pm tried to call customer to see if their power is restored, but phone number for customer is wrong. 2 x 3A HV Fuses replaced at Fuses NG307 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.015998 | 11 | 2017 | 2017-01-22 | C | 3 | 0.015998 | 8.9932e-06
1 | 15622220 | 2017-01-22 07:20 | 2017-01-22 11:15 | 234 | 1 | 234.9833 | 0.00070442 | 0.000695 | 2.9977e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | feeder fault | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.000695 | 11 | 2017 | 2017-01-22 | C | 1 | 0.000695 | 2.9977e-06
1 | 15622502 | 2017-01-22 07:43 | 2017-01-22 09:26 | 102 | 169 | 16268.8667 | 0.04877 | 0.047249 | 0.00050662 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 224199 | CONDUCTOR - REPAIR/REHANG | at 07:43, Paengaroa Sub, CB 1 Gulliver Rd Feeder, Recloser 9460, Tripped, O/C, L/O. Faultmen dispatched & investigation began. Sectionalised / Patrolled lines. Found branch on line at Pole 224199 - removed with hot stick. All Power Restored on Completion. Steve Doran Attended. No Materials Used. | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.047249 | 11 | 2017 | 2017-01-22 | C | 169 | 0.047249 | 0.00050662
1 | 15623924 | 2017-01-22 08:01 | 2017-01-22 12:30 | 269 | 129 | 11425.4 | 0.03425 | 0.03309 | 0.00038671 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 231049 | CONDUCTOR - REPAIR/REHANG | at 07:57, Pongakawa Sub, CB 4 Old Coach Rd Feeder, Sectionaliser 9875, Tripped, Ph A B C O/C, L/O. Faultmen dispatched & investigation began. Feeder sectionalised / patrolled. Found lines down at Pole 231049. Isolated lines at Fuses SG7-001. Permit issued & repairs carried out. All Power Restored on Completion. Dennis Ngatai Attended. 2x Links and 9m of conductor replaced - 1 phase, less than 1 span. NDR: TBA | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.03309 | 11 | 2017 | 2017-01-22 | C | 129 | 0.03309 | 0.00038671
1 | 15624540 | 2017-01-22 09:30 | 2017-01-22 11:50 | 140 | 22 | 3080 | 0.009233 | 0.009035 | 6.595e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 757310 | CONDUCTOR - REPAIR/REHANG | Lines down across road on fence. Approx 2.3km from main road Mrs Zeiltjes 067524064 Advised SMC of 999 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.009035 | 11 | 2017 | 2017-01-22 | C | 22 | 0.009035 | 6.595e-05
1 | 15624601 | 2017-01-22 10:44 | 2017-01-22 10:56 | 11 | 43 | 508.1167 | 0.0015232 | 0.001136 | 0.0001289 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 218165 | CONDUCTOR - REPAIR/REHANG | at 10:18, Paengaroa Sub, CB 1 Gulliver Rd Feeder. Faultman was dispatched to a tree branch in lines. Faultman requested line be de-energised to cut branch away from lines with hot stick. Switching carried out to reconfigure network to de-energise lines: Closed ABS SE6-032, Opened ABS SE6-083. De-energised lines at Recloser 9460: Opened at 10:44, Closed at 10:55. Branch cut away and removed. All OK. No Materials Used. Jackson Achillies Attended. Could not get pole number from pole - closest pole: 218165 Tanker driver advised that there is a branch on the lines outside Bill West Contractors which is near the golfcourse Richard 073047074 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001136 | 11 | 2017 | 2017-01-22 | C | 43 | 0.001136 | 0.0001289
1 | 15625080 | 2017-01-22 08:25 | 2017-01-22 13:25 | 300 | 2 | 600.4667 | 0.0018 | 0.001782 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 269751 | FUSE - ELEMENT/LINK (HV) | 2x 2amp Fuses at TP1875 due to wind. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001782 | 11 | 2017 | 2017-01-22 | C | 2 | 0.001782 | 5.9954e-06
1 | 15625188 | 2017-01-22 08:38 | 2017-01-22 17:55 | 557 | 11 | 1198.5333 | 0.0035929 | 0.003493 | 3.2975e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 846233 | FUSE - ELEMENT/LINK (HV) | LV to HV email sent 5:18pm - Fuse WH140 - Check 115 Muggeridge Rd (OMS 15626430) - 167 Muggeridge Road (OMS 15639400) - 138 GEARY ROAD (OMS 15635824) - 71 MANAWAPOU ROAD (OMS 15636922) 2 x 10amp fuses replaced at 17:55 RT :572 | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.003493 | 11 | 2017 | 2017-01-22 | C | 11 | 0.003493 | 3.2975e-05
1 | 15625433 | 2017-01-22 08:41 | 2017-01-22 16:01 | 439 | 8 | 3516.5333 | 0.010542 | 0.010469 | 2.3982e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 737941 | CONDUCTOR - REPAIR/REHANG | CB 6551 Tripped L/O All phases. Line patrolled. Isolation made at ABS Line repaired at pole 737941. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.010469 | 6.6 | 2017 | 2017-01-22 | C | 8 | 0.010469 | 2.3982e-05
1 | 15625840 | 2017-01-22 13:03 | 2017-01-22 14:05 | 62 | 41 | 2542 | 0.0076202 | 0.007251 | 0.00012291 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-519 | FUSE - ELEMENT/LINK (HV) | at 13:03, Tauranga GXP, CB 15 Cameron Rd Feeder. Faultman dispatched to no power / part powers. Found 1x HV Fuse Blown at Links Box SD4-362/L1. Isolated Lines at Fuses SD4-161. Permit issued & fuse replaced. All Power Restored on Completion. 1x 20A HRC HV Fuse Replaced. Link Box Feeding Transforming TD4-519. Check 16 BURNS STREET, OMS 15627253 and 9 ST GEORGE STREET, OMS 15627501 is related Crew replacement requested as current crew is tech and not able to deal with HV TX issue. Switch SD4-362 | F3 | CAMERON RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.007251 | 11 | 2017 | 2017-01-22 | C | 41 | 0.007251 | 0.00012291
1 | 15625894 | 2017-01-22 09:15 | 2017-01-22 15:52 | 397 | 8 | 3177.0667 | 0.009524 | 0.009452 | 2.3982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | h0257 | FUSE - ELEMENT/LINK (HV) | fc804 2 x 6amp wind | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.009452 | 11 | 2017 | 2017-01-22 | C | 8 | 0.009452 | 2.3982e-05
1 | 15626070 | 2017-01-22 07:34 | 2017-01-22 20:46 | 791 | 147 | 110085.3333 | 0.33001 | 0.32868 | 0.00044067 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ?? | FUSE - ELEMENT/LINK (HV) | Cut a line break at 779962 due to lines down. to be fixed later. Note also had 2x blown fuses at Temp 02 site, also fixed as part of this, resolved a number of jobs | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.32868 | 11 | 2017 | 2017-01-22 | C | 147 | 0.32868 | 0.00044067
1 | 15626781 | 2017-01-22 10:15 | 2017-01-22 18:57 | 522 | 7 | 3658.9 | 0.010968 | 0.010905 | 2.0984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 776332 | FUSE - ELEMENT/LINK (HV) | sent to ONC for follow up 24/1 sent to hub 3 x 3amp 1500 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.010905 | 11 | 2017 | 2017-01-22 | C | 7 | 0.010905 | 2.0984e-05
1 | 15627509 | 2017-01-22 11:56 | 2017-01-23 21:03 | 1987 | 32 | 62144 | 0.18629 | 0.186 | 9.5927e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738505 | CONDUCTOR - REPAIR/REHANG | Please check oms 15628164 before completing 2.49pm emailed svs hub for update Trees through lines found at Pole 738505 Isolated at Fuses 6130 Trees cleared and lines repaired Used 40 mtrs conductor & 12 sleeves | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.186 | 11 | 2017 | 2017-01-22 | C | 32 | 0.186 | 9.5927e-05
1 | 15628227 | 2017-01-22 10:59 | 2017-01-22 18:20 | 440 | 3 | 1322.9 | 0.0039657 | 0.003938 | 8.9932e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 782712 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 8A fuse | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.003938 | 6.6 | 2017 | 2017-01-22 | C | 3 | 0.003938 | 8.9932e-06
1 | 15630238 | 2017-01-22 07:12 | 2017-01-22 17:05 | 593 | 68 | 40331.9333 | 0.1209 | 0.12029 | 0.00020385 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762573 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 20A fuse | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.12029 | 11 | 2017 | 2017-01-22 | C | 68 | 0.12029 | 0.00020385
1 | 15630529 | 2017-01-22 11:29 | 2017-01-22 14:44 | 195 | 2 | 390.5667 | 0.0011708 | 0.001152 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 715659 | FUSE - ELEMENT/LINK (HV) | 2x6amp Fuses at TA1410 due to wind | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001152 | 11 | 2017 | 2017-01-22 | C | 2 | 0.001152 | 5.9954e-06
1 | 15630595 | 2017-01-22 11:21 | 2017-01-22 14:38 | 197 | 1029 | 170389.25 | 0.51078 | 0.50153 | 0.0040859 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND |  | UNKNOWN | CB 7 tripped B & C Phase O/C - Line Patrolled. No cause of fault noted. | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.50153 | 11 | 2017 | 2017-01-22 | C | 1029 | 0.50153 | 0.0040859
1 | 15632132 | 2017-01-22 12:14 | 2017-01-22 18:59 | 404 | 682 | 197751.8333 | 0.59281 | 0.58667 | 0.007983 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P36909 | RECLOSER (HV) |  | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.58667 | 11 | 2017 | 2017-01-22 | C | 682 | 0.58667 | 0.007983
1 | 15633576 | 2017-01-22 12:33 | 2017-01-22 16:30 | 237 | 92 | 18380.0167 | 0.055098 | 0.054271 | 0.00029678 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | N0293 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | at 12:31, Paeroa Sub, CB 5 Bennett St Feeder, Sectionaliser 9380, Tripped, No Flags, L/O. Faultmen dispatched & investigation began. Found tree branch on line at Pole N0293. Removed with hot stick. Closed 9380 at 15:27. After closing, found 1x Blown HV Fuse at FC848. Isolated Lines at FP837. Reloaded, Relivened 1x 10A HV Fuse at FC848 at 16:22. Relivened Lines at FP837 at 16:30. All Power Restored on Completion. James Brier Attended. No Materials Used. Check - did this included 730 MARATOTO ROAD, PAEROA (OMS 15625107) - if so please advise SMC | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.054271 | 11 | 2017 | 2017-01-22 | C | 92 | 0.054271 | 0.00029678
1 | 15634734 | 2017-01-22 12:44 | 2017-01-22 20:25 | 460 | 214 | 41804.2 | 0.12532 | 0.12339 | 0.001265 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 746585 | INSULATOR | Replace strain insulator at ABS 548 on pole 746585 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.12339 | 11 | 2017 | 2017-01-22 | C | 214 | 0.12339 | 0.001265
1 | 15635829 | 2017-01-22 12:59 | 2017-01-22 16:07 | 188 | 1079 | 23533.4333 | 0.070547 | 0.060843 | 0.0034774 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P42172 | CONDUCTOR - REPAIR/REHANG | NDR: 52556, due to trees | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.060843 | 11 | 2017 | 2017-01-22 | C | 1079 | 0.060843 | 0.0034774
1 | 15637364 | 2017-01-22 19:13 | 2017-01-22 20:14 | 61 | 92 | 5612 | 0.016823 | 0.015995 | 0.00027579 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1660 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faulty transformer T1660 replaced. While closing HV fuses following replacement, 1 x HV fuses base broke. Line isolated at ABS S319, 11090/1, links 11090/4 T4034 & T673 (both with DG's). All 3 fuses bases were changed due to condition. All supply restored. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.015995 | 11 | 2017 | 2017-01-22 | C | 92 | 0.015995 | 0.00027579
1 | 15637773 | 2017-01-22 13:34 | 2017-01-22 13:48 | 13 | 70 | 945 | 0.0028329 | 0.002203 | 0.00020984 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | H21 trip closed after 13 mins | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.002203 | 6.6 | 2017 | 2017-01-22 | C | 70 | 0.002203 | 0.00020984
1 | 15638057 | 2017-01-22 13:49 | 2017-01-22 17:24 | 215 | 114 | 14820.8 | 0.044429 | 0.043403 | 0.00084536 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 738170 | BINDER |  | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.043403 | 11 | 2017 | 2017-01-22 | C | 114 | 0.043403 | 0.00084536
1 | 15638228 | 2017-01-22 20:24 | 2017-01-22 21:19 | 55 | 6 | 330 | 0.00098925 | 0.000935 | 1.7986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p23150 | BINDER | Broken HV binder. ISOLATED BY FUSES l38 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000935 | 11 | 2017 | 2017-01-22 | C | 6 | 0.000935 | 1.7986e-05
1 | 15638490 | 2017-01-22 15:47 | 2017-01-22 16:30 | 42 | 19 | 811.6167 | 0.002433 | 0.002262 | 5.6957e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727053 | CONDUCTOR - REPAIR/REHANG | 11kV line down at pole 727053. Materials Used: 8m line 3 sleeves | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.002262 | 11 | 2017 | 2017-01-22 | C | 19 | 0.002262 | 5.6957e-05
1 | 15639123 | 2017-01-22 13:40 | 2017-01-22 18:35 | 295 | 31 | 9146.55 | 0.027419 | 0.02714 | 9.293e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764777 | FUSE - ELEMENT/LINK (HV) | Paul Cooper Replaced 2 x 10A fuse Les also responded to his 1r | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.02714 | 11 | 2017 | 2017-01-22 | C | 31 | 0.02714 | 9.293e-05
1 | 15639187 | 2017-01-22 18:30 | 2017-01-23 12:46 | 1096 | 6 | 6576 | 0.019713 | 0.019659 | 1.7986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 796648 | CONDUCTOR - REPAIR/REHANG | Tree through lines past fuses 461, to remain off over night. Requires line crew to make repairs on Monday, 2 R issued line repaired @ pole 796648 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.019659 | 11 | 2017 | 2017-01-22 | C | 6 | 0.019659 | 1.7986e-05
1 | 15639216 | 2017-01-22 17:30 | 2017-01-22 18:50 | 80 | 84 | 6685 | 0.02004 | 0.019284 | 0.00025181 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 365465 | CONDUCTOR - REPAIR/REHANG | Outage required btn ABS 446 & Gas/Sw 12001 to repair lines down. (Duty NC advises part power - one line down). Materials Used: 2 x sleeved, 16m conductor, 3m x binder | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.019284 | 11 | 2017 | 2017-01-22 | C | 84 | 0.019284 | 0.00025181
1 | 15639436 | 2017-01-22 14:43 | 2017-01-22 20:10 | 326 | 5 | 1634.75 | 0.0049006 | 0.004855 | 1.4989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 724975 | FUSE - ELEMENT/LINK (HV) | Lines patrolled and replace 3 x 8A fuses | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.004855 | 11 | 2017 | 2017-01-22 | C | 5 | 0.004855 | 1.4989e-05
1 | 15639755 | 2017-01-22 15:06 | 2017-01-22 23:15 | 489 | 2 | 978.6 | 0.0029336 | 0.002915 | 5.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 772370 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 4146 - cause weather Used 2 x 3 amp fuses | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.002915 | 11 | 2017 | 2017-01-22 | C | 2 | 0.002915 | 5.9954e-06
1 | 15639952 | 2017-01-22 15:16 | 2017-01-23 12:30 | 1274 | 27 | 34403.4 | 0.10313 | 0.10289 | 8.0939e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763879 | CONDUCTOR - REPAIR/REHANG | Fuses 5193 found with 2 x blown fuses, dropped out the third until line patrol can be conducted. Repaired Damaged Line at Pole Own AP issued to Bruce Meeks Isolate at fuses 5193. Earth at Pole 763879 Used 1 x Sleev and Re-sag. 2 x HV Fuses Restore time 12:30 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.10289 | 11 | 2017 | 2017-01-22 | C | 27 | 0.10289 | 8.0939e-05
1 | 15642484 | 2017-01-22 10:08 | 2017-01-22 16:47 | 398 | 12 | 4784 | 0.014341 | 0.014233 | 3.5973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 712186 | BINDER | Repair a floating conductor at pole 712186. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.014233 | 11 | 2017 | 2017-01-22 | C | 12 | 0.014233 | 3.5973e-05
1 | 15642912 | 2017-01-22 16:02 | 2017-01-23 15:23 | 1401 | 1 | 1401 | 0.0041998 | 0.00419 | 2.9977e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W5248 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer W5248 Blown. To be Replaced. Transformer Replaced | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.00419 | 11 | 2017 | 2017-01-22 | C | 1 | 0.00419 | 2.9977e-06
1 | 15643437 | 2017-01-22 16:13 | 2017-01-22 19:14 | 180 | 230 | 22766.4833 | 0.068248 | 0.066179 | 0.00085435 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | nil | UNKNOWN | CB 1 tripped Locked out. Patrolled, sectionaslised, no fault found, very windy at the time, suspect debris or line clash | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.066179 | 11 | 2017 | 2017-01-22 | C | 230 | 0.066179 | 0.00085435
1 | 15647139 | 2017-01-22 16:37 | 2017-01-23 16:45 | 1447 | 5 | 7239.6667 | 0.021703 | 0.021657 | 1.4989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 786222 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 3A fuse weather | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.021657 | 11 | 2017 | 2017-01-22 | C | 5 | 0.021657 | 1.4989e-05
1 | 15647196 | 2017-01-23 14:11 | 2017-01-23 20:29 | 378 | 107 | 16591.95 | 0.049738 | 0.048775 | 0.00032075 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771820 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | transformer X432 blown and to be replaced tomorrow generators provided for the night Transformer X432 replaced under own AP Used 1 x 50 kVA 3 Ph transformer | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.048775 | 11 | 2017 | 2017-01-23 | C | 107 | 0.048775 | 0.00032075
1 | 15648251 | 2017-01-22 13:40 | 2017-01-22 18:35 | 295 | 1 | 295.05 | 0.00088448 | 0.000875 | 2.9977e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Paul Cooper Replaced 2 x 10A fuse. Part of job 15639123. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000875 | 11 | 2017 | 2017-01-22 | C | 1 | 0.000875 | 2.9977e-06
1 | 15648315 | 2017-01-22 15:52 | 2017-01-23 20:36 | 1724 | 4 | 3077.5833 | 0.0092258 | 0.009189 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 849422 | CONDUCTOR - REPAIR/REHANG | HV lines on deck past Fuses 7876 on TIN-C937-Castlepoint fdr, ASW Lines down at pole 849422 repaired. Isolation at fuses 7876. Tree through line. NDR to be provided by Downer. 10 metres 16mm Cu conductor, 6 joint sleeves, 4 connectors materials used. All supply restored. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.009189 | 11 | 2017 | 2017-01-22 | C | 4 | 0.009189 | 1.1991e-05
1 | 15649114 | 2017-01-22 10:55 | 2017-01-22 17:45 | 409 | 18 | 7373.1 | 0.022103 | 0.02194 | 5.3959e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | S12759 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuse | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.02194 | 11 | 2017 | 2017-01-22 | C | 18 | 0.02194 | 5.3959e-05
1 | 15649776 | 2017-01-22 18:34 | 2017-01-22 20:45 | 131 | 1 | 131.4167 | 0.00039395 | 0.000384 | 2.9977e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 763839 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000384 | 11 | 2017 | 2017-01-22 | C | 1 | 0.000384 | 2.9977e-06
1 | 15650472 | 2017-01-23 10:05 | 2017-01-23 11:35 | 90 | 2 | 180 | 0.00053958 | 0.000521 | 5.9953e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715584 | CROSSARM - WHOLE ASSEMBLY | Crossarm complete replaced at Pole 715584 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000521 | 11 | 2017 | 2017-01-23 | C | 2 | 0.000521 | 5.9953e-06
1 | 15650645 | 2017-01-22 19:14 | 2017-01-22 20:17 | 63 | 6 | 380.3 | 0.00114 | 0.001086 | 1.7986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 727801 | CONDUCTOR - REPAIR/REHANG | Isolation at transformer L4025 to enable Temp repairs to be made to neutral line. will need to return later for permanent repairs. Follow up job created (15652051) | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.001086 | 11 | 2017 | 2017-01-22 | C | 6 | 0.001086 | 1.7986e-05
1 | 15651249 | 2017-01-22 04:06 | 2017-01-22 21:26 | 1040 | 35 | 36400.5833 | 0.10912 | 0.1088 | 0.00010492 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12510 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Broken fuse holder at T8/377. Replace 1 x fuse carrier | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.1088 | 11 | 2017 | 2017-01-22 | C | 35 | 0.1088 | 0.00010492
1 | 15651392 | 2017-01-22 20:00 | 2017-01-23 11:23 | 923 | 2 | 1846 | 0.0055338 | 0.005515 | 5.9954e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3290 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | X-arm replaced at Pole 712667 Transformer N3290 Faulty and Replaced. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.005515 | 11 | 2017 | 2017-01-22 | C | 2 | 0.005515 | 5.9954e-06
1 | 15651396 | 2017-01-22 19:55 | 2017-01-23 18:00 | 1325 | 130 | 40880.6333 | 0.12255 | 0.12138 | 0.00077941 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/A | UNKNOWN | Line patrol done up to fuses 762 & 2524 refer OMS 15652922 fo completion | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.12138 | 11 | 2017 | 2017-01-22 | C | 130 | 0.12138 | 0.00077941
1 | 15651792 | 2017-01-22 20:18 | 2017-01-22 20:32 | 14 | 49 | 686 | 0.0020564 | 0.001615 | 0.00014689 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 753222 | JUMPER | Repairs to LV jumpers at Transformer due to flash over | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001615 | 11 | 2017 | 2017-01-22 | C | 49 | 0.001615 | 0.00014689
1 | 15652525 | 2017-01-22 20:54 | 2017-01-22 21:58 | 63 | 302 | 19257.5333 | 0.057729 | 0.055013 | 0.00090532 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P48240 | JUMPER | LOS to ALF Sub due to Blown jumper on Fuses I10 at T1. Replaced one jumper NOte a lot of requests made on individual jobs, butr all canceled or rejected due to all being associated with the blown jumper, ASW | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.055013 | 33 | 2017 | 2017-01-22 | C | 302 | 0.055013 | 0.00090532
1 | 15657330 | 2017-01-22 18:54 | 2017-01-23 11:50 | 1016 | 65 | 26837.3833 | 0.080451 | 0.079866 | 0.00022483 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P02618 | INSULATOR | Replace 2 x Insulators on Pole P02618 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.079866 | 11 | 2017 | 2017-01-22 | C | 65 | 0.079866 | 0.00022483
1 | 15658052 | 2017-01-23 01:59 | 2017-01-23 14:55 | 776 | 2 | 1552.5667 | 0.0046541 | 0.004636 | 5.9953e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719107 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Please check oms 15672608 - FM confirmed that 225 Taikatu is affected by outage TX: T5450 needs to be replaced FM confirmed 216 and 225 Taikatu are affected and have spoken to customers. Currently still without power. Pole: 719107 24/1 9.30am emailed svs hub for update Transformer replaced | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.004636 | 11 | 2017 | 2017-01-23 | C | 2 | 0.004636 | 5.9953e-06
1 | 15658113 | 2017-01-23 05:54 | 2017-01-23 06:49 | 54 | 830 | 39693.6 | 0.11899 | 0.11152 | 0.0024881 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | RECLOSER (HV) | REcloser 4770 Tripped E/F O/C. Line sectionalised and patrolled. Supply restored with no obvious cause found. | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.11152 | 11 | 2017 | 2017-01-23 | C | 830 | 0.11152 | 0.0024881
1 | 15659174 | 2017-01-22 05:18 | 2017-01-22 10:55 | 337 | 4 | 1348 | 0.0040409 | 0.004004 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 715435 | CONDUCTOR - REPAIR/REHANG | Has advised that there is a line down which runs from the power on the road to another power pole which is located on the property The line is down on the road outside the cowshed There are no sparks or smoke coming from the line Customer requests this be attended to asap as once the area goes live again this will cause problems Also requests a call to advise time frame of someone attending - is scared to sleep while this line is down Andy Collins 027 435 6187 - Retailer called this morning following up about this job Note: had to enter this job as site inspection as OMS 15628256 has been verified tap - advising scada dressing issue no outage. 6.45am advised Joanne at svs hub & emailed - Advised Murray in control See Also OMS #'s 15609757, 15628256 & 15630204 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.004004 | 11 | 2017 | 2017-01-22 | C | 4 | 0.004004 | 1.1991e-05
1 | 15659199 | 2017-01-23 06:58 | 2017-01-23 13:30 | 392 | 1 | 392.1167 | 0.0011754 | 0.001166 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 712527 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuse | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.001166 | 11 | 2017 | 2017-01-23 | C | 1 | 0.001166 | 2.9976e-06
1 | 15659214 | 2017-01-23 07:01 | 2017-01-23 10:00 | 178 | 7 | 1249.9667 | 0.003747 | 0.003684 | 2.0984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S0708 | FUSE - ELEMENT/LINK (HV) | 2 x 10amp and 2 holder outage at fuses wouldn't verify but all ICP accounted for in outage | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.003684 | 11 | 2017 | 2017-01-23 | C | 7 | 0.003684 | 2.0984e-05
1 | 15659272 | 2017-01-23 07:14 | 2017-01-23 13:00 | 345 | 11 | 3801.7833 | 0.011397 | 0.011297 | 3.2975e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P26465 | FUSE - ELEMENT/LINK (HV) | Please check oms 15661312, 15666167 Advised Svs hub of lv to hv update & emailed & advised control Reload at Fuses I8 2 x 8A Fuses Weather | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.011297 | 11 | 2017 | 2017-01-23 | C | 11 | 0.011297 | 3.2975e-05
1 | 15659395 | 2017-01-23 07:31 | 2017-01-23 13:35 | 363 | 2 | 727.5333 | 0.0021809 | 0.002162 | 5.9953e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 773724 | FUSE - ELEMENT/LINK (HV) | Reload 1 x 5A Fuse At Transformer X81 Weather | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002162 | 11 | 2017 | 2017-01-23 | C | 2 | 0.002162 | 5.9953e-06
1 | 15659613 | 2017-01-23 07:58 | 2017-01-23 10:07 | 129 | 830 | 82534.5 | 0.24741 | 0.23995 | 0.0024881 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB4770 E/F Trip Line patrolled nothing found | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.23995 | 11 | 2017 | 2017-01-23 | C | 830 | 0.23995 | 0.0024881
1 | 15660884 | 2017-01-23 15:08 | 2017-01-23 20:28 | 320 | 685 | 21974.1833 | 0.065872 | 0.059711 | 0.0020954 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734752 | INSULATOR | 33kV CB 2782 tripped E/F to lock out due to high winds. 33kV Line needs patrolling to find possible fault. URGENT Damaged 33 kV insulator found at Pole 734752 Isolated at ABS's (33kV 353 353, 526, 525 &, 6767) 11kV 5803, 5761 &, 5776) Used 1 x 33kV Insulator) | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.059711 | 11 | 2017 | 2017-01-23 | C | 685 | 0.059711 | 0.0020954
1 | 15660931 | 2017-01-23 08:18 | 2017-01-23 11:20 | 182 | 74 | 13410.3 | 0.0402 | 0.039534 | 0.00022183 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/gear 2056/4 | NONE | 11kV CB 8 tripped to lock out no flags on SCADA (Field reported C phase E/F) Switching to locate fault issue encountered operational issues with CB 8 not closing via SCADA with control fail indications. Later ascertained CB was closing, NOC SCADA team investigating issue. Suspected cable fault between Sw/gear 2056/4 and HAT Sub CB 6 (as this the open point between feeders) DNO 170112. DNO to manage cable testing etc | F2 | TAUPO 1 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.039534 | 11 | 2017 | 2017-01-23 | C | 74 | 0.039534 | 0.00022183
1 | 15661208 | 2017-01-22 18:34 | 2017-01-23 10:50 | 976 | 14 | 13669.8333 | 0.040979 | 0.040852 | 4.1968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01225 | FUSE - ELEMENT/LINK (HV) | h106 1 x10 h108 2 x 6amp | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.040852 | 11 | 2017 | 2017-01-22 | C | 14 | 0.040852 | 4.1968e-05
1 | 15661481 | 2017-01-23 08:47 | 2017-01-23 14:30 | 342 | 1 | 342.7 | 0.0010273 | 0.001018 | 2.9976e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 712790 | CABLE - REPLACE LESS THAN 5 METRES | HV Cable re-attached at Pole 712790 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001018 | 11 | 2017 | 2017-01-23 | C | 1 | 0.001018 | 2.9976e-06
1 | 15661604 | 2017-01-23 14:39 | 2017-01-23 17:52 | 192 | 35 | 6723.5 | 0.020155 | 0.01984 | 0.00010492 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P29733 | POLE | advised Joanne at svs hub & emailed & advised control Pole P29733 replaced and relocated further up the hill on closing ABS S33 insulator broke DNO 170114 applied | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.01984 | 11 | 2017 | 2017-01-23 | C | 35 | 0.01984 | 0.00010492
1 | 15665577 | 2017-01-23 10:59 | 2017-01-23 13:45 | 165 | 112 | 18575.2 | 0.055683 | 0.054675 | 0.00033574 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44243 | JUMPER | 11.06am called svs hub and advised about job. section of line between ABS A93 & A94 Isolated to repair blown jumper @ pole P44243 ballance of line backfed via ABS B39 for duration of repairs Please check OMS 15665744 is related? No | F1 | DAIRYFACT | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.054675 | 11 | 2017 | 2017-01-23 | C | 112 | 0.054675 | 0.00033574
1 | 15665739 | 2017-01-23 11:06 | 2017-01-23 16:57 | 350 | 3 | 1051.6 | 0.0031524 | 0.003125 | 8.993e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | L63 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse at Fuses L63. Not shown in eMap | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.003125 | 11 | 2017 | 2017-01-23 | C | 3 | 0.003125 | 8.993e-06
1 | 15666081 | 2017-01-23 05:23 | 2017-01-23 11:15 | 351 | 17 | 2715.7167 | 0.0081409 | 0.007987 | 5.0961e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P28577 | FUSE - ELEMENT/LINK (HV) | 2 x10 @I44 wind | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.007987 | 11 | 2017 | 2017-01-23 | C | 17 | 0.007987 | 5.0961e-05
1 | 15666227 | 2017-02-22 09:31 | 2017-02-22 14:49 | 318 | 149 | 604 | 0.0018098 | 0.00047 | 5.9927e-06 | NAPA ID:26196 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | 026196 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TF7-083 | NONE | Replace poles, hardware and conductor. Works location: Rotoehu Rd. WO 30019161 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000235 | 5.5 | 2017 | 2017-02-22 | B | 149 | 0.00047 | 5.9927e-06
1 | 15668024 | 2017-02-14 08:35 | 2017-02-14 14:22 | 347 | 9 | 3123 | 0.0093588 | 0.009277 | 2.6971e-05 | NAPA ID:27328 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 027328 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 772414 | NONE | Replace five 11kv defect poles 2 x two poles structures, poles 772414, 772415 red tagged poles. Works location: Breamore Rd, Waverley. WO 30027707 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0046385 | 5.5 | 2017 | 2017-02-14 | B | 9 | 0.009277 | 2.6971e-05
1 | 15668039 | 2017-01-23 12:05 | 2017-01-24 13:50 | 1544 | 6 | 9267.3 | 0.027781 | 0.027726 | 1.7986e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736387 | CROSSARM - WHOLE ASSEMBLY | Broken crossarm at Pole 736393. Cannot be fixed tonight. Lines isolated at Fuses 6029. Will be fixed tomorrow. X-arm replaced at Pole 736387 | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.027726 | 6.6 | 2017 | 2017-01-23 | C | 6 | 0.027726 | 1.7986e-05
1 | 15670504 | 2017-02-09 09:04 | 2017-02-09 14:23 | 319 | 3 | 957 | 0.0028681 | 0.002841 | 8.9908e-06 | NAPA ID:27349 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 027349 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC4077 | NONE | Carry out maintenance on lines/poles from FC4077. Works location: Paeroa-Kopu Rd, Puriri. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.0014205 | 5.5 | 2017 | 2017-02-09 | B | 3 | 0.002841 | 8.9908e-06
1 | 15670580 | 2017-02-01 10:00 | 2017-02-01 13:34 | 214 | 46 | 9844 | 0.029505 | 0.029091 | 0.00013788 | NAPA ID:28337 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028337 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | move pole 745110 away from bank edge and install a set of temporary 11KV knife links onto pole 742986 Temporary fuse number TEMP85 . Note rewrite of switching 27554 to include installation of temp links 85 . This outage has been advertised under NAPA 27554 . | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.014545 | 5.5 | 2017 | 2017-02-01 | B | 46 | 0.029091 | 0.00013788
1 | 15670644 | 2017-02-09 09:17 | 2017-02-09 14:42 | 325 | 3 | 975 | 0.002922 | 0.002895 | 8.9908e-06 | NAPA ID:27541 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 027541 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O13308 | NONE | Replace pole O13308 using live-line techniques and then replace transformer structure TC2659 on the new pole. Works location: Canal West Rd, Thames. WO 30036726 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0014475 | 5.5 | 2017 | 2017-02-09 | B | 3 | 0.002895 | 8.9908e-06
1 | 15670699 | 2017-01-23 12:29 | 2017-01-23 15:52 | 202 | 406 | 36140.9667 | 0.10834 | 0.10469 | 0.0012171 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | FC1487 | CONDUCTOR - REPAIR/REHANG | CB 3 Trip. E/F. L/O. Half of Feeder backfed from PKO CB6 up to Recloser RC26. Rest of feeder sectionalised fault found to have been caused by wind blown debris beyond fuses FC1487. Debris had blown away from lines and feeder relivened OK. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.10469 | 11 | 2017 | 2017-01-23 | C | 406 | 0.10469 | 0.0012171
1 | 15672160 | 2017-01-23 12:41 | 2017-01-23 16:10 | 209 | 1 | 209 | 0.00062652 | 0.000617 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2203 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses Replaced at Fuses 2203. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000617 | 11 | 2017 | 2017-01-23 | C | 1 | 0.000617 | 2.9976e-06
1 | 15672990 | 2017-01-23 20:52 | 2017-01-23 21:55 | 63 | 1 | 63 | 0.00018885 | 0.000179 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737105 | JUMPER | Check 50A ROTOKARE ROAD, OMS 15686955 is related and 5 other no powers Burnt off jumper found at fuses 6039 Isolated at Fuses 6051 Used 1 x sleeve | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000179 | 11 | 2017 | 2017-01-23 | C | 1 | 0.000179 | 2.9976e-06
1 | 15673283 | 2017-01-23 14:05 | 2017-01-23 21:09 | 424 | 1204 | 112169.25 | 0.33625 | 0.32542 | 0.0036092 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 216060 | POLE | 676 Pyes Pa road, tree has bought down line F2231862 - ETA required Fire advised were 15 mins away CB 13003 was back feeding CB 13004 for NAPA 27005 CB 13003 also had a LLP 27839 Isolated between ABS IP634, S4732 & SE3-019. backfeed rest of area Repaired lines down caused by tree & relivened Materials: 3x Crossarm+Whole assembly, 1x Pole, 3x HV Fuses & Carriers 8A, 3x Binders, 3x Jumpers. NDR: TBA lane cook advised he has left site. | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.32542 | 11 | 2017 | 2017-01-23 | C | 1204 | 0.32542 | 0.0036092
1 | 15684972 | 2017-02-09 09:00 | 2017-02-09 12:33 | 213 | 24 | 5112 | 0.01532 | 0.015104 | 7.1927e-05 | NAPA ID:28177 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028177 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.007552 | 5.5 | 2017 | 2017-02-09 | B | 24 | 0.015104 | 7.1927e-05
1 | 15685051 | 2017-02-13 08:35 | 2017-02-13 14:08 | 333 | 24 | 7992 | 0.02395 | 0.023734 | 7.1923e-05 | NAPA ID:28179 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028179 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.011867 | 5.5 | 2017 | 2017-02-13 | B | 24 | 0.023734 | 7.1923e-05
1 | 15685154 | 2017-02-21 08:45 | 2017-02-21 14:24 | 339 | 24 | 8136 | 0.024379 | 0.024163 | 7.1915e-05 | NAPA ID:28181 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028181 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012082 | 5.5 | 2017 | 2017-02-21 | B | 24 | 0.024163 | 7.1915e-05
1 | 15685218 | 2017-02-23 09:15 | 2017-02-23 15:18 | 363 | 24 | 8712 | 0.026104 | 0.025888 | 7.1912e-05 | NAPA ID:28182 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028182 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012944 | 5.5 | 2017 | 2017-02-23 | B | 24 | 0.025888 | 7.1912e-05
1 | 15685267 | 2017-02-28 08:34 | 2017-02-28 14:34 | 360 | 24 | 8640 | 0.025887 | 0.02567 | 7.1907e-05 | NAPA ID:28184 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028184 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.012835 | 5.5 | 2017 | 2017-02-28 | B | 24 | 0.02567 | 7.1907e-05
1 | 15686178 | 2017-01-23 15:16 | 2017-01-23 19:50 | 274 | 1 | 274.2 | 0.00082197 | 0.000812 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 792230 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp HT fuses x2002 wind 792230 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000812 | 11 | 2017 | 2017-01-23 | C | 1 | 0.000812 | 2.9976e-06
1 | 15686525 | 2017-01-23 15:43 | 2017-01-23 16:40 | 56 | 3 | 170.95 | 0.00051246 | 0.000485 | 8.993e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8471 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses Replaced at Fuses 8471 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000485 | 11 | 2017 | 2017-01-23 | C | 3 | 0.000485 | 8.993e-06
1 | 15686583 | 2017-01-23 21:48 | 2017-01-23 22:12 | 24 | 30 | 720 | 0.0021583 | 0.001888 | 8.9931e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733076 | UNKNOWN | Crossarm found swinging free at Pole 733076 Isolated at Fuses 6266 Used 1 x bolt, washer & nut | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.001888 | 11 | 2017 | 2017-01-23 | C | 30 | 0.001888 | 8.9931e-05
1 | 15687390 | 2017-01-23 15:47 | 2017-01-23 19:45 | 237 | 14 | 3331.3 | 0.0099862 | 0.00986 | 4.1968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P00603 | BINDER | Floating Conduct found at pole - cause weather Isolated at Fuses H108 Used 2 metres binder wire & 2 x 15 amp fuses | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.00986 | 11 | 2017 | 2017-01-23 | C | 14 | 0.00986 | 4.1968e-05
1 | 15687736 | 2017-01-23 17:15 | 2017-01-23 19:33 | 138 | 4 | 552 | 0.0016547 | 0.001618 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 263 UPPER GLENN ROAD | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer 5320E due to LV lines down LV lines made safe and to repaired at a later date refer OMS 15686264 Used 3 x 2amp fuses and 1 x carrier | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001618 | 11 | 2017 | 2017-01-23 | C | 4 | 0.001618 | 1.1991e-05
1 | 15689688 | 2017-01-23 20:40 | 2017-01-24 01:18 | 278 | 316 | 40010.2 | 0.11994 | 0.1171 | 0.00094727 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 36240 | CONDUCTOR - REPAIR/REHANG | CB 23 Tripped E/F Tree through lines found at pole 36240 Isolated at ABS B16 Used 60 metres of conductor, 4 x sleeves NDR # N300278 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.1171 | 11 | 2017 | 2017-01-23 | C | 316 | 0.1171 | 0.00094727
1 | 15690707 | 2017-01-24 04:47 | 2017-01-24 05:39 | 51 | 66 | 3408.9 | 0.010219 | 0.009625 | 0.00019784 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36019 | JUMPER | Broken Jumper found at Pole P36019 - cause Isolated at ABS B16 Used 1 x Quick lug 2 metres of conductor | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.009625 | 11 | 2017 | 2017-01-24 | C | 66 | 0.009625 | 0.00019784
1 | 15691164 | 2017-01-23 17:27 | 2017-01-23 19:49 | 142 | 4 | 568 | 0.0017027 | 0.001666 | 1.1991e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843704 | FUSE - ELEMENT/LINK (HV) | recreation | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.001666 | 11 | 2017 | 2017-01-23 | C | 4 | 0.001666 | 1.1991e-05
1 | 15691220 | 2017-01-24 07:23 | 2017-01-24 09:18 | 114 | 10 | 1149.8333 | 0.0034468 | 0.003356 | 2.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792300 | FUSE - ELEMENT/LINK (HV) | 7.44am advised Joanne at svs hub of upgrade from LV to HV fault Please check oms 15691329 & 15691351 4607 2 x 6amp cow | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.003356 | 11 | 2017 | 2017-01-24 | C | 10 | 0.003356 | 2.9976e-05
1 | 15693819 | 2017-01-26 08:10 | 2017-01-26 10:07 | 117 | 108 | 12636 | 0.037877 | 0.036906 | 0.00032374 | NAPA ID:28371 TP_BUNNYTHORPE GXP > KEITH ST SUB > KEITH ST 23 | 11 | Planned | 028371 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | G240C | NONE | Carry out repairs to RM6 G240C earth switch. Spring found to be incorrect position, refitted ok | F3 | KEITH ST 23 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.018453 | 5.5 | 2017 | 2017-01-26 | B | 108 | 0.036906 | 0.00032374
1 | 15694134 | 2017-01-24 12:01 | 2017-01-24 13:15 | 74 | 39 | 2886 | 0.0086512 | 0.0083 | 0.00011691 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5450 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Emergency Isolation for safety to replace Transformer T5450 Damaged during Storm. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.0083 | 11 | 2017 | 2017-01-24 | C | 39 | 0.0083 | 0.00011691
1 | 15694644 | 2017-02-10 09:00 | 2017-02-10 13:57 | 297 | 13 | 3861 | 0.011571 | 0.011454 | 3.896e-05 | NAPA ID:27342 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027342 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP448 | NONE | Switching to provide Backfeed to IP448 & OPEN. Apply Cover-Up to Live side of TEMP09. Reconductor between Pole Structures 857893/857894 and T13172/T1613 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.005727 | 5.5 | 2017 | 2017-02-10 | B | 13 | 0.011454 | 3.896e-05
1 | 15695205 | 2017-01-24 11:06 | 2017-01-24 14:50 | 224 | 10 | 2240 | 0.0067147 | 0.006624 | 2.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 779935 | POLE | Cut a line break at 779962 due to lines down. to be fixed later. Note also had 2x blown fuses at Temp 02 site, also fixed as part of this, resolved a number of jobs | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.006624 | 11 | 2017 | 2017-01-24 | C | 10 | 0.006624 | 2.9976e-05
1 | 15695680 | 2017-01-27 09:04 | 2017-01-27 14:46 | 342 | 3 | 1010 | 0.0030275 | 0.003 | 8.9925e-06 | NAPA ID:28381 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 028381 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 836013 | POLE | 1: Create 11kV Line Break at pole 836103. 2: AP to replace poles and Crossarms. 3: Close 11kV Line break at pole 836103. NEW switching due to LLP for Temp ABS istall not successful. This replaces switching 26031. Advertings under NAPA 26031. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0015 | 5.5 | 2017 | 2017-01-27 | B | 3 | 0.003 | 8.9925e-06
1 | 15696614 | 2017-01-24 20:09 | 2017-01-24 23:41 | 212 | 1 | 212.2833 | 0.00063635 | 0.000627 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P34009 | CONDUCTOR - REPAIR/REHANG | Report of Line Down at Pole P34009. Isolated at Sw/Gear 373. As well as line down 3x jumpers had blown. Repaired using 5mtrs of flounder conductor, 3x full tension compression sleeves, 1x polymer, 1x thimble, 1x flounder conductor joint, & 2x cu to ali conductor joints. Caused by duck hitting lines. CB 9 at Manawatu Beef Packers Sub was also found to be tripped after the lines had been repaired. Relivened ok. | F2 | WORKS | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000627 | 11 | 2017 | 2017-01-24 | C | 1 | 0.000627 | 2.9976e-06
1 | 15697337 | 2017-02-13 09:30 | 2017-02-13 12:22 | 172 | 2 | 344 | 0.0010309 | 0.001012 | 5.9935e-06 | NAPA ID:27845 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 027845 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | o13983 | NONE | RECONFIGURE LV XARMS AND TRANSF AT TC3903, REPLACE LV XARMS AT O3428, INSTALL 2 X GROUND STAYS AND RESTRAIN LV TO RESOLVE CLEARANCE ISSUES. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000506 | 5.5 | 2017 | 2017-02-13 | B | 2 | 0.001012 | 5.9935e-06
1 | 15702725 | 2017-01-25 09:32 | 2017-01-25 11:33 | 120 | 10 | 1205.6667 | 0.0036141 | 0.003524 | 2.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P09331 | FUSE - ELEMENT/LINK (HV) | Reload at fues I26 2 x 6A Wind | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003524 | 11 | 2017 | 2017-01-25 | C | 10 | 0.003524 | 2.9976e-05
1 | 15709646 | 2017-02-14 08:55 | 2017-02-14 15:39 | 404 | 18 | 7272 | 0.021792 | 0.02163 | 5.3941e-05 | NAPA ID:27360 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 027360 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S0450 | NONE | Replace 11kV Pole S0450 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.010815 | 5.5 | 2017 | 2017-02-14 | B | 18 | 0.02163 | 5.3941e-05
1 | 15709884 | 2017-01-25 14:33 | 2017-01-25 17:13 | 160 | 254 | 3882 | 0.011637 | 0.009352 | 0.00076139 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7214 | JUMPER | Safety Manager 699552. Just Put back in top of fuse | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.009352 | 11 | 2017 | 2017-01-25 | C | 254 | 0.009352 | 0.00076139
1 | 15709928 | 2017-01-25 12:32 | 2017-01-25 14:23 | 111 | 130 | 13216.8333 | 0.039619 | 0.038449 | 0.00038969 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781437 | JUMPER | Recloser 573 Trip E/F found conductor close to steel crossarm at pole 781437 repositioned conductor with hot stick | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.038449 | 11 | 2017 | 2017-01-25 | C | 130 | 0.038449 | 0.00038969
1 | 15710078 | 2017-01-25 12:36 | 2017-01-25 15:00 | 143 | 241 | 14407.3667 | 0.043188 | 0.04102 | 0.00072242 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730454 | INSULATOR | Broken Insulator found at Pole 730454. Insulator Replaced. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.04102 | 11 | 2017 | 2017-01-25 | C | 241 | 0.04102 | 0.00072242
1 | 15710739 | 2017-02-08 11:57 | 2017-02-08 15:07 | 190 | 12 | 216 | 0.00064735 | 0.000539 | 7.1928e-05 | NAPA ID:27689 TP_MANGAMAIRE GXP > MANGAMUTU SUB | 11 | Planned | 027689 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | p12740 | NONE | Capital works to connect new U/G cable at new pole where T15 was which is connected to new switch 10350/3, live line line break closed at T7/451 to liven 10350/3 then liven 10333. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0002695 | 5.5 | 2017 | 2017-02-08 | B | 12 | 0.000539 | 7.1928e-05
1 | 15710786 | 2017-01-25 12:52 | 2017-01-25 15:20 | 147 | 2 | 295.5 | 0.00088579 | 0.000867 | 5.9952e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5707 | FUSE - ELEMENT/LINK (HV) | 2 x 2A HV Fuses replaced at Fuses 5707 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000867 | 11 | 2017 | 2017-01-25 | C | 2 | 0.000867 | 5.9952e-06
1 | 15710832 | 2017-01-25 13:01 | 2017-01-25 14:55 | 113 | 231 | 20918.4667 | 0.062705 | 0.060627 | 0.00069245 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | H21 | UNKNOWN | Motukawa CB H21 tripped E/F and L/O. Sectionalised and no fault found. | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.060627 | 6.6 | 2017 | 2017-01-25 | C | 231 | 0.060627 | 0.00069245
1 | 15713108 | 2017-02-24 09:35 | 2017-02-24 11:15 | 100 | 1 | 100 | 0.00029963 | 0.00029 | 2.9963e-06 | NAPA ID:28408 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 028408 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | tc2534 | NONE | Replace 11kV P/M Transformer TC2534 (30.11.3). | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000145 | 5.5 | 2017 | 2017-02-24 | B | 1 | 0.00029 | 2.9963e-06
1 | 15731371 | 2017-01-25 14:25 | 2017-01-25 15:49 | 83 | 10 | 837.1667 | 0.0025095 | 0.002419 | 2.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p09331 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp 1549 i26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.002419 | 11 | 2017 | 2017-01-25 | C | 10 | 0.002419 | 2.9976e-05
1 | 15733386 | 2017-01-25 15:21 | 2017-01-25 18:00 | 159 | 238 | 4458.3333 | 0.013364 | 0.011224 | 0.00071343 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P43252 | INSULATOR | Kairanga CB11 Tripped on E/F. 1 insulator and 1 binder replaced at pole P43252. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.011224 | 11 | 2017 | 2017-01-25 | C | 238 | 0.011224 | 0.00071343
1 | 15737497 | 2017-01-25 15:42 | 2017-01-25 18:03 | 140 | 1 | 140.8333 | 0.00042216 | 0.000413 | 2.9976e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2298 KAHUTARA ROAD, FEATHERSTON | UNKNOWN | NNF - part of earlier fault in the area | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000413 | 11 | 2017 | 2017-01-25 | C | 1 | 0.000413 | 2.9976e-06
1 | 15742601 | 2017-01-25 15:48 | 2017-01-25 18:26 | 158 | 241 | 20965.05 | 0.062845 | 0.060677 | 0.00072242 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB6 | UNKNOWN | CB 6 Tripped E/F O/C. and L/O | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.060677 | 11 | 2017 | 2017-01-25 | C | 241 | 0.060677 | 0.00072242
1 | 15743355 | 2017-01-25 15:51 | 2017-01-25 16:44 | 52 | 830 | 43796.3333 | 0.13128 | 0.12382 | 0.002488 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | REC 4770 Tripped E/F Line patrolled nothing found | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.12382 | 11 | 2017 | 2017-01-25 | C | 830 | 0.12382 | 0.002488
1 | 15744724 | 2017-01-26 09:09 | 2017-01-26 14:40 | 331 | 34 | 11254 | 0.033735 | 0.033428 | 0.00010192 | NAPA ID:28426 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 028426 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9377 | NONE | Replace poles,hardware and conductor. Install | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.016714 | 5.5 | 2017 | 2017-01-26 | B | 34 | 0.033428 | 0.00010192
1 | 15745604 | 2017-01-25 16:58 | 2017-01-25 20:04 | 186 | 111 | 7580.3 | 0.022723 | 0.021724 | 0.00044964 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P08303 | INSULATOR | RS K45 A/R, L/O, O/C B Phase. Sectionalised & patrolled with floating conductor found at Pole P08303. Work area isolated & back feed installed via MABS N34. Repaired using 1x 11kV pin & Insulator, & 2mtrs of Ali Binder | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.021724 | 11 | 2017 | 2017-01-25 | C | 111 | 0.021724 | 0.00044964
1 | 15746007 | 2017-01-25 17:05 | 2017-01-25 21:40 | 275 | 44 | 12110.2667 | 0.036302 | 0.035906 | 0.00013189 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 15745938 | FUSE - ELEMENT/LINK (HV) | Patrolled line nothing found. Replaced 2 x 10 HT fuses at 7570 | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.035906 | 11 | 2017 | 2017-01-25 | C | 44 | 0.035906 | 0.00013189
1 | 15747112 | 2017-01-25 17:53 | 2017-01-25 20:12 | 138 | 357 | 28242.65 | 0.08466 | 0.081449 | 0.0010701 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | k2331 | INSULATOR | CB 1 L/O on E/F sectionalised and then reported cross arm on fire near pole K13010. Isolated at ABS 2534, replaced 2 faulty insulators on pole K2331. relivened | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.081449 | 11 | 2017 | 2017-01-25 | C | 357 | 0.081449 | 0.0010701
1 | 15747622 | 2017-01-25 18:08 | 2017-01-25 19:38 | 90 | 830 | 36762.9 | 0.1102 | 0.10274 | 0.002488 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 706438 | INSULATOR | RS 4770 A/R, L/O, E/F. Feeder sectionalised & patrolled with broken insulator found. Work area isolated & back feed installed via SS4771. Repaired using 1x 11kV pin & insulator, & 1x Ali Binder | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.10274 | 11 | 2017 | 2017-01-25 | C | 830 | 0.10274 | 0.002488
1 | 15749572 | 2017-01-25 19:09 | 2017-01-25 20:58 | 109 | 10 | 1091.5 | 0.0032719 | 0.003181 | 2.9976e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | See OMS 15748994 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003181 | 11 | 2017 | 2017-01-25 | C | 10 | 0.003181 | 2.9976e-05
1 | 15749689 | 2017-01-25 16:39 | 2017-01-26 21:20 | 1721 | 6 | 10326.3 | 0.030954 | 0.0309 | 1.7986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | N48 | FUSE - ELEMENT/LINK (HV) | Replaced 1x 6Amp HV Fuse Link. See OMS 15744808 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.0309 | 11 | 2017 | 2017-01-25 | C | 6 | 0.0309 | 1.7986e-05
1 | 15750432 | 2017-01-26 05:19 | 2017-01-26 07:38 | 139 | 5 | 696.25 | 0.0020871 | 0.002042 | 1.4988e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 267475 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp @ FP 893 2 x 6amp @ TC1402 due to possum | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.002042 | 11 | 2017 | 2017-01-26 | C | 5 | 0.002042 | 1.4988e-05
1 | 15762272 | 2017-02-16 09:06 | 2017-02-16 14:51 | 345 | 4 | 1380 | 0.0041354 | 0.004099 | 1.1987e-05 | NAPA ID:24854 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024854 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 781816 | NONE | Reconductor from pole 781816 to 781827 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0020495 | 5.5 | 2017 | 2017-02-16 | B | 4 | 0.004099 | 1.1987e-05
1 | 15762295 | 2017-02-17 09:04 | 2017-02-17 15:04 | 360 | 15 | 5400 | 0.016182 | 0.016046 | 4.4949e-05 | NAPA ID:24855 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024855 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 781721 | NONE | Replace poles 781721, 781726, 781745, 781744, 781743, 781742, 781741, 781740, 781739, 781738, 781746 and 781737 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.008023 | 5.5 | 2017 | 2017-02-17 | B | 15 | 0.016046 | 4.4949e-05
1 | 15762396 | 2017-02-24 09:00 | 2017-02-24 14:28 | 328 | 15 | 4920 | 0.014742 | 0.014607 | 4.4945e-05 | NAPA ID:24872 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024872 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 781706 | NONE | Run new conductor from fuses 708 to pole 781706 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0073035 | 5.5 | 2017 | 2017-02-24 | B | 15 | 0.014607 | 4.4945e-05
1 | 15762693 | 2017-01-26 08:07 | 2017-01-26 10:21 | 133 | 47 | 4332.7667 | 0.012988 | 0.012565 | 0.00014089 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 843653 | NONE | Recloser CB2811 tripped on Phase A-B. Area patrolled with tree poblem found at Pole 843653. (Defected by Faultman). Restored OK but problem is ongoing. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.012565 | 11 | 2017 | 2017-01-26 | C | 47 | 0.012565 | 0.00014089
1 | 15764235 | 2017-02-09 08:30 | 2017-02-09 15:12 | 402 | 10 | 4020 | 0.012048 | 0.011957 | 2.997e-05 | NAPA ID:27298 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11 | Planned | 027298 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 795971 | POLE | replace rusty iron rail poles , 7 sites , one red tag iron rail pole 795971 Omatane south rd. Control advise that under switching the earth fault detection for Recloser 4227/2 & 4199/2 can be disabled then close in the loop at 11kV ABS 1217 then open fuses 636. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0059785 | 5.5 | 2017 | 2017-02-09 | B | 10 | 0.011957 | 2.997e-05
1 | 15765249 | 2017-01-26 15:01 | 2017-01-26 16:49 | 108 | 14 | 1512 | 0.0045323 | 0.004406 | 4.1966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | W1320 | CONDUCTOR - REPAIR/REHANG | check for safety - lines down on road, pulled down by truck and trailer between Coroglen and Tairua Whitianga Rd . ( WHT4 ) Emergency switching to repair line down x 1 ( fuse blown at fuses FC4086 ) Isolation at fuses FC4086 ( spur no back feeds ) Line repaired all service restored Materials 10 meters conductor, 2 x H/V sleeves, 1 x 15A H/V fuse NDR No to follow | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.004406 | 11 | 2017 | 2017-01-26 | C | 14 | 0.004406 | 4.1966e-05
1 | 15765742 | 2017-01-26 15:09 | 2017-01-26 17:34 | 144 | 1 | 144.3333 | 0.00043265 | 0.000423 | 2.9975e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5440E | UNKNOWN | NNF - Full power upon arrival. FM checked the network and also the meter and couldn't see any issues. Believes it was part of the feeder fault earlier on today | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000423 | 11 | 2017 | 2017-01-26 | C | 1 | 0.000423 | 2.9975e-06
1 | 15766667 | 2017-02-22 09:05 | 2017-02-22 15:10 | 365 | 15 | 5475 | 0.016405 | 0.01627 | 4.4946e-05 | NAPA ID:24870 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024870 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 781736 | NONE | Replace poles 781736, 781735, 781734, 781732, 781731, 781730, 781728 and replace xarms 844595, 781733, 781749, 781748, 842369, 359165, 781723, 781722, 781720, 781719, 781717, 781716, 781715. Works location; Brewer Rd. WO 30017731 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.008135 | 5.5 | 2017 | 2017-02-22 | B | 15 | 0.01627 | 4.4946e-05
1 | 15766715 | 2017-02-16 09:30 | 2017-02-16 14:20 | 290 | 22 | 6380 | 0.019119 | 0.01892 | 6.5926e-05 | NAPA ID:27283 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 027283 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses R44 | NONE | To replace red tagged pole (GP). Works location: Ridge Rd Central. WO 30034861 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.00946 | 5.5 | 2017 | 2017-02-16 | B | 22 | 0.01892 | 6.5926e-05
1 | 15766721 | 2017-02-17 09:42 | 2017-02-17 13:49 | 247 | 71 | 13049 | 0.039103 | 0.038464 | 0.00021276 | NAPA ID:27630 TP_MANGAMAIRE GXP > MANGAMUTU SUB > RUAWHATA | 11 | Planned | 027630 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P16451 | NONE | To replace red tagged pole #P16451. Works location: Waituna Rd, Pahiatua. WO 30033512 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.019232 | 5.5 | 2017 | 2017-02-17 | B | 71 | 0.038464 | 0.00021276
1 | 15766748 | 2017-02-20 09:00 | 2017-02-20 15:20 | 380 | 3 | 1140 | 0.003416 | 0.003389 | 8.9894e-06 | NAPA ID:27775 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027775 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7700 | POLE | replace 11kv poles and hardware | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0016945 | 5.5 | 2017 | 2017-02-20 | B | 3 | 0.003389 | 8.9894e-06
1 | 15766773 | 2017-01-27 01:45 | 2017-01-27 02:21 | 36 | 563 | 20643.3333 | 0.061879 | 0.056816 | 0.0016876 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | CB 856 L/O on O/C | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.056816 | 11 | 2017 | 2017-01-27 | C | 563 | 0.056816 | 0.0016876
1 | 15767687 | 2017-01-27 06:44 | 2017-01-27 12:22 | 338 | 120 | 31065.3333 | 0.093119 | 0.092039 | 0.0004796 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04955 | INSULATOR | Tripping on recloser V27 on Phase A, EF. Isolation required beyond ABS V35 (Conductor off insulator). 6 Insulators replaced at Pole P04955. Restored OK. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.092039 | 11 | 2017 | 2017-01-27 | C | 120 | 0.092039 | 0.0004796
1 | 15768233 | 2017-01-27 07:41 | 2017-01-27 08:04 | 22 | 3003 | 44812.7333 | 0.13433 | 0.10732 | 0.0090016 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | TAQ & BCH Subs | NONE | Tripping on WGN GXP CB2232 (Phase B O/C, EF) and Taupo Quay 33kV CB222 (Phase B OC, EF) causing loss of supply to Beach Rd and Taupo Quay Subs. Beach Rd Sub transferred to BRK GXP and Taupo Quay backfed from Hatricks Sub via 11kV Cable tie. Patrol carried out but nothing found. (Suspect bird). All restored OK. Further intensive patrol to be carried out. | F1 | IMLAY | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 0.10732 | 11 | 2017 | 2017-01-27 | C | 3003 | 0.10732 | 0.0090016
1 | 15771425 | 2017-02-14 10:23 | 2017-02-14 14:45 | 262 | 5 | 1310 | 0.0039257 | 0.00388 | 1.4984e-05 | NAPA ID:28417 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 028417 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC472 | NONE | Upgrade 11kV LV Xarm from Wood to Steel at P/M Transformer TC472. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.00194 | 5.5 | 2017 | 2017-02-14 | B | 5 | 0.00388 | 1.4984e-05
1 | 15771566 | 2017-02-15 08:45 | 2017-02-18 10:35 | 4429 | 10 | 1608.3333 | 0.0048197 | 0.004729 | 5.9934e-05 | NAPA ID:27526 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 027526 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829054 | NONE | make 11kv line breaks at poles 829054,829055,829056 and 829077,829078 to make outage area between poles 829054 and 829078 replace multiple poles and cross arms and then re-instate line breaks | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.0023645 | 5.5 | 2017 | 2017-02-15 | B | 10 | 0.004729 | 5.9934e-05
1 | 15772767 | 2017-01-27 11:25 | 2017-01-27 12:14 | 48 | 218 | 7897.3833 | 0.023673 | 0.021712 | 0.00065346 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | R11 | UNKNOWN | line sectionalised and supply restored with no apparent fault found suspect bird strike | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.021712 | 11 | 2017 | 2017-01-27 | C | 218 | 0.021712 | 0.00065346
1 | 15773552 | 2017-02-15 06:00 | 2017-02-15 16:29 | 628 | 54 | 1727.1 | 0.0051756 | 0.00469 | 0.00032364 | NAPA ID:24380 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV | 11 | Planned | 024380 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-SV1 | NONE | Switching only - Install Backfeed and off-load TX TD4-SV1 LLP 1. Install line break at pole 203309 & restore to TD4-SV1 LLP 2. Install line break at pole & 203316 AP. Replace 11kV pole 860399 and connect new 185mm 11kV cable to O/H line (connect to new RMU 13114/1) LLP 3. Close line break at pole 203316 and liven to 13114/1 Check Rotation at 13141/1 LLP 4. Open fuses SD4-684 & Close line break at pole 203309 & restore to TD4-SV1. | F3 | GATE PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002345 | 5.5 | 2017 | 2017-02-15 | B | 54 | 0.00469 | 0.00032364
1 | 15774957 | 2017-01-27 14:07 | 2017-01-27 17:40 | 213 | 11 | 2343 | 0.0070232 | 0.006924 | 3.2973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | C734 | POLE | Tree on lines, customer has no power 13.36 Caller called back and said the pole has snapped holding these lines. Notified SMC. Removed trees and replaced pole C734 and associated hardware | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.006924 | 11 | 2017 | 2017-01-27 | C | 11 | 0.006924 | 3.2973e-05
1 | 15775027 | 2017-02-15 09:00 | 2017-02-15 13:32 | 272 | 1 | 272 | 0.0008151 | 0.000806 | 2.9967e-06 | NAPA ID:27371 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 027371 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Otamakite Rd, Puriri | NONE | Install Stay insulators on Single Wire line | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000403 | 5.5 | 2017 | 2017-02-15 | B | 1 | 0.000806 | 2.9967e-06
1 | 15776316 | 2017-01-27 13:03 | 2017-01-27 16:50 | 226 | 316 | 23185.9167 | 0.0695 | 0.066658 | 0.00094722 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P35122 | CONDUCTOR - REPAIR/REHANG | Initiial AR at 13:03, crew requested to patrol lines. Further AR's, rang SMC to ask when crew would be assigned and told they would follow it up with local depot. After several more AR's called SMC again and asked them to escalate to FRM and was told they had done this but no one was available to patrol 15:03 CB 23 tripped 15:27 Crew contact NC from depot for instruction Feeder patrolled and broken HT lead found at Transformer T1/260. Isolation required between ABS B11 and B13 with backfeed at ABS 10194. Conductor joined and one 3A HT Transformer fuse replaced | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.066658 | 11 | 2017 | 2017-01-27 | C | 316 | 0.066658 | 0.00094722
1 | 15776879 | 2017-01-27 16:45 | 2017-01-28 12:20 | 1175 | 57 | 3135.25 | 0.009398 | 0.008885 | 0.00017086 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798748 | POLE | fire coms called for ETA - called Cindy she advised 35mins. ( FEA C916 ) Isolation of faulty pole at Fuses 7272 ( no back feeds ) Left isolated and earthed overnight, requires digger transformer feeds only pump customer advised Line isolated at fuses 7272 and pole replaced on 28/01/17. Main line between ABS S505, C634/1, Links C634/6 isolated after pole replacement to repair HV jumper out of bottom of fuse. All supply restored on completion. 1 x busck pole, 1 x donut, 1 x crossarm, 3 x HV pins & insulators & binder materials required. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.008885 | 11 | 2017 | 2017-01-27 | C | 57 | 0.008885 | 0.00017086
1 | 15777275 | 2017-01-27 17:41 | 2017-01-27 19:44 | 122 | 4 | 488.8 | 0.0014652 | 0.001429 | 1.199e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 078 | FUSE - ELEMENT/LINK (HV) | 2 X 8 amp HT Fuses at Fuses 078 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001429 | 11 | 2017 | 2017-01-27 | C | 4 | 0.001429 | 1.199e-05
1 | 15777400 | 2017-01-27 18:33 | 2017-01-28 15:11 | 1238 | 10 | 1518 | 0.0045502 | 0.00446 | 5.6953e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | at 14:02, Alfredton Sub, CB I23 Brooklands Feeder. Line was patrolled after recent fuses blowing at Fuses I26. Found broken conductor at Pole P27920. Isolated Lines at Fuses I26. Permit issued & repairs carried out. All Power Restored on completion. Guy Herbert Attended. 2x Connectors Used. Conductor is old and aged - apparently there is a job to have this conductor all replaced. 2 X 6 Amp HT Fuses at I26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00446 | 11 | 2017 | 2017-01-27 | C | 10 | 0.00446 | 5.6953e-05
1 | 15779167 | 2017-01-28 02:58 | 2017-01-28 04:08 | 70 | 361 | 20003.4333 | 0.05996 | 0.056713 | 0.0010821 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 6 | UNKNOWN | CB 6 A/B Phase E/F | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.056713 | 11 | 2017 | 2017-01-28 | C | 361 | 0.056713 | 0.0010821
1 | 15780772 | 2017-01-28 12:20 | 2017-01-28 16:56 | 276 | 24 | 6624 | 0.019855 | 0.019639 | 7.1939e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P26259 | CONDUCTOR - REPAIR/REHANG | at 12:20, Turitea Sub, CB 4 Aokautere Feeder. Faultman found tree cutters who had felled a tree through lines at Pole P26259. Isolated Lines at Fuses H62. Permit issued and repairs carried out. All Power Restored on Completion. Nick Brown Attended. Materials: 4x Connectors, 2x Binders, More than 1 span not all phases of conductor. NDR: 045177 Check OMS 15780788 102 Harrison Hill road when closing | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.019639 | 11 | 2017 | 2017-01-28 | C | 24 | 0.019639 | 7.1939e-05
1 | 15781425 | 2017-01-28 15:50 | 2017-01-28 16:54 | 64 | 24 | 1546.8 | 0.0046365 | 0.00442 | 7.1939e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805667 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 10A Fuses at Fuses 495. Unknown Cause. Mark Spearpoint Attended. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00442 | 11 | 2017 | 2017-01-28 | C | 24 | 0.00442 | 7.1939e-05
1 | 15781476 | 2017-01-28 16:27 | 2017-01-28 17:50 | 83 | 75 | 6272.5 | 0.018802 | 0.018127 | 0.00022481 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 216534 | CONDUCTOR - REPAIR/REHANG | Advised SMC and control of 999 ETA of 1pm Trees growing up into line causing arcing required urgent attention at pole 216534. Unable to carry out alive due to risk of contact with line. Emergency shut with isolations at ABS SE4-001, 9676/1, Links 9676/4 & ABS S4732 to remove trees from line. All supply restored at completion. Work carried out under fire service direction. NDR to be forwarded by Downer | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.018127 | 11 | 2017 | 2017-01-28 | C | 75 | 0.018127 | 0.00022481
1 | 15783207 | 2017-01-29 01:37 | 2017-01-29 10:41 | 543 | 1047 | 205157.4 | 0.61495 | 0.60553 | 0.0031383 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 765701 | POLE | Tripping on Cb8 on Phase A,BC OC. (Car / Pole at 64 Puriri St, Wanganui). Fire Service Event No. F2235441. Isolation required between Used 1 X Pole 1 X HT Crossarm Complete 2 X LV Crossarms Complete 20M 70mm Copper Conductor 4 X LV Fuses NDR 30378 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.60553 | 11 | 2017 | 2017-01-29 | C | 1047 | 0.60553 | 0.0031383
1 | 15784534 | 2017-01-29 11:10 | 2017-01-29 12:43 | 93 | 1 | 93.2167 | 0.00027941 | 0.00027 | 2.9974e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | 2 X 6 Amp HT fuses ar I26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00027 | 11 | 2017 | 2017-01-29 | C | 1 | 0.00027 | 2.9974e-06
1 | 15784843 | 2017-01-29 12:00 | 2017-01-29 13:30 | 89 | 1 | 89.5 | 0.00026827 | 0.000259 | 2.9974e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N27 | FUSE - ELEMENT/LINK (HV) | 2 X 6 Amp HT Fuses at N27 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000259 | 11 | 2017 | 2017-01-29 | C | 1 | 0.000259 | 2.9974e-06
1 | 15785013 | 2017-01-29 17:50 | 2017-01-29 18:48 | 58 | 7 | 406 | 0.001217 | 0.001154 | 2.0982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 799718 | UNKNOWN | Removed branch from across line at pole 799718. 2x10amp HV fuses blown Replaced | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.001154 | 11 | 2017 | 2017-01-29 | C | 7 | 0.001154 | 2.0982e-05
1 | 15785279 | 2017-01-29 21:00 | 2017-01-30 15:25 | 1105 | 53 | 12915 | 0.038712 | 0.038235 | 0.00015886 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2378T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 Fuses found tripped at 2995. area patrolled but nothing found, reloadad, relivened but tripped agin.Further patrol / sectionalising carried out. Transformer 2378T found to be faulty. Isolated and replaced. (30kVA). Transformer was replaced but new transformer was faulty. Another transformer was used and livened at 15:25 30.01.17 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.038235 | 11 | 2017 | 2017-01-29 | C | 53 | 0.038235 | 0.00015886
1 | 15785717 | 2017-01-29 23:26 | 2017-01-30 00:07 | 40 | 1040 | 8433.15 | 0.025278 | 0.015925 | 0.00071938 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB4232 | UNKNOWN | Initial Auto-reclose on OKN CB4400/2 on O/C, B Phase EF. CB 4232/2 had tripped on O/C B Phase, EF also.. (Noted that A/R function on this recloser had been left off in error sometime). Reclose attempt of CB4232 to CB 4660 successful. Discussed with faultman, rough terrain, impractical to patrol. Further reclose on CB4660 successful. Unknown cause. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.015925 | 11 | 2017 | 2017-01-29 | C | 1040 | 0.015925 | 0.00071938
1 | 15787870 | 2017-01-30 09:33 | 2017-01-30 11:25 | 111 | 241 | 12208.7667 | 0.036594 | 0.034427 | 0.00072237 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730453 | CROSSARM - WHOLE ASSEMBLY | CB T31 Trip. E/F. O/C. L/O. Caused by broken crossarm at Pole 730453 Isolated between ABS 5960 and Fuses 5933 and Crossarm Replaced 1 X 11kV Crossarm Complete. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.034427 | 11 | 2017 | 2017-01-30 | C | 241 | 0.034427 | 0.00072237
1 | 15788612 | 2017-02-20 08:50 | 2017-02-20 13:09 | 259 | 46 | 11914 | 0.0357 | 0.035286 | 0.00013784 | NAPA ID:28511 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 028511 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC674 | NONE | upgrade TC 674 to 50kVA install new 11mtre concrete pole. Works location: Chepmell Rd, Morrinsville. WO 30034146 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.017643 | 5.5 | 2017 | 2017-02-20 | B | 46 | 0.035286 | 0.00013784
1 | 15788639 | 2017-02-21 09:15 | 2017-02-21 14:56 | 341 | 31 | 10571 | 0.031675 | 0.031396 | 9.289e-05 | NAPA ID:26555 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | 026555 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Uriti Rd | NONE | We have to unbind and straighten poles to take the tension off the network as wires are string tight and could break if left longer. The methodology is to do this every 16-18months by the powerCo engineers as the land is moving | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.015698 | 5.5 | 2017 | 2017-02-21 | B | 31 | 0.031396 | 9.289e-05
1 | 15790004 | 2017-01-30 12:04 | 2017-01-30 15:05 | 181 | 1094 | 19863.8833 | 0.05954 | 0.049702 | 0.0014597 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 846904 | LIGHTNING ARRESTOR (HV) | Recloser 6837 tripped B Phase OC & EF Caused by faulty Lightning Arrestor at Pole 846904.( Recloser 6837 ) Isolation between ABS's CA421, CA448, CA482 and Recloser 6560. Lightning arrestors Cut away. Recloser 6837 would not close after fault. DNO 170120 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.049702 | 11 | 2017 | 2017-01-30 | C | 1094 | 0.049702 | 0.0014597
1 | 15792797 | 2017-02-24 10:30 | 2017-02-24 12:50 | 140 | 6 | 840 | 0.0025169 | 0.002462 | 1.7978e-05 | NAPA ID:28467 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | 028467 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 227804 | NONE | REPLACE AT RISK RED TAG POLE # 227804. Works location: Schrieber Rd. WO 30035627 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001231 | 5.5 | 2017 | 2017-02-24 | B | 6 | 0.002462 | 1.7978e-05
1 | 15792922 | 2017-01-30 14:02 | 2017-01-30 15:44 | 102 | 241 | 16622.3333 | 0.049824 | 0.047656 | 0.00072237 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773596 | INSULATOR | CB 6 A/R, L/O, E/F, O/C. Sectionalised & patrol had begun when call came through of explosions from pole. FM found a broken 11kV Insulator. Shutdown & repairs carried out using 1x 11kV Pin & Insulator, & 1x Binder | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.047656 | 11 | 2017 | 2017-01-30 | C | 241 | 0.047656 | 0.00072237
1 | 15794269 | 2017-01-30 18:33 | 2017-01-30 19:55 | 81 | 31 | 2529.0833 | 0.0075806 | 0.007301 | 9.2919e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764817 | CONDUCTOR - REPAIR/REHANG | Floating Conductors found at Pole 764817 Isolated at Fuses 5301 Used 3 Dead ends, 6 sleeves & 10 metres of conductor | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.007301 | 11 | 2017 | 2017-01-30 | C | 31 | 0.007301 | 9.2919e-05
1 | 15794964 | 2017-01-30 18:48 | 2017-01-30 20:40 | 112 | 1 | 112.0333 | 0.00033581 | 0.000326 | 2.9973e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781049 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer X228 - cause Unknown Use 2 X 2 amp fuses | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000326 | 11 | 2017 | 2017-01-30 | C | 1 | 0.000326 | 2.9973e-06
1 | 15795301 | 2017-02-02 09:00 | 2017-02-02 14:13 | 313 | 35 | 10955 | 0.032835 | 0.03252 | 0.0001049 | NAPA ID:28544 TP_GREYTOWN GXP | 11 | Planned | 028544 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | On pole 850765 Install new sectionaliser 11094/2. complete with LINKS 11094/4 & /6. 11kV ABS S564 to be relabelled 11094/1. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.01626 | 5.5 | 2017 | 2017-02-02 | B | 35 | 0.03252 | 0.0001049
1 | 15795433 | 2017-01-30 23:03 | 2017-01-31 00:56 | 113 | 1 | 113 | 0.0003387 | 0.000329 | 2.9973e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | 794935 | UNKNOWN | 11.04pm called and advised Lianne at svs hub and emailed & advised control Salt build up causing arcing | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000329 | 11 | 2017 | 2017-01-30 | C | 1 | 0.000329 | 2.9973e-06
1 | 15795800 | 2017-01-31 08:20 | 2017-01-31 11:45 | 204 | 254 | 16958.8 | 0.050831 | 0.048547 | 0.00076133 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 720350 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, ALL PHASES | CB KA 7 O/C E/F 08:30 - Lines down reported by Brendon Hammersley on 027 470 5233 at 637 Ahipaipa Road, Hawera. Notified OCT. Caused by tractor hitting Stay Wire. NDR # 43222 10 mtrs Poko Alu Wire. 3 Poko Sleeves. 20 mtrs 7044 Copper Conductor 6 7044 Sleeves. Stay wire to be finished off tomorrow. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.048547 | 11 | 2017 | 2017-01-31 | C | 254 | 0.048547 | 0.00076133
1 | 15797973 | 2017-02-21 09:55 | 2017-02-21 15:56 | 361 | 25 | 9025 | 0.027043 | 0.026818 | 7.4911e-05 | NAPA ID:27289 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 027289 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P11201 | NONE | To replace red tagged poles bells road (GP). Works location: Bells Rd. WO 30025840 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.013409 | 5.5 | 2017 | 2017-02-21 | B | 25 | 0.026818 | 7.4911e-05
1 | 15798121 | 2017-01-31 10:47 | 2017-01-31 11:25 | 37 | 65 | 2431 | 0.0072866 | 0.006702 | 0.00019483 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P00747 | NONE | RS V5 A/R, L/O, O/C B & C Phase line patrolled trees in line pole P00747 1530 Waihi valley Rd NCTL to Gavin Paget to arrange tree crews. Sorted for Friday 3rd via referral attached | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.006702 | 11 | 2017 | 2017-01-31 | C | 65 | 0.006702 | 0.00019483
1 | 15798490 | 2017-02-17 09:17 | 2017-02-17 15:33 | 376 | 108 | 40618.25 | 0.12172 | 0.12075 | 0.00032363 | NAPA ID:27911 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 027911 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 829142 | NONE | Change insulators and 11kv poles on double circuit west side of Watsons Rd from Sub o corner of Olivers and Watsons Rds As discussed with Dave Patten. WOrks location: Watsons Rd. WO 30037589 | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.060373 | 5.5 | 2017 | 2017-02-17 | B | 108 | 0.12075 | 0.00032363
1 | 15798520 | 2017-01-31 11:28 | 2017-01-31 14:11 | 163 | 447 | 52777.75 | 0.15819 | 0.15417 | 0.0013398 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 853677 | CONDUCTOR - REPAIR/REHANG | RS S113 A/R, L/O, E/F. FM patrolled & found a 33kV Arm Brace had come loose & dropped down onto the 1kV tripping the feeder. 11kV & 33kV Isolated & Back Feed installed via SS S108. Repaired using 2x 16mm Nuts, & 2x 16mm Washers | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.15417 | 11 | 2017 | 2017-01-31 | C | 447 | 0.15417 | 0.0013398
1 | 15799238 | 2017-02-01 09:45 | 2017-02-01 13:51 | 246 | 4 | 984 | 0.0029493 | 0.002913 | 1.1989e-05 | NAPA ID:28553 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 028553 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace rotten TX structure TC3362. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0014565 | 5.5 | 2017 | 2017-02-01 | B | 4 | 0.002913 | 1.1989e-05
1 | 15799691 | 2017-02-23 09:08 | 2017-02-23 15:32 | 384 | 25 | 9600 | 0.028765 | 0.02854 | 7.4909e-05 | NAPA ID:27407 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 027407 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole K1760 | NONE | Change poles and x-arms and shift Fuses FC2203 to pole K1760. Works location: Maukoro Landing. WO 30017833 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.01427 | 5.5 | 2017 | 2017-02-23 | B | 25 | 0.02854 | 7.4909e-05
1 | 15800196 | 2017-02-28 09:35 | 2017-02-28 15:30 | 355 | 1 | 355 | 0.0010636 | 0.001054 | 2.9961e-06 | NAPA ID:27417 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 027417 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2203 | NONE | Change Hardware at various sites. Works location: Maukoro Landing. WO 30017833 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000527 | 5.5 | 2017 | 2017-02-28 | B | 1 | 0.001054 | 2.9961e-06
1 | 15800836 | 2017-02-16 08:45 | 2017-02-16 14:08 | 323 | 4 | 1292 | 0.0038717 | 0.003835 | 1.1987e-05 | NAPA ID:27528 TP_TE MATAI GXP | 11 | Planned | 027528 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | se6-226 | NONE | REPLACE POLES AND RECON 33KV FEEDER | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0019175 | 5.5 | 2017 | 2017-02-16 | B | 4 | 0.003835 | 1.1987e-05
1 | 15801124 | 2017-02-01 10:15 | 2017-02-01 16:22 | 367 | 2 | 734 | 0.0022 | 0.002182 | 5.9946e-06 | NAPA ID:28584 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11 | Planned | 028584 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | removal of tree branch around 11kv line | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001091 | 5.5 | 2017 | 2017-02-01 | B | 2 | 0.002182 | 5.9946e-06
1 | 15801518 | 2017-01-31 17:20 | 2017-01-31 19:54 | 154 | 81 | 7003.1167 | 0.020991 | 0.020262 | 0.00024279 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB C935 | UNKNOWN | CB C935 A/R, O/C A & C Phase. CB Auto Reclosed 3x within 4 minutes so NOC Operator disabled A/R function. Feeder then tripped at 17:27 hrs. Lines patrolled with no fault found | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.020262 | 11 | 2017 | 2017-01-31 | C | 81 | 0.020262 | 0.00024279
1 | 15802226 | 2017-01-31 09:16 | 2017-01-31 11:12 | 116 | 1 | 116 | 0.00034769 | 0.000338 | 2.9973e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12589 | CROSSARM - WHOLE ASSEMBLY | Broken Termination and Dropper arm. Isolated and repaired. Defect # 224-10425 1 x Termination Arm 1 x Dropper Arm TJ Tanoa Faultman. | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000338 | 11 | 2017 | 2017-01-31 | C | 1 | 0.000338 | 2.9973e-06
1 | 15802358 | 2017-01-31 19:16 | 2017-01-31 20:22 | 66 | 2 | 132.5667 | 0.00039735 | 0.000379 | 5.9947e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O14006 | FUSE - ELEMENT/LINK (HV) | James Kennerley Attended. Reloaded, Relivened 2x 6A HV Fuses at Fuses FC4009. Unknown Cause. 7.28pm Ofa from Trustpower called to ask if FM could call Art the Chorus contractor - passed onto Lianne at svs hub | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000379 | 11 | 2017 | 2017-01-31 | C | 2 | 0.000379 | 5.9947e-06
1 | 15802450 | 2017-01-31 20:07 | 2017-01-31 21:19 | 71 | 65 | 4662.6667 | 0.013976 | 0.013391 | 0.00019483 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V5 | COMMUNICATIONS EQUIPMENT | Coms failed to Recloser V5 so unable to reclose for over a hour, faultman called out to operate recloser, coms returned while faultman on route. Recloser closed This followed OMS 15798121 and branch was found in line causing clashing. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.013391 | 11 | 2017 | 2017-01-31 | C | 65 | 0.013391 | 0.00019483
1 | 15803099 | 2017-02-01 06:25 | 2017-02-01 08:28 | 122 | 12 | 1472.8 | 0.0044144 | 0.004306 | 3.5968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12824 | FUSE - ELEMENT/LINK (HV) | 3x 15amp @ FP1182 0828 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.004306 | 11 | 2017 | 2017-02-01 | C | 12 | 0.004306 | 3.5968e-05
1 | 15804379 | 2017-02-01 06:59 | 2017-02-01 07:57 | 58 | 5622 | 76732.8 | 0.22999 | 0.17944 | 0.016851 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB 2782 | UNKNOWN | CB 2782 tripped on neutral time O/C & E/F flags, line was patrolled and sectionalised and no fault was found. Faultman suspect bird strike as there are a lot of birds flying around the lines. Part of Cardiff CB Q11 is been backfed due to 33KV line work under 11KV lines. | S1 | CLOTON ROAD NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.17944 | 11 | 2017 | 2017-02-01 | C | 5622 | 0.17944 | 0.016851
1 | 15813389 | 2017-02-01 09:51 | 2017-02-01 11:02 | 71 | 69 | 4103 | 0.012298 | 0.011677 | 0.00020681 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8163 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Check OMS: 15813353 Have sent email and advised SMC of possible HV extent. Called to check for eta. They advised FM currently on temp disco ETA: 45mins Faultman found a burnt & broken fuse holder on Fuses 8163, line was isolated at ABS's 268, 523 & 359 to replace the fuse holder. 1 X 30 amp HV fuse replaced. 1 X fuse holder replaced. outage shown on 15821557 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.011677 | 11 | 2017 | 2017-02-01 | C | 69 | 0.011677 | 0.00020681
1 | 15814572 | 2017-02-01 22:03 | 2017-02-01 22:52 | 49 | 17 | 833 | 0.0024968 | 0.002343 | 5.0954e-05 | NAPA ID:28601 TP_CARRINGTON GXP > CITY SUB > CITY 5 | 11 | Planned | 028601 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12178 | NONE | Replace tx 282 and connect from new 11kV switch gear 12178. IR 9508 HV outage on switchgear 530 to cut away cable to tx 282( during this time the LV supply from tx 282 will be removed and newly installed LV backfeed cable to be connected to supply consumers during tx replacement LV OUTAGE REF #3903). Open, lock and tag switch 530/6 (no earth switch). After completion to isolate cable between 215/2 and 530/3 for AP work to install new switchgear 12178 and new 500kVA tx 282. | F2 | CITY 5 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.0011715 | 5.5 | 2017 | 2017-02-01 | B | 17 | 0.002343 | 5.0954e-05
1 | 15814576 | 2017-02-01 09:39 | 2017-02-01 13:06 | 207 | 1023 | 78154.4333 | 0.23425 | 0.22505 | 0.0030662 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 17 | UNKNOWN | CB 17 L/O on E/F. Feeder sensationalized and no fault cause located. Due to no fault cause and the high ICP count NCTL requested the crew to undertake an in depth inspection of all of the feeder assets to see if any fault cause could be found. This too has provided no leads as to the fault cause either. | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.22505 | 11 | 2017 | 2017-02-01 | C | 1023 | 0.22505 | 0.0030662
1 | 15816451 | 2017-02-12 08:38 | 2017-02-12 15:25 | 407 | 196 | 53924 | 0.1616 | 0.15984 | 0.00058738 | NAPA ID:26757 TP_MASTERTON GXP | 11 | Planned | 026757 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 828614 | NONE | Offload TX's before opening LINKS. Replacing 5 double 33/11kv poles pole Nos 828614-828612-828608 -828607 and 828603. Generator to be connected to Transformer T3912. | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.079919 | 5.5 | 2017 | 2017-02-12 | B | 196 | 0.15984 | 0.00058738
1 | 15816994 | 2017-02-01 11:03 | 2017-02-01 14:56 | 232 | 164 | 38179.2 | 0.11443 | 0.11296 | 0.00049156 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 354081 | INSULATOR | 1 X HT Insulator at Pole 354081 | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.11296 | 11 | 2017 | 2017-02-01 | C | 164 | 0.11296 | 0.00049156
1 | 15817708 | 2017-02-21 08:00 | 2017-02-21 16:17 | 497 | 90 | 29517.2 | 0.088447 | 0.087637 | 0.00026968 | NAPA ID:27092 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | 027092 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3723 | NONE | Install new RMU between IC1916 and transformer TC3723, on this shut the cable from IC1916 will be disconnected from terminal A of transformer 3723 and then connected to 13127/1 and a new cable will be run from 13127/2 to terminal A of transformer 3723. Also cable from IC3141 will be disconnected from terminal A of transformer 3723 and will be connected to 13127/3 on the second shut on the 23/02/17. after the cable break at T-blade power will be restored via IC3147 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.043819 | 5.5 | 2017 | 2017-02-21 | B | 90 | 0.087637 | 0.00026968
1 | 15818437 | 2017-02-01 12:56 | 2017-02-01 14:45 | 109 | 10 | 1090.5 | 0.0032686 | 0.003178 | 2.9973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p09331 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp wind 1441 @ i26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003178 | 11 | 2017 | 2017-02-01 | C | 10 | 0.003178 | 2.9973e-05
1 | 15821276 | 2017-02-01 14:42 | 2017-02-01 15:31 | 48 | 112 | 5398.4 | 0.016181 | 0.015173 | 0.0003357 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | TX1540 | CONDUCTOR - REPAIR/REHANG | 1395 VALLEY ROAD Tree branch over in the paddock and is on the line burning. SMC and Control advised Removed Banch at Transformer X1540 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.015173 | 11 | 2017 | 2017-02-01 | C | 112 | 0.015173 | 0.0003357
1 | 15821488 | 2017-02-01 16:26 | 2017-02-01 17:40 | 74 | 23 | 1702 | 0.0051014 | 0.004894 | 6.8938e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/228 - Akitio | JUMPER | Check for safety - TX is arcing and sparking. T9/228 and Pole:10190 Andy from Downer called in sent out HV planned outage to retailers | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.004894 | 11 | 2017 | 2017-02-01 | C | 23 | 0.004894 | 6.8938e-05
1 | 15821811 | 2017-02-01 15:28 | 2017-02-01 18:15 | 167 | 40 | 6680 | 0.020022 | 0.019662 | 0.00011989 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 816878 | CONDUCTOR - REPAIR/REHANG | Sent out hv planned outage to retailers Removed Tree From Line | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.019662 | 11 | 2017 | 2017-02-01 | C | 40 | 0.019662 | 0.00011989
1 | 15821879 | 2017-02-01 17:08 | 2017-02-01 18:06 | 58 | 52 | 3016 | 0.0090399 | 0.008572 | 0.00015586 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 359782 Te Ore Ore Sub | CROSSARM - WHOLE ASSEMBLY | Crossarm Hanging Off Pole Please Check OMS 15822217 is related | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.008572 | 11 | 2017 | 2017-02-01 | C | 52 | 0.008572 | 0.00015586
1 | 15821968 | 2017-02-22 08:30 | 2017-02-22 16:40 | 489 | 111 | 43354.5 | 0.12991 | 0.12891 | 0.00033859 | NAPA ID:27549 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | 027549 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 782300 | NONE | Replace four defect 11kv poles, pole 782300 is a red tag pole, poles 850964, 780191, 842112 are close to the edge of the Waitotara river after the floods and need to be moved. Generator is being supplied to the school. Generator connect to wrong transformer, had to change location of generator, faultman unable to supply new transformer number connected to LV fuses at Pole 780513 to supply school. so work started late. advised that work should still get completed in outage time frame. Coms an issue during whole job, issues contacting faultman to confirm they clear of lines before livening caused over run | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.064454 | 5.5 | 2017 | 2017-02-22 | B | 111 | 0.12891 | 0.00033859
1 | 15823549 | 2017-02-01 21:00 | 2017-02-02 00:10 | 190 | 231 | 31681.25 | 0.094958 | 0.092881 | 0.0013158 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | CB H21 Trip, E/F. NOTE: H21 also supplying H41 due to CB H41 currently DNO'd FM sectionalised and fault narrowed down to being in first half of Tarata Feeder, but feeder then closed in & cause of fault could not be located. Request put in by NOC for line patrol of suspected area to be carried out tomorrow in daylight. | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.092881 | 6.6 | 2017 | 2017-02-01 | C | 231 | 0.092881 | 0.0013158
1 | 15824708 | 2017-02-01 22:28 | 2017-02-01 22:57 | 29 | 95 | 2755 | 0.0082576 | 0.007403 | 0.00028474 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1828 | JUMPER | at 22:04, Mikkelsen Rd Sub, CB 5 Maungakawa Rd Feeder. Faultman found jumper had come out of connection on center phase fuse at Transformer TC1828. Isolated Lines at ABS IC676 & IC1241. Permit issued & repairs carried out. All Power Restored on Completion. Perry Hicks Attended. No Materials Used. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.007403 | 11 | 2017 | 2017-02-01 | C | 95 | 0.007403 | 0.00028474
1 | 15825618 | 2017-02-02 05:43 | 2017-02-02 07:40 | 117 | 58 | 6786 | 0.020339 | 0.019817 | 0.00017384 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 705102 | FUSE - ELEMENT/LINK (HV) | Check OMS: 15826028 - 241 Bayley 2 x 15amp @ 6285 7.40 poss bird | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.019817 | 11 | 2017 | 2017-02-02 | C | 58 | 0.019817 | 0.00017384
1 | 15825637 | 2017-02-02 12:07 | 2017-02-02 12:48 | 41 | 3 | 123 | 0.00036866 | 0.000341 | 8.9917e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N0170 | FUSE - ELEMENT/LINK (HV) | Transformer TC5657 fuse holder burnt & requires replacement, feeds an irrigator customer informed not to operate, supply still intact Isolation at fuses FC4132 ( spur no back feed ) Fuse replaced ( pole N0170 ) all service restored Materials 1 x 15 A H/V, O/H fuse outage on child | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000341 | 11 | 2017 | 2017-02-02 | C | 3 | 0.000341 | 8.9917e-06
1 | 15825647 | 2017-02-02 06:02 | 2017-02-02 08:49 | 167 | 3 | 503.35 | 0.0015087 | 0.001481 | 8.9917e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 229390 | FUSE - ELEMENT/LINK (HV) | 2 x8amp swan @fp894 0837 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001481 | 11 | 2017 | 2017-02-02 | C | 3 | 0.001481 | 8.9917e-06
1 | 15825714 | 2017-03-02 09:50 | 2017-03-02 11:57 | 127 | 28 | 3556 | 0.010654 | 0.010402 | 8.3889e-05 | NAPA ID:27739 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 027739 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 360099 | NONE | To replace red tagged x arms on pole 360099 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.005201 | 5.5 | 2017 | 2017-03-02 | B | 28 | 0.010402 | 8.3889e-05
1 | 15826155 | 2017-02-02 07:20 | 2017-02-02 10:03 | 162 | 16 | 2870.4 | 0.0086033 | 0.008459 | 5.3951e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | U12606 | FUSE - ELEMENT/LINK (HV) | 3x 3amp @fc 755 unknown cause 0938 outage on child job | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.008459 | 11 | 2017 | 2017-02-02 | C | 16 | 0.008459 | 5.3951e-05
1 | 15826257 | 2017-02-02 08:01 | 2017-02-02 11:27 | 205 | 186 | 16288.0333 | 0.048819 | 0.047147 | 0.00097411 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805129 | INSULATOR | 1 X 22kV HT Insulator 1m 16mm Copper Conductor Pole 805129 CB 1133 Tripped A Phase O/C E/F | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.047147 | 22 | 2017 | 2017-02-02 | C | 186 | 0.047147 | 0.00097411
1 | 15826453 | 2017-03-02 12:08 | 2017-03-02 14:41 | 153 | 9 | 1377 | 0.0041255 | 0.004044 | 2.6964e-05 | NAPA ID:28526 TP_STRATFORD GXP > STRATHMORE | 11 | Planned | 028526 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX 2727T | NONE | Replace Tx 2727T and Xarms if necessessary at 2727T (refer Phil Marsh Powerco as for urgency) | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.002022 | 5.5 | 2017 | 2017-03-02 | B | 9 | 0.004044 | 2.6964e-05
1 | 15826891 | 2017-02-03 09:48 | 2017-02-03 14:43 | 294 | 65 | 19160.9167 | 0.057429 | 0.056844 | 0.00019482 | NAPA ID:28610 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 028610 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | v5 | NONE | To cut trees away from 11kv line | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.028422 | 5.5 | 2017 | 2017-02-03 | B | 65 | 0.056844 | 0.00019482
1 | 15827055 | 2017-02-20 | 2017-02-20 00:40 | 39 | 40 | 1594 | 0.0047764 | 0.004416 | 0.00011986 | NAPA ID:28402 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 028402 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB 13126 | NONE | Locate problem why the CB 13126 (controlling TC713) will not rack into Circuit Earth and Close. | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.002208 | 5.5 | 2017 | 2017-02-20 | B | 40 | 0.004416 | 0.00011986
1 | 15827625 | 2017-02-21 08:45 | 2017-02-21 15:22 | 397 | 7 | 2585 | 0.0077458 | 0.007682 | 2.0975e-05 | NAPA ID:28627 TP_TE MATAI GXP | 11 | Planned | 028627 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 263962 | NONE | SWITCHING TO ISOLATE 33kV LINE AND PROVIDE 11kV BACKFEEDS. OFFLOAD & CREATE LLB AT pole 263962. OFFLOAD & CREATE LLB AT pole 221559. REPLACE 33 / 11 kV POLE 226053 AND RECON 33KV FEEDER. CLOSE BREAK AT pole 221559 AND RESTORE. CLOSE BREAK AT pole 263962 AND RESTORE. Switching/advertising re-write of 27531. WO 30036939. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.003841 | 5.5 | 2017 | 2017-02-21 | B | 7 | 0.007682 | 2.0975e-05
1 | 15827663 | 2017-02-02 09:03 | 2017-02-02 11:56 | 172 | 30 | 5168.5 | 0.015491 | 0.015221 | 8.9918e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732813 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp @5870 Unknown 1145 | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.015221 | 11 | 2017 | 2017-02-02 | C | 30 | 0.015221 | 8.9918e-05
1 | 15829181 | 2017-02-02 09:10 | 2017-02-02 10:12 | 61 | 166 | 9183.0333 | 0.027524 | 0.026031 | 0.00049755 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6286/2 | UNKNOWN | Recloser 6286/2 tripped on E/F flags, line was patrolled and sectionalised and no fault was found, it was raining very heavily in the area at time of tripping. Recloser tripped again at 13:05 (OMS 15834015) and a tree was found touching line due to weight of the rain. Tree contractor will cut in the morning (OMS 15835483) | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.026031 | 11 | 2017 | 2017-02-02 | C | 166 | 0.026031 | 0.00049755
1 | 15829862 | 2017-02-02 09:28 | 2017-02-02 11:59 | 151 | 44 | 6644 | 0.019914 | 0.019518 | 0.00013188 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p16417 | FUSE - ELEMENT/LINK (HV) | **Check: would this affect 237 Waituna Road (OMS 15830126), 585 MAKAIRO TRACK, PAHIATUA (OMS 15830183) LV to HV email sent and voicemail left with Phil (was already en route) to check Q68 on the way 4 x 10amp @ q68 fuses 1155 found branch on line p16417 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.019518 | 11 | 2017 | 2017-02-02 | C | 44 | 0.019518 | 0.00013188
1 | 15830130 | 2017-02-22 08:45 | 2017-02-22 14:10 | 325 | 79 | 25675 | 0.076933 | 0.076222 | 0.00023672 | NAPA ID:28572 TP_HINUERA GXP > TIRAU SUB > PROSPECT ST | 11 | Planned | 028572 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3753 | NONE | Isolate earth and tag 9952 and TC3753, Through joint cables to 13105/4 to FC2484, Through joint 13105/3 and 9952, Remove T Blade and TC3753 | F4 | PROSPECT ST | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.038111 | 5.5 | 2017 | 2017-02-22 | B | 79 | 0.076222 | 0.00023672
1 | 15830135 | 2017-02-20 09:00 | 2017-02-20 14:05 | 305 | 3 | 915 | 0.0027418 | 0.002714 | 8.9894e-06 | NAPA ID:26979 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11 | Planned | 026979 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-074 | NONE | Replace Pole, crossarms, hardware and transformer TD5-074 | F4 | BRUCE RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.001357 | 5.5 | 2017 | 2017-02-20 | B | 3 | 0.002714 | 8.9894e-06
1 | 15833052 | 2017-02-02 11:52 | 2017-02-02 13:45 | 113 | 1 | 113 | 0.00033869 | 0.000329 | 2.9972e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798360 | FUSE - ELEMENT/LINK (HV) | 2 x 10 @7275 1345 wind outage on child | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000329 | 11 | 2017 | 2017-02-02 | C | 1 | 0.000329 | 2.9972e-06
1 | 15833186 | 2017-02-24 10:29 | 2017-02-24 14:20 | 231 | 4 | 924 | 0.0027686 | 0.002732 | 1.1985e-05 | NAPA ID:28614 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 028614 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P47303 | NONE | To replace red tagged 33kv & 11kv pole P47303 Mt Butters (GP) | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001366 | 5.5 | 2017 | 2017-02-24 | B | 4 | 0.002732 | 1.1985e-05
1 | 15834015 | 2017-02-02 13:06 | 2017-02-02 15:15 | 129 | 166 | 9585.0333 | 0.028729 | 0.027236 | 0.00049755 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 764941 | NONE | Recloser 6286/2 tripped on Ed/F flags, line was sectionalised and patrolled and faultman found burn marks on a tree at pole 764941 that is making contact in the heavy rain, a referral job will be made to have the trees cut by tree contractor. Referal OMS Number: 15835483. There had been an earlier trip and patrol (OMS 15829181) with NFF. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.027236 | 11 | 2017 | 2017-02-02 | C | 166 | 0.027236 | 0.00049755
1 | 15834592 | 2017-02-24 09:30 | 2017-02-24 14:50 | 320 | 16 | 5120 | 0.015341 | 0.015197 | 4.7941e-05 | NAPA ID:27728 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | 027728 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P04260 | NONE | To replace red tagged pole P04260 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0075985 | 5.5 | 2017 | 2017-02-24 | B | 16 | 0.015197 | 4.7941e-05
1 | 15834965 | 2017-02-02 16:45 | 2017-02-02 17:33 | 48 | 34 | 1632 | 0.0048915 | 0.004585 | 0.00010191 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218755 | CROSSARM - WHOLE ASSEMBLY | Broken HV crossarm pole 218755 Allen Cameron 02041056999. Isolation between normal open ABS SE7 017 & ABS SF7 041 X arm replaced all service restored Materials 1 x H/V x arm complete | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.004585 | 11 | 2017 | 2017-02-02 | C | 34 | 0.004585 | 0.00010191
1 | 15835025 | 2017-02-15 09:00 | 2017-02-15 14:40 | 339 | 33 | 9142.3333 | 0.027397 | 0.0271 | 9.8891e-05 | NAPA ID:27696 TP_MANGAMAIRE GXP > MANGAMUTU SUB | 11 | Planned | 027696 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | make connection of the 4 new U/G cables from the new switchgear to each of the new poles,Cut away the O/H lines, remove T14, liven, phase | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.01355 | 5.5 | 2017 | 2017-02-15 | B | 33 | 0.0271 | 9.8891e-05
1 | 15835177 | 2017-02-03 10:00 | 2017-02-03 11:38 | 98 | 2 | 196 | 0.00058745 | 0.000569 | 5.9944e-06 | Referral | 11.00000000 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC2712 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | TX TC2712 is leaking oil out of the hv bushings and dripping on the ground.. Needs to be replaced asap Advised control Advised Cindy that because this tx is leaking onto the ground then they will need to attend asap to replace the tx safety manager will need to be filled out 5.35pm Coops called to advise they will attend first thing tomorrow morning 3/2/17 Transformer TC2712 was replaced. | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000569 | 11 | 2017 | 2017-02-03 | C | 2 | 0.000569 | 5.9944e-06
1 | 15835549 | 2017-02-03 10:30 | 2017-02-03 12:30 | 120 | 2 | 240 | 0.00071933 | 0.000701 | 5.9944e-06 | NAPA ID:28663 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 028663 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X869 | NONE | replace old 10 kva T/F 869 due to high voltage and rusty hanger arms , internal tapping , customer complaint Off time 10:30, On Time 12:30. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0003505 | 5.5 | 2017 | 2017-02-03 | B | 2 | 0.000701 | 5.9944e-06
1 | 15835972 | 2017-02-02 16:04 | 2017-02-03 02:37 | 633 | 120 | 13085.2167 | 0.03922 | 0.03814 | 0.0012559 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 264386 | CABLE - REPAIR | Recloser 9539/2 tripped on E/F flags, line was sectionalised and patrolled and a suspected fault was located on cable from Fuses FP62 to the first pole across the road at pole 264386, line was isolated at Fuses FP62 and the customers on transformers TP1166 & TP1283 have been supplied with generators. Advised SMC that Mike Jeffery is no longer attending and Brent Williams will. Brent Williams test cable and it was not good but can not locate the fault as the cable goes under the road, cable will be DNO'd . DNO Tag 170203. Cable between Fuses FP62 & pole 264386 is going to be replaced. 04/02/17 ????? | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.03814 | 11 | 2017 | 2017-02-02 | C | 120 | 0.03814 | 0.0012559
1 | 15836796 | 2017-02-02 14:53 | 2017-02-02 16:40 | 107 | 6 | 642.3 | 0.0019251 | 0.001871 | 1.7984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N13091 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp @ tc2846 unknown 1640 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.001871 | 11 | 2017 | 2017-02-02 | C | 6 | 0.001871 | 1.7984e-05
1 | 15838135 | 2017-02-02 21:24 | 2017-02-02 22:44 | 79 | 1960 | 116177.35 | 0.34821 | 0.33059 | 0.0058746 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 21 | UNKNOWN | 9.27pm advised Les this job has moved up to feeder fault CB 21 Trip, O/C A & B Phase. Sectionalised & patrolled beyond where fault locaters had operated on Awahuri Feilding Rd with no fault found | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.33059 | 11 | 2017 | 2017-02-02 | C | 1960 | 0.33059 | 0.0058746
1 | 15838430 | 2017-02-02 23:00 | 2017-02-03 04:55 | 354 | 46 | 15170.3 | 0.045469 | 0.045055 | 0.00013787 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 750359 | POLE | 9.12pm advised at svs hub & emailed & advised control Car hit Pole with Transformer 948 on it. Backfeeds carried out & work area isolated. D Tech Services called to site to locate fibre cables & Traffic management onsite also. Materials used: 11m Pole, Fuse Arm, Transformer Arm, 3x HV Fuse Holders Complete with Links, 2m Pin Arm, & Donut & Block NDR # N100301 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.045055 | 11 | 2017 | 2017-02-02 | C | 46 | 0.045055 | 0.00013787
1 | 15841308 | 2017-02-02 21:43 | 2017-02-03 00:33 | 170 | 145 | 10084.7833 | 0.030227 | 0.028922 | 0.0004346 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731943 | INSULATOR | CB Q21 Trip. Sectionalised & patrolled with faulty insulator found at ABS 5996. ABS jumpered through using 2mtrs of 70mm conductor & 2x conductor joints. ABS DNO'd for repair or replacement | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.028922 | 11 | 2017 | 2017-02-02 | C | 145 | 0.028922 | 0.0004346
1 | 15841625 | 2017-02-02 21:43 | 2017-02-03 14:45 | 1021 | 166 | 26716.2333 | 0.080076 | 0.078582 | 0.00049755 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 764941 | CONDUCTOR - REPAIR/REHANG | RS 6286 A/R, L/O, E/F. Sectionalised & Patrolled. Trees in lines at Pole 764941 in Kiwi Rd. Line Isolated via Fuses 5360 & left off overnight. Trees need to be cut tomorrow Tree were cut at poles 764941, 764944 & 764954 all the trees were outside notice zone but due to heavy rain were making contact with the lines. REF OMS 15835483 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.078582 | 11 | 2017 | 2017-02-02 | C | 166 | 0.078582 | 0.00049755
1 | 15842293 | 2017-02-02 22:26 | 2017-02-02 22:42 | 15 | 46 | 721.4333 | 0.0021623 | 0.001748 | 0.00013787 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser L/O on O/C, Reclosed OK | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001748 | 11 | 2017 | 2017-02-02 | C | 46 | 0.001748 | 0.00013787
1 | 15842363 | 2017-02-02 22:41 | 2017-02-03 01:00 | 139 | 10 | 1392.6667 | 0.0041742 | 0.004084 | 2.9973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | I26 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuses. The customer said that this happens all the time. its always the network line by the rd. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.004084 | 11 | 2017 | 2017-02-02 | C | 10 | 0.004084 | 2.9973e-05
1 | 15842560 | 2017-02-02 23:31 | 2017-02-03 06:50 | 438 | 69 | 7000.8667 | 0.020983 | 0.020362 | 0.00020681 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 220820 | POLE | Fire comms reported van vs pole at 744 TePuke Highway KiwiRail controls access to their corridor. Men stood down while train operating. ( ATU 4 tripped O/C, E/F car v pole 220820 isolation between ABS SE5 026 & ABS SE5 011 back feed via ABS SE5 144 pole replaced all H/V restored. transformers TD5 241 & TP2784 require generator due to damaged L/V NDR No Materials 2:10pm - 1:50pm all LV are now live and back on HV u/g cable to be repaired - Dennis working with control. | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.020362 | 11 | 2017 | 2017-02-02 | C | 69 | 0.020362 | 0.00020681
1 | 15842953 | 2017-02-03 03:00 | 2017-02-03 12:33 | 573 | 83 | 14996.3833 | 0.044947 | 0.044201 | 0.00046457 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739304 | CONDUCTOR - REPAIR/REHANG | CB 7121 tripped on B phase O/C & E/F flags, line was patrolled and sectionalised, Fuses 5453 were Isolated as fault was past the fuses, fault was left until morning as to patrol as weather was bad and access had to be made on foot and was to dangerous.Faultman found a line down across the river at pole 739304. 5 meters of Squirrel conductor was used. 3 X sleeves used. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.044201 | 11 | 2017 | 2017-02-03 | C | 83 | 0.044201 | 0.00046457
1 | 15843197 | 2017-02-03 07:35 | 2017-02-03 09:19 | 104 | 11 | 1144 | 0.0034288 | 0.003329 | 3.2969e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763996 | INSULATOR | Faultman found a blown fuse at Fuses 5313 after a patrol the faultman found a broken 11KV insulator on pole 763996, line was isolated at Fuses 5313 to replace the insulator. 1 X 11KV insualtor replaced. 1 X binder used. 1 X 10 amp HV fuse replaced | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003329 | 11 | 2017 | 2017-02-03 | C | 11 | 0.003329 | 3.2969e-05
1 | 15844342 | 2017-02-03 06:47 | 2017-02-03 06:57 | 10 | 10 | 104 | 0.00031171 | 0.000221 | 2.9972e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09331 | FUSE - ELEMENT/LINK (HV) | 2x 6amp @ I26 657 wind | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.000221 | 11 | 2017 | 2017-02-03 | C | 10 | 0.000221 | 2.9972e-05
1 | 15844580 | 2017-02-03 07:36 | 2017-02-03 10:20 | 163 | 18 | 2951.4 | 0.008846 | 0.008684 | 5.395e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803835 | FUSE - ELEMENT/LINK (HV) | 2 x 15amp fuses bird @x1746 2 x 15amp fuses @ 549 10:20 | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.008684 | 11 | 2017 | 2017-02-03 | C | 18 | 0.008684 | 5.395e-05
1 | 15845884 | 2017-02-22 07:30 | 2017-02-22 16:30 | 540 | 1 | 540 | 0.0016181 | 0.001609 | 2.9963e-06 | NAPA ID:27988 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 027988 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RMU SC2-085>089 | NONE | Replace existing three way Series 1 RMU SC2-085>089, existing five way Series 1 RMU SC2-090>098 and existing metering unit with a five way Siemens 8DJH MRTTR unit with inbuilt metering unit. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.0008045 | 5.5 | 2017 | 2017-02-22 | B | 1 | 0.001609 | 2.9963e-06
1 | 15846206 | 2017-02-25 12:11 | 2017-02-25 12:15 | 3 | 1 | 3.8833 | 1.1635e-05 | 0 | 2.9962e-06 | NAPA ID:27904 TP_KOPU GXP > THAMES SUB | 11 | Planned | 027904 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | CB15, 16, 17, 3, 5 and 6 Opened / closed in turn for Timing Testing | F1 | A & G PRICE | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2017-02-25 | B | 1 | 0 | 2.9962e-06
1 | 15849261 | 2017-02-04 08:03 | 2017-02-04 11:10 | 187 | 3 | 561 | 0.0016814 | 0.001654 | 8.9915e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5038E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fault job actually on Transformer 5038E (Not 5047E) with strange voltages.. All 3 fuses removed, reloaded to check contacts. Faulty Transformer 5038E replaced along with 3 HT Transformer fuses at 10A Rating (Poor condition) and LV fuses. Isolation required from Fuses TA822. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001654 | 11 | 2017 | 2017-02-04 | C | 3 | 0.001654 | 8.9915e-06
1 | 15849535 | 2017-02-03 18:19 | 2017-02-03 18:42 | 23 | 10 | 232.5 | 0.00069685 | 0.000606 | 2.9972e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | 2 X 6 Amp at Fuses I26 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.000606 | 11 | 2017 | 2017-02-03 | C | 10 | 0.000606 | 2.9972e-05
1 | 15850893 | 2017-02-04 10:27 | 2017-02-04 11:21 | 54 | 12 | 648 | 0.0019422 | 0.001834 | 3.5966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 355763 | INSULATOR | Outage required beyond fuses V64 to replace 3 insulators and binders. Also 3 X 6A HT fuses replaced at V64 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.001834 | 11 | 2017 | 2017-02-04 | C | 12 | 0.001834 | 3.5966e-05
1 | 15851356 | 2017-02-04 12:35 | 2017-02-04 14:29 | 114 | 10 | 1145.6667 | 0.0034338 | 0.003343 | 2.9972e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | Tripping on 2 HT fuses at I26 (Ongoing issue with poor conductor unraveling in the wind). Reloaded OK - 2A Rating. Faultman will investigate repairs ASAP. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003343 | 11 | 2017 | 2017-02-04 | C | 10 | 0.003343 | 2.9972e-05
1 | 15853036 | 2017-02-04 22:16 | 2017-02-05 00:53 | 157 | 1 | 157.0333 | 0.00047066 | 0.000461 | 2.9971e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | FC754 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses. Suspect Bird Strike. Unable to get to Transformer to do final checks. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000461 | 11 | 2017 | 2017-02-04 | C | 1 | 0.000461 | 2.9971e-06
1 | 15853053 | 2017-02-04 22:58 | 2017-02-04 23:31 | 33 | 196 | 6543.1333 | 0.019611 | 0.017848 | 0.00058745 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB TA7 | UNKNOWN | No Flag CB TA7. Line patrolled and no fault found. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.017848 | 11 | 2017 | 2017-02-04 | C | 196 | 0.017848 | 0.00058745
1 | 15853599 | 2017-02-04 23:38 | 2017-02-05 01:20 | 101 | 1 | 101.65 | 0.00030466 | 0.000295 | 2.9971e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L106 | FUSE - ELEMENT/LINK (HV) | 2 X 10 Amp HT Fuses At L106 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000295 | 11 | 2017 | 2017-02-04 | C | 1 | 0.000295 | 2.9971e-06
1 | 15854152 | 2017-02-05 08:21 | 2017-02-05 08:32 | 11 | 3004 | 20285 | 0.060797 | 0.033786 | 0.0090034 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2182 | UNKNOWN | Wanganui East CB 2182 tripped on O/C N/T and E/F causing LOS to Wanganui No 3 Line, Kiwi St, Eastown Rd, Wanganui East and Ikitara Rd feeders. Line Patrolled and no fault found. | S4 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 0.033786 | 33 | 2017 | 2017-02-05 | C | 3004 | 0.033786 | 0.0090034
1 | 15857828 | 2017-02-05 11:45 | 2017-02-05 16:19 | 274 | 115 | 27761.7 | 0.083205 | 0.082171 | 0.00039262 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837358 | CONDUCTOR - REPAIR/REHANG | Recloser C217 Trip B & C Ph Fault. Feeder patrolled & sectionalised Lines down between poles 837358 & 837357 due to willow tree branch, Isolated at ABS S147, no back feeds available.9 sleeves, 10m conducter | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.082171 | 11 | 2017 | 2017-02-05 | C | 115 | 0.082171 | 0.00039262
1 | 15858350 | 2017-02-05 13:41 | 2017-02-07 13:24 | 2862 | 1 | 2862.7167 | 0.0085799 | 0.00857 | 2.9971e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758350 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuse found blown at Transformer 3308T transform found to be faulty Customer happy for it to be changed later 6/2 - 12:35pm emailed SMC for an update. 6/2 email from Lianne 7:30pm: - (I have just started my shift and doesn't look like anyone has replied to your email. I spoke to Jade who attended the original job at this address and he told me that Paul Fitzpatrick will be replacing this transformer tomorrow. I did leave notes to that affect when I left my shift at 5.30am this morning but it may have been misunderstood). Transformer replaced (7/2/17) | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00857 | 11 | 2017 | 2017-02-05 | C | 1 | 0.00857 | 2.9971e-06
1 | 15858967 | 2017-02-05 21:28 | 2017-02-05 23:15 | 106 | 18 | 1925.4 | 0.0057707 | 0.005608 | 5.3948e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N30 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses N30, line patrolled no fault found suspect duck strike. 2 X 10 amp HV fuses replaced. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.005608 | 11 | 2017 | 2017-02-05 | C | 18 | 0.005608 | 5.3948e-05
1 | 15859003 | 2017-02-05 21:50 | 2017-02-06 00:24 | 154 | 4 | 617.4667 | 0.0018506 | 0.001814 | 1.1989e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP767 | FUSE - ELEMENT/LINK (HV) | 2 X 10A HV Fuses replaced. Patrolled but no real hard cause found. Some trees near lines outside 87. Asplundh organised to cut these. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.001814 | 11 | 2017 | 2017-02-05 | C | 4 | 0.001814 | 1.1989e-05
1 | 15859010 | 2017-02-06 00:46 | 2017-02-06 01:30 | 44 | 58 | 2552 | 0.0076486 | 0.007127 | 0.00017383 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2552T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found a blown fuse on transformer 2552T, after reloading and closing the fuse it blown and tripped Recloser 4915/2, transformer was isolated and Recloser closed, transformer will be changed in morning. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.007127 | 11 | 2017 | 2017-02-06 | C | 58 | 0.007127 | 0.00017383
1 | 15871163 | 2017-02-06 07:35 | 2017-02-06 09:22 | 106 | 43 | 4598.1333 | 0.013781 | 0.013394 | 0.00012887 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701588 | FUSE - ELEMENT/LINK (HV) | Lv to HV emailed SMC get F/man to check fuses 6799 fuses found blown at fuses 6799 - cause unknown Used 2 x 20 amp fuses | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.013394 | 11 | 2017 | 2017-02-06 | C | 43 | 0.013394 | 0.00012887
1 | 15871358 | 2017-02-06 09:20 | 2017-02-06 11:23 | 122 | 18 | 2208.3 | 0.0066185 | 0.006456 | 5.3948e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10131 | FUSE - ELEMENT/LINK (HV) | 10:14 advised SMC of this job waiting - unsure if this is related to OMS 15871338 - SMC will get Anjay to call dispatch when he is onsite (was not related to this job) Fuses found blown at Fuses N30 - Cause Unknown Used 2 x 10amp | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.006456 | 11 | 2017 | 2017-02-06 | C | 18 | 0.006456 | 5.3948e-05
1 | 15872803 | 2017-02-06 13:12 | 2017-02-07 12:56 | 1424 | 1040 | 74927.8833 | 0.22457 | 0.21521 | 0.0067405 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P23991 | CONDUCTOR - REPAIR/REHANG | CB 8 tripped E/F L/O Lines down found at pole P23991 during sectionlising - Isolated at ABS E17 Lines repaired - used 4 metres of conductor and 8 sleeveson livening feeder tripped Trees through lines found at Pole P14894 - isolated again at ABS E17 Temp line break made at Pole P14895 Generators install for 2 ICP's Lines to be repaired in following days. Material used listed under NDR 300287 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.21521 | 11 | 2017 | 2017-02-06 | C | 1040 | 0.21521 | 0.0067405
1 | 15876863 | 2017-02-06 18:54 | 2017-02-06 19:37 | 43 | 10 | 431.5 | 0.0012932 | 0.001203 | 2.9971e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | FUSE - ELEMENT/LINK (HV) | 2 * 10A fuses reloaded OK at Fuses I26, Ongoing problem with defective conductor. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001203 | 11 | 2017 | 2017-02-06 | C | 10 | 0.001203 | 2.9971e-05
1 | 15877095 | 2017-02-06 22:50 | 2017-02-07 11:45 | 775 | 12 | 9300 | 0.027873 | 0.027765 | 3.5965e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 843481 | CONDUCTOR - REPAIR/REHANG | Check for safety - Sparking lines, customer is concerned as the sparks are landing in dry grass Advised control and SMC of 999. Tree branch found resting on line causing arcing. Fuses 6863 open for safety with NDR N100302 raised by faultman. (Tree contractors to be organised for morning) Isolated and Earthed at fuses 6863. Trees removed from lines at pole 843481. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.027765 | 11 | 2017 | 2017-02-06 | C | 12 | 0.027765 | 3.5965e-05
1 | 15877220 | 2017-02-06 21:50 | 2017-02-07 13:54 | 964 | 106 | 22874.6333 | 0.068557 | 0.067604 | 0.00055146 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p04884 | CONDUCTOR - REPAIR/REHANG | Tripping on CB1 on B Phase, EF. Feeder patrolled and sectionalised and restored with Fuses V18 open. Impracticle to patrol during night. Will check Range Rd during daylight hours. This job should have been 2r as there were two seperate faults on this feeder, lines hanging extremely low at Pole 373707, and floating conductors at Pole P04884 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.067604 | 11 | 2017 | 2017-02-06 | C | 106 | 0.067604 | 0.00055146
1 | 15877926 | 2017-02-07 04:44 | 2017-02-07 09:55 | 311 | 10 | 3110 | 0.0093208 | 0.00923 | 2.997e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09331 | FUSE - ELEMENT/LINK (HV) | Retailer has advised that the powerlines going into 80 Saunders Roads are 1m off the road. Unable to get hold of Musa via phone or RT. SMC (Jo) advised 9:20am Powerlines going into the property. This has been an ongoing issue and the customer is urgently seeking an update as there is a newborn baby on the way and customer experiencing multiple outages. Retailer used the term "lines unravelling". He has been told there is "a job in the system to get this sorted" Please get as much information from FM when signing off as possible and update William on 06 375 8381 There is also a fax that came in 07/02 09:06 am - no power. Powerco is aware of the ongoing issues with this piece of O/H Line. Musa Advised that he checked 80 Saunders Rd before Reload/reliven and that were no Lines down. Reload at Fuses I26 2 x 15A Ongoing HV line Issues | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.00923 | 11 | 2017 | 2017-02-07 | C | 10 | 0.00923 | 2.997e-05
1 | 15880181 | 2017-02-23 08:43 | 2017-02-23 16:59 | 496 | 90 | 8910 | 0.026698 | 0.025888 | 0.00053934 | NAPA ID:27308 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | 027308 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3738 | NONE | Finish install of new safelink (13127), connecting cables from IC3141 to 13127/3 and TC3738 to 13127/4 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.012944 | 5.5 | 2017 | 2017-02-23 | B | 90 | 0.025888 | 0.00053934
1 | 15880789 | 2017-02-21 08:30 | 2017-02-21 15:15 | 405 | 27 | 10935 | 0.032766 | 0.032523 | 8.0904e-05 | NAPA ID:27684 TP_KOPU GXP > THAMES SUB > THAMES COAST | 11 | Planned | 027684 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 20 Te Puru Creek Rd, Thames | NONE | TO REPLACE EXISTING H STRUCTURE WITH NEW 11M BUSCK POLE. | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.016262 | 5.5 | 2017 | 2017-02-21 | B | 27 | 0.032523 | 8.0904e-05
1 | 15881302 | 2017-02-21 09:10 | 2017-02-21 14:04 | 294 | 2 | 588 | 0.0017619 | 0.001743 | 5.9928e-06 | NAPA ID:27535 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 027535 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | tc1132 | NONE | Disconnect existing drop-out fuses on transformer structure TC1132 using Live-line techniques and then replace drop-out fuses, transformer and LV crossarm. Reconnect drop-out fuses using live-line techniques and commission replacement transformer. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0008715 | 5.5 | 2017 | 2017-02-21 | B | 2 | 0.001743 | 5.9928e-06
1 | 15881626 | 2017-02-22 09:00 | 2017-02-22 13:24 | 264 | 13 | 3432 | 0.010284 | 0.010166 | 3.8953e-05 | NAPA ID:27688 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 027688 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R12878 | POLE | TO REPLACE POLES R12878 & R12883 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.005083 | 5.5 | 2017 | 2017-02-22 | B | 13 | 0.010166 | 3.8953e-05
1 | 15881912 | 2017-02-20 08:30 | 2017-02-20 15:21 | 411 | 181 | 44951 | 0.1347 | 0.13307 | 0.00078208 | NAPA ID:28546 TP_MASTERTON GXP > TE ORE ORE SUB > COLOMBO RD | 11 | Planned | 028546 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 833246 | NONE | replace red tag pole 833246. 10 day shutdown notice RED TAG POLE (Gavin.P.) | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.066534 | 5.5 | 2017 | 2017-02-20 | B | 181 | 0.13307 | 0.00078208
1 | 15886850 | 2017-02-08 08:48 | 2017-02-08 16:04 | 436 | 64 | 13468 | 0.040364 | 0.039788 | 0.00038362 | NAPA ID:28751 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | 028751 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B0758 | CONDUCTOR - REPAIR/REHANG | Resag B0758-B0757, Repair B0758, RPL TC2894 Structure | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.019894 | 5.5 | 2017 | 2017-02-08 | B | 64 | 0.039788 | 0.00038362
1 | 15887834 | 2017-02-08 01:41 | 2017-02-08 03:27 | 105 | 213 | 9002.1 | 0.026979 | 0.025064 | 0.00063836 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 7 | UNKNOWN | CB 7 tripped B Ph N O/C l/O No Fault found during sectionlising | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.025064 | 11 | 2017 | 2017-02-08 | C | 213 | 0.025064 | 0.00063836
1 | 15888812 | 2017-02-08 07:34 | 2017-02-08 11:57 | 262 | 213 | 20583.8 | 0.06169 | 0.059774 | 0.00063836 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 788412 | INSULATOR | CB 7 A/R, L/O, E/F. Patrolled & Sectionalised with a line down found at Pole 788412 & a floating conductor found at Pole 788312 Materials used: Pole 788412- 5mtrs squirrel conductor, 2 sleeves, 1x Pin & Insulator, & 2x Binders Pole 788312- 3x Pins & Insulators, & 3x Binders | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.059774 | 11 | 2017 | 2017-02-08 | C | 213 | 0.059774 | 0.00063836
1 | 15889759 | 2017-02-08 08:42 | 2017-02-08 09:16 | 34 | 217 | 7414.1667 | 0.02222 | 0.020269 | 0.00065035 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB R11 | UNKNOWN | Thorough line patrol carried out (poles, transformers, insulators surrge arrestors and all other equipment) with nothing obvious found | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.020269 | 11 | 2017 | 2017-02-08 | C | 217 | 0.020269 | 0.00065035
1 | 15895444 | 2017-02-23 09:15 | 2017-02-23 11:11 | 116 | 21 | 2436 | 0.0072991 | 0.00711 | 6.2923e-05 | NAPA ID:27336 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 027336 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP448 | NONE | Remove TEMP09 Hardware and Reconductor between IP448-IC368. Works location: Thames Cost Rd, Thames. WO 30019659 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.003555 | 5.5 | 2017 | 2017-02-23 | B | 21 | 0.00711 | 6.2923e-05
1 | 15895497 | 2017-02-23 09:15 | 2017-02-23 10:30 | 75 | 3 | 225 | 0.00067418 | 0.000647 | 8.989e-06 | NAPA ID:27052 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > SANDHURST | 11 | Planned | 027052 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD5-174 | NONE | Replace transformer TD5-174. Works location: Mangatawa Lane. WO 30019175 | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.0003235 | 5.5 | 2017 | 2017-02-23 | B | 3 | 0.000647 | 8.989e-06
1 | 15895508 | 2017-02-08 18:31 | 2017-02-08 19:28 | 57 | 102 | 3347 | 0.010031 | 0.009113 | 0.00030569 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P37259 | JUMPER | Broken Jumper found as part of dispatch job - cause age Isolated at ABS L41 with fuses opened at Transformers T1/388 & T1/211 due to embedded generation Used 1 mtr conductor 4 x connectors | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.009113 | 11 | 2017 | 2017-02-08 | C | 102 | 0.009113 | 0.00030569
1 | 15895580 | 2017-02-23 09:01 | 2017-02-23 14:13 | 312 | 6 | 1873.8 | 0.0056146 | 0.00556 | 1.7978e-05 | NAPA ID:27046 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > SANDHURST | 11 | Planned | 027046 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD5-005 | NONE | Replace Pole, crossarms & hardware. Works location: Mangatawa Lane. WO 30019175 | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.00278 | 5.5 | 2017 | 2017-02-23 | B | 6 | 0.00556 | 1.7978e-05
1 | 15895772 | 2017-02-16 09:28 | 2017-02-16 14:52 | 324 | 18 | 5844 | 0.017512 | 0.01735 | 5.394e-05 | NAPA ID:28764 TP_BRUNSWICK GXP > KAI IWI SUB > MISSION RD | 11 | Planned | 028764 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace red tag 11kv pole number 782812 | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.008675 | 5.5 | 2017 | 2017-02-16 | B | 18 | 0.01735 | 5.394e-05
1 | 15896439 | 2017-02-08 18:32 | 2017-02-09 01:26 | 413 | 199 | 37809.0833 | 0.11331 | 0.11152 | 0.0020709 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | R0936 | CONDUCTOR - REPAIR/REHANG | RC28 tripped to L/O. O/C flag. Line sectionalised & patrolled with temp line break created at pole R0831 for additional isolating. Tree branch eventually located over line at pole R0936. Removed with hot stick. Temp line break closed. All supply restored. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.11152 | 11 | 2017 | 2017-02-08 | C | 199 | 0.11152 | 0.0020709
1 | 15898548 | 2017-02-08 18:58 | 2017-02-09 01:34 | 396 | 844 | 86139.1667 | 0.25816 | 0.25057 | 0.0072737 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9455/2 | CABLE - REPLACE LESS THAN 5 METRES | CB 6 Mikkelsen Rd sub tripped to L/O. O/C flag. Subsequent Hi current & low voltage alarms activating on T1 & T2 at Mikkelsen sub indicated very heavy fault. Reports of explosion & arcing received on cnr of Shakespeare Rd & Farmer St identified a tree branch entangled in HV lines at pole C3489. Branch removed from line but CB 6 again tripped on attempted reclose. Again very heavy fault indications received. Line sectionalised and O/H patrolled (most of it U/G) and a fault on cable beyond Sw/gear 9455/2 identified. No backfeeds available, generators connected to transformers TC3813 & TP957. Cable fault location/repair to be commenced 09/02/17. On reflection, its possible the faulted cable was always initial problem with the branch located in line possibly caused by repulsing lines following initial trip and may explain heavy fault indications received?? Restoration of supply to transformer TC4007 was left until completion of sectionalising as report of flash at the transformer was one of several reports received following trip. Discussion with customer who reported it confirmed it was only the explosion he heard , no flash as indicated on fault info received. DNO 170206 created for cable fault location/repair in morning. | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.25057 | 11 | 2017 | 2017-02-08 | C | 844 | 0.25057 | 0.0072737
1 | 15902918 | 2017-02-08 23:32 | 2017-02-09 02:44 | 192 | 353 | 25483.0333 | 0.076373 | 0.073198 | 0.0010579 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | K0584 | NONE | CB 3 Tahuna sub tripped to L/O. E/F flag. Line sectionalised & patrolled. Possom located & removed from pole K0584. All supply restored. Note - no possum guard fitted to any of the poles on section of line beyond ABS 576. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.073198 | 11 | 2017 | 2017-02-08 | C | 353 | 0.073198 | 0.0010579
1 | 15906572 | 2017-02-09 06:51 | 2017-02-09 12:35 | 344 | 239 | 11767.4667 | 0.035267 | 0.033117 | 0.00071927 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3353T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Recloser 6497/2 tripped on E/F flags, line was sectionalised and a fault was found at transformer 3353T, fuses 5739 had been isolated by faultman that had been attending a part power fault call at transformer 3353T under OMS 15906434. At time of tripping were not certain if fault was at transformer only after supply was restored to rest of feeder and transformer 3353T was inspected did we find transformer was damaged. 2R - Require Transformer Replacement at 3353T Generator to be installed at transformer 3354T 08:05, off 12:25, on 12:35 | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.033117 | 11 | 2017 | 2017-02-09 | C | 239 | 0.033117 | 0.00071927
1 | 15907309 | 2017-02-09 07:25 | 2017-02-09 09:33 | 127 | 1034 | 102253.05 | 0.30645 | 0.29715 | 0.0030989 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 242 | UNKNOWN | 0754 Only Paul Clutterbuck is attending, dual name due to error at HUB, HUB are awaiting Jeremy Hill to get staff Scott Bullock & Others have done a lot of testing on Silver Ferns Farm s Gear About from 10:00 to end of job Found Main Switch on Silver Fern Farm to be faulty Isolated and replaced switch but this was not the Fault that Caused the tripping We think that the ABS used for back Feed is the problem which has been repaired under DNO 170207 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.29715 | 11 | 2017 | 2017-02-09 | C | 1034 | 0.29715 | 0.0030989
1 | 15909851 | 2017-02-09 07:53 | 2017-02-09 09:17 | 84 | 957 | 73673.0167 | 0.22079 | 0.21219 | 0.0028681 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Recloser 3139/2 & 3141/2 | UNKNOWN | 33kV CB 3139 and 3141 both tripped to lockout. LOS to Tuhitarata sub. Unable to back feed sub remotely as per notes below. On line LFI's are not providing any information, are hit and miss with providing basics let alone fault data, require follow up or removal with a reliable product. Re-livened 33kV line after a cursory patrol. Multiple issue with SMC not being proactive in getting resources in a timely manner, escalated by NCTL to Phil Marsh for prompt follow up with SMC manager. Over view over of resourcing issues below: 0808 phoned HUB to find out who is attending , asked Joanne. Also advised now need an extra 1R 0815 phoned HUB still trying to find staff , Denis Rose is FRM who is trying to get staff advised of SAIDI implications and number of customers off 0817 phoned Denis said Sam and Lucas are attending this not reflected on OMS , Denis to ring HUB to have this corrected,advised of 0825 request for fleet link number of Sam 503, and Adrian 527 . Sam to contact Control for direction 0831 Lucas advises Control he is third man, still acknowledged NOC Note: Unable to back feed sub remotely due to field not yet being commissioned to service. Installed but not commissioned. Device 11095 on TUH C927 and Devices 11093 Reg set and 11094 also not commissioned. Having these devices installed and commissioned would have significantly reduced SAIDI loss. Unknown as to when these devices are due for commissioning. Question: Why are devices (such as these) not being commissioned on completion of installation? Why is Powerco tolerating long delays to commissioning equipment? 33kV line Patrolled in depth no fault cause found | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.21219 | 33 | 2017 | 2017-02-09 | C | 957 | 0.21219 | 0.0028681
1 | 15912970 | 2017-02-25 10:15 | 2017-02-25 13:20 | 185 | 9 | 1665 | 0.0049888 | 0.004907 | 2.6966e-05 | NAPA ID:28566 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 028566 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4356 | NONE | Change transformer and HV fuses and x-arm on TC4356. Works location: Orchard Rd West, Ngatea. WO 30019177 | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0024535 | 5.5 | 2017 | 2017-02-25 | B | 9 | 0.004907 | 2.6966e-05
1 | 15913530 | 2017-02-09 09:15 | 2017-02-09 12:38 | 202 | 13 | 2636.6167 | 0.0079018 | 0.007784 | 3.896e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | P11436 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses F16 2 x 10A Cause unknown but Should have been picked up by Robin Smith OMS 16906449. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.007784 | 11 | 2017 | 2017-02-09 | C | 13 | 0.007784 | 3.896e-05
1 | 15913667 | 2017-03-02 09:00 | 2017-03-02 15:48 | 408 | 13 | 5304 | 0.015891 | 0.015774 | 3.8949e-05 | NAPA ID:28798 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 028798 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP448 | NONE | Hardware changes between IP448 and TEMP09. Connection & disconnection of Generator at Transformer TC1500 under same AP as main Job. Works location: Thames Coast Rd, Thames. WO 30019659 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.007887 | 5.5 | 2017 | 2017-03-02 | B | 13 | 0.015774 | 3.8949e-05
1 | 15913694 | 2017-03-01 09:40 | 2017-03-01 12:00 | 140 | 2 | 280 | 0.0008389 | 0.00082 | 5.9921e-06 | NAPA ID:27625 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 027625 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3568 | NONE | To replace the 11kV arms & Fuses, 400V Arm and install a 400V Fuse/Disconnector on TC3568. Works location: Westlea Rd, Cambridge. WO 30019182 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.00041 | 5.5 | 2017 | 2017-03-01 | B | 2 | 0.00082 | 5.9921e-06
1 | 15913909 | 2017-03-03 09:50 | 2017-03-03 14:12 | 262 | 33 | 8646 | 0.025903 | 0.025606 | 9.8868e-05 | NAPA ID:28616 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11 | Planned | 028616 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 5231E | NONE | isolate Tx 5231E , Disconnect Hv and Lv cables , remove Tx from pad , replace broken Tx pad , reinstall Tx. Works location: Disraeli St, Hawera. WO 30015683 | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.012803 | 5.5 | 2017 | 2017-03-03 | B | 33 | 0.025606 | 9.8868e-05
1 | 15914167 | 2017-02-24 10:35 | 2017-02-24 16:52 | 376 | 122 | 25151.65 | 0.075362 | 0.074265 | 0.00036555 | NAPA ID:28575 TP_STRATFORD GXP | 11 | Planned | 028575 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5455 | NONE | Shut 5 of week 20/2/17 to 25/2/17 - Install 11Kv dead line break at pole 737822.Liven Pembroke Rd back up replace Dno Abs 5455 with Sectos Sw & associated links + Close line breaks at poles 372414 & 737603 + 33Kv poles as well. Close line break Live at pole 737822. Note: School fed from TX 2841T will have small generator installed on water pump for toilets as organised with school . ABS 6691 added to isolation point re embedded generation TX 4485T . | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.037132 | 5.5 | 2017 | 2017-02-24 | B | 122 | 0.074265 | 0.00036555
1 | 15914212 | 2017-02-27 09:38 | 2017-02-27 15:10 | 332 | 2 | 664 | 0.0019895 | 0.001971 | 5.9923e-06 | NAPA ID:27091 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 027091 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE3-093 | NONE | Rebuild Transformer Structure TE3-093. Works location: Keenan Rd. WO 30019175 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0009855 | 5.5 | 2017 | 2017-02-27 | B | 2 | 0.001971 | 5.9923e-06
1 | 15914223 | 2017-02-09 14:22 | 2017-02-09 15:05 | 43 | 35 | 1505 | 0.0045104 | 0.004195 | 0.00010489 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc5057 | JUMPER | Email sent to retailer re outage to repair HV jumper at TX TC5057 new OMS job number when Alan opened ABS is OMS 1591659. Found jumper broken at tc5057. Isolated at ABS 287, repaired jumper and relivened | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.004195 | 11 | 2017 | 2017-02-09 | C | 35 | 0.004195 | 0.00010489
1 | 15914542 | 2017-02-09 13:13 | 2017-02-09 16:02 | 168 | 6 | 1013.5 | 0.0030374 | 0.002983 | 1.7982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762643 | FUSE - ELEMENT/LINK (HV) | IS 15914542 LINKED? Advised Shannon of linked job branch on line pulling down avacado trees with digger and clashed lines - NDR # N100304 4.8m lines that run through the orchard FM will put in urgent defect for these lines to be raised | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.002983 | 11 | 2017 | 2017-02-09 | C | 6 | 0.002983 | 1.7982e-05
1 | 15914611 | 2017-03-03 08:53 | 2017-03-03 09:39 | 46 | 19 | 874 | 0.0026185 | 0.002447 | 5.6924e-05 | NAPA ID:27589 TP_OPUNAKE GXP > TASMAN SUB > TE KIRI | 11 | Planned | 027589 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 714473 | NONE | replace Hv pin Arm. Works location: Eltham Rd, Te Kiri. WO 30015292 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0012235 | 5.5 | 2017 | 2017-03-03 | B | 19 | 0.002447 | 5.6924e-05
1 | 15914694 | 2017-02-09 17:42 | 2017-02-09 18:05 | 23 | 7 | 161 | 0.00048251 | 0.000419 | 2.0979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 216 NO 3 ROAD | INSULATOR | Isolated transformer at HT fuses to carry out repairs on LT bushings Off 17:42 On 18:05 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.000419 | 11 | 2017 | 2017-02-09 | C | 7 | 0.000419 | 2.0979e-05
1 | 15914773 | 2017-02-09 16:32 | 2017-02-09 16:45 | 13 | 3 | 39 | 0.00011688 | 8.9e-05 | 8.9908e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tf5-053 | INSULATOR | Isolated transformer via HT fuses to check LT bushings due to sparking Repaired LV jumper on transformer bushing Off 16:32 On 16:45 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 8.9e-05 | 11 | 2017 | 2017-02-09 | C | 3 | 8.9e-05 | 8.9908e-06
1 | 15914824 | 2017-02-09 14:17 | 2017-02-09 19:47 | 330 | 837 | 35860.3167 | 0.10747 | 0.099946 | 0.0025085 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | C1241 | POLE | CB 8 tripped on A & C phase O/C and ground fault flags, received at call of fire under lines at pole C3254 and a car vs pole C1241. For fire services to put out the fire under the 11KV lines CB 1 had to be opened by NC at the desk, line was isolated at ABS's 582, 2506 and IC1112 to replace the pole C1241 hit by car. Line was also de energised between CB 8 and ABS IC688 to check 11KV cables were all OK, cables were all clear and supply restored except to isolated area. This fault also caused 33KV CB 40 at Waitoa Sub to trip due to the flare up of the 11KV line fault, CB 40 was after all was inspected. NDR: 56453 1 x 11 metre busck pole, 1 x single HV arm, 1 x double LV arm materials required. LV - FM advised about 6 customers are still without power fed from TX: TC2357. Properties need to be seen by an electrical inspector. All porerties should be restored by tonight 09/02. FM to call if they have to leave any properties isolated. - FM has advised all power has been restored. Spoken with Control all ok to complete. NOC note: Pole that was hit, C1211 was due to be replaced 10/02/17 by Northpower. This complete pole, was all made off lying adjacent to the hit pole. This was not used, Downer brought in another pole and assets. Question: Why would the built pole, already to be used, not be used? Would having used this pre-built pole have saved time and thus reduced SAIDI loss to Powerco? | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.099946 | 11 | 2017 | 2017-02-09 | C | 837 | 0.099946 | 0.0025085
1 | 15916712 | 2017-02-09 14:58 | 2017-02-09 17:50 | 171 | 1 | 171.7667 | 0.00051478 | 0.000505 | 2.9969e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 133 & Transformer X2831 | FUSE - ELEMENT/LINK (HV) | 2 X 2 Amp HT Fuses at transformer X2831 & 1 X 3 Amp at Fuses 133 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000505 | 11 | 2017 | 2017-02-09 | C | 1 | 0.000505 | 2.9969e-06
1 | 15916891 | 2017-02-09 15:24 | 2017-02-09 18:01 | 157 | 555 | 36806.6667 | 0.11031 | 0.10532 | 0.0016633 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | O895 | CONDUCTOR - REPAIR/REHANG | CB 1 L/O on O/C & E/F. Backfeed from SC08 to RC27. Sectionalised and found branch on centre phase at pole O895, removed branch and relivened | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.10532 | 11 | 2017 | 2017-02-09 | C | 555 | 0.10532 | 0.0016633
1 | 15920351 | 2017-03-01 09:10 | 2017-03-01 14:58 | 348 | 15 | 5220 | 0.01564 | 0.015504 | 4.4941e-05 | NAPA ID:24875 TP_WAVERLEY GXP > WAITOTARA | 11 | Planned | 024875 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 359165 | NONE | run new wire from pole 781706 to pole 359165. Works location: Brewer Rd. WO 30017731 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.007752 | 5.5 | 2017 | 2017-03-01 | B | 15 | 0.015504 | 4.4941e-05
1 | 15920379 | 2017-03-02 09:10 | 2017-03-02 14:30 | 320 | 1 | 320 | 0.00095873 | 0.000949 | 2.996e-06 | NAPA ID:28030 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11 | Planned | 028030 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 796149 | NONE | break 11 kv jumpers by hot stick method at pole796149 , to allow change of 11 kv arms under A/P at pole 796151 , straighten t/f pole , trees to be remove in large span. Works location: Potaka Rd, Taihape. WO 30032266 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0004745 | 5.5 | 2017 | 2017-03-02 | B | 1 | 0.000949 | 2.996e-06
1 | 15920395 | 2017-03-03 09:49 | 2017-03-03 12:15 | 146 | 1 | 146 | 0.00043742 | 0.000428 | 2.9959e-06 | NAPA ID:28033 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 028033 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 785971 | NONE | disconnect 11 kv jumpers at pole 785971 by hot stick method to allow for A/P to remove larch pole 785979 in slip zone , resag 11kv wires , reconnect 11 kv jumpers at pole 785971. Works location: Ruanui Rd, Taihape. WO 30034624 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000214 | 5.5 | 2017 | 2017-03-03 | B | 1 | 0.000428 | 2.9959e-06
1 | 15920433 | 2017-03-03 09:15 | 2017-03-03 14:17 | 302 | 1 | 302 | 0.00090479 | 0.000895 | 2.9959e-06 | NAPA ID:27548 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027548 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1283 | NONE | replace t1283. Works location Upper Plain Rd, Masterton. WO 30033869 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0004475 | 5.5 | 2017 | 2017-03-03 | B | 1 | 0.000895 | 2.9959e-06
1 | 15920450 | 2017-03-03 09:37 | 2017-03-03 14:15 | 278 | 10 | 2780 | 0.0083289 | 0.008238 | 2.996e-05 | NAPA ID:27731 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 027731 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T/42 | NONE | To replace red tagged pole p06232 TX pole T9/42 (GP). Works location: Manuhara Rd. OW 30023940 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.004119 | 5.5 | 2017 | 2017-03-03 | B | 10 | 0.008238 | 2.996e-05
1 | 15920572 | 2017-03-03 09:33 | 2017-03-03 11:22 | 109 | 13 | 1417 | 0.0042453 | 0.004128 | 3.8948e-05 | NAPA ID:27794 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027794 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7701 | NONE | Replace 11kv xarms at different worksites on spur line feed off 11kv links 7701 upper plain rd. Works location: Upper Plain Rd, Masterton. WO 30034406 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.002064 | 5.5 | 2017 | 2017-03-03 | B | 13 | 0.004128 | 3.8948e-05
1 | 15920604 | 2017-03-04 07:39 | 2017-03-04 09:52 | 133 | 1 | 133 | 0.00039846 | 0.000389 | 2.9959e-06 | NAPA ID:27654 TP_BRUNSWICK GXP > CASTLECLIFF SUB > PURIRI ST | 11 | Planned | 027654 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/Gear 2045 | NONE | Isolate switchgear 2045 due to failed acoustic test. Clean cable terminations and reliven. Works location: Waters & Farr. WO 30034170 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.0001945 | 5.5 | 2017 | 2017-03-04 | B | 1 | 0.000389 | 2.9959e-06
1 | 15920643 | 2017-03-07 10:00 | 2017-03-07 13:40 | 220 | 8 | 1760 | 0.0052726 | 0.0052 | 2.3967e-05 | NAPA ID:28450 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 028450 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 794665 | NONE | Lift conductors onto new installed pole old pole number 794665. Works location: Taurimu Turakina Valley, Marton. WO 30032488 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.0026 | 5.5 | 2017 | 2017-03-07 | B | 8 | 0.0052 | 2.3967e-05
1 | 15920674 | 2017-03-07 08:45 | 2017-03-07 11:55 | 190 | 2 | 380 | 0.0011384 | 0.00112 | 5.9916e-06 | NAPA ID:27314 TP_BRUNSWICK GXP > CASTLECLIFF SUB > HEADS RD | 11 | Planned | 027314 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X183 | NONE | Replace X183 for new 200kva Tx. Works location: Todd St. WO 30033929 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.00056 | 5.5 | 2017 | 2017-03-07 | B | 2 | 0.00112 | 5.9916e-06
1 | 15920686 | 2017-03-07 08:30 | 2017-03-07 13:22 | 292 | 2 | 584 | 0.0017496 | 0.001731 | 5.9916e-06 | NAPA ID:27797 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027797 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7695 | NONE | replace 11kv poles and hardware. Works location: Upper Plain Rd, Masterton. WO 30034406 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0008655 | 5.5 | 2017 | 2017-03-07 | B | 2 | 0.001731 | 5.9916e-06
1 | 15920807 | 2017-03-09 08:45 | 2017-03-09 11:50 | 185 | 1 | 185 | 0.00055421 | 0.000545 | 2.9957e-06 | NAPA ID:27798 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027798 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8153 | NONE | Replace 11kv poles and hardware. Works location: Upper Plain Rd, Masterton. WO 30034406 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0002725 | 5.5 | 2017 | 2017-03-09 | B | 1 | 0.000545 | 2.9957e-06
1 | 15921869 | 2017-02-10 03:31 | 2017-02-10 06:55 | 204 | 32 | 6540.8 | 0.019602 | 0.019314 | 9.5901e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709924 | FUSE - ELEMENT/LINK (HV) | 2 x 15 @ fuses 6433 06:55 swan | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.019314 | 11 | 2017 | 2017-02-10 | C | 32 | 0.019314 | 9.5901e-05
1 | 15922179 | 2017-03-03 10:06 | 2017-03-03 11:14 | 68 | 22 | 1496 | 0.004482 | 0.004284 | 6.5912e-05 | NAPA ID:27862 TP_HUIRANGI GXP > BELL BLOCK SUB > LEPPERTON | 11 | Planned | 027862 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 745225 | NONE | To change xarm on pole 745225 at Powerco's request. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002142 | 5.5 | 2017 | 2017-03-03 | B | 22 | 0.004284 | 6.5912e-05
1 | 15922566 | 2017-03-06 10:13 | 2017-03-06 16:09 | 356 | 7 | 2494.6833 | 0.0074737 | 0.00741 | 2.0971e-05 | NAPA ID:27679 TP_HINUERA GXP | 11 | Planned | 027679 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP409 | NONE | Replace pole HINTIR004 with ABS IP409. Isolate 33kV and install line breaks for preparation for 9am shutdown. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.003705 | 5.5 | 2017 | 2017-03-06 | B | 7 | 0.00741 | 2.0971e-05
1 | 15923214 | 2017-03-07 09:00 | 2017-03-07 14:48 | 348 | 33 | 11484 | 0.034404 | 0.034107 | 9.8862e-05 | NAPA ID:28266 TP_STRATFORD GXP > DOUGLAS SUB > TOKO | 6.6 | Planned | 028266 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 740350 | NONE | Install new stay & straighten Hv pole 740350 , cut trees at poles 740400 & at Tx 3186 on Ruapuha rd | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.017053 | 3.3 | 2017 | 2017-03-07 | B | 33 | 0.034107 | 9.8862e-05
1 | 15923373 | 2017-03-07 08:45 | 2017-03-07 15:17 | 392 | 37 | 14504 | 0.043451 | 0.043118 | 0.00011085 | NAPA ID:28216 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 028216 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K1550 | NONE | Replace-straighten poles, crossarms and hardware. Install TEMP73 Links at Pole K1550. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.021559 | 5.5 | 2017 | 2017-03-07 | B | 37 | 0.043118 | 0.00011085
1 | 15923503 | 2017-02-15 09:53 | 2017-02-15 15:23 | 330 | 19 | 6270 | 0.018789 | 0.018618 | 5.6937e-05 | NAPA ID:28840 TP_MANGAMAIRE GXP > ALFREDTON SUB > BROOKLANDS | 11 | Planned | 028840 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | To replace 11kv pole I26 install temp fuses at pole P28470 replace 11kv xarms | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.009309 | 5.5 | 2017 | 2017-02-15 | B | 19 | 0.018618 | 5.6937e-05
1 | 15923579 | 2017-03-07 09:06 | 2017-03-07 11:45 | 159 | 6 | 954 | 0.002858 | 0.002804 | 1.7975e-05 | NAPA ID:27841 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 6.6 | Planned | 027841 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 370870 | NONE | Installing new lv conductor between poles 370870-763064 isolating HV fuses for safety as the jumpers are to close to the LV lines. | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.001402 | 3.3 | 2017 | 2017-03-07 | B | 6 | 0.002804 | 1.7975e-05
1 | 15924638 | 2017-02-10 16:32 | 2017-02-10 20:58 | 266 | 256 | 19854.55 | 0.059502 | 0.0572 | 0.00076721 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 230219 | CONDUCTOR - REPAIR/REHANG | ( PGA 7 ) recloser S6031 tripped A, B & C Ph O/C, E/F, L/O Lines down x 2 beyond ABS S6011, Isolation between ABS S6011 & ABS SF6 039 5.20pm Police called to advise that there is another line down at 264 Allport road police event number P028464343 - FM is already on Allport Road and they know about this job - 5.24pm called police back and advised | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0572 | 11 | 2017 | 2017-02-10 | C | 256 | 0.0572 | 0.00076721
1 | 15927245 | 2017-02-10 18:05 | 2017-02-10 19:08 | 63 | 43 | 2709 | 0.0081187 | 0.007732 | 0.00012887 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4288 | FUSE - ELEMENT/LINK (HV) | Staywire over HT at Pole 784178 Removed using Hot Sticks Isolated at ABS 1026 Staywire to be repaired on 11/02/17 under Find & Fix | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.007732 | 11 | 2017 | 2017-02-10 | C | 43 | 0.007732 | 0.00012887
1 | 15929878 | 2017-02-11 07:52 | 2017-02-11 08:13 | 20 | 149 | 866.8333 | 0.0025978 | 0.001258 | 0.00044653 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5609 | JUMPER | Refer OMS 15929482 for details - 2 seperate OMS outages for same fault, got messy | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.001258 | 11 | 2017 | 2017-02-11 | C | 149 | 0.001258 | 0.00044653
1 | 15930106 | 2017-02-11 09:28 | 2017-02-11 10:43 | 75 | 3 | 225 | 0.0006743 | 0.000647 | 8.9906e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3147 | STAY WIRE | called and emailed SMC Called advised of safety process - cust poss due to sheep rubbing up to stay wire. Transformer TC3147 offloaded to replace broken stay wire ( wire close to live H/V conductor ) stay wire repaired all servive restored Materials 10 x meters stay wire, 1 x dead end | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000647 | 11 | 2017 | 2017-02-11 | C | 3 | 0.000647 | 8.9906e-06
1 | 15930315 | 2017-02-11 10:28 | 2017-02-11 10:58 | 30 | 36 | 1075 | 0.0032216 | 0.002897 | 0.00010789 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12628 | AIR BREAK SWITCH - ABS (HV) | Planned job initially being carried out to replace ABS S33 (LLP NAPA 28559-1) but considered too dangerous to do live. ABS had deteriorated with a broken insulator hanging by a jumper and broken insulators at the ABS. Isolation made between ABS S2, S34 and S36 with backfeed at ABS U23. All ABS Jumpers cut away at S33 for safety and a further outage to be planned to carryout replacement. (Phil Barnes, Robin Smith on site). | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.002897 | 11 | 2017 | 2017-02-11 | C | 36 | 0.002897 | 0.00010789
1 | 15930381 | 2017-02-11 10:38 | 2017-02-11 12:19 | 101 | 689 | 69589 | 0.20855 | 0.20235 | 0.0020648 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P33478 | POLE | 5.46 pm advised Dianne at svs hub & emailed Advised Control 17.50pm ETA 25mins advised fire service Electra called advising that they took a call from Police - P028464805 advising of this job also. - called police comms to advise of eta Pole P33478 damaged. Has been made safe and will replace pole tomorrow (Saturday) NDR # N300287 Outage Carried out on Saturday 11/02/17 with isolation's from the recloser, ABS L33 and L36. Pole replaced along with all associated hardware. Relivened OK. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.20235 | 11 | 2017 | 2017-02-11 | C | 689 | 0.20235 | 0.0020648
1 | 15931413 | 2017-02-11 12:50 | 2017-02-11 14:35 | 105 | 10 | 1050 | 0.0031467 | 0.003056 | 2.9969e-05 |  | 11 | Planned | 028514 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W12665 | NONE | NAPA 28514: Replace line hardware and reconductor from Pole W12665. ( WHT 4 ) Fuses FC2314 opened to close line break pole W12665 & reconductor Line break cut at pole W2038 to isolate transformer structure TC3206 damaged in fire ( house destroyed ) Generator removed from transformer TC4877 normal supply re instated Normal supply to transformer TC4877 re instated no customer home main sw to house left off with note 11 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.001528 | 5.5 | 2017 | 2017-02-11 | B | 10 | 0.003056 | 2.9969e-05
1 | 15931550 | 2017-02-11 16:30 | 2017-02-11 21:37 | 307 | 9 | 2763 | 0.0082804 | 0.008199 | 2.6972e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1737N | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 1 HT fuse blown at Transformer 1737N. (Transformer faulty, requires replacement). (NOTE: 1 HT Fuse blew at 8464 when re livening attempt, reloaded OK - 10A 1 X 50 KVA ). | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.008199 | 11 | 2017 | 2017-02-11 | C | 9 | 0.008199 | 2.6972e-05
1 | 15931817 | 2017-03-17 09:55 | 2017-03-17 14:14 | 259 | 4 | 1036 | 0.0031032 | 0.003067 | 1.1981e-05 | NAPA ID:28517 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 028517 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P04764 | NONE | To replace red tagged poles (GP) poles P04764 & P04765 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0015335 | 5.5 | 2017 | 2017-03-17 | B | 4 | 0.003067 | 1.1981e-05
1 | 15931819 | 2017-03-19 09:00 | 2017-03-19 10:04 | 64 | 130 | 8320 | 0.024921 | 0.023752 | 0.00038938 | NAPA ID:28562 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 028562 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P18138 | NONE | Replace pole P18138. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.011876 | 5.5 | 2017 | 2017-03-19 | B | 130 | 0.023752 | 0.00038938
1 | 15931821 | 2017-03-15 08:46 | 2017-03-15 14:44 | 358 | 64 | 22939.7333 | 0.068715 | 0.068139 | 0.00019171 | NAPA ID:27808 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027808 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Skeets Rd | NONE | Replacing 11kv poles and hardware | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.03407 | 5.5 | 2017 | 2017-03-15 | B | 64 | 0.068139 | 0.00019171
1 | 15932245 | 2017-02-11 22:20 | 2017-02-12 01:34 | 193 | 247 | 17132.4833 | 0.051344 | 0.049123 | 0.0011718 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 725958 | NONE | Found Opposum at pole 725958 Removed using Hot Sticks | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.049123 | 11 | 2017 | 2017-02-11 | C | 247 | 0.049123 | 0.0011718
1 | 15934184 | 2017-02-12 02:54 | 2017-02-12 07:28 | 274 | 3 | 781.6 | 0.0023423 | 0.002315 | 8.9904e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13877 | FUSE - ELEMENT/LINK (HV) | 2 8 amp fuses blown at FC4005. line patrolled reloaded & livened | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002315 | 11 | 2017 | 2017-02-12 | C | 3 | 0.002315 | 8.9904e-06
1 | 15934201 | 2017-02-12 07:56 | 2017-02-12 09:24 | 88 | 7 | 619.7333 | 0.0018572 | 0.001794 | 2.0978e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5987 | FUSE - ELEMENT/LINK (HV) | 1 Phase down at Transformer 2185T. All 3 HT fuses removed to ascertain problem. Reclosed OK. Further patrol up road found 1 HT fuse out at 5987. Reloaded OK, 6A. Cause unknown. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001794 | 11 | 2017 | 2017-02-12 | C | 7 | 0.001794 | 2.0978e-05
1 | 15936300 | 2017-02-12 13:52 | 2017-02-12 15:33 | 100 | 111 | 8905.4 | 0.026688 | 0.02569 | 0.00033265 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | K45 | UNKNOWN | Tripping on recloser CB K45 on B,C Phase O/C and EF. Feeder patrolled / sectionalised but nothing found. Restored OK. Cause unknown. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.02569 | 11 | 2017 | 2017-02-12 | C | 111 | 0.02569 | 0.00033265
1 | 15936557 | 2017-02-12 16:05 | 2017-02-12 16:35 | 30 | 87 | 2610 | 0.0078217 | 0.007039 | 0.00026072 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P42838 | POLE | Car/pole reported along Stoney Creek Rd. Fire service requested safety isolation while injured passengers/ car were moved away. Isolation required between 11kV ABS E63 and E64. Supply restored OK after emergency service clear. No serious damage to pole. | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.007039 | 11 | 2017 | 2017-02-12 | C | 87 | 0.007039 | 0.00026072
1 | 15938847 | 2017-02-13 00:33 | 2017-02-13 02:30 | 117 | 1430 | 15375.9833 | 0.046079 | 0.033222 | 0.00066529 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P02734 | INSULATOR | Replaced1 X HT Insulator at next pole from P02734 | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.033222 | 11 | 2017 | 2017-02-13 | C | 1430 | 0.033222 | 0.00066529
1 | 15940945 | 2017-02-13 06:31 | 2017-02-13 07:15 | 43 | 10 | 435.5 | 0.0013051 | 0.001215 | 2.9968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09331 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp w3ind @i26 0715 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001215 | 11 | 2017 | 2017-02-13 | C | 10 | 0.001215 | 2.9968e-05
1 | 15941997 | 2017-02-13 07:06 | 2017-02-13 09:10 | 123 | 6 | 743.3 | 0.0022275 | 0.002173 | 1.7981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373430 | FUSE - ELEMENT/LINK (HV) | 7101 2 x8 wind 9:10 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002173 | 11 | 2017 | 2017-02-13 | C | 6 | 0.002173 | 1.7981e-05
1 | 15942740 | 2017-02-16 08:45 | 2017-02-16 15:04 | 379 | 24 | 9096 | 0.027258 | 0.027041 | 7.192e-05 | NAPA ID:28800 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028800 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Replace poles between 809548 & 809645. install 11KV Temp links 82 on pole 809578 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.01352 | 5.5 | 2017 | 2017-02-16 | B | 24 | 0.027041 | 7.192e-05
1 | 15942933 | 2017-02-13 07:40 | 2017-02-13 11:55 | 254 | 29 | 6483.55 | 0.01943 | 0.019169 | 8.6907e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 811673 | CONDUCTOR - REPAIR/REHANG | Check whether 419 KAIWAKA ROAD (OMS 15943004) is related sectionaliser C633 Trip No flags Lines down at pole 811673 due to trees isolated at ABS S1203 Repaired using 2 x Sleeves & 2m Conductor | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.019169 | 11 | 2017 | 2017-02-13 | C | 29 | 0.019169 | 8.6907e-05
1 | 15943022 | 2017-02-13 08:48 | 2017-02-13 09:39 | 51 | 9 | 459 | 0.0013755 | 0.001294 | 2.6971e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 776408 | CONDUCTOR - REPAIR/REHANG | Lines down - has caused fire. Approximately 200M down from intersection. Fire enroute - ETA required #F2245093 ndr047113 branch on line removed under ap @pole 776408 isolated at fuses 4205 lines checked no damage | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.001294 | 11 | 2017 | 2017-02-13 | C | 9 | 0.001294 | 2.6971e-05
1 | 15943105 | 2017-02-13 08:18 | 2017-02-13 09:19 | 60 | 302 | 18312.1333 | 0.054878 | 0.052162 | 0.00090503 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | spoke to hub chasing faultman CB XT 40 Trip O/C Line patrolled nothing found | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.052162 | 33 | 2017 | 2017-02-13 | C | 302 | 0.052162 | 0.00090503
1 | 15944501 | 2017-02-13 08:34 | 2017-02-13 11:00 | 145 | 117 | 15246.15 | 0.045689 | 0.044637 | 0.00035062 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Tinui CB C936 tripped on PH A & B OC | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.044637 | 11 | 2017 | 2017-02-13 | C | 117 | 0.044637 | 0.00035062
1 | 15945073 | 2017-02-13 08:56 | 2017-02-13 12:27 | 210 | 13 | 2737.3667 | 0.0082033 | 0.008086 | 3.8958e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 798399 | CONDUCTOR - REPAIR/REHANG | Line down - on Cross Creek Road - no road number given and phone number not valid. SMC advised. Please link 15946837 Lines down due to weather at Pole 798400. Repaired using 5m Conductor & 3 x Sleeves | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.008086 | 11 | 2017 | 2017-02-13 | C | 13 | 0.008086 | 3.8958e-05
1 | 15945080 | 2017-02-13 08:57 | 2017-02-13 13:47 | 290 | 123 | 17177.7 | 0.051478 | 0.050372 | 0.0003686 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819573 | CONDUCTOR - REPAIR/REHANG | 220 Underhill Road - trees on lines - lines on road - Owen Calson 027 233 7391 SMC advised 9:20am recloser C430 found open (non Scadaised) Line patrolled found lines down at pole 819573 isolated at Fuses 7522 NDR 21917 | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.050372 | 11 | 2017 | 2017-02-13 | C | 123 | 0.050372 | 0.0003686
1 | 15946955 | 2017-02-13 10:05 | 2017-02-13 13:40 | 215 | 398 | 68078.3333 | 0.20402 | 0.20044 | 0.0011927 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | cb2 trip O/C line patrolled nothing found | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.20044 | 11 | 2017 | 2017-02-13 | C | 398 | 0.20044 | 0.0011927
1 | 15947741 | 2017-02-28 09:57 | 2017-02-28 15:42 | 345 | 3 | 1035 | 0.003101 | 0.003074 | 8.9883e-06 | NAPA ID:27749 TP_TE MATAI GXP | 11 | Planned | 027749 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 221102 | NONE | Replace poles, hardware and conductor between poles 221102 & 394793 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001537 | 5.5 | 2017 | 2017-02-28 | B | 3 | 0.003074 | 8.9883e-06
1 | 15947751 | 2017-02-13 10:29 | 2017-02-13 13:55 | 206 | 183 | 16530.1833 | 0.049537 | 0.047892 | 0.00054841 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 839010 | CONDUCTOR - REPAIR/REHANG | 203 Kaka Amu Road - trees on line, now on fire - advised coops Rec C216 tripped found to be tree through line at pole 839010 Isolated at ABS 11062 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.047892 | 11 | 2017 | 2017-02-13 | C | 183 | 0.047892 | 0.00054841
1 | 15948827 | 2017-02-13 11:07 | 2017-02-13 12:11 | 64 | 1343 | 70821.1167 | 0.21224 | 0.20016 | 0.0063562 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | reports 2 faultman 1 vehicle CB 24 Trip O/C E/F line patrolled nothing found | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.20016 | 11 | 2017 | 2017-02-13 | C | 1343 | 0.20016 | 0.0063562
1 | 15952251 | 2017-02-13 12:41 | 2017-02-13 14:42 | 121 | 1343 | 48349.1 | 0.14489 | 0.13282 | 0.0042854 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21564 | INSULATOR | Cb 24 Tripped C Ph O/C E/F Faulty Insulator found at pole P21564 Used 1 x Insulator, 2 metres 35 mm earth wire | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.13282 | 11 | 2017 | 2017-02-13 | C | 1343 | 0.13282 | 0.0042854
1 | 15953882 | 2017-02-13 14:47 | 2017-02-13 16:43 | 116 | 1 | 116 | 0.00034763 | 0.000338 | 2.9967e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838539 | CONDUCTOR - REPAIR/REHANG | 2R - Report from Contractor of 11kV Lines down Past Blown Fuse 7877. Isolated at Fuses 7877, line repaired Used 10 mtrs conductor, 4 sleeves, 2 x binders NDR number to come | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.000338 | 11 | 2017 | 2017-02-13 | C | 1 | 0.000338 | 2.9967e-06
1 | 15954265 | 2017-02-13 13:25 | 2017-02-14 08:31 | 1145 | 480 | 21018.65 | 0.062988 | 0.058672 | 0.0014385 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224715 | CONDUCTOR - REPAIR/REHANG | 1.29 called hub to advise CB 8 tripped due to fault past Recloser 9502. Hot line tag was applied to CB 8 for NAPA 28653 this resulted in sensitive earth settings dropping the feeder instead of allowing recloser 9502 to clear the fault.line patrolled multiple faults between recloser 9502 & ABS SF5-044. Lins down past fuses SF5-003, Jumper blown off the bottom of fuses SF5-024. Line isolated past fuses SF5-008 due to pole from kiwi fruit orchard being very close to the 11kV wires, left off for safety. Recloser 9502 closed successfully after these isolations. Jumper from fuses SF5-024 Pulled clear with hotstick. Centre fuse removed as 2 phase transformers past this point. DNO created to fix this jumper. Lines repaired past fuses SF5-003. Joe:- Transformer TF5-083 has on one connected to It, Emap shows 2 ICP's assigned to it. There is no LV connected and the fuses were open & hanging. Can it be removed from the network. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.058672 | 11 | 2017 | 2017-02-13 | C | 480 | 0.058672 | 0.0014385
1 | 15956050 | 2017-03-08 08:45 | 2017-03-08 15:23 | 398 | 39 | 15522 | 0.0465 | 0.046149 | 0.00011684 | NAPA ID:28341 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028341 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742913 | NONE | change poles 742913, 742946, 742947, 742949, 742950, 742951 and cut 11kv jumpers on pole 742913 which feed wortley rd and tie back on line to create a line break from Lincoln Road for duration of job | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.023075 | 5.5 | 2017 | 2017-03-08 | B | 39 | 0.046149 | 0.00011684
1 | 15956203 | 2017-03-10 09:15 | 2017-03-10 14:58 | 343 | 15 | 5145 | 0.015413 | 0.015277 | 4.4935e-05 | NAPA ID:28344 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028344 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742953 | NONE | change poles 742953, 742955, 742956, 742957, 742959 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0076385 | 5.5 | 2017 | 2017-03-10 | B | 15 | 0.015277 | 4.4935e-05
1 | 15956976 | 2017-02-13 17:25 | 2017-02-13 18:05 | 40 | 6 | 240 | 0.00071923 | 0.000665 | 1.7981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727076 | JUMPER | Faultman found a broken jumper on pole 727076, line was isolated at Fuses 6801. 1metre 16mm copper conductor. 1 X joint connector | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000665 | 11 | 2017 | 2017-02-13 | C | 6 | 0.000665 | 1.7981e-05
1 | 15957198 | 2017-02-13 15:03 | 2017-02-13 17:12 | 128 | 2 | 257.5667 | 0.00077187 | 0.000753 | 5.9935e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810762 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 7354 & 7355 - cause wind Used 2 x 5 amp fuses and 2 x 10 amp fuses | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000753 | 11 | 2017 | 2017-02-13 | C | 2 | 0.000753 | 5.9935e-06
1 | 15957219 | 2017-02-13 17:16 | 2017-02-13 18:20 | 63 | 2 | 127.8667 | 0.00038319 | 0.000365 | 5.9935e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 453 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer 453 2 X 3 amp HV fuses replaced. | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.000365 | 11 | 2017 | 2017-02-13 | C | 2 | 0.000365 | 5.9935e-06
1 | 15957838 | 2017-02-13 08:16 | 2017-02-13 17:21 | 544 | 4 | 2179.8 | 0.0065324 | 0.006496 | 1.1987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7636 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at Fuses 7636 - cause wind Used 1 x 10 amp fuses | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.006496 | 11 | 2017 | 2017-02-13 | C | 4 | 0.006496 | 1.1987e-05
1 | 15957918 | 2017-02-13 15:18 | 2017-02-13 17:49 | 151 | 6 | 906.6 | 0.0027169 | 0.002662 | 1.7981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373430 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 7101 - cause wind Used 2 x 8 amp | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002662 | 11 | 2017 | 2017-02-13 | C | 6 | 0.002662 | 1.7981e-05
1 | 15958701 | 2017-02-13 18:12 | 2017-02-13 20:36 | 144 | 44 | 6336.7333 | 0.01899 | 0.018594 | 0.00013186 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7570 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses replaced at Fuses 7570. Caused by tree Branches contacting lines and causing them to clash beyond Pole 817678. Downer defecting this and organising trees to be trimmed. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.018594 | 11 | 2017 | 2017-02-13 | C | 44 | 0.018594 | 0.00013186
1 | 15959651 | 2017-02-13 18:52 | 2017-02-13 21:25 | 153 | 822 | 42907.1333 | 0.12858 | 0.12119 | 0.0024634 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 818367 | CONDUCTOR - REPAIR/REHANG | Tree Branch inside the notice zone contacted lines and brought line down at Pole 818367 Isolated at fabs 8171 CB C953 Trip e/f Line rehung. 2 x Joiners used | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.12119 | 11 | 2017 | 2017-02-13 | C | 822 | 0.12119 | 0.0024634
1 | 15962387 | 2017-02-13 20:45 | 2017-02-13 22:13 | 88 | 38 | 3357.9333 | 0.010063 | 0.009721 | 0.00011388 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7029 | FUSE - ELEMENT/LINK (HV) | 2 x 15A HV Fuses replaced at Fuses 7029 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.009721 | 11 | 2017 | 2017-02-13 | C | 38 | 0.009721 | 0.00011388
1 | 15962521 | 2017-02-13 22:36 | 2017-02-14 00:44 | 127 | 33 | 4213.55 | 0.012627 | 0.01233 | 9.8894e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9579/2 | FUSE - ELEMENT/LINK (HV) | Trustpower repotrs flash from tx , advised Cindy at HUB 2 x 25A HV Fuses Replaced. | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.01233 | 11 | 2017 | 2017-02-13 | C | 33 | 0.01233 | 9.8894e-05
1 | 15962534 | 2017-02-13 21:00 | 2017-02-14 02:30 | 330 | 4 | 1320 | 0.0039558 | 0.003919 | 1.1987e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2168T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faulty Transformer 2168T changed - isolation required from fuses 6201 for safety. Transformer replaced and livened. Also replaced 15A HRC fuse at 6201. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.003919 | 11 | 2017 | 2017-02-13 | C | 4 | 0.003919 | 1.1987e-05
1 | 15962887 | 2017-02-13 22:11 | 2017-02-14 09:35 | 683 | 105 | 55539.8 | 0.16644 | 0.1655 | 0.00031466 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P08448 | CONDUCTOR - REPAIR/REHANG | cb 1 TRIPPED b pH o/c e/f Unable to find fault at night Faultman returned in morning, Line down found at pole P04884 - Isolated at ABS's V2, V3, V15 and Fuses V16 Line Repaired - Used 1 metre of conductor 2 x sleeves | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.1655 | 11 | 2017 | 2017-02-13 | C | 105 | 0.1655 | 0.00031466
1 | 15964312 | 2017-02-14 05:26 | 2017-02-14 06:42 | 76 | 68 | 5174.8 | 0.015508 | 0.014896 | 0.00020378 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819988 | FUSE - ELEMENT/LINK (HV) | 7607 2 x 8amp 06:30 wind | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.014896 | 11 | 2017 | 2017-02-14 | C | 68 | 0.014896 | 0.00020378
1 | 15964383 | 2017-02-14 06:29 | 2017-02-14 09:12 | 162 | 145 | 12664.6833 | 0.037953 | 0.036649 | 0.00043453 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 575 | UNKNOWN | Recloser 575 Tripped B,C Ph O/C Line patrolled with no fault found | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.036649 | 11 | 2017 | 2017-02-14 | C | 145 | 0.036649 | 0.00043453
1 | 15965688 | 2017-02-14 06:59 | 2017-02-14 09:50 | 170 | 15 | 2564.5 | 0.0076851 | 0.00755 | 4.4951e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373585 | FUSE - ELEMENT/LINK (HV) | 12 x 10amp @7379 wind 09:50 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.00755 | 11 | 2017 | 2017-02-14 | C | 15 | 0.00755 | 4.4951e-05
1 | 15965977 | 2017-02-14 09:30 | 2017-02-14 11:20 | 110 | 7 | 770 | 0.0023075 | 0.002244 | 2.0977e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 15965797 | CONDUCTOR - REPAIR/REHANG | Pls also check 368 Te awa awa road 15965977 if related - part power also Fuses found blown at Fuses 7636 - caused by low hanging line at pole 822547 Isolated at Fuses 7636 line rehung Used 2 x binders, 2 x 10 amp fuses | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002244 | 11 | 2017 | 2017-02-14 | C | 7 | 0.002244 | 2.0977e-05
1 | 15966057 | 2017-03-15 08:54 | 2017-03-15 16:00 | 426 | 2 | 852 | 0.0025521 | 0.002534 | 5.9908e-06 | NAPA ID:28345 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028345 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742962 | NONE | change poles 742962, 742964, 742966, 742968, 742970, 742971 and 742973 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.001267 | 5.5 | 2017 | 2017-03-15 | B | 2 | 0.002534 | 5.9908e-06
1 | 15966129 | 2017-03-17 08:57 | 2017-03-17 13:08 | 251 | 15 | 3765 | 0.011277 | 0.011142 | 4.493e-05 | NAPA ID:28343 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028343 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742973 | NONE | change poles 742973, 742974, 742976, 742977, 742978, | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.005571 | 5.5 | 2017 | 2017-03-17 | B | 15 | 0.011142 | 4.493e-05
1 | 15966466 | 2017-02-14 08:29 | 2017-02-14 10:10 | 101 | 138 | 9020 | 0.027031 | 0.025789 | 0.00041355 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C774 & C13721 | UNKNOWN | SMC advised 8:29am Recloser RC11 tripped on E/F flags, line was patrolled and sectionalised and faultman found burn marks on a tree at pole C774, suspect this is what caused tripping, faultman has taken photos and will pass it on to tree contractor, they also found a jumper that was bent over on pole C1372, suspect caused by birds sitting on it jumper was straightened with hot line stick - this section of line goes to no customer it's just a section of line that is energised only. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.025789 | 11 | 2017 | 2017-02-14 | C | 138 | 0.025789 | 0.00041355
1 | 15966991 | 2017-03-21 09:15 | 2017-03-21 14:50 | 335 | 15 | 5025 | 0.015051 | 0.014915 | 4.4927e-05 | NAPA ID:28350 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028350 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742960 | NONE | change poles742960, 742980, 742952, 742979 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0074575 | 5.5 | 2017 | 2017-03-21 | B | 15 | 0.014915 | 4.4927e-05
1 | 15967228 | 2017-02-14 06:44 | 2017-02-14 08:54 | 130 | 5 | 650 | 0.0019479 | 0.001902 | 1.4984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 836702 | FUSE - ELEMENT/LINK (HV) | **Check - would this have affected 240A Black Rock Road OMS 15965670** also 15965715, 15965803. Have called hub to advise of this and sent through lv-hv extent. Advised FRM @ fuses7181 2 x10 a wind 08:54 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.001902 | 11 | 2017 | 2017-02-14 | C | 5 | 0.001902 | 1.4984e-05
1 | 15967293 | 2017-03-28 08:49 | 2017-03-28 14:00 | 311 | 46 | 14311 | 0.042859 | 0.042445 | 0.00013776 | NAPA ID:28348 TP_CARRINGTON GXP > MANGOREI > JUNCTION RD | 11 | Planned | 028348 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 742960 | NONE | reconductor line from pole 742960 to pole 742913 and remove line break at pole 742914 and remove Temporary knife links at pole 742986, TEMP85 | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.021222 | 5.5 | 2017 | 2017-03-28 | B | 46 | 0.042445 | 0.00013776
1 | 15970119 | 2017-02-14 10:52 | 2017-02-14 11:04 | 12 | 355 | 4260 | 0.012766 | 0.009574 | 0.0010638 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 814277 | UNKNOWN | Road Crossing at BrandonSt & Lyon Street Isolated for House move urgently as house stuck in middle of the road Isolated at ABS's 8056, S587 &, S575 Switching done by Brad Keating Power Related service (Load escort) | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.009574 | 11 | 2017 | 2017-02-14 | C | 355 | 0.009574 | 0.0010638
1 | 15970600 | 2017-03-09 09:20 | 2017-03-09 14:00 | 280 | 14 | 3920 | 0.011743 | 0.011617 | 4.194e-05 | NAPA ID:28222 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 028222 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Mangawhero Road | NONE | Replace-straighten poles, crossarms and hardware. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0058085 | 5.5 | 2017 | 2017-03-09 | B | 14 | 0.011617 | 4.194e-05
1 | 15970898 | 2017-02-14 12:10 | 2017-02-14 16:30 | 259 | 446 | 49117.5333 | 0.14719 | 0.14318 | 0.0013365 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | IC3045 | SWITCH (HV) | Advised SMC 12:12pm Advised Fire Comms ETA of 40mins - explosion near sub INT Baird/Elizabeth Smoke coming from Tx at 3 Billah Street - next street over Advised Fire Comms updated ETA of 15mins CB 6 tripped on C phase O/C & E/F flags received a call from fire services & customer of smoke at Sw/Gear IC3045, faultman found that 11KV bus at sw/Gear unit had faulted, feeder was isolated at Sw/Gears 9468/1, IC1524, IC1920 and at T-blade TC3774, so Sw/Gear unit can be repaired or replaced. A Generator is to be installed on transformer TC4449. | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.14318 | 11 | 2017 | 2017-02-14 | C | 446 | 0.14318 | 0.0013365
1 | 15971383 | 2017-03-22 09:01 | 2017-03-22 16:04 | 423 | 13 | 5499 | 0.01647 | 0.016353 | 3.8936e-05 | NAPA ID:27065 TP_KINLEITH GXP | 11 | Planned | 027065 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | A0067 | NONE | install line break at pole A0067 issue LLP to Tom Tanoa install line break at pole KINBRD074 issue LLP to James Kennerley Issue AP to TJ Tanoa to replace ABS 984 &1003 and replace 11 poles reinstate line breaks at poles A0067 KINBRD074 | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.0081765 | 5.5 | 2017 | 2017-03-22 | B | 13 | 0.016353 | 3.8936e-05
1 | 15971515 | 2017-02-14 13:30 | 2017-02-14 15:05 | 95 | 58 | 5510 | 0.016512 | 0.01599 | 0.00017381 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 825034 | POLE | 174 HURURUA ROAD, CARTERTON - FM has replaced 2x 80A fuses at pole 825131 due to wind. Unable to test to confirm power is restored due to this job becoming the verified job for the feeder fault in the area. Isolations put in place to install new pole to lift lines Isolated at ABS S320, with Fuses 7575 Opened to isolated embedded generation | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.01599 | 11 | 2017 | 2017-02-14 | C | 58 | 0.01599 | 0.00017381
1 | 15971561 | 2017-03-14 09:02 | 2017-03-14 12:28 | 206 | 1 | 206 | 0.00061707 | 0.000608 | 2.9954e-06 | NAPA ID:27587 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 027587 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pohongina East Rd | NONE | Replace 11KV Tranny & Xarms. Note single phase TX. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000304 | 5.5 | 2017 | 2017-03-14 | B | 1 | 0.000608 | 2.9954e-06
1 | 15972896 | 2017-03-14 09:47 | 2017-03-14 15:59 | 372 | 13 | 4836 | 0.014486 | 0.014369 | 3.8941e-05 | NAPA ID:27072 TP_KINLEITH GXP > BAIRD ROAD SUB > PAPANUI ST | 11 | Planned | 027072 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 984 | NONE | reconductor between ABS 984 & ABS 1003 | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.0071845 | 5.5 | 2017 | 2017-03-14 | B | 13 | 0.014369 | 3.8941e-05
1 | 15972903 | 2017-03-15 09:34 | 2017-03-15 12:58 | 204 | 6 | 1225.5 | 0.0036709 | 0.003617 | 1.7973e-05 | NAPA ID:28528 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 028528 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1867 Pahiatua Pongaroa Rd | NONE | To replace 11kv xarms and tx | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0018085 | 5.5 | 2017 | 2017-03-15 | B | 6 | 0.003617 | 1.7973e-05
1 | 15973393 | 2017-03-01 09:00 | 2017-03-01 13:17 | 257 | 60 | 15428 | 0.046224 | 0.045684 | 0.00017976 | NAPA ID:27860 TP_BUNNYTHORPE GXP | 11 | Planned | 027860 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Bunnythorpe to Milson | NONE | This is to install Bird B Gone to existing 33kv xarms ON POLES BETWEEN P41969 & P42004. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.022842 | 5.5 | 2017 | 2017-03-01 | B | 60 | 0.045684 | 0.00017976
1 | 15974452 | 2017-02-14 14:45 | 2017-02-14 16:45 | 119 | 3 | 359.7 | 0.0010779 | 0.00105 | 8.9902e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N12968 | FUSE - ELEMENT/LINK (HV) | 2 x3amp @ fp930 unknown 16:45 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.00105 | 11 | 2017 | 2017-02-14 | C | 3 | 0.00105 | 8.9902e-06
1 | 15974524 | 2017-03-10 09:46 | 2017-03-10 14:58 | 312 | 3 | 936 | 0.0028039 | 0.002776 | 8.987e-06 | NAPA ID:28693 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 028693 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Te Wharau Rd, Carterton | NONE | Replace multiple 11kv poles and cross arms | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001388 | 5.5 | 2017 | 2017-03-10 | B | 3 | 0.002776 | 8.987e-06
1 | 15974657 | 2017-03-17 09:32 | 2017-03-17 14:45 | 313 | 10 | 3132.3333 | 0.0093824 | 0.009292 | 2.9953e-05 | NAPA ID:28695 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 028695 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829077 | NONE | Replace multiple 11kv poles and cross arms and make line break for shuts #2#3#4 at poles 829077 and 829078 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.004646 | 5.5 | 2017 | 2017-03-17 | B | 10 | 0.009292 | 2.9953e-05
1 | 15975684 | 2017-02-14 20:45 | 2017-02-14 21:30 | 45 | 48 | 2160 | 0.006473 | 0.006041 | 0.00014384 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M1010 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Outage required between ABS MA164 and MA121 to replace a broken DDO barrell at Transformer M1010. (Backfeed at ABS KA138). Relivened OK. Also replaced 1 X 6A HV fuse. | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.006041 | 11 | 2017 | 2017-02-14 | C | 48 | 0.006041 | 0.00014384
1 | 15976184 | 2017-02-14 22:01 | 2017-02-15 12:16 | 855 | 191 | 36575.4 | 0.10961 | 0.10789 | 0.00057238 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 775590 | CONDUCTOR - REPAIR/REHANG | Reports of No Powers found recloser 142 had tripped (No Comms). (Backfeed put in from Gas/Sw 4621/2 to CB 107). Area patrolled / sectionalised with the fault traced to the spur line beyond fuses 113. Remainder of feeder restored. Not practical to patrol area during the night due to terrain. Will be investigated further in morning. Line patrolled beyond fuses 113 and found trees on lines @ pole 775590 and removed | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.10789 | 11 | 2017 | 2017-02-14 | C | 191 | 0.10789 | 0.00057238
1 | 15976818 | 2017-02-15 01:31 | 2017-02-15 02:10 | 39 | 563 | 21966.3833 | 0.065827 | 0.060765 | 0.0016871 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 822937 | CIRCUIT BREAKER (HV) | CB C856 Trip A phase O/C E/F Line patrolled Possum found at pole 822937. possum blown clear Feeder Relivened. No Possum guard fitted to pole | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.060765 | 11 | 2017 | 2017-02-15 | C | 563 | 0.060765 | 0.0016871
1 | 15978029 | 2017-02-15 08:04 | 2017-02-15 11:25 | 200 | 1 | 200.5833 | 0.00060109 | 0.000592 | 2.9967e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838091 | FUSE - ELEMENT/LINK (HV) | 7138 2 x6amp wind 11:25 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.000592 | 11 | 2017 | 2017-02-15 | C | 1 | 0.000592 | 2.9967e-06
1 | 15979226 | 2017-02-20 09:20 | 2017-02-20 15:33 | 373 | 196 | 37157 | 0.11134 | 0.10958 | 0.00058731 | NAPA ID:27737 TP_KOPU GXP > TAIRUA SUB > PLEASANT POINT | 11 | Planned | 027737 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9057/3 | NONE | Install new 3 core 185mm cable between RMU9057/3 and TC3744 | F3 | PLEASANT POINT | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.054789 | 5.5 | 2017 | 2017-02-20 | B | 196 | 0.10958 | 0.00058731
1 | 15979458 | 2017-03-01 11:00 | 2017-03-01 15:04 | 243 | 200 | 48796.6667 | 0.1462 | 0.1444 | 0.00059922 | NAPA ID:28214 TP_KOPU GXP > COROMANDEL SUB > WYUNA BAY | 11 | Planned | 028214 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 269 | NONE | Changing Xarms and Line Hardware Various sites. Works location: Long Bay Rd, Coromandel. WO 30031902 | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.072201 | 5.5 | 2017 | 2017-03-01 | B | 200 | 0.1444 | 0.00059922
1 | 15979488 | 2017-03-01 09:30 | 2017-03-01 13:14 | 223 | 5 | 1119.4167 | 0.0033539 | 0.003308 | 1.498e-05 | NAPA ID:27133 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KEENAN RD | 11 | Planned | 027133 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE3-018 | NONE | Replace Transformer TE3-018, fit 400v fuse unit and replace LV crossarms. Works location: Belk Rd. WO 30019175 | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001654 | 5.5 | 2017 | 2017-03-01 | B | 5 | 0.003308 | 1.498e-05
1 | 15981921 | 2017-02-15 12:02 | 2017-02-15 14:37 | 155 | 288 | 16081.4 | 0.048191 | 0.045602 | 0.00086305 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714378 | CONDUCTOR - REPAIR/REHANG | CB 9 A/R, L/O, E/F. Call came in of lines down near corner of Eltham Rd & Waiteka Rd. Backfeeds installed via ABS TA896 & ABS TA115. Lines bought down by truck. NDR #N100310 Repaired using 100mtrs of 16mm cu conductor & 12x sleeves | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.045602 | 11 | 2017 | 2017-02-15 | C | 288 | 0.045602 | 0.00086305
1 | 15984879 | 2017-03-02 08:50 | 2017-03-02 14:50 | 360 | 93 | 14678.8333 | 0.043978 | 0.043142 | 0.00027863 | NAPA ID:27863 TP_BUNNYTHORPE GXP | 11 | Planned | 027863 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P42013 | NONE | This is to install Bird B Gone to existing 33kv xarms and 11kv xarms: AP1: Between poles P39093 & P39085. AP2: Between poles P42013 & P42005 and P41955. Switching combined due to switching request. WORKS LOCATION: Bunnythorpe to Milson. WO 30014403 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.021571 | 5.5 | 2017 | 2017-03-02 | B | 93 | 0.043142 | 0.00027863
1 | 15984964 | 2017-03-03 09:00 | 2017-03-03 13:31 | 271 | 2 | 542 | 0.0016238 | 0.001605 | 5.9919e-06 | NAPA ID:27152 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 027152 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD3-238 | NONE | Replace Transformer TD3-238 replace crossarms and hardware on spur line. Works location: Poripori Rd. WO 30019175 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0008025 | 5.5 | 2017 | 2017-03-03 | B | 2 | 0.001605 | 5.9919e-06
1 | 15985106 | 2017-02-15 14:08 | 2017-02-15 15:04 | 55 | 6422 | 209535.4833 | 0.62792 | 0.57018 | 0.019245 |  | 11 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T6 transformer | TRANSFORMER - ZONE TRANSFORMER (HV) | * LOS to entire OTE sub at 14:07 Hrs. * T6 Bank 33kV CB 62 & 11kV CB 36 both tripped simultaneously on T6 'surge'. * Note T7 out of service as part of sub upgrade via NAPA 27723 (33kV Switchboard replacement) * Back fed ICP's on 11kV successfully. First back fed applied at 14:27 hrs and final back fed completed at 15:03 hrs. * Testing found the cause of the outage was due to a faulty temperature sensor on the tap changer compartment that is wired in parallel with the surge circuit (Hence seeing the surge alarm). * Can confirm the outage was NOT caused by any of the project works occurring at the time. * NOC sort engineering input and authority to remove the faulted temperature sensor from the circuit. * Approved to remove the faulted sensor from the trip circuit. * Requires lowering tank oil levels to remove the sensor due to its unique installation on the OLTC tank, will need to be done at a later date. Residual job 100230 created to get this issue resolved. * T6 Transformer re-livened at 16:54 hrs. Load restored to T6 at 17:28 hrs. All 11kV back feeds removed by 19:18 hrs. * Fiona (NOC) FYI we had three field switchers and a sub tech attending this fault. | F3 | BROOKFIELD TCE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.57018 | 11 | 2017 | 2017-02-15 | C | 6422 | 0.57018 | 0.019245
1 | 15991559 | 2017-03-07 09:45 | 2017-03-07 15:15 | 330 | 9 | 2970 | 0.0088976 | 0.008816 | 2.6962e-05 | NAPA ID:28101 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028101 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645 Reduced Outage 945hrs to 1545hrs. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.004408 | 5.5 | 2017 | 2017-03-07 | B | 9 | 0.008816 | 2.6962e-05
1 | 15991636 | 2017-03-09 08:30 | 2017-03-09 14:28 | 358 | 9 | 3222 | 0.0096522 | 0.009571 | 2.6961e-05 | NAPA ID:28102 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028102 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.0047855 | 5.5 | 2017 | 2017-03-09 | B | 9 | 0.009571 | 2.6961e-05
1 | 15991671 | 2017-03-14 09:15 | 2017-03-14 15:17 | 362 | 9 | 3258 | 0.0097593 | 0.009678 | 2.6959e-05 | NAPA ID:28103 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028103 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645 Reduced Outage 0915 to 1500hrs. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.004839 | 5.5 | 2017 | 2017-03-14 | B | 9 | 0.009678 | 2.6959e-05
1 | 15991694 | 2017-03-16 08:45 | 2017-03-16 14:42 | 357 | 9 | 3213 | 0.0096242 | 0.009543 | 2.6959e-05 | NAPA ID:28104 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028104 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.0047715 | 5.5 | 2017 | 2017-03-16 | B | 9 | 0.009543 | 2.6959e-05
1 | 15992627 | 2017-03-21 08:45 | 2017-03-21 14:50 | 365 | 9 | 3285 | 0.0098391 | 0.009758 | 2.6956e-05 | NAPA ID:28105 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028105 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.004879 | 5.5 | 2017 | 2017-03-21 | B | 9 | 0.009758 | 2.6956e-05
1 | 15993099 | 2017-03-23 08:55 | 2017-03-23 15:01 | 366 | 9 | 3301.95 | 0.0098896 | 0.009808 | 2.6956e-05 | NAPA ID:28106 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028106 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809578 | NONE | Replace poles between 809578 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.004904 | 5.5 | 2017 | 2017-03-23 | B | 9 | 0.009808 | 2.6956e-05
1 | 15993136 | 2017-03-28 11:20 | 2017-03-28 15:05 | 225 | 24 | 5400 | 0.016172 | 0.015956 | 7.1876e-05 | NAPA ID:28107 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 028107 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 809548 | NONE | Replace poles between 809548 & 809645. Works location: Parewanui Rd, Bulls. WO 30032246 Work stated 2 hours late due to switching not being done SMC said they had not received it, Documentation said it was sent 19/02/17 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.007978 | 5.5 | 2017 | 2017-03-28 | B | 24 | 0.015956 | 7.1876e-05
1 | 15993567 | 2017-02-15 18:13 | 2017-02-15 19:15 | 61 | 3 | 185.7 | 0.00055649 | 0.000529 | 8.9901e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H3067 | CROSSARM - WHOLE ASSEMBLY | 4.23pm emailed svs hub & called and advised Cindy & advised control Replace rotten crossarm at pole H3067. Isolation at Fuses FC1437. Crossarm & insulators used | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000529 | 11 | 2017 | 2017-02-15 | C | 3 | 0.000529 | 8.9901e-06
1 | 15993846 | 2017-02-15 21:10 | 2017-02-15 21:12 | 2 | 4 | 8 | 2.3974e-05 | 0 | 1.1987e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2298A KAHUTARA ROAD | UNKNOWN | Voltage at Transformer T2296 found to be low , other transformers in area tested ok Transformer Isolated to change tap setting | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2017-02-15 | C | 4 | 0 | 1.1987e-05
1 | 15993867 | 2017-02-15 18:18 | 2017-02-15 19:38 | 79 | 21 | 1678.6 | 0.0050303 | 0.004841 | 6.2931e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 825011 | FUSE - ELEMENT/LINK (HV) | Check OMS: 15993884 - 216 Wilton. reloaded & relivened 2x6amp fuses blown at 8049. line patrolled & fuses reloaded & relivened. Line patrolled 2x10amp fuses blown at 7670 | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.004841 | 11 | 2017 | 2017-02-15 | C | 21 | 0.004841 | 6.2931e-05
1 | 15993968 | 2017-02-15 21:00 | 2017-02-15 21:38 | 38 | 40 | 1520 | 0.004555 | 0.004195 | 0.00011987 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3440 | FUSE - HOLDER/BASE (LV) | Replacement of Andelect Fuse in transformer TC3440. Isolation at Sw/Gear IC1969 for safety to carryout the repairs. Material 200amp fuse 1 x andelect base complete | F3 | MOSSOPS RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.004195 | 11 | 2017 | 2017-02-15 | C | 40 | 0.004195 | 0.00011987
1 | 15996510 | 2017-02-16 10:03 | 2017-02-16 10:35 | 32 | 12 | 387 | 0.0011597 | 0.001051 | 3.596e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718645 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Work Area shutdown via Fuses MA537 & burnt up HV Fuse Holder at Transformer M4365 was replaced. Materials used: 1x HV Fuse Holder complete with 6Amp Link | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001051 | 11 | 2017 | 2017-02-16 | C | 12 | 0.001051 | 3.596e-05
1 | 15996735 | 2017-03-06 08:55 | 2017-03-06 09:42 | 47 | 12 | 564 | 0.0016897 | 0.001581 | 3.595e-05 | NAPA ID:28436 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 028436 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD5-267 | NONE | Change PG on pn 220079 TD5-267. Works location: Waitao Rd, Tauranga. WO 30033829 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0007905 | 5.5 | 2017 | 2017-03-06 | B | 12 | 0.001581 | 3.595e-05
1 | 15999132 | 2017-03-02 05:30 | 2017-03-02 17:01 | 691 | 135 | 17415 | 0.052176 | 0.050962 | 0.00080893 | NAPA ID:28015 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > MOUNT | 11 | Planned | 028015 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD5-128 | NONE | 1. Remove fuses L1 at HV link-box SD5-061 and LV back-feed Transformer TD5-128 (AP1 0530-0630) 2. Replace old 200kva mini-sub with new 200kva unitised Transformer at TD5-128 (AP2 0630-1500) 3. Test HV cables / Transformer TD5-128 > SD5-161 L1 (TP1 1500-1600) 4. Replace fuses L1 at HV link-box SD5-061 and remove LV back-feed to Transformer TD5-128 (AP3 1600-1700). WORKS LOCATION: Tahara Cres, Mt Maunganui. WO 30019178 | F2 | MOUNT | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.025481 | 5.5 | 2017 | 2017-03-02 | B | 135 | 0.050962 | 0.00080893
1 | 15999304 | 2017-02-16 10:06 | 2017-02-16 11:12 | 65 | 138 | 6988.4 | 0.020942 | 0.019701 | 0.00041354 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS RC11 A/R, L/O, E/F Sectionalised & Patrolled with No Fault Found | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.019701 | 11 | 2017 | 2017-02-16 | C | 138 | 0.019701 | 0.00041354
1 | 16000943 | 2017-03-03 08:58 | 2017-03-03 14:22 | 324 | 22 | 7128 | 0.021355 | 0.021157 | 6.5912e-05 | NAPA ID:28468 TP_TE MATAI GXP > TE PUKE SUB > KAITUNA | 11 | Planned | 028468 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE6-021 | NONE | REPLACE POLE TX TE6-021 223975 AND 7 HV ARMS / FUSES . DFT 154-11548. Works location: Kenana Rd. WO 30033763 | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.010578 | 5.5 | 2017 | 2017-03-03 | B | 22 | 0.021157 | 6.5912e-05
1 | 16001360 | 2017-02-16 13:55 | 2017-02-16 15:15 | 80 | 1 | 80.5 | 0.00024123 | 0.000232 | 2.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 445055 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp bird 15 :15 @ TX L4475 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000232 | 11 | 2017 | 2017-02-16 | C | 1 | 0.000232 | 2.9966e-06
1 | 16001369 | 2017-02-16 16:38 | 2017-02-16 17:24 | 45 | 37 | 1690.2 | 0.005065 | 0.004732 | 0.00011088 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K13423 | JUMPER | Retailer rung to advise , has been out since 1355, phoned HUB , advised they are aware of it , due to feeder faults, have been trying to get someone there Had earlier advised HUB there is another job on same road and go to Fuses 576 Spoke to Marty as the SMC have no systems and advised him to head to the fuses FM found broken HV jumper at Pole K13423. Isolated at ABS 837 & repaired using a M10 bolt, nut, & washers NOTE: ABS has a lot of rusty bolts and is in very poor condition. DNO Tag Applied. DNO # 170215 | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.004732 | 11 | 2017 | 2017-02-16 | C | 37 | 0.004732 | 0.00011088
1 | 16001402 | 2017-02-16 14:05 | 2017-02-16 16:49 | 164 | 292 | 10412.1833 | 0.031202 | 0.028576 | 0.00087502 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | H2253 | FUSE - ELEMENT/LINK (HV) | CB 5 A/R, L/O, E/F B Phase Sectionalised & Patrolled with fault being found due to tree branches contacting HV line. Isolated at Fuses FC2160 and branches removed by FM from bucket truck. More work will be required by Tree Contractor at a later date. Materials used: 3x 10Amp HV Fuse Links. NDR # 56501 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.028576 | 11 | 2017 | 2017-02-16 | C | 292 | 0.028576 | 0.00087502
1 | 16002902 | 2017-02-16 15:18 | 2017-02-16 21:02 | 344 | 439 | 26661.25 | 0.079895 | 0.075948 | 0.00041354 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C875 | INSULATOR | RS RC11 A/R, L/O, E/F, O/C B Phase 1529 Phoned FSM Steve McKinney , no details of who is attending on job 1534 Phoned HUB for update due to phone issues, have had slowed them down , Mike Jeffery and Mike Cornellius attending 1544 Steve phoned back, first time he had heard about the feeder fault Fault sectionalised and found to be between RC11 & ABS 605. Faulty insulator eventually found at pole C875. Isolations at ABS 605, 628 & links IP141. 2 x pins & insulators materials required. All supply restored at 21:02 Comms was lost to recloser RC11 during fault switching Suspect batteries on recloser may have failed due to time AC was off? OMS 16006462 created to have recloser checked. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.075948 | 11 | 2017 | 2017-02-16 | C | 439 | 0.075948 | 0.00041354
1 | 16003659 | 2017-02-16 16:27 | 2017-02-16 17:43 | 75 | 1 | 75.8167 | 0.0002272 | 0.000218 | 2.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc2715 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 3amp ht fuses at TC2715 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000218 | 11 | 2017 | 2017-02-16 | C | 1 | 0.000218 | 2.9966e-06
1 | 16005099 | 2017-02-16 19:31 | 2017-02-17 00:04 | 273 | 231 | 18323.4 | 0.054909 | 0.052832 | 0.0013245 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | H21 | UNKNOWN | Numerrous trips on CB H21. Tripped and L/O at 19:30 on E/F. Patrolled and nothing found. Feeder continued to A/R until tripping again at 00:03. This is recorded on OMS 16007648. 1932 Advisded HUB of Feeder fault , advised Cindy 1940 FSM is Germaine , who is responding is FSM | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.052832 | 6.6 | 2017 | 2017-02-16 | C | 231 | 0.052832 | 0.0013245
1 | 16007648 | 2017-02-17 00:09 | 2017-02-17 06:48 | 399 | 231 | 69198.4 | 0.20736 | 0.20528 | 0.00090198 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762078 | INSULATOR | Motukawa CB H21 tripped. Patrolled and 2 x HV insulators replaced at pole 762078. | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.20528 | 6.6 | 2017 | 2017-02-17 | C | 231 | 0.20528 | 0.00090198
1 | 16009112 | 2017-02-17 03:51 | 2017-02-17 06:32 | 161 | 301 | 23813.7167 | 0.071361 | 0.068654 | 0.00090198 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720903 | INSULATOR | Cambria CB 5 - Tawhiti Rd - RS 6561 tripped on E/F and L/O. Patrol found cracked insulator at Pole 720903. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.068654 | 11 | 2017 | 2017-02-17 | C | 301 | 0.068654 | 0.00090198
1 | 16010175 | 2017-03-15 09:00 | 2017-03-15 12:56 | 235 | 5 | 1178.6667 | 0.0035306 | 0.003485 | 1.4977e-05 | NAPA ID:28076 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 028076 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | No 4 Line Pohongina | NONE | Straighten 11KV pole & repair conductor | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0017425 | 5.5 | 2017 | 2017-03-15 | B | 5 | 0.003485 | 1.4977e-05
1 | 16010260 | 2017-02-17 07:24 | 2017-02-17 09:00 | 96 | 5 | 482.4167 | 0.0014456 | 0.0014 | 1.4983e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | O13929 | FUSE - ELEMENT/LINK (HV) | Reload at Transformer TC2715 2 x 3A Cause Unknown | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0014 | 11 | 2017 | 2017-02-17 | C | 5 | 0.0014 | 1.4983e-05
1 | 16014335 | 2017-02-17 08:15 | 2017-02-17 10:20 | 125 | 86 | 10750 | 0.032214 | 0.03144 | 0.00025771 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | P03344 | FUSE - ELEMENT/LINK (HV) | 2 X 20 amp ht fuses at FABS H106 no outage on feeder fault on child job was forced up in error | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.03144 | 11 | 2017 | 2017-02-17 | C | 86 | 0.03144 | 0.00025771
1 | 16015380 | 2017-02-17 08:26 | 2017-02-17 13:06 | 279 | 129 | 25271 | 0.075727 | 0.074567 | 0.00038656 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7910766 | NONE | Tree in Lines at Pole 7910766 Trees caused HV / LV Clash NDR Trees removed and HV relivened but.... Safety Disconnection Numbers issued to 3 LV Sites #A15680 #A13802, & #A13804. These will require inspection before re-livening. that will be at Powerco's expense NDR 047407 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.074567 | 11 | 2017 | 2017-02-17 | C | 129 | 0.074567 | 0.00038656
1 | 16015562 | 2017-02-21 09:00 | 2017-02-21 15:57 | 417 | 10 | 4170 | 0.012495 | 0.012405 | 2.9964e-05 | NAPA ID:29047 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 029047 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W12664 | NONE | RECONDUCTOR FROM POLE W12666 TO POLE W12664 TO REPAIR BUSH FIRE DAMAGE TO OH LINES | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.0062025 | 5.5 | 2017 | 2017-02-21 | B | 10 | 0.012405 | 2.9964e-05
1 | 16016277 | 2017-02-17 10:06 | 2017-02-17 11:44 | 98 | 3 | 294 | 0.000881 | 0.000854 | 8.9898e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | F12556 | FUSE - ELEMENT/LINK (HV) | FM found two blown HV Fuses at Fuses FC2150. This was due to a vine growing up Transformer Pole F12556 which had completely covered the transformer & shorted out the HV bushings. Another faultman attended with bucket truck to remove vines. Replaced 2x blown 3Amp HV Fuses at FC2150 & relivened. | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000854 | 11 | 2017 | 2017-02-17 | C | 3 | 0.000854 | 8.9898e-06
1 | 16017426 | 2017-02-17 09:52 | 2017-02-17 10:54 | 61 | 1 | 61.5833 | 0.00018454 | 0.000175 | 2.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P02115 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses E90 2 x 10A Fuses Bird Strike | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000175 | 11 | 2017 | 2017-02-17 | C | 1 | 0.000175 | 2.9966e-06
1 | 16017636 | 2017-03-09 10:00 | 2017-03-09 11:22 | 82 | 106 | 8692 | 0.026039 | 0.025086 | 0.00031755 | NAPA ID:27909 TP_KAITIMAKO GXP > WELCOME BAY SUB | 11 | Planned | 027909 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP553 | NONE | Change over secondary CT wiring on recently installed automated CFC 9053 - incorrect from factory | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.012543 | 5.5 | 2017 | 2017-03-09 | B | 106 | 0.025086 | 0.00031755
1 | 16018363 | 2017-02-17 13:17 | 2017-02-17 13:20 | 2 | 136 | 394.4 | 0.0011819 | 0 | 0.00040754 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 754333 | NONE | 2R - Report form Contractor of large Branch on Lines at Pole 754333. Chris reports that branch needs immediate removal and lines are still live. Short urgent shut to be co-ordinated by NC. Opened at ABS 138. Branch removed using hot sticks. NDR 100312 | F3 | BROOKLANDS 13 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2017-02-17 | C | 136 | 0 | 0.00040754
1 | 16018558 | 2017-03-19 09:03 | 2017-03-19 13:10 | 247 | 4 | 988 | 0.0029593 | 0.002923 | 1.1981e-05 | NAPA ID:28936 TP_WANGANUI GXP > HATRICKS WHARF SUB > MARANGAI | 11 | Planned | 028936 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X3166 | NONE | Replace 110kva transformer and Xarms at X3166 | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 0.0014615 | 5.5 | 2017 | 2017-03-19 | B | 4 | 0.002923 | 1.1981e-05
1 | 16019866 | 2017-03-17 09:20 | 2017-03-17 14:57 | 337 | 1 | 337 | 0.0010094 | 0.001 | 2.9953e-06 | NAPA ID:28403 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 028403 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2270 | NONE | Replace TX structure T2270 with new and change pole 839954 one span away from isolation point 7867. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.0005 | 5.5 | 2017 | 2017-03-17 | B | 1 | 0.001 | 2.9953e-06
1 | 16019899 | 2017-02-21 09:45 | 2017-02-21 16:48 | 423 | 16 | 6768 | 0.02028 | 0.020136 | 4.7943e-05 | NAPA ID:29131 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 029131 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7715 | NONE | tree cutting by treescape under cacd | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.010068 | 5.5 | 2017 | 2017-02-21 | B | 16 | 0.020136 | 4.7943e-05
1 | 16020353 | 2017-02-17 19:25 | 2017-02-17 22:39 | 194 | 2 | 388.9333 | 0.0011655 | 0.001147 | 5.9932e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4060 | FUSE - ELEMENT/LINK (HV) | 3 x 3 amp HV fuses replaced at transformer TC4060. Lightning in area | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001147 | 11 | 2017 | 2017-02-17 | C | 2 | 0.001147 | 5.9932e-06
1 | 16021443 | 2017-02-17 20:43 | 2017-02-17 22:27 | 104 | 2 | 208.4333 | 0.00062459 | 0.000606 | 5.9932e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2879 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV Fuses | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000606 | 11 | 2017 | 2017-02-17 | C | 2 | 0.000606 | 5.9932e-06
1 | 16021460 | 2017-02-17 20:44 | 2017-02-17 23:30 | 166 | 1 | 166.05 | 0.00049759 | 0.000488 | 2.9966e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1565 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV fuses and one carrier | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000488 | 11 | 2017 | 2017-02-17 | C | 1 | 0.000488 | 2.9966e-06
1 | 16021493 | 2017-02-17 20:58 | 2017-02-17 21:53 | 54 | 4 | 218.8 | 0.00065566 | 0.000619 | 1.1986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X73 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV Fuses | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000619 | 11 | 2017 | 2017-02-17 | C | 4 | 0.000619 | 1.1986e-05
1 | 16021547 | 2017-02-17 19:21 | 2017-02-17 21:10 | 109 | 2 | 218 | 0.00065326 | 0.000635 | 5.9932e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1377 | FUSE - ELEMENT/LINK (HV) | 2 x 3 amp HV fuses replaced at transformer TC1377. Lightning in area. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000635 | 11 | 2017 | 2017-02-17 | C | 2 | 0.000635 | 5.9932e-06
1 | 16021612 | 2017-02-17 21:32 | 2017-02-18 00:29 | 176 | 3 | 529.95 | 0.0015881 | 0.001561 | 8.9898e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2400 | FUSE - ELEMENT/LINK (HV) | Replaced 3x 3a HV Fuses | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001561 | 11 | 2017 | 2017-02-17 | C | 3 | 0.001561 | 8.9898e-06
1 | 16021626 | 2017-02-17 21:43 | 2017-02-18 10:27 | 763 | 114 | 32247.8667 | 0.096634 | 0.095609 | 0.00058734 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 810196 | CONDUCTOR - REPAIR/REHANG | 17/02 2111 PHONED DUTY RESTORATION ,WAS NOT AWARE OF THIS 10 M Conductor 2 X Sleeves At Pole 810196 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.095609 | 11 | 2017 | 2017-02-17 | C | 114 | 0.095609 | 0.00058734
1 | 16021807 | 2017-02-17 22:30 | 2017-02-17 23:08 | 38 | 4 | 153.9333 | 0.00046128 | 0.000425 | 1.1986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2067 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000425 | 11 | 2017 | 2017-02-17 | C | 4 | 0.000425 | 1.1986e-05
1 | 16022236 | 2017-02-17 23:58 | 2017-02-18 00:27 | 28 | 204 | 5753.9667 | 0.017242 | 0.015408 | 0.00061131 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 8764 | UNKNOWN | Tripped A&B Phase O/C & E/F also CB 6942 tripped on A&B phase O/C & E/F Both closed on load after stat period (Suspect lightning) | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.015408 | 11 | 2017 | 2017-02-17 | C | 204 | 0.015408 | 0.00061131
1 | 16023298 | 2017-02-18 06:17 | 2017-02-18 08:50 | 152 | 3 | 457.95 | 0.0013723 | 0.001345 | 8.9897e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1179 | FUSE - ELEMENT/LINK (HV) | Was at Transformer X1179 Not X72. Record altered to correct | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001345 | 11 | 2017 | 2017-02-18 | C | 3 | 0.001345 | 8.9897e-06
1 | 16023312 | 2017-02-18 06:42 | 2017-02-18 13:00 | 378 | 1 | 378.1333 | 0.0011331 | 0.001124 | 2.9965e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 380258 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer found blown. To be replaced. (Lightning). TP200 replaced | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.001124 | 11 | 2017 | 2017-02-18 | C | 1 | 0.001124 | 2.9965e-06
1 | 16023336 | 2017-02-18 07:09 | 2017-02-18 10:15 | 186 | 3 | 558.05 | 0.0016722 | 0.001645 | 8.9897e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2379 | FUSE - ELEMENT/LINK (HV) | 3 X 3Amp HT Fuses at X2379 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001645 | 11 | 2017 | 2017-02-18 | C | 3 | 0.001645 | 8.9897e-06
1 | 16023485 | 2017-02-18 08:41 | 2017-02-18 10:55 | 134 | 1 | 134 | 0.00040154 | 0.000392 | 2.9965e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP229 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses Replaced. At Fuses FP229. This customer actually on Transformer TP332 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000392 | 11 | 2017 | 2017-02-18 | C | 1 | 0.000392 | 2.9965e-06
1 | 16023502 | 2017-02-18 08:48 | 2017-02-18 13:20 | 272 | 2 | 544.3 | 0.001631 | 0.001613 | 5.9931e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2525 & 2654 | FUSE - ELEMENT/LINK (HV) | 2 X 2 Amp Fuses at transformer X2525 2 X 6 Amp at Fuses 2654 Job would not go up to Fuses 2654. Amended to correct at QA | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001613 | 11 | 2017 | 2017-02-18 | C | 2 | 0.001613 | 5.9931e-06
1 | 16023874 | 2017-02-18 09:16 | 2017-02-18 11:13 | 117 | 4 | 469.3333 | 0.0014064 | 0.00137 | 1.1986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3029 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses @tc3029 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.00137 | 11 | 2017 | 2017-02-18 | C | 4 | 0.00137 | 1.1986e-05
1 | 16024023 | 2017-02-18 09:37 | 2017-02-18 13:18 | 220 | 201 | 10768.2167 | 0.032268 | 0.03046 | 0.00038656 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231024 | CONDUCTOR - REPAIR/REHANG | CB 4 Trip. A/R. Sectionaliser 9875 Trip. E/F. O/C. Sectionalised. Line down found past Fuses SF7-001. Line isolated at SG7-001 and rest of feeder restored. 9 meters Namu conductor 11 sleeves No OMS job created when Sec 9874 opened. E-Map not tied to OSI SCADA | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.03046 | 11 | 2017 | 2017-02-18 | C | 201 | 0.03046 | 0.00038656
1 | 16024526 | 2017-02-18 10:28 | 2017-02-18 11:51 | 83 | 218 | 13877.05 | 0.041584 | 0.039623 | 0.00065325 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB R11 | UNKNOWN | CB R11 E/F Patrolled Nothing Found. SD contacted to put up extra LFIs and to do an in depth survey. No results to date. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.039623 | 11 | 2017 | 2017-02-18 | C | 218 | 0.039623 | 0.00065325
1 | 16025651 | 2017-02-18 12:04 | 2017-02-18 16:08 | 244 | 2 | 488.9667 | 0.0014652 | 0.001447 | 5.9931e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219979 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TD5-190 Blown. To Be Replaced Transformer Replaced. Livened at 1608 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.001447 | 11 | 2017 | 2017-02-18 | C | 2 | 0.001447 | 5.9931e-06
1 | 16025749 | 2017-02-18 12:40 | 2017-02-18 14:10 | 90 | 1 | 90.4667 | 0.00027109 | 0.000262 | 2.9965e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X921 | FUSE - ELEMENT/LINK (HV) | 2 X 3 Amp HT Fuse at Transformer X921 | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000262 | 11 | 2017 | 2017-02-18 | C | 1 | 0.000262 | 2.9965e-06
1 | 16026563 | 2017-02-18 20:09 | 2017-02-18 21:30 | 80 | 2 | 161.6 | 0.00048425 | 0.000466 | 5.9931e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 370729 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV Fuses | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000466 | 11 | 2017 | 2017-02-18 | C | 2 | 0.000466 | 5.9931e-06
1 | 16026659 | 2017-02-18 21:03 | 2017-02-18 21:50 | 47 | 2694 | 124630.7167 | 0.37346 | 0.34925 | 0.0080728 |  | 33 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P09318 | NONE | * 1st event: 11kV CB 8 tripped A & C Phase O/C and auto closed. * 2nd event: LTN CB 1182 tripped C phase O/C, TUR CB Y40 tripped A phase O/C both to lock out. * Additional event:, TUR CB Y10 tripped on Back up (suspect due to anti-islanding to TWP) to lock out. * Resulted LOS to TUR sub. Note, CB 8 A/R event is correct as 33kV CB's had already opened by the time A/R event on CB 8 was completed. * Report from public, received of tree branch struck by lightning and fell onto line @ pole P09318 (one pole away from Transformer site T2/903. Branch was laid across all three phases. * This site is 11kV, approx 400m away from nearest 33kV line. * Branch removed from line using sticks. * All supply restored to TUR customers by 21:49hrs. Note: On review of alarming in SCADA found Linton army camp CB 4 tripped to lock out. Due to multiple control fail alarms up on auto-changeover system. Device 10055 did not show closed at any time, suspect the scheme failed to operate, requires investigation. Linton army camp CB 4 re-closed on site as required closing spring to be charged up manually. * Monday morning review of event files and discussion between NOC and M Allpress, it was agreed we have a potential issue on the 33kV line, either suspect a line clash or a defective line asset. Line being patrolled in detail as arranged between NOC and K Frew (new outage management process for unknown sub trans issues, SAIDI mitigation). Details of patrol to be added later once patrol completed, NCTL. | S3 | LINTON-TURITEA 33KV | LINTON | Manawatu | TP_LINTON | Western Electricity | POWERCO | 0.34925 | 33 | 2017 | 2017-02-18 | C | 2694 | 0.34925 | 0.0080728
1 | 16029467 | 2017-02-18 22:13 | 2017-02-19 00:37 | 143 | 1 | 143.7667 | 0.00043081 | 0.000421 | 2.9965e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1651 | FUSE - ELEMENT/LINK (HV) | Replaced 3x 10a HV fuses | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000421 | 11 | 2017 | 2017-02-18 | C | 1 | 0.000421 | 2.9965e-06
1 | 16031266 | 2017-02-19 08:16 | 2017-02-19 08:54 | 38 | 1760 | 14051.6167 | 0.042106 | 0.026284 | 0.0031613 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 3120 | UNKNOWN | 33kV CB 3120 Tripped to L/O. Line Patrolled. No Fault Found. TPV CB's 1 & 7 also A/R at the same time. again Unknown Cause. E/F 11kV Backfeeds that could be put in via SCADA were done immediately but final backfeed wasn't able to be put in place until a faultman arrived to do switching. If the Open point between ATU CB1 and TPV CB4 was changed from Sw/gear 9479/3 to SCADA controlled Sw/gear 9444/1 the final backfeed could have been done immediately as well saving a lot of SAIDI. | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.026284 | 33 | 2017 | 2017-02-19 | C | 1760 | 0.026284 | 0.0031613
1 | 16032842 | 2017-02-19 09:33 | 2017-02-19 15:17 | 344 | 2 | 688.2333 | 0.0020623 | 0.002044 | 5.993e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X70 | TRANSFORMER - INSTRUMENT TRANSFORMER | Transformer X70 replaced with new (Severe damage due to lightning strike during the night). Relivened OK. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002044 | 11 | 2017 | 2017-02-19 | C | 2 | 0.002044 | 5.993e-06
1 | 16032908 | 2017-02-19 10:23 | 2017-02-19 11:57 | 94 | 7 | 658 | 0.0019717 | 0.001908 | 2.0976e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X626 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | Incorrect Transformer - should be X626 (3 HV Fuses tripped, reloaded OK 3A Rating - Lightning). Outage shown on child | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.001908 | 11 | 2017 | 2017-02-19 | C | 7 | 0.001908 | 2.0976e-05
1 | 16033109 | 2017-02-19 12:25 | 2017-02-19 13:37 | 71 | 1 | 71.7333 | 0.00021495 | 0.000205 | 2.9965e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1636 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | 3 HT fuses replaced at X1636 (3A Rating) - Lightning | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000205 | 11 | 2017 | 2017-02-19 | C | 1 | 0.000205 | 2.9965e-06
1 | 16033133 | 2017-02-19 12:47 | 2017-02-19 14:43 | 116 | 1 | 116.1 | 0.0003479 | 0.000338 | 2.9965e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2946 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | 2 HT Fuses replaced (3A Rating) at X2946, Lightning | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000338 | 11 | 2017 | 2017-02-19 | C | 1 | 0.000338 | 2.9965e-06
1 | 16036005 | 2017-02-19 15:52 | 2017-02-19 22:00 | 368 | 1420 | 74515.9333 | 0.22329 | 0.21052 | 0.0042551 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 841799 | POLE | Car vs Pole Advised control and SMC of 999 Police called and advised lines are low but not down NDR 47503 Used 1 X Pole 1X Donut 1 X Breast Block Reused arms off old pole as were not that old | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.21052 | 11 | 2017 | 2017-02-19 | C | 1420 | 0.21052 | 0.0042551
1 | 16037489 | 2017-02-19 16:30 | 2017-02-19 19:08 | 158 | 1 | 158.4833 | 0.0004749 | 0.000465 | 2.9965e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X593 & X592 | FUSE - ELEMENT/LINK (HV) | 2 X 2 Amp At X593 1 X 5 Amp at X592 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000465 | 11 | 2017 | 2017-02-19 | C | 1 | 0.000465 | 2.9965e-06
1 | 16038238 | 2017-02-20 01:24 | 2017-02-20 01:42 | 18 | 396 | 4802.2 | 0.01439 | 0.010829 | 0.0011866 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser RC26 auto reclosed on E/F, CB 3 L/O on O/C. Backfeed to recloser RC 26. Closed CB 3 CB 3 to be patrolled during daylight. Trees in the lines Perry will defect. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.010829 | 11 | 2017 | 2017-02-20 | C | 396 | 0.010829 | 0.0011866
1 | 16038877 | 2017-02-20 05:44 | 2017-02-20 12:01 | 377 | 6 | 2262 | 0.0067781 | 0.006724 | 1.7979e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 379205 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer W5045 3/50kVA Replaced. Power restore 12:01 **Please link 16038947 and 16038904 if related.** | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.006724 | 11 | 2017 | 2017-02-20 | C | 6 | 0.006724 | 1.7979e-05
1 | 16039220 | 2017-03-09 09:32 | 2017-03-09 15:02 | 329 | 38 | 12515.3 | 0.037492 | 0.03715 | 0.00011384 | NAPA ID:28497 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 028497 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 747387 | NONE | Install Links TEMP14 at pole 747419, replace solid links 543, install links 12184 at pole 747387 and various poles and equipment in work area. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.018575 | 5.5 | 2017 | 2017-03-09 | B | 38 | 0.03715 | 0.00011384
1 | 16040822 | 2017-02-20 10:20 | 2017-02-20 10:25 | 5 | 7 | 35 | 0.00010488 | 4.1e-05 | 2.0975e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 387156 | NONE | high voltage at transformer TC1663. Marty has checked 2 other transformers & the voltages are correct. Transformer has had cowshed load removed from, the cowshed now has its own Tx. Transformer Tapped Down. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 4.1e-05 | 11 | 2017 | 2017-02-20 | C | 7 | 4.1e-05 | 2.0975e-05
1 | 16040998 | 2017-03-20 09:30 | 2017-03-20 14:35 | 305 | 15 | 4575 | 0.013703 | 0.013568 | 4.4928e-05 | NAPA ID:28504 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 028504 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kapi Road | NONE | replacement of various poles and equipment in work area. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.006784 | 5.5 | 2017 | 2017-03-20 | B | 15 | 0.013568 | 4.4928e-05
1 | 16041004 | 2017-02-19 16:30 | 2017-02-19 19:08 | 158 | 1 | 158.4833 | 0.0004749 | 0.000465 | 2.9965e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783818 | FUSE - ELEMENT/LINK (HV) | Replace 2 x fuses at X593 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000465 | 11 | 2017 | 2017-02-19 | C | 1 | 0.000465 | 2.9965e-06
1 | 16041117 | 2017-03-28 09:32 | 2017-03-28 15:20 | 348 | 15 | 5220 | 0.015633 | 0.015498 | 4.4922e-05 | NAPA ID:28505 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 028505 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kaipi Road | NONE | replacement of various poles and equipment in work area. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.007749 | 5.5 | 2017 | 2017-03-28 | B | 15 | 0.015498 | 4.4922e-05
1 | 16041385 | 2017-02-20 09:48 | 2017-02-20 12:05 | 137 | 5 | 689.5833 | 0.0020663 | 0.002021 | 1.4982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2715 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses Replaced. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002021 | 11 | 2017 | 2017-02-20 | C | 5 | 0.002021 | 1.4982e-05
1 | 16041395 | 2017-03-30 09:30 | 2017-03-30 14:50 | 320 | 15 | 4800 | 0.014375 | 0.014239 | 4.4921e-05 | NAPA ID:28597 TP_CARRINGTON GXP > MANGOREI > KAIPI RD | 11 | Planned | 028597 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kapi Road | NONE | replacement of various poles and equipment in work area. | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.0071195 | 5.5 | 2017 | 2017-03-30 | B | 15 | 0.014239 | 4.4921e-05
1 | 16042526 | 2017-02-20 12:09 | 2017-02-20 17:15 | 306 | 5 | 1530.5 | 0.0045861 | 0.004541 | 1.4982e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2715 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer has blown, replace transformer. TC2715. LV/HV | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.004541 | 11 | 2017 | 2017-02-20 | C | 5 | 0.004541 | 1.4982e-05
1 | 16043085 | 2017-02-20 14:12 | 2017-02-20 16:15 | 123 | 1 | 123 | 0.00036857 | 0.000359 | 2.9964e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786776 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses at Transformer X2676 Outage recorded on th child job | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000359 | 11 | 2017 | 2017-02-20 | C | 1 | 0.000359 | 2.9964e-06
1 | 16043508 | 2017-02-20 11:55 | 2017-02-20 13:30 | 95 | 3 | 285 | 0.000854 | 0.000827 | 8.9894e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | KINMAR073 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | Isolation of Transformer TC3061 for running of new LV conducter. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.000827 | 11 | 2017 | 2017-02-20 | C | 3 | 0.000827 | 8.9894e-06
1 | 16043831 | 2017-02-20 15:22 | 2017-02-20 17:13 | 111 | 1 | 111.15 | 0.00033306 | 0.000324 | 2.9964e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2635 | FUSE - ELEMENT/LINK (HV) | 3 HT fuses rep-laced at X2635 (3A Rating) - Lightning | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000324 | 11 | 2017 | 2017-02-20 | C | 1 | 0.000324 | 2.9964e-06
1 | 16044734 | 2017-02-20 20:20 | 2017-02-20 21:14 | 53 | 1567 | 41366.1167 | 0.12395 | 0.10987 | 0.0046955 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB3722,CBWH6 | UNKNOWN | * Transformer 33kV CB's 3722 and 3738 and 11kV CB WH6 all tripped on Differential. * LOS to Whareroa Sub. All Customers back fed on 11kV by 2126 hrs. NCTL advised. transformer isolated and earthed up, Subs team initial inspection unable to find cause of tripping. * NOC advised NCTL no immediate cause found. NCTL advise to leave sub back fed as back feeds stable. NOC to organise for testing in morning. *Morning: NCTL advised Robin Pitwood of the issue. Robin has provided a brief as to what testing is to be undertaken. * Note: we had a similar outage with this transformer last year, due to this aspect we will be stepping through all aspects of the asset, protection, CB's, cables etc carefully and concisely to ascertain what the issue is. * NO ETA at this stage. * Created DNO 170219 to manage investigation and testing of assets | S2 | WHAREROA 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 0.10987 | 11 | 2017 | 2017-02-20 | C | 1567 | 0.10987 | 0.0046955
1 | 16049238 | 2017-02-21 07:36 | 2017-02-21 09:30 | 113 | 8 | 909.4667 | 0.0027252 | 0.002653 | 2.3971e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1573 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.002653 | 11 | 2017 | 2017-02-21 | C | 8 | 0.002653 | 2.3971e-05
1 | 16049260 | 2017-03-17 09:00 | 2017-03-17 12:41 | 221 | 1 | 221 | 0.00066197 | 0.000652 | 2.9953e-06 | NAPA ID:28401 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 028401 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T60 | NONE | Replace 2 HV poles on spur line to T60 (just outside of Tinui settlement) | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.000326 | 5.5 | 2017 | 2017-03-17 | B | 1 | 0.000652 | 2.9953e-06
1 | 16049283 | 2017-03-18 09:00 | 2017-03-18 14:45 | 345 | 2 | 690 | 0.0020668 | 0.002048 | 5.9906e-06 | NAPA ID:28411 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 028411 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T63 | NONE | Replace 4 HV poles on spur line to T63 | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.001024 | 5.5 | 2017 | 2017-03-18 | B | 2 | 0.002048 | 5.9906e-06
1 | 16049299 | 2017-02-21 08:06 | 2017-02-21 09:55 | 109 | 3 | 328.2 | 0.00098343 | 0.000956 | 8.9893e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P48016 | FUSE - ELEMENT/LINK (HV) | Retailer believes pole fuse has blown. Replaced 3 x 2amp fuses at T8/123 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000956 | 11 | 2017 | 2017-02-21 | C | 3 | 0.000956 | 8.9893e-06
1 | 16049309 | 2017-03-18 09:18 | 2017-03-18 15:13 | 355 | 4 | 1420 | 0.0042533 | 0.004217 | 1.1981e-05 | NAPA ID:28414 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 028414 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 838217 | NONE | Replace HV poles on the ICA Station Homestead 838217, 838222 & 8383223 | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.0021085 | 5.5 | 2017 | 2017-03-18 | B | 4 | 0.004217 | 1.1981e-05
1 | 16049444 | 2017-03-20 09:00 | 2017-03-20 12:56 | 236 | 4 | 944 | 0.0028275 | 0.002791 | 1.1981e-05 | NAPA ID:28418 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 028418 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 838214 | NONE | Shut 2 - Change HV Poles 838214 and 838219. Work site between poles 838211 and 838220. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.0013955 | 5.5 | 2017 | 2017-03-20 | B | 4 | 0.002791 | 1.1981e-05
1 | 16049595 | 2017-03-16 09:01 | 2017-03-16 12:43 | 221 | 3 | 665.9 | 0.0019946 | 0.001967 | 8.9862e-06 | NAPA ID:27814 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 027814 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 563 Upperplain Rd, Masterton | NONE | Replace 11kv poles and hardware | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0009835 | 5.5 | 2017 | 2017-03-16 | B | 3 | 0.001967 | 8.9862e-06
1 | 16049963 | 2017-02-21 09:49 | 2017-02-21 12:30 | 161 | 1 | 161.45 | 0.00048378 | 0.000474 | 2.9964e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 781942 | FUSE - ELEMENT/LINK (HV) | Reload at Transformer X2636. 3 x 2A Fuses Bird Strike | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000474 | 11 | 2017 | 2017-02-21 | C | 1 | 0.000474 | 2.9964e-06
1 | 16059876 | 2017-02-21 12:21 | 2017-02-21 17:14 | 293 | 75 | 22003.3667 | 0.065932 | 0.065257 | 0.00022473 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 837940 | POLE | Advised SMC of 999 ETA 1 hour (12:26) - have advised Fire comms of ETA Pole (837940) found on fire Isolated at ABS S169 Fire caused by bird strike Used 1 x pole 1 x complete HV cross arm Contractor required to get pole to site and installed | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.065257 | 11 | 2017 | 2017-02-21 | C | 75 | 0.065257 | 0.00022473
1 | 16061211 | 2017-02-21 16:03 | 2017-02-21 16:16 | 13 | 660 | 8646 | 0.025907 | 0.019974 | 0.0019777 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | CB5 | UNKNOWN | CB5 Tripped when doing restoration switching under NAPA 29145. As part of the planned work Live Line work was carried out to connect new Sw/gear to the network. A Hot Line Tag was applied to CB5 for the LLP. This tag was still on when switching was being carried out. This is presumed to be the cause of the trip. | F3 | MOEHAU ST | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.019974 | 11 | 2017 | 2017-02-21 | C | 660 | 0.019974 | 0.0019777
1 | 16062563 | 2017-02-21 19:21 | 2017-02-21 20:16 | 55 | 4 | 221.8 | 0.00066461 | 0.000628 | 1.1986e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P1821 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A H/V, O/H fuses at fuses FP1666 & 1 x 6A H/V O/H fuse at transformer TC6249 ( bird strike ) | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000628 | 11 | 2017 | 2017-02-21 | C | 4 | 0.000628 | 1.1986e-05
1 | 16063737 | 2017-02-21 21:04 | 2017-02-21 22:44 | 99 | 5 | 497.8333 | 0.0014917 | 0.001446 | 1.4982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7247 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses tripped at 7247, Reloaded OK - 10A Rating (Suspect bird strike) | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.001446 | 11 | 2017 | 2017-02-21 | C | 5 | 0.001446 | 1.4982e-05
1 | 16063835 | 2017-02-21 22:02 | 2017-02-21 23:42 | 100 | 423 | 4672.1667 | 0.014 | 0.010197 | 0.0012675 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 2742 | UNKNOWN | Tripping on 33kV SFD CB2742 causing loss of supply to Motukawa (Flags 2742 O/C Neutral Time). Motukawa backfed via HUI GXP. Line patrolled (as much as practical at night) and sectionalised. Line all returned to service OK and Motukawa restored to normal configuration. Calm night, suspect Opossum. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.010197 | 33 | 2017 | 2017-02-21 | C | 423 | 0.010197 | 0.0012675
1 | 16066722 | 2017-02-21 13:43 | 2017-02-21 14:19 | 36 | 28 | 1008 | 0.0030204 | 0.002768 | 8.39e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | recreation | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.002768 | 11 | 2017 | 2017-02-21 | C | 28 | 0.002768 | 8.39e-05
1 | 16066807 | 2017-02-22 09:46 | 2017-02-22 10:05 | 19 | 5 | 95 | 0.00028466 | 0.000239 | 1.4982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208345 | JUMPER | Please check OMS 16066807 - 52 Killen when closing Faultman found a jumper on transformer TB1104 had rusted off at the HV bushing, transformer was isolated to refasten the jumper. 1 X bolt & lug used | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.000239 | 11 | 2017 | 2017-02-22 | C | 5 | 0.000239 | 1.4982e-05
1 | 16066873 | 2017-02-22 08:08 | 2017-02-22 10:05 | 116 | 11 | 1283.5167 | 0.0038459 | 0.003747 | 3.296e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13938 | FUSE - ELEMENT/LINK (HV) | fp 1186 2 x 8amp unknown 10:05 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003747 | 11 | 2017 | 2017-02-22 | C | 11 | 0.003747 | 3.296e-05
1 | 16066943 | 2017-02-22 08:20 | 2017-02-22 12:25 | 244 | 2 | 489.4 | 0.0014664 | 0.001448 | 5.9927e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P2036 | FUSE - ELEMENT/LINK (HV) | Reload at Spurline Fuses FC:P2036/1 - Don to get Label from SCADA 2 x 3A Fuses Bird Strike | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.001448 | 11 | 2017 | 2017-02-22 | C | 2 | 0.001448 | 5.9927e-06
1 | 16068567 | 2017-02-22 09:20 | 2017-02-22 09:30 | 10 | 1261 | 8649.7833 | 0.025918 | 0.014582 | 0.0028735 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Parkville Sub | PROTECTION (HV) | * 33kV MGM GXP CB 1352 tripped E/F O/C inverse time, Auto re closed successfully. * However Parkville sub 11kV Cb's 1, 2, 3, 4 all tripped incorrectly to lock out on AUFLS (auto frequency load shed) activation. * LOS to all Parkville ICP's. * Reset AUFLs relays via SCADA and reclosed CB's remotely. Downers inspected Sub and relays, all OK. * NCTL to Mike Allpress to discuss issue, requested relay downloads as it is suspected there is an issue with relays. This has now been completed. Confirmed by Mike relays have operated incorrectly. Mike has requested the AUFL's component be disabled asap to prevent re-occurrence. * Note: not a human element as per 'cause' due to SEL relay issue. | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.014582 | 33 | 2017 | 2017-02-22 | C | 1261 | 0.014582 | 0.0028735
1 | 16068947 | 2017-03-21 09:40 | 2017-03-21 15:36 | 356 | 24 | 8544 | 0.025591 | 0.025374 | 7.1884e-05 | NAPA ID:29133 TP_MANGAMAIRE GXP > MANGAMUTU SUB > RUAWHATA | 11 | Planned | 029133 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P48609 | NONE | To replace red tagged poles p48609,p48647 (GP) | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.012687 | 5.5 | 2017 | 2017-03-21 | B | 24 | 0.025374 | 7.1884e-05
1 | 16069860 | 2017-03-13 11:02 | 2017-03-13 12:17 | 75 | 74 | 5550 | 0.016625 | 0.01596 | 0.00022167 | NAPA ID:27603 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11 | Planned | 027603 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Taranaki Street | NONE | Install new RMU in Taranaki Street | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.00798 | 5.5 | 2017 | 2017-03-13 | B | 74 | 0.01596 | 0.00022167
1 | 16069899 | 2017-02-22 12:31 | 2017-02-22 14:16 | 104 | 1 | 104.75 | 0.00031387 | 0.000304 | 2.9963e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC3707 | UNKNOWN | Part of NAPA 27688 - Advised customer to check with retailer when notification letters are being sent | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000304 | 11 | 2017 | 2017-02-22 | C | 1 | 0.000304 | 2.9963e-06
1 | 16071675 | 2017-02-22 20:02 | 2017-02-22 20:46 | 44 | 3004 | 49711 | 0.14895 | 0.12195 | 0.0090012 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 2182 | UNKNOWN | FRM advised 8:17pm. Tripping on 33kV CB2182 on O/C Inst. causing loss of Supply to Wanganui East Sub. (11kV Backfed via Gas/Sw 998 and 4793). Patrol carried out, no fault located but many magpies sighted in area. Reclosed OK and restored to normal configuration. Notes: In depth patrol completed on the 23.02.2017 which located 2 magpies , one was fresh and one was slightly older and we suspect the cause of the first recorded fault. (OMS 15854152 05.02.2017) 27 magpies ?one group of 20 and one of 7 were counted in the area. | S4 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 0.12195 | 33 | 2017 | 2017-02-22 | C | 3004 | 0.12195 | 0.0090012
1 | 16079811 | 2017-03-27 09:25 | 2017-03-27 11:14 | 109 | 17 | 371 | 0.0011111 | 0.000958 | 5.0913e-05 | NAPA ID:28326 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | 028326 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 1412 Rotoehu Rd, Te Puke | NONE | link box cable maintenace | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000479 | 5.5 | 2017 | 2017-03-27 | B | 17 | 0.000958 | 5.0913e-05
1 | 16081847 | 2017-02-23 12:29 | 2017-02-23 14:48 | 139 | 279 | 21641 | 0.064844 | 0.062336 | 0.0011656 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 218167 | CONDUCTOR - REPAIR/REHANG | CB 1tripped on B & C phase O/C flags line was patrolled and sectionalised, received a call from customer to branches on the lines at 965 SH 2, line was isolated at ABS's IP128, SE6/082, SE6-035 and Links 13164/6 to cut way the branches at pole 218167. The trees are in side the notice zone. | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.062336 | 11 | 2017 | 2017-02-23 | C | 279 | 0.062336 | 0.0011656
1 | 16082805 | 2017-03-14 08:15 | 2017-03-14 15:30 | 435 | 14 | 6090 | 0.018243 | 0.018116 | 4.1937e-05 | NAPA ID:26844 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 026844 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 778156 | NONE | Pole replacement 778156 - 778179 & Upgrade TX 1932 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.009058 | 5.5 | 2017 | 2017-03-14 | B | 14 | 0.018116 | 4.1937e-05
1 | 16083840 | 2017-02-23 17:09 | 2017-02-23 18:15 | 66 | 33 | 2178 | 0.0065261 | 0.006229 | 9.888e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 747609 | CABLE - REPLACE LESS THAN 5 METRES | Check for safety - Lines down, tree twisted when being cut down and collected one line. No known loss of supply Have advised customer of hazard process SMC advised 4:22pm **Check - part power at 2129 Egmont Road (OMS 16083887)** Control and SMC advised of possible HV extent 4:54pm Isolated at Fuses 8198 Used 2 metres conductor 3 x sleeves NDR # N100321 | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.006229 | 11 | 2017 | 2017-02-23 | C | 33 | 0.006229 | 9.888e-05
1 | 16084144 | 2017-02-23 17:52 | 2017-02-23 19:42 | 109 | 412 | 35687.1333 | 0.10693 | 0.10323 | 0.0012345 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9948 | UNKNOWN | Trip Recloser 9948. O/C. L/O. Patrolled no fault found. Report of a flash at Pole M2499 from public. Pole isolated and climbed. Nothing could be found to have caused a flash. Feeder relivened OK. | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.10323 | 11 | 2017 | 2017-02-23 | C | 412 | 0.10323 | 0.0012345
1 | 16085233 | 2017-02-23 18:04 | 2017-02-23 19:12 | 68 | 86 | 5889.5667 | 0.017647 | 0.016874 | 0.00025769 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H106 | FUSE - ELEMENT/LINK (HV) | 2 Fuses found blown at Fuses H106 - Cause Possible Bird strike (Lakes in area) Used 2 x 20 amp HV fuses | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.016874 | 11 | 2017 | 2017-02-23 | C | 86 | 0.016874 | 0.00025769
1 | 16085976 | 2017-02-23 21:40 | 2017-02-24 01:25 | 225 | 2 | 450 | 0.0013484 | 0.00133 | 5.9927e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747612 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | **Check: 1918 Egmont Road, Inglewood - Tx 926 - OMS 16086851** Fuses found blown at Transformer 868 - cause transformer faulty Transformer replaced Used 1 x 15kVA transformer | F4 | KAIPI RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.00133 | 11 | 2017 | 2017-02-23 | C | 2 | 0.00133 | 5.9927e-06
1 | 16091688 | 2017-03-01 10:19 | 2017-03-01 12:21 | 121 | 55 | 6683.4167 | 0.020024 | 0.019529 | 0.00016478 | NAPA ID:29256 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | 029256 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | 11kV pole C2819 | NONE | Replace pole C2819 to gain legal clearance over driveway. Works location: Rawhiti Rd, Te Aroha. WO 30008227 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0097645 | 5.5 | 2017 | 2017-03-01 | B | 55 | 0.019529 | 0.00016478
1 | 16092304 | 2017-03-18 08:30 | 2017-03-18 16:10 | 460 | 55 | 5142 | 0.015402 | 0.014907 | 0.00016474 | NAPA ID:28404 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | 028404 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses SE6-215 | NONE | 11kV linkbox & cable term maintenace. Works location: Rangiuru Rd. WO 30022937 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0074535 | 5.5 | 2017 | 2017-03-18 | B | 55 | 0.014907 | 0.00016474
1 | 16092573 | 2017-03-19 08:30 | 2017-03-19 12:10 | 220 | 15 | 1494 | 0.0044749 | 0.00434 | 4.4929e-05 | NAPA ID:28407 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 028407 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fused ABS SF6-022 | NONE | 11kV linkbox & cable terminatation maintenace. Works location: Old Coach Rd. WO 30022938 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.00217 | 5.5 | 2017 | 2017-03-19 | B | 15 | 0.00434 | 4.4929e-05
1 | 16092898 | 2017-02-24 11:20 | 2017-02-24 16:38 | 318 | 297 | 93578.3667 | 0.28039 | 0.27772 | 0.0008899 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838617 | CONDUCTOR - REPAIR/REHANG | Caller advised - Horne Logging - Michael Gaine 027 444 2509 Loader has hit the lines, they have not come down but unsure if they have caused and damage or a fault On investigation found @ POLE 838617 all therr phases down and repaired NDR 34899 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.27772 | 11 | 2017 | 2017-02-24 | C | 297 | 0.27772 | 0.0008899
1 | 16093252 | 2017-02-24 11:31 | 2017-02-24 11:42 | 11 | 300 | 3375 | 0.010113 | 0.007415 | 0.00089889 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | P2243 | PROTECTION (HV) | Recloser 9853/2 L/O on E/F. Live line gang working on NAPA 28075-01 had a HLT applied to recloser 9823/2. They had an accidental jumper contact which tripped recloser 9853/2. They confirmed all OK and clear for a reliven. Safety Manager 711358. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.007415 | 11 | 2017 | 2017-02-24 | C | 300 | 0.007415 | 0.00089889
1 | 16093758 | 2017-03-13 09:15 | 2017-03-27 09:52 | 20197 | 75 | 3928 | 0.011766 | 0.011092 | 0.00028158 | NAPA ID:27799 TP_BUNNYTHORPE GXP > FEILDING SUB > BUSINESS | 11 | Planned | 027799 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11Kv Transformer T3/135 | NONE | Upgrade transformer T3/135 and switchgear 211/212/FS84 with new 500kva citypad and new CFC safelink switch. AP1 Make line break at T3/502. AP2 Remove exsiting transformer and switchgear. TP3 Test 11kv cable for phasing. AP4 Install new TX and Switchgear complete all jointing. TP5 Megger testing of new 11kv Cable and joints. AP6 Close line break at T3/502. Liven and test new switchgear and transformer. Please note all LV from T3/135 will be feed out of Tx 7431P. WORKS LOCATION: BOWEN ST. wo 30018763 | F2 | BUSINESS | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.005546 | 5.5 | 2017 | 2017-03-13 | B | 75 | 0.011092 | 0.00028158
1 | 16094436 | 2017-02-24 16:18 | 2017-02-24 17:48 | 90 | 263 | 22857.8 | 0.068489 | 0.066124 | 0.00078803 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T0970 | CONDUCTOR - REPAIR/REHANG | Check for safety - Tree contractors in working in the area have noticed a line about to fall off the insulator. Possible HV. Chris B from Asplundh stated to Stu that pole is T0970. Isolated between 9871/1, 9871/4, 2722, FP801, FP1467 & FP1815. Repaired line at pole T0970 & relivened | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.066124 | 11 | 2017 | 2017-02-24 | C | 263 | 0.066124 | 0.00078803
1 | 16094848 | 2017-03-20 10:30 | 2017-03-20 15:31 | 301 | 4 | 1204 | 0.0036062 | 0.00357 | 1.1981e-05 | NAPA ID:29195 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 029195 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 834480 | NONE | reconductor 11kv line between pole 834480 and t1883. Works location: Racecourse Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.001785 | 5.5 | 2017 | 2017-03-20 | B | 4 | 0.00357 | 1.1981e-05
1 | 16097439 | 2017-02-25 07:35 | 2017-02-25 09:40 | 124 | 4 | 499.7333 | 0.0014973 | 0.001461 | 1.1985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3336 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 2amp ht fuses, checked LT for fault. no fault found | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.001461 | 11 | 2017 | 2017-02-25 | C | 4 | 0.001461 | 1.1985e-05
1 | 16097599 | 2017-02-25 09:16 | 2017-02-25 11:37 | 140 | 330 | 10159.7 | 0.030441 | 0.027474 | 0.00098877 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 13080/2 | UNKNOWN | Recloser 9121/2 L/O on O/C, Sectionaliser 13080/2 L/O on O/C A, B & C phase. Reclosed 9121/2. Sectionalised beyound 13080/2 and found NO fault | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.027474 | 11 | 2017 | 2017-02-25 | C | 330 | 0.027474 | 0.00098877
1 | 16098154 | 2017-02-25 11:06 | 2017-02-25 11:44 | 37 | 12 | 424.5667 | 0.0012721 | 0.001164 | 3.5955e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB6 | UNKNOWN | O/C B & C Phase. Patrolled nothing found | F1 | BRYCE ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.001164 | 11 | 2017 | 2017-02-25 | C | 12 | 0.001164 | 3.5955e-05
1 | 16099024 | 2017-03-24 08:30 | 2017-03-24 15:12 | 402 | 88 | 35376 | 0.10595 | 0.10516 | 0.00026356 | NAPA ID:29102 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 029102 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 8144482 | NONE | replace defective poles 814482 and 814277. Works location: Lyon St, Featherston. WO 30030519 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.052581 | 5.5 | 2017 | 2017-03-24 | B | 88 | 0.10516 | 0.00026356
1 | 16099123 | 2017-03-30 10:22 | 2017-03-30 13:20 | 178 | 10 | 1780 | 0.0053306 | 0.00524 | 2.9947e-05 | NAPA ID:28081 TP_LINTON GXP > KAIRANGA SUB > DAIRYFACT | 11 | Planned | 028081 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P43739 | NONE | Replace 11KV pole P43739. Works location: Reserve Rd, Longburn. WO 30024417 | F1 | DAIRYFACT | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.00262 | 5.5 | 2017 | 2017-03-30 | B | 10 | 0.00524 | 2.9947e-05
1 | 16099163 | 2017-02-25 21:15 | 2017-02-25 22:07 | 52 | 5 | 260.5833 | 0.00078078 | 0.000735 | 1.4981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M27 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses M27. 2 X 6 amp HV fuse replaced. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000735 | 11 | 2017 | 2017-02-25 | C | 5 | 0.000735 | 1.4981e-05
1 | 16099260 | 2017-02-25 23:36 | 2017-02-26 01:09 | 93 | 504 | 39384.5 | 0.11801 | 0.11348 | 0.0012734 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Sectionaliser 9870 line patrolled nothing found | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.11348 | 11 | 2017 | 2017-02-25 | C | 504 | 0.11348 | 0.0012734
1 | 16099818 | 2017-02-26 04:08 | 2017-02-26 09:01 | 293 | 165 | 48345 | 0.14485 | 0.14337 | 0.00049438 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | TA2 012 | FUSE - ELEMENT/LINK (HV) | WBH 5 Recloser 9870 tripped ( oms 16099260 ) returned to service no fault found part powers beyond FABS IP452 blown fuses in Link Box TA2 012, dead rat found in link box TA2 012 isolation at FABS IP452 ( no back feeds ) fuses replaced all service restored Materials 1 x 20A H/V U/G fuse L1, 1 x 31A H/V U/G fuse L2 Link box defected not vermin proof | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.14337 | 11 | 2017 | 2017-02-26 | C | 165 | 0.14337 | 0.00049438
1 | 16100673 | 2017-02-26 10:42 | 2017-02-26 12:35 | 113 | 3 | 339 | 0.0010157 | 0.000988 | 8.9886e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 818807 | FUSE - ELEMENT/LINK (HV) | Fire comms enroute, require an ETA Event #F2254571 Have notified SMC. FEA C911 Isolation at fuses 7216 ( spur no back feed ) to remove branch from lines at pole 818807 ( member of public felling tree ) branch removed all service restored NDR No to follow Materials 2 x 10A H/V, O/H fuses | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000988 | 11 | 2017 | 2017-02-26 | C | 3 | 0.000988 | 8.9886e-06
1 | 16103002 | 2017-03-18 08:45 | 2017-03-18 14:02 | 317 | 3 | 951 | 0.0028485 | 0.002821 | 8.9859e-06 | NAPA ID:28698 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 028698 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Te Wharau Rd, Carterton | NONE | Replace multiple 11kv poles and cross arms | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.0014105 | 5.5 | 2017 | 2017-03-18 | B | 3 | 0.002821 | 8.9859e-06
1 | 16103635 | 2017-02-27 11:25 | 2017-02-27 11:56 | 31 | 10 | 310 | 0.00092881 | 0.000838 | 2.9962e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798560 | BINDER | oUTAGE REQUIRED FROM FUSES 7261 TO REPAIR A FLOATING CONDUCTOR ON VILES rd. OLD COPPER BINDER HAD BROKE, REPLACED AND REBOUND OK. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000838 | 11 | 2017 | 2017-02-27 | C | 10 | 0.000838 | 2.9962e-05
1 | 16103874 | 2017-03-10 09:30 | 2017-03-10 15:20 | 350 | 42 | 14700 | 0.044036 | 0.043658 | 0.00012582 | NAPA ID:28696 TP_HUIRANGI GXP > BELL BLOCK SUB > AIRPORT DRIVE | 11 | Planned | 028696 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Remove exiting 200KV ground mount transformer 2011N, replace for a new 300kva ground mount Transformer - Upgrade 11KV fuses. | F1 | AIRPORT DRIVE | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.021829 | 5.5 | 2017 | 2017-03-10 | B | 42 | 0.043658 | 0.00012582
1 | 16104078 | 2017-03-21 08:35 | 2017-03-22 15:31 | 1855 | 59 | 88849.0833 | 0.26612 | 0.26559 | 0.00035343 | NAPA ID:28339 TP_HINUERA GXP > PUTARURU SUB > ARAPUNI ST | 11 | Planned | 028339 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/Gear IC2037 | NONE | Replace switchgear IC2037 and IC2038 with new Siemens 8DJH RRT switch unit. Works location: Arapuni St. WO 30019194 | F1 | ARAPUNI ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.13279 | 5.5 | 2017 | 2017-03-21 | B | 59 | 0.26559 | 0.00035343
1 | 16104436 | 2017-02-27 13:09 | 2017-02-27 15:09 | 120 | 4 | 482.8667 | 0.0014468 | 0.00141 | 1.1985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01306 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp @t9/181 bird strike 1509 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.00141 | 11 | 2017 | 2017-02-27 | C | 4 | 0.00141 | 1.1985e-05
1 | 16106043 | 2017-02-27 16:18 | 2017-02-27 18:05 | 106 | 16 | 1708 | 0.0051175 | 0.004973 | 4.7939e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | o792 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 15A H/V, O/H fuses at fuses FC4174 ( bird strike ) | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.004973 | 11 | 2017 | 2017-02-27 | C | 16 | 0.004973 | 4.7939e-05
1 | 16106184 | 2017-02-27 18:57 | 2017-02-27 20:26 | 89 | 532 | 46854.8 | 0.14039 | 0.1356 | 0.001594 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | Recloser 9773/2 L/O on O/C Reported flash from 239 Roberts Rd, checked all OK Opened sectionaliser 13085, SS9396 & 9892, reclosed recloser 9773 OK, reclosed other sectionaliser OK NO fault found | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.1356 | 11 | 2017 | 2017-02-27 | C | 532 | 0.1356 | 0.001594
1 | 16107816 | 2017-02-27 23:04 | 2017-02-28 00:43 | 98 | 1 | 98.65 | 0.00029557 | 0.000286 | 2.9961e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 364322 | FUSE - ELEMENT/LINK (HV) | 2 X 15 Amp HT Fuses at FABS 4564 Due To Opossum | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000286 | 11 | 2017 | 2017-02-27 | C | 1 | 0.000286 | 2.9961e-06
1 | 16107901 | 2017-02-28 07:32 | 2017-02-28 09:51 | 139 | 36 | 5008.8 | 0.015007 | 0.014683 | 0.00010786 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | N1802 | FUSE - ELEMENT/LINK (HV) | 1R LV to HV upgrade. Please check fuses as we have multiple part power faults past this point. Advised SMC of possible HV extent. ***Please check OMS 16107915, 16107924, 16107998, 16107953, 16108701, 16108730, 16108741*** Opossum found on line at Pole N1802. Knocked off with Fuse Stick. 2 X 15A HV Fuses Replaced. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.014683 | 11 | 2017 | 2017-02-28 | C | 36 | 0.014683 | 0.00010786
1 | 16108778 | 2017-03-22 09:00 | 2017-03-22 14:42 | 342 | 8 | 456 | 0.0013658 | 0.001293 | 4.7922e-05 | NAPA ID:28985 TP_KOPU GXP | 11 | Planned | 028985 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T13163 | CONDUCTOR - REPAIR/REHANG | Reconductor between Pole T13163 and ABS IC368 Connection & disconnection of Generator at Transformer TC1501 under same AP as main Job | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0006465 | 5.5 | 2017 | 2017-03-22 | B | 8 | 0.001293 | 4.7922e-05
1 | 16109630 | 2017-02-28 11:56 | 2017-02-28 18:30 | 393 | 140 | 1655.75 | 0.0049608 | 0.003702 | 0.00042245 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X2635 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 1 HV Fuse at Transformer X2635 initially found tripped. A reload attempt caused recloser CB 2032 to trip on EF. Fuses all open to isolate for Transformer change. Recloser 2032 reclosed. (Fault called in at X2636, actually X2635). Used 1X 15 KVA Transformer. Main Switch at Pump Shed left off Farmer has been told due to not being able to check Rotate | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.003702 | 11 | 2017 | 2017-02-28 | C | 140 | 0.003702 | 0.00042245
1 | 16109973 | 2017-02-28 11:26 | 2017-02-28 15:15 | 229 | 4 | 916 | 0.0027445 | 0.002708 | 1.1985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | RANGITAUTAU ROAD | FUSE - ELEMENT/LINK (HV) | @ x 4032 2 x 3amp fuse lightening 15:15 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002708 | 11 | 2017 | 2017-02-28 | C | 4 | 0.002708 | 1.1985e-05
1 | 16111136 | 2017-02-28 15:02 | 2017-02-28 17:32 | 150 | 4 | 600 | 0.0017977 | 0.001761 | 1.1985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T795 | CONDUCTOR - REPAIR/REHANG | Check for safety - Lines down on the ground. Have completed the hazard process. Using nearest ICP. Advised control and SMC of 999. HV isolation required on Transformer T795 for LV repairs. 2 LV Conductors repaired / rehung with 4 sleeves and several metres of ferret. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001761 | 11 | 2017 | 2017-02-28 | C | 4 | 0.001761 | 1.1985e-05
1 | 16111618 | 2017-02-28 19:15 | 2017-02-28 19:49 | 34 | 4 | 136 | 0.00040747 | 0.000371 | 1.1985e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 228730 | STAY WIRE | Shelter belt trimmer has cut through staywire - area is safe but pole has moved Craig Beaumont (027) 271 4358 Beaumont Shelter Trimming *Craig will call his insurance company to make a claim now so any details of costs/how to pay would be appreciated!* PGA5 offload transformer TF6 045 to replace staywire Off 19:15 - On 19:49 NDR 44728 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.000371 | 11 | 2017 | 2017-02-28 | C | 4 | 0.000371 | 1.1985e-05
1 | 16112160 | 2017-02-28 18:51 | 2017-02-28 20:10 | 79 | 2 | 158.2 | 0.00047399 | 0.000456 | 5.9922e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8257 | FUSE - ELEMENT/LINK (HV) | 2 X 8 Amp HT Fuses At 8257 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.000456 | 11 | 2017 | 2017-02-28 | C | 2 | 0.000456 | 5.9922e-06
1 | 16113398 | 2017-03-01 08:15 | 2017-03-01 12:45 | 270 | 109 | 23779 | 0.071244 | 0.070264 | 0.00032657 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P45209 | POLE | * Check for safety - Car vs Pole, lines down. ETA required. Advised control and SMC of 999 * ETA 15 mins - Advised fire comms, New information from them to say lines have not come down but pole has moved and lines are strained. * On arrival, identified as 11kV. * Lines isolated via ABS's B41, B42 & B43 to replace pole P45209. * NDR: 300297 1x pole and complete hardware. * NOTE: Had to push out isolation area than actually required as found ABS B44 had a tag applied to it in field. No additional SAIDI loss though. Investigation found the asset had a broken operating handle at the top. No DNO listed in NOC database. Further investigation found the asset had been amber defected 14th November 2016 with a work order issued on the 15th. Due to the operational constraint and required process NOC created DNO 170302. The remedial works are booked for 15/3/17 via NAPA 29113 using the original work order. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.070264 | 11 | 2017 | 2017-03-01 | C | 109 | 0.070264 | 0.00032657
1 | 16113582 | 2017-03-01 07:33 | 2017-03-01 09:43 | 130 | 4 | 520 | 0.001558 | 0.001522 | 1.1984e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12650 | FUSE - ELEMENT/LINK (HV) | 2 x3amp@ t8 /374 09:43 magpie | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001522 | 11 | 2017 | 2017-03-01 | C | 4 | 0.001522 | 1.1984e-05
1 | 16113601 | 2017-03-21 09:15 | 2017-03-21 14:55 | 340 | 41 | 13940 | 0.041753 | 0.041384 | 0.0001228 | NAPA ID:28144 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | 028144 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S118 | NONE | Change 11/33 kv poles and TXs Morris Rd between S118 and pole 853644 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.020692 | 5.5 | 2017 | 2017-03-21 | B | 41 | 0.041384 | 0.0001228
1 | 16114280 | 2017-03-22 09:30 | 2017-03-22 12:20 | 170 | 7 | 1190 | 0.0035642 | 0.003501 | 2.0966e-05 | NAPA ID:29351 TP_STRATFORD GXP > CARDIFF SUB > CLIMIE RD | 11 | Planned | 029351 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2616t | NONE | Existing transformer 2616T to be upgraded on existing structure from 30kva to 50kva | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.0017505 | 5.5 | 2017 | 2017-03-22 | B | 7 | 0.003501 | 2.0966e-05
1 | 16114488 | 2017-03-01 09:55 | 2017-03-01 11:41 | 105 | 392 | 41342.9333 | 0.12387 | 0.12034 | 0.0011745 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P14773 | POLE | Relates to OMS 16111299 for replacement of Pole P14773. Line wasd isolated at ABS's J41, J42 & J45 and at transformer T3/240 to replace the pole & all the hardware. NDR: 39302 1 X pole & all hardware | F3 | RESIDENTIAL | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.12034 | 11 | 2017 | 2017-03-01 | C | 392 | 0.12034 | 0.0011745
1 | 16115051 | 2017-03-01 13:34 | 2017-03-01 13:56 | 22 | 39 | 858 | 0.0025706 | 0.00222 | 0.00011685 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738072 | BINDER | 1R - Paddosck Side Binder requires Urgent replacement. -Pole 738072 - Eltham CB R11 - Wingrove Rd Isolated at ABS's 6020, 6093 and 6167 with backfeed installed via ABS 6034 Binders replaced - used 1 x binder | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.00222 | 11 | 2017 | 2017-03-01 | C | 39 | 0.00222 | 0.00011685
1 | 16116163 | 2017-03-04 10:10 | 2017-03-04 11:56 | 105 | 1 | 105.6667 | 0.00031657 | 0.000307 | 2.9959e-06 | NAPA ID:29452 TP_WAIHOU GXP > INGHAMS SUB > INGHAMS 1 | 11 | Planned | 029452 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP728 | NONE | DNO 170224, Shut down and Disconnection of Generator off 400 volt cable Tails on TP728, connect cables to Inghams switch board to same TP728. Change FP283 fuses to new 125amp one. Reliven via CB1 inghams sub. Replacement of Transformer TP728 due to faulty Red Phase HV Bushing. Sorry the powerco po number from Andrew 30043569 no go used this one. This is only approx. shutdown time....... | F1 | INGHAMS 1 | WAIHOU | Valley | INGHAMS SUB | Eastern Electricity | POWERCO | 0.0001535 | 5.5 | 2017 | 2017-03-04 | B | 1 | 0.000307 | 2.9959e-06
1 | 16117412 | 2017-03-01 14:39 | 2017-03-01 15:55 | 75 | 601 | 35182.75 | 0.10541 | 0.10001 | 0.0018006 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB's T11 & T31 | UNKNOWN | * 11kV CB's T11 & T31 both tripped A,B,C Ph O/C to lock out. * Note Tree trimming being carried out via planned CAC on CB T11 circuit - Tree trimmers contacted and stood down (checked if that may of caused fault, all OK, confirmed as not the cause of trip. * CB T11 had a Hot Line Tag applied as part of safety measures for CAC works. * Being an outside 11kV BUS, the structure was inspected prior to re-livening to check for any evidence of flash over or fault cause. No evidence of fault cause in structure. * NOC suspect T11 protection (HLT) may have over-reached into T31 circuit. T11, successfully re-closed. * T31 circuit sensationalized, no fault found, successfully re-livened. * May require protection investigation on suspected HLT issue. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.10001 | 11 | 2017 | 2017-03-01 | C | 601 | 0.10001 | 0.0018006
1 | 16118613 | 2017-03-24 09:15 | 2017-03-24 16:35 | 440 | 36 | 15840 | 0.047441 | 0.047117 | 0.00010782 | NAPA ID:29430 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11 | Planned | 029430 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36000 | NONE | Change from over head 11kv to underground 11kv from poles 36000 to 36002 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.023558 | 5.5 | 2017 | 2017-03-24 | B | 36 | 0.047117 | 0.00010782
1 | 16119227 | 2017-03-01 15:01 | 2017-03-01 16:17 | 76 | 20 | 1532 | 0.00459 | 0.00441 | 5.9922e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Refer OMS 16117169 for details | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00441 | 11 | 2017 | 2017-03-01 | C | 20 | 0.00441 | 5.9922e-05
1 | 16120645 | 2017-03-01 18:16 | 2017-03-01 20:49 | 153 | 498 | 39830 | 0.11933 | 0.11486 | 0.001492 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 3738 | CABLE - REPAIR | ( PUT2 ) recloser 9948/2 tripped O/C C Ph, L/O, feeder sectionalised with possible cable fault between Sw/Gear 13127/4 & T/Blade 3738 position A with back feed via Sw/Gear IC3149 all service restored | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.11486 | 11 | 2017 | 2017-03-01 | C | 498 | 0.11486 | 0.001492
1 | 16121182 | 2017-03-01 18:31 | 2017-03-01 21:10 | 159 | 27 | 4300.65 | 0.012885 | 0.012642 | 8.0894e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5193 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses tripped at 5193. Piko Rd patrolled but nothing found. Reloaded OK (15A Rating) | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.012642 | 11 | 2017 | 2017-03-01 | C | 27 | 0.012642 | 8.0894e-05
1 | 16122137 | 2017-03-02 06:50 | 2017-03-02 11:14 | 264 | 30 | 1860 | 0.0055726 | 0.005302 | 0.00017976 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP481 | FUSE - ELEMENT/LINK (HV) | 2 x Fuses at FP481 found blown. Suspect cable fault. Generator being arranged to be installed at transformer TP497 Generator was connected, cable tested but all proved to be ok. Cable livened with 3 amp fuses proving cable fault free. Blown fuses suspected to be caused by bird strike in span of O/H towards transformer TP497. Fuses replaced with correct rating. Generator removed. All supply restored to normal. | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.005302 | 11 | 2017 | 2017-03-02 | C | 30 | 0.005302 | 0.00017976
1 | 16125525 | 2017-03-02 09:21 | 2017-03-02 11:49 | 148 | 1 | 148.0667 | 0.00044361 | 0.000434 | 2.996e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2982T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | TX is in poor condition Cross arms in poor condition. Will defect TX and cross arms. 765116 2982T Deterioration Adjacent assets checked and deteriorated as well. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000434 | 11 | 2017 | 2017-03-02 | C | 1 | 0.000434 | 2.996e-06
1 | 16125828 | 2017-03-02 09:57 | 2017-03-02 11:40 | 102 | 584 | 14116.7667 | 0.042294 | 0.037045 | 0.00095274 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | CONDUCTOR - REPAIR/REHANG | 1 x A/R on CB 5 Coromandel sub. L/O on sectionaliser 9839/2. O/C & E/F flags. Line sectionalised & patrolled. NC received report at 10:56 of concrete truck contacting line a around 195 Manaia Rd. Lines were isolated at ABS IC311 & IP448 at time of report for sectionalising. Hiab removed from line using hotstick at pole V13097. All supply restored. The outage only involved up to ABS IP448 as it was open at time with backfeed in place for unrelated planned outage. (NAPA 28798). Reports of truck vs. lines. Enter into safety manager. See Job history log for additional comments. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.037045 | 11 | 2017 | 2017-03-02 | C | 584 | 0.037045 | 0.00095274
1 | 16127344 | 2017-03-15 06:03 | 2017-03-16 16:00 | 2037 | 56 | 5996.6667 | 0.017963 | 0.017459 | 0.00033549 | NAPA ID:28223 TP_WAIKINO GXP > WAIHI SUB > GILMOUR ST | 11 | Planned | 028223 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13150 | NONE | Replacement of reyrolle JKSS switch with Siemens 8DJH RRT Switchgear 13150 | F3 | GILMOUR ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.0087295 | 5.5 | 2017 | 2017-03-15 | B | 56 | 0.017459 | 0.00033549
1 | 16128146 | 2017-03-03 09:46 | 2017-03-03 10:10 | 24 | 58 | 1392 | 0.0041704 | 0.003649 | 0.00017377 | NAPA ID:29530 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | 029530 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 3738 | CABLE - REPLACE LESS THAN 5 METRES | make cable break at TC 3738 to Isolate cable to locate cable fault | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.0018245 | 5.5 | 2017 | 2017-03-03 | B | 58 | 0.003649 | 0.00017377
1 | 16128712 | 2017-03-02 22:25 | 2017-03-03 02:18 | 233 | 1 | 233.3833 | 0.00069923 | 0.00069 | 2.996e-06 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | FP282 | UNKNOWN | 33kV CB22 Trip 11kV CB17 Trip Fuse/Sw FP282 at Inghams Plant Three Fuses found Blown. BUS and Fuse/Sw isolated and Fuse Chamber cleaned. Everything tested and nothing found wrong. Unsure of why all 3 fuses blew. Suspect a Rat crawled into Fuse Chamber. BUS and Fuse/Sw livened back up OK Once again CB1 did not trip as it should have and fault was cleared by CB 22 and 17. Someone needs to check the protection settings of CB1. | S3 | WAIHOU392-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 0.00069 | 33 | 2017 | 2017-03-02 | C | 1 | 0.00069 | 2.996e-06
1 | 16134058 | 2017-03-03 13:10 | 2017-03-03 13:53 | 43 | 3 | 129 | 0.00038648 | 0.000359 | 8.9879e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 362096 | DEAD-ENDS | Reterminate conductor onto Poles 362096 & 362018 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000359 | 11 | 2017 | 2017-03-03 | C | 3 | 0.000359 | 8.9879e-06
1 | 16134482 | 2017-03-29 09:15 | 2017-03-29 12:21 | 186 | 144 | 26784 | 0.080212 | 0.078918 | 0.00043125 | NAPA ID:29124 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11 | Planned | 029124 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace network pole 700074 with new 11m Busck pole for fibre pole replacement | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.039459 | 5.5 | 2017 | 2017-03-29 | B | 144 | 0.078918 | 0.00043125
1 | 16134551 | 2017-03-17 10:15 | 2017-03-17 13:30 | 195 | 3 | 585 | 0.0017523 | 0.001725 | 8.986e-06 | NAPA ID:28718 TP_HUIRANGI GXP | 11 | Planned | 028718 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5104 | NONE | We are replacing 11kv ABS 5104. DNO 161209 | F4 | WAITARA EAST TOWN | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.0008625 | 5.5 | 2017 | 2017-03-17 | B | 3 | 0.001725 | 8.986e-06
1 | 16135139 | 2017-03-03 19:21 | 2017-03-03 23:10 | 229 | 337 | 68042.9 | 0.20386 | 0.20083 | 0.0011325 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20466 | CONDUCTOR - REPAIR/REHANG | Recloser L10 tripped on E/F flags. line was patrolled and line down was found at pole P20466, line was isolated at ABS L13 to repair line, secund fault was found at transformer T1/325 had a blown jumper to it, line was isolated at ABS L17 to repair the jumper. 2 X sleeves & 1 X amp | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.20083 | 11 | 2017 | 2017-03-03 | C | 337 | 0.20083 | 0.0011325
1 | 16135483 | 2017-03-03 19:22 | 2017-03-03 19:49 | 26 | 836 | 22558.0667 | 0.067584 | 0.060069 | 0.0025047 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 833255 | CONDUCTOR - REPAIR/REHANG | CB C823 Trip. O/C. L/O. Report of a Bird Strike at 1 Kiwi St. Duck found on ground below lines by a member of the public at Pole 833255 No damage could be seen. Feeder closed back in OK | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.060069 | 11 | 2017 | 2017-03-03 | C | 836 | 0.060069 | 0.0025047
1 | 16137749 | 2017-03-04 17:27 | 2017-03-04 18:44 | 77 | 23 | 1771 | 0.0053058 | 0.005099 | 6.8907e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4399 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Faulty HV fuse base at transformer TC4399. Line isolated between ABS 2600 & 2595 for repairs. All 3 fuse bases replaced. Also 1 x HV crossarm & assemblies replaced. All supply restored at completion of repairs. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.005099 | 11 | 2017 | 2017-03-04 | C | 23 | 0.005099 | 6.8907e-05
1 | 16137764 | 2017-03-04 17:14 | 2017-03-04 17:35 | 21 | 54 | 1134 | 0.0033974 | 0.002912 | 0.00016178 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P19036 | JUMPER | Repaired jumper on pole P19036 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.002912 | 11 | 2017 | 2017-03-04 | C | 54 | 0.002912 | 0.00016178
1 | 16140499 | 2017-03-04 19:27 | 2017-03-04 23:00 | 213 | 1 | 213.4 | 0.00063934 | 0.00063 | 2.9959e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 765120 | CONDUCTOR - REPAIR/REHANG | Faultman found lines down caused by trees at pole 765120, line was isolated at Fuses 8684 to repair the lines and tree contractor cut tree way from lines. 60 meters of 16mm copper conductor used. 6 X sleeves. NDR: to follow later | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.00063 | 11 | 2017 | 2017-03-04 | C | 1 | 0.00063 | 2.9959e-06
1 | 16140525 | 2017-03-04 18:49 | 2017-03-04 20:32 | 102 | 2 | 205.7 | 0.00061627 | 0.000598 | 5.9918e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU205 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses PU205. 2 X 6 amp HV fuses replaced. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000598 | 11 | 2017 | 2017-03-04 | C | 2 | 0.000598 | 5.9918e-06
1 | 16140693 | 2017-03-04 21:31 | 2017-03-04 23:26 | 115 | 2 | 230 | 0.00068907 | 0.000671 | 5.9918e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/262 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found transformer T7/262 to be faulty, transformer was isolated and replaced. | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000671 | 11 | 2017 | 2017-03-04 | C | 2 | 0.000671 | 5.9918e-06
1 | 16140754 | 2017-03-04 21:51 | 2017-03-05 00:15 | 144 | 10 | 1443.3333 | 0.0043242 | 0.004234 | 2.9959e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 045 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 045 cause by duck strike. 2 X 10 amp fuses replaced | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.004234 | 11 | 2017 | 2017-03-04 | C | 10 | 0.004234 | 2.9959e-05
1 | 16141132 | 2017-03-05 11:13 | 2017-03-05 14:59 | 225 | 64 | 14330.6667 | 0.042933 | 0.042358 | 0.00038348 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P06283 | INSULATOR | 11.45 - called SMC as Control had not heard from FM. Fixed staywire at Pole P06283 Used 1 X Eye Bolt 1 X Polyma Insulator | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.042358 | 11 | 2017 | 2017-03-05 | C | 64 | 0.042358 | 0.00038348
1 | 16142255 | 2017-03-05 14:11 | 2017-03-05 15:49 | 97 | 669 | 38541.1333 | 0.11547 | 0.10945 | 0.0020043 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1 | UNKNOWN | CB 1 L/O on O/C A & B. Recloser 9804 Opened but ABR did not work. 9805 would not close via SCADA and would not close on site. closed bypass 9805/1. Sectionalised rest of feeder and found NO fault | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.10945 | 11 | 2017 | 2017-03-05 | C | 669 | 0.10945 | 0.0020043
1 | 16143661 | 2017-03-05 17:06 | 2017-03-05 17:25 | 18 | 3 | 55.9 | 0.00016747 | 0.00014 | 8.9877e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7262 | JUMPER | Put Jumper bcak in Bottom of fuses 7262 Nothing used 30/3/2017: Crew assignment times have been amended to reflect the Crew Transition reflected in the original OMS job 16143607 (Cancelled and Merged to this OMS Number) for KPI Reporting Purposes. (axk). | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.00014 | 11 | 2017 | 2017-03-05 | C | 3 | 0.00014 | 8.9877e-06
1 | 16144047 | 2017-03-05 18:46 | 2017-03-05 21:17 | 151 | 257 | 5490.0833 | 0.016448 | 0.014137 | 0.00076995 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 449964 | CROSSARM - WHOLE ASSEMBLY | Car V Pole Replaced crossarm and repaired conductor NDR N100328 | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.014137 | 11 | 2017 | 2017-03-05 | C | 257 | 0.014137 | 0.00076995
1 | 16144540 | 2017-03-05 20:09 | 2017-03-05 22:30 | 141 | 6 | 848.5 | 0.002542 | 0.002488 | 1.7975e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | N48 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a hv fuses | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.002488 | 11 | 2017 | 2017-03-05 | C | 6 | 0.002488 | 1.7975e-05
1 | 16145370 | 2017-03-05 23:18 | 2017-03-06 02:34 | 196 | 396 | 24458.5667 | 0.073276 | 0.069716 | 0.0011864 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | Walton CB 3 | NONE | CB 3 tripped to L/O. E/F flag. Line sectionalised & patrolled beyond ABS IC755 were found to have operated. Operational patrol carried out but no apparent fault found. IC755 reclosed successfully. Suspect opossum was on line and cleared?? Clear night and comment by faultman of sighting several during patrol. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.069716 | 11 | 2017 | 2017-03-05 | C | 396 | 0.069716 | 0.0011864
1 | 16147096 | 2017-03-06 08:33 | 2017-03-06 13:14 | 281 | 306 | 67722.0833 | 0.20289 | 0.20014 | 0.0013541 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797333 | CONDUCTOR - REPAIR/REHANG | Batteries went dead 13 mins after Tripping so could not try Reclose Faultman 45 Mins away have requested Batteries Replaced Today 06/03/17 Used 3 Connector at Pole 797333 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.20014 | 11 | 2017 | 2017-03-06 | C | 306 | 0.20014 | 0.0013541
1 | 16147977 | 2017-03-28 10:01 | 2017-03-28 10:09 | 8 | 16 | 128.1 | 0.00038364 | 0.000239 | 4.7917e-05 | NAPA ID:29523 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11 | Planned | 029523 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3645 South Rd, Pihama | NONE | DNO 170216. Disconnect Pihama Regulators to investigate and repair faulty unit. After disconnection complete, connect and liven temp regulators at the site, liven and commission. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0001195 | 5.5 | 2017 | 2017-03-28 | B | 16 | 0.000239 | 4.7917e-05
1 | 16148116 | 2017-03-26 09:44 | 2017-03-26 12:42 | 178 | 35 | 5153 | 0.015433 | 0.015118 | 0.00010482 | NAPA ID:28248 TP_HAWERA GXP > WHAREROA SUB > MANUTAHI | 11 | Planned | 028248 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 728357 | NONE | Replace defected pole 728357 with new 11m busck pole | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.007559 | 5.5 | 2017 | 2017-03-26 | B | 35 | 0.015118 | 0.00010482
1 | 16148139 | 2017-03-06 09:45 | 2017-03-06 11:58 | 133 | 3 | 399 | 0.0011953 | 0.001168 | 8.9875e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C14328 | CROSSARM - WHOLE ASSEMBLY | ( FRM 6 ) Emergency switching to replace broken arm at pole C14328. Isolation at fuses FC1417 ( spur no back feed ) Arm replaced all service restored. Materials 1 x double arm complete | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.001168 | 11 | 2017 | 2017-03-06 | C | 3 | 0.001168 | 8.9875e-06
1 | 16148149 | 2017-03-20 10:00 | 2017-03-20 10:12 | 12 | 8 | 96 | 0.00028754 | 0.000215 | 2.3962e-05 | NAPA ID:29368 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 029368 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-008 | NONE | CHECK FUSE RATING AT SF6-008 AND CHANGE IF REQUIRED | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0001075 | 5.5 | 2017 | 2017-03-20 | B | 8 | 0.000215 | 2.3962e-05
1 | 16149433 | 2017-03-24 08:47 | 2017-03-24 15:15 | 387 | 11 | 4265.6167 | 0.012776 | 0.012676 | 3.2945e-05 | NAPA ID:28148 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | 028148 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 358641 | NONE | Change 11kv Poles and arms Watsons Rd between poles 358641 & 827221 , isolation area from TEMP 69 to TEMP71 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.006338 | 5.5 | 2017 | 2017-03-24 | B | 11 | 0.012676 | 3.2945e-05
1 | 16149910 | 2017-03-06 12:54 | 2017-03-06 14:32 | 98 | 37 | 3626 | 0.010863 | 0.01053 | 0.00011085 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K13381 | CROSSARM - WHOLE ASSEMBLY | ( TAH4 ) Line patrol report burnt arm & floating conductor at pole K13381 Isolation at ABS IC484 ( spur no back feed ) Arm replaced conductor re bound all service restored Materials 1 x H/V arm complete Northpower completed the job, NOC made asumption Downers in attendance Northpower not to attend repairs on fly as per A Wilson | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.01053 | 11 | 2017 | 2017-03-06 | C | 37 | 0.01053 | 0.00011085
1 | 16155953 | 2017-03-06 18:54 | 2017-03-06 20:18 | 84 | 6 | 504 | 0.0015099 | 0.001455 | 1.7975e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | se8-008 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10amp ht fuse outage on child | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001455 | 11 | 2017 | 2017-03-06 | C | 6 | 0.001455 | 1.7975e-05
1 | 16156700 | 2017-03-07 02:05 | 2017-03-07 02:57 | 52 | 84 | 4368 | 0.013086 | 0.01233 | 0.00025165 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tc494 | FUSE - HOLDER/BASE (LV) | Isolated transformer tc494 at fuses fp806 to replace burnt out lv fuses at transformer outage on child | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.01233 | 11 | 2017 | 2017-03-07 | C | 84 | 0.01233 | 0.00025165
1 | 16157342 | 2017-03-07 09:29 | 2017-03-07 09:50 | 20 | 1786 | 32913.9167 | 0.098604 | 0.082552 | 0.0053505 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | unknown | UNKNOWN | PKO CB 3162 tripped B Ph O/C, E/F, L/O Loss of WLN Sub & WAH T1 WLN Sub & WAH T1 back feed via BRN CB 3022 ( HIN GXP ) line patrolled between PKO & WLN Subs with no fault found ( suspect bird strike ) PKO CB 3162 put on soak & returned to normal configuratioin | S2 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 0.082552 | 33 | 2017 | 2017-03-07 | C | 1786 | 0.082552 | 0.0053505
1 | 16159518 | 2017-03-07 09:57 | 2017-03-07 11:59 | 122 | 257 | 12518.8 | 0.037504 | 0.035194 | 0.00076992 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 742753 | CONDUCTOR - REPAIR/REHANG | ( BBK 7 ) recloser 6610/2 tripped E/F, L/O report of contractor truck contact with lines at pole 742753. ( see CAC 22027 ) Isolations between normal open point ABS 350 & ABS 344 with recloser 6610 returned to service lines x 2 repaired all service restored. Materials 10 meters conductor, 15 x H/V sleeves NDR to follow See safety manager No 738738 | F3 | WAITARA RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.035194 | 11 | 2017 | 2017-03-07 | C | 257 | 0.035194 | 0.00076992
1 | 16159807 | 2017-03-07 10:09 | 2017-03-07 10:12 | 2 | 654 | 1885.7 | 0.0056492 | 0 | 0.0019593 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | W0024 | RECLOSER (HV) | at 10:09, Whitianga Sub, CB 2 Cook Drive Feeder, Recloser 9519, Tripped, No Flags, L/O. This tripping happened when Comms tech was trying to upgrade the firmware to the recloser. Believe the protection settings became corrupted during the firmware update and caused recloser to trip. Comms tech advised NOC Control promptly. Backfeed supplied via SCADA from WHT 2: Closed Sectionaliser 9847. All Power Restored at 10:11. Safety Manager No: 738707 | F3 | COOK DRIVE | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2017-03-07 | C | 654 | 0 | 0.0019593
1 | 16161411 | 2017-03-28 10:00 | 2017-03-28 14:10 | 250 | 3 | 255 | 0.00076368 | 0.000736 | 1.7969e-05 | NAPA ID:29478 TP_TE MATAI GXP > PONGAKAWA SUB | 11 | Planned | 029478 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS SE7-025 | NONE | Replace HV arms at ABS SE7-025. Cant be done live line due to safety. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000368 | 5.5 | 2017 | 2017-03-28 | B | 3 | 0.000736 | 1.7969e-05
1 | 16161748 | 2017-03-14 08:37 | 2017-03-14 16:32 | 475 | 47 | 22325 | 0.066874 | 0.066451 | 0.00014079 | NAPA ID:29636 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | 029636 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | 1: Change 11/33kv poles between 829153 & 852031. 2: Change 11kV ABS S118 to 11kV Fuses. 3: Create 11kV Span break Between poles 827251, 827249 and 853636. 4: Create 11kV Span break between poles 827243 & 827242. 5: Connect new 11kV Underbuilt between poles 853636 & new pole between poles 827241 & 827242. 6: Install new 11kV ABS 1111 on pole 829153 but not connected to network. (Will be connected at a later date). 7: Transfer 11kV TX T1412 across the road to new line. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.033225 | 5.5 | 2017 | 2017-03-14 | B | 47 | 0.066451 | 0.00014079
1 | 16161770 | 2017-03-07 15:37 | 2017-03-07 19:05 | 207 | 75 | 8471.1333 | 0.025378 | 0.024703 | 0.00022469 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 853111 | CONDUCTOR - REPAIR/REHANG | Recloser 7417 L/O on O/C & E/F. sectionalised and found floating wire beyound fuses 8135 which is a private line. isolated at fuses & repaired floating wire | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.024703 | 11 | 2017 | 2017-03-07 | C | 75 | 0.024703 | 0.00022469
1 | 16163709 | 2017-03-07 18:50 | 2017-03-07 21:55 | 185 | 46 | 3332.1667 | 0.0099826 | 0.009569 | 0.00013781 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2213T | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | 2 x HV fuses found blown on transformer 2213T. One of the fuse bases was very insecure on crossarm to reload. Line isolated between ABS 6111 & 5961 to resecure base to crossarm (bolts required tightning) and reload fuses. All supply restored. Blown fuses replaced were 2 x 2 amp | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.009569 | 11 | 2017 | 2017-03-07 | C | 46 | 0.009569 | 0.00013781
1 | 16164286 | 2017-03-07 23:15 | 2017-03-07 23:52 | 36 | 38 | 1394.6 | 0.004178 | 0.003836 | 0.00011384 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714811 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Report of arcing from member of public was caused by tracking from a faulty HV fuses base on pole 714811. Line isolated at ABS TA869, TA876 & 6751 to replace. All supply restored following repairs. 1 x HV fuse base and 1 x 6 amp fuse materials required. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.003836 | 11 | 2017 | 2017-03-07 | C | 38 | 0.003836 | 0.00011384
1 | 16164641 | 2017-03-08 00:50 | 2017-03-10 15:15 | 3744 | 199 | 192321.3333 | 0.57615 | 0.57436 | 0.00059616 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | R0939 | POLE | RC 28 L/O on O/C touched base with Steve Mckinney 0830 no access to site slips and flooding. Police advised Hub at 0633 that faultmen were unable to access the site to make repairs due to safety concerns. 8 & 15 Wahitpu lane line down 021 292 0713 , Scott Smith 12:10PM - Tree has fallen on the lines, bringing the lines down across the road and neighbours cannot get out of their property and have no power. - 15 WAHITAPU LANE - OPOUTERE Pole found down past Fuses FC2421. Fault Isolated and feeder restored. Will have to wait for better weather to replace pole. Pole replaced and lines repaired. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.57436 | 11 | 2017 | 2017-03-08 | C | 199 | 0.57436 | 0.00059616
1 | 16165398 | 2017-03-08 03:39 | 2017-03-08 05:38 | 119 | 6064 | 696822.2 | 2.0875 | 2.033 | 0.018166 |  | 33 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | WHI-WGM 178 | CONDUCTOR - REPAIR/REHANG | CB 40 at Waihi L/O on O/C & E/F Found slip had brought down a larch tree that brushed the 33kV & 11kV line. Cleared tree and relivened Whangamata Sub | S5 | WAIHI-WHANGAMATA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 2.033 | 33 | 2017 | 2017-03-08 | C | 6064 | 2.033 | 0.018166
1 | 16171483 | 2017-03-08 04:57 | 2017-03-08 08:45 | 228 | 3 | 685.35 | 0.0020532 | 0.002026 | 8.9873e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | N13023 | FUSE - ELEMENT/LINK (HV) | 3 x 2A HV Fuses Replaced at Transformer TC4879 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.002026 | 11 | 2017 | 2017-03-08 | C | 3 | 0.002026 | 8.9873e-06
1 | 16171497 | 2017-03-08 07:41 | 2017-03-08 08:43 | 62 | 33 | 2046 | 0.0061293 | 0.005832 | 9.886e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 215086 | CONDUCTOR - REPAIR/REHANG | Trees touching lines between Pole 215086 and 215087. Lines isolated at Fuse Switch 9579/4 and trees cut back. 2 x 25A HV Fuses replaced | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.005832 | 11 | 2017 | 2017-03-08 | C | 33 | 0.005832 | 9.886e-05
1 | 16173053 | 2017-03-08 06:11 | 2017-03-08 07:24 | 72 | 941 | 68300.9167 | 0.20461 | 0.19616 | 0.002819 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 393248 | CONDUCTOR - REPAIR/REHANG | Trip caused by tree branches falling through lines at Pole 393248. Relivened OK | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.19616 | 11 | 2017 | 2017-03-08 | C | 941 | 0.19616 | 0.002819
1 | 16174602 | 2017-03-08 06:31 | 2017-03-08 08:16 | 104 | 7 | 734.1833 | 0.0021994 | 0.002136 | 2.097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | d1499 | FUSE - ELEMENT/LINK (HV) | 2 x 8amp @fp116 08:16 windy | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.002136 | 11 | 2017 | 2017-03-08 | C | 7 | 0.002136 | 2.097e-05
1 | 16174646 | 2017-03-08 06:39 | 2017-03-08 07:35 | 56 | 3 | 168.05 | 0.00050344 | 0.000476 | 8.9873e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810198 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | 2 x 3amp @ 1294 possum @0735 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.000476 | 11 | 2017 | 2017-03-08 | C | 3 | 0.000476 | 8.9873e-06
1 | 16174786 | 2017-03-08 07:21 | 2017-03-08 11:45 | 264 | 537 | 109271.1167 | 0.32735 | 0.32252 | 0.0044937 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | U0205 | CONDUCTOR - REPAIR/REHANG | NCTL to SMC 0758: Query acknowledgement of job, status to be changed, has been issued to Steve Johnson. However Steve advised SMC that the roads to this location are closed, no access, no eta. Trees found brushing the lines in the high wind between Pole U0205 and U0206. Branches cut away from lines and feeder restored. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.32252 | 11 | 2017 | 2017-03-08 | C | 537 | 0.32252 | 0.0044937
1 | 16175541 | 2017-03-08 07:36 | 2017-03-08 09:08 | 91 | 71 | 2974 | 0.0089094 | 0.008271 | 0.0002127 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | T3/521 | CABLE - REPLACE LESS THAN 5 METRES | Heard from Steve Easthope from Manfield Park Trust 0274 433 047 has advised that a worker has post hole borer drilled straight through an UG HV cable. Worker has not received a shock at all. Emergency service have not been called. Steve's team have cordoned off the area as per hazard process of keeping minimum distance of 10M. Have done hazard process with person on site. Address given for incident is 59 South Street, Feilding. ***Please enter into safety manager*** NDR 51256 Cable DNO 170312 To be repaired under planned works | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.008271 | 11 | 2017 | 2017-03-08 | C | 71 | 0.008271 | 0.0002127
1 | 16175928 | 2017-03-29 08:30 | 2017-03-29 09:05 | 35 | 34 | 1190 | 0.0035638 | 0.003258 | 0.00010182 | NAPA ID:28342 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 028342 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2074 | NONE | Replace switchgear IC2074, IC2076 and LC840 with new Siemens 8DJH RRT switch unit. 1: Create Bushings to Bus break and Connect LV generator to TC840. 2: Replace RMU. 3: Disconnect generator and close Bushing to Bus break. | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.001629 | 5.5 | 2017 | 2017-03-29 | B | 34 | 0.003258 | 0.00010182
1 | 16176222 | 2017-03-08 08:07 | 2017-03-08 10:46 | 159 | 153 | 14357.1167 | 0.043011 | 0.041635 | 0.00045835 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 711682 | CONDUCTOR - REPAIR/REHANG | NG4 tripped A Ph O/C, E/F, L/O. Tree through 1 x line at pole 711682 Isolation at fuses NG404 ( spur no back feed ) Rest of feeder returned to service tree cut away, all service restored Materials 10 meters conductor, 2 x sleeves, 3 x 15A H/V fuses NDR to follow | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.041635 | 11 | 2017 | 2017-03-08 | C | 153 | 0.041635 | 0.00045835
1 | 16179467 | 2017-03-08 10:38 | 2017-03-08 17:00 | 382 | 8 | 3056 | 0.0091551 | 0.009083 | 2.3966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V75 | INSULATOR | Urgent faultman to site broken insulator during planned works under NAPA 28114 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.009083 | 11 | 2017 | 2017-03-08 | C | 8 | 0.009083 | 2.3966e-05
1 | 16179496 | 2017-03-08 09:31 | 2017-03-10 15:15 | 3224 | 27 | 17925.9667 | 0.053702 | 0.053459 | 8.0886e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 267382 | CONDUCTOR - REPAIR/REHANG | Trees removed supply restored | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.053459 | 11 | 2017 | 2017-03-08 | C | 27 | 0.053459 | 8.0886e-05
1 | 16179518 | 2017-03-08 09:39 | 2017-03-08 10:35 | 55 | 19 | 1055.1333 | 0.0031609 | 0.00299 | 5.692e-05 | Wind | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 220233 | FUSE - ELEMENT/LINK (HV) | Reload at SD5-130 2 x 15A Fuse Wind | F4 | BRUCE RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.00299 | 11 | 2017 | 2017-03-08 | C | 19 | 0.00299 | 5.692e-05
1 | 16181045 | 2017-03-08 10:01 | 2017-03-08 19:01 | 540 | 555 | 85370.7167 | 0.25575 | 0.25076 | 0.0016627 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | O048 | POLE | Check for safety - Car vs Pole,lines down over vehicle and victim trapped inside. ETA required please Jane has spoken to someone Victoria (0275 018 315) onsite and advised of hazard process Called and emailed SMC advised Control ETA 10mins Advised Fire Service of ETA NDR 585054 Jay Edwards 3 Rata St Kerepehi Police event no PO28760043 CB 1 opened due to above reports | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.25076 | 11 | 2017 | 2017-03-08 | C | 555 | 0.25076 | 0.0016627
1 | 16182098 | 2017-03-09 06:59 | 2017-03-09 08:08 | 69 | 52 | 3588 | 0.010749 | 0.010281 | 0.00015578 | NAPA ID:29648 TP_HINUERA GXP > BROWNE STREET SUB > TAINUI ST | 11 | Planned | 029648 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | SWITCHING RE-WRITE FOR NAPA 28225. Replacement of Reyrolle and GEC Switches IC1518 (13180/3), IC1503 (13180/1) and TC4486 (13180/2) with Siemens 8DJH TRR Unit. | F3 | TAINUI ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0051405 | 5.5 | 2017 | 2017-03-09 | B | 52 | 0.010281 | 0.00015578
1 | 16182440 | 2017-03-08 10:37 | 2017-03-08 13:10 | 153 | 845 | 75666.0167 | 0.22668 | 0.21908 | 0.00352 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | C2854 | CIRCUIT BREAKER (HV) | MIK 6 tripped A, B & C Ph O/C, L/O feeder sectionalised with no fault found high wind at time of tripping & suspect line clash over river crossing ( poles C2854 - C3494 ) MIK 6 partial offloaded to MIK 1 to mitigate further tripping until resolved. ABS 2618 unable to be opened DNO 170205 DNO 1703132 | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.21908 | 11 | 2017 | 2017-03-08 | C | 845 | 0.21908 | 0.00352
1 | 16183595 | 2017-03-08 10:42 | 2017-03-08 12:13 | 90 | 8 | 726.5333 | 0.0021765 | 0.002104 | 2.3966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 317173 | FUSE - ELEMENT/LINK (HV) | Check 501 KAITEMAKO ROAD, OMS 16185147 is related. 2 x 8A HV Fuses Replaced | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.002104 | 11 | 2017 | 2017-03-08 | C | 8 | 0.002104 | 2.3966e-05
1 | 16183921 | 2017-03-08 11:01 | 2017-03-08 13:40 | 158 | 1 | 158.65 | 0.00047528 | 0.000466 | 2.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13644 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses FC2718 2 x 10A Wind | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000466 | 11 | 2017 | 2017-03-08 | C | 1 | 0.000466 | 2.9957e-06
1 | 16184001 | 2017-03-08 11:06 | 2017-03-08 12:32 | 86 | 927 | 77492.7167 | 0.23215 | 0.22382 | 0.0027771 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T1069 | CONDUCTOR - REPAIR/REHANG | CB 4 Trip to L/O Feeder sectionalised tree branch found on lines at Pole T1069. Removed with Hot Stick | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.22382 | 11 | 2017 | 2017-03-08 | C | 927 | 0.22382 | 0.0027771
1 | 16185834 | 2017-03-08 11:51 | 2017-03-08 16:07 | 255 | 114 | 16536.2 | 0.049539 | 0.048514 | 0.00061114 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 371191 | CONDUCTOR - REPAIR/REHANG | Lines down at pole 371191 caused by trees NDR 56361 Repairs used 8M Conductor 6 x Sleeves 1 x 10A Fuse | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.048514 | 11 | 2017 | 2017-03-08 | C | 114 | 0.048514 | 0.00061114
1 | 16186248 | 2017-03-08 13:13 | 2017-03-08 13:37 | 24 | 5 | 120 | 0.00035949 | 0.000314 | 1.4979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 716434 | CONDUCTOR - REPAIR/REHANG | Using nearest ICP - lines down at approx 700 Oeo Road LV Lines down repaired using 4 m Conductor 2 x LV Sleeves 1 x Binder 1 x Insulator Transformer T7375 Off 13:13 On 13:37 for LV Repairs | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000314 | 11 | 2017 | 2017-03-08 | C | 5 | 0.000314 | 1.4979e-05
1 | 16186263 | 2017-03-08 11:57 | 2017-03-08 12:26 | 28 | 1048 | 16031.75 | 0.048027 | 0.038608 | 0.0031396 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P39977 | POLE | Car V pole, lines down. Occupant trapped in vehicle. ETA required. advised Control called and emailed SMC. ETA as advised by HUB 15 minutes, Fire Service Advised. Transformer T4/14 Offline LV Pole P39977 and LV Road Crossing to be repaired. T4/14 Anjay has arranged extra persons to help with pole repair. Suspects LV will be off until approximately 3pm. LV Emergency outage posted at 1pm. Require Time T4/14 was restored and Gear used for repairs Anjay leaving site 2.11pm - Dave Whale and line cres on site to complete work. 10.30pm confirmation from Lianne at SMC FM is no longer on site - have e-Text and phoned asking for him to call and close job. Replaced a 9.5 bus pole. Finished at 4.30pm. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.038608 | 11 | 2017 | 2017-03-08 | C | 1048 | 0.038608 | 0.0031396
1 | 16186300 | 2017-03-08 12:03 | 2017-03-08 17:56 | 353 | 6 | 653.9667 | 0.0019591 | 0.001905 | 5.9915e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1642 | CROSSARM - WHOLE ASSEMBLY | Crossarm Replaced at Pole N1642 30 M Conductor | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.001905 | 11 | 2017 | 2017-03-08 | C | 6 | 0.001905 | 5.9915e-06
1 | 16188330 | 2017-03-08 18:20 | 2017-03-08 19:25 | 65 | 44 | 2860 | 0.0085679 | 0.008172 | 0.00013181 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1265 | JUMPER | ( NGA 4 ) emergency switching to replace/repair burnt jumper at transformer N1265 Isolations between normal open ABS,s NG248 & NG479 & ABS NG426. jumper repaired all service restored | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.008172 | 11 | 2017 | 2017-03-08 | C | 44 | 0.008172 | 0.00013181
1 | 16188368 | 2017-03-20 09:08 | 2017-03-20 15:30 | 382 | 104 | 39728 | 0.11899 | 0.11806 | 0.0003115 | NAPA ID:29669 TP_KOPU GXP | 11 | Planned | 029669 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 333622 | NONE | Change 66kV and 11kV pole and X-arm at pole 333622, KPUCGN019, 020, 023, 024 and S12985. | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.059029 | 5.5 | 2017 | 2017-03-20 | B | 104 | 0.11806 | 0.0003115
1 | 16188768 | 2017-03-08 14:16 | 2017-03-08 14:53 | 37 | 9 | 340.2 | 0.0010192 | 0.000938 | 2.6962e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C645 | CROSSARM - ARM ONLY | ( MIK 4 ) Emergency switching to replace king bolt at pole C645 Isolation at fuses FP1608 ( spur no back feed ) King bolt replaced all service restored | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000938 | 11 | 2017 | 2017-03-08 | C | 9 | 0.000938 | 2.6962e-05
1 | 16189074 | 2017-03-28 09:15 | 2017-03-28 15:31 | 376 | 9 | 3384 | 0.010134 | 0.010053 | 2.6953e-05 | NAPA ID:29654 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | 029654 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 827215 | NONE | Change 11kv poles and cross arms Watsons Rd Install new 11kv fuses 11112 @ pole 827215 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.0050265 | 5.5 | 2017 | 2017-03-28 | B | 9 | 0.010053 | 2.6953e-05
1 | 16189163 | 2017-03-08 14:05 | 2017-03-08 15:42 | 97 | 5 | 486.0833 | 0.0014562 | 0.001411 | 1.4979e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 718259 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses MA110 2 x 8A Fuses Trees NDR N100332 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001411 | 11 | 2017 | 2017-03-08 | C | 5 | 0.001411 | 1.4979e-05
1 | 16189634 | 2017-03-08 15:26 | 2017-03-08 16:00 | 34 | 86 | 2924 | 0.0087596 | 0.007986 | 0.00025764 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | P03343 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fused ABS H106 - Cause Used 2 x 15A Patrolled Cause Unknown | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.007986 | 11 | 2017 | 2017-03-08 | C | 86 | 0.007986 | 0.00025764
1 | 16190248 | 2017-03-08 14:38 | 2017-03-08 19:05 | 267 | 537 | 108097.4667 | 0.32384 | 0.31901 | 0.0016087 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | u0207 | CONDUCTOR - REPAIR/REHANG | Lines down half way up Paku Hill Tairau, Matt Hishon 021 767 995 rec 9848 trip o/c found tree through lines at pole u0207 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.31901 | 11 | 2017 | 2017-03-08 | C | 537 | 0.31901 | 0.0016087
1 | 16191164 | 2017-03-30 08:00 | 2017-03-30 10:21 | 141 | 129 | 16341 | 0.048937 | 0.047778 | 0.00038632 | NAPA ID:29679 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 13TH AVE | 11 | Planned | 029679 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SK6-001 | NONE | Replace Magnefix SK6-001, SK6-003 with CFCF 9826 | F3 | 13TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.023889 | 5.5 | 2017 | 2017-03-30 | B | 129 | 0.047778 | 0.00038632
1 | 16191196 | 2017-03-08 14:54 | 2017-03-08 19:20 | 266 | 10 | 2660 | 0.0079687 | 0.007878 | 2.9958e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD5-073 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 14:54, Te Maunga Sub, CB 5 Bruce Rd Feeder. Faultman found transformer TD5-073 had blown. Own Isolation & Access Permit to Replace Transformer. All Power Restored on Completion. 1x Transformer & 6x 5A HV Fuses Replaced. Jackson Achilles Attended. Emailed NI as incorrect tx feed for this ICP. | F4 | BRUCE RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.007878 | 11 | 2017 | 2017-03-08 | C | 10 | 0.007878 | 2.9958e-05
1 | 16191282 | 2017-03-08 15:02 | 2017-03-08 21:12 | 369 | 2 | 739.1667 | 0.0022144 | 0.002196 | 5.9915e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2524 | FUSE - ELEMENT/LINK (HV) | 2 x 3 amp fuses replaced at 2524. Suspected to be caused by conductor clash in wind | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002196 | 11 | 2017 | 2017-03-08 | C | 2 | 0.002196 | 5.9915e-06
1 | 16191482 | 2017-03-08 15:24 | 2017-03-08 17:46 | 142 | 98 | 11457.85 | 0.034325 | 0.033444 | 0.00029359 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | O1678 | CONDUCTOR - REPAIR/REHANG | rec 9464 Trip Debri found on lines at Poles O1678, O1679 & O1680 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.033444 | 11 | 2017 | 2017-03-08 | C | 98 | 0.033444 | 0.00029359
1 | 16193071 | 2017-03-08 14:10 | 2017-03-08 20:16 | 365 | 147 | 50620.6667 | 0.15165 | 0.15033 | 0.0004943 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P00409 | CONDUCTOR - REPAIR/REHANG | NEED TO LINK 16191310 Twisted lines outside TX T3/486 - 1786 Makino Road , Halcombe will also need repairing before you liven (These twisted wires turned out to be unrelated) Recloser M81 tripped to L/O. Tree through line located between poles P00409 & P19324. Isolations at ABS M55 & M57 for repairs. Back feed not established to ABS M57 for duration of outage due to resourses. NDR 300300. Materials required - 20 metres squirell conductor, 12 squirell sleeves, 10 metres 25mm Cu conductor for LV, 1 x LV pin & ins All supply restored following repairs. Job not closed. Safety manager entry required? Refer to Andrew W | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.15033 | 11 | 2017 | 2017-03-08 | C | 147 | 0.15033 | 0.0004943
1 | 16193198 | 2017-03-08 11:30 | 2017-03-08 17:20 | 350 | 7 | 2452.5667 | 0.0073473 | 0.007284 | 2.097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4048 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, ALL PHASES | Isolate at Transformer X4048 HV Fuses to replace LV conductor Replace 20m 16mm conductor, 2 x 100A HRC fuses NDR N200090 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.007284 | 11 | 2017 | 2017-03-08 | C | 7 | 0.007284 | 2.097e-05
1 | 16193813 | 2017-03-08 16:29 | 2017-03-09 14:20 | 1311 | 1 | 1311.3167 | 0.0039284 | 0.003919 | 2.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1423 | FUSE - ELEMENT/LINK (HV) | 2 x 10 A HV Fuses replaced. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003919 | 11 | 2017 | 2017-03-08 | C | 1 | 0.003919 | 2.9957e-06
1 | 16194963 | 2017-03-08 16:47 | 2017-03-08 17:22 | 35 | 891 | 1693.7667 | 0.0050741 | 0 | 0.00014679 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | V1197 | CONDUCTOR - REPAIR/REHANG | Tree branch found on lines at Pole V1197 Recloser RP19 would not close via SCADA or on Local. Bypass closed over the top if recloser. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2017-03-08 | C | 891 | 0 | 0.00014679
1 | 16196811 | 2017-03-08 22:40 | 2017-03-08 23:05 | 25 | 2 | 50 | 0.00014979 | 0.000131 | 5.9915e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4224 | JUMPER | at 22:40, Tower Rd Sub, CB 3 Te Poi Feeder. Faultman found blown jumper at Transformer TC4224. Own Isolation & AP to repair broken jumper. All Power Restored on Completion. Mike Cornelius Attended. 2x 80A HRC Fuses & 1x 3A HV Fuse Replaced. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000131 | 11 | 2017 | 2017-03-08 | C | 2 | 0.000131 | 5.9915e-06
1 | 16196815 | 2017-03-08 18:12 | 2017-03-09 10:46 | 994 | 891 | 83931.3667 | 0.25144 | 0.24343 | 0.0020611 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1449 | CONDUCTOR - REPAIR/REHANG | at 18:12, Coromandel Sub, CB 5 Manaia Feeder, Sectionaliser 9839, Tripped, No Flags, L/O. Faultmen dispatched & investigation began. Report of Lines down on Tapu Creek Farm. Isolated lines at ABS IC359. Permit issued to create temp line break to isolate lines down (Transformer TC5530 affected). Power restored to remainder of feeder. Repairs still required to lines down on Tapu Creek Farm Repairs carried out Replaced 1 span x 2 conductors at Pole T1449 to Transformer TC5530 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.24343 | 11 | 2017 | 2017-03-08 | C | 891 | 0.24343 | 0.0020611
1 | 16197638 | 2017-03-08 15:22 | 2017-03-08 20:28 | 306 | 15 | 3930 | 0.011773 | 0.011638 | 4.4936e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q0278 | CONDUCTOR - REPAIR/REHANG | check OMS 16193970 - 110 FERGUS ROAD part power is related as well Line pulled back up. 30/3/2017: Crew assignment times (1R Only) have been amended to reflect the Crew Transition reflected in the original OMS job 16191455 (Cancelled and Merged to this OMS Number) for KPI Reporting Purposes. (axk). | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.011638 | 11 | 2017 | 2017-03-08 | C | 15 | 0.011638 | 4.4936e-05
1 | 16198038 | 2017-03-08 20:30 | 2017-03-08 22:15 | 105 | 7 | 737.45 | 0.0022092 | 0.002146 | 2.097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4982 | FUSE - ELEMENT/LINK (HV) | 2 x 6 amp HV fuses replaced at fuses 4982. Probable conductor clash in wind. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.002146 | 11 | 2017 | 2017-03-08 | C | 7 | 0.002146 | 2.097e-05
1 | 16198621 | 2017-03-08 22:38 | 2017-03-09 09:20 | 642 | 7 | 4494.4667 | 0.013464 | 0.013401 | 2.097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D1499 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp @FP116 wind trees 09:20 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.013401 | 11 | 2017 | 2017-03-08 | C | 7 | 0.013401 | 2.097e-05
1 | 16199576 | 2017-03-08 23:39 | 2017-03-08 23:58 | 18 | 894 | 16539 | 0.049547 | 0.041512 | 0.0026782 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7 | UNKNOWN | at 23:39, Coromandel Sub, CB 7 Kapanga Rd Feeder, Tripped, Ph A + B O/C, L/O. Faultmen dispatched. Manual Reclose Attempt tried after 18 minutes and CB held in. Cursory Patrol Carried out by faultmen, nothing found. Shane Walker Attended. | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.041512 | 11 | 2017 | 2017-03-08 | C | 894 | 0.041512 | 0.0026782
1 | 16203689 | 2017-03-09 04:11 | 2017-03-09 05:55 | 103 | 440 | 25821.5 | 0.077354 | 0.073399 | 0.0013181 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 9 tripped to L/O. E/F & B Ph O/C flags Line sectionalised & patrolled. No apparent fault found. All supply restored. | F2 | OHAKEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.073399 | 11 | 2017 | 2017-03-09 | C | 440 | 0.073399 | 0.0013181
1 | 16206623 | 2017-03-09 04:29 | 2017-03-09 08:30 | 241 | 666 | 59510.3667 | 0.17828 | 0.17229 | 0.0023816 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser 10303 tripped to L/O | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.17229 | 11 | 2017 | 2017-03-09 | C | 666 | 0.17229 | 0.0023816
1 | 16207446 | 2017-03-09 05:01 | 2017-03-09 10:35 | 333 | 4 | 1335.2667 | 0.0040001 | 0.003964 | 1.1983e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 392329 | FUSE - ELEMENT/LINK (HV) | 2 x3amp wind 10:35 @ tc1053 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.003964 | 11 | 2017 | 2017-03-09 | C | 4 | 0.003964 | 1.1983e-05
1 | 16207457 | 2017-03-09 05:22 | 2017-03-09 05:42 | 19 | 894 | 17269.1 | 0.051733 | 0.043698 | 0.0026782 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 7 | UNKNOWN | at 05:22, Coromandel Sub, CB 7 Kapanga Rd Feeder, Tripped, Ph A O/C, L/O. Faultmen dispatched. Manual reclose tried after 19 minutes and held in. Fautlman believes that cause may be tree debris hitting the lines at lots of trees in the area and very high winds at time of tripping - cannot confirm this though. Shane Walker Attended | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.043698 | 11 | 2017 | 2017-03-09 | C | 894 | 0.043698 | 0.0026782
1 | 16208512 | 2017-03-09 08:49 | 2017-03-09 10:55 | 126 | 3 | 378 | 0.0011324 | 0.001105 | 8.9871e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T8/263 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found transformer T8/263 to be faulty, transformer was isolated and replaced. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001105 | 11 | 2017 | 2017-03-09 | C | 3 | 0.001105 | 8.9871e-06
1 | 16208532 | 2017-03-09 07:41 | 2017-03-09 10:13 | 152 | 43 | 6536 | 0.01958 | 0.019193 | 0.00012882 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21338 | JOINT - CONDUCTOR JOINT | Faultman found line down at pole P21338 caused by a failed amps clamp, line was isolated at Fuses L43 to make the repairs. 10 meters Squirell conductor replaced 2 X sleeves 2 x amps clamps | F2 | OHAKEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.019193 | 11 | 2017 | 2017-03-09 | C | 43 | 0.019193 | 0.00012882
1 | 16208893 | 2017-03-09 07:39 | 2017-03-09 11:10 | 211 | 15 | 2893.5 | 0.0086681 | 0.008533 | 4.4936e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12761 | BINDER | Floating conductor at pole V12761. Conductor reb Rec 9929 tripped no flags | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.008533 | 11 | 2017 | 2017-03-09 | C | 15 | 0.008533 | 4.4936e-05
1 | 16210077 | 2017-03-09 08:36 | 2017-03-09 11:20 | 163 | 1 | 163.65 | 0.00049025 | 0.000481 | 2.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | c13644 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | 2x10 @fc 2718 and barrell WIND 11:20 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000481 | 11 | 2017 | 2017-03-09 | C | 1 | 0.000481 | 2.9957e-06
1 | 16210145 | 2017-03-09 08:45 | 2017-03-09 10:29 | 103 | 2 | 207.2333 | 0.00062081 | 0.000602 | 5.9914e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1258 | FUSE - ELEMENT/LINK (HV) | Owner of property has gone out to see if she can find the fault. Have advised SMC. 2 x 2A HV Fuses replaced | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000602 | 11 | 2017 | 2017-03-09 | C | 2 | 0.000602 | 5.9914e-06
1 | 16210782 | 2017-03-09 09:40 | 2017-03-09 13:15 | 215 | 3 | 645.9 | 0.0019349 | 0.001907 | 8.9871e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1641 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses and 1 Fuse Barrel replaced. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.001907 | 11 | 2017 | 2017-03-09 | C | 3 | 0.001907 | 8.9871e-06
1 | 16211184 | 2017-03-09 10:08 | 2017-03-09 11:51 | 102 | 98 | 5969.85 | 0.017884 | 0.017003 | 0.00036248 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H0717 | BINDER | Recloser RC25 Tripped B ph O/C E/F Floating conductor found at Pole H0701 during sectionlising Isolaeted at Fuses FP1355 Used 1 x binder | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.017003 | 11 | 2017 | 2017-03-09 | C | 98 | 0.017003 | 0.00036248
1 | 16212245 | 2017-03-09 11:26 | 2017-03-09 12:47 | 80 | 86 | 6941.6333 | 0.020795 | 0.020022 | 0.00025763 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03343 | FUSE - ELEMENT/LINK (HV) | 2 x 15A fuses fitted to Fused ABS H106. Chris has no 20A fuses on board so will have to return later in the day to replace again. Asked Chris to patrol the lines past H106 to check that all fuses in and holding. Left in Test Mode to stop another job being created when the ABS is opened again. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.020022 | 11 | 2017 | 2017-03-09 | C | 86 | 0.020022 | 0.00025763
1 | 16212791 | 2017-03-30 09:45 | 2017-03-30 14:25 | 280 | 22 | 1012 | 0.0030307 | 0.002833 | 0.00013177 | NAPA ID:29482 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 029482 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE7-005 | NONE | Replace HV X-arms below ABS SE7-005. Cannot be done live line due to safety. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.0014165 | 5.5 | 2017 | 2017-03-30 | B | 22 | 0.002833 | 0.00013177
1 | 16216101 | 2017-03-09 07:35 | 2017-03-09 15:58 | 502 | 11 | 5525.6667 | 0.016553 | 0.016454 | 3.2953e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13184 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | replace Tx 1x50kva tx and 2x6amp fuses | F2/F4 | LOVEGROVE RD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.016454 | 11 | 2017 | 2017-03-09 | C | 11 | 0.016454 | 3.2953e-05
1 | 16216152 | 2017-03-09 14:15 | 2017-03-09 16:52 | 157 | 8 | 1258.1333 | 0.003769 | 0.003697 | 2.3966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5905 | FUSE - ELEMENT/LINK (HV) | called through to SMC 2 x 6A HV Fuses 2 x 100A LV Fuses 1 x LV Pin Insulator 1 x Binder | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003697 | 11 | 2017 | 2017-03-09 | C | 8 | 0.003697 | 2.3966e-05
1 | 16216647 | 2017-03-09 12:00 | 2017-03-09 15:42 | 222 | 11 | 2442 | 0.0073155 | 0.007216 | 3.2953e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q0278 | CONDUCTOR - REPAIR/REHANG | Removal of generator after line break installed under OMS 16197638 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.007216 | 11 | 2017 | 2017-03-09 | C | 11 | 0.007216 | 3.2953e-05
1 | 16216847 | 2017-03-09 16:09 | 2017-03-09 16:39 | 29 | 1 | 29.8667 | 8.9472e-05 | 8e-05 | 2.9957e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | - | UNKNOWN | Full power on arrival - was part of OMS 16212245. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 8e-05 | 11 | 2017 | 2017-03-09 | C | 1 | 8e-05 | 2.9957e-06
1 | 16217050 | 2017-03-09 19:09 | 2017-03-10 01:31 | 382 | 7 | 2674 | 0.0080105 | 0.007947 | 2.097e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P32242 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer T1/240 Faulty. Fuses at C27 Upgraded to 6 amp. Transformer Fuses are reloaded with 3amp. 1x30/3/11kV transformer replaced 3xHV fuses complete replaced 3x3amp , 3x6 amp fuse elements | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.007947 | 11 | 2017 | 2017-03-09 | C | 7 | 0.007947 | 2.097e-05
1 | 16217448 | 2017-03-09 18:29 | 2017-03-09 20:45 | 135 | 2 | 271.2667 | 0.00081264 | 0.000794 | 5.9914e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC527 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 2A HV Fuses at Transformer TC527. Bad weather in the area at the time. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000794 | 11 | 2017 | 2017-03-09 | C | 2 | 0.000794 | 5.9914e-06
1 | 16217951 | 2017-03-09 22:16 | 2017-03-10 01:20 | 183 | 86 | 15815.4 | 0.047378 | 0.046605 | 0.00025763 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03343 | FUSE - ELEMENT/LINK (HV) | 2 fuses blown at H106. FABS opened Fuses replaced with 25amp fuse elements. FABS H106 Closed. line patrolled. Needs to have an operational Line patrol to see if lines are clashing 2r line patrol not done as requested cancelled at 1400 as still at acknowleged | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.046605 | 11 | 2017 | 2017-03-09 | C | 86 | 0.046605 | 0.00025763
1 | 16219233 | 2017-03-10 01:07 | 2017-03-10 06:27 | 320 | 325 | 43847.2167 | 0.13135 | 0.12843 | 0.00097359 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P26757 | CONDUCTOR - REPAIR/REHANG | Recloser 10227 Opened due to report of lines still arching & causing a fire. A/R earlier in the evening. Isolated at ABS B18, 10194, B21. Back feed from ABS B23. Branch accoss the line at pole downed Line repaired, relivened NDR to Follow Materials 40m squirrel conducter 5 full tension sleeves | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.12843 | 11 | 2017 | 2017-03-10 | C | 325 | 0.12843 | 0.00097359
1 | 16220396 | 2017-03-10 05:45 | 2017-03-10 05:50 | 5 | 50 | 250 | 0.00074892 | 0.000299 | 0.00014978 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738500 | FUSE - ELEMENT/LINK (HV) | 2x8 amp fuses blown at 6130, abs 6167 open fuses 6130 replaced ABS 6167 closed. Possibly birds. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000299 | 11 | 2017 | 2017-03-10 | C | 50 | 0.000299 | 0.00014978
1 | 16220626 | 2017-03-10 07:40 | 2017-03-10 09:48 | 128 | 739 | 71647.9167 | 0.21463 | 0.20799 | 0.0026572 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 337856 | CONDUCTOR - REPAIR/REHANG | Recloser 9226/2 tripped to L/O. No flags but CB 3 E/F & O/C flags picked up at Whitianag sub. Line sectionalised & patrolled. Tree branch removd from line at pole 337856 with a hot stick. Some visible burn damage to insulator on ABS 9742/1 caused by this will be defected by Downers for repair/replacement. There was a delay is restoring backfeed from GMSG 9495/1 as this switch could not be operated via SCADA. There is a note attached to switch stating there is known problem with control of this switch (DNO 170106) this DNO has been signed off as completed but switch still not operational vai SCADA. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.20799 | 11 | 2017 | 2017-03-10 | C | 739 | 0.20799 | 0.0026572
1 | 16222022 | 2017-03-10 08:04 | 2017-03-10 14:38 | 394 | 2 | 788.4 | 0.0023618 | 0.002343 | 5.9913e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2670 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | stu has driven past this morning and found 2 HV fuses hanging out, Has inspected Transformer and confirmed that it's blown and needs replacing replaced tx checked and tested all ok 15kva tx relivened 1435 lihghtening | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.002343 | 11 | 2017 | 2017-03-10 | C | 2 | 0.002343 | 5.9913e-06
1 | 16222853 | 2017-03-30 09:01 | 2017-03-30 15:00 | 359 | 29 | 10420.1833 | 0.031206 | 0.030945 | 8.6847e-05 | NAPA ID:28227 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 028227 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6003 | NONE | Replace-straighten poles, crossarms and hardware. Re level ground mount transformer TC6003 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.015473 | 5.5 | 2017 | 2017-03-30 | B | 29 | 0.030945 | 8.6847e-05
1 | 16224353 | 2017-03-10 15:19 | 2017-03-10 18:18 | 178 | 1 | 178.8667 | 0.00053583 | 0.000526 | 2.9956e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4881 | FUSE - ELEMENT/LINK (HV) | 2 x 6 amp HV fuses replaced at transformer TC4881 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000526 | 11 | 2017 | 2017-03-10 | C | 1 | 0.000526 | 2.9956e-06
1 | 16224732 | 2017-03-10 17:16 | 2017-03-10 18:17 | 60 | 1 | 60.6833 | 0.00018179 | 0.000172 | 2.9956e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE6-234 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses SE6-234 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000172 | 11 | 2017 | 2017-03-10 | C | 1 | 0.000172 | 2.9956e-06
1 | 16226684 | 2017-03-11 02:20 | 2017-03-11 04:05 | 105 | 22 | 2310 | 0.0069199 | 0.006722 | 6.5904e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 701772 | POLE | 1R Car / Pole. Please investigate. (Fire Comms No. F2263906). Isolation required between ABS 295 and Fuses 8279 with backfeed at ABS 351.. Pole extensively damaged but lines all up. (No trippings). Pole changed, relivened OK. NDR N100333 | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.006722 | 11 | 2017 | 2017-03-11 | C | 22 | 0.006722 | 6.5904e-05
1 | 16226948 | 2017-03-11 00:47 | 2017-03-11 02:47 | 120 | 213 | 17430.2833 | 0.052215 | 0.0503 | 0.00063807 |  | 22 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4137/2 | UNKNOWN | Tripping on Recloser CB4137/2 on O/C A-C Phase. Feeder patrolled / sectionalised but nothing found. Restored OK. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.0503 | 22 | 2017 | 2017-03-11 | C | 213 | 0.0503 | 0.00063807
1 | 16227182 | 2017-03-11 01:03 | 2017-03-11 01:19 | 15 | 418 | 4990.7333 | 0.01495 | 0.011193 | 0.0012522 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB3 | UNKNOWN | CB 3 trip. Backfeed put in via RS 9679 up to RS 9556. CB3 closed back in OK after 15min. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.011193 | 11 | 2017 | 2017-03-11 | C | 418 | 0.011193 | 0.0012522
1 | 16227821 | 2017-03-11 02:19 | 2017-03-11 07:07 | 287 | 120 | 19907.3667 | 0.059635 | 0.058556 | 0.00035948 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | A0280 | CROSSARM - WHOLE ASSEMBLY | Trip. Recloser 9539 Trip. E/F. L/O. Sectionalised. Fault found at Pole A0280. Broken Crossarm and Burnt Crossarm. This pole also has FABS attached. Isolation at ABS 987. Crossarm replaced. 1 x HV crossarm with 3 Ph assembly replaced. All supply restored. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.058556 | 11 | 2017 | 2017-03-11 | C | 120 | 0.058556 | 0.00035948
1 | 16228060 | 2017-03-11 03:09 | 2017-03-11 07:30 | 260 | 140 | 18016.3 | 0.05397 | 0.052711 | 0.00058115 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P05797 | INSULATOR | Replaced 1x 11kv insulator and repaired line. Section of line between ABS P68 and P66 isolated and balance of line backfed via ABS N40 for duration of repairs | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.052711 | 11 | 2017 | 2017-03-11 | C | 140 | 0.052711 | 0.00058115
1 | 16229299 | 2017-03-11 12:00 | 2017-03-11 12:19 | 19 | 2 | 38 | 0.00011383 | 9.5e-05 | 5.9912e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TC5561 | SERVICE BOX - GYRO/PILLAR/POD (LV) | 12.40 - Incorrectly took FM offsite - still currently taking photos etc. Will ring shortly to clear job All clear 12.55 Replaced 1UG Gyro Box 3 x 10amp HV fuses - has spoken and gone through Control TX: TC5561 Cause: vehicle, NDR: 31035 Nothing else repaired or replaced Transformer TC5561 was isolated at fuse/sw FC720 to replace blown HV fuse also blown at transformer. | F3 | JOAN GASKELL DR | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 9.5e-05 | 11 | 2017 | 2017-03-11 | C | 2 | 9.5e-05 | 5.9912e-06
1 | 16229567 | 2017-03-11 06:17 | 2017-03-11 12:28 | 370 | 261 | 41513.3 | 0.12436 | 0.12201 | 0.00078186 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 394600 | POLE | CB 3 Pongakawa sub tripped to L/O. O/C & E/F flags. Line being sectionalised & patrolled when report of pole down received on Old Coach Rd. Backfeed was in place from Recloser 9679/2 to recloser 9556/2 following previous fault tripping so supply not lost to all of the feeder when CB tripped. Pole 394600 found to have fallen down a bank and fell across road when bank gave way during heavy rain. Line isolated at ABS SF7-031, SF8-005 & SE7-025. Pole relocated across other side of road. As built info to be supplied by Downer. All supply restored following pole relocation. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.12201 | 11 | 2017 | 2017-03-11 | C | 261 | 0.12201 | 0.00078186
1 | 16231089 | 2017-03-11 10:15 | 2017-03-11 14:05 | 230 | 42 | 9660 | 0.028938 | 0.02856 | 0.00012582 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SD4-262 | CABLE - REPLACE LESS THAN 5 METRES | Check OMS: 16231184 - 6 Burns St HV fuse found blown at SD4-362. HV link box isolated at fuses SD4-161, fuse replaced, fuse blew at SD4-161 on reclosing with transformer still off loaded. Apparent cable fault before transformer SD4-519. Generator installed. Cable fault locating/repairs to be carried following storm faults/repairs at later date. | F3 | CAMERON RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.02856 | 11 | 2017 | 2017-03-11 | C | 42 | 0.02856 | 0.00012582
1 | 16231609 | 2017-03-11 08:43 | 2017-03-11 11:03 | 139 | 480 | 23052.5833 | 0.069057 | 0.064743 | 0.0021509 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 224934 | POLE | CB 8 tripped to L/O. O/C & E/F flags.Line sectionalised & patrolled. Dispatch advised Control pole and lines down at 221 Browns Road. Pole 224934 found to have fallen over onto road verge following land slip. Line isolated at SE6-135 & SE6-137 to create temp line break for isolation at pole 224935. Line break created, isolation between that and SE6-135 left for pole replacement at later stage. All supply restored. 1x Pole, 2x Crossarms, 6x Insulators, all 3 phases greater than 1 span of conductor, 6x binders. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.064743 | 11 | 2017 | 2017-03-11 | C | 480 | 0.064743 | 0.0021509
1 | 16233113 | 2017-03-11 09:23 | 2017-03-11 11:35 | 132 | 153 | 16238.8 | 0.048645 | 0.04727 | 0.00045833 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712317 | CROSSARM - COMPONENT(S) ONLY | CB NG4 ARC & Tripped A&B Phase O/C & E/F during sectionalising report received of line down @ pole 712317 on investigation found it was a twisted crossarm with a broken centrebolt .Section of line between ABS NG402 & NG 434 Isolated to carry out repairs Balance of line backfed for duration via ABS NG 326 Replaced centre bolt on pole 712317 | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.04727 | 11 | 2017 | 2017-03-11 | C | 153 | 0.04727 | 0.00045833
1 | 16235046 | 2017-03-11 15:46 | 2017-03-11 15:49 | 3 | 17 | 51 | 0.00015278 | 0 | 5.0926e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE6-133 | FUSE - ELEMENT/LINK (HV) | 1 x 10 amp HV fuse replaced in fuse/sw SE6-133. RMU isolated at Sw/gear 9608/3 to change fuse. Problem still existed on relivening. 1 x 20 amp fuse at SE6-232 found blown. Reloaded and livened. All supply restored. Please check and link OMS: 16236561 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2017-03-11 | C | 17 | 0 | 5.0926e-05
1 | 16236168 | 2017-03-11 13:40 | 2017-03-11 14:59 | 79 | 2 | 158.5333 | 0.00047491 | 0.000456 | 5.9912e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 11103 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8a HV fuses @ 11103 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000456 | 11 | 2017 | 2017-03-11 | C | 2 | 0.000456 | 5.9912e-06
1 | 16236888 | 2017-03-11 18:19 | 2017-03-12 00:42 | 383 | 677 | 83891.4 | 0.25131 | 0.24522 | 0.002028 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 218311 | POLE | CB 3 tripped to L/O. E/F & A & C Ph O/C flags Car v pole reported by fire service. 206 Arawa Ave Maketu F2264484 09 4867948 Replaced pole complete | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.24522 | 11 | 2017 | 2017-03-11 | C | 677 | 0.24522 | 0.002028
1 | 16239083 | 2017-03-12 02:04 | 2017-03-12 16:10 | 845 | 2248 | 69643.65 | 0.20862 | 0.18842 | 0.0067341 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 752571 | POLE | CB 12 tripped on A, B & C phase O/C flags, faultman found on the way to sectionalise a car vs pole, line was isolated at ABS 157, Sw/gear's 73/3 & 6407/4 to replace the pole.Line break put in place leaving transformer 615 off Pole 752571 and transformer 615 replaced and inspector checking installations as they suspect there was a possible 11k v 400v contact A safety disconnect had to be made to 17 Portland Drive - Disconnect number A13038 on pole 752574. NDR: N100334. This job was a 2 R job. | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.18842 | 11 | 2017 | 2017-03-12 | C | 2248 | 0.18842 | 0.0067341
1 | 16242087 | 2017-03-12 05:15 | 2017-03-12 08:13 | 178 | 85 | 15169.6667 | 0.045442 | 0.044678 | 0.00025462 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H106 | FUSE - ELEMENT/LINK (HV) | Line patrolled and no obvious cause found (suspect lightning) Replaced 2x 50 a HV Fuses @ H106 outage on child | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.044678 | 11 | 2017 | 2017-03-12 | C | 85 | 0.044678 | 0.00025462
1 | 16242174 | 2017-03-12 07:24 | 2017-03-12 08:40 | 76 | 6 | 456 | 0.001366 | 0.001312 | 1.7973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 778971 | FUSE - ELEMENT/LINK (HV) | Rerplaced 2x 6a hv fuses outage on child | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.001312 | 11 | 2017 | 2017-03-12 | C | 6 | 0.001312 | 1.7973e-05
1 | 16242252 | 2017-03-12 07:55 | 2017-03-12 10:35 | 159 | 5 | 799.5 | 0.002395 | 0.00235 | 1.4978e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1353 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV fuses | F4 | JUNCTION RD | CARRINGTON ST 33 | Taranaki | MANGOREI | Western Electricity | POWERCO | 0.00235 | 11 | 2017 | 2017-03-12 | C | 5 | 0.00235 | 1.4978e-05
1 | 16242273 | 2017-03-12 07:59 | 2017-03-12 12:21 | 262 | 5 | 1311.3333 | 0.0039282 | 0.003883 | 1.4978e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725013 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8a HV Fuses blown due twisted wires | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.003883 | 11 | 2017 | 2017-03-12 | C | 5 | 0.003883 | 1.4978e-05
1 | 16242622 | 2017-03-12 09:19 | 2017-03-12 14:05 | 286 | 489 | 39659 | 0.1188 | 0.11441 | 0.0015517 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | ic1969 | CABLE - REPLACE LESS THAN 5 METRES | CB 7 L/O on E/F & O/C. Sectionalised and found fault between IC1969 & transformer TC3440. Connected generator to TC3440 DNO 170316 | F3 | MOSSOPS RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.11441 | 11 | 2017 | 2017-03-12 | C | 489 | 0.11441 | 0.0015517
1 | 16243507 | 2017-03-12 09:59 | 2017-03-12 11:44 | 105 | 2 | 210.7333 | 0.00063127 | 0.000613 | 5.9911e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11103 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8a HV Fuses found bird under pole 842266 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000613 | 11 | 2017 | 2017-03-12 | C | 2 | 0.000613 | 5.9911e-06
1 | 16243921 | 2017-03-12 14:21 | 2017-03-12 17:00 | 158 | 76 | 12059.9333 | 0.036127 | 0.035443 | 0.00022766 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | TINUI VALLEY ROAD | CONDUCTOR - REPAIR/REHANG | Found tree on line. Isolated at S169. Removed tree & relivened NDR still to be provided | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.035443 | 11 | 2017 | 2017-03-12 | C | 76 | 0.035443 | 0.00022766
1 | 16244699 | 2017-03-13 03:53 | 2017-03-13 04:50 | 56 | 4 | 226.6667 | 0.00067899 | 0.000643 | 1.1982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-086 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses SD5-086. Suspect bird strike | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000643 | 11 | 2017 | 2017-03-13 | C | 4 | 0.000643 | 1.1982e-05
1 | 16244745 | 2017-03-13 08:02 | 2017-03-13 09:02 | 60 | 19 | 1140 | 0.0034149 | 0.003244 | 5.6915e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3833 | FUSE - HOLDER/BASE (LV) | MOV 1 isolate & earth transformer TC3833 ( T Blade ) to replace burnt fuse holder ( L/V ) Isolation between Links IP541 & sw/gear 9472/1 with back feed via ABS 1082. Replaced 1 x L/V Fuse base & 1 x 200A fuse All service restored ( old age ) | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.003244 | 11 | 2017 | 2017-03-13 | C | 19 | 0.003244 | 5.6915e-05
1 | 16247722 | 2017-03-13 14:07 | 2017-03-13 20:28 | 380 | 500 | 49014.8167 | 0.14683 | 0.14233 | 0.0016985 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | OAK 6 | UNKNOWN | OAK 6 tripped E/F, L/O Feeder sectionalised with fault isolated to beyond fuses 8487 encounted locked gate with access restricted to foot patrol . Section of line sectionalised and full supply restored with no apparent cause found. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.14233 | 11 | 2017 | 2017-03-13 | C | 500 | 0.14233 | 0.0016985
1 | 16249095 | 2017-03-13 14:48 | 2017-03-13 14:53 | 5 | 1432 | 7420.7333 | 0.022229 | 0.00936 | 0.0042896 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2912 | UNKNOWN | Doing LLP 29089-01 Closed ABS B Phase not closed all the way tripped on B Phase Over current | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.00936 | 11 | 2017 | 2017-03-13 | C | 1432 | 0.00936 | 0.0042896
1 | 16250574 | 2017-03-13 14:58 | 2017-03-13 17:24 | 145 | 171 | 14732.35 | 0.044131 | 0.042594 | 0.00082377 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | n2037 | NONE | Recloser 9688 L/O No flags. Sectionalised and found branch on line past fuses FC2409. Isolated at fuses and removed branch from line. Relivened NDR 51015 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.042594 | 11 | 2017 | 2017-03-13 | C | 171 | 0.042594 | 0.00082377
1 | 16252672 | 2017-03-13 16:02 | 2017-03-13 16:15 | 13 | 1 | 13.3833 | 4.009e-05 | 3.1e-05 | 2.9955e-06 |  | 66 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Thames sub | LIGHTNING ARRESTOR (HV) | CB 15 & CB QC24 tripped simultaneously. Loss of supply to T3 bank & A & G Price. CB16 closed restoring supply to A & G Price. Visual inspection identified faulty lightning arrestor on 66kV bus.T3 isolated at CB 15 & ABS QC31. Faulty arrestor disconnected. T3 relivened & bus switching restored to normal. All 3 arrestors require replacing in opinion of Brent. He will address this via defect procedure. No protection relay operations received at NOC via SCADA. On site E/F & Y Ph O/C flags had operated. These are connected IO's and should have been received. SCADA auto/manual control on T3 tap changer no longer available?? Both these issues need further investigation. | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 3.1e-05 | 66 | 2017 | 2017-03-13 | C | 1 | 3.1e-05 | 2.9955e-06
1 | 16253895 | 2017-03-13 17:01 | 2017-03-13 20:53 | 232 | 1049 | 60146.6 | 0.18017 | 0.17074 | 0.0033909 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E60 | INSULATOR | Report from public - Loud explosion sounds, next to sub. Fire comms #F2266229 ETA required 04 801 0812. Additional notes - pole Z27 outside substation Surge arrestors blown causing damage to insulators and flared up into the 33kv ... Replaced insulators and cut away surge arrestors Please check OMS 16256616 - 156 Kelvin Grove when closing | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.17074 | 11 | 2017 | 2017-03-13 | C | 1049 | 0.17074 | 0.0033909
1 | 16257298 | 2017-03-14 03:39 | 2017-03-14 05:38 | 119 | 181 | 9396.2 | 0.028146 | 0.026519 | 0.00054218 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9070/2 | CABLE - REPLACE LESS THAN 5 METRES | Fuse switch 9070/2 found tripped. Cable isolated & tested. Faulty cable identified between transformers TD4-615 & TD4-747. Cable to TD4-747 disconnected at TD4-615, RMU 9070 isolated at sw/gear 9073/1, 9342/3 & ABS IP473 to change fuses, transformer TD4-615 relivened. Generator being arranged to connect at TD4-747 Warren and Mike were offsite @7am - as advised by Frank from TGA | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.026519 | 11 | 2017 | 2017-03-14 | C | 181 | 0.026519 | 0.00054218
1 | 16257531 | 2017-03-14 06:22 | 2017-03-14 08:35 | 133 | 423 | 19761.5667 | 0.059196 | 0.055394 | 0.0012671 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | L0244 | POLE | CB 6 tripped to L/O. E/F & A & C Ph O/C flags. Report of car v pole cnr SH 27 & Cussens Rd. Reported by fire service F2266443 - Phone 09 4867949 Isolated at ABS ic677 ic635 backfed via ABSIC2137 8m conductor 8 sleeves | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.055394 | 11 | 2017 | 2017-03-14 | C | 423 | 0.055394 | 0.0012671
1 | 16260294 | 2017-03-14 09:56 | 2017-03-14 11:19 | 82 | 500 | 19511.3167 | 0.058446 | 0.053952 | 0.0014977 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | na | UNKNOWN | OAK 6 tripped E/F, L/O feeder sectionalised no fault found, all service restored Feeder split beyond ABS 156 to OAK 8 at ABS 52 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.053952 | 11 | 2017 | 2017-03-14 | C | 500 | 0.053952 | 0.0014977
1 | 16261670 | 2017-03-14 10:10 | 2017-03-14 11:21 | 71 | 6 | 426 | 0.0012761 | 0.001222 | 1.7973e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 224934 | POLE | Line isolated at SE6-135 & SE6-137 to create temp line break for isolation at pole 224935. Line break created, isolation between that and SE6-135 left for pole replacement at later stage. All supply restored. 1x Pole, 2x Crossarms, 6x Insulators, all 3 phases greater than 1 span of conductor, 6x binders. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001222 | 11 | 2017 | 2017-03-14 | C | 6 | 0.001222 | 1.7973e-05
1 | 16262627 | 2017-03-14 13:10 | 2017-03-14 14:50 | 100 | 2 | 200 | 0.0005991 | 0.000581 | 5.9909e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12598 | FUSE - ELEMENT/LINK (HV) | 2 x6ap @fc816 poss bird 14:50 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000581 | 11 | 2017 | 2017-03-14 | C | 2 | 0.000581 | 5.9909e-06
1 | 16263578 | 2017-03-14 18:30 | 2017-03-14 20:10 | 100 | 34 | 3400 | 0.010185 | 0.009879 | 0.00010185 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826802 | CROSSARM - WHOLE ASSEMBLY | Pole 826802 Can a fault person please be dispatched to this site now as an 11kV arm is falling from the pole . Gavin Paget 027 230 3514 Isolated between ABS S194 & S156. replaced 2 x crosarms 2 x polymers & 2 x 10amp ht fuses | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.009879 | 11 | 2017 | 2017-03-14 | C | 34 | 0.009879 | 0.00010185
1 | 16263912 | 2017-03-14 21:30 | 2017-03-14 22:45 | 75 | 6 | 450 | 0.001348 | 0.001294 | 1.7973e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728527 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace transformer W1030 due to oil leak | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.001294 | 11 | 2017 | 2017-03-14 | C | 6 | 0.001294 | 1.7973e-05
1 | 16264099 | 2017-03-14 19:52 | 2017-03-14 22:30 | 157 | 374 | 23770.5667 | 0.071205 | 0.067843 | 0.0011203 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-519 | CABLE - REPLACE LESS THAN 5 METRES | at 19:52, Tauranga GXP, CB 15 Cameron Rd Feeder, Recloser 9917, Tripped, E/F, L/O. Faultmen dispatched & investigation began. Found cable had faulted beyond fuses SD4-161. Isolated cable at Fuses SD4-161. Generator connected to Transformer TD4-519 to restore supply. Permit issued & repairs carried out. All Power Restored on Completion. Mike Hata Attended. 1x joint kit 1x termination kit. 4m of cable single core 25mm2 4:30pm Email sent chasing close off notes - KN | F3 | CAMERON RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.067843 | 11 | 2017 | 2017-03-14 | C | 374 | 0.067843 | 0.0011203
1 | 16264719 | 2017-03-14 22:59 | 2017-03-15 00:14 | 74 | 254 | 14293.9 | 0.042817 | 0.040534 | 0.00076085 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NFF | UNKNOWN | line sectionalised and patrolled with no obvious cause found CB H131 Trip O/C | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.040534 | 11 | 2017 | 2017-03-14 | C | 254 | 0.040534 | 0.00076085
1 | 16266067 | 2017-03-15 03:42 | 2017-03-15 05:32 | 110 | 173 | 11521.8833 | 0.034513 | 0.032958 | 0.00051821 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9320 | UNKNOWN | Recloser 9320 L/O on O/C B. Sectionalised and found NO fault | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.032958 | 11 | 2017 | 2017-03-15 | C | 173 | 0.032958 | 0.00051821
1 | 16266696 | 2017-03-15 09:00 | 2017-03-15 09:39 | 39 | 1 | 39 | 0.00011682 | 0.000107 | 2.9954e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE5-015 | JUMPER | at 09:00, Atuaroa Sub, CB 4 Te Puke Nth Feeder. Faultman found blown jumper at Transformer TE5-015. Own Isolation & AP Issued to repair jumper. All Power Restored on Completion. Jackson Achilles Attended. 3x connectors replaced. | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.000107 | 11 | 2017 | 2017-03-15 | C | 1 | 0.000107 | 2.9954e-06
1 | 16267098 | 2017-03-15 16:51 | 2017-03-15 17:09 | 18 | 7 | 126.2333 | 0.00037813 | 0.000315 | 2.0968e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 353618 | CROSSARM - COMPONENT(S) ONLY | Refixed 11kV Cross arm to Pole using 1x 300mm bolt, 2x washers, & 2x nuts. NOC requested 2x 1R to keep shutdown time to a minimum. | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000315 | 11 | 2017 | 2017-03-15 | C | 7 | 0.000315 | 2.0968e-05
1 | 16267443 | 2017-03-16 10:07 | 2017-03-16 11:00 | 53 | 70 | 3710 | 0.011113 | 0.010483 | 0.00020968 | NAPA ID:29817 TP_KAITIMAKO GXP > WELCOME BAY SUB > POIKE | 11 | Planned | 029817 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-747 | NONE | remove generator. Works location: Hollister Lane, Tauranga. WO 30024975 | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.0052415 | 5.5 | 2017 | 2017-03-16 | B | 70 | 0.010483 | 0.00020968
1 | 16267684 | 2017-03-16 14:11 | 2017-03-16 15:29 | 78 | 42 | 3276 | 0.0098129 | 0.009435 | 0.00012581 | NAPA ID:29818 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMERON RD | 11 | Planned | 029818 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-519 | NONE | Remove generator from TD4-519. Generator removed but cables could not be connected so Generator was re-connected. Another job will need to be created to fix cable and remove generator | F3 | CAMERON RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0047175 | 5.5 | 2017 | 2017-03-16 | B | 42 | 0.009435 | 0.00012581
1 | 16267688 | 2017-03-15 11:30 | 2017-03-15 12:31 | 61 | 115 | 6862.0833 | 0.020555 | 0.019521 | 0.00034448 | Please | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 1022 | NONE | Recloser 1022 Trip E/F & O/C. NZ Energy closed their CB which led to recloser trip whilst HLT tag was applied for tree trimming. This was a procedure error which will be investigated. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.019521 | 6.6 | 2017 | 2017-03-15 | C | 115 | 0.019521 | 0.00034448
1 | 16268818 | 2017-03-19 07:00 | 2017-03-19 08:32 | 92 | 83 | 7294 | 0.021847 | 0.021101 | 0.00024861 | NAPA ID:29828 TP_STRATFORD GXP > ELTHAM SUB > ELTHAM TOWN NORTH | 11 | Planned | 029828 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 732055 | AIR BREAK SWITCH - ABS (HV) | Remove 11kV ABS 6192 from network pole 732055 & jumper through. (DNO 160916) (and also 6153 if time allows , leaving HV fuses 6343 to feed Tx 3384T) ABS 6192 repaired and not removed ABS 6153 not removed Fuses 6343 Replaced per instruction from Jerry Almano | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.010551 | 5.5 | 2017 | 2017-03-19 | B | 83 | 0.021101 | 0.00024861
1 | 16268971 | 2017-03-15 15:06 | 2017-03-15 19:58 | 292 | 385 | 25986.45 | 0.077841 | 0.074381 | 0.0011532 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | I0381 | POLE | Tractor has taken Pole out, Pole and lines are on the ground, tractor is on fire. Fire is enroute F2267703 - ETA requried. PKO3 tripped E/F, B & C Ph O/C, L/O Car v pole I0381 Isolation between ABS's IC1155 & IC2116. Remainder of feeder returned to service via PKO 3 Transformer TC3918 restored at 20:50 NDR 56503 1 x pole 1 x ht arm 2 x lv arm | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.074381 | 11 | 2017 | 2017-03-15 | C | 385 | 0.074381 | 0.0011532
1 | 16272288 | 2017-03-15 11:58 | 2017-03-15 17:45 | 347 | 34 | 11808.2 | 0.035371 | 0.035065 | 0.00010185 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708552 | FUSE - ELEMENT/LINK (HV) |  | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.035065 | 11 | 2017 | 2017-03-15 | C | 34 | 0.035065 | 0.00010185
1 | 16272462 | 2017-03-16 08:59 | 2017-03-16 11:05 | 126 | 2 | 252.4333 | 0.00075614 | 0.000738 | 5.9908e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 819434 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 11103 2 x 10A Bird Strike | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000738 | 11 | 2017 | 2017-03-16 | C | 2 | 0.000738 | 5.9908e-06
1 | 16273413 | 2017-03-30 08:52 | 2017-03-30 14:15 | 323 | 24 | 7752 | 0.023215 | 0.022999 | 7.1874e-05 | NAPA ID:29849 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 029849 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809548 | NONE | Replace poles between 809548 & 809645 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.011499 | 5.5 | 2017 | 2017-03-30 | B | 24 | 0.022999 | 7.1874e-05
1 | 16273606 | 2017-03-16 13:54 | 2017-03-16 17:16 | 202 | 4 | 809.5333 | 0.0024249 | 0.002388 | 1.1982e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848414 | CONDUCTOR - REPAIR/REHANG | FM investigating part power found line down at Pole 848414 due to trees in the lines burning line down. Isolated at Fuses 7871 & then trees cut by Treescape, before FM could repair downed line. Materials used: 15mtrs of No.8 wire, 3x sleeves, & 1x 10Amp HV fuse link. NDR # | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.002388 | 11 | 2017 | 2017-03-16 | C | 4 | 0.002388 | 1.1982e-05
1 | 16273839 | 2017-03-16 13:44 | 2017-03-16 15:24 | 100 | 9 | 900 | 0.0026959 | 0.002614 | 2.6959e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP673 | FUSE - ELEMENT/LINK (HV) | This customer is actually off another transformer Fuses FP673 blown. 2 x 15A HV Fuses Replaced. | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.002614 | 11 | 2017 | 2017-03-16 | C | 9 | 0.002614 | 2.6959e-05
1 | 16274852 | 2017-03-16 20:48 | 2017-03-17 01:05 | 256 | 4 | 1027.6667 | 0.0030783 | 0.003042 | 1.1982e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TG6-003 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 23:15, Paengaroa Sub, CB 5 Roydon Downs Feeder. Faultman found transformer TG6-003 had blown. Own Isolation & Access Permit issued. Transformer Replaced. All Power Restored on Completion. Hayden Bedgood attended. 2R requested to get electrician out to confirm if TX is stuffed - to be discussed at invoicing depending on scope of work required | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.003042 | 11 | 2017 | 2017-03-16 | C | 4 | 0.003042 | 1.1982e-05
1 | 16276065 | 2017-03-17 03:52 | 2017-03-17 05:30 | 98 | 16 | 1568 | 0.0046967 | 0.004552 | 4.7926e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU303 | FUSE - ELEMENT/LINK (HV) | Part Power 2 X 15 Amp Fuses at PU303 | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.004552 | 11 | 2017 | 2017-03-17 | C | 16 | 0.004552 | 4.7926e-05
1 | 16276116 | 2017-03-17 06:44 | 2017-03-17 09:30 | 165 | 1 | 165.65 | 0.00049618 | 0.000487 | 2.9953e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | rec 9932 | UNKNOWN | line patrol nothing found non scada recloser tripped closed back in 09:30 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000487 | 11 | 2017 | 2017-03-17 | C | 1 | 0.000487 | 2.9953e-06
1 | 16276364 | 2017-03-17 09:21 | 2017-03-17 12:41 | 200 | 291 | 8358 | 0.025035 | 0.02242 | 0.0001258 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 746491 | POLE | Report of Car / Pole om Manutahi Rd at Pole 746491. Extensive damage required a pole change. Isolation required between ABS 35 and ABS 386. (NOTE: CB5 auto-reclosed on O/C when ABS 35 open). Pole changed along with associated hardware. 1 HT Transformer 579 also replaced (15A). Relivened OK. Awaiting NDR No. N100336 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.02242 | 11 | 2017 | 2017-03-17 | C | 291 | 0.02242 | 0.0001258
1 | 16280592 | 2017-03-17 11:35 | 2017-03-17 12:27 | 51 | 1 | 51.95 | 0.00015561 | 0.000146 | 2.9953e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735394 | FUSE - ELEMENT/LINK (HV) | 1 x2amp hv fuse@ 3201T old age 12:27 | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.000146 | 11 | 2017 | 2017-03-17 | C | 1 | 0.000146 | 2.9953e-06
1 | 16282701 | 2017-03-17 13:35 | 2017-03-17 17:52 | 256 | 806 | 95029.2 | 0.28465 | 0.2774 | 0.0042893 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB7 | UNKNOWN | Tripping on CB7 on A Phase EF. Fault proved elusive to find. Feeder sectionalised and all restored OK. Feeder then tripped again on the same flags around 1/2 hour later. Full patrol carried out with feeder sectionalised but nothing found again. Restored OK. (Part of Frankly Rd and Mangorei Rd backfed via VS12001/2). Discussed with FRM - considered to late to organise a helicopter to patrol. 21.03.2017: Line patrolled and floating wire found at pole 701657. Repaired under OMS 16306317. | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.2774 | 11 | 2017 | 2017-03-17 | C | 806 | 0.2774 | 0.0042893
1 | 16286986 | 2017-03-17 20:38 | 2017-03-17 22:50 | 132 | 45 | 5953.5 | 0.017833 | 0.017428 | 0.00013479 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V43 | FUSE - ELEMENT/LINK (HV) | LV to HV emailed SMC to send Fman to fuse V43 Replaced 2x 10Amp HV Fuse Links & 1x HV fuse carrier. Cause Unknown | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.017428 | 11 | 2017 | 2017-03-17 | C | 45 | 0.017428 | 0.00013479
1 | 16287118 | 2017-03-17 20:07 | 2017-03-17 22:25 | 138 | 27 | 3732.3 | 0.01118 | 0.010936 | 8.0874e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 458 | FUSE - ELEMENT/LINK (HV) | Replaced 3x 10Amp HV fuses. Cause unknown, Suspect bird strike. Crew Transition Times for attending faultman from OMS 16286994 (Cancelled & Merged to this job) have been amended for KPI reporting purposes. (axk) | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.010936 | 11 | 2017 | 2017-03-17 | C | 27 | 0.010936 | 8.0874e-05
1 | 16291371 | 2017-03-18 01:51 | 2017-03-18 03:26 | 95 | 666 | 3899.95 | 0.011682 | 0.005696 | 0.0019949 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 10303/2 | UNKNOWN | RS 10303 A/R, E/F, O/C B & C Phase Sectionalised & Patrolled with no fault found Note: Fault was downstream of RS F26 but F26 did not trip. Suspect we may have a protection issue | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.005696 | 11 | 2017 | 2017-03-18 | C | 666 | 0.005696 | 0.0019949
1 | 16294057 | 2017-03-18 12:00 | 2017-03-18 14:07 | 127 | 4 | 508 | 0.0015216 | 0.001485 | 1.1981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | M2240 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found transformer M2240 to be faulty, transformer was isolated and changed. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001485 | 11 | 2017 | 2017-03-18 | C | 4 | 0.001485 | 1.1981e-05
1 | 16294813 | 2017-03-18 16:57 | 2017-03-18 19:08 | 130 | 254 | 16399.65 | 0.049122 | 0.046839 | 0.0014497 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 719945 | CONDUCTOR - REPAIR/REHANG | CB KA7 A/R, L/O, E/F. Sectionalised & Patrolled with fault found to be due to some fencing wire that had been thrown up onto HV. Removed using hot stick. Nil materials used. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.046839 | 11 | 2017 | 2017-03-18 | C | 254 | 0.046839 | 0.0014497
1 | 16295690 | 2017-03-18 18:33 | 2017-03-18 20:00 | 86 | 3 | 260.35 | 0.00077983 | 0.000752 | 8.9859e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 940 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV fuses. Suspect bird strike as line crosses river and no other cause found | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000752 | 11 | 2017 | 2017-03-18 | C | 3 | 0.000752 | 8.9859e-06
1 | 16296339 | 2017-03-19 08:11 | 2017-03-19 09:45 | 93 | 18 | 1682.8167 | 0.0050405 | 0.004878 | 5.3915e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1867 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses FP1867 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.004878 | 11 | 2017 | 2017-03-19 | C | 18 | 0.004878 | 5.3915e-05
1 | 16296672 | 2017-03-19 10:14 | 2017-03-19 14:54 | 279 | 4 | 1119.1333 | 0.0033521 | 0.003316 | 1.1981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | M2240 | FUSE - HOLDER/BASE (LV) | Replaced 3x lV fuse boxes and repaired several lv joints | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003316 | 11 | 2017 | 2017-03-19 | C | 4 | 0.003316 | 1.1981e-05
1 | 16297565 | 2017-03-19 19:04 | 2017-03-20 | 296 | 2 | 592.8 | 0.0017756 | 0.001757 | 5.9905e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 221866 | CABLE - REPLACE LESS THAN 5 METRES | Cable found to be faulty between Fuses SE6-097 and Transformer TE6-178 will need to be located on Monday. Generators have been installed at both Transformers TE6-178 and TE6-220 Put on at 00:00 hrs DNO 170320 Created 20/03/17 for cable repairs. Cable fault located & repairs carried out. Napa 29944 (OMS 16305588) application been applied for to carry out restoration due to Ferro resonance issues. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001757 | 11 | 2017 | 2017-03-19 | C | 2 | 0.001757 | 5.9905e-06
1 | 16298002 | 2017-03-20 00:06 | 2017-03-20 02:18 | 132 | 236 | 25263.9167 | 0.075671 | 0.073549 | 0.00070687 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB NG2 | UNKNOWN | CB NG 2 tripped no flags, line was sectionalised and patrolled no fault was found. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.073549 | 11 | 2017 | 2017-03-20 | C | 236 | 0.073549 | 0.00070687
1 | 16299095 | 2017-03-20 07:22 | 2017-03-20 13:01 | 339 | 108 | 9789.25 | 0.029321 | 0.02835 | 0.00032348 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798307 | CONDUCTOR - REPAIR/REHANG | rec C634 trip O/C E/F Line sectionalised and found trees over lines and lines down between pole 798307 and transformer T3435 Section between Fuses 7276 and ABS S626 isolated and backfed via SW 11035 for duration of repairs | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.02835 | 11 | 2017 | 2017-03-20 | C | 108 | 0.02835 | 0.00032348
1 | 16299658 | 2017-03-18 15:30 | 2017-03-18 15:53 | 23 | 40 | 920 | 0.0027557 | 0.002396 | 0.00011981 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Outage for generator removal. | F3 | MOSSOPS RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.002396 | 11 | 2017 | 2017-03-18 | C | 40 | 0.002396 | 0.00011981
1 | 16301079 | 2017-03-20 12:01 | 2017-03-20 14:04 | 123 | 19 | 2337 | 0.0069998 | 0.006829 | 5.6909e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7220 | JUMPER | Check 194 BOUNDARY ROAD, OMS 16301156 is related And 163 Boundary Rd, OMS 16301344. Have advised SMC of LV to HV extent, email and phone. Line isolated from links 7220 to replace jumper into bottom of links | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.006829 | 11 | 2017 | 2017-03-20 | C | 19 | 0.006829 | 5.6909e-05
1 | 16302374 | 2017-03-21 10:00 | 2017-03-21 11:20 | 80 | 40 | 3200 | 0.0095845 | 0.009225 | 0.00011981 | NAPA ID:29928 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 029928 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole R13207 | NONE | TO CREATE TEMP LINE BREAK TO ISOLATE SECTION OF 11KV LINE WITH BADLY DAMAGED STRAIN XARM AT R13207,R13208. Works location: Tairua Rd, Whangamata. WO 30024974 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.0046125 | 5.5 | 2017 | 2017-03-21 | B | 40 | 0.009225 | 0.00011981
1 | 16302882 | 2017-03-20 19:04 | 2017-03-20 20:11 | 67 | 26 | 1742 | 0.0052176 | 0.004984 | 7.7875e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798719 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | Outage required between ABS S531 and S532 to repair a broken DDO at Transformer T2131. (Backfeed at Sw 11035). Materials used ; Full set DDO fuse holders and 3 HV Fuses (6A Rating). | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.004984 | 11 | 2017 | 2017-03-20 | C | 26 | 0.004984 | 7.7875e-05
1 | 16304601 | 2017-03-20 18:53 | 2017-03-20 21:48 | 175 | 16 | 2800 | 0.0083866 | 0.008242 | 4.7923e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794700 | CONDUCTOR - REPAIR/REHANG | Faultman found a line down at pole 794700, line was isolated at ABS 1125, Fuses 859 & transformer 4796W to repair the line. 7 meters 16mm copper used. 2 X 16mm Sleeves. 3 meters of binder. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.008242 | 11 | 2017 | 2017-03-20 | C | 16 | 0.008242 | 4.7923e-05
1 | 16304634 | 2017-03-20 21:38 | 2017-03-20 22:45 | 67 | 7 | 469 | 0.0014048 | 0.001341 | 2.0966e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE4-047 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Few houses off. Changed a 100 amp fuse, tested okay. Got down and went to house, and power was off. TE4-047. Lost power - yellow phase - ;last Monday, same thing today. Going to have to change Tx - everyone on that tx on part power. 2R put in for Tx replacement. Transformer replaced, tested OK. | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.001341 | 11 | 2017 | 2017-03-20 | C | 7 | 0.001341 | 2.0966e-05
1 | 16304841 | 2017-03-20 13:57 | 2017-03-20 19:08 | 311 | 3 | 933.45 | 0.0027959 | 0.002768 | 8.9856e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11339 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | OMS 16302486 just cancelled itself and made this job when the transformer was put back on line. Faultman found transformer T8/243 to be faulty transformer was replaced and on livening faultman found the LV cable going under the road to be faulty. Faultman to install a temp LV cable to customer in the morning. 30/3/2017: Crew assignment times have been amended to reflect the Crew Transition reflected in the original OMS job 16302486 (Cancelled and Merged to this OMS Number) for KPI Reporting Purposes. (axk). | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.002768 | 11 | 2017 | 2017-03-20 | C | 3 | 0.002768 | 8.9856e-06
1 | 16305788 | 2017-03-21 03:21 | 2017-03-21 04:24 | 63 | 242 | 3893.6333 | 0.011662 | 0.009487 | 0.00072483 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6749/2 | UNKNOWN | Recloser 6749/2 tripped on Aphase O/C & E/F flag, at time of tripping a section of Brooklands CB 7 was been back fed due to on going fault that was not found (17/03/17). Line was sectionalised and patrolled no fault found, will request a line patrol in day light. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.009487 | 11 | 2017 | 2017-03-21 | C | 242 | 0.009487 | 0.00072483
1 | 16306317 | 2017-03-21 12:59 | 2017-03-21 13:40 | 41 | 7 | 287 | 0.00085961 | 0.000796 | 2.0966e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701657 | BINDER | Operational Line patrol at day light in this section as keeps tripping on A phase O/C & E/F operational line patrol required between these points on Brooklands 7 Floating conductor found at Pole 701657 Isolated at ABS's 351, 370, 353 and 496 with a back feed via VS 12001/2 Neil Woodhead also on site on request from SMC Used 1 x binder | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000796 | 11 | 2017 | 2017-03-21 | C | 7 | 0.000796 | 2.0966e-05
1 | 16306673 | 2017-03-25 07:20 | 2017-03-25 07:55 | 35 | 58 | 2030 | 0.0060798 | 0.005558 | 0.00017371 | NAPA ID:29901 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11.00000000 | Planned | 029901 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3738 | NONE | Firstly (TP) Test 11kV Cable from TC3738 Source A to GAS SW 13127/4, Then (AP) connect 11kV Cable back up to Sourse A Bushing in Transformer TC3738 Sourse A. Then Liven Network to normal configuration. Remove DNO 170304 once completed. Works location: Hwy 1, Putaruru. WO 30043724 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.002779 | 5.5 | 2017 | 2017-03-25 | B | 58 | 0.005558 | 0.00017371
1 | 16307286 | 2017-03-21 09:48 | 2017-03-21 14:15 | 267 | 1 | 267.4667 | 0.00080111 | 0.000792 | 2.9951e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 854818 | FUSE - ELEMENT/LINK (HV) | 2 x 3A at Fuses 6993 Cause Unknown 14:15 | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000792 | 11 | 2017 | 2017-03-21 | C | 1 | 0.000792 | 2.9951e-06
1 | 16309723 | 2017-03-21 11:19 | 2017-03-21 12:31 | 72 | 2 | 144 | 0.0004313 | 0.000413 | 5.9903e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.000413 | 11 | 2017 | 2017-03-21 | C | 2 | 0.000413 | 5.9903e-06
1 | 16310208 | 2017-03-21 18:50 | 2017-03-21 22:47 | 237 | 1 | 237.3833 | 0.000711 | 0.000702 | 2.9951e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 221485 | CONDUCTOR - REPAIR/REHANG | 6:14 ETa 15mins - advised Murray at fire coms. 11kV Broken conductor beyond fuses S5524. (Isolation required). Repairs made and relivened OK. Required 10m Namu conductor and 4 jointers. Suspect damage had been caused by conductor rubbing against branches causing a small fire and breaking the line. | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.000702 | 11 | 2017 | 2017-03-21 | C | 1 | 0.000702 | 2.9951e-06
1 | 16310259 | 2017-03-21 18:33 | 2017-03-21 19:34 | 61 | 4 | 245.3333 | 0.00073481 | 0.000698 | 1.1981e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7288 | FUSE - ELEMENT/LINK (HV) | 2 HV Fuses Tripped at 7288 (Bird strike). Reloaded OK (6A Rating). | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000698 | 11 | 2017 | 2017-03-21 | C | 4 | 0.000698 | 1.1981e-05
1 | 16310496 | 2017-03-21 20:16 | 2017-03-21 23:17 | 180 | 59 | 10646.55 | 0.031888 | 0.031357 | 0.00017671 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC2-055 | FUSE - ELEMENT/LINK (HV) | Upgrade from LV - HV - Please check fuses SC2-005 - SMC advised. 1 HT fuse tripped at SC2-055, Patrolled OK, Relivened. (30A Rating). | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.031357 | 11 | 2017 | 2017-03-21 | C | 59 | 0.031357 | 0.00017671
1 | 16315680 | 2017-03-22 05:57 | 2017-03-22 17:05 | 668 | 5573 | 562010.2167 | 1.6833 | 1.6332 | 0.042614 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3569 | CABLE - REPLACE LESS THAN 5 METRES | * 11kV CB's 18 and 19 tripped to lock out on fast BUS Trip activation on T2 side of BUS. Resulted in loss of supply to feeders 7, 9 11. * Also CB 5 tripped to locked out (Feeder on T1 side of BUS). * Note Cb 5 and 9 had identical trip protection flagging----- viewed as odd. * Note: Majority of CB 3 back feed onto CB 11 due to fault back on 21st not yet resolved. * BUS inspected, re livened OK. Protection relays downloaded and sent to M Allpress for immediate analysis. ***See note below * Investigation to CB 5 found 11kV ABS 256 had one flicker still engaged thus linking with CB 9 feeder. Flicker forcibly opened via hot stick, CB 9 supply restored, ABS 256 now DNO 170323. * CB 5 left in back fed state to allow testing on cable out from sub as was initially assessed as seeing a genuine fault, tested clear, restored to service. * Investigation of Fast BUS trip scheme revealed it had operated incorrectly. Close inspection of CB 11 revealed a wiring error. This is preventing a 'block' signal to the Fast BUS trip scheme to avoid erroneous operation. * Fast BUS trip has now been disabled. * Issues on CB 3 with numerous tripping's of field device 9637, * Fault finally located. Faulted under ground cable between Transformers TC3569 and TC TC3484. Faulted cable Now DNO'd 170324. (This cable is the originator of the fault sequences) * Protection review required on field ground mount circuit breakers 9637/ 2 and 3 for unreliable operation. Can we also query if reverse power flow across 9637/2 is an issue or not (Protection wise) please * Protection review and repairs to Fast BUS scheme and 11kV CB 11 (Wiring issued defected by Downer) Note: Craig Young may have been assigned to manage the Fast BUS scheme issues. * TEMPORARY GENERATION installed to transformer TC3569. (Temp line break made at Transformer TC3484) ***NCTL comment- Big thank you to Mike Allpress for his prompt management and feedback to me regarding protection analysis, very much appreciated, helped us to manage the event and restore supply quicker. :) 24/3/2017 - 08:34am - appears genterator has failed - SMC has sent FM out to investigate | F2/F3 | PORT RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 1.6332 | 11 | 2017 | 2017-03-22 | C | 5573 | 1.6332 | 0.042614
1 | 16316864 | 2017-03-22 06:30 | 2017-03-22 13:28 | 418 | 246 | 43451.2167 | 0.13014 | 0.12793 | 0.0010363 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757631 | INSULATOR | CB 6 L/O on E/F. Sectionalised and found fault between ABS 244, 187 & 414. Replaced faulty insulator on pole 757631 & relivened 1 x polymer 1 x deadend 1 x bucket truck on site traffic control | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.12793 | 11 | 2017 | 2017-03-22 | C | 246 | 0.12793 | 0.0010363
1 | 16318627 | 2017-03-22 07:18 | 2017-03-22 09:58 | 159 | 306 | 32916.9833 | 0.09859 | 0.09584 | 0.00091651 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | PU4 | UNKNOWN | CB 4 L/O on E/F A,B & C. Sectionalised and found no fault | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.09584 | 11 | 2017 | 2017-03-22 | C | 306 | 0.09584 | 0.00091651
1 | 16330140 | 2017-03-22 08:53 | 2017-03-22 12:35 | 221 | 10 | 2218.3333 | 0.0066442 | 0.006554 | 2.9951e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 393379 | FUSE - ELEMENT/LINK (HV) | Please check OMS: 16331819 - 101 MCMEEKAN DRIVE, possibly related?? 1 10 amp @ FC 916 unkown 12:35 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.006554 | 11 | 2017 | 2017-03-22 | C | 10 | 0.006554 | 2.9951e-05
1 | 16800127 | 2017-03-22 11:55 | 2017-03-22 14:06 | 130 | 306 | 18730.95 | 0.056101 | 0.053351 | 0.00091651 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704206 | INSULATOR | CB PU 4 L/O on E/F Found insulator faulty on pole 704206. Isolated at fuses PU474. Replaced 2 x insulators & relivened | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.053351 | 11 | 2017 | 2017-03-22 | C | 306 | 0.053351 | 0.00091651
1 | 16863499 | 2017-03-22 13:37 | 2017-03-22 15:00 | 82 | 2 | 165 | 0.00049419 | 0.000476 | 5.9902e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 11103 | FUSE - ELEMENT/LINK (HV) | Dead Bird at Poles 819444 & 819445 2 X 10 Amp At Fuses 11103 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000476 | 11 | 2017 | 2017-03-22 | C | 2 | 0.000476 | 5.9902e-06
1 | 16863562 | 2017-03-22 13:52 | 2017-03-22 19:06 | 313 | 14 | 4394.1333 | 0.013161 | 0.013035 | 4.1932e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P25891 | CONDUCTOR - REPAIR/REHANG | Check 811 Kahuterawa rd, OMS 16863582 is related. And 473 KAHUTERAWA ROAD, OMS 16863744. Lines down accross reiver and tangled in trees Line break created @ pole P25891 and generator connected @ transformer T2/356 Returned following day and repaired lines, replaced crossarms etc. Removed Generator from Transformer T2/356 & closed temp line break. See NDR for details of materials used. NDR #N300305 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.013035 | 11 | 2017 | 2017-03-22 | C | 14 | 0.013035 | 4.1932e-05
1 | 16865505 | 2017-03-23 06:28 | 2017-03-23 08:03 | 94 | 22 | 2083.0333 | 0.0062388 | 0.006041 | 6.5892e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P17423 | FUSE - ELEMENT/LINK (HV) | 2 x 10A 08:05 bird strike | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.006041 | 11 | 2017 | 2017-03-23 | C | 22 | 0.006041 | 6.5892e-05
1 | 16887406 | 2017-03-23 10:47 | 2017-03-23 13:07 | 140 | 861 | 36055 | 0.10799 | 0.10025 | 0.0025788 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 9637/3 | UNKNOWN | CB 9637/2 Tripped, CB 9637/3 Tripped A/R Due to current back feeds in place CB 9637/2 is feeding CB 9637/3 CB 9637/3 opened and CB 9637/2 closed Sectionlising carried out past CB 9637/3 after work parties contacted and stood down No fault found during sectionlising Outage on child due to gis errors | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.10025 | 11 | 2017 | 2017-03-23 | C | 861 | 0.10025 | 0.0025788
1 | 16909958 | 2017-03-27 09:41 | 2017-03-27 13:21 | 220 | 36 | 7912 | 0.023696 | 0.023372 | 0.00010782 | NAPA ID:30040 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11 | Planned | 030040 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12628 | NONE | To replace 11kv ABS S33 and Xarms. DNO 170114 | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.011686 | 5.5 | 2017 | 2017-03-27 | B | 36 | 0.023372 | 0.00010782
1 | 16910058 | 2017-03-23 15:23 | 2017-03-23 16:05 | 42 | 10 | 424.1667 | 0.0012704 | 0.00118 | 2.9951e-05 |  | 11 | Planned | 028699 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829101 | NONE |  | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.00059 | 5.5 | 2017 | 2017-03-23 | B | 10 | 0.00118 | 2.9951e-05
1 | 16911189 | 2017-03-23 20:16 | 2017-03-23 22:50 | 154 | 17 | 2619.7 | 0.0078462 | 0.007693 | 5.0916e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 949 | FUSE - ELEMENT/LINK (HV) | 2 X 10 Amp Fuses at Fuses 949 Bird Strike ??? | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.007693 | 11 | 2017 | 2017-03-23 | C | 17 | 0.007693 | 5.0916e-05
1 | 16911311 | 2017-03-23 21:13 | 2017-03-23 22:18 | 64 | 10 | 646.5 | 0.0019363 | 0.001846 | 2.9951e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | OUTAGE RESTORED | OUTAGE RESTORED | 829101 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, ALL PHASES | Close Temp Line Break at poles 829101 & 829102 so that planned shut down on 24/03/17 can go ahead. Completed by Lucas Grant | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001846 | 11 | 2017 | 2017-03-23 | C | 10 | 0.001846 | 2.9951e-05
1 | 16916630 | 2017-03-26 22:48 | 2017-03-26 23:30 | 42 | 10 | 420 | 0.0012579 | 0.001168 | 2.9949e-05 | NAPA ID:30050 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 030050 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829101 | NONE | Create 11kV Line Break at Pole 829101. (Line break will be closed the following night. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000584 | 5.5 | 2017 | 2017-03-26 | B | 10 | 0.001168 | 2.9949e-05
1 | 16916655 | 2017-03-27 22:00 | 2017-03-27 23:02 | 61 | 10 | 616.6667 | 0.0018468 | 0.001756 | 2.9949e-05 | NAPA ID:30053 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 030053 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829101 | NONE | Close 11kV Line Break at Pole 829101. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000878 | 5.5 | 2017 | 2017-03-27 | B | 10 | 0.001756 | 2.9949e-05
1 | 16918233 | 2017-03-25 08:51 | 2017-03-25 09:26 | 34 | 2523 | 78939.1833 | 0.23642 | 0.21375 | 0.0075563 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1072 | UNKNOWN | CB 1072 tripped on A, B & C phase fault, Substation was back fed via CB 1092, line was patrolled and no fault was found. | S3 | TAIHAPE A 33KV | MATAROA | Wanganui | TP_MATAROA | Western Electricity | POWERCO | 0.21375 | 33 | 2017 | 2017-03-25 | C | 2523 | 0.21375 | 0.0075563
1 | 16924763 | 2017-03-25 13:34 | 2017-03-25 14:40 | 65 | 86 | 5637.3 | 0.016884 | 0.01611 | 0.00025757 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H106 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses H106, line was checked no fault was found. 2 X 50 amp HV fuses replaced. This line needs to be checked from Fuses H106 to the end as these fuse keep blowing and they have 50 Amps in them now and still have a problem. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.01611 | 11 | 2017 | 2017-03-25 | C | 86 | 0.01611 | 0.00025757
1 | 16925897 | 2017-03-25 21:28 | 2017-03-25 22:48 | 80 | 398 | 23522.4 | 0.070449 | 0.066872 | 0.001192 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 3 | UNKNOWN | Cb 3 Tripped E/F Recloser RC26 had E/F Trip flag activated, Sectionliser had E/f B ph O/C trip flag activated. No fault found during sectionlising | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.066872 | 11 | 2017 | 2017-03-25 | C | 398 | 0.066872 | 0.001192
1 | 16927165 | 2017-03-26 02:47 | 2017-03-26 05:00 | 132 | 423 | 2732.1833 | 0.0081827 | 0.004382 | 0.0012698 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2742 | UNKNOWN | CB 2742 Trip, E/F. Caused total outage of Motukawa Sub. Sub Backfed via MABS 253 & affected line sectionalised & partially patrolled. No fault found | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.004382 | 33 | 2017 | 2017-03-26 | C | 423 | 0.004382 | 0.0012698
1 | 16927636 | 2017-03-26 04:55 | 2017-03-26 16:45 | 709 | 176 | 34728.3167 | 0.10401 | 0.10243 | 0.0010452 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 809755 | POLE | RS 4659/2 A/R, L/O, O/C, E/F Car vs pole & transformer on pole 809755 . FM advised 11kV/400v line clash due to car v pole - a few meters smelling of smoke. Have advised him to engage an electrical inspector to check before relivening (costs will fall under NDR) and provide us with a list of addresses/ICPs so we can notify the retailers. 1 x pole & all hardware replaced. 1 X transformer replaced | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.10243 | 11 | 2017 | 2017-03-26 | C | 176 | 0.10243 | 0.0010452
1 | 16928711 | 2017-03-26 08:13 | 2017-03-26 10:19 | 126 | 6 | 758.9 | 0.0022728 | 0.002218 | 1.797e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1412 | FUSE - ELEMENT/LINK (HV) | 2 x HV fuses found blown at fuses FC1412. On discussion with property owner, f/man (Andrew King) was made aware the HV line was contacted yesterday by a boat mast when a boat was being sailed over an estuary under line on high tide. There was apparently quite an explosion when the contact was made and the fuses blew. The line is well signed of danger notices for sailers, but maybe some other form of prevention required? High tide clearances visually checked by Andrew & and appear to be fine but more accurate checks should be carried out?. Andrew is attempting to identfy boat owner/sailor and contact him. NDR number 047823. Photos also to be supplied by Andrew. 2 x 2 amp HF fuses reloaded & relivetned at fuses FC1412 Safety Manager Reference: 749761 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.002218 | 11 | 2017 | 2017-03-26 | C | 6 | 0.002218 | 1.797e-05
1 | 16929371 | 2017-03-26 09:23 | 2017-03-26 10:25 | 61 | 86 | 5321.9667 | 0.015939 | 0.015166 | 0.00025756 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H106 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses H106, this is an ongoing problem, faultman was asked by NOC to reload and liven the section of line and then was asked to patrol the line to look for possible cause of tripping, faultman reported that they can not find a problem with this line, customers reported to faultman that the this happens no matter if there is wind or not. Faultman will talk to Ken Pattie in the morning to find out were to from here. 2 x 50 amp HV fuses replaced. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.015166 | 11 | 2017 | 2017-03-26 | C | 86 | 0.015166 | 0.00025756
1 | 16935410 | 2017-03-27 11:50 | 2017-03-27 13:00 | 70 | 23 | 1610 | 0.0048218 | 0.004615 | 6.8882e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 3 TUTEA PLACE | CABLE - REPLACE LESS THAN 5 METRES | Suspected Cable Fault. to be repaired tomorrow. Voltages ok at transformer but not at the first link box. 09.40 - svs hub advised FM is 15mins away Generator onsite to restore power, returning tomorrow to install new cable. FM advised lance Cook will have generator times. Generator connected at 13:00 DNO 170326 created | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.004615 | 11 | 2017 | 2017-03-27 | C | 23 | 0.004615 | 6.8882e-05
1 | 16935534 | 2017-03-27 06:34 | 2017-03-27 08:57 | 143 | 557 | 41613.5167 | 0.12463 | 0.11962 | 0.0016681 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P19038 | CONDUCTOR - REPAIR/REHANG | CB 5 Tripped B Ph O/C E/F Advised Control report of white light and smoke coming from 139 Kimber St Lines down found at Pole P19038 During sectionlising Isolated at ABS M77 Lines repaired - Used 3 x Sleeves, 5 metres conductor Cause Bird strike | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.11962 | 11 | 2017 | 2017-03-27 | C | 557 | 0.11962 | 0.0016681
1 | 16937009 | 2017-03-27 08:09 | 2017-03-27 09:45 | 96 | 1 | 96.3667 | 0.00028861 | 0.000279 | 2.9948e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | u12668 | FUSE - ELEMENT/LINK (HV) | Please check OMS: 16937256 - 158 HIKUAI SETTLEMENT related?? 2 X 2A @ TC1347 Lightening | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.000279 | 11 | 2017 | 2017-03-27 | C | 1 | 0.000279 | 2.9948e-06
1 | 16937720 | 2017-03-27 08:50 | 2017-03-27 10:13 | 83 | 16 | 1328 | 0.0039772 | 0.003833 | 4.7918e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 792455 | FUSE - ELEMENT/LINK (HV) | 2 X 15A @ Fuses2951 Bird Strike | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.003833 | 11 | 2017 | 2017-03-27 | C | 16 | 0.003833 | 4.7918e-05
1 | 16938829 | 2017-03-27 09:28 | 2017-03-27 15:50 | 382 | 559 | 36917.55 | 0.11056 | 0.10554 | 0.0026654 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | M0731 | NONE | This feeder fault proved someewhat elusive to find. Initial tripping on CB6 on EF flags. Feeder patrolled and sectionalised with a tree branch removed from Pole M0731 on Horahora Rd. Removed safely with fuse stick and all relivened OK. However CB6 tripped again at 12:19 some 36 minutes later. Fault locators suggest fault on Horahora Rd so more extensive patrol carried out. Livened to links IP521 then all relivened OK again. (Load on Recloser 9636/2 transferred to 9704/2 at start to limit SAIDI). Rain in area, suspect insulator. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.10554 | 11 | 2017 | 2017-03-27 | C | 559 | 0.10554 | 0.0026654
1 | 16939555 | 2017-03-27 11:45 | 2017-03-27 13:23 | 98 | 11 | 1078 | 0.0032285 | 0.003129 | 3.2944e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 269172 | CROSSARM - WHOLE ASSEMBLY | 2R please assign Graham Hill for fuse repairs Rotten crossarm on Pole 769172 and drop outs dangling - Paul Osbourne will be onsite Power from fuses 2930 onwards will be off between approx 10.30 - 1500 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.003129 | 11 | 2017 | 2017-03-27 | C | 11 | 0.003129 | 3.2944e-05
1 | 16940033 | 2017-03-27 09:14 | 2017-03-27 11:07 | 112 | 5 | 563.4167 | 0.0016874 | 0.001642 | 1.4974e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 724975 | FUSE - ELEMENT/LINK (HV) | 2 X 10A @ CA465 Unknown @ 11:07 28/03/2017: Crew times amended to reflect the initial OMS Crew Times (OMS 16937987). axk | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001642 | 11 | 2017 | 2017-03-27 | C | 5 | 0.001642 | 1.4974e-05
1 | 16940088 | 2017-03-27 13:50 | 2017-03-27 14:14 | 24 | 5 | 120 | 0.00035939 | 0.000314 | 1.4974e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 154 COLYTON ROAD | JUMPER | Repair jumpers at transformer T4/379 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000314 | 11 | 2017 | 2017-03-27 | C | 5 | 0.000314 | 1.4974e-05
1 | 16941451 | 2017-03-27 11:29 | 2017-03-27 13:54 | 144 | 1422 | 18120.5167 | 0.054269 | 0.041492 | 0.0047708 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 721698 | INSULATOR | Tripping on Sectionaliser 10283 and Cambria CB9. Flags CB 9 Phase A-B-C O/C. Sw/gear 702EF Out, O/C in. Sw/gear 758 EF in, O/C out. Report of flash along Glover Rd. Isolation required between ABS CA710 and CA781. Backfeed at CB 8820/2. Fault caused by blown insulator and defective crossarm. Full crossarm assembly fitted, relivened OK. | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.041492 | 11 | 2017 | 2017-03-27 | C | 1422 | 0.041492 | 0.0047708
1 | 16943678 | 2017-03-27 08:32 | 2017-03-27 12:00 | 207 | 2 | 415.5 | 0.0012444 | 0.001226 | 5.9897e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 264666 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp lightening @TC1348 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.001226 | 11 | 2017 | 2017-03-27 | C | 2 | 0.001226 | 5.9897e-06
1 | 16950005 | 2017-03-27 14:15 | 2017-03-27 15:30 | 75 | 5 | 375 | 0.0011231 | 0.001078 | 1.4974e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228480 | JUMPER | Jayden from Electrical Inspection Services 0272467731 reporting HV lines touching the cross arm on pole 228480 ( Tx - TF7153) the pole is on the farm - need to drive past the house to get to the pole Advised SMC Faulty jumper located on pole 228480. Line isolated at fuses SF7-020 to carry out repairs. 2 x connectors only materials required. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001078 | 11 | 2017 | 2017-03-27 | C | 5 | 0.001078 | 1.4974e-05
1 | 16954405 | 2017-03-27 15:50 | 2017-03-27 17:49 | 118 | 97 | 6323.2667 | 0.018937 | 0.018065 | 0.0002905 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740344 | BINDER | Tripping on 6.6kV recloser 4835 on Phase B, EF. Fault traced to broken binder on Raupuha Rd (Conductor lying on crossarm) with isolation required from Fuses 6104. Conductor rebound in OK and relivened. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.018065 | 6.6 | 2017 | 2017-03-27 | C | 97 | 0.018065 | 0.0002905
1 | 16955540 | 2017-03-27 21:54 | 2017-03-28 00:22 | 148 | 2 | 296.3 | 0.00088738 | 0.000869 | 5.9897e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7033 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses replaced | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000869 | 11 | 2017 | 2017-03-27 | C | 2 | 0.000869 | 5.9897e-06
1 | 16956307 | 2017-03-28 09:42 | 2017-03-28 11:32 | 109 | 1933 | 162432.3833 | 0.48646 | 0.46909 | 0.005789 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB11 | UNKNOWN | CB 3 Trip A,B,C O/C E/F. Line patrolled & Sectionalized No Fault found. Flags reset at sectionaliser 9514 & CB 11. Operational line patrol requested between Sw/Gear 9637/2 & Temp Line Break at Poles R0719, R0721 & R12948. Kanuka around Transformer T3546 removed some signs of burning on branches. Unknown if this was cause of outage so not included as cause field. | F3 | HETHERINGTON RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.46909 | 11 | 2017 | 2017-03-28 | C | 1933 | 0.46909 | 0.005789
1 | 16959165 | 2017-03-28 10:50 | 2017-03-28 13:00 | 130 | 2 | 260 | 0.00077866 | 0.00076 | 5.9896e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M1750 | CROSSARM - WHOLE ASSEMBLY | Hazard process done. 2R - double strain arm is broken, dangling off. Replace cross arm and restrain HV OH. Outage required from Fuses FC1026 to replace full crossarm assembly. (Aged). | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.00076 | 11 | 2017 | 2017-03-28 | C | 2 | 0.00076 | 5.9896e-06
1 | 16959713 | 2017-03-28 11:50 | 2017-03-28 13:32 | 102 | 2 | 204 | 0.00061094 | 0.000592 | 5.9896e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 762120 | CONDUCTOR - REPAIR/REHANG | Lines down - lying across main highway and cars are running it over. Thinks it is one phase. Hazard process done. David 021 228 4197 Will be an NDR - TBA upon completion. TX 5095T is off. Isoaltion required from Fuses 5222 ro repair / rehang a broken conductor. (Pulled down by Maize harvester). 1 HT fuse had blown at Fuses 5222. (Awaiting NDR). | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000592 | 11 | 2017 | 2017-03-28 | C | 2 | 0.000592 | 5.9896e-06
1 | 16960819 | 2017-03-28 09:21 | 2017-03-28 11:49 | 148 | 3 | 445.25 | 0.0013334 | 0.001306 | 8.9844e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 807303 | FUSE - ELEMENT/LINK (HV) | 2 X 3 Amp @ X1309 at 11:49 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.001306 | 11 | 2017 | 2017-03-28 | C | 3 | 0.001306 | 8.9844e-06
1 | 16960980 | 2017-03-28 13:05 | 2017-03-28 16:47 | 222 | 58 | 7645 | 0.022895 | 0.022374 | 0.0001737 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4288 | UNKNOWN | Fuses at 4288 found blown, sectionlising carrier out past this point No Fault Found 29/38/2017: Crew Assignment Times amended to reflect initial Crew Status Transitions from the job that they were merged from (OMS 16595613). This has been done for KPI Reporting purposes. (axk). | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.022374 | 11 | 2017 | 2017-03-28 | C | 58 | 0.022374 | 0.0001737
1 | 16961141 | 2017-03-30 13:29 | 2017-03-30 15:40 | 131 | 44 | 5764 | 0.017262 | 0.016866 | 0.00013177 | NAPA ID:30117 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 030117 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R0719 | CONDUCTOR - REPAIR/REHANG | AP1 - Repair fault on O/H line (damaged strain arm at poles R13207,R13208) between temporary Line break and ABS 211. AP2 - Close Temporary Line Break at triple pole structure R0719, R0721, R12948. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.008433 | 5.5 | 2017 | 2017-03-30 | B | 44 | 0.016866 | 0.00013177
1 | 16961264 | 2017-03-28 13:32 | 2017-03-28 14:41 | 68 | 57 | 3902.6 | 0.011688 | 0.011175 | 0.00017071 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 249389 | NONE | FRM Ted Glasgow is aware of this. Recloser 9610 Tripped, A O/C flags from onsite by faultman. Line Patrolled at transformer TE4-149 (pole249389) bark pulled off crossarm | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.011175 | 11 | 2017 | 2017-03-28 | C | 57 | 0.011175 | 0.00017071
1 | 16962800 | 2017-03-28 15:45 | 2017-03-28 17:17 | 91 | 57 | 5226.9 | 0.015654 | 0.015141 | 0.00017071 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 384438 | RECLOSER (HV) | Recloser 9610 Trip No Flags from SCADA. Recloser faulty, San Jones has intergated the log & found the recloser has opened for no cause. DNO created 170329 | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.015141 | 11 | 2017 | 2017-03-28 | C | 57 | 0.015141 | 0.00017071
1 | 16963190 | 2017-03-28 15:48 | 2017-03-28 19:10 | 201 | 705 | 75125.2833 | 0.22499 | 0.21865 | 0.0021114 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5769 | SWITCH (HV) | Tripping on Cloton Rd CB4 on Phase B-C O/C, O/C INVT & Intertrip. CHEAL Recloser CB6942 also tripped on Phase A O/C, EF . (Reclosed after Consultation with their control Room). Fault caused by defective ABS 5769 on Regan St in Stratford. Flicker had broken and jammed inbetween Frame causing damage. Isolation required between ABSs 5791, 4987, 5800, 5813 and 5795. Backfeed in place at ABS 5713 and Sw/Gear 5766/3. 141, 142, 143 Regan Street have been left off as they need their meters inspected by an electrical inspector. Phil Webby is arranging this and have advised the customers. Replaced spring for ABS, 16m 16mm copper, 5m 25mm copper, 6x HD connectors, 2x 25mm copper sleeves and 10x 16mm copper sleeves 143 has been repaired and livened. | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.21865 | 11 | 2017 | 2017-03-28 | C | 705 | 0.21865 | 0.0021114
1 | 16964755 | 2017-03-28 18:53 | 2017-03-28 19:54 | 61 | 98 | 4655.8667 | 0.013944 | 0.013063 | 0.00029349 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1 | UNKNOWN | CB 1 tripped on B phase E/F flags, line was patrolled and sectionalised and no fault was found. When CB 1 tripped it did not make a job had to open ABS 278 to create the job. | F2 | DE HAVILAND NORTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.013063 | 11 | 2017 | 2017-03-28 | C | 98 | 0.013063 | 0.00029349
1 | 16966844 | 2017-03-29 02:36 | 2017-03-29 06:08 | 212 | 559 | 37781.3333 | 0.11315 | 0.10812 | 0.0012878 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M00573 | INSULATOR | 2 x A/R on CB 6 were followed by L/O. E/F flag. Backfeed from sectionaliser 9704/2 to recloser 9636/2 completed within statutory minute. Other backfeeds established from ABS 861 to 1072 and ABS 1102 to 1310. Rest of feeder sectionalised & patrolled. Fault had been identified as being between ABS 1337, 1310 & 1072 when a report from public via retailer of flashes seen from pole in vicinity of transformer TC1860. Faulty insulator located at pole MO573. Isolations as above to replace insulator. All supply restored on completion. This feeder has had periodic trippings in previous days with no apparent fault found on each occasion. This faulty insulator would be probable cause of each tripping. Be off you dodgy insulator. SAIDI lives on!!! | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.10812 | 11 | 2017 | 2017-03-29 | C | 559 | 0.10812 | 0.0012878
1 | 16969954 | 2017-03-29 08:54 | 2017-03-29 09:08 | 14 | 78 | 1092 | 0.0032703 | 0.002569 | 0.00023359 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746944 | INSULATOR | ABS 441 cut away to ABS 57 due to Broken Insulator on ABS 441 DNO170330 This happened during planned work, ABS 441 is isolated. | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.002569 | 11 | 2017 | 2017-03-29 | C | 78 | 0.002569 | 0.00023359
1 | 16970779 | 2017-03-29 11:22 | 2017-03-29 12:06 | 43 | 55 | 2410.8333 | 0.0072199 | 0.006725 | 0.00016471 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 808051 | CROSSARM - COMPONENT(S) ONLY | Crossarm bolt at Pole 808051 found to be disconnected and cross arm hanging at a angle Isolated at ABS O93 and Links 4137-6 with back feed via VS 848 Bolt refitted and nuts applied Used 2 x nuts | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.006725 | 22 | 2017 | 2017-03-29 | C | 55 | 0.006725 | 0.00016471
1 | 16971622 | 2017-03-29 13:55 | 2017-03-29 15:47 | 111 | 140 | 3763.5 | 0.011271 | 0.010013 | 0.0001168 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | N/A - NOT APPLICABLE | UNKNOWN | SEC N57 Trip Lightening in area line patrolled nothing found | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.010013 | 11 | 2017 | 2017-03-29 | C | 140 | 0.010013 | 0.0001168
1 | 16972529 | 2017-03-29 17:06 | 2017-03-29 18:16 | 70 | 5 | 350.25 | 0.0010489 | 0.001004 | 1.4974e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13628 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses Found Blown at Transformer T4/159 - Cause lightening Used 2 x 6 amp fuses | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.001004 | 11 | 2017 | 2017-03-29 | C | 5 | 0.001004 | 1.4974e-05
1 | 16972857 | 2017-03-29 19:18 | 2017-03-29 20:45 | 87 | 1 | 87.0667 | 0.00026075 | 0.000251 | 2.9947e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X951 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000251 | 11 | 2017 | 2017-03-29 | C | 1 | 0.000251 | 2.9947e-06
1 | 16972872 | 2017-03-29 19:29 | 2017-03-29 21:19 | 110 | 1 | 110.45 | 0.00033077 | 0.000321 | 2.9947e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1406 | FUSE - ELEMENT/LINK (HV) | Replaced 1x 3a HV fuses | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000321 | 11 | 2017 | 2017-03-29 | C | 1 | 0.000321 | 2.9947e-06
1 | 16973065 | 2017-03-29 20:31 | 2017-03-30 10:35 | 844 | 1 | 844.45 | 0.0025289 | 0.002519 | 2.9947e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03710 | FUSE - ELEMENT/LINK (HV) | Fault man can see the fuses have blown but is unable to gain access to fuses due to foliage and distance. A crew will need to go in the morning to clear vegetation. Unable to get hold of the customer. Have advised SMC. 30/03 - 06.30 - confirmed with Joanne at svs hub FM will attend at first light at 07.30 2 x 2amp and 1 holder lightning 10:35 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.002519 | 11 | 2017 | 2017-03-29 | C | 1 | 0.002519 | 2.9947e-06
1 | 16973868 | 2017-03-29 23:43 | 2017-03-30 10:34 | 651 | 629 | 42097 | 0.12607 | 0.12042 | 0.0018837 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 782601 | POLE | Car vs Pole Event No F2277222. Replace pole and repair lines. | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.12042 | 11 | 2017 | 2017-03-29 | C | 629 | 0.12042 | 0.0018837
1 | 16976786 | 2017-03-30 04:58 | 2017-03-30 05:49 | 51 | 59 | 3009 | 0.0090112 | 0.008481 | 0.00017669 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5734 | JUMPER | Repaired 1 Link | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.008481 | 11 | 2017 | 2017-03-30 | C | 59 | 0.008481 | 0.00017669
1 | 16977523 | 2017-03-30 07:57 | 2017-03-30 12:09 | 252 | 634 | 53110.2833 | 0.15905 | 0.15335 | 0.0018987 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 211327 | POLE | CB 11 trip on O/C. Fault caused by Truck / Trailer unit hitting a pole on SH29A. Isolation required bwteen Sw/Gear 9186/1, Sw/gear 9243/1 ans ABS SD3-029 with backfeeds at ABS SD3-039 and Sectionaliser 9807. 11m Pole replaced along with full crossarm assembly. Relivened OK. NOTE: Some delay putting in bacfeeds, Sectionaliser 9807 would not close via SCADA and Recloser 9698 has no Comms. Awaiting NDR | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.15335 | 11 | 2017 | 2017-03-30 | C | 634 | 0.15335 | 0.0018987
1 | 16980020 | 2017-03-30 08:22 | 2017-03-30 14:20 | 357 | 1 | 357.7333 | 0.0010713 | 0.001062 | 2.9947e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P05189 | FUSE - ELEMENT/LINK (HV) | 2 x 3A @T5/229 Weather 14:20 Customer called requesting why he had to wait for so long - as he saw the contractor drive up the road, - Called SMC - Joanne for ETA 1:15pm advised customer ETA 1 hour | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.001062 | 11 | 2017 | 2017-03-30 | C | 1 | 0.001062 | 2.9947e-06
1 | 16980112 | 2017-03-30 10:30 | 2017-03-30 11:19 | 49 | 26 | 1274 | 0.0038153 | 0.003581 | 7.7863e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12005/2 | JOINT - CONDUCTOR JOINT | hv isloated to repair lv bushing | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003581 | 11 | 2017 | 2017-03-30 | C | 26 | 0.003581 | 7.7863e-05
1 | 16980343 | 2017-03-30 11:14 | 2017-03-30 13:20 | 126 | 4 | 504 | 0.0015093 | 0.001473 | 1.1979e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 766518 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Crackling heard from within the Tx - coming from behind the door closest to the pole. Customer lives near this Tx and hasn't heard the sound before. Dylan (Strong Electrical) (021) 0244 6819 Ground Mount Transformer X801 found to be making arcing noises - Isolated at Transformer fuses on pole 766518 and Earthed For AP to tighten All HV And LV Transformer terminations. Please link OMS 16982049 when closing | F3 | CEMETERY | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001473 | 11 | 2017 | 2017-03-30 | C | 4 | 0.001473 | 1.1979e-05
1 | 16986842 | 2017-03-31 13:16 | 2017-03-31 13:44 | 28 | 425 | 4070.3 | 0.012189 | 0.008371 | 0.0012727 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | UNKNOWN | CB 2742 Tripped O/C N/Time Patrolled Nothing Found | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.008371 | 33 | 2017 | 2017-03-31 | C | 425 | 0.008371 | 0.0012727
1 | 16987276 | 2017-03-31 13:18 | 2017-03-31 13:55 | 36 | 1 | 36.9333 | 0.0001106 | 0.000101 | 2.9946e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/277 | FUSE - ELEMENT/LINK (HV) | 2 x 2A HV Fuses and Barrels at Transformer T4/277 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000101 | 11 | 2017 | 2017-03-31 | C | 1 | 0.000101 | 2.9946e-06
1 | 16988299 | 2017-03-31 13:34 | 2017-03-31 13:53 | 18 | 1421 | 20943.0667 | 0.062718 | 0.049951 | 0.0042554 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | X20 | UNKNOWN | CB X20 Trip, E/F, O/C C Phase. Caused total outage of Kimbolton Sub. Backfeeds applied to restore all power.. Full line patrol carried out with no fault found. Relivened ok. | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.049951 | 33 | 2017 | 2017-03-31 | C | 1421 | 0.049951 | 0.0042554
5202 |  |  |  |  | 837431 | 83270718 | 249.9788 | 242.5034 | 2.6858
[7 empty] | Planned | 45.9744 | 0.22809
[7 empty] | unplanned | 196.529 | 2.4577
[8 empty] | 242.5034 | 2.6858
[5 empty] | Stage 3 - Powerco Definitions |  |  |  | MED | 50% planned
[5 empty] | Filtered Saidi |  | 242.5034 |  | 227.2077 | 204.2205
[5 empty] | Filtered Saifi |  | 2.6858 |  | 2.6008 | 2.4868
[5 empty] | Number of Filtered Records |  | 5202 |  | 5202 | 5202
[5 empty] | Filtered Customer Minutes |  | 83270718.3667 |  | 83270718 | 83270718
Formulas:
date = INT([Reg Outage Start Date Time])

## 2016
Job ID | Reg Outage Start Date Time | Reg Outage End Date Time | Job Outage Duration Mins | Reg Customers Affected Count | Customer Minutes | Avg Cust Mins Pre Shave | Avg Cust Mins Post Shave | Unadjusted SAIDI | Adjusted Job Outage Duration Mins | Adjusted SAIDI | SAIFI | Job Description | Voltage | Planned / Unplanned | System | ComCom Classification | Job Cause Description | Site ID | Comments | Feeder Security | Feeder Name | GXP Name | Network Name | Substation Name | Region | Owner | Date and time converted to Date only | Class | SAIDI with planned at 50% weighting | SAIFI with planned at 50% weighting | disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
3260909 | 2015-09-13 14:25 | 2015-09-13 15:25 | 60 | 13 | 780 | 60 | 57 | 0.0023585 | 741 | 0.0022406 | 3.9309e-05 | NAPA ID:05240 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/305 | Replace 11KV crossarm, 11KV Fuse arm and 11KV Fuses T1/305. Replace LV transformer arms & transformer. Work Location: Rangitiki Line, Palmerston North. Work Order: 10160119 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-09-13 | b | 0.0011203 | 1.9654e-05 | 2016 | 2015-09-13 | B | 13 | 0.0022406 | 3.9309e-05
3880413 | 2015-04-10 09:35 | 2015-04-10 13:07 | 212.1167 | 117 | 24771.8667 | 211.7254 | 208.7254 | 0.074904 | 24420.8667 | 0.073843 | 0.00035378 | NAPA ID:06943 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV C420/1 | REPLACEMENT OF RED TAG POLE 829732. Works location: Te Wharau Rd. WO 30001246 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-04-10 | b | 0.036921 | 0.00017689 | 2016 | 2015-04-10 | B | 117 | 0.073843 | 0.00035378
3886054 | 2015-04-15 09:44 | 2015-04-15 12:13 | 149 | 4 | 596 | 149 | 146 | 0.0018022 | 584 | 0.0017659 | 1.2095e-05 | NAPA ID:07158 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 785853 | replace poles behind fuses 2518 harakikitangi rd , from poles 785853 -785858. Works location: Harakikitangi Rd Taihape. WO 10161734 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-15 | b | 0.00088294 | 6.048e-06 | 2016 | 2015-04-15 | B | 4 | 0.0017659 | 1.2095e-05
3905376 | 2015-04-01 07:03 | 2015-04-01 07:13 | 10 | 10 | 100 | 10 | 7 | 0.00030238 | 70 | 0.00021166 | 3.0238e-05 | NAPA ID:06731 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X465 | Replacing poles and equipment on spur line supplying Tx's X465, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd. Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-01 | b | 0.00010583 | 1.5119e-05 | 2016 | 2015-04-01 | B | 10 | 0.00021166 | 3.0238e-05
4038546 | 2015-04-02 09:06 | 2015-04-02 10:08 | 62.2 | 194 | 11968.4333 | 61.693 | 58.693 | 0.03619 | 11386.4333 | 0.03443 | 0.00058661 | NAPA ID:07130 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10234 | Create line breaks at T3/498 and T3/397 so that switch 434/435/436/437 can be replaced. Close line breaks and commission switch. Work Location: West Street, Feilding. Work Order: 10157269. | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-02 | b | 0.017215 | 0.0002933 | 2016 | 2015-04-02 | B | 194 | 0.03443 | 0.00058661
4038555 | 2015-04-08 14:10 | 2015-04-08 15:09 | 59.4 | 325 | 18999.8 | 58.4609 | 55.4609 | 0.057451 | 18024.8 | 0.054503 | 0.00098272 | NAPA ID:07771 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/498, T3/397 | Create line breaks at T3/498 and T3/397 so that switch 434/435/436/437 can be replaced. Close line breaks and commission switch. Work Location: West Street, Feilding. Work Order 10157269 | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-08 | b | 0.027251 | 0.00049136 | 2016 | 2015-04-08 | B | 325 | 0.054503 | 0.00098272
4048003 | 2015-04-09 09:00 | 2015-04-09 13:31 | 271 | 87 | 23577 | 271 | 268 | 0.071291 | 23316 | 0.070502 | 0.00026307 | NAPA ID:07139 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/308 | Cut over cable from 434 to new safelink switch. Work Location: East Street, Feilding. Work Order 10157269. | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-09 | b | 0.035251 | 0.00013153 | 2016 | 2015-04-09 | B | 87 | 0.070502 | 0.00026307
4048037 | 2015-04-10 09:01 | 2015-04-10 13:05 | 244.85 | 215 | 52642.75 | 244.85 | 241.85 | 0.15918 | 51997.75 | 0.15723 | 0.00065011 | NAPA ID:07141 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10234 | Cut over last leg from 436 to new safelink 10234. Work Location: East Street, Feilding. Work Order 10157269. | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-10 | b | 0.078614 | 0.00032505 | 2016 | 2015-04-10 | B | 215 | 0.15723 | 0.00065011
4082427 | 2015-04-08 09:25 | 2015-04-08 14:16 | 291 | 24 | 6984 | 291 | 288 | 0.021118 | 6912 | 0.0209 | 7.257e-05 | NAPA ID:07746 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 809550, 809557 | Replace defect poles 809557 and 809550 HV cross arms on poles 809565 and 809601. Work Location: Forest Road, Bulls. Work Order 10150361. Off 09:25 On 14:16. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-04-08 | b | 0.01045 | 3.6285e-05 | 2016 | 2015-04-08 | B | 24 | 0.0209 | 7.257e-05
4082676 | 2015-04-01 09:30 | 2015-04-01 13:20 | 230 | 32 | 7360 | 230 | 227 | 0.022255 | 7264 | 0.021965 | 9.676e-05 | NAPA ID:06763 TP_CARRINGTON GXP > OAKURA SUB > INLAND COAST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1258 | Replace 11kV transformer pole and transformer 1258. Work Location: 231 Upper Pitone Road, Okato. Work Order 30000006. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-01 | b | 0.010982 | 4.838e-05 | 2016 | 2015-04-01 | B | 32 | 0.021965 | 9.676e-05
4082814 | 2015-04-08 09:00 | 2015-04-08 11:15 | 135 | 47 | 6345 | 135 | 132 | 0.019186 | 6204 | 0.018759 | 0.00014212 | NAPA ID:07159 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 787500 | Change softwood pole 787500 due to poor condition. Work Location: Mangahane Road. Work Order 30000001. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-08 | b | 0.0093797 | 7.1058e-05 | 2016 | 2015-04-08 | B | 47 | 0.018759 | 0.00014212
4082843 | 2015-04-08 09:18 | 2015-04-08 13:07 | 229 | 2 | 98 | 49 | 46 | 0.00029633 | 92 | 0.00027819 | 6.0475e-06 | NAPA ID:06985 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12194 | Replace TX and LV X-Arms on pole P12194 (T5/187). Existing TX to be replaced. Woprk Order 10160678. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-08 | b | 0.00013909 | 3.024e-06 | 2016 | 2015-04-08 | B | 2 | 0.00027819 | 6.0475e-06
4082927 | 2015-04-08 09:10 | 2015-04-08 14:20 | 310 | 7 | 2170 | 310 | 307 | 0.0065616 | 2149 | 0.0064981 | 2.1166e-05 | NAPA ID:06942 TP_MASTERTON GXP > GLADSTONE SUB > PUKETIRO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T343 | Replacement of transformer pole and new transformer. Work Location: Te Awa Awa Road. Work Order 30000711. Off time 09:10. On time 14:20. | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-04-08 | b | 0.003249 | 1.0583e-05 | 2016 | 2015-04-08 | B | 7 | 0.0064981 | 2.1166e-05
4082938 | 2015-04-01 14:12 | 2015-04-01 16:00 | 108 | 60 | 6480 | 108 | 105 | 0.019594 | 6300 | 0.01905 | 0.00018143 | NAPA ID:07217 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12405 | Replace cross arms & HV Fuses at pole D12405. Work Location: State Highway 1, Piarere. Work Order 30000336. Job was later going out and been returned due to bad comms. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-01 | b | 0.0095248 | 9.0713e-05 | 2016 | 2015-04-01 | B | 60 | 0.01905 | 0.00018143
4082939 | 2015-04-02 08:29 | 2015-04-02 14:32 | 362.2333 | 6 | 2173.4 | 362.2333 | 359.2333 | 0.0065718 | 2155.4 | 0.0065174 | 1.8143e-05 | NAPA ID:07478 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7776 | Rerouting 11kV line away from slip. Work Location: Mangapurupuru Road. Work Order: 10162814. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-02 | b | 0.0032587 | 9.071e-06 | 2016 | 2015-04-02 | B | 6 | 0.0065174 | 1.8143e-05
4083585 | 2015-04-01 01:08 | 2015-04-01 04:29 | 200.6 | 9 | 1805.4 | 200.6 | 197.6 | 0.0054591 | 1778.4 | 0.0053775 | 2.7214e-05 | NAPA ID:06913 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD2-235 | Replace transformer due to transformer been hit by vehicle. Work Location: Corner Barrett Road and State Highway 2, Omokoroa. Work Order 30000965. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-04-01 | b | 0.0026887 | 1.3607e-05 | 2016 | 2015-04-01 | B | 9 | 0.0053775 | 2.7214e-05
4083704 | 2015-04-02 09:32 | 2015-04-02 11:26 | 113.6667 | 47 | 5342.3333 | 113.6667 | 110.6667 | 0.016154 | 5201.3333 | 0.015728 | 0.00014212 | NAPA ID:07691 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V0527 | Replace pole and 2 spans of conductor. Work Location: 247 The 309 Road, Waiau, Coromandel. Work Order 30000256. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-04-02 | b | 0.0078638 | 7.1058e-05 | 2016 | 2015-04-02 | B | 47 | 0.015728 | 0.00014212
4088333 | 2015-04-07 08:55 | 2015-04-07 14:06 | 310.45 | 33 | 4779.75 | 144.8409 | 141.8409 | 0.014453 | 4680.75 | 0.014153 | 9.9784e-05 | NAPA ID:07686 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SA2-030 L1 - L2, SA2-016, L1 - L2, TA2-010 | Resin DGS SMTC @ SA2-030 L1 & L2, SA2-016 L1 & L2 and TA2-010. Work Location: Various sites at Waihi Beach and Athenree. Work Order 10151196. | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.0070767 | 4.9892e-05 | 2016 | 2015-04-07 | B | 33 | 0.014153 | 9.9784e-05
4088413 | 2015-04-07 10:06 | 2015-04-07 13:55 | 228.9167 | 23 | 5265.0833 | 228.9167 | 225.9167 | 0.01592 | 5196.0833 | 0.015712 | 6.9546e-05 | NAPA ID:07670 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227654 | To Install Earth Spigott into existing D.O.Fuses. Work Location: 111 Rogers Road, Otamarakau. Work Order 10161617. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.0078559 | 3.4773e-05 | 2016 | 2015-04-07 | B | 23 | 0.015712 | 6.9546e-05
4089543 | 2015-04-01 09:00 | 2015-04-01 09:05 | 5 | 19 | 95 | 5 | 2 | 0.00028726 | 38 | 0.0001149 | 5.7451e-05 | NAPA ID:07611 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE7-032 | To open fuses SE7-032. Check/replace fuses with 10A Links. Work Location: 261 Arawa Avenue, Maketu, Te Puke. Work Order 10146569. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-01 | b | 5.7451e-05 | 2.8726e-05 | 2016 | 2015-04-01 | B | 19 | 0.0001149 | 5.7451e-05
4089559 | 2015-04-01 09:15 | 2015-04-01 15:30 | 375 | 29 | 10875 | 375 | 372 | 0.032883 | 10788 | 0.03262 | 8.7689e-05 | NAPA ID:07505 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1220, IC2605 | To replace 11kV poles and cross arms on Water Works Road Te Miro. Work Order 30000212. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-04-01 | b | 0.01631 | 4.3845e-05 | 2016 | 2015-04-01 | B | 29 | 0.03262 | 8.7689e-05
4089560 | 2015-04-07 09:03 | 2015-04-07 14:01 | 298.1667 | 15 | 4465.5 | 297.7 | 294.7 | 0.013503 | 4420.5 | 0.013367 | 4.5356e-05 | NAPA ID:06766 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer TE3-223 | REPLACE POLES AND ARMS AS PER SCOPE OF WORKS | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.0066833 | 2.2678e-05 | 2016 | 2015-04-07 | B | 15 | 0.013367 | 4.5356e-05
4089577 | 2015-04-07 09:20 | 2015-04-07 14:59 | 339.7833 | 15 | 5096.75 | 339.7833 | 336.7833 | 0.015411 | 5051.75 | 0.015275 | 4.5356e-05 | NAPA ID:07908 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N12681 | Replace poles and insulators. Work Location: 17 Bradshaw Road, Paeroa. Work Order 10180180. | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.0076376 | 2.2678e-05 | 2016 | 2015-04-07 | B | 15 | 0.015275 | 4.5356e-05
4089620 | 2015-04-08 09:00 | 2015-04-08 13:36 | 275.5667 | 38 | 10471.5333 | 275.5667 | 272.5667 | 0.031663 | 10357.5333 | 0.031319 | 0.0001149 | NAPA ID:06767 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Downstream of ABS IP48 | REPLACE POLES AND ARMS - TX STRUCTURE AS PER SCOPE OF WORKS | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.015659 | 5.7451e-05 | 2016 | 2015-04-08 | B | 38 | 0.031319 | 0.0001149
4092196 | 2015-04-08 08:47 | 2015-04-08 10:18 | 91.1167 | 1 | 91.1167 | 91.1167 | 88.1167 | 0.00027551 | 88.1167 | 0.00026644 | 3.0238e-06 | NAPA ID:07706 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | IC1474, IC1498 | Scheduled maintenance on IC1498 & IC1474. Work Location: Golden Cross Road, Waitewheta. Work Order 10151196. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00013322 | 1.512e-06 | 2016 | 2015-04-08 | B | 1 | 0.00026644 | 3.0238e-06
4093197 | 2015-04-08 09:30 | 2015-04-08 14:38 | 308.05 | 10 | 3080.5 | 308.05 | 305.05 | 0.0093147 | 3050.5 | 0.009224 | 3.0238e-05 | NAPA ID:07623 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227370 | To replace pole 227370 (Intersection of SH2 & Narnic Lane). Work Order 15146569. Actual outage area is between Temp ABS84 and Temp Links85 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.004612 | 1.5119e-05 | 2016 | 2015-04-08 | B | 10 | 0.009224 | 3.0238e-05
4093307 | 2015-04-08 09:46 | 2015-04-08 11:45 | 119.5667 | 21 | 2510.9 | 119.5667 | 116.5667 | 0.0075924 | 2447.9 | 0.0074019 | 6.3499e-05 | NAPA ID:07673 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 231044 | To replace arm on pole 231044. Work Location: 1655 Maniatutu Road, Pongakawa. Work Order 10161617. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.0037009 | 3.1749e-05 | 2016 | 2015-04-08 | B | 21 | 0.0074019 | 6.3499e-05
4093308 | 2015-04-08 10:01 | 2015-04-08 12:22 | 141.3 | 2 | 282.6 | 141.3 | 138.3 | 0.00085451 | 276.6 | 0.00083637 | 6.0475e-06 | NAPA ID:07642 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 325428 | Relocate pole 325428 to other side of road. Work Location: 401 Mahuta Roiad, Mangatarata. Work Order 10169591. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00041819 | 3.024e-06 | 2016 | 2015-04-08 | B | 2 | 0.00083637 | 6.0475e-06
4093534 | 2015-04-07 09:16 | 2015-04-07 15:56 | 400.0333 | 1 | 400.0333 | 400.0333 | 397.0333 | 0.0012096 | 397.0333 | 0.0012005 | 3.0238e-06 | NAPA ID:07675 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1118 | LLP1: Cut jumpers on pole M1314 to create isolation point for Access Permit. Before Live-line permit is issued PUT -5 and PUT-6 to be paralleled, ABS 1118 is to be opened and drop-out fuses FP794 are to be opened. AP1: Replace pole M1240 with a new doubl | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.00060027 | 1.512e-06 | 2016 | 2015-04-07 | B | 1 | 0.0012005 | 3.0238e-06
4099347 | 2015-04-02 09:10 | 2015-04-02 09:38 | 28 | 107 | 2202 | 20.5794 | 17.5794 | 0.0066583 | 1881 | 0.0056877 | 0.00032354 | NAPA ID:06764 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3 006 | REPLACE POLES AND ARMS AS PER SCOPE OF WORKS . Posponed due to weather ( live line component etc ) | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-02 | b | 0.0028438 | 0.00016177 | 2016 | 2015-04-02 | B | 107 | 0.0056877 | 0.00032354
4099825 | 2015-04-10 08:46 | 2015-04-10 12:45 | 239.4667 | 5 | 1197.3333 | 239.4667 | 236.4667 | 0.0036204 | 1182.3333 | 0.0035751 | 1.5119e-05 | NAPA ID:07681 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 785732 | A/P to lower wire from poles 785732 to 785733 to allow for tree removal. PPPD 46746. Work location: Deacons Road, Taihape. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-10 | b | 0.0017875 | 7.559e-06 | 2016 | 2015-04-10 | B | 5 | 0.0035751 | 1.5119e-05
4100045 | 2015-04-10 09:00 | 2015-04-10 14:15 | 315 | 3 | 945 | 315 | 312 | 0.0028575 | 936 | 0.0028302 | 9.0713e-06 | NAPA ID:06992 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/207 | Replace LV X-Arms on pole P12171 (T5/207). Existing TX to be replaced with new. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-10 | b | 0.0014151 | 4.536e-06 | 2016 | 2015-04-10 | B | 3 | 0.0028302 | 9.0713e-06
4100628 | 2015-04-02 09:26 | 2015-04-02 15:00 | 334.0167 | 280 | 28915.2167 | 103.2686 | 100.2686 | 0.087433 | 28075.2167 | 0.084893 | 0.00084665 | NAPA ID:07682 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Sw/G SA2/58 | Scheduled Maintenance on SA2-58 L1 & L2 and TA2113 L1 & L2. Works location: Seaforth Rd Waihi Beach WO 10151196 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-02 | b | 0.042446 | 0.00042333 | 2016 | 2015-04-02 | B | 280 | 0.084893 | 0.00084665
4100853 | 2015-04-08 09:10 | 2015-04-08 10:50 | 100 | 5 | 500 | 100 | 97 | 0.0015119 | 485 | 0.0014665 | 1.5119e-05 | NAPA ID:07192 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3166 | Replace LV Tx crossarms. Works locatioN: Taihoa North Rd Matamata. WO 30000330 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00073326 | 7.559e-06 | 2016 | 2015-04-08 | B | 5 | 0.0014665 | 1.5119e-05
4100902 | 2015-04-08 12:36 | 2015-04-08 14:31 | 114.7667 | 3 | 344.3 | 114.7667 | 111.7667 | 0.0010411 | 335.3 | 0.0010139 | 9.0713e-06 | NAPA ID:07193 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2376 | Relace 11kv Termination arms. Works location: Omahine Rd Matamata. WO 30000332 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00050693 | 4.536e-06 | 2016 | 2015-04-08 | B | 3 | 0.0010139 | 9.0713e-06
4101003 | 2015-04-09 09:19 | 2015-04-09 11:07 | 107.7 | 3 | 323.1 | 107.7 | 104.7 | 0.00097698 | 314.1 | 0.00094976 | 9.0713e-06 | NAPA ID:07201 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2248 | Replace 11kV termination arms. Works location: Tauranga Rd Matamata. WO 30000331 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.00047488 | 4.536e-06 | 2016 | 2015-04-09 | B | 3 | 0.00094976 | 9.0713e-06
4101006 | 2015-04-08 08:30 | 2015-04-08 10:04 | 94.1333 | 1 | 94.1333 | 94.1333 | 91.1333 | 0.00028464 | 91.1333 | 0.00027557 | 3.0238e-06 | NAPA ID:06919 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CRANE SUPPLY | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-170 | Maintanence on 11kv Switchgear, TX TD4-170. Works location: Port of Tauranga. WO 10177791 | F1 | CRANE SUPPLY | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00013778 | 1.512e-06 | 2016 | 2015-04-08 | B | 1 | 0.00027557 | 3.0238e-06
4101008 | 2015-04-08 11:29 | 2015-04-08 11:55 | 26.4833 | 1 | 26.4833 | 26.4833 | 23.4833 | 8.0079e-05 | 23.4833 | 7.1008e-05 | 3.0238e-06 | NAPA ID:06921 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CRANE SUPPLY | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4-252 | Maintanence on TX TC4-252 and clean TX Room. Works location: Port of Tauranga. WO 10177791 | F1 | CRANE SUPPLY | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 3.5504e-05 | 1.512e-06 | 2016 | 2015-04-08 | B | 1 | 7.1008e-05 | 3.0238e-06
4101863 | 2015-04-09 13:00 | 2015-04-09 14:57 | 117.3167 | 6 | 703.9 | 117.3167 | 114.3167 | 0.0021284 | 685.9 | 0.002074 | 1.8143e-05 | NAPA ID:06929 TP_MT MAUNGANUI 33 GXP > TRITON SUB > WHARF | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer TC4-233 | Maintanence on RMU's and TX TC4-233 / TC4-174. Works location: Port of Tauranga WO 10177791 | F1 | WHARF | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.001037 | 9.071e-06 | 2016 | 2015-04-09 | B | 6 | 0.002074 | 1.8143e-05
4102058 | 2015-04-08 09:23 | 2015-04-08 15:04 | 340.8833 | 103 | 35060.6333 | 340.3945 | 337.3945 | 0.10601 | 34751.6333 | 0.10508 | 0.00031145 | NAPA ID:07015 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 221179 | RE-CONFIGURE 11KV LINES AT POLE 221179. INSTALL NEW RL15 SECTIONALISER 9834/2 AND LINKS 9834/6 AT POLE 22179. Works Location: Maungarangi Rd. WO IR6423 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.05254 | 0.00015572 | 2016 | 2015-04-08 | B | 103 | 0.10508 | 0.00031145
4102074 | 2015-04-10 08:30 | 2015-04-10 09:45 | 74.65 | 18 | 1343.7 | 74.65 | 71.65 | 0.004063 | 1289.7 | 0.0038997 | 5.4428e-05 | NAPA ID:07581 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC4-088 | Maintanence on RMU and TX also clean up Sub. Works location: Port of Tauranga. WO 10177791. | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-10 | b | 0.0019499 | 2.7214e-05 | 2016 | 2015-04-10 | B | 18 | 0.0038997 | 5.4428e-05
4102227 | 2015-04-09 09:16 | 2015-04-09 13:40 | 264.45 | 96 | 15350 | 159.8958 | 156.8958 | 0.046415 | 15062 | 0.045544 | 0.00029028 | NAPA ID:07351 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TF7-075 | To replace 11kV Pin arm with Wide arms (11KV Shutdown) To rebuild the transformer. structure (Transformer Only). Works location: Pongakawa Bush Rd. WO 10161617 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.022772 | 0.00014514 | 2016 | 2015-04-09 | B | 96 | 0.045544 | 0.00029028
4103543 | 2015-04-08 08:54 | 2015-04-08 10:53 | 118.4167 | 4 | 473.6667 | 118.4167 | 115.4167 | 0.0014323 | 461.6667 | 0.001396 | 1.2095e-05 | NAPA ID:06910 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F12395 | 1: LLP To install 11kV line break at Pole # F12395. Works location: Hwy 27 Matamata. WO 10148252 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-08 | b | 0.00069799 | 6.048e-06 | 2016 | 2015-04-08 | B | 4 | 0.001396 | 1.2095e-05
4103781 | 2015-04-09 08:54 | 2015-04-09 14:40 | 346 | 4 | 1384 | 346 | 343 | 0.0041849 | 1372 | 0.0041486 | 1.2095e-05 | NAPA ID:06912 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F12395 | To undertake 11kV reconstruction between recloser 9852 and the 11kV line break at Pole # F12395. Works location: Hwy 27 Matamata. WO 10148252 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.0020743 | 6.048e-06 | 2016 | 2015-04-09 | B | 4 | 0.0041486 | 1.2095e-05
4103790 | 2015-04-10 09:04 | 2015-04-10 10:51 | 107 | 4 | 428 | 107 | 104 | 0.0012942 | 416 | 0.0012579 | 1.2095e-05 | NAPA ID:06914 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F12395 | To replace 11kV line break at pole # F12395. Works location: Hwy 27 Matamata. WO 10148252 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-10 | b | 0.00062894 | 6.048e-06 | 2016 | 2015-04-10 | B | 4 | 0.0012579 | 1.2095e-05
4105091 | 2015-04-10 11:05 | 2015-04-10 13:57 | 172.35 | 6 | 1034.1 | 172.35 | 169.35 | 0.0031269 | 1016.1 | 0.0030724 | 1.8143e-05 | NAPA ID:07699 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5265 | Replace Transformer TC5265. Works location: Pumpkin Flat Rd. WO 10148220. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-04-10 | b | 0.0015362 | 9.071e-06 | 2016 | 2015-04-10 | B | 6 | 0.0030724 | 1.8143e-05
4106095 | 2015-04-10 10:15 | 2015-04-10 15:33 | 318 | 10 | 3180 | 318 | 315 | 0.0096156 | 3150 | 0.0095248 | 3.0238e-05 | NAPA ID:07671 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 229205 | To replace pole 229205, replace Arms & Hardware on poles 229206, 229207 &229210. Works location: Old Coach Rd, Pongakawa. WO 10161617. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-10 | b | 0.0047624 | 1.5119e-05 | 2016 | 2015-04-10 | B | 10 | 0.0095248 | 3.0238e-05
4114504 | 2015-04-12 09:02 | 2015-04-12 16:16 | 433.3833 | 62 | 26869.7667 | 433.3833 | 430.3833 | 0.081248 | 26683.7667 | 0.080685 | 0.00018747 | NAPA ID:07386 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > KOROMIKO ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-019 | AP1: Replace existing series 1 SDAF3 with a Safelink CFC. During outage will also replace LV fusing on transformer TK5-019. TP1: Test 11kV cable connected to new Safelink Switch. AP2: Complete final cable connections onto new Safelink unit. Works locati | F2 | KOROMIKO ST | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-04-12 | b | 0.040343 | 9.3737e-05 | 2016 | 2015-04-12 | B | 62 | 0.080685 | 0.00018747
4115323 | 2015-04-14 09:02 | 2015-04-14 11:19 | 137.3333 | 48 | 6592 | 137.3333 | 134.3333 | 0.019933 | 6448 | 0.019497 | 0.00014514 | NAPA ID:07203 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 715 | Replace 11kV double Arms. Works location: SH 29 Matamata. WO 10000337 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-14 | b | 0.0097486 | 7.257e-05 | 2016 | 2015-04-14 | B | 48 | 0.019497 | 0.00014514
4115342 | 2015-04-17 09:49 | 2015-04-17 11:09 | 80.7833 | 131 | 10540.5167 | 80.462 | 77.462 | 0.031872 | 10147.5167 | 0.030684 | 0.00039611 | NAPA ID:06236 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > EVANS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-194 | Maintenance on 11kv Linkbox TD5-194. Works location: Kane Rd. WO 10143069. | F3 | EVANS RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-04-17 | b | 0.015342 | 0.00019806 | 2016 | 2015-04-17 | B | 131 | 0.030684 | 0.00039611
4115598 | 2015-04-14 09:00 | 2015-04-14 15:36 | 396 | 38 | 15048 | 396 | 393 | 0.045502 | 14934 | 0.045157 | 0.0001149 | NAPA ID:07697 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Pole P02365 | Cut trees around 11Kv on Rue Rue Road in two locations. Works location: Rue Rue Rd PPPD 46297 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-04-14 | b | 0.022578 | 5.7451e-05 | 2016 | 2015-04-14 | B | 38 | 0.045157 | 0.0001149
4115602 | 2015-04-16 09:00 | 2015-04-16 15:28 | 388 | 31 | 12028 | 388 | 385 | 0.03637 | 11935 | 0.036089 | 9.3737e-05 | NAPA ID:07608 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F0255 | Isolate section of 11kV lines between IC1267 and Pole # F0255 to replace pole at TC2106 in conjunction with 11kV and LV arm replacements. Works location: Burwood Rd Matamata. WO 10491423 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-16 | b | 0.018044 | 4.6868e-05 | 2016 | 2015-04-16 | B | 31 | 0.036089 | 9.3737e-05
4115621 | 2015-04-15 08:31 | 2015-04-15 15:00 | 388.1667 | 79 | 30665.1667 | 388.1667 | 385.1667 | 0.092724 | 30428.1667 | 0.092007 | 0.00023888 | NAPA ID:06626 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3786 | Replace existing T blade 300kva transformer with new 300kVA city pad transformer (TC3786). Works location: Manuka St Matamata. WO 10148293 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-15 | b | 0.046004 | 0.00011944 | 2016 | 2015-04-15 | B | 79 | 0.092007 | 0.00023888
4115622 | 2015-04-15 08:59 | 2015-04-15 16:13 | 434 | 34 | 14756 | 434 | 431 | 0.044619 | 14654 | 0.04431 | 0.00010281 | NAPA ID:06994 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P12132 | Replace xarms on Poles P12132 & 12133, remove existing two pole transformer structure (T5/133) comprising poles P13956 & P13957 and replace with new single pole and reinstall a new transformer. Works location: Beaconsfield Valley Rd. WO 10160678 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-15 | b | 0.022155 | 5.1404e-05 | 2016 | 2015-04-15 | B | 34 | 0.04431 | 0.00010281
4121517 | 2015-04-14 08:31 | 2015-04-14 11:21 | 169.5333 | 3 | 508.6 | 169.5333 | 166.5333 | 0.0015379 | 499.6 | 0.0015107 | 9.0713e-06 | NAPA ID:06940 TP_MASTERTON GXP > AKURA SUB > NGAUMUTAWA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 828159 | replace red tag poles 828159 and 828158. Works location: Hillcrest St Masterton. WO 30001015 | F2 | NGAUMUTAWA RD | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-04-14 | b | 0.00075533 | 4.536e-06 | 2016 | 2015-04-14 | B | 3 | 0.0015107 | 9.0713e-06
4121531 | 2015-04-16 09:00 | 2015-04-16 14:37 | 337 | 363 | 122331 | 337 | 334 | 0.3699 | 121242 | 0.36661 | 0.0010976 | NAPA ID:07329 TP_HUIRANGI GXP > WAITARA WEST SUB > BLAKE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 744644 | Replace Pole744644 + ABS4928 With Double 11M Busck. Upgrade Lv Conductors. Works location: Raleigh St High St. WO 30000205 | F1 | BLAKE ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 2015-04-16 | b | 0.1833 | 0.00054881 | 2016 | 2015-04-16 | B | 363 | 0.36661 | 0.0010976
4121860 | 2015-04-15 10:40 | 2015-04-15 11:35 | 54.65 | 7 | 382.55 | 54.65 | 51.65 | 0.0011567 | 361.55 | 0.0010932 | 2.1166e-05 | NAPA ID:07595 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole D12706 | To replace King bolt at Pole # D12706. Works location: Kentucky Rd. WO 10144922 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-15 | b | 0.00054662 | 1.0583e-05 | 2016 | 2015-04-15 | B | 7 | 0.0010932 | 2.1166e-05
4122659 | 2015-05-03 09:00 | 2015-05-03 12:06 | 186 | 1210 | 225060 | 186 | 183 | 0.68053 | 221430 | 0.66955 | 0.0036588 | NAPA ID:08050 TP_OHAKUNE GXP > TP_OHAKUNE | 33 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | Ohakune Sub | Transpower - Daily - Ohakune - LOS to connect mobile substation for zone transformer replacement project . | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-05-03 | b | 0.33478 | 0.0018294 | 2016 | 2015-05-03 | B | 1210 | 0.66955 | 0.0036588
4123512 | 2015-04-15 09:15 | 2015-04-15 12:46 | 211.4333 | 2 | 422.8667 | 211.4333 | 208.4333 | 0.0012786 | 416.8667 | 0.0012605 | 6.0475e-06 | NAPA ID:07588 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole D1506 | To install line break for tree cutting on 11kV spur line to TC4732, once jumpers have been removed new 11kV fuses FP1674 will be install under the AP. Once trees are removed the new fuses will be connected under a LLP and supply to TC4732 restored. Works | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-15 | b | 0.00063025 | 3.024e-06 | 2016 | 2015-04-15 | B | 2 | 0.0012605 | 6.0475e-06
4126592 | 2015-04-15 09:29 | 2015-04-15 14:33 | 304.2833 | 32 | 9737.0667 | 304.2833 | 301.2833 | 0.029443 | 9641.0667 | 0.029152 | 9.676e-05 | NAPA ID:07704 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV M72 | Finishing cutting trees near 11Kv. Works location: Pryces Line. PPPD 46602 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-04-15 | b | 0.014576 | 4.838e-05 | 2016 | 2015-04-15 | B | 32 | 0.029152 | 9.676e-05
4126620 | 2015-04-16 10:12 | 2015-04-16 14:20 | 248 | 59 | 14632 | 248 | 245 | 0.044244 | 14455 | 0.043708 | 0.0001784 | NAPA ID:04507 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC2047 | Replace 11kV crossarms. Works location: SH 1 Tokoroa. WO 10155882 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-04-16 | b | 0.021854 | 8.9201e-05 | 2016 | 2015-04-16 | B | 59 | 0.043708 | 0.0001784
4130873 | 2015-04-01 09:40 | 2015-04-01 15:15 | 335 | 71 | 5563.5 | 78.3592 | 75.3592 | 0.016823 | 5350.5 | 0.016179 | 0.00021469 | NAPA ID:06760 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | 1/ REPLACE POLES AND ARMS ALONG MCLAREN FALLS ROAD. 2/ REMOVE TEMP ABS #25 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-01 | b | 0.0080893 | 0.00010734 | 2016 | 2015-04-01 | B | 71 | 0.016179 | 0.00021469
4131496 | 2015-04-16 00:31 | 2015-04-16 01:51 | 80.0333 | 1 | 80.0333 | 80.0333 | 77.0333 | 0.000242 | 77.0333 | 0.00023293 | 3.0238e-06 | NAPA ID:07287 TP_WANGANUI GXP > TAUPO QUAY SUB > TAUPO 1 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU 2056 | Replace J3 type switchgear 2056 for new CFCC safelink. Customer on X3037 has been advised of shutdown. Works location: Taupo Quay Wanganui. WO 10158119 | F2 | TAUPO 1 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2015-04-16 | b | 0.00011647 | 1.512e-06 | 2016 | 2015-04-16 | B | 1 | 0.00023293 | 3.0238e-06
4132332 | 2015-04-14 09:17 | 2015-04-14 15:30 | 373.55 | 398 | 148672.9 | 373.55 | 370.55 | 0.44955 | 147478.9 | 0.44594 | 0.0012035 | NAPA ID:06101 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 9405 | Replacing pole number 207293 with a larger pole and reconfiguring equipment on the pole to allow the installation of a sectionaliser. Works location: Athenree Rd Athenree. WO 10148362. Delays experienced in supply restoration due to contractor vehicle pro | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-14 | b | 0.22297 | 0.00060173 | 2016 | 2015-04-14 | B | 398 | 0.44594 | 0.0012035
4132584 | 2015-04-17 09:16 | 2015-04-17 13:10 | 234.1333 | 57 | 13345.6 | 234.1333 | 231.1333 | 0.040354 | 13174.6 | 0.039837 | 0.00017235 | NAPA ID:07735 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | ABS 251 | Tree trimming betwenn poles 791170 & 791171 and poles 791335 & 791336. Works location: Mangamahu Rd, Fordell. PPPD 46500, 46495. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-17 | b | 0.019918 | 8.6177e-05 | 2016 | 2015-04-17 | B | 57 | 0.039837 | 0.00017235
4132590 | 2015-04-16 08:51 | 2015-04-16 15:07 | 376 | 1 | 376 | 376 | 373 | 0.0011369 | 373 | 0.0011279 | 3.0238e-06 | NAPA ID:07000 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse N27 | Replace xarms on pole P07812 (T5/66) and associated spur line poles. Works location: Mangamako Rd Kimbolton. WO 10160678 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-16 | b | 0.00056393 | 1.512e-06 | 2016 | 2015-04-16 | B | 1 | 0.0011279 | 3.0238e-06
4132625 | 2015-04-16 09:29 | 2015-04-16 15:05 | 336 | 26 | 8736 | 336 | 333 | 0.026416 | 8658 | 0.02618 | 7.8618e-05 | NAPA ID:06946 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 834384 | Replace 4 11kv poles 834384 834390 T1693 and 834394. Works location: Ruamahanga Gorge Rd. WO 30000873. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-04-16 | b | 0.01309 | 3.9309e-05 | 2016 | 2015-04-16 | B | 26 | 0.02618 | 7.8618e-05
4132634 | 2015-04-16 09:47 | 2015-04-16 12:18 | 151.25 | 4 | 605 | 151.25 | 148.25 | 0.0018294 | 593 | 0.0017931 | 1.2095e-05 | NAPA ID:07161 TP_MATAROA GXP > WAIOURU SUB > IRIRANGI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 899 | Replace fuses 899 with new chance drop out fuse g/b , AP to replace term arms to t/f 887. Works location: Waiouru South State Hwy 1. WO 30003155 | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-04-16 | b | 0.00089655 | 6.048e-06 | 2016 | 2015-04-16 | B | 4 | 0.0017931 | 1.2095e-05
4133879 | 2015-04-21 09:01 | 2015-04-21 15:30 | 389.4 | 50 | 19470 | 389.4 | 386.4 | 0.058873 | 19320 | 0.058419 | 0.00015119 | NAPA ID:04508 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B0773 | replace 11kV crossarms, install new section fuses FP 1647 at pole B0804. Works location: SH 1 Tokoroa. WO 10155882 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-04-21 | b | 0.02921 | 7.5594e-05 | 2016 | 2015-04-21 | B | 50 | 0.058419 | 0.00015119
4135365 | 2015-04-09 08:19 | 2015-04-11 09:20 | 2940.4333 | 1 | 2940.4333 | 2940.4333 | 2937.4333 | 0.0088912 | 2937.4333 | 0.0088821 | 3.0238e-06 | NAPA ID:07667 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > OROPI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | TD4-590 | Isolate TX so that work can be done on the LV distribution board. | F3 | OROPI RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.004441 | 1.512e-06 | 2016 | 2015-04-09 | B | 1 | 0.0088821 | 3.0238e-06
4135367 | 2015-04-09 09:00 | 2015-04-09 15:22 | 382 | 152 | 58064 | 382 | 379 | 0.17557 | 57608 | 0.17419 | 0.00045961 | NAPA ID:06738 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1283 | Replace cross arms and associated equipment between ABS1283 & TEMP41. Shutdown from 900 to 1500. Works location: Griffiths St. WO 6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.087096 | 0.00022981 | 2016 | 2015-04-09 | B | 152 | 0.17419 | 0.00045961
4135414 | 2015-04-09 09:05 | 2015-04-09 14:15 | 309.3333 | 21 | 6496 | 309.3333 | 306.3333 | 0.019642 | 6433 | 0.019452 | 6.3499e-05 | NAPA ID:08135 TP_GREYTOWN GXP > KEMPTON SUB > PONATAHI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | T950 | TREE CUTTING and replacing transformer t950 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2015-04-09 | b | 0.0097259 | 3.1749e-05 | 2016 | 2015-04-09 | B | 21 | 0.019452 | 6.3499e-05
4135425 | 2015-04-21 09:18 | 2015-04-21 15:05 | 346.65 | 38 | 13172.7 | 346.65 | 343.65 | 0.039831 | 13058.7 | 0.039486 | 0.0001149 | NAPA ID:07791 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | ABS 2551 | Isolation and access permit needed for 11kV line for tree work. Work Location: 676 Pohonui Road, Taihape. PPPD 53589 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-21 | b | 0.019743 | 5.7451e-05 | 2016 | 2015-04-21 | B | 38 | 0.039486 | 0.0001149
4135438 | 2015-04-20 08:56 | 2015-04-20 15:40 | 403.8333 | 5 | 2018.3167 | 403.6633 | 400.6633 | 0.0061029 | 2003.3167 | 0.0060576 | 1.5119e-05 | NAPA ID:07001 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P05765, P05785 | Replacing cross arms along Conspicuos Road, Apiti from poles P05765 to P05785. Work Order 10160678. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-20 | b | 0.0030288 | 7.559e-06 | 2016 | 2015-04-20 | B | 5 | 0.0060576 | 1.5119e-05
4135448 | 2015-04-15 09:13 | 2015-04-15 15:45 | 392.4833 | 153 | 24605.15 | 160.818 | 157.818 | 0.0744 | 24146.15 | 0.073012 | 0.00046264 | NAPA ID:07043 TP_TAURANGA 33 GXP | 33 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 380004 | REPLACE POLES AND ARMS ON 33KV LINES 11KV to be Isolated & Earthed. Line Break to be made at 11kV pole 380004. Short outage required to Create and Close break. Works location Cambridge Rd Wairoa Rd. WO IR7179 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-04-15 | b | 0.036506 | 0.00023132 | 2016 | 2015-04-15 | B | 153 | 0.073012 | 0.00046264
4135461 | 2015-04-16 09:20 | 2015-04-16 14:24 | 304.1333 | 211 | 45961.6333 | 217.8276 | 214.8276 | 0.13898 | 45328.6333 | 0.13706 | 0.00063801 | NAPA ID:06036 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 204944 | AP: Replacing 11kV crossarm on pole 204944 and replacing transformer TC2-032. Both activities cannot be completed using live-line techniques. LLP: Install ABS 9865/1 on pole 204944 using G&B techniques. Works location: Wright Rd Katikati. WO 10148358 | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-04-16 | b | 0.068531 | 0.00031901 | 2016 | 2015-04-16 | B | 211 | 0.13706 | 0.00063801
4138487 | 2015-04-16 08:48 | 2015-04-16 13:36 | 288 | 84 | 24192 | 288 | 285 | 0.073151 | 23940 | 0.072389 | 0.000254 | NAPA ID:06726 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 2654 | Replace cross arms and associated equipment ABS 2654 between open jumper and Temp41 ABS. Works locatioN: Margaret St/Clothier St/Charles Crescent. WO 6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-16 | b | 0.036194 | 0.000127 | 2016 | 2015-04-16 | B | 84 | 0.072389 | 0.000254
4138510 | 2015-04-14 09:45 | 2015-04-14 10:20 | 35 | 2 | 70 | 35 | 32 | 0.00021166 | 64 | 0.00019352 | 6.0475e-06 | NAPA ID:08094 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer W5217 | Replace TX W5217 (small oil leak from sight glass). Works location: Nolan Rd Hawera WO 10151987 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-14 | b | 9.676e-05 | 3.024e-06 | 2016 | 2015-04-14 | B | 2 | 0.00019352 | 6.0475e-06
4142627 | 2015-04-17 14:01 | 2015-04-17 14:56 | 55.85 | 1 | 55.85 | 55.85 | 52.85 | 0.00016888 | 52.85 | 0.00015981 | 3.0238e-06 | NAPA ID:06243 TP_MT MAUNGANUI 33 GXP > TRITON SUB > HEWLETTS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC4-587 | Maintenance on 11kV Linkbox SC4-706-SC4-712. Works location: Hutton Place, Tauranga. WO 10143069. | F2 | HEWLETTS RD | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-17 | b | 7.9903e-05 | 1.512e-06 | 2016 | 2015-04-17 | B | 1 | 0.00015981 | 3.0238e-06
4142942 | 2015-04-21 10:16 | 2015-04-21 15:28 | 311.3667 | 29 | 9029.6333 | 311.3667 | 308.3667 | 0.027303 | 8942.6333 | 0.02704 | 8.7689e-05 | NAPA ID:07271 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V76 | To Change 11Kv conductor over from exciting structures to new structures. Works location: Route 52 Pongaroa. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-21 | b | 0.01352 | 4.3845e-05 | 2016 | 2015-04-21 | B | 29 | 0.02704 | 8.7689e-05
4142955 | 2015-04-21 09:16 | 2015-04-21 15:19 | 363.3833 | 98 | 35611.5667 | 363.3833 | 360.3833 | 0.10768 | 35317.5667 | 0.10679 | 0.00029633 | NAPA ID:06711 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC3003 | Replace cross arms and associated equipment on 11kv and 400v line between pole M13207 & pole M2534. Works location: Marchant St/Margaret St Putaruru. WO 6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-21 | b | 0.053396 | 0.00014816 | 2016 | 2015-04-21 | B | 98 | 0.10679 | 0.00029633
4143800 | 2015-04-23 09:23 | 2015-04-23 15:02 | 339 | 94 | 31866 | 339 | 336 | 0.096355 | 31584 | 0.095502 | 0.00028423 | NAPA ID:06703 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 923 | Replace cross arms and associated equipment ABS 923 between from ABS923 & ABS TEMP42. Works location: Reservoir St. WO 6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-23 | b | 0.047751 | 0.00014212 | 2016 | 2015-04-23 | B | 94 | 0.095502 | 0.00028423
4156886 | 2015-04-12 18:16 | 2015-04-12 20:44 | 147.95 | 1 | 147.95 | 147.95 | 144.95 | 0.00044737 | 144.95 | 0.00043829 | 3.0238e-06 | NAPA ID:08179 TP_CARRINGTON GXP > KATERE SUB > KATERE 11 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6753 | 10 Yearly 11kV metering calibration. Actual negotiated outages with sites due to complete site shutdown. Works location: Vickers Rd. WO 10160481. | F2 | KATERE 11 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-04-12 | b | 0.00021915 | 1.512e-06 | 2016 | 2015-04-12 | B | 1 | 0.00043829 | 3.0238e-06
4156947 | 2015-04-13 05:30 | 2015-04-13 07:02 | 91.65 | 1 | 91.65 | 91.65 | 88.65 | 0.00027713 | 88.65 | 0.00026806 | 3.0238e-06 | NAPA ID:08185 TP_CARRINGTON GXP > KATERE SUB > KATERE 6 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch 8619/3 | 10 Yearly 11kV metering calibration. Actual negotiated outages with sites due to complete site shutdown. Works location: Rifle Range Rd. WO 10160482. | F2 | KATERE 6 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-04-13 | b | 0.00013403 | 1.512e-06 | 2016 | 2015-04-13 | B | 1 | 0.00026806 | 3.0238e-06
4157005 | 2015-04-07 10:22 | 2015-04-07 13:08 | 166.2333 | 4 | 664.9333 | 166.2333 | 163.2333 | 0.0020106 | 652.9333 | 0.0019743 | 1.2095e-05 | NAPA ID:07568 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > POOLES RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer TD4-288 | Shutdown transformer TD4-288 to, install LV fuse carriers | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.00098716 | 6.048e-06 | 2016 | 2015-04-07 | B | 4 | 0.0019743 | 1.2095e-05
4158596 | 2015-04-13 10:38 | 2015-04-13 13:00 | 142.4 | 23 | 3275.2 | 142.4 | 139.4 | 0.0099034 | 3206.2 | 0.0096948 | 6.9546e-05 | NAPA ID:08244 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 709165 | Replace Rotten double pin 11Kv x arm on pole 709165. Works location: Ohura/Kirai Rd Corner. WO 10136575 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-13 | b | 0.0048474 | 3.4773e-05 | 2016 | 2015-04-13 | B | 23 | 0.0096948 | 6.9546e-05
4159900 | 2015-05-01 08:45 | 2015-05-01 14:13 | 328 | 36 | 11808 | 328 | 325 | 0.035705 | 11700 | 0.035378 | 0.00010886 | NAPA ID:07172 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 370 | make LL gaps in network to remove old switchgear 370/371 and install new safelink 10233 (CCC) commission and liven new switch and close LL gaps. Works location: Makino Rd Feilding. WO 10147564 | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-05-01 | b | 0.017689 | 5.4428e-05 | 2016 | 2015-05-01 | B | 36 | 0.035378 | 0.00010886
4160228 | 2015-04-21 09:38 | 2015-04-21 11:10 | 92.5667 | 7 | 647.9667 | 92.5667 | 89.5667 | 0.0019593 | 626.9667 | 0.0018958 | 2.1166e-05 | NAPA ID:06214 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD3-206 | Maintanence on link box TD3-206. Works location: Redwood Lane. WO 10142547. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-21 | b | 0.0009479 | 1.0583e-05 | 2016 | 2015-04-21 | B | 7 | 0.0018958 | 2.1166e-05
4160335 | 2015-04-21 11:35 | 2015-04-21 13:02 | 87.7833 | 16 | 1404.5333 | 87.7833 | 84.7833 | 0.004247 | 1356.5333 | 0.0041018 | 4.838e-05 | NAPA ID:06215 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SD3-072, SD3-161 | Maintenance on Linkboxs SD3-072 & SD3-161. Work Location: Gragan Road. Work Order 10142547. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-21 | b | 0.0020509 | 2.419e-05 | 2016 | 2015-04-21 | B | 16 | 0.0041018 | 4.838e-05
4160352 | 2015-04-20 08:36 | 2015-04-20 12:49 | 252.45 | 44 | 11107.8 | 252.45 | 249.45 | 0.033587 | 10975.8 | 0.033188 | 0.00013305 | NAPA ID:07046 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 200616 | Replace 33kV pole 200616. Work Location: Clarke Road. PPPD IR7179 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-04-20 | b | 0.016594 | 6.6523e-05 | 2016 | 2015-04-20 | B | 44 | 0.033188 | 0.00013305
4160611 | 2015-04-01 07:39 | 2015-04-01 12:20 | 280.8 | 1 | 280.8 | 280.8 | 277.8 | 0.00084907 | 277.8 | 0.00084 | 3.0238e-06 | Restore Supply on Device TE6-194 | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | SE6-133 | Linked to O/H. and 4160775 - 273 Browns rd (yes this is related) linked to O/H. FM advise he has found blown ddo fuses but it is only one cable feeding one transformer so not sure at this stage is the other issues are related. #335 Browns Road is fed of | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-04-01 | c | 0.00084 | 3.024e-06 | 2016 | 2015-04-01 | C | 1 | 0.00084 | 3.0238e-06
4160778 | 2015-04-01 09:20 | 2015-04-01 09:39 | 19.4167 | 1 | 19.4167 | 19.4167 | 16.4167 | 5.8711e-05 | 16.4167 | 4.964e-05 | 3.0238e-06 | Restore Supply on Device T9/292 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V83 | 2 X 10 Amp fuses No other assets repaired or replaced at site. Adjacent assets up to Powerco Standard. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-01 | c | 4.964e-05 | 3.024e-06 | 2016 | 2015-04-01 | C | 1 | 4.964e-05 | 3.0238e-06
4160796 | 2015-04-01 08:20 | 2015-04-01 17:04 | 523.3833 | 63 | 32973.15 | 523.3833 | 520.3833 | 0.099703 | 32784.15 | 0.099131 | 0.0001905 | Restore Supply on Device IC3726A/B | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2642 | Replace 11kV ABS IC2642. Parent OMS 4094166 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-01 | b | 0.049566 | 9.5248e-05 | 2016 | 2015-04-01 | B | 63 | 0.099131 | 0.0001905
4160952 | 2015-04-01 09:04 | 2015-04-01 14:07 | 303.2667 | 57 | 17286.2 | 303.2667 | 300.2667 | 0.052269 | 17115.2 | 0.051752 | 0.00017235 | Restore Supply on Device T2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9 | To replace 11kV poles and run new conductor. Work Location: State Highway 2, Pahiatua. Work Order 10148081. Parent 4082788 | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-04-01 | b | 0.025876 | 8.6177e-05 | 2016 | 2015-04-01 | B | 57 | 0.051752 | 0.00017235
4161264 | 2015-04-07 10:15 | 2015-04-07 11:28 | 73 | 35 | 2555 | 73 | 70 | 0.0077257 | 2450 | 0.0074082 | 0.00010583 | NAPA ID:08298 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole H1262 | Replace pole H1262 hit by car. Works location: Whakahongi Rd Morrinsville. WO 4158564 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-04-07 | b | 0.0037041 | 5.2916e-05 | 2016 | 2015-04-07 | B | 35 | 0.0074082 | 0.00010583
4161326 | 2015-04-01 09:22 | 2015-04-01 12:35 | 193 | 4 | 772 | 193 | 190 | 0.0023343 | 760 | 0.0022981 | 1.2095e-05 | Restore Supply on Device L1060 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726792 | replaced 2x 6a HV fuse links OH due to possible bird strike. nothing else repaired or replaced, adjacent assets up to powerco standard. worked through control | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-04-01 | c | 0.0022981 | 1.2095e-05 | 2016 | 2015-04-01 | C | 4 | 0.0022981 | 1.2095e-05
4162909 | 2015-05-06 09:15 | 2015-05-06 14:17 | 302.3 | 10 | 3018.2 | 301.82 | 298.82 | 0.0091263 | 2988.2 | 0.0090356 | 3.0238e-05 | NAPA ID:07180 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 813019 | replacement of transformer pole T1281 and replacement of transformer arms on T1120. Works locatioN: Todds Rd Martinborough. WO 10161143 | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.0045178 | 1.5119e-05 | 2016 | 2015-05-06 | B | 10 | 0.0090356 | 3.0238e-05
4162925 | 2015-05-05 09:30 | 2015-05-05 14:10 | 279.9167 | 20 | 5598.3333 | 279.9167 | 276.9167 | 0.016928 | 5538.3333 | 0.016747 | 6.0475e-05 | NAPA ID:08041 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS S152 | trimming and felling trees between poles 780 523 and 780522. Works location: Blairlogie. PPPD 53670 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-05 | b | 0.0083733 | 3.0238e-05 | 2016 | 2015-05-05 | B | 20 | 0.016747 | 6.0475e-05
4163094 | 2015-04-01 19:41 | 2015-04-01 21:29 | 107.8 | 29 | 3126.2 | 107.8 | 104.8 | 0.0094529 | 3039.2 | 0.0091898 | 8.7689e-05 | Restore Supply on Device TC4469 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V0210 | at19:41, Coromandel Sub, CB 5 Manaia Feeder. Report of LV lines down at Pole V0210 fed from Transformer TC4469. Faultman contacted Control to isolate at HV to repair lines down. Own Isolation & AP. On trying to close in HV fuses after repairs, faultman re | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-04-01 | c | 0.0091898 | 8.7689e-05 | 2016 | 2015-04-01 | C | 29 | 0.0091898 | 8.7689e-05
4163131 | 2015-04-01 20:38 | 2015-04-01 22:45 | 127.1167 | 1 | 127.1167 | 127.1167 | 124.1167 | 0.00038437 | 124.1167 | 0.0003753 | 3.0238e-06 | Restore Supply on Device 2951 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792455 | fuse link 2951 2x 11kv links and 2x 15 amp hv fuses at pole 792455 caused by unknown SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED fm did work through control | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-01 | c | 0.0003753 | 3.024e-06 | 2016 | 2015-04-01 | C | 1 | 0.0003753 | 3.0238e-06
4164564 | 2015-04-02 05:30 | 2015-04-02 06:55 | 85.35 | 1 | 85.35 | 85.35 | 82.35 | 0.00025808 | 82.35 | 0.00024901 | 3.0238e-06 | Restore Supply on Device TC472 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc2671 | replace 1 x 10 amp hv fuse. cause: unknown. 1 out 3 phases. tx tc2671 not tc472 as per oms. sent e-mail to Kasey. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-02 | c | 0.00024901 | 3.024e-06 | 2016 | 2015-04-02 | C | 1 | 0.00024901 | 3.0238e-06
4164573 | 2015-04-02 06:44 | 2015-04-02 15:00 | 496.0333 | 9 | 4464.3 | 496.0333 | 493.0333 | 0.013499 | 4437.3 | 0.013417 | 2.7214e-05 | Restore Supply on Device 2727T | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 708746 | Faultman found Fuses 5369 blown line was patrolled and a branch was found over the line at pole 708746, branch was removed with hot line sticks. 2 x 6 Amp HV fuses replaced. Chris Katene attended. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-02 | c | 0.013417 | 2.7214e-05 | 2016 | 2015-04-02 | C | 9 | 0.013417 | 2.7214e-05
4164581 | 2015-04-02 07:10 | 2015-04-02 09:02 | 111.9333 | 1 | 111.9333 | 111.9333 | 108.9333 | 0.00033846 | 108.9333 | 0.00032939 | 3.0238e-06 | Restore Supply on Device T9/292 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | Fuses V83 reload and relivened. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-02 | c | 0.00032939 | 3.024e-06 | 2016 | 2015-04-02 | C | 1 | 0.00032939 | 3.0238e-06
4164607 | 2015-04-02 07:44 | 2015-04-02 09:42 | 117.2167 | 1 | 117.2167 | 117.2167 | 114.2167 | 0.00035444 | 114.2167 | 0.00034536 | 3.0238e-06 | Restore Supply on Device TC673 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | FP935 | replaced x 2 - 6amp HV TX fuses cause by ducks - at Fuse # FP935 No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-04-02 | c | 0.00034536 | 3.024e-06 | 2016 | 2015-04-02 | C | 1 | 0.00034536 | 3.0238e-06
4164844 | 2015-05-05 08:45 | 2015-05-05 15:46 | 420.6833 | 34 | 14303.2333 | 420.6833 | 417.6833 | 0.04325 | 14201.2333 | 0.042941 | 0.00010281 | NAPA ID:08127 TP_GREYTOWN GXP > FEATHERSTON SUB > WAITE ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 814704 | TRANSFORMER REPLACEMENT. Works location: SH2 FItzherbert Street. WO 10160117 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.021471 | 5.1404e-05 | 2016 | 2015-05-05 | B | 34 | 0.042941 | 0.00010281
4164852 | 2015-04-22 10:03 | 2015-04-22 11:40 | 97.3 | 4 | 389.2 | 97.3 | 94.3 | 0.0011768 | 377.2 | 0.0011406 | 1.2095e-05 | NAPA ID:08359 TP_STRATFORD GXP > CARDIFF SUB > CARDIFF RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/G 8837 | Replace lightning arrestors at Stratford ski field. Works location: Stratford Ski Field. WO 10156508. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-04-22 | b | 0.00057028 | 6.048e-06 | 2016 | 2015-04-22 | B | 4 | 0.0011406 | 1.2095e-05
4166116 | 2015-04-28 10:31 | 2015-04-28 15:33 | 301.5333 | 22 | 6633.7333 | 301.5333 | 298.5333 | 0.020059 | 6567.7333 | 0.019859 | 6.6523e-05 | NAPA ID:07421 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 919 | Project number IR6978 Rangikura Reconstruction Replace 5 poles 771673 to pole 771666. Works location: Rangikura Road. WO IR6978. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-04-28 | b | 0.0099296 | 3.3261e-05 | 2016 | 2015-04-28 | B | 22 | 0.019859 | 6.6523e-05
4166123 | 2015-05-08 09:00 | 2015-05-08 14:54 | 354 | 6 | 2124 | 354 | 351 | 0.0064225 | 2106 | 0.006368 | 1.8143e-05 | NAPA ID:07425 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 2952 | Project number IR6978 Rangikura Reconstruction Replace 5 poles 771662 to 371227 Peat Road. Works location: Peat Rd. WO IR6978. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-08 | b | 0.003184 | 9.071e-06 | 2016 | 2015-05-08 | B | 6 | 0.006368 | 1.8143e-05
4166131 | 2015-05-11 09:45 | 2015-05-11 14:08 | 263 | 6 | 1578 | 263 | 260 | 0.0047715 | 1560 | 0.0047171 | 1.8143e-05 | NAPA ID:07456 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 2952 | Project number IR6978 Rangikura Reconstruction Replace poles 771654 to 771650 Peat Road. Works location: Peat Rd WO IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-11 | b | 0.0023585 | 9.071e-06 | 2016 | 2015-05-11 | B | 6 | 0.0047171 | 1.8143e-05
4166135 | 2015-05-18 09:00 | 2015-05-18 15:12 | 372 | 6 | 2232 | 372 | 369 | 0.006749 | 2214 | 0.0066946 | 1.8143e-05 | NAPA ID:07457 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 2952 | Project number IR6978 Rangikura Reconstruction Replace poles 771654 to 771650 Peat Road. Works location: Peat Rd WO IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-18 | b | 0.0033473 | 9.071e-06 | 2016 | 2015-05-18 | B | 6 | 0.0066946 | 1.8143e-05
4166148 | 2015-05-20 09:19 | 2015-05-20 15:23 | 363.8333 | 6 | 2183 | 363.8333 | 360.8333 | 0.0066009 | 2165 | 0.0065464 | 1.8143e-05 | NAPA ID:07460 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 2952 | Project number IR6978 Rangikura Reconstruction Run wire poles 771664 to 771645. Works location: Peat Rd. WO IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-20 | b | 0.0032732 | 9.071e-06 | 2016 | 2015-05-20 | B | 6 | 0.0065464 | 1.8143e-05
4166879 | 2015-04-09 08:30 | 2015-04-09 09:55 | 85.1167 | 5 | 425.5833 | 85.1167 | 82.1167 | 0.0012869 | 410.5833 | 0.0012415 | 1.5119e-05 | NAPA ID:08404 TP_MT MAUNGANUI 33 GXP > TRITON SUB > WHARF | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G SC4-605 | Maintanence on TX and clean out Sub. Works location: Port of Tauranga Sub 2. WO 10177791 | F1 | WHARF | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-09 | b | 0.00062075 | 7.559e-06 | 2016 | 2015-04-09 | B | 5 | 0.0012415 | 1.5119e-05
4166947 | 2015-05-06 09:01 | 2015-05-06 12:47 | 226.15 | 98 | 22162.7 | 226.15 | 223.15 | 0.067015 | 21868.7 | 0.066126 | 0.00029633 | NAPA ID:08166 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV M76 | Cutting tree around the 11kV. Works location; Lees Rd Feilding. PPPD 53628 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.033063 | 0.00014816 | 2016 | 2015-05-06 | B | 98 | 0.066126 | 0.00029633
4167460 | 2015-04-03 10:10 | 2015-04-03 17:34 | 443.7833 | 24 | 10637.8667 | 443.2444 | 440.2444 | 0.032166 | 10565.8667 | 0.031949 | 7.257e-05 | Restore Supply on Device TC4449 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4449 | f/m suspects blown tx requesting Don Masters to attend to check - blue phase is gone and oil all over door. 8.53am blown ht fuse inside - black oil leaking from tx. will isolate tx through control - this tx was only replaced a couple of months ago. Transf | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-04-03 | c | 0.031949 | 7.257e-05 | 2016 | 2015-04-03 | C | 24 | 0.031949 | 7.257e-05
4167465 | 2015-04-03 07:34 | 2015-04-03 09:08 | 93.4 | 18 | 1681.2 | 93.4 | 90.4 | 0.0050835 | 1627.2 | 0.0049203 | 5.4428e-05 | Restore Supply on Device T9/292 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | 2 HT Fuses tripped at V83. reloaded / relivened OK. (2 * 10A). Suspect bird strike - many geese and ducks in area | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-03 | c | 0.0049203 | 5.4428e-05 | 2016 | 2015-04-03 | C | 18 | 0.0049203 | 5.4428e-05
4167735 | 2015-04-03 21:39 | 2015-04-03 22:20 | 41 | 28 | 1148 | 41 | 38 | 0.0034713 | 1064 | 0.0032173 | 8.4665e-05 | Restore Supply on Device T34 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/366 | 2R requested, HV jumper to be replaced, shut down required. Used 1 M Conductor 2 X Line Taps | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-04-03 | c | 0.0032173 | 8.4665e-05 | 2016 | 2015-04-03 | C | 28 | 0.0032173 | 8.4665e-05
4168255 | 2015-04-04 07:29 | 2015-04-04 09:15 | 106.1833 | 18 | 1911.3 | 106.1833 | 103.1833 | 0.0057793 | 1857.3 | 0.005616 | 5.4428e-05 | Restore Supply on Device T9/292 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | Tripping on 2 HT Fuses at V83. Ongoing bird problem with ducks and Geese in area. Reloaded / relivened OK (2 X 10A). T Pocock attended. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.005616 | 5.4428e-05 | 2016 | 2015-04-04 | C | 18 | 0.005616 | 5.4428e-05
4168257 | 2015-04-04 07:34 | 2015-04-04 10:06 | 151.7333 | 115 | 10695.6167 | 93.0054 | 90.0054 | 0.032341 | 10350.6167 | 0.031298 | 0.00034773 | Restore Supply on Device 564 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 810080 | Tripping on reloser CB564 on Phase A, O/C, E/F. Feeder patrolled / sectionalised with a line found down on Mangmahoe Rd. Isolation required from fuses 997. Conductor resleeved / rehung OK. Suspect bird strike with duck pond nearby. Gary Fisher and Karl Ro | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.031298 | 0.00034773 | 2016 | 2015-04-04 | C | 115 | 0.031298 | 0.00034773
4168432 | 2015-04-04 09:44 | 2015-04-04 11:32 | 108.3 | 1 | 108.3 | 108.3 | 105.3 | 0.00032747 | 105.3 | 0.0003184 | 3.0238e-06 | Restore Supply on Device 7762 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 826953 | Outage required from Fuses 7762 to replace a broken pole (Aged equipment). Pole and cross arm replaced along with all hardware. (Single phase 11kV). Relivened. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.0003184 | 3.024e-06 | 2016 | 2015-04-04 | C | 1 | 0.0003184 | 3.0238e-06
4168753 | 2015-04-04 13:07 | 2015-04-04 14:40 | 93 | 39 | 3627 | 93 | 90 | 0.010967 | 3510 | 0.010613 | 0.00011793 | Restore Supply on Device 6119 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3425 | Outage required on Hunter rd between ABS 6005 and 6119 to repair a burnt DDO fus at Transformer 3425T. (Backfeed at ABS 5961. Full set of fuse holders replaced / relivened. Job was child to 4168469 - did not close off | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.010613 | 0.00011793 | 2016 | 2015-04-04 | C | 39 | 0.010613 | 0.00011793
4171027 | 2015-04-04 14:32 | 2015-04-04 15:33 | 61.0833 | 1 | 61.0833 | 61.0833 | 58.0833 | 0.0001847 | 58.0833 | 0.00017563 | 3.0238e-06 | Restore Supply on Device T7/426 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 6 sedcole st, pahiatua | 6 Sedcole Street, Pahiatua Branch across HV lines. 2.38pm - taken to control. Suspect this was cause of earlier auto-reclose. Branch removed OK by Trevor (NDR 19191) - no loss of supply. | F2 | PAHIATUA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.00017563 | 3.024e-06 | 2016 | 2015-04-04 | C | 1 | 0.00017563 | 3.0238e-06
4171053 | 2015-04-04 15:21 | 2015-04-04 15:36 | 14.95 | 115 | 1719.25 | 14.95 | 11.95 | 0.0051986 | 1374.25 | 0.0041554 | 0.00034773 | Restore Supply on Device 564 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N/A - NOT APPLICABLE | CB 564 tripped on Phase A-C O/C. Ongoing bird problems - reclosed OK and faultman called off job. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.0041554 | 0.00034773 | 2016 | 2015-04-04 | C | 115 | 0.0041554 | 0.00034773
4171188 | 2015-04-04 16:03 | 2015-04-04 16:56 | 53.0667 | 1 | 53.0667 | 53.0667 | 50.0667 | 0.00016046 | 50.0667 | 0.00015139 | 3.0238e-06 | Restore Supply on Device T1793 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7261 | tHIS IS PART OF oms 147170 - NO LOSS OF SUPPLY, BROKEN JUMPER REPAIRED LIVELINE AT 7261 fUSES | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0.00015139 | 3.024e-06 | 2016 | 2015-04-04 | C | 1 | 0.00015139 | 3.0238e-06
4171321 | 2015-04-04 19:01 | 2015-04-04 19:03 | 2 | 599 | 1198 | 2 | -1 | 0.0036225 | 0 | 0 | 0.0018112 | Restore Supply on Device C928 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS S533 | Put Temp Jumper on ABS S533 Jason will Defect This ABS | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-04-04 | c | 0 | 0.0018112 | 2016 | 2015-04-04 | C | 599 | 0 | 0.0018112
4172103 | 2015-04-05 02:14 | 2015-04-05 08:31 | 376.95 | 991 | 130068.3 | 131.2495 | 128.2495 | 0.3933 | 127095.3 | 0.38431 | 0.0029965 | Restore Supply on Device S41 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 732809 | 1 x 11mtr pole 3HV Insulators HV crossarm. LV crossarms 5 LV Insulators 20mtrs 75mm copper conductor, crimp sleeves. Paul Fitzpatrick and Jade Williams attended. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-04-05 | c | 0.38431 | 0.0029965 | 2016 | 2015-04-05 | C | 991 | 0.38431 | 0.0029965
4173750 | 2015-04-05 10:43 | 2015-04-05 12:21 | 98.15 | 1 | 98.15 | 98.15 | 95.15 | 0.00029678 | 95.15 | 0.00028771 | 3.0238e-06 | Restore Supply on Device TC1592 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TC1927 | Transformer TC1927 1 x 2Amp 11kV Fuse blown suspect bird strike due to feathers below transformer | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-05 | c | 0.00028771 | 3.024e-06 | 2016 | 2015-04-05 | C | 1 | 0.00028771 | 3.0238e-06
4174642 | 2015-04-05 16:31 | 2015-04-05 20:56 | 264.8 | 1182 | 208362.0167 | 176.2792 | 173.2792 | 0.63004 | 204816.0167 | 0.61931 | 0.0035741 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 800726, 800724 | Tripping on Arahina CB7 due to Car V Pole on Skerman St Marton. (Fire Comms Event # F1820930). Isolation required between ABS 1381 and 211 with backfeed at ABS467. 3 conductors repaired with 15 metres of 16mm and 6 sleeves. Relivened OK. 2 Poles were dama | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-04-05 | c | 0.61931 | 0.0035741 | 2016 | 2015-04-05 | C | 1182 | 0.61931 | 0.0035741
4176248 | 2015-04-06 07:57 | 2015-04-06 10:08 | 130.65 | 26 | 3396.9 | 130.65 | 127.65 | 0.010271 | 3318.9 | 0.010036 | 7.8618e-05 | Restore Supply on Device CA454 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CA454 | Advised hub to send faultman to fuses CA454. 2 X HV Fuses Replaced. Bird Strike at Pole 424845. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-04-06 | c | 0.010036 | 7.8618e-05 | 2016 | 2015-04-06 | C | 26 | 0.010036 | 7.8618e-05
4176368 | 2015-04-06 11:11 | 2015-04-06 12:22 | 71.2 | 156 | 9810 | 62.8846 | 59.8846 | 0.029663 | 9342 | 0.028248 | 0.00047171 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9274/2 | Recloser 9274/2 has tripped - 2 x 1 r requested for line patrol/sectionalising. Line sectionalised & patrolled - no apparent fault found - all supply restored at 12:22 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-06 | c | 0.028248 | 0.00047171 | 2016 | 2015-04-06 | C | 156 | 0.028248 | 0.00047171
4176947 | 2015-04-06 13:12 | 2015-04-06 15:03 | 111.45 | 79 | 8804.55 | 111.45 | 108.45 | 0.026623 | 8567.55 | 0.025906 | 0.00023888 | Restore Supply on Device TC4-208 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4-208 | Burnt HV fuse barrel replaced | F3 | TAWA ST | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-06 | c | 0.025906 | 0.00023888 | 2016 | 2015-04-06 | C | 79 | 0.025906 | 0.00023888
4177096 | 2015-04-06 19:13 | 2015-04-06 20:23 | 70.0833 | 1 | 70.0833 | 70.0833 | 67.0833 | 0.00021192 | 67.0833 | 0.00020284 | 3.0238e-06 | Restore Supply on Device T3/49 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | M83 | 2 HT Fuses found tripped at M83. Reloaded, relivened with 2 X 6A. Suspect bird strike | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-06 | c | 0.00020284 | 3.024e-06 | 2016 | 2015-04-06 | C | 1 | 0.00020284 | 3.0238e-06
4177216 | 2015-04-07 08:33 | 2015-04-07 08:35 | 1.8333 | 151 | 276.8333 | 1.8333 | -1.1667 | 0.00083708 | 0 | 0 | 0.00045659 | Electric Job | 11 | Unplanned | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 9779 | at 08:33 Lake Rd Sub, CB 5 Bucklands Rd Feeder. Accidental tripping occured at Recloser 9779 when faultman was trying to reset Flags at recloser. Approximately 2 minute outage occured. All Power Restored on completion. Safety Manager: 461355. Reset EF Fla | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-04-07 | c | 0 | 0.00045659 | 2016 | 2015-04-07 | C | 151 | 0 | 0.00045659
4177274 | 2015-04-07 07:41 | 2015-04-07 09:05 | 84.1167 | 1 | 84.1167 | 84.1167 | 81.1167 | 0.00025435 | 81.1167 | 0.00024528 | 3.0238e-06 | Restore Supply on Device Z151 | 22 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 805319 | Sewerage Treatment Pond. Wayne has advised that 2 power fuses have gone and need replacing urgently as he does not know how long they have been out for and no machines are working. Wayne has also advised that Sewerage has started to go into the creek. Adv | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-04-07 | c | 0.00024528 | 3.024e-06 | 2016 | 2015-04-07 | C | 1 | 0.00024528 | 3.0238e-06
4178552 | 2015-04-07 10:57 | 2015-04-07 18:50 | 473.0167 | 32 | 14339.8167 | 448.1193 | 445.1193 | 0.04336 | 14243.8167 | 0.04307 | 9.676e-05 | Restore Supply on Device TE7-072 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FP132 | 10.19 advised talia at hub. fire require eta 09486 7948. used closest icp. 10:35am - Hub advised Ginny ETA 20mins Advised Tui at fire ETA 20mins. Josh will remain on site - Clint leaving site. HV spreader Cross arm has been replaced. Still carrying out | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-07 | c | 0.04307 | 9.676e-05 | 2016 | 2015-04-07 | C | 32 | 0.04307 | 9.676e-05
4178963 | 2015-04-07 15:56 | 2015-04-07 17:10 | 74 | 137 | 10138 | 74 | 71 | 0.030655 | 9727 | 0.029412 | 0.00041426 | Restore Supply on Device 3293T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3293T | at 15:56 Kaponga Sub, CB T11 Duthie Rd Feeder. Found Broken DDO's at Transformer 3293T that needed replacing. Isolated Lines at ABS 5685, T13 & Links T12. Backfeed supplied from KAA T41, ABS 6069 Closed. Permit issued & repairs carried out. All Power Rest | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-04-07 | c | 0.029412 | 0.00041425 | 2016 | 2015-04-07 | C | 137 | 0.029412 | 0.00041426
4179033 | 2015-04-25 05:00 | 2015-04-25 06:29 | 89.2 | 24 | 2140.8 | 89.2 | 86.2 | 0.0064733 | 2068.8 | 0.0062556 | 7.257e-05 | NAPA ID:08331 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/588 | Repair Cable crutch @ Tx T6/588 (Tracking & Electrical Discharge). Works location: Tremain Ave, Palmerston North. WO 10149593. | F1 | RUAHINE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-04-25 | b | 0.0031278 | 3.6285e-05 | 2016 | 2015-04-25 | B | 24 | 0.0062556 | 7.257e-05
4179043 | 2015-04-23 09:30 | 2015-04-23 13:49 | 259 | 45 | 11655 | 259 | 256 | 0.035242 | 11520 | 0.034834 | 0.00013607 | NAPA ID:07982 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 1010 | We are switching the existing overhead transformer to a ground mount. The transformer will remain the same number 1010 but the Fuse number at the pole will be 12074. Works location: Wairau Road. WO 10149658. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-23 | b | 0.017417 | 6.8035e-05 | 2016 | 2015-04-23 | B | 45 | 0.034834 | 0.00013607
4179195 | 2015-04-07 15:01 | 2015-04-07 20:13 | 312.2833 | 135 | 22126.6167 | 163.9009 | 160.9009 | 0.066906 | 21721.6167 | 0.065681 | 0.00040821 | Restore Supply on Device RP10 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 223437 | Recloser RP10 tripped to L/O - O/C & E/F flags - blown jumper on lightning arrestor located on pole 223256. This was isolated at ABS SE5-279 & links IP563 & repaired. Recloser RP10 tripped again on completion of repairs & relivening. Blown jumper was pos | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-07 | c | 0.065681 | 0.00040821 | 2016 | 2015-04-07 | C | 135 | 0.065681 | 0.00040821
4179349 | 2015-04-28 09:22 | 2015-04-28 10:23 | 60.6 | 68 | 4120.8 | 60.6 | 57.6 | 0.01246 | 3916.8 | 0.011843 | 0.00020562 | NAPA ID:08154 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 2646 | Open cable jumper at TC3781 A toward ABS 2646 for shutdown on the 29th April using Napa 6713. Works location: Bent Street, Putaruru. WO IR6899. | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-28 | b | 0.0059217 | 0.00010281 | 2016 | 2015-04-28 | B | 68 | 0.011843 | 0.00020562
4179512 | 2015-04-07 16:23 | 2015-04-07 17:46 | 83.7833 | 1 | 83.7833 | 83.7833 | 80.7833 | 0.00025334 | 80.7833 | 0.00024427 | 3.0238e-06 | Restore Supply on Device 4682T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3293T | 4.30pm spoke with Control and David confirmed that this customer will be part of feeder fault job OMS 4179365. 5.41pm - Mavis advise her power is back on. was part of oms 4179365 with parent job 4178963. sent e-mail to Kasey Chadwick/Rochelle Vincent and | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-04-07 | c | 0.00024427 | 3.024e-06 | 2016 | 2015-04-07 | C | 1 | 0.00024427 | 3.0238e-06
4179750 | 2015-04-07 17:03 | 2015-04-07 17:06 | 3.05 | 68 | 207.4 | 3.05 | 0.05 | 0.00062713 | 0 | 0 | 0.00020562 | Restore Supply on Device RP10 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RP10 | Recloser RP10 tripped to L/O - O/C & E/F flags - blown jumper on lightning arrestor located on pole 223256. This was isolated at ABS SE5-279 & links IP563 & repaired. Recloser RP10 tripped again on completion of repairs & relivening. Blown jumper was pos | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-07 | c | 0 | 0.00020562 | 2016 | 2015-04-07 | C | 68 | 0 | 0.00020562
4180776 | 2015-04-07 16:43 | 2015-04-07 20:42 | 239.0833 | 5 | 1195.4167 | 239.0833 | 236.0833 | 0.0036147 | 1180.4167 | 0.0035693 | 1.5119e-05 | Restore Supply on Device 1416W | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1416W | 4.43pm advised Tans at svs hub of job Transformer X57 Replaced Isolated at DDO's for Transformer. See OMS 4179523 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-07 | c | 0.0035693 | 1.5119e-05 | 2016 | 2015-04-07 | C | 5 | 0.0035693 | 1.5119e-05
4180785 | 2015-04-07 21:18 | 2015-04-07 22:48 | 90.3167 | 8 | 722.5333 | 90.3167 | 87.3167 | 0.0021848 | 698.5333 | 0.0021122 | 2.419e-05 | Restore Supply on Device 7236 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7236 | 2 Fuses found Blown at Fuses 7236 - Area known to have bird strikes - Fuses reloaded - used 2 X 10amp HV fuses | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-04-07 | c | 0.0021122 | 2.419e-05 | 2016 | 2015-04-07 | C | 8 | 0.0021122 | 2.419e-05
4180825 | 2015-04-08 09:50 | 2015-04-08 12:44 | 174.4 | 5 | 872 | 174.4 | 171.4 | 0.0026367 | 857 | 0.0025914 | 1.5119e-05 | Restore Supply on Device TC3588 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12362 | 2R requested as, part power to Transformer caused by fault at N12362, links 2189. Broken lead on HV line, Fault to be fixed live line. Don leaving site as it is safe until live line crew arrive. Temp fix to reconnect loose jumper. F/man submitting amber 1 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-08 | c | 0.0025914 | 1.5119e-05 | 2016 | 2015-04-08 | C | 5 | 0.0025914 | 1.5119e-05
4181177 | 2015-05-05 11:35 | 2015-05-05 15:52 | 256.7167 | 26 | 6674.6333 | 256.7167 | 253.7167 | 0.020182 | 6596.6333 | 0.019947 | 7.8618e-05 | NAPA ID:08364 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV S11 | tree cutting. Works location: Clarkes Rd Eketahuna. PPPD 43405 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.0099733 | 3.9309e-05 | 2016 | 2015-05-05 | B | 26 | 0.019947 | 7.8618e-05
4181186 | 2015-04-08 09:18 | 2015-04-08 13:21 | 242.3167 | 60 | 14539 | 242.3167 | 239.3167 | 0.043962 | 14359 | 0.043418 | 0.00018143 | Restore Supply on Device 5400 | 6.6 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2710T | at 10:55 Motukawa CB H11 Ratapiko Feeder. 3x Broken DDO's found at Transformer 2710T. Isolated lines at Fused ABS 5400. Permit issued & repairs carried out. All Power Restored on completion. Jade Williams Attended. 3x Connectors Used, 3x DDO Fuse Carriers | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.043418 | 0.00018143 | 2016 | 2015-04-08 | C | 60 | 0.043418 | 0.00018143
4182034 | 2015-04-29 09:00 | 2015-04-29 15:21 | 381 | 99 | 37719 | 381 | 378 | 0.11405 | 37422 | 0.11316 | 0.00029935 | NAPA ID:06713 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3781 | Replace 11kv and 400 v cross arms and associated equipment From ABS TEMP42 to both side of ABS 2646 . We will be opening the jumper at TC3781 A on Napa 8153 and close the jumper on Napa 8154. Works location: Reservoir St Putaruru. WO IR6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-29 | b | 0.056578 | 0.00014968 | 2016 | 2015-04-29 | B | 99 | 0.11316 | 0.00029935
4182386 | 2015-05-01 09:05 | 2015-05-01 09:55 | 50.0333 | 68 | 3402.2667 | 50.0333 | 47.0333 | 0.010288 | 3198.2667 | 0.0096708 | 0.00020562 | NAPA ID:08153 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2646 | Close 11Kv cable jumper at TC3781 A after the shutdown on the 29th April on Napa 6713. Works location: Bent St Putaruru. WO IR6899 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.0048354 | 0.00010281 | 2016 | 2015-05-01 | B | 68 | 0.0096708 | 0.00020562
4182392 | 2015-04-08 12:15 | 2015-04-08 15:10 | 175.0333 | 1 | 175.0333 | 175.0333 | 172.0333 | 0.00052926 | 172.0333 | 0.00052019 | 3.0238e-06 | Restore Supply on Device T2013 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2013 | Replaced 2 X HV fuses. Control signed job off but could not close job. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.00052019 | 3.024e-06 | 2016 | 2015-04-08 | C | 1 | 0.00052019 | 3.0238e-06
4190764 | 2015-04-29 09:45 | 2015-04-29 14:51 | 305.55 | 18 | 5499.9 | 305.55 | 302.55 | 0.01663 | 5445.9 | 0.016467 | 5.4428e-05 | NAPA ID:06997 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole I0115 | Install new 30-11-1 transformer at pole I0115. Works location: Mangateparu Loop Rd. WO 30003292 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-04-29 | b | 0.0082335 | 2.7214e-05 | 2016 | 2015-04-29 | B | 18 | 0.016467 | 5.4428e-05
4191020 | 2015-04-08 14:17 | 2015-04-08 19:45 | 328.0167 | 121 | 21472.2667 | 177.4567 | 174.4567 | 0.064927 | 21109.2667 | 0.063829 | 0.00036588 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P01093 | RS V27 Tripped B Ph, E/F - Bird found on line at Pole P01093 during sectionlising - Isolated at Fuses V43 - Bird cleared using hot sticks | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.063829 | 0.00036587 | 2016 | 2015-04-08 | C | 121 | 0.063829 | 0.00036588
4191831 | 2015-04-08 15:05 | 2015-04-08 16:41 | 96.0333 | 1 | 96.0333 | 96.0333 | 93.0333 | 0.00029038 | 93.0333 | 0.00028131 | 3.0238e-06 | Restore Supply on Device T4/181 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | p45550 | broken staywire on 11 kv pole. pole # P45550. cause: deterioration. Follow-up job: oms 4194148. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.00028131 | 3.024e-06 | 2016 | 2015-04-08 | C | 1 | 0.00028131 | 3.0238e-06
4192449 | 2015-04-08 16:04 | 2015-04-08 18:01 | 116.3 | 211 | 22263.0333 | 105.512 | 102.512 | 0.067318 | 21630.0333 | 0.065404 | 0.00063801 | Restore Supply on Device 2 | 22 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4137 | Line sectionalised and patrolled with no apparent cause found | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.065404 | 0.00063801 | 2016 | 2015-04-08 | C | 211 | 0.065404 | 0.00063801
4194018 | 2015-04-08 16:09 | 2015-04-08 17:41 | 91.3667 | 211 | 5220.8667 | 24.7434 | 21.7434 | 0.015787 | 4587.8667 | 0.013873 | 0.00063801 | Restore Supply on Device X1535 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB7 | CB7 ARC and tripped. Line patrolled and no fault found. Wind and heavy rain at the time. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.013873 | 0.00063801 | 2016 | 2015-04-08 | C | 211 | 0.013873 | 0.00063801
4194512 | 2015-04-08 19:55 | 2015-04-08 22:33 | 158.35 | 829 | 43554.35 | 52.5384 | 49.5384 | 0.1317 | 41067.35 | 0.12418 | 0.0025067 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742125 | CB 2 tripped O/C, E/F - Lines on fire reported by Public - Isolated at ABS's 443 & 6505 with a back feed via ABS 445 - Replaced full cross arm at Pole 742125 - used 1 complete HV Cross Arm | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.12418 | 0.0025067 | 2016 | 2015-04-08 | C | 829 | 0.12418 | 0.0025067
4196583 | 2015-04-08 22:42 | 2015-04-09 03:47 | 305.5833 | 364 | 25489.95 | 70.0273 | 67.0273 | 0.077076 | 24397.95 | 0.073774 | 0.0011006 | Restore Supply on Device WH2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 729785 | Broken Insulator found at Pole 729785 during sectionalising - Isolated at Fuses WH295 - used 1x HV insulator | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-08 | c | 0.073774 | 0.0011006 | 2016 | 2015-04-08 | C | 364 | 0.073774 | 0.0011006
4198654 | 2015-04-09 06:12 | 2015-04-09 08:26 | 134 | 716 | 43974.9667 | 61.4176 | 58.4176 | 0.13297 | 41826.9667 | 0.12647 | 0.002165 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 | Patrolled nothing Found Had trouble closing CB5 so Back feed till it was fixed Shazil khan fixed. This has been sent to OSI to amend times as we are unable to | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.12647 | 0.002165 | 2016 | 2015-04-09 | C | 716 | 0.12647 | 0.002165
4199394 | 2015-04-09 08:40 | 2015-04-09 09:39 | 59 | 1 | 56 | 56 | 53 | 0.00016933 | 53 | 0.00016026 | 3.0238e-06 | Restore Supply on Device X1038 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Links 133 | 2x HT fuse link 133. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.00016026 | 3.024e-06 | 2016 | 2015-04-09 | C | 1 | 0.00016026 | 3.0238e-06
4199408 | 2015-05-01 09:42 | 2015-05-01 11:01 | 78.3667 | 22 | 1724.0667 | 78.3667 | 75.3667 | 0.0052132 | 1658.0667 | 0.0050136 | 6.6523e-05 | NAPA ID:08096 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses LI732 | Replace Hv Xarm and Hv fuse arm and HV fuses at TX L1412, pole 728006. Works location: Lower Ball Rd Patea. WO 10160359 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-01 | b | 0.0025068 | 3.3261e-05 | 2016 | 2015-05-01 | B | 22 | 0.0050136 | 6.6523e-05
4199415 | 2015-04-09 07:48 | 2015-04-09 14:43 | 414.2667 | 1 | 414.2667 | 414.2667 | 411.2667 | 0.0012526 | 411.2667 | 0.0012436 | 3.0238e-06 | Restore Supply on Device P28 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t4/146 | 1.10 woody advised he has an AP and is starting work now. replaced 50 kva tx 4x 6amp hv fuses tx t4/146 fm thinks could have been damaged by lightening. SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.0012436 | 3.024e-06 | 2016 | 2015-04-09 | C | 1 | 0.0012436 | 3.0238e-06
4199438 | 2015-04-29 09:04 | 2015-04-29 15:22 | 378.0167 | 15 | 5670.25 | 378.0167 | 375.0167 | 0.017145 | 5625.25 | 0.017009 | 4.5356e-05 | NAPA ID:03779 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 248814 | To break 11kV jumpers L/line at Pole # 248814 and replace ABS IC1333 complete with termination arms. Works location: Livingstone Rd Te Poi. WO 10484459 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-29 | b | 0.0085047 | 2.2678e-05 | 2016 | 2015-04-29 | B | 15 | 0.017009 | 4.5356e-05
4200144 | 2015-04-09 08:56 | 2015-04-09 12:31 | 215.2 | 211 | 9138.3833 | 43.3099 | 40.3099 | 0.027632 | 8505.3833 | 0.025718 | 0.00063801 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 788236 | Replaced 1 X crossarm & 3 X insualtors at pole 788236 | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.025718 | 0.00063801 | 2016 | 2015-04-09 | C | 211 | 0.025718 | 0.00063801
4203253 | 2015-04-09 08:56 | 2015-04-09 09:53 | 56.9 | 1 | 56.9 | 56.9 | 53.9 | 0.00017205 | 53.9 | 0.00016298 | 3.0238e-06 | Restore Supply on Device X2831 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | fern flats road | this is the same at 4199394 as advised by glen in control no crews requested | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.00016298 | 3.024e-06 | 2016 | 2015-04-09 | C | 1 | 0.00016298 | 3.0238e-06
4216443 | 2015-04-09 12:03 | 2015-04-09 13:36 | 93.5667 | 2 | 187.1333 | 93.5667 | 90.5667 | 0.00056585 | 181.1333 | 0.0005477 | 6.0475e-06 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tx 1335 | 3x 15amp ddo fuse elements. Pole 829960. Tx 1335. Age. Full Power Restored. Nothing else repaired or replaced Adjacent assets - ok | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.0005477 | 6.048e-06 | 2016 | 2015-04-09 | C | 2 | 0.0005477 | 6.0475e-06
4219018 | 2015-05-08 08:33 | 2015-05-08 15:31 | 418.05 | 114 | 47581.8833 | 417.3849 | 414.3849 | 0.14388 | 47239.8833 | 0.14284 | 0.00034471 | NAPA ID:08124 TP_MASTERTON GXP > CHAPEL SUB > CORNWALL ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV822965 | TRANSFORMER REPLACEMENT. Works location: College St Masterton. WO 10160117 | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-05-08 | b | 0.071421 | 0.00017235 | 2016 | 2015-05-08 | B | 114 | 0.14284 | 0.00034471
4220673 | 2015-04-09 13:57 | 2015-04-09 14:28 | 31.8167 | 894 | 28131.6667 | 31.4672 | 28.4672 | 0.085063 | 25449.6667 | 0.076954 | 0.0027032 | Restore Supply on Device 10 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | 751493 | CB 10 tripped on A, B & C phase O/C flags. Received call of Car vs pole at pole 751493, line was isolated at ABS 417 & Magnefix 362/1. 1 X cable pot head replaced. 3 X Lightning arrestors. Cable covers. | F3 | BROOKLANDS 10 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.076954 | 0.0027032 | 2016 | 2015-04-09 | C | 894 | 0.076954 | 0.0027032
4222539 | 2015-05-08 09:18 | 2015-05-08 14:18 | 300 | 58 | 17400 | 300 | 297 | 0.052613 | 17226 | 0.052087 | 0.00017538 | NAPA ID:08208 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV B1 | Cutting trees around the 11 Kv. Works location: Kairanga Bunnythorpe Rd. PPPD 46737 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-08 | b | 0.026044 | 8.7689e-05 | 2016 | 2015-05-08 | B | 58 | 0.052087 | 0.00017538
4230328 | 2015-04-09 18:53 | 2015-04-09 22:12 | 199 | 237 | 36130 | 152.4473 | 149.4473 | 0.10925 | 35419 | 0.1071 | 0.00071663 | Restore Supply on Device LI1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 6718 | david fire service - power pole arcing and now no power F1823319 - eta required 04 801 0812 - advised 3 poles past Whnuakura School at 52 Kaharoa Road 7.08pm - Advised Jill at Fire Comms an ETA of 20 minutes. 7.15pm - advise smc that Grant Phillips from p | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.1071 | 0.00071663 | 2016 | 2015-04-09 | C | 237 | 0.1071 | 0.00071663
4232628 | 2015-04-09 22:16 | 2015-04-09 23:47 | 91 | 358 | 24998 | 69.8268 | 66.8268 | 0.075588 | 23924 | 0.07234 | 0.0010825 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Manaia sub | CB 5 ARC (4adv) and trip B phase O/C & E/F. Line sectionalised and supply restored with no apparent fault found . | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.07234 | 0.0010825 | 2016 | 2015-04-09 | C | 358 | 0.07234 | 0.0010825
4233927 | 2015-04-10 01:47 | 2015-04-10 03:40 | 112.3833 | 295 | 8722.4667 | 29.5677 | 26.5677 | 0.026375 | 7837.4667 | 0.023699 | 0.00089201 | Restore Supply on Device 9 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 9 | CB 9 tripped to L/O - E/F & O/C flags - 2 x 1 r requested - initial backfeed established by opening recloser RP02 & closing sectionaliser 9777/2 - line sectionalised & patrolled - no apparent fault found - all supply restored | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.023699 | 0.00089201 | 2016 | 2015-04-10 | C | 295 | 0.023699 | 0.00089201
4234922 | 2015-04-10 07:48 | 2015-04-10 08:48 | 60 | 17 | 1020 | 60 | 57 | 0.0030842 | 969 | 0.00293 | 5.1404e-05 | Restore Supply on Device TC4384 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2323 | Faultman found a blown jumper and broken insulator at Fuses 2323 on pole D12809, line was isolated at ABS's 2505 & 2629 to replace the jumper and insulator. 1 X jumper & sleeve replaced. 1 X 11KV insulator replaced. This job may be a 2 R. See OMS 4233927 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.00293 | 5.1404e-05 | 2016 | 2015-04-10 | C | 17 | 0.00293 | 5.1404e-05
4234937 | 2015-05-04 08:42 | 2015-05-04 11:50 | 188 | 3 | 564 | 188 | 185 | 0.0017054 | 555 | 0.0016782 | 9.0713e-06 | NAPA ID:08474 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/132 | Replace LV X-Arms on pole P12181 (T5/132). Existing TX to be reused. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-04 | b | 0.00083909 | 4.536e-06 | 2016 | 2015-05-04 | B | 3 | 0.0016782 | 9.0713e-06
4234984 | 2015-05-01 13:24 | 2015-05-01 15:44 | 140 | 3 | 420 | 140 | 137 | 0.00127 | 411 | 0.0012428 | 9.0713e-06 | NAPA ID:08487 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4681 | To upgrade existing 30kVa Transformer to 50kVa and replace LV cross arms. Works location: Washbourne Rd. WO 30000212 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.00062138 | 4.536e-06 | 2016 | 2015-05-01 | B | 3 | 0.0012428 | 9.0713e-06
4235238 | 2015-05-04 09:22 | 2015-05-04 11:04 | 101.45 | 1 | 101.45 | 101.45 | 98.45 | 0.00030676 | 98.45 | 0.00029769 | 3.0238e-06 | NAPA ID:08489 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole 726938 | replace pole and hardware # 726942 & 726938 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-04 | b | 0.00014884 | 1.512e-06 | 2016 | 2015-05-04 | B | 1 | 0.00029769 | 3.0238e-06
4235491 | 2015-05-11 09:25 | 2015-05-11 14:39 | 314 | 8 | 2512 | 314 | 311 | 0.0075957 | 2488 | 0.0075231 | 2.419e-05 | NAPA ID:07975 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1118 | Rewiring between poles M1228 andM12548. Works location: Wapotu Rd. WO 10134042 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-11 | b | 0.0037616 | 1.2095e-05 | 2016 | 2015-05-11 | B | 8 | 0.0075231 | 2.419e-05
4235496 | 2015-05-06 09:35 | 2015-05-06 14:15 | 280 | 1 | 280 | 280 | 277 | 0.00084665 | 277 | 0.00083758 | 3.0238e-06 | NAPA ID:08473 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | t5/214 | Replace TX and LV X-Arms on pole P13408. Existing TX T5/214 to be replaced. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.00041879 | 1.512e-06 | 2016 | 2015-05-06 | B | 1 | 0.00083758 | 3.0238e-06
4235628 | 2015-04-10 09:46 | 2015-04-10 13:20 | 214 | 6 | 1284 | 214 | 211 | 0.0038825 | 1266 | 0.0038281 | 1.8143e-05 | Restore Supply on Device FP1462 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses FP1462 | LLP. To relocate fuses FP1462 to the opposite side of the pole to improve Clearances. AP: To Change the phasing on two transformers and the spur line beyond SE7-053. Works location: Wharere Rd Te Puke. WO 10146569 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-10 | b | 0.001914 | 9.071e-06 | 2016 | 2015-04-10 | B | 6 | 0.0038281 | 1.8143e-05
4236051 | 2015-04-28 08:45 | 2015-04-28 14:37 | 351.7 | 157 | 44786.7 | 285.2656 | 282.2656 | 0.13542 | 44315.7 | 0.134 | 0.00047473 | NAPA ID:08412 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 211827 | REPLACE POLES AND ARMS AS PER SCOPE OF WORKS. Works location: Belk Road. WO 10148098. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-04-28 | b | 0.067 | 0.00023736 | 2016 | 2015-04-28 | B | 157 | 0.134 | 0.00047473
4236807 | 2015-04-09 09:54 | 2015-04-10 14:31 | 1716.6 | 713 | 39833.2167 | 55.8671 | 52.8671 | 0.12045 | 37694.2167 | 0.11398 | 0.0021559 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 717757 | CB 5 tripped on B phase O/C & E/F flags, line was sectionalised and patrolled and faultman found line down at pole 717757, line was isolated at ABS's MA191 & 6619. At time of tripping faultman carring out a sub inspection found that CB 5's spring charge m | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-04-09 | c | 0.11398 | 0.0021559 | 2016 | 2015-04-09 | C | 713 | 0.11398 | 0.0021559
4238462 | 2015-05-05 09:12 | 2015-05-05 15:50 | 398.2167 | 4 | 1592.8667 | 398.2167 | 395.2167 | 0.0048164 | 1580.8667 | 0.0047802 | 1.2095e-05 | NAPA ID:07656 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B12570 | Part 1: LLP To install L/Line breaks at Pole B0535. Part 2: LLP To Remove 11KV leads on both sides of 9916. Part 3: AP to replace pole and transfer switch 9916 to new pole. Part 4: LLP to close 11kV break at Pole #B0535. Part 5: To close 11kV break at Pol | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-05 | b | 0.0023901 | 6.048e-06 | 2016 | 2015-05-05 | B | 4 | 0.0047802 | 1.2095e-05
4238972 | 2015-05-01 09:06 | 2015-05-01 11:55 | 168.85 | 2 | 337.7 | 168.85 | 165.85 | 0.0010211 | 331.7 | 0.001003 | 6.0475e-06 | NAPA ID:08045 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE5-185 | Morning Replace Transformer TE5-185. Works location: Te Puke Quarry Rd, Te Puke. WO 10147830. | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.00050149 | 3.024e-06 | 2016 | 2015-05-01 | B | 2 | 0.001003 | 6.0475e-06
4239173 | 2015-05-01 11:56 | 2015-05-01 14:04 | 128.0333 | 1 | 128.0333 | 128.0333 | 125.0333 | 0.00038714 | 125.0333 | 0.00037807 | 3.0238e-06 | NAPA ID:08047 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE5-016 | Afternoon Replace Transformer TE5-016. Works location: Te Puke Quarry Rd, Te Puke. WO 10147830 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.00018903 | 1.512e-06 | 2016 | 2015-05-01 | B | 1 | 0.00037807 | 3.0238e-06
4239175 | 2015-04-10 11:57 | 2015-04-10 15:12 | 195.0333 | 1 | 195.0333 | 195.0333 | 192.0333 | 0.00058973 | 192.0333 | 0.00058066 | 3.0238e-06 | Restore Supply on Device X1826 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 1 X 2 AMP TX FUSE DUE TO DETERIORATION No other assets repaired or replaced Adjacent assets ok | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.00058066 | 3.024e-06 | 2016 | 2015-04-10 | C | 1 | 0.00058066 | 3.0238e-06
4239189 | 2015-05-12 09:06 | 2015-05-12 15:15 | 369.6333 | 10 | 3696.3333 | 369.6333 | 366.6333 | 0.011177 | 3666.3333 | 0.011086 | 3.0238e-05 | NAPA ID:08209 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV H108 | Cutting trees around the 11Kv. Works location: Kahuterawa Rd Linton. PPPD 46715 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-05-12 | b | 0.0055431 | 1.5119e-05 | 2016 | 2015-05-12 | B | 10 | 0.011086 | 3.0238e-05
4239318 | 2015-05-01 09:31 | 2015-05-01 13:24 | 233 | 7 | 1631 | 233 | 230 | 0.0049318 | 1610 | 0.0048683 | 2.1166e-05 | NAPA ID:08291 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > TARA RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-137 | Replace TX due to damage to the HV cable box. Works location: Tara Rd, Papamoa. WO 30002256. | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.0024341 | 1.0583e-05 | 2016 | 2015-05-01 | B | 7 | 0.0048683 | 2.1166e-05
4239326 | 2015-05-01 09:27 | 2015-05-01 14:12 | 284.5167 | 3 | 1704.05 | 568.0167 | 565.0167 | 0.0051526 | 1695.05 | 0.0051254 | 9.0713e-06 | NAPA ID:08399 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE3-103 | Install new section of 11kv cable from pole and joint to underground 11kv cables. Works location: Belk Rd Tauranga. WO 10159715. Fuse at SE3-029 blew on relivening. Cable isolated again and tested for fault. Cable tests proved numerous sheath faults on ca | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.0025627 | 4.536e-06 | 2016 | 2015-05-01 | B | 3 | 0.0051254 | 9.0713e-06
4239330 | 2015-05-01 08:37 | 2015-05-01 14:34 | 356.6667 | 3 | 1070 | 356.6667 | 353.6667 | 0.0032354 | 1061 | 0.0032082 | 9.0713e-06 | NAPA ID:08007 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1795 | Replace T/X from 15kVA to 50kVA. Replace L/V crossarms. Works location: Gerrand Rd, Paeroa. WO 10166941 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.0016041 | 4.536e-06 | 2016 | 2015-05-01 | B | 3 | 0.0032082 | 9.0713e-06
4239401 | 2015-05-06 10:28 | 2015-05-06 14:41 | 252.9833 | 65 | 16443.9167 | 252.9833 | 249.9833 | 0.049722 | 16248.9167 | 0.049133 | 0.00019654 | NAPA ID:08435 TP_OPUNAKE GXP > TASMAN SUB > IHAIA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS TA105 | Replace 3 x DNO Abs's & Xarms TA124 - TA137 & TA168. Works location: Ihaia Rd Opunake. WO 30008125 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.024566 | 9.8272e-05 | 2016 | 2015-05-06 | B | 65 | 0.049133 | 0.00019654
4239418 | 2015-05-13 08:30 | 2015-05-13 16:07 | 457 | 29 | 13253 | 457 | 454 | 0.040074 | 13166 | 0.039811 | 8.7689e-05 | NAPA ID:08131 TP_MASTERTON GXP > AWATOITOI SUB > BLAIRLOGIE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 835593 | TRANSFORMER REPLACEMENT. Works location: Blue Pacific Parade Riverdale. WO 10160117 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-05-13 | b | 0.019905 | 4.3845e-05 | 2016 | 2015-05-13 | B | 29 | 0.039811 | 8.7689e-05
4239744 | 2015-04-10 11:57 | 2015-04-10 15:32 | 214.3833 | 1 | 214.3833 | 214.3833 | 211.3833 | 0.00064824 | 211.3833 | 0.00063917 | 3.0238e-06 | Restore Supply on Device X2462 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | X2462 | Linked to OMS 4238708, Same job. No further equipment used. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.00063917 | 3.024e-06 | 2016 | 2015-04-10 | C | 1 | 0.00063917 | 3.0238e-06
4241338 | 2015-05-03 09:01 | 2015-05-03 12:57 | 236 | 45 | 10620 | 236 | 233 | 0.032112 | 10485 | 0.031704 | 0.00013607 | NAPA ID:08286 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9106 | Isolate TX so that the LV frame panel can be replaced and TX straightend. Works location: Montgomery Rd Tauranga. WO 10162245 | F2 | WAIHI RD | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-05-03 | b | 0.015852 | 6.8035e-05 | 2016 | 2015-05-03 | B | 45 | 0.031704 | 0.00013607
4241819 | 2015-05-08 09:00 | 2015-05-08 13:07 | 247 | 160 | 39520 | 247 | 244 | 0.1195 | 39040 | 0.11805 | 0.0004838 | NAPA ID:06694 TP_KINLEITH GXP > BAIRD ROAD SUB > DALMENY ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9468 | Upgrade 11kV conductor between pole B12621 & pole B0241. Works location: Billah St Tokoroa. WO: PPPD6998 | F2/F3 | DALMENY ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-08 | b | 0.059024 | 0.0002419 | 2016 | 2015-05-08 | B | 160 | 0.11805 | 0.0004838
4241822 | 2015-04-14 06:10 | 2015-04-14 07:08 | 58.3 | 50 | 2915 | 58.3 | 55.3 | 0.0088143 | 2765 | 0.0083607 | 0.00015119 | NAPA ID:08578 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11k VABS SC4-068 | Isolate 11kv Lines feeding DDO's SC4-088 and repair 11kv Term feed from DDO's SC4-088. Works location: Nikau Cres Mt Maunganui. WO 30008451 | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-04-14 | b | 0.0041803 | 7.5594e-05 | 2016 | 2015-04-14 | B | 50 | 0.0083607 | 0.00015119
4242948 | 2015-04-10 18:42 | 2015-04-10 20:57 | 135.05 | 1 | 135.05 | 135.05 | 132.05 | 0.00040836 | 132.05 | 0.00039929 | 3.0238e-06 | Restore Supply on Device TP2045 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2045 | plz check if oms 4242953 105B McAlpine Road Tatuanui and oms 4242970 - 43 McAlpine Road are related, same substation and feeder. replace 2 x 3amp ddo fuses. cause: lightning. tx tp2045. re-liven at 8.45pm. 8.56pm - FM advise DDO fuses out along the road d | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.00039929 | 3.024e-06 | 2016 | 2015-04-10 | C | 1 | 0.00039929 | 3.0238e-06
4242977 | 2015-04-10 19:17 | 2015-04-10 22:27 | 190.3 | 156 | 29627 | 189.9167 | 186.9167 | 0.089585 | 29159 | 0.08817 | 0.00047171 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222875 | Blown Insulator at Pole 222875. 1 X HV Pin Insulator. 1m Namu Conductor 2 x Namu sleeves and Binder | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.08817 | 0.00047171 | 2016 | 2015-04-10 | C | 156 | 0.08817 | 0.00047171
4243142 | 2015-04-10 19:37 | 2015-04-10 21:30 | 112.9667 | 8 | 903.7333 | 112.9667 | 109.9667 | 0.0027327 | 879.7333 | 0.0026601 | 2.419e-05 | Restore Supply on Device TC4572 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4572 | *** please check if oms 4243158 - 58 WAIKUMETE ROAD off tx tc650 is part of this outage *** Replace 3 x 3 amp HT fuses. Cause: lightning. Transformers TC4572. O14307. time: re-liven 9:30pm. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.0026601 | 2.419e-05 | 2016 | 2015-04-10 | C | 8 | 0.0026601 | 2.419e-05
4245402 | 2015-04-10 18:49 | 2015-04-10 21:15 | 146.0167 | 10 | 1460.1667 | 146.0167 | 143.0167 | 0.0044152 | 1430.1667 | 0.0043245 | 3.0238e-05 | Restore Supply on Device FC2278 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses FC2278, Transformers TC2188 & TC4916 | HV Fuses Replaced at Fuses FC2278, Transformers TC2188 & TC4916. Paul Replaced these fuses as he found them on instructions from Control Room. Lightning Strike. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.0043245 | 3.0238e-05 | 2016 | 2015-04-10 | C | 10 | 0.0043245 | 3.0238e-05
4246213 | 2015-04-10 20:59 | 2015-04-11 11:40 | 880.9167 | 209 | 49236.0333 | 235.5791 | 232.5791 | 0.14888 | 48609.0333 | 0.14698 | 0.00063197 | Restore Supply on Device NG3 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N3280 | 10.03pm - report of sparking pole on cnr SH45 and Kina Rd at the hall. 319 KINA ROAD - please check tx N3285 as customer reported tx struck by lightning and then whole house shook. 10.21pm - advise smc. Found transformer N3280 blown and requires replaceme | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.14698 | 0.00063197 | 2016 | 2015-04-10 | C | 209 | 0.14698 | 0.00063197
4246731 | 2015-04-10 21:12 | 2015-04-12 00:59 | 1667.15 | 154 | 31863.55 | 206.9062 | 203.9062 | 0.096348 | 31401.55 | 0.094951 | 0.00046566 | Restore Supply on Device NG4 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Transformers N1010 & N1020 | Cb NG4 ARC & Trip 3 phase E/F Line sectionalised and found 2 transformers N1010 & N1020 faulty and to be replaced. Work carried out during Saturday and Transformers replaced by 14:08. Lightning strikes. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.094951 | 0.00046566 | 2016 | 2015-04-10 | C | 154 | 0.094951 | 0.00046566
4246896 | 2015-04-10 22:10 | 2015-04-10 23:27 | 76.9667 | 1 | 76.9667 | 76.9667 | 73.9667 | 0.00023273 | 73.9667 | 0.00022366 | 3.0238e-06 | Restore Supply on Device 894 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8489 | Reload and close | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.00022366 | 3.024e-06 | 2016 | 2015-04-10 | C | 1 | 0.00022366 | 3.0238e-06
4246903 | 2015-04-10 19:17 | 2015-04-10 22:45 | 207.7 | 12 | 2492.4 | 207.7 | 204.7 | 0.0075364 | 2456.4 | 0.0074276 | 3.6285e-05 | Restore Supply on Device TC594 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC596 | Re-liven at 22.45pm. Transformer TC596. Replace 2 x 3 amp HT Fuses. Cause: lightning. Tested voltages: 420 volts between phases and 229-230V for phase to earth. | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.0074276 | 3.6285e-05 | 2016 | 2015-04-10 | C | 12 | 0.0074276 | 3.6285e-05
4247184 | 2015-04-10 23:45 | 2015-04-11 00:41 | 55.7667 | 31 | 1728.7667 | 55.7667 | 52.7667 | 0.0052274 | 1635.7667 | 0.0049462 | 9.3737e-05 | Restore Supply on Device FP1438 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O14242 | Jumper blown off at Pole O14242. Lightning. Reattached. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-10 | c | 0.0049462 | 9.3737e-05 | 2016 | 2015-04-10 | C | 31 | 0.0049462 | 9.3737e-05
4247394 | 2015-04-11 04:49 | 2015-04-11 05:40 | 50.8667 | 62 | 3153.7333 | 50.8667 | 47.8667 | 0.0095361 | 2967.7333 | 0.0089737 | 0.00018747 | Electric Job | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T3100 | Faultman found fuses blown . Checked transformer and established it needs to be replaced Transformer T23100 replaced | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.0089737 | 0.00018747 | 2016 | 2015-04-11 | C | 62 | 0.0089737 | 0.00018747
4247980 | 2015-04-11 05:49 | 2015-04-11 09:56 | 246.35 | 5 | 1231.75 | 246.35 | 243.35 | 0.0037245 | 1216.75 | 0.0036792 | 1.5119e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | SH2 at Domain Off Ramp, Papamoa | Report from Police that there are Lines Down. Event # P020834918. Car V Pole Pole # 382261. ( TMA 5 ) Isolation at Fuses FP 1411 ( spur line ) transformer TD5 070 affected, pole replaced all service restored, re sag line. NDR No 51851. Materials 1 x pole, | F4 | BRUCE RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-04-11 | c | 0.0036792 | 1.5119e-05 | 2016 | 2015-04-11 | C | 5 | 0.0036792 | 1.5119e-05
4248012 | 2015-04-11 06:39 | 2015-04-11 09:30 | 171.4667 | 1 | 171.4667 | 171.4667 | 168.4667 | 0.00051847 | 168.4667 | 0.0005094 | 3.0238e-06 | Restore Supply on Device X4016 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1135 | 2 x hv oh 8 amp pole x4016 worked through links 2709 due to birds. Reloaded / relivened OK. SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.0005094 | 3.024e-06 | 2016 | 2015-04-11 | C | 1 | 0.0005094 | 3.0238e-06
4248024 | 2015-04-11 07:41 | 2015-04-11 08:46 | 64.85 | 3 | 194.55 | 64.85 | 61.85 | 0.00058827 | 185.55 | 0.00056106 | 9.0713e-06 | Restore Supply on Device X1534 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x1534 | 3x 3amp 11kv tx fuse due lightning strike at x 1534 pole 849144 hv oh will advise control SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED . 3 HT Fuses found tripped at X1534 - reloaded / relivened OK (3A). Lightning strike. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00056106 | 9.071e-06 | 2016 | 2015-04-11 | C | 3 | 0.00056106 | 9.0713e-06
4248048 | 2015-04-11 08:06 | 2015-04-11 12:29 | 262.9 | 5 | 1267.85 | 253.57 | 250.57 | 0.0038337 | 1252.85 | 0.0037883 | 1.5119e-05 | Restore Supply on Device 3371T | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3317T | 3 HT fuses found tripped at X3317T - Reloaded / relivened OK. (3 3A). Lightning strike. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.0037883 | 1.5119e-05 | 2016 | 2015-04-11 | C | 5 | 0.0037883 | 1.5119e-05
4248061 | 2015-04-11 08:15 | 2015-04-11 15:18 | 423 | 1 | 423 | 423 | 420 | 0.0012791 | 420 | 0.00127 | 3.0238e-06 | Restore Supply on Device X79 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2709 | 3.10 phoned customer on cell no reply steve is confident this is the same as 4248012. "2 x hv oh 8 amp pole X4016 worked through control links 2709 due to birds. Reloaded / relivened OK." | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00127 | 3.024e-06 | 2016 | 2015-04-11 | C | 1 | 0.00127 | 3.0238e-06
4248167 | 2015-04-11 09:47 | 2015-04-11 13:42 | 234.8667 | 3 | 704.6 | 234.8667 | 231.8667 | 0.0021305 | 695.6 | 0.0021033 | 9.0713e-06 | Restore Supply on Device 2236T | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2236T | 3 HT fuses found tripped at Transformer 3367T - OMS job reads as 2236T?? Reloaded / relivened OK (3 X 3A). Lightning strike Email to Jo to check SAIDI | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.0021033 | 9.071e-06 | 2016 | 2015-04-11 | C | 3 | 0.0021033 | 9.0713e-06
4248272 | 2015-05-05 09:34 | 2015-05-05 13:00 | 205.6333 | 5 | 1028.1667 | 205.6333 | 202.6333 | 0.0031089 | 1013.1667 | 0.0030636 | 1.5119e-05 | NAPA ID:08495 TP_OPUNAKE GXP > NGARIKI SUB > SOUTH RD NGARIKI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses NG378 | Replace whole Tx structure N3125. Works location: Witiora Rd Opunake. WO 30003262 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.0015318 | 7.559e-06 | 2016 | 2015-05-05 | B | 5 | 0.0030636 | 1.5119e-05
4248287 | 2015-04-11 11:43 | 2015-04-11 13:20 | 96.8833 | 7 | 678.1833 | 96.8833 | 93.8833 | 0.0020507 | 657.1833 | 0.0019872 | 2.1166e-05 | Restore Supply on Device 5268 | 6.6 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3796T | Outage required from ABS 5268 to repair damage at Transformer 3796T after a lightning strike. Full set Fuses / holder required at Transformer. Relivened OK. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.0019872 | 2.1166e-05 | 2016 | 2015-04-11 | C | 7 | 0.0019872 | 2.1166e-05
4248317 | 2015-04-11 12:22 | 2015-04-11 14:18 | 116.0667 | 1 | 116.0667 | 116.0667 | 113.0667 | 0.00035096 | 113.0667 | 0.00034189 | 3.0238e-06 | Restore Supply on Device TC4351 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2318 | Suspected lightning replaced 2 x 10A H/V, O/H fuses at Fuses FC2318. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-04-11 | c | 0.00034189 | 3.024e-06 | 2016 | 2015-04-11 | C | 1 | 0.00034189 | 3.0238e-06
4248341 | 2015-05-07 08:31 | 2015-05-07 15:14 | 403.0167 | 39 | 15717.65 | 403.0167 | 400.0167 | 0.047526 | 15600.65 | 0.047173 | 0.00011793 | NAPA ID:08027 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M1945 | Replace poles,crossarms and conductor between Poles M1945 & M2435.Works location: Leslie Rd Putaruru. WO 30002575. ABS 952 was to be replace as well but no switch available so repaired instead. Issues with repairs meant job ran over time by 40 minutes | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-07 | b | 0.023586 | 5.8963e-05 | 2016 | 2015-05-07 | B | 39 | 0.047173 | 0.00011793
4248415 | 2015-04-10 21:00 | 2015-04-11 14:04 | 1024.0833 | 6 | 6144.5 | 1024.0833 | 1021.0833 | 0.018579 | 6126.5 | 0.018525 | 1.8143e-05 | Restore Supply on Device 2803T | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2803T | 3 Ht fuses replaced at Transformer 2803T (3A). Lightning strike Brent Moratti on site | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.018525 | 1.8143e-05 | 2016 | 2015-04-10 | C | 6 | 0.018525 | 1.8143e-05
4248824 | 2015-04-10 21:00 | 2015-04-11 09:00 | 720 | 2 | 1440 | 720 | 717 | 0.0043542 | 1434 | 0.0043361 | 6.0475e-06 | Restore Supply on Device 4196T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4196T | 2 Ht fuses replaced at Transformer 4196T (2A). Lightning strike. B.Moratti on site | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.0043361 | 6.048e-06 | 2016 | 2015-04-10 | C | 2 | 0.0043361 | 6.0475e-06
4248846 | 2015-04-10 21:00 | 2015-04-11 14:00 | 1020 | 4 | 4080 | 1020 | 1017 | 0.012337 | 4068 | 0.012301 | 1.2095e-05 | Restore Supply on Device 3435T | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3435T | 2 Ht fuses replaced at Transformer 3435T (2A). Lightning strike | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-10 | c | 0.012301 | 1.2095e-05 | 2016 | 2015-04-10 | C | 4 | 0.012301 | 1.2095e-05
4249079 | 2015-04-11 16:21 | 2015-04-11 17:13 | 52 | 988 | 34816 | 35.2389 | 32.2389 | 0.10528 | 31852 | 0.096313 | 0.0029875 | Restore Supply on Device 8800/11 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12009 | Tripping on CB11 on B-C O/C, Inst O/C, E/F. Feeder patrolled and lightning arrestors found blown at Links 12009. All clear, relivened OK. To be defected. | F1 | GLOVER RD EAST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.096313 | 0.0029875 | 2016 | 2015-04-11 | C | 988 | 0.096313 | 0.0029875
4250109 | 2015-04-11 17:02 | 2015-04-11 20:16 | 193.9167 | 1 | 193.9167 | 193.9167 | 190.9167 | 0.00058636 | 190.9167 | 0.00057729 | 3.0238e-06 | Restore Supply on Device 3732T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer 3732T | No other assets repaired or replaced at site. Adjacent assets up to Powerco Standard | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00057729 | 3.024e-06 | 2016 | 2015-04-11 | C | 1 | 0.00057729 | 3.0238e-06
4250145 | 2015-04-11 18:18 | 2015-04-11 18:59 | 40.3167 | 2 | 80.6333 | 40.3167 | 37.3167 | 0.00024382 | 74.6333 | 0.00022567 | 6.0475e-06 | Restore Supply on Device 8852 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | C7030 Transformer | Checked transformer all good checked houses & they were all on | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00022567 | 6.048e-06 | 2016 | 2015-04-11 | C | 2 | 0.00022567 | 6.0475e-06
4250306 | 2015-04-11 19:21 | 2015-04-11 21:10 | 109.8667 | 2 | 219.7333 | 109.8667 | 106.8667 | 0.00066442 | 213.7333 | 0.00064628 | 6.0475e-06 | Restore Supply on Device NG382 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3285 | Replaced 3 X DDOs at transformer n3285 Also Replaced Transformer N3285 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00064628 | 6.048e-06 | 2016 | 2015-04-11 | C | 2 | 0.00064628 | 6.0475e-06
4250317 | 2015-04-11 20:01 | 2015-04-11 21:31 | 89.8333 | 1 | 89.8333 | 89.8333 | 86.8333 | 0.00027163 | 86.8333 | 0.00026256 | 3.0238e-06 | Restore Supply on Device 3587T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | AS ABOVE | 1 X 2Amp fuse at transformer 2259T. 1X 2 amp fuse at transformer 4193T. 3 X 2 Amp fuses At Transformer 3587T. This outage for 3587T only. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-04-11 | c | 0.00026256 | 3.024e-06 | 2016 | 2015-04-11 | C | 1 | 0.00026256 | 3.0238e-06
4250327 | 2015-04-11 21:15 | 2015-04-12 04:16 | 420.9667 | 166 | 35217.5 | 212.1536 | 209.1536 | 0.10649 | 34719.5 | 0.10498 | 0.00050194 | Electric Job | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD5-145 | Power Box on road side on Fire. LV Board Burnt up. Complete LV Board Replaced. Numerous LV Cable Joints made. HV Boots Replaced. Some minor circuits and streetlights to be repaired on Monday 13th April | F2 | MOUNT | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-04-11 | c | 0.10498 | 0.00050194 | 2016 | 2015-04-11 | C | 166 | 0.10498 | 0.00050194
4250907 | 2015-04-12 11:30 | 2015-04-12 12:33 | 62.8333 | 698 | 28482.4667 | 40.8058 | 37.8058 | 0.086124 | 26388.4667 | 0.079792 | 0.0021106 | Restore Supply on Device 242 | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 242 | Transpower advise of Tripping on Waverley CB242 Waitotara Feeder. (No flaggings). Feeder patrolled / sectionalised but nothing found. Restored OK. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-04-12 | c | 0.079792 | 0.0021106 | 2016 | 2015-04-12 | C | 698 | 0.079792 | 0.0021106
4251681 | 2015-05-05 08:30 | 2015-05-05 15:30 | 420.2333 | 252 | 105898.8 | 420.2333 | 417.2333 | 0.32021 | 105142.8 | 0.31793 | 0.00076199 | NAPA ID:08021 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 751088 | Replace various network poles in work area. Install temp Fuses 40 at pole 751084 and temp Fuses 39 at pole 751088. Cut Jumpers at pole 846481 to create break. Works location: McLean St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.15896 | 0.00038099 | 2016 | 2015-05-05 | B | 252 | 0.31793 | 0.00076199
4251684 | 2015-05-08 08:45 | 2015-05-08 14:40 | 355 | 68 | 24140 | 355 | 352 | 0.072994 | 23936 | 0.072377 | 0.00020562 | NAPA ID:08022 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 846481 | Replace various network poles in work area. Replace exsisting O/H TX 1374 with new Ground mount tx. Install new 11kv cable and Fuses 12061. Works location: McLean St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-08 | b | 0.036188 | 0.00010281 | 2016 | 2015-05-08 | B | 68 | 0.072377 | 0.00020562
4251697 | 2015-05-13 08:46 | 2015-05-13 14:39 | 353.4333 | 71 | 25093.7667 | 353.4333 | 350.4333 | 0.075878 | 24880.7667 | 0.075233 | 0.00021469 | NAPA ID:08024 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8360 | Replace various network poles in work area. Works location: Haymblyn St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-13 | b | 0.037617 | 0.00010734 | 2016 | 2015-05-13 | B | 71 | 0.075233 | 0.00021469
4251712 | 2015-05-19 08:45 | 2015-05-19 14:44 | 359 | 51 | 18309 | 359 | 356 | 0.055362 | 18156 | 0.054899 | 0.00015421 | NAPA ID:08028 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 846481 | Replace TX structure 773 and at completion close line break at pole 846481. Works location: Nobs Line. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-19 | b | 0.02745 | 7.7106e-05 | 2016 | 2015-05-19 | B | 51 | 0.054899 | 0.00015421
4251716 | 2015-04-12 17:15 | 2015-04-12 18:19 | 63.7 | 20 | 1274 | 63.7 | 60.7 | 0.0038523 | 1214 | 0.0036708 | 6.0475e-05 | Restore Supply on Device 7205 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815106 | Outage required from fuses 7205 to replace a broken insulator. Replaced, relivened. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-04-12 | c | 0.0036708 | 6.0475e-05 | 2016 | 2015-04-12 | C | 20 | 0.0036708 | 6.0475e-05
4251744 | 2015-05-21 08:46 | 2015-05-21 13:52 | 305.5833 | 62 | 18946.1667 | 305.5833 | 302.5833 | 0.057289 | 18760.1667 | 0.056726 | 0.00018747 | NAPA ID:08030 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 203 | Replace various network poles in work area. Works location: Beach St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-21 | b | 0.028363 | 9.3737e-05 | 2016 | 2015-05-21 | B | 62 | 0.056726 | 0.00018747
4251747 | 2015-05-26 09:08 | 2015-05-26 13:16 | 248 | 62 | 15376 | 248 | 245 | 0.046493 | 15190 | 0.045931 | 0.00018747 | NAPA ID:08031 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 203 | Replace various network poles in work area. Reconductor from fuses 8341 to tx 489. Works location: Beach St WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-26 | b | 0.022965 | 9.3737e-05 | 2016 | 2015-05-26 | B | 62 | 0.045931 | 0.00018747
4253644 | 2015-04-12 18:45 | 2015-04-12 21:19 | 153.7833 | 3 | 461.35 | 153.7833 | 150.7833 | 0.001395 | 452.35 | 0.0013678 | 9.0713e-06 | Restore Supply on Device SD4-679 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuse SD4 679 | Completed under oms 4252284 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-04-12 | c | 0.0013678 | 9.071e-06 | 2016 | 2015-04-12 | C | 3 | 0.0013678 | 9.0713e-06
4253736 | 2015-04-12 22:13 | 2015-04-12 23:35 | 81.7167 | 1 | 81.7167 | 81.7167 | 78.7167 | 0.00024709 | 78.7167 | 0.00023802 | 3.0238e-06 | Restore Supply on Device 6774 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6774 | Two X 10 Amp Fuses Trees down the road maybe the cause | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-04-12 | c | 0.00023802 | 3.024e-06 | 2016 | 2015-04-12 | C | 1 | 0.00023802 | 3.0238e-06
4253980 | 2015-04-12 22:16 | 2015-04-12 23:55 | 98.9667 | 1 | 98.9667 | 98.9667 | 95.9667 | 0.00029925 | 95.9667 | 0.00029018 | 3.0238e-06 | Restore Supply on Device 607 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Job 4253736 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-04-12 | c | 0.00029018 | 3.024e-06 | 2016 | 2015-04-12 | C | 1 | 0.00029018 | 3.0238e-06
4254629 | 2015-04-13 02:47 | 2015-04-13 06:51 | 244.15 | 698 | 44236.9667 | 63.3767 | 60.3767 | 0.13376 | 42142.9667 | 0.12743 | 0.0021106 | Restore Supply on Device 242 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781393 | CB 242 Tripped - Damaged Insulator found during sectionlising - Isolated at Fuses 2719 - Used 1x HV Insolater and Binder 1 X 10 Fuse | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-04-13 | c | 0.12743 | 0.0021106 | 2016 | 2015-04-13 | C | 698 | 0.12743 | 0.0021106
4256546 | 2015-04-13 02:23 | 2015-04-13 05:24 | 181.15 | 196 | 30745.4667 | 156.8646 | 153.8646 | 0.092967 | 30157.4667 | 0.091189 | 0.00059266 | Restore Supply on Device T3651 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Section C422/2 |  | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.091189 | 0.00059266 | 2016 | 2015-04-13 | C | 196 | 0.091189 | 0.00059266
4256771 | 2015-04-13 07:05 | 2015-04-13 08:36 | 90.1333 | 1 | 90.1333 | 90.1333 | 87.1333 | 0.00027254 | 87.1333 | 0.00026347 | 3.0238e-06 | Restore Supply on Device T2515 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7717 | Fuses found bown at fuses 7717 - Used 2 x 10 HV fuses | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.00026347 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.00026347 | 3.0238e-06
4261727 | 2015-04-13 07:45 | 2015-04-13 10:22 | 156.3333 | 106 | 5778.7833 | 54.5168 | 51.5168 | 0.017474 | 5460.7833 | 0.016512 | 0.00032052 | Restore Supply on Device 2592 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 789901 | Sectionliser 2592 Tripped A,B Ph E/F - Tree through line found at Pole 789901 - Isolated at ABS 2551 &* Lines 2714 - Lines Repair - Used 10 mtrs of Conductor and 4x sleeves - Faultman to supply NDR # N 300045 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.016512 | 0.00032052 | 2016 | 2015-04-13 | C | 106 | 0.016512 | 0.00032052
4261769 | 2015-04-13 07:58 | 2015-04-13 14:33 | 394.45 | 29 | 2080.5167 | 71.742 | 68.742 | 0.006291 | 1993.5167 | 0.0060279 | 8.7689e-05 | Restore Supply on Device T9/242 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole | Blown Jumper Found at Pole - Isolated at ABS's V76 & V73 with backfeed via I29 - jumper repaired - used 10 mtrs Conductor & 12 connecters. Email sent to Jo to check possible SAIDI component | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.0060279 | 8.7689e-05 | 2016 | 2015-04-13 | C | 29 | 0.0060279 | 8.7689e-05
4261800 | 2015-04-13 08:22 | 2015-04-13 09:02 | 40.7 | 1 | 40.7 | 40.7 | 37.7 | 0.00012307 | 37.7 | 0.000114 | 3.0238e-06 | Restore Supply on Device T842 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | Power on when faultman arrived. Flicked off briefly due to feeder fault on job 4253998. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.000114 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.000114 | 3.0238e-06
4261827 | 2015-04-13 08:52 | 2015-04-13 10:56 | 123.8333 | 1 | 123.8333 | 123.8333 | 120.8333 | 0.00037444 | 120.8333 | 0.00036537 | 3.0238e-06 | Restore Supply on Device X2900 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 785980 | Replaced 2 x 2A HV fuses; caused by lightning. All other assets okay; nothing else replaced. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.00036537 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.00036537 | 3.0238e-06
4261857 | 2015-04-13 09:12 | 2015-04-13 10:08 | 56.7667 | 423 | 19215.4 | 45.4265 | 42.4265 | 0.058103 | 17946.4 | 0.054266 | 0.0012791 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Farmer Rd Sub CB 6 Tatuanui Feeder | at 09:11 Farmer Rd Sub, CB 6 Tatuanui Feeder, Tripped, O/C, L/O. Faultmen dispatched and investigation began. Feeder sectionalised, no fault found. Was lightning in the area at the time of tripping. Marty Keenan Attended. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.054266 | 0.0012791 | 2016 | 2015-04-13 | C | 423 | 0.054266 | 0.0012791
4262295 | 2015-05-04 09:10 | 2015-05-04 11:50 | 160 | 2 | 320 | 160 | 157 | 0.0009676 | 314 | 0.00094946 | 6.0475e-06 | NAPA ID:08512 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/187 | Replace TX and LV X-Arms on pole P12194 (T5/187). Existing TX to be replaced. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-04 | b | 0.00047473 | 3.024e-06 | 2016 | 2015-05-04 | B | 2 | 0.00094946 | 6.0475e-06
4263146 | 2015-05-05 12:32 | 2015-05-05 14:18 | 106 | 1 | 106 | 106 | 103 | 0.00032052 | 103 | 0.00031145 | 3.0238e-06 | NAPA ID:08517 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | t2/215 | Replace LV xarms on pole P13942 (T5/280). Existing Tx to be reinstalled | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.00015572 | 1.512e-06 | 2016 | 2015-05-05 | B | 1 | 0.00031145 | 3.0238e-06
4263154 | 2015-05-05 08:40 | 2015-05-05 11:15 | 155 | 1 | 155 | 155 | 152 | 0.00046868 | 152 | 0.00045961 | 3.0238e-06 | NAPA ID:08519 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/280 | Replace LV xarms on pole P13944 (T5/280). Existing Tx to be reinstalled. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.00022981 | 1.512e-06 | 2016 | 2015-05-05 | B | 1 | 0.00045961 | 3.0238e-06
4263158 | 2015-04-13 09:37 | 2015-04-13 10:14 | 36.6667 | 288 | 10560 | 36.6667 | 33.6667 | 0.031931 | 9696 | 0.029318 | 0.00087084 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Browne St Sub CB 5 Station Rd Feeder | at 09:37 Browne St Sub, CB 5 Station Rd Feeder, Tripped, Ph B Fault, E/F, L/O. Faultmen dispatched and investigation began. Manual Reclose tried at 10:14 and feeder held in. Line Patrolled. No Fault Found. Unknown Cause. Perry Hicks Attended. | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.029318 | 0.00087084 | 2016 | 2015-04-13 | C | 288 | 0.029318 | 0.00087084
4263458 | 2015-04-14 08:51 | 2015-04-14 10:54 | 123.2833 | 100 | 12328.3333 | 123.2833 | 120.2833 | 0.037278 | 12028.3333 | 0.036371 | 0.00030238 | NAPA ID:08603 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC410 | Replace x-arm found on acoustic fault test. Works location: Piako Rd. WO 10100473 | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-14 | b | 0.018185 | 0.00015119 | 2016 | 2015-04-14 | B | 100 | 0.036371 | 0.00030238
4264176 | 2015-04-14 08:47 | 2015-04-14 14:42 | 355.2 | 73 | 16237.8 | 222.4356 | 219.4356 | 0.049099 | 16018.8 | 0.048437 | 0.00022073 | NAPA ID:08594 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC482 | Replace X-arms found as urgent during Accoustic testing - 2 shuts. Works location: Kaihere Rd. WO 10100473 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-14 | b | 0.024219 | 0.00011037 | 2016 | 2015-04-14 | B | 73 | 0.048437 | 0.00022073
4264325 | 2015-04-13 14:42 | 2015-04-13 15:47 | 65 | 64 | 4160 | 65 | 62 | 0.012579 | 3968 | 0.011998 | 0.00019352 | Restore Supply on Device TC1416 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1416 | burned off jumper to ddo. FM requesting 2R to repair the jumper with switching being done by another FM. advise FM it is 1R activity. *** please sort at invoicing level *** Line was isolated at ABS IC 482 & at Sw/Gear 9459/1 to repair jumper to transforme | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.011998 | 0.00019352 | 2016 | 2015-04-13 | C | 64 | 0.011998 | 0.00019352
4264334 | 2015-05-07 09:15 | 2015-05-07 15:18 | 363 | 40 | 14520 | 363 | 360 | 0.043905 | 14400 | 0.043542 | 0.00012095 | NAPA ID:08207 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS K56 | CACD IS FOR TREESCAPE 2 TREE SITES. AP is so we can replace an 11Kv arm. Works location: Lower and Upper Pakihikura Rd. PPPD 46859 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-07 | b | 0.021771 | 6.0475e-05 | 2016 | 2015-05-07 | B | 40 | 0.043542 | 0.00012095
4264788 | 2015-04-13 13:37 | 2015-04-13 14:40 | 62.9 | 18 | 1117.55 | 62.0861 | 59.0861 | 0.0033792 | 1063.55 | 0.0032159 | 5.4428e-05 | Restore Supply on Device X453 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 2909 | Two Fuses Found Blown at Fuses 2909 - Line Patrolled with Branch found below line at Pole 793127 - Fuses Closed - Used 2x 8 amp HV fuses. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.0032159 | 5.4428e-05 | 2016 | 2015-04-13 | C | 18 | 0.0032159 | 5.4428e-05
4264812 | 2015-04-13 13:30 | 2015-04-13 14:26 | 55.6833 | 33 | 1837.55 | 55.6833 | 52.6833 | 0.0055563 | 1738.55 | 0.005257 | 9.9784e-05 | Restore Supply on Device 7601 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N/A - NOT APPLICABLE | CB C839 Tripped A/R - RS C408 Tripped A/R - Sec C422 found tripped, Closed and healed in at night - Line Patrol organised for morning. Faulty insulator found at Pole 824369 - Isolated at Fuses 7601 - Insulator replaced - Used 2 x HV insulators parent is a | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.005257 | 9.9784e-05 | 2016 | 2015-04-13 | C | 33 | 0.005257 | 9.9784e-05
4265450 | 2015-04-13 16:28 | 2015-04-13 19:16 | 168 | 13 | 2184 | 168 | 165 | 0.0066039 | 2145 | 0.006486 | 3.9309e-05 | Restore Supply on Device TD6-044 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 228019 | Emergency switching to replace pole 228019 & hardware ( king bolt let go ). TPV 3 Isolation at ABS SE6 079 ( no back feeds ) pole & hardware replaced all service restored. Materials 1 x pole, 1 x arm, 3 x H/V insulators, 2 x H/V sleeves. | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.006486 | 3.9309e-05 | 2016 | 2015-04-13 | C | 13 | 0.006486 | 3.9309e-05
4265455 | 2015-05-10 08:53 | 2015-05-10 13:51 | 298.1 | 351 | 104633.1 | 298.1 | 295.1 | 0.31639 | 103580.1 | 0.3132 | 0.0010613 | NAPA ID:08236 TP_HUIRANGI GXP > INGLEWOOD SUB > BROOKES ST | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5404 | replace pole and all hardware. replace abs 5533 and ddos 6368 with new fused abs. replace 6.6kv pot head. Works location: Kelly St. WO 30003085 | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-05-10 | b | 0.1566 | 0.00053067 | 2016 | 2015-05-10 | B | 351 | 0.3132 | 0.0010613
4265573 | 2015-04-13 15:46 | 2015-04-13 17:55 | 129.3833 | 5 | 558.0167 | 111.6033 | 108.6033 | 0.0016873 | 543.0167 | 0.001642 | 1.5119e-05 | Restore Supply on Device LI799 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L4347 | at 15:23 Livingstone Sub, CB LI7 Kakaramea Feeder, Recloser 6722 Tripped, No Flags, Auto Reclosed. Calls came in of no power/part powers. Found 1x Blown DDO at Fuses LI799 & 3x Blown DDO's at Transformer L4347. Reloaded relivened fuses and all power Resto | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.001642 | 1.5119e-05 | 2016 | 2015-04-13 | C | 5 | 0.001642 | 1.5119e-05
4265637 | 2015-04-13 16:37 | 2015-04-13 23:25 | 408.4833 | 1 | 408.4833 | 408.4833 | 405.4833 | 0.0012352 | 405.4833 | 0.0012261 | 3.0238e-06 | Restore Supply on Device TF5-015 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP264 | Check to see if OMS 4265640 (490 Mangatoi Rd) and oms 4265654 (869 Mangatoi Rd) are related. also 540 Mangatoi Rd OMS 4265787. 8:53pm David advised these jobs will be related. David Joynt could not find fault and could not get into a couple of the pptys | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.0012261 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.0012261 | 3.0238e-06
4265803 | 2015-04-13 18:24 | 2015-04-13 18:25 | 1.5333 | 85 | 130.3333 | 1.5333 | -1.4667 | 0.0003941 | 0 | 0 | 0.00025702 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 4199/2 | Faultman worked on wrong recloser and caused trip on RS 4199/2. Saftey Manager 464730 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0 | 0.00025702 | 2016 | 2015-04-13 | C | 85 | 0 | 0.00025702
4266556 | 2015-04-13 19:33 | 2015-04-13 20:58 | 85 | 258 | 16063.6833 | 62.2623 | 59.2623 | 0.048573 | 15289.6833 | 0.046232 | 0.00078013 | Restore Supply on Device H131 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | H131 | Tripping on CBH131 on Reverse EF1. Feeder patrolled / sectionalised but nothing found. Restored OK. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.046232 | 0.00078013 | 2016 | 2015-04-13 | C | 258 | 0.046232 | 0.00078013
4266841 | 2015-04-13 19:49 | 2015-04-13 21:00 | 71.0667 | 1 | 71.0667 | 71.0667 | 68.0667 | 0.00021489 | 68.0667 | 0.00020582 | 3.0238e-06 | Restore Supply on Device TD4-183 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD4-183 | 7.52pm - advise smc. was part of the earlier fault in the area and original job rolled up to the tap level job. created this job as a check for safety. no fault found - part of OMS 4265694 - td4-183. candle burnt off. replace 15 amp ddo fuse. cause: old | F3 | BROOKFIELD TCE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-04-13 | c | 0.00020582 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.00020582 | 3.0238e-06
4266879 | 2015-04-13 21:21 | 2015-04-13 22:21 | 60.1167 | 7 | 420.8167 | 60.1167 | 57.1167 | 0.0012724 | 399.8167 | 0.0012089 | 2.1166e-05 | Restore Supply on Device X1835 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1835 | check to see if 4266884 - 459 Beach rd is related to this - advised Hub. Tripping on 2 HT fuses (3A) at Transformer TX1835 - reloaded OK. Lightning in area | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.001209 | 2.1166e-05 | 2016 | 2015-04-13 | C | 7 | 0.0012089 | 2.1166e-05
4266951 | 2015-04-13 23:03 | 2015-04-14 05:21 | 378 | 1 | 378 | 378 | 375 | 0.001143 | 375 | 0.0011339 | 3.0238e-06 | Restore Supply on Device T5/286 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | Unumbered pole | Fuses N59 tripped on 2 phases. Fallen snow has caused a tree breanch to fall across conductors. Requires cutting away before relivening. (Isolation from Fuses N59). Bucket truck called out, tree branch cut away and relivened OK | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-04-13 | c | 0.0011339 | 3.024e-06 | 2016 | 2015-04-13 | C | 1 | 0.0011339 | 3.0238e-06
4267687 | 2015-04-14 03:47 | 2015-04-14 10:25 | 398.6167 | 681 | 20101.6167 | 29.5178 | 26.5178 | 0.060782 | 18058.6167 | 0.054605 | 0.0020592 | Restore Supply on Device 9 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 39256 | Lines down found at Pole 39256 caused by jumper between lines burning through the line - Isolated at ABS's D78, D77,D84, & D79 - Back feeds installed via VS 10182/2, ABS D75, ABS D89 and ABS E8 - ABS D90 failed while installing back feeds - Lines repair | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.054605 | 0.0020592 | 2016 | 2015-04-14 | C | 681 | 0.054605 | 0.0020592
4267691 | 2015-04-14 05:47 | 2015-04-14 07:35 | 107.7 | 2 | 213.9 | 106.95 | 103.95 | 0.00064678 | 207.9 | 0.00062864 | 6.0475e-06 | Restore Supply on Device M4240 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M4240 | Reloaded-Relivened 2x 2A HV Fuses at Transformer M4240. All Power Restored on completion. Outage OMS No. 4268440. | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.00062864 | 6.048e-06 | 2016 | 2015-04-14 | C | 2 | 0.00062864 | 6.0475e-06
4268459 | 2015-04-14 07:22 | 2015-04-14 09:12 | 110.7167 | 4 | 442.8667 | 110.7167 | 107.7167 | 0.0013391 | 430.8667 | 0.0013028 | 1.2095e-05 | Restore Supply on Device 532 | 22 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 532 | Fuses found blown at Fuses 532 - reported duck hit lines, line patroled with no fault found - used 2 x 6 amp fuses | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.0013028 | 1.2095e-05 | 2016 | 2015-04-14 | C | 4 | 0.0013028 | 1.2095e-05
4268471 | 2015-04-14 07:28 | 2015-04-14 18:41 | 672.6833 | 3 | 2018.05 | 672.6833 | 669.6833 | 0.0061021 | 2009.05 | 0.0060749 | 9.0713e-06 | Restore Supply on Device FC2198 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3617 | Transformer TC3617 isolated at fuses FC2198. Arrangements being made to have transformer changed. Colin advised that this tx needs to replaced mitre 10 will have a generator they need to change the syle of tx this is affecting 3 other customers and they | F3 | GILMOUR ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-04-14 | c | 0.0060749 | 9.071e-06 | 2016 | 2015-04-14 | C | 3 | 0.0060749 | 9.0713e-06
4268542 | 2015-04-20 09:50 | 2015-04-20 15:11 | 320.8333 | 455 | 145979.1667 | 320.8333 | 317.8333 | 0.44141 | 144614.1667 | 0.43728 | 0.0013758 | NAPA ID:07154 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Feilding | Replace 11kV Sw/Gear 330/331 with Sw/Gear 10232. | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-20 | b | 0.21864 | 0.00068791 | 2016 | 2015-04-20 | B | 455 | 0.43728 | 0.0013758
4277808 | 2015-04-14 09:21 | 2015-04-14 14:40 | 319 | 9 | 2871 | 319 | 316 | 0.0086812 | 2844 | 0.0085996 | 2.7214e-05 | Restore Supply on Device TD3-235 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | TD3-235 | this is duplicate of 4268512 no fm dispat Transformer TD3-235 hit and demolished by vehicle - NDR number 52804 - transformer isolated at its own HV fuses - 200kva ground mount replaced & all supply restored - 1 x 200kva transformer, 2 x HV termination ki | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-04-14 | c | 0.0085996 | 2.7214e-05 | 2016 | 2015-04-14 | C | 9 | 0.0085996 | 2.7214e-05
4277819 | 2015-04-14 07:25 | 2015-04-14 09:28 | 122.95 | 5 | 614.75 | 122.95 | 119.95 | 0.0018589 | 599.75 | 0.0018135 | 1.5119e-05 | Restore Supply on Device X2418 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2418 | 2 fuse found blown at Transformer X2418 after lightening in area - used 2 x 2amp fuses | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.0018135 | 1.5119e-05 | 2016 | 2015-04-14 | C | 5 | 0.0018135 | 1.5119e-05
4277849 | 2015-05-05 09:45 | 2015-05-05 18:19 | 514.3667 | 2 | 1028.7333 | 514.3667 | 511.3667 | 0.0031106 | 1022.7333 | 0.0030925 | 6.0475e-06 | NAPA ID:08581 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T9/266 | replace H structures wihoki valley road. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.0015463 | 3.024e-06 | 2016 | 2015-05-05 | B | 2 | 0.0030925 | 6.0475e-06
4277859 | 2015-05-06 10:20 | 2015-05-06 15:36 | 315.5 | 2 | 631 | 315.5 | 312.5 | 0.001908 | 625 | 0.0018899 | 6.0475e-06 | NAPA ID:08588 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | p04414 | To Change 11kv H structures | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.00094492 | 3.024e-06 | 2016 | 2015-05-06 | B | 2 | 0.0018899 | 6.0475e-06
4277896 | 2015-04-14 10:27 | 2015-04-14 15:05 | 278.4667 | 3 | 835.4 | 278.4667 | 275.4667 | 0.002526 | 826.4 | 0.0024988 | 9.0713e-06 | Restore Supply on Device 4977 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 708780 | at 13:40 Strathmore Sub, CB 7131. Trees down on lines at Pole 708780. Isolated lines at Fuses 4977. Permit issued and repairs carried out. All power restored on completion. Alan Rarere Attended. 4x Conductor Connectors Used. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.0024988 | 9.071e-06 | 2016 | 2015-04-14 | C | 3 | 0.0024988 | 9.0713e-06
4278038 | 2015-04-14 13:35 | 2015-04-14 13:41 | 5.6 | 8 | 39.65 | 4.9562 | 1.9563 | 0.00011989 | 15.65 | 4.7322e-05 | 2.419e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6635 | Jade Williams Attended. Could not find any trees on line or anyone stuck inside tractor. Did say that it did look as if there was a contracting working down the road that may have been working close to the lines but contractors denied having touched the l | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-04-14 | c | 4.7322e-05 | 2.419e-05 | 2016 | 2015-04-14 | C | 8 | 4.7322e-05 | 2.419e-05
4278124 | 2015-05-05 08:01 | 2015-05-05 16:30 | 509.7167 | 31 | 2516.7833 | 81.1866 | 78.1866 | 0.0076102 | 2423.7833 | 0.0073289 | 9.3737e-05 | NAPA ID:07742 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE5-092 | 1. Create 11kv cable break at link-box SE5-110 (TE5-092 side) and install generator at TE5-092 (0800-0900) 2. Back-feed up to cable break at link-box SE5-110 3. Replace series one switchgear & kiosk with new CFC (9926/1 /2 /3) Safelink, concrete pad & enc | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-05 | b | 0.0036645 | 4.6868e-05 | 2016 | 2015-05-05 | B | 31 | 0.0073289 | 9.3737e-05
4278171 | 2015-05-07 10:25 | 2015-05-07 17:25 | 420 | 2 | 840 | 420 | 417 | 0.00254 | 834 | 0.0025218 | 6.0475e-06 | NAPA ID:08589 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P04414 | Replace 11Kv H structures. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-07 | b | 0.0012609 | 3.024e-06 | 2016 | 2015-05-07 | B | 2 | 0.0025218 | 6.0475e-06
4278208 | 2015-05-06 09:45 | 2015-05-06 12:14 | 149.1333 | 19 | 2833.5333 | 149.1333 | 146.1333 | 0.0085679 | 2776.5333 | 0.0083956 | 5.7451e-05 | NAPA ID:08566 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 794106 | Replace 11kv jumpers on pole 794106. Works location: Turakina Valley Marton. WO 30003255 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.0041978 | 2.8726e-05 | 2016 | 2015-05-06 | B | 19 | 0.0083956 | 5.7451e-05
4278209 | 2015-05-08 10:05 | 2015-05-08 16:50 | 405 | 2 | 810 | 405 | 402 | 0.0024492 | 804 | 0.0024311 | 6.0475e-06 | NAPA ID:08590 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P04414 | To Replace H Structures. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-08 | b | 0.0012156 | 3.024e-06 | 2016 | 2015-05-08 | B | 2 | 0.0024311 | 6.0475e-06
4279371 | 2015-04-14 15:58 | 2015-04-14 17:40 | 102.35 | 9 | 755.8167 | 83.9796 | 80.9796 | 0.0022854 | 728.8167 | 0.0022038 | 2.7214e-05 | Restore Supply on Device X1055 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 1100 | 4.02pm - advise smc. Fuses found blown at Fuses 1100, Transformers X1055, X281, and X2913 1after lightening in area - used 3x 8amp, 2x 3amp and 3x 3amp fuses | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.0022038 | 2.7214e-05 | 2016 | 2015-04-14 | C | 9 | 0.0022038 | 2.7214e-05
4279432 | 2015-05-07 12:00 | 2015-05-07 16:51 | 290.3167 | 265 | 244.6333 | 0.92314 | -2.0769 | 0.00073971 | 0 | 0 | 0.0008013 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KPE Sub, Feeder 5, 04144, Cracked insulator | ***Red Defect*** Ken Pattie had an accoustic patrol done to locate faulty equipment causing GFN operation. Site id as per report, ASW, NCTL. NOTE, NOT part of KPI reporting, ASW. All being managed by Kim Lambert, via planned applications due to HV outages |  | Unknown | Unknown | Unknown | Unknown | Western Electricity | POWERCO | 2015-05-07 | c | 0 | 0.0008013 | 2016 | 2015-05-07 | C | 265 | 0 | 0.0008013
4280067 | 2015-04-15 04:09 | 2015-04-15 04:10 | 1 | 76 | 76 | 1 | -2 | 0.00022981 | 0 | 0 | 0.00022981 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7417 | Recloser CB 7417 A/R on Phase B-C O/C, E/F. Cause unknown | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-04-15 | c | 0 | 0.00022981 | 2016 | 2015-04-15 | C | 76 | 0 | 0.00022981
4280147 | 2015-04-15 06:14 | 2015-04-15 07:40 | 86.0667 | 1 | 86.0667 | 86.0667 | 83.0667 | 0.00026025 | 83.0667 | 0.00025117 | 3.0238e-06 | Restore Supply on Device TC5780 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC4233 | Bird Strike has caused fuses to blow: Replaced 2x 6Amp Fuse Links. Pole C14095 has come over slightly. Pole needs to be reblocked . Perry to defect. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-04-15 | c | 0.00025117 | 3.024e-06 | 2016 | 2015-04-15 | C | 1 | 0.00025117 | 3.0238e-06
4280765 | 2015-05-11 10:50 | 2015-05-11 14:15 | 205 | 3 | 615 | 205 | 202 | 0.0018596 | 606 | 0.0018324 | 9.0713e-06 | NAPA ID:08609 TP_GREYTOWN GXP > KEMPTON SUB > WEST ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | Transformer T3799 | upgrade existing 15KVA single phase transformer to new 30KVA single phase transformer Off Time 10:50 On 14:15 | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2015-05-11 | b | 0.0009162 | 4.536e-06 | 2016 | 2015-05-11 | B | 3 | 0.0018324 | 9.0713e-06
4280885 | 2015-05-13 08:00 | 2015-05-13 16:34 | 513.8833 | 4 | 2055.5333 | 513.8833 | 510.8833 | 0.0062154 | 2043.5333 | 0.0061792 | 1.2095e-05 | NAPA ID:08371 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 834972 | tree cutting. Works location: Stuart Rd Masterton. PPPD 44358 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-13 | b | 0.0030896 | 6.048e-06 | 2016 | 2015-05-13 | B | 4 | 0.0061792 | 1.2095e-05
4280895 | 2015-04-15 10:39 | 2015-04-15 11:53 | 74 | 1 | 74 | 74 | 71 | 0.00022376 | 71 | 0.00021469 | 3.0238e-06 | Restore Supply on Device T4207 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11001 | Replaced 2X HV Fuses | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-04-15 | c | 0.00021469 | 3.024e-06 | 2016 | 2015-04-15 | C | 1 | 0.00021469 | 3.0238e-06
4291220 | 2015-04-15 13:16 | 2015-04-15 15:05 | 108.5167 | 18 | 1953.3 | 108.5167 | 105.5167 | 0.0059063 | 1899.3 | 0.005743 | 5.4428e-05 | Restore Supply on Device T9/292 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | p04575 | trevor advises worked through control. replaced 2x 10a ddo fuse links at fuses V83. taken to todd in control for closure as has a saidi component attached | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-15 | c | 0.005743 | 5.4428e-05 | 2016 | 2015-04-15 | C | 18 | 0.005743 | 5.4428e-05
4291332 | 2015-04-15 14:11 | 2015-04-15 14:58 | 47.0167 | 1 | 47.0167 | 47.0167 | 44.0167 | 0.00014217 | 44.0167 | 0.0001331 | 3.0238e-06 | Restore Supply on Device SE6-075 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | SE6-075 | Re-set High tension circuit breaker that had tripped. Due to overload. All other assets OK | F1 | RANGIURU | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-04-15 | c | 0.0001331 | 3.024e-06 | 2016 | 2015-04-15 | C | 1 | 0.0001331 | 3.0238e-06
4291524 | 2015-04-15 15:42 | 2015-04-15 17:37 | 115 | 24 | 2755.4 | 114.8083 | 111.8083 | 0.0083317 | 2683.4 | 0.008114 | 7.257e-05 | Restore Supply on Device X1834 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 495 | replace 2 x 10 amp ht fuses. cause: unknown, possibly birds. fuse # 495. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-15 | c | 0.008114 | 7.257e-05 | 2016 | 2015-04-15 | C | 24 | 0.008114 | 7.257e-05
4291929 | 2015-04-14 18:52 | 2015-04-14 19:02 | 9.7833 | 1247 | 12199.8167 | 9.7833 | 6.7833 | 0.036889 | 8458.8167 | 0.025577 | 0.0037706 | Restore Supply on Device C855 | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A | Suspect tripped due to switching to restore Norfolk to normal configuration Off 18:52 on 19:02 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-04-14 | c | 0.025577 | 0.0037706 | 2016 | 2015-04-14 | C | 1247 | 0.025577 | 0.0037706
4293792 | 2015-04-16 04:46 | 2015-04-16 08:53 | 246.6 | 54 | 13316.4 | 246.6 | 243.6 | 0.040266 | 13154.4 | 0.039776 | 0.00016328 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | pole 827720 | Patrolled and found branch on line @ pole 827720 removed using sticks. NDR 23390. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-16 | c | 0.039776 | 0.00016328 | 2016 | 2015-04-16 | C | 54 | 0.039776 | 0.00016328
4293900 | 2015-04-16 07:41 | 2015-04-16 14:54 | 432.55 | 1 | 432.55 | 432.55 | 429.55 | 0.0013079 | 429.55 | 0.0012989 | 3.0238e-06 | Restore Supply on Device X4343 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794798 | Shan requested undo to assigned. Replaced 3x HV fuses at fuse 4035. Job was completed through control at 11.30 this morning but was not signed off | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-04-16 | c | 0.0012989 | 3.024e-06 | 2016 | 2015-04-16 | C | 1 | 0.0012989 | 3.0238e-06
4294633 | 2015-04-16 10:18 | 2015-04-16 10:35 | 16.7 | 912 | 14747.6667 | 16.1707 | 13.1707 | 0.044593 | 12011.6667 | 0.03632 | 0.0027577 | Restore Supply on Device 1122 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1122 | THIS ACTUALLY TRIPPED AT 10:08 AM BUT E MAP WAS NOT WORKING!!! Opunake CB 1122 Trip, O/C, E/F. Caused total loss of supply to Pungarehu Sub due to removed CB at Ngariki preventing ringfeed. CB 1122 set to one shot so decision made to attempt reclose after | F1,F2,F3 | PUNGAREHU 33KV | OPUNAKE | Taranaki | TP_OPUNAKE | Western Electricity | POWERCO | 2015-04-16 | c | 0.03632 | 0.0027577 | 2016 | 2015-04-16 | C | 912 | 0.03632 | 0.0027577
4295993 | 2015-04-16 13:31 | 2015-04-16 14:53 | 82.0333 | 1 | 82.0333 | 82.0333 | 79.0333 | 0.00024805 | 79.0333 | 0.00023898 | 3.0238e-06 | Restore Supply on Device T8/180 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P540248 | Checked and relivened after tree cutter caused lines to clash. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-04-16 | c | 0.00023898 | 3.024e-06 | 2016 | 2015-04-16 | C | 1 | 0.00023898 | 3.0238e-06
4296621 | 2015-04-16 17:34 | 2015-04-16 19:14 | 100 | 6 | 600 | 100 | 97 | 0.0018143 | 582 | 0.0017598 | 1.8143e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848323 | Urgent shutdown to 11kV from fuses 7318 and 33kv CB 3178/2 from Hau Nui sub required to replace crossarm - Used 2x complete HV crossarms | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-04-16 | c | 0.0017598 | 1.8143e-05 | 2016 | 2015-04-16 | C | 6 | 0.0017598 | 1.8143e-05
4296899 | 2015-04-17 00:34 | 2015-04-17 03:10 | 155.5667 | 99 | 7601 | 76.7778 | 73.7778 | 0.022984 | 7304 | 0.022086 | 0.00029935 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TX569 | Recloser 6748 Tripped Neutal Over current - Transformer 569 found to be faulty during sectinolising - isolated at owwnDDO's - Transformer replaced - Used 1x 50kVA transformer | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-04-17 | c | 0.022086 | 0.00029935 | 2016 | 2015-04-17 | C | 99 | 0.022086 | 0.00029935
4297211 | 2015-04-17 06:42 | 2015-04-17 07:24 | 42.6167 | 835 | 33056.7833 | 39.589 | 36.589 | 0.099956 | 30551.7833 | 0.092381 | 0.0025248 | Restore Supply on Device C829 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 830111 | Te Ore Ore CB C829 tripped A/B O/C. Line patrolled and Conductor found down at pole 830111. | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-04-17 | c | 0.092381 | 0.0025248 | 2016 | 2015-04-17 | C | 835 | 0.092381 | 0.0025248
4313071 | 2015-04-17 12:41 | 2015-04-17 14:53 | 132.1333 | 1 | 132.1333 | 132.1333 | 129.1333 | 0.00039954 | 129.1333 | 0.00039047 | 3.0238e-06 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 20309, P20311 | Insulators & cross arms on both HV poles need replacing asap. This is a red defect. Shaz advises that this can not be done today as they can not access switching point as it is in the middle of a racing track and the racing is on at the moment. Shaz advi | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-04-17 | c | 0.00039047 | 3.024e-06 | 2016 | 2015-04-17 | C | 1 | 0.00039047 | 3.0238e-06
4320365 | 2015-05-06 09:16 | 2015-05-06 15:41 | 385.2167 | 160 | 61634.6667 | 385.2167 | 382.2167 | 0.18637 | 61154.6667 | 0.18492 | 0.0004838 | NAPA ID:06693 TP_KINLEITH GXP > BAIRD ROAD SUB > DALMENY ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B12621, B0241, B12618, B12626 | Isolate HV overhead line and 2 transformers to replace cross arms on line. Work Location: Billah Street and Benella Street, Tokoroa. PPPD 6998. | F2/F3 | DALMENY ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-06 | b | 0.092459 | 0.0002419 | 2016 | 2015-05-06 | B | 160 | 0.18492 | 0.0004838
4320478 | 2015-05-02 08:13 | 2015-05-02 10:20 | 127.05 | 2 | 254.1 | 127.05 | 124.05 | 0.00076834 | 248.1 | 0.0007502 | 6.0475e-06 | NAPA ID:08731 TP_BRUNSWICK GXP > CASTLECLIFF SUB > BRYCE ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X3200 | Remove FABS 2688 via LLP and connect new HV cable to feed RMU 4749-1. RMU 4749-2 will feed new 1000kVA transformer 4749-3 will be a spare. Note: new 1000kVA transformer will take the old transformer number X3200. New transformer, RMU and all HV cables and | F1 | BRYCE ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-05-02 | b | 0.0003751 | 3.024e-06 | 2016 | 2015-05-02 | B | 2 | 0.0007502 | 6.0475e-06
4320486 | 2015-04-17 09:41 | 2015-04-17 11:23 | 101.7167 | 44 | 4475.5333 | 101.7167 | 98.7167 | 0.013533 | 4343.5333 | 0.013134 | 0.00013305 | Restore Supply on Device S566 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812435 | ABS S566 Opened and Tagged. Repairs made at pole 812435. | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-04-17 | c | 0.013134 | 0.00013305 | 2016 | 2015-04-17 | C | 44 | 0.013134 | 0.00013305
4320534 | 2015-05-05 08:32 | 2015-05-05 15:28 | 416.3667 | 66 | 27480.2 | 416.3667 | 413.3667 | 0.083094 | 27282.2 | 0.082495 | 0.00019957 | NAPA ID:07879 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 266 | change xarms , erect poles and move wire on to new poles from pole 787310 to 787407 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-05 | b | 0.041247 | 9.9784e-05 | 2016 | 2015-05-05 | B | 66 | 0.082495 | 0.00019957
4321333 | 2015-04-17 17:24 | 2015-04-17 18:07 | 42.6833 | 2 | 85.3667 | 42.6833 | 39.6833 | 0.00025813 | 79.3667 | 0.00023999 | 6.0475e-06 | Restore Supply on Device 5012E | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5012E | HV Isolated for safety on Transformer 5012E whilst LV repairs were made. This job was the parent job for OMS 4321301 but no crew request rolled up to this parent job. When FM signed off oms 4321301, this job was left open. FM did advise control of the on | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-04-17 | c | 0.00023999 | 6.048e-06 | 2016 | 2015-04-17 | C | 2 | 0.00023999 | 6.0475e-06
4321396 | 2015-04-17 21:17 | 2015-04-17 21:50 | 32.8167 | 65 | 2133.0833 | 32.8167 | 29.8167 | 0.0064499 | 1938.0833 | 0.0058603 | 0.00019654 | Restore Supply on Device 605 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C992 | HV line between ABS 605, 628 & Links IP141 isolated to retie floater reported earlier under OMS # 4321342. 1 x pin & insulator & 1 x tie materials required. All supply restored following repair. Perry Hicks attended. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-04-17 | c | 0.0058603 | 0.00019654 | 2016 | 2015-04-17 | C | 65 | 0.0058603 | 0.00019654
4321504 | 2015-04-18 08:24 | 2015-04-18 08:55 | 30.8667 | 3 | 91.7333 | 30.5778 | 27.5778 | 0.00027738 | 82.7333 | 0.00025017 | 9.0713e-06 | Restore Supply on Device X2229 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 586 | 2 X 20 Amp Fuses. Ducks | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.00025017 | 9.071e-06 | 2016 | 2015-04-18 | C | 3 | 0.00025017 | 9.0713e-06
4321539 | 2015-04-18 08:25 | 2015-04-18 15:55 | 450.6167 | 229 | 54589.95 | 238.3841 | 235.3841 | 0.16507 | 53902.95 | 0.16299 | 0.00069244 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | M0463 | Recloser 9636/2 tripped (no flags). Feeder sectionalised & tree/branch found on lines at pole M0463. Isolations between normal open ABS 1314 & ABS 860. Rest of feeder returned to service. Delays 1 Faultman had to attendfrom Tauranga. 2 Bad comms, Asplundh | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0.16299 | 0.00069244 | 2016 | 2015-04-18 | C | 229 | 0.16299 | 0.00069244
4322557 | 2015-04-18 09:04 | 2015-04-18 09:05 | 1 | 122 | 122 | 1 | -2 | 0.0003689 | 0 | 0 | 0.0003689 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | Taupo Quay CB4 | This was open for 1 min Refer to Safety Manager 464253. | F2 | RIDGWAY ST | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0 | 0.0003689 | 2016 | 2015-04-18 | C | 122 | 0 | 0.0003689
4322792 | 2015-04-18 10:02 | 2015-04-18 12:59 | 177.35 | 487 | 34392.5667 | 70.6213 | 67.6213 | 0.10399 | 32931.5667 | 0.099577 | 0.0014726 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755736 | Car V Pole Pulled pole back up rehang conductor. No NDR number some thing about he does not get 1 Now till later. Materials Used: 30 metres of conductor. Chris Viviers attended. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.099577 | 0.0014726 | 2016 | 2015-04-18 | C | 487 | 0.099577 | 0.0014726
4323684 | 2015-04-18 11:12 | 2015-04-18 17:45 | 392.8 | 1315 | 158639.1667 | 120.6381 | 117.6381 | 0.47969 | 154694.1667 | 0.46776 | 0.0039762 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 212491 | CB7 ( WBY ) & Recloser 9209/2 tripped E/F, O/C, L/O ABR scheme did not operate correctly & may require investigation. Car V Pole 212491 Isolations between Links 9209/4, ABS 9209/1 & ABS SE4 012. CB7 returned to service & back feed closed via Sectionalise | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0.46776 | 0.0039762 | 2016 | 2015-04-18 | C | 1315 | 0.46776 | 0.0039762
4325912 | 2015-04-18 12:21 | 2015-04-18 13:59 | 98.2167 | 5 | 301.4333 | 60.2867 | 57.2867 | 0.00091146 | 286.4333 | 0.00086611 | 1.5119e-05 | Restore Supply on Device X1844 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Links 495 | 2 X 10 Amp fuses. Ducks. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.00086611 | 1.5119e-05 | 2016 | 2015-04-18 | C | 5 | 0.00086611 | 1.5119e-05
4326039 | 2015-04-18 16:33 | 2015-04-18 19:46 | 193 | 1 | 193 | 193 | 190 | 0.00058359 | 190 | 0.00057451 | 3.0238e-06 | Restore Supply on Device 3082T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3082T | 2 X 3 Amp | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.00057452 | 3.024e-06 | 2016 | 2015-04-18 | C | 1 | 0.00057451 | 3.0238e-06
4326054 | 2015-04-18 15:51 | 2015-04-18 17:31 | 100.2667 | 1 | 100.2667 | 100.2667 | 97.2667 | 0.00030318 | 97.2667 | 0.00029411 | 3.0238e-06 | Restore Supply on Device 2314T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8888 | 8888 Fuses. 2 x 3 amp | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.00029411 | 3.024e-06 | 2016 | 2015-04-18 | C | 1 | 0.00029411 | 3.0238e-06
4326075 | 2015-04-18 16:35 | 2015-04-18 18:13 | 97.85 | 1 | 97.85 | 97.85 | 94.85 | 0.00029587 | 94.85 | 0.0002868 | 3.0238e-06 | Restore Supply on Device 3788T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 6218 | 2 x 3 amp fuses | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-04-18 | c | 0.0002868 | 3.024e-06 | 2016 | 2015-04-18 | C | 1 | 0.0002868 | 3.0238e-06
4326094 | 2015-04-18 16:46 | 2015-04-18 16:49 | 3.4667 | 475 | 1646.6667 | 3.4667 | 0.46667 | 0.0049791 | 0 | 0 | 0.0014363 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 9225 | WHB 5 Recloser 9225 tripped O/C, L/O feeder sectionalised no fault found high winds & rain at time of tripping. | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0 | 0.0014363 | 2016 | 2015-04-18 | C | 475 | 0 | 0.0014363
4327087 | 2015-04-18 22:17 | 2015-04-19 02:15 | 238.3333 | 135 | 25388.6 | 188.0637 | 185.0637 | 0.076769 | 24983.6 | 0.075544 | 0.00040821 | Restore Supply on Device RP10 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 223457 | Report from Police that there is a pole leaning into the hedge at 878 # 3 Rd. Police Event # P020915595. Pole Block, 2 metres Namu and 5 sleeves used to straighten pole and re-string conductors. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0.075544 | 0.00040821 | 2016 | 2015-04-18 | C | 135 | 0.075544 | 0.00040821
4327960 | 2015-04-18 23:19 | 2015-04-19 07:15 | 475.5167 | 612 | 55885.05 | 91.3154 | 88.3154 | 0.16898 | 54049.05 | 0.16343 | 0.0018505 | Restore Supply on Device 2 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE5-085 | at 23:19 Atuaroa Sub, CB 2 No. 3 Rd Feeder, Tripped, O/C. Faultman dispatched & Investigation began. Feeder sectionalised. Found 11kV Cable beyond Fused ABS SE5-085 has faulted. Isolated Cable at SE5-085. Remainder of feeder restored. Generators currently | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0.16343 | 0.0018505 | 2016 | 2015-04-18 | C | 612 | 0.16343 | 0.0018505
4329718 | 2015-04-19 08:52 | 2015-04-19 10:22 | 90.2833 | 1 | 90.2833 | 90.2833 | 87.2833 | 0.000273 | 87.2833 | 0.00026392 | 3.0238e-06 | Restore Supply on Device 3797T | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3797T | Tripping on 3HT Fuses on Transformer 3797T. (Caused by lightning during night). Fuse holder and fuses all replaced. Reloaded/relivened OK. (3 X 2A). | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-04-19 | c | 0.00026392 | 3.024e-06 | 2016 | 2015-04-19 | C | 1 | 0.00026392 | 3.0238e-06
4329837 | 2015-04-19 09:06 | 2015-04-19 11:49 | 163.2667 | 2 | 326.5333 | 163.2667 | 160.2667 | 0.00098736 | 320.5333 | 0.00096922 | 6.0475e-06 | Restore Supply on Device 4286T | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5623 | 3 HT fuses tripped at 5623. Suspect lightning from last night. Reloaded/relivened OK. (3 X 6A). | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-04-19 | c | 0.00096922 | 6.048e-06 | 2016 | 2015-04-19 | C | 2 | 0.00096922 | 6.0475e-06
4329960 | 2015-04-19 11:42 | 2015-04-19 14:45 | 183 | 1 | 183 | 183 | 180 | 0.00055335 | 180 | 0.00054428 | 3.0238e-06 | Restore Supply on Device TD3-155 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD3 114 | Replace faulty transformer TD3 114 ( cracked bushing ). Email sent to Jo to check possible SAIDI component. | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-04-19 | c | 0.00054428 | 3.024e-06 | 2016 | 2015-04-19 | C | 1 | 0.00054428 | 3.0238e-06
4330192 | 2015-04-19 14:34 | 2015-04-19 16:37 | 122.5833 | 53 | 5268.65 | 99.4085 | 96.4085 | 0.015931 | 5109.65 | 0.01545 | 0.00016026 | Restore Supply on Device 177 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 790783 | Outage required from ABS 177 to Links 1173 to repair a broken conductor. (Backfeed at ABS 1487). Fault caused by tree cutter felling a branch across the lines on Thonpson Rd. DETAILS - Peter Robinson, Ph 027 4312080). Conductor rehung with 2 sleeves use | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-04-19 | c | 0.01545 | 0.00016026 | 2016 | 2015-04-19 | C | 53 | 0.01545 | 0.00016026
4331278 | 2015-04-20 06:59 | 2015-04-20 09:10 | 130.65 | 1 | 130.65 | 130.65 | 127.65 | 0.00039505 | 127.65 | 0.00038598 | 3.0238e-06 | Restore Supply on Device X119 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X119 | Replaced 1x 3A 11kv fuse. 2 fuses out but only one needed to be replaced. Other was OK. Not sure of the cause. All other assets OK. Nothing else replaced or repaired | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.00038598 | 3.024e-06 | 2016 | 2015-04-20 | C | 1 | 0.00038598 | 3.0238e-06
4331281 | 2015-04-20 07:49 | 2015-04-20 08:24 | 34.8333 | 4 | 139.3333 | 34.8333 | 31.8333 | 0.00042131 | 127.3333 | 0.00038503 | 1.2095e-05 | Restore Supply on Device 593 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8185 | Swan Though the lines 2 HV Fuses blown at fuses 8185. 2 X 6 Amp Fuses. | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.00038503 | 1.2095e-05 | 2016 | 2015-04-20 | C | 4 | 0.00038503 | 1.2095e-05
4331307 | 2015-04-20 07:36 | 2015-04-20 10:47 | 190.5667 | 3 | 571.7 | 190.5667 | 187.5667 | 0.0017287 | 562.7 | 0.0017015 | 9.0713e-06 | Restore Supply on Device 4878T | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5841 | CB 5841 Tripped. Lines patrolled & Waihapa site transformers physically checked. No Fault Found. CB closed on site. No SCADA indication of Waihapa site. | F1 | ORIGIN 2 | STRATFORD | Taranaki | WAIHAPA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.0017015 | 9.071e-06 | 2016 | 2015-04-20 | C | 3 | 0.0017015 | 9.0713e-06
4331313 | 2015-04-20 07:43 | 2015-04-20 12:27 | 284.8 | 1 | 284.8 | 284.8 | 281.8 | 0.00086117 | 281.8 | 0.0008521 | 3.0238e-06 | Restore Supply on Device 2135T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2135T | 2 HV Fuses blown. Checked Transfomer no fault found. Replaced 2 HV Fuses 2 x 2Amp HV Fuse Link | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.0008521 | 3.024e-06 | 2016 | 2015-04-20 | C | 1 | 0.0008521 | 3.0238e-06
4333927 | 2015-04-20 11:36 | 2015-04-20 13:57 | 140.8667 | 285 | 29332.8 | 102.9221 | 99.9221 | 0.088695 | 28477.8 | 0.08611 | 0.00086177 | Restore Supply on Device 1087 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1087 | Tripping on Recloser CB1087. Area patrolled / sectionalised but all restored OK. Suspect problem with CB1087, bringing up continuous alarm, failed to operate from NOC or locally. Left bypassed, DNO 150413. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.08611 | 0.00086177 | 2016 | 2015-04-20 | C | 285 | 0.08611 | 0.00086177
4336909 | 2015-04-18 16:47 | 2015-04-18 17:46 | 59 | 475 | 25464 | 53.6084 | 50.6084 | 0.076997 | 24039 | 0.072688 | 0.0014363 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 9225 | 11kV Recreated outage for OMS 4326094, ASW Note: the open point recloser 9405 was closed at the time into kauri Point, CB2-Bowentown feeder to ABS IP534. Orginal Job Notes from OMS: WHB 5 Recloser 9225 tripped O/C, L/O feeder sectionalised no fault found | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-18 | c | 0.072688 | 0.0014363 | 2016 | 2015-04-18 | C | 475 | 0.072688 | 0.0014363
4337499 | 2015-05-14 09:04 | 2015-05-14 12:42 | 218.05 | 20 | 4361 | 218.05 | 215.05 | 0.013187 | 4301 | 0.013005 | 6.0475e-05 | NAPA ID:08123 TP_MASTERTON GXP > CLAREVILLE SUB > CHESTER RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S348 | TRANSFORMER REPLACEMENT. Works location: Hwy 2 Masterton. WO 10160117 | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-05-14 | b | 0.0065026 | 3.0238e-05 | 2016 | 2015-05-14 | B | 20 | 0.013005 | 6.0475e-05
4338002 | 2015-04-20 14:42 | 2015-04-20 17:50 | 188.4167 | 125 | 23552.0833 | 188.4167 | 185.4167 | 0.071216 | 23177.0833 | 0.070082 | 0.00037797 | Restore Supply on Device S105 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 831085 | Outage required between ABS S105 and S138 to replace a broken Pole caused by a truck accident. (Backfeed at Sw/Gear c254). Pole replaced along with a new HV crossarm and hardware. 2 LV Crossarms reused. Relivened OK. awaiting NDR No. from Brad | F2 | HOPE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.070082 | 0.00037797 | 2016 | 2015-04-20 | C | 125 | 0.070082 | 0.00037797
4338576 | 2015-04-20 15:08 | 2015-04-20 17:35 | 147 | 18 | 2646 | 147 | 144 | 0.0080009 | 2592 | 0.0078376 | 5.4428e-05 | Restore Supply on Device T9/287 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | Check if 4338786 (421 Haunui Rd) is related before signing off. 2 Fuses tripped at V83. Ongoing bird problem, reloaded / relivened OK. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.0078376 | 5.4428e-05 | 2016 | 2015-04-20 | C | 18 | 0.0078376 | 5.4428e-05
4338780 | 2015-05-14 06:34 | 2015-05-14 06:54 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08110 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206. Short 10 min outage at beginning and end of day to connect and | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-14 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-14 | B | 16 | 0.00082246 | 4.838e-05
4338783 | 2015-05-07 09:01 | 2015-05-07 13:17 | 256.25 | 34 | 8712.5 | 256.25 | 253.25 | 0.026345 | 8610.5 | 0.026036 | 0.00010281 | NAPA ID:07132 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SC2-102 | CHANGE 33KV / 11KV POLES 209129 209127. Works location: Hwy 2 Omokoroa. IR7180 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-05-07 | b | 0.013018 | 5.1404e-05 | 2016 | 2015-05-07 | B | 34 | 0.026036 | 0.00010281
4338926 | 2015-04-20 17:45 | 2015-04-20 21:59 | 253.4667 | 1 | 253.4667 | 253.4667 | 250.4667 | 0.00076642 | 250.4667 | 0.00075735 | 3.0238e-06 | Restore Supply on Device W2085 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725425 | AS PER BILL ELECTRCIAN FROM LASER )WATER PUMP IS NOT WORKING ITFEEDS WATER TO COWSHED AND FARM) NO WATER TO FARM, THE WATER PUMP IS LOCATED ON OHANGHAI ROAD, HALFWAY DOWN THE HILL BEFORE DAVIDSON ROAD, THE FAULT IS AT POLE#725425, TRANSFORMER# W2094, FUS | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.00075735 | 3.024e-06 | 2016 | 2015-04-20 | C | 1 | 0.00075735 | 3.0238e-06
4338955 | 2015-04-20 18:26 | 2015-04-20 20:59 | 153.3 | 1 | 153.3 | 153.3 | 150.3 | 0.00046354 | 150.3 | 0.00045447 | 3.0238e-06 | Restore Supply on Device Z73 | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 2661 | No power to pump shed - lights working but nothing else - Alex ,Paddocks onsite but no stock in them at the moment, | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.00045447 | 3.024e-06 | 2016 | 2015-04-20 | C | 1 | 0.00045447 | 3.0238e-06
4339023 | 2015-04-20 20:33 | 2015-04-21 00:23 | 229.8333 | 315 | 18101.8 | 57.466 | 54.466 | 0.054736 | 17156.8 | 0.051878 | 0.00095248 | Restore Supply on Device 6427 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W5282 | Replaced 30kVa Transformer W5282 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-20 | c | 0.051878 | 0.00095248 | 2016 | 2015-04-20 | C | 315 | 0.051878 | 0.00095248
4340938 | 2015-04-21 07:43 | 2015-04-21 10:24 | 160.85 | 293 | 8563.45 | 29.2268 | 26.2268 | 0.025894 | 7684.45 | 0.023236 | 0.00088596 | Restore Supply on Device WH217 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH203 | Maryann Dudley phoned 027 484 2650 to advise flashing at pole on boundary of farm along from 876 Ohangai Road and part power to cowshed at 22 Katewheta Road. Advised Brett on 0274301865 and Spelly in control. 11kV ABS WH203 faulty, ASW. ABS WH217 opened t | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-21 | c | 0.023236 | 0.00088596 | 2016 | 2015-04-21 | C | 293 | 0.023236 | 0.00088596
4341558 | 2015-05-19 06:42 | 2015-05-19 07:02 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08112 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-19 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-19 | B | 16 | 0.00082246 | 4.838e-05
4341634 | 2015-05-20 06:56 | 2015-05-20 07:16 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08113 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-20 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-20 | B | 16 | 0.00082246 | 4.838e-05
4341649 | 2015-05-21 05:05 | 2015-05-21 05:25 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08114 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-21 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-21 | B | 16 | 0.00082246 | 4.838e-05
4341708 | 2015-05-22 05:18 | 2015-05-22 05:38 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08115 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-22 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-22 | B | 16 | 0.00082246 | 4.838e-05
4341723 | 2015-05-27 06:45 | 2015-05-27 07:05 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08116 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-27 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-27 | B | 16 | 0.00082246 | 4.838e-05
4341735 | 2015-05-28 06:51 | 2015-05-28 07:11 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08320 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981. Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-28 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-28 | B | 16 | 0.00082246 | 4.838e-05
4341739 | 2015-04-21 08:55 | 2015-04-21 10:57 | 121.8833 | 1 | 121.8833 | 121.8833 | 118.8833 | 0.00036855 | 118.8833 | 0.00035947 | 3.0238e-06 | Restore Supply on Device W2175 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | urupa | This is related to earlier outage oms 4240083 and power was all restored on arrival but needed to check as could not get hold of customer | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-21 | c | 0.00035947 | 3.024e-06 | 2016 | 2015-04-21 | C | 1 | 0.00035947 | 3.0238e-06
4341741 | 2015-05-29 06:17 | 2015-05-29 06:37 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:08323 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-29 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-29 | B | 16 | 0.00082246 | 4.838e-05
4342038 | 2015-05-08 09:25 | 2015-05-08 14:35 | 310 | 15 | 4650 | 310 | 307 | 0.01406 | 4605 | 0.013924 | 4.5356e-05 | NAPA ID:08242 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2146 | To replace some line equipment on SWER transformer structure TC2146 and install a recloser (9901) on the load side of the transformer. Works location: Bradshaw Rd Paeroa WO 10104424 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-05-08 | b | 0.0069622 | 2.2678e-05 | 2016 | 2015-05-08 | B | 15 | 0.013924 | 4.5356e-05
4342240 | 2015-05-01 08:23 | 2015-05-01 15:06 | 402.9167 | 47 | 18937.0833 | 402.9167 | 399.9167 | 0.057261 | 18796.0833 | 0.056835 | 0.00014212 | NAPA ID:08830 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > GRENADA ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/G 9531 | Cut concrete near cable with concrete saw and knock concrete off cable to free it from the concrete securing the water stop cock in case of movement. Works location: Pacific Coast Village, Papamoa. WO 10165991. | F3 | GRENADA ST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-05-01 | b | 0.028417 | 7.1058e-05 | 2016 | 2015-05-01 | B | 47 | 0.056835 | 0.00014212
4342245 | 2015-05-12 00:03 | 2015-05-12 01:35 | 92.5667 | 43 | 2743.4 | 63.8 | 60.8 | 0.0082954 | 2614.4 | 0.0079053 | 0.00013002 | NAPA ID:08184 TP_KOPU GXP > THAMES SUB > POLLEN ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1850 | CONNECT HV CABEL TO TC3832 SORCE A CABEL REPAIRED AND TESTED 26.3.15. Job happening at Monday Midnight (00:01 - 12/05/2015). Works location: Pollen St Thames. WO 30001541 | F2 | POLLEN ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-05-12 | b | 0.0039527 | 6.5011e-05 | 2016 | 2015-05-12 | B | 43 | 0.0079053 | 0.00013002
4343036 | 2015-05-19 08:43 | 2015-05-19 15:51 | 427.8667 | 66 | 28239.2 | 427.8667 | 424.8667 | 0.085389 | 28041.2 | 0.08479 | 0.00019957 | NAPA ID:08255 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2566 | change xarms ,erect poles and move wire on to new poles from poles 787310 to 787407. Works location: Otaurei Rd Taihape. WO 30001023 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-19 | b | 0.042395 | 9.9784e-05 | 2016 | 2015-05-19 | B | 66 | 0.08479 | 0.00019957
4343058 | 2015-04-21 15:33 | 2015-04-21 19:11 | 217.6333 | 25 | 5440.8333 | 217.6333 | 214.6333 | 0.016452 | 5365.8333 | 0.016225 | 7.5594e-05 | Restore Supply on Device T5405 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5405 | Outage required from Fuses TA857 to repair a broken Fuse Holder at Transformer T5405. (All 3 holders / fuses replaced). | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-04-21 | c | 0.016225 | 7.5594e-05 | 2016 | 2015-04-21 | C | 25 | 0.016225 | 7.5594e-05
4343091 | 2015-04-21 16:10 | 2015-04-21 17:49 | 99.55 | 26 | 2588.3 | 99.55 | 96.55 | 0.0078264 | 2510.3 | 0.0075905 | 7.8618e-05 | Restore Supply on Device 595 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 595 | two fuses found blown at Fuses 595 - line Patrolled with no fault found - used 2x 20amp fuses | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-04-21 | c | 0.0075905 | 7.8618e-05 | 2016 | 2015-04-21 | C | 26 | 0.0075905 | 7.8618e-05
4343491 | 2015-04-22 07:55 | 2015-04-22 11:01 | 185.85 | 15 | 2787.75 | 185.85 | 182.85 | 0.0084295 | 2742.75 | 0.0082934 | 4.5356e-05 | Restore Supply on Device SE6-133 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | SE6-133 | Fuse switch SE6-133 found tripped. Dave to carry out cursory line patrol. Nothing found during line patrol. Fuses reloaded & livened ok. Cause unknown. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-04-22 | c | 0.0082934 | 4.5356e-05 | 2016 | 2015-04-22 | C | 15 | 0.0082934 | 4.5356e-05
4343535 | 2015-05-02 09:25 | 2015-05-02 14:18 | 292.7833 | 1 | 292.7833 | 292.7833 | 289.7833 | 0.00088531 | 289.7833 | 0.00087624 | 3.0238e-06 | NAPA ID:08871 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 10TH AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9255 | Isolate Switchgear and replace Switchgear with Motorized Switch Unit. Works location: Cameron Rd WO 30008186 | F2 | 10TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-05-02 | b | 0.00043812 | 1.512e-06 | 2016 | 2015-05-02 | B | 1 | 0.00087624 | 3.0238e-06
4343553 | 2015-04-22 09:22 | 2015-04-22 15:20 | 357.8667 | 2 | 715.7333 | 357.8667 | 354.8667 | 0.0021642 | 709.7333 | 0.0021461 | 6.0475e-06 | Restore Supply on Device TC2-167 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2-167 | Offload transformer TC2-167 for preplanned LV works on Work order 10170109, Brian Fisher. Off @ 09:22/On @ 15:20. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-04-22 | c | 0.0021461 | 6.048e-06 | 2016 | 2015-04-22 | C | 2 | 0.0021461 | 6.0475e-06
4344813 | 2015-04-30 22:06 | 2015-05-01 02:42 | 276.1667 | 127 | 35073.1667 | 276.1667 | 273.1667 | 0.10605 | 34692.1667 | 0.1049 | 0.00038402 | NAPA ID:08186 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5227 | REMOVE LV SWITCHGEAR OF TC5227 AND INSTALL NEW SWITCHGEAR AND FRAME. NOTE LV SWITCHGEAR IS OVERHEATING AND IN DANGER OF FAILING AS PER AMBER DEFECT. | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-04-30 | b | 0.05245 | 0.00019201 | 2016 | 2015-04-30 | B | 127 | 0.1049 | 0.00038402
4345946 | 2015-04-22 12:49 | 2015-04-22 15:11 | 142.2333 | 370 | 1675 | 4.527 | 1.527 | 0.0050648 | 565 | 0.0017084 | 0.0011188 | Restore Supply on Device M2050 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2045 | Transformer M2045 is blown. Transformer M2045 has no LV connected to it. FM is going to cut the transformer & HV fuses away from the overhead line. Transformer still up Pole will need to be removed at some stage. Joe this transformer shows 5 ICP's connect | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-04-22 | c | 0.0017084 | 0.0011188 | 2016 | 2015-04-22 | C | 370 | 0.0017084 | 0.0011188
4346001 | 2015-05-06 08:48 | 2015-05-06 11:29 | 160.3833 | 182 | 6289.6167 | 34.5583 | 31.5583 | 0.019018 | 5743.6167 | 0.017367 | 0.00055032 | NAPA ID:07182 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS A61, A79 | make line gap at transformer T6/251 (towards A61), make line gap at T6/181 (towards A790) remove A79 and A61, change pole P44202, install new safelink 10241 and run new U/G cables, change configuration of network as per attached plan. Job ongoing but outa | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.0086837 | 0.00027516 | 2016 | 2015-05-06 | B | 182 | 0.017367 | 0.00055032
4347453 | 2015-04-22 22:28 | 2015-04-22 22:45 | 16.6167 | 7 | 116.3167 | 16.6167 | 13.6167 | 0.00035171 | 95.3167 | 0.00028821 | 2.1166e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2773 | At 22:28 Tahuna Sub, CB 2 Mangateparu Feeder. Found loose neutral connection at transformer TC2733. Own Isolation & AP. Repaired neutral connection - All OK. Pieter Diedericks Attended. No Materials Used. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-04-22 | c | 0.00028821 | 2.1166e-05 | 2016 | 2015-04-22 | C | 7 | 0.00028821 | 2.1166e-05
4347462 | 2015-04-22 20:21 | 2015-04-23 04:19 | 478.1667 | 738 | 49560.2 | 67.1547 | 64.1547 | 0.14986 | 47346.2 | 0.14316 | 0.0022315 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | F0114 | At 20:21 Browne St Sub, CB 3 Smith St Feeder, Tripped, Ph B Fault, E/F, L/O. Faultmen dispatched and investigation began. BRN 3 was backfeeding part of BRN 9: ABS IC1301 Closed, Recloser 9852 Open. Opened IC1301 and CB 3 Restored at 21:04. Used Recloser 9 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-04-22 | c | 0.14316 | 0.0022315 | 2016 | 2015-04-22 | C | 738 | 0.14316 | 0.0022315
4349365 | 2015-04-22 21:29 | 2015-04-22 23:53 | 144.85 | 106 | 10781.2 | 101.7094 | 98.7094 | 0.0326 | 10463.2 | 0.031638 | 0.00032052 | Restore Supply on Device E33 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P13242 | Tripping on Recloser CB E33 on Phase B O/C, EF. Area patrolled and sectionalised with an Opossum found on Pollock Rd at pole P13242. Removed OK and all relivened. NOTE: None of the Poles down Pollock Rd have Opossum guards fitted. (Transformer Pole the ex | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-04-22 | c | 0.031638 | 0.00032052 | 2016 | 2015-04-22 | C | 106 | 0.031638 | 0.00032052
4349766 | 2015-05-04 09:06 | 2015-05-04 16:06 | 420 | 4 | 1680 | 420 | 417 | 0.0050799 | 1668 | 0.0050436 | 1.2095e-05 | NAPA ID:08211 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC1058 | Replace 11/33kV Poles, crossarms and hardware between poles LAKBRN 099 and 115. Works location: Hinuera Rd Matamata. WO 30001970 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-05-04 | b | 0.0025218 | 6.048e-06 | 2016 | 2015-05-04 | B | 4 | 0.0050436 | 1.2095e-05
4349789 | 2015-04-23 07:48 | 2015-04-23 10:32 | 164.2833 | 556 | 32421.3833 | 58.3118 | 55.3118 | 0.098035 | 30753.3833 | 0.092991 | 0.0016812 | Restore Supply on Device WH1 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 725741 | CB WH1 Trip, No flags. WH1 was also backfeeding a large section of WH2. Fault due to digger bringing down lines on feeder WH2. NDR #43036. Materials used 6x16mm Crimp sleeves & 6mtrs of bare cu. 16mm wire. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-23 | c | 0.092991 | 0.0016812 | 2016 | 2015-04-23 | C | 556 | 0.092991 | 0.0016812
4351974 | 2015-04-23 12:13 | 2015-04-24 01:39 | 806.25 | 1077 | 98687.5167 | 91.6319 | 88.6319 | 0.29841 | 95456.5167 | 0.28864 | 0.0032566 | Restore Supply on Device 7 | 11 | Unplanned | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | 9218/3 | at 12:12 Whitianga Sub, CB 7 Joan Gaskill Drive Feeder, Tripped, E/F, L/O. Report Received from Northpower that they had struck an 11kV Cable while working. Unsure of complete details. Faultman dispatched and fault area isolated at Sw/gear 9218/3. Permit | F3 | JOAN GASKELL DR | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-04-23 | c | 0.28864 | 0.0032566 | 2016 | 2015-04-23 | C | 1077 | 0.28864 | 0.0032566
4355255 | 2015-04-24 04:23 | 2015-04-24 08:31 | 247.9333 | 527 | 32958.4667 | 62.5398 | 59.5398 | 0.099659 | 31377.4667 | 0.094878 | 0.0015935 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole ? FM on Stand down | Sectionaliser 9876/2 Trip A,B,C O/C E/F Tree branch broke & bought down line. Line sectionalised. Isolated at ABS IP598. Line Repaired. Bucket truck needed to carry out repairs. NDR 17973. Materials: 2 full tension namu sleeves, 10m namu conductor. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-04-24 | c | 0.094878 | 0.0015935 | 2016 | 2015-04-24 | C | 527 | 0.094878 | 0.0015935
4356244 | 2015-04-28 10:00 | 2015-04-28 11:20 | 80 | 4 | 320 | 80 | 77 | 0.0009676 | 308 | 0.00093132 | 1.2095e-05 | NAPA ID:08921 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC215 | To replace the broken LV transformer arm, Install a 3 phase 400V Disconector, Repace 400V Arms on ole H0145 & Remove the old TVEPB Phone wired from pole H0144 to H0148. | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-04-28 | b | 0.00046566 | 6.048e-06 | 2016 | 2015-04-28 | B | 4 | 0.00093132 | 1.2095e-05
4356317 | 2015-04-24 09:10 | 2015-04-24 10:34 | 83.8 | 41 | 3435.8 | 83.8 | 80.8 | 0.010389 | 3312.8 | 0.010017 | 0.00012397 | Restore Supply on Device TC3036 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3036 | Isloation of Transformer TC3036 to install LV Disconnector. FM Fames Kennerly. | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-04-24 | c | 0.010017 | 0.00012397 | 2016 | 2015-04-24 | C | 41 | 0.010017 | 0.00012397
4356575 | 2015-05-12 09:31 | 2015-05-12 15:34 | 362.8167 | 39 | 14149.85 | 362.8167 | 359.8167 | 0.042786 | 14032.85 | 0.042432 | 0.00011793 | NAPA ID:08648 TP_HAWERA GXP > MANAIA SUB > MANAIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 8762 | Replace broken double pole 718549. Works location: South Rd Manaia. WO 10161325 | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-05-12 | b | 0.021216 | 5.8963e-05 | 2016 | 2015-05-12 | B | 39 | 0.042432 | 0.00011793
4356953 | 2015-05-14 08:35 | 2015-05-14 14:40 | 364.6167 | 21 | 7656.95 | 364.6167 | 361.6167 | 0.023153 | 7593.95 | 0.022962 | 6.3499e-05 | NAPA ID:08818 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC404 | Install Pole and new transformer to eleviate Power quality issue's PQI#1172. Works location: Pukahu Rd Paeroa. WO 10138970 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-14 | b | 0.011481 | 3.1749e-05 | 2016 | 2015-05-14 | B | 21 | 0.022962 | 6.3499e-05
4357043 | 2015-04-28 11:20 | 2015-04-28 17:24 | 364 | 1 | 364 | 364 | 361 | 0.0011006 | 361 | 0.0010916 | 3.0238e-06 | NAPA ID:08915 TP_HINUERA GXP > TIRAU SUB > NZDC A & B | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | T4512 | Isolate TX T4512 so Kiwi Control can replace the LV switchboard | F1 | NZDG TIRAU 1 | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-04-28 | b | 0.00054579 | 1.512e-06 | 2016 | 2015-04-28 | B | 1 | 0.0010916 | 3.0238e-06
4361524 | 2015-04-24 17:49 | 2015-04-24 19:15 | 86.7833 | 1 | 86.7833 | 86.7833 | 83.7833 | 0.00026241 | 83.7833 | 0.00025334 | 3.0238e-06 | Restore Supply on Device T1109 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 7598 | The customer has advised that there is a pole fuse out at the irrigation that is causing power outage. Fuse found blown at Fuses 7598 - line patrolled possible duck strike (pond under lines) - used 2x10 fuses. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-24 | c | 0.00025334 | 3.024e-06 | 2016 | 2015-04-24 | C | 1 | 0.00025334 | 3.0238e-06
4362229 | 2015-04-25 20:01 | 2015-04-25 21:38 | 96.65 | 2 | 193.3 | 96.65 | 93.65 | 0.00058449 | 187.3 | 0.00056635 | 6.0475e-06 | Restore Supply on Device T4/2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses E93 | Replaced 2X HV fuses | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-04-25 | c | 0.00056635 | 6.048e-06 | 2016 | 2015-04-25 | C | 2 | 0.00056635 | 6.0475e-06
4362236 | 2015-04-25 23:23 | 2015-04-26 01:30 | 126.7333 | 322 | 40808.1333 | 126.7333 | 123.7333 | 0.12339 | 39842.1333 | 0.12047 | 0.00097365 | Electric Job | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | pole 707713 | Replaced pole 707713 and 1 crossarm complete and lv cble duct. NDR number 045605. | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-04-25 | c | 0.12047 | 0.00097365 | 2016 | 2015-04-25 | C | 322 | 0.12047 | 0.00097365
4365077 | 2015-04-26 02:38 | 2015-04-26 04:50 | 132.0333 | 826 | 37215.4 | 45.055 | 42.055 | 0.11253 | 34737.4 | 0.10504 | 0.0024976 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 11kv Line | Turitea CB4 Aokautere A/R Tripped E/F. Line sectionalised and possum located at pole P44494. Possum removed. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-04-26 | c | 0.10504 | 0.0024976 | 2016 | 2015-04-26 | C | 826 | 0.10504 | 0.0024976
4367506 | 2015-04-26 07:15 | 2015-04-26 07:51 | 35.9667 | 18 | 647.4 | 35.9667 | 32.9667 | 0.0019576 | 593.4 | 0.0017943 | 5.4428e-05 | Restore Supply on Device S23 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/324 | Burnt Jumper located at transformer T8/324. Repaired Jumper. 1 metre of conductor used. Phil Barnes attended. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-04-26 | c | 0.0017943 | 5.4428e-05 | 2016 | 2015-04-26 | C | 18 | 0.0017943 | 5.4428e-05
4367600 | 2015-04-26 12:27 | 2015-04-26 13:27 | 59.3167 | 1 | 59.3167 | 59.3167 | 56.3167 | 0.00017936 | 56.3167 | 0.00017029 | 3.0238e-06 | Restore Supply on Device X39 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X39 | plz check if oms 4367615 related 70 Western Line Part power. Lead off at Transformer X39 | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-04-26 | c | 0.00017029 | 3.024e-06 | 2016 | 2015-04-26 | C | 1 | 0.00017029 | 3.0238e-06
4367615 | 2015-04-26 12:57 | 2015-04-26 13:28 | 30.8333 | 1 | 30.8333 | 30.8333 | 27.8333 | 9.3233e-05 | 27.8333 | 8.4161e-05 | 3.0238e-06 | Restore Supply on Device X38 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | x38 | poss related to oms 4367600 - advised Lianne at svs hub of this job part Of OMS 4367600 Email to Jo to check SAIDI | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-04-26 | c | 8.4161e-05 | 3.024e-06 | 2016 | 2015-04-26 | C | 1 | 8.4161e-05 | 3.0238e-06
4367674 | 2015-04-26 17:12 | 2015-04-26 19:37 | 144.95 | 30 | 4050.9833 | 135.0328 | 132.0328 | 0.012249 | 3960.9833 | 0.011977 | 9.0713e-05 | Restore Supply on Device 1382 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8484 | Replaced 2 X hv fuses @ 8484. | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-26 | c | 0.011977 | 9.0713e-05 | 2016 | 2015-04-26 | C | 30 | 0.011977 | 9.0713e-05
4368965 | 2015-04-27 07:32 | 2015-04-27 08:40 | 67.55 | 336 | 20784.25 | 61.8579 | 58.8579 | 0.062847 | 19776.25 | 0.059799 | 0.001016 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 6 | CB 6 tripped on B phase O/C flags line was patrolled no fault was found, suspect tripping was caused when LV line broke at transformer X1237 and flicked up into the 11 KV lines. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.059799 | 0.001016 | 2016 | 2015-04-27 | C | 336 | 0.059799 | 0.001016
4370010 | 2015-04-27 09:09 | 2015-04-27 13:58 | 288.6 | 123 | 21358.7333 | 173.6482 | 170.6482 | 0.064584 | 20989.7333 | 0.063468 | 0.00037192 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793535 | Recloser 4236/2 tripped on A & C phase O/C & E/F flags, received call of line down on SH3, line was isolated at ABS's 434 & 1184 to repair the line down at pole 793535. 3 X 25 mm sleeves used. 10 meters 25mm copper conductor replaced. NDR: 30417. This job | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.063468 | 0.00037192 | 2016 | 2015-04-27 | C | 123 | 0.063468 | 0.00037192
4370185 | 2015-04-27 11:32 | 2015-04-27 20:31 | 538.9 | 34 | 12942.4 | 380.6588 | 377.6588 | 0.039135 | 12840.4 | 0.038826 | 0.00010281 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 796998 | check if OMS 4370190 and 4372212 is related. Broken 11kV cross arm requesting 2r to replace xarm and needs assistance. Faultman isolated the line at Fuses 7447 to replace cross arm on pole 796998. 1 x cross arm & all hardware replaced.Transformer T1305 wa | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.038826 | 0.00010281 | 2016 | 2015-04-27 | C | 34 | 0.038826 | 0.00010281
4370741 | 2015-04-27 11:13 | 2015-04-27 12:16 | 62.1833 | 328 | 12839.1667 | 39.1438 | 36.1438 | 0.038823 | 11855.1667 | 0.035847 | 0.00099179 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 263373 | Lines down at 1 Rowe Road. WBY 7 Recloser 9209 tripped E/F, O/C L/O. Found king bolt failed at pole 263373. Isolation at ABS SE4 011 ( no back feed ) remainder of feeder returned to service via Recloser 9209. King bolt replaced, all service restored. Mate | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.035847 | 0.00099179 | 2016 | 2015-04-27 | C | 328 | 0.035847 | 0.00099179
4372225 | 2015-04-27 11:37 | 2015-04-27 13:13 | 96.8167 | 1 | 96.8167 | 96.8167 | 93.8167 | 0.00029275 | 93.8167 | 0.00028368 | 3.0238e-06 | Restore Supply on Device TE4-223 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of feeder fault | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.00028368 | 3.024e-06 | 2016 | 2015-04-27 | C | 1 | 0.00028368 | 3.0238e-06
4372298 | 2015-04-27 12:07 | 2015-04-27 14:25 | 138.0167 | 6 | 828.1 | 138.0167 | 135.0167 | 0.002504 | 810.1 | 0.0024495 | 1.8143e-05 | Restore Supply on Device TD5-202 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5 137 | Replace 1 x 8A O/H, H/V fuse ( bark on line ). | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.0024495 | 1.8143e-05 | 2016 | 2015-04-27 | C | 6 | 0.0024495 | 1.8143e-05
4372307 | 2015-04-27 12:18 | 2015-04-27 14:56 | 158 | 28 | 4424 | 158 | 155 | 0.013377 | 4340 | 0.013123 | 8.4665e-05 | Restore Supply on Device 4004 | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 783018 | Recloser 4004 tripped on B phase O/C flags line has been patrolled and no fault was found. REF to OMS: 4366827 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.013123 | 8.4665e-05 | 2016 | 2015-04-27 | C | 28 | 0.013123 | 8.4665e-05
4372355 | 2015-04-27 11:49 | 2015-04-27 17:08 | 319 | 29 | 9251 | 319 | 316 | 0.027973 | 9164 | 0.02771 | 8.7689e-05 | Restore Supply on Device 6289 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 704549 | Faultman found lines down, line was isolated at Fuses 6289. Faultman had to leave site to go isolate another line that had cross arm on fire as he was the only faultman in area at time, before returning to repair the lines down. 1 Xbinder, 1 metre 16mm c | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.02771 | 8.7689e-05 | 2016 | 2015-04-27 | C | 29 | 0.02771 | 8.7689e-05
4372395 | 2015-04-27 12:52 | 2015-04-27 18:00 | 307.9833 | 259 | 35736.6667 | 137.9794 | 134.9794 | 0.10806 | 34959.6667 | 0.10571 | 0.00078315 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | W13399 | TAI 5 Recloser 9170 tripped E/F, L/O. Feeder sectionalised with fault found to be beyond ABS 323. Isolation at ABS 323 ( spur line no back feeds ) Remainder of feeder returned to service. Ben Edwards own isolation & issues own AP to repair lines down (Com | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.10571 | 0.00078315 | 2016 | 2015-04-27 | C | 259 | 0.10571 | 0.00078315
4373378 | 2015-04-27 13:06 | 2015-04-27 15:10 | 124.1 | 5 | 620.5 | 124.1 | 121.1 | 0.0018762 | 605.5 | 0.0018309 | 1.5119e-05 | Restore Supply on Device TB2-090 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SB2 115 | Check if oms 4374792 is related. Replace 2 x 10 A O/H H/V fuses ( Line clash suspected ). | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.0018309 | 1.5119e-05 | 2016 | 2015-04-27 | C | 5 | 0.0018309 | 1.5119e-05
4373385 | 2015-04-27 13:08 | 2015-04-27 16:30 | 201.9833 | 103 | 11239.4833 | 109.1212 | 106.1212 | 0.033986 | 10930.4833 | 0.033051 | 0.00031145 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 221803 | TPV 4 Sectionaliser 9834 tripped E/F, B Ph O/C L/O. Tree found on lines at pole 221803. Isolation at ABS SE6 176 to cut line break pole 221803. ( isolating transformers TE6 127 & TE6 328 ) . After line break made ABS SE6 176 closed & rest of feeder retur | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.033051 | 0.00031145 | 2016 | 2015-04-27 | C | 103 | 0.033051 | 0.00031145
4374507 | 2015-04-27 13:12 | 2015-04-27 18:21 | 308.9333 | 59 | 18227.0667 | 308.9333 | 305.9333 | 0.055114 | 18050.0667 | 0.054579 | 0.0001784 | Restore Supply on Device 5298E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710197 | Check is OMS 4374781, 4374818, 4374829 and 4374771are related. Faultman found floating wire on pole 710197, line was isolated at Fuses 5555 to replace burnt cross arm. 1 x cross arm & all it's hardware replaced. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.054579 | 0.0001784 | 2016 | 2015-04-27 | C | 59 | 0.054579 | 0.0001784
4375540 | 2015-04-27 15:38 | 2015-04-27 20:15 | 277.75 | 678 | 89902.8 | 132.6 | 129.6 | 0.27184 | 87868.8 | 0.26569 | 0.0020501 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P218384 | advised hub and control that line down int of wilson road north and spencer avenue te puke f 1833921 need eta advised fire eta 4.30pm. FM REQUESTING 2R TO REPLACE LV AND HV LINES AND LV XARMS PKW 1 Recloser 9513 tripped E/F, O/C, L/O. report of lines dow | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.26569 | 0.0020501 | 2016 | 2015-04-27 | C | 678 | 0.26569 | 0.0020501
4378070 | 2015-04-27 19:49 | 2015-04-27 22:23 | 153.35 | 403 | 36567.4 | 90.738 | 87.738 | 0.11057 | 35358.4 | 0.10692 | 0.0012186 | Restore Supply on Device TC4867 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | H1459 | Fire comms #F1834050. ETA of 10 mins given. Faultman confirmed CB tripped even though showing closed ABS 2575 dress open to create actual outage refer OMS 4375540. Pole H1459 broken and completely clear of network, Cable twisted together at this location, | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-04-27 | c | 0.10692 | 0.0012186 | 2016 | 2015-04-27 | C | 403 | 0.10692 | 0.0012186
4378086 | 2015-04-27 19:57 | 2015-04-28 02:16 | 379.0167 | 1 | 379.0167 | 379.0167 | 376.0167 | 0.0011461 | 376.0167 | 0.001137 | 3.0238e-06 | Restore Supply on Device 533 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Transformer 469 | Changed 30kvA transformer Installed LV Fuses as nothing there all Power back on at 0135 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.001137 | 3.024e-06 | 2016 | 2015-04-27 | C | 1 | 0.001137 | 3.0238e-06
4378232 | 2015-04-27 20:38 | 2015-04-27 21:13 | 35.35 | 183 | 6469.05 | 35.35 | 32.35 | 0.019561 | 5920.05 | 0.017901 | 0.00055335 | Restore Supply on Device T1235 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser C216 | Recloser C216 aws found open. Reclosed once faultman on site all good. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.017901 | 0.00055335 | 2016 | 2015-04-27 | C | 183 | 0.017901 | 0.00055335
4378989 | 2015-04-27 20:55 | 2015-04-28 12:40 | 944.6667 | 34 | 32118.6667 | 944.6667 | 941.6667 | 0.097119 | 32016.6667 | 0.096811 | 0.00010281 | Restore Supply on Device 4997 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5546 | Line patrolled. No Fault found. Fuses 5546 Found Open. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.096811 | 0.00010281 | 2016 | 2015-04-27 | C | 34 | 0.096811 | 0.00010281
4379515 | 2015-04-27 21:10 | 2015-04-28 02:48 | 337.4667 | 269 | 31239 | 116.1301 | 113.1301 | 0.094459 | 30432 | 0.092019 | 0.00081339 | Restore Supply on Device 7131 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 709135 | Tree in Lines at Pole 709135 called out Tricky Trees to remove tree. NDR TBA | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-27 | c | 0.092019 | 0.00081339 | 2016 | 2015-04-27 | C | 269 | 0.092019 | 0.00081339
4380555 | 2015-04-28 11:35 | 2015-04-28 12:42 | 67.4333 | 67 | 4518.0333 | 67.4333 | 64.4333 | 0.013661 | 4317.0333 | 0.013054 | 0.00020259 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole H1459, Landsdowne Road, Waharoa | Replace broken pole H1459. Also need to check CB3 as unable to control from NOC. Related to car vs pole job 4378070 from 27/04. SCADA card replaced at walton sub station due to rodent damage. No LOS | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-04-28 | c | 0.013054 | 0.00020259 | 2016 | 2015-04-28 | C | 67 | 0.013054 | 0.00020259
4380601 | 2015-04-28 00:07 | 2015-04-28 00:55 | 48.2667 | 1 | 48.2667 | 48.2667 | 45.2667 | 0.00014595 | 45.2667 | 0.00013688 | 3.0238e-06 | Restore Supply on Device 1192 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1192 | 2 X3 amp | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.00013688 | 3.024e-06 | 2016 | 2015-04-28 | C | 1 | 0.00013688 | 3.0238e-06
4380630 | 2015-04-28 03:15 | 2015-04-28 16:05 | 770.35 | 3 | 2311.05 | 770.35 | 767.35 | 0.0069881 | 2302.05 | 0.0069608 | 9.0713e-06 | Restore Supply on Device 8834 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 739344 | Repair/ Replace Crossarms & conductor at pole 739344 due to tree falling through lines. Islation Fuses 8834 for the night, 28/04 isolation was fuses 5453 so that wires could be reconnected at the fuses 8834. no back feeds available 2 crossarms c/w insulat | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.0069608 | 9.071e-06 | 2016 | 2015-04-28 | C | 3 | 0.0069608 | 9.0713e-06
4381939 | 2015-04-28 07:15 | 2015-04-28 12:00 | 284.5167 | 4 | 1136.3833 | 284.0958 | 281.0958 | 0.0034362 | 1124.3833 | 0.0033999 | 1.2095e-05 | Restore Supply on Device T3364 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T3364 | 11kV cable fault suspected at Transformer 3364. Fuses 7681 open, Generator installed at t3364. Followup job to be initiated. | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.0033999 | 1.2095e-05 | 2016 | 2015-04-28 | C | 4 | 0.0033999 | 1.2095e-05
4381961 | 2015-04-28 09:50 | 2015-04-28 12:44 | 174 | 72 | 12528 | 174 | 171 | 0.037882 | 12312 | 0.037229 | 0.00021771 | Restore Supply on Device 4031T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740906 | ICP USED OF NEAREST ADDRESS. ADVISED HUB JOANNE. TONY FUSES 5196. HV WORKED THROUGH CONTROL REPLACED DDO HOLDER AND FUSE 25 AMP HV OH POLE 740906 DUE TO AGE. SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED. FULL POWER RESTO | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.037229 | 0.00021771 | 2016 | 2015-04-28 | C | 72 | 0.037229 | 0.00021771
4382442 | 2015-04-28 11:02 | 2015-04-28 11:38 | 35.6833 | 28 | 999.1333 | 35.6833 | 32.6833 | 0.0030211 | 915.1333 | 0.0027671 | 8.4665e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786053 | 1R Carryout line patrol after ongoing fault. Line patrol found a floating conductor - isolation required from Fuses 2537 to ABS 1375 with backfeed at ABS 2590. One 11kV Insulator replaced, rebound OK and restored to service. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.0027671 | 8.4665e-05 | 2016 | 2015-04-28 | C | 28 | 0.0027671 | 8.4665e-05
4382758 | 2015-04-28 08:24 | 2015-04-28 10:35 | 131 | 3 | 392.9667 | 130.9889 | 127.9889 | 0.0011882 | 383.9667 | 0.001161 | 9.0713e-06 | Restore Supply on Device TC3984 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP671 | 2 fuse blown at FP761 Swan Through lines. Dead Swan Visually seen (RIP) OMS 4382758 on up stream side of fuses so wouldn't roll up. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-04-28 | c | 0.001161 | 9.071e-06 | 2016 | 2015-04-28 | C | 3 | 0.001161 | 9.0713e-06
4385251 | 2015-04-28 10:12 | 2015-04-28 10:53 | 41 | 641 | 18823.9 | 29.3665 | 26.3665 | 0.056919 | 16900.9 | 0.051104 | 0.0019382 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 752367 | Fault found to be a floating wire up korito Rd at pole752367 OMS 4387735 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.051104 | 0.0019382 | 2016 | 2015-04-28 | C | 641 | 0.051104 | 0.0019382
4385894 | 2015-04-28 16:55 | 2015-04-28 17:19 | 23.5667 | 1 | 23.5667 | 23.5667 | 20.5667 | 7.126e-05 | 20.5667 | 6.2189e-05 | 3.0238e-06 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 722763 | 1 HT fuse found tripped - Failed to reload. Isolation required from Fuses WH819 to repair a damaged jumper at Transformer W5013. Relivened OK, suspect bird strike. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-28 | c | 6.2189e-05 | 3.024e-06 | 2016 | 2015-04-28 | C | 1 | 6.2189e-05 | 3.0238e-06
4386513 | 2015-04-28 12:28 | 2015-04-28 13:47 | 78.6167 | 49 | 3826 | 78.0816 | 75.0816 | 0.011569 | 3679 | 0.011124 | 0.00014816 | Restore Supply on Device N2205 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712011 | ADVISED SHANNON AT HUB. CONTROL ADVISED. Part of the parent outage 4389710. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.011124 | 0.00014816 | 2016 | 2015-04-28 | C | 49 | 0.011124 | 0.00014816
4387270 | 2015-04-28 13:40 | 2015-04-28 15:10 | 89.7 | 6 | 984.9833 | 164.1639 | 161.1639 | 0.0029784 | 966.9833 | 0.0029239 | 1.8143e-05 | Restore Supply on Device 3327T | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 709461 | approx 4kms up Matau North Road, - trees in the lines and line hanging low. ADVISED JOANNE HUB 3.43pm Shan asked to have a crew replacement. Crossarm tipped over by tree branch, crossarm braces re straightened at Pole 709461. Isolation at Fuses 12006 No B | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.0029239 | 1.8143e-05 | 2016 | 2015-04-28 | C | 6 | 0.0029239 | 1.8143e-05
4387735 | 2015-04-28 10:12 | 2015-04-28 13:42 | 209.4333 | 35 | 7330.1667 | 209.4333 | 206.4333 | 0.022165 | 7225.1667 | 0.021847 | 0.00010583 | Restore Supply on Device 8253 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752367 | Floating wire at Pole 752367 Caused feeder to trip on OMS4385251. Wire rebound in Isolation at Fuses 8253 no Back feeds available | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-04-28 | c | 0.021847 | 0.00010583 | 2016 | 2015-04-28 | C | 35 | 0.021847 | 0.00010583
4387821 | 2015-05-13 11:39 | 2015-05-13 15:04 | 205.2667 | 12 | 2463.2 | 205.2667 | 202.2667 | 0.0074481 | 2427.2 | 0.0073393 | 3.6285e-05 | NAPA ID:07822 TP_KOPU GXP > KEREPEHI SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC428 | Replace in-line H structure O14024/O14025 with single 11m Busck including replacement transformer TC428 Live Line Break at Pole O3694. Works location: Hwy 25 Thames. WO 10162320 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-13 | b | 0.0036696 | 1.8143e-05 | 2016 | 2015-05-13 | B | 12 | 0.0073393 | 3.6285e-05
4387832 | 2015-05-01 12:27 | 2015-05-01 12:40 | 13 | 4 | 52 | 13 | 10 | 0.00015724 | 40 | 0.00012095 | 1.2095e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Buchanan Place, Masterton | 2R investigate cable Fault - T3364, assign Brian butler (Wairarapa HV). Original OMS 4381939 BERNIE ADVISED THEY ARE ON GENERATOR. 30/4 - 3.19pm - email sent to svshub for follow up | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.00012095 | 1.2095e-05 | 2016 | 2015-05-01 | C | 4 | 0.00012095 | 1.2095e-05
4387851 | 2015-04-28 12:13 | 2015-04-28 14:32 | 139.5167 | 1227 | 84994.7833 | 69.2704 | 66.2704 | 0.257 | 81313.7833 | 0.24587 | 0.0037102 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 1 | Feeder Sectionalised but no fault found. Lots of birds around. Suspect a Bird Strike. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-28 | c | 0.24587 | 0.0037102 | 2016 | 2015-04-28 | C | 1227 | 0.24587 | 0.0037102
4389782 | 2015-04-28 12:59 | 2015-04-29 02:28 | 808.5667 | 1052 | 97946 | 93.1046 | 90.1046 | 0.29617 | 94790 | 0.28662 | 0.003181 | Restore Supply on Device 6 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Between Link boxes TD4 533 & TD4 525 | fn requesting 2r to test and locate underground cable fault test equipment required to be bought to site. 121 victory street tauranga link box sd4533. hilton leaving site at 2.56. 5.19pm Andy leaving site, Marc staying onsite. Cable fault ( 1 x core ) bet | F3 | VICTORY STREET | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-04-28 | c | 0.28662 | 0.003181 | 2016 | 2015-04-28 | C | 1052 | 0.28662 | 0.003181
4392418 | 2015-04-28 08:34 | 2015-04-28 13:50 | 316 | 9 | 2844 | 316 | 313 | 0.0085996 | 2817 | 0.0085179 | 2.7214e-05 | Restore Supply on Device TC673 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC 673, FP935 | Tied to Stu Simpsons Job. OMS 4382801 2 x 3A HV Fuses Replaced | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-04-28 | c | 0.0085179 | 2.7214e-05 | 2016 | 2015-04-28 | C | 9 | 0.0085179 | 2.7214e-05
4396355 | 2015-04-29 03:24 | 2015-04-29 06:48 | 204.4833 | 1227 | 139895.7167 | 114.0144 | 111.0144 | 0.42301 | 136214.7167 | 0.41188 | 0.0037102 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 1 Pongakawa | PKW CB1 & recloser 9513 tripped A, B & C ph O/C, E/F L/O ABR scheme operated rec 9548 opened & 9760 closed. Feeder sectionalised nothing found | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-29 | c | 0.41188 | 0.0037102 | 2016 | 2015-04-29 | C | 1227 | 0.41188 | 0.0037102
4398186 | 2015-04-29 07:14 | 2015-04-29 08:35 | 80.7333 | 298 | 22666.0667 | 76.0606 | 73.0606 | 0.068537 | 21772.0667 | 0.065834 | 0.00090108 | Restore Supply on Device T11 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842589 | CB T11 Tripped b Ph O/C E/F - Broken Binder found at Pole 842589 during sectionlising - Isolated at ABS's 6127, 6145 & 8903/1 - Binder Replaced - Used 1x Binder | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0.065834 | 0.00090108 | 2016 | 2015-04-29 | C | 298 | 0.065834 | 0.00090108
4398835 | 2015-05-21 10:01 | 2015-05-21 10:47 | 46.4333 | 177 | 8218.7 | 46.4333 | 43.4333 | 0.024851 | 7687.7 | 0.023246 | 0.00053521 | NAPA ID:07414 TP_TAURANGA 33 GXP > OTUMOETAI SUB > VALE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC4-001 | INSTALL HV - LV POLE. Works location: Whitaker St. WO 10148312 | F3 | VALE ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-05-21 | b | 0.011623 | 0.0002676 | 2016 | 2015-05-21 | B | 177 | 0.023246 | 0.00053521
4398847 | 2015-05-20 09:04 | 2015-05-20 15:21 | 376.8333 | 206 | 77627.6667 | 376.8333 | 373.8333 | 0.23473 | 77009.6667 | 0.23286 | 0.00062289 | NAPA ID:07413 TP_TAURANGA 33 GXP > OTUMOETAI SUB > VALE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 206257 | 1/ BREAK JUMPERS AT POLE 206257. 2/ REPLACE POLES AND XARMS. 3 RE MAKE JUMPERS AT POLE 2306257. Works location: Lemon Grove Ave.WO 10148312 | F3 | VALE ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-05-20 | b | 0.11643 | 0.00031145 | 2016 | 2015-05-20 | B | 206 | 0.23286 | 0.00062289
4399048 | 2015-04-29 10:19 | 2015-04-29 11:57 | 97.6667 | 58 | 5664.6667 | 97.6667 | 94.6667 | 0.017129 | 5490.6667 | 0.016602 | 0.00017538 | Restore Supply on Device WH860 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 722745 | Replace Crossarm at pole 722745. Parent job is 4356486 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-04-29 | b | 0.0083012 | 8.7689e-05 | 2016 | 2015-04-29 | B | 58 | 0.016602 | 0.00017538
4399455 | 2015-04-29 12:47 | 2015-04-30 12:00 | 1393.0667 | 1227 | 34140.9833 | 27.8248 | 24.8248 | 0.10323 | 30459.9833 | 0.092104 | 0.0037102 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | PKW CB 1 | CB1 Trip. E/F. L/O. Backfeeds put in up to Recloser 9513 via RS9460 and Recloser 9548 via RS9760. Rest of feeder sectionalised but no fault found. Feeder has been split up into sections to try and narrow down the fault. Further investigation required. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-29 | c | 0.092104 | 0.0037102 | 2016 | 2015-04-29 | C | 1227 | 0.092104 | 0.0037102
4401908 | 2015-04-29 16:03 | 2015-04-29 18:25 | 142 | 253 | 15440.05 | 61.0279 | 58.0279 | 0.046687 | 14681.05 | 0.044392 | 0.00076501 | Restore Supply on Device C927 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 799400 | CB C927 tripped on B phase O/C & E/F flags, line was sectionalise and a line was found down at transformer T3689 on pole 799400, line was isolated at ABS's S512 & s588 to repair the line. This job is a 2 R job. 4 meters 25mm Ali conductor & 4 fargo joints | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0.044392 | 0.00076501 | 2016 | 2015-04-29 | C | 253 | 0.044392 | 0.00076501
4403374 | 2015-04-29 20:46 | 2015-04-29 22:10 | 84 | 7 | 588 | 84 | 81 | 0.001778 | 567 | 0.0017145 | 2.1166e-05 | Restore Supply on Device C27 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P32241 | Isolation at Fuses C27. Suspect line clash. Moved insulator over on crossarm to better regulate lines. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0.0017145 | 2.1166e-05 | 2016 | 2015-04-29 | C | 7 | 0.0017145 | 2.1166e-05
4403386 | 2015-04-29 19:26 | 2015-04-29 19:29 | 3.2333 | 1 | 3.2333 | 3.2333 | 0.23333 | 9.7768e-06 | 0 | 0 | 3.0238e-06 | Restore Supply on Device T666 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | T666 | Rapid# 58 Somerset Rd, Aprox 800 mtrs down driveway, past cowshed and towards the back of the farm TX replaced - Power restored. Have asked FM to contact control to advise of completion. Replaced 3Phase, 25kVA due to short on LV Bushings. Unknown cause. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0 | 3.024e-06 | 2016 | 2015-04-29 | C | 1 | 0 | 3.0238e-06
4403437 | 2015-04-29 21:43 | 2015-04-29 22:19 | 36.1667 | 1 | 36.1667 | 36.1667 | 33.1667 | 0.00010936 | 33.1667 | 0.00010029 | 3.0238e-06 | Restore Supply on Device M4120 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M4120 | Repair broken HV jumper due to age. Isolated at HV fuses M4120. Materials 1 x 3amp HV link. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0.00010029 | 3.024e-06 | 2016 | 2015-04-29 | C | 1 | 0.00010029 | 3.0238e-06
4403442 | 2015-04-29 20:37 | 2015-04-30 08:56 | 738.9333 | 72 | 52440.85 | 728.3451 | 725.3451 | 0.15857 | 52224.85 | 0.15792 | 0.00021771 | Restore Supply on Device V67 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P41979 | Repair Broken jumper at Fuses V68 due to corrosion.. Nil materials used | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-04-29 | c | 0.15792 | 0.00021771 | 2016 | 2015-04-29 | C | 72 | 0.15792 | 0.00021771
4407251 | 2015-04-29 23:16 | 2015-04-30 01:40 | 143.8167 | 1 | 143.8167 | 143.8167 | 140.8167 | 0.00043487 | 140.8167 | 0.0004258 | 3.0238e-06 | Restore Supply on Device TC688 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fused ABS IP416 | repaired under oms 4403669 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-04-29 | c | 0.0004258 | 3.024e-06 | 2016 | 2015-04-29 | C | 1 | 0.0004258 | 3.0238e-06
4407255 | 2015-04-30 01:41 | 2015-04-30 01:56 | 15.45 | 284 | 4387.8 | 15.45 | 12.45 | 0.013268 | 3535.8 | 0.010691 | 0.00085875 | Restore Supply on Device RP14 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RP14 | COR 1Recloser RP14 tripped L/O, closed & held 15 min later, not patrolled | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-04-30 | c | 0.010691 | 0.00085875 | 2016 | 2015-04-30 | C | 284 | 0.010691 | 0.00085875
4408561 | 2015-04-30 03:43 | 2015-04-30 06:26 | 162.8 | 299 | 10031.0667 | 33.5487 | 30.5487 | 0.030332 | 9134.0667 | 0.027619 | 0.0009041 | Restore Supply on Device 6561-2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6561 | RS 6561/2 Tripped O/C B & C Ph A/R - Line Patrolled with no Fault found | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.027619 | 0.0009041 | 2016 | 2015-04-30 | C | 299 | 0.027619 | 0.0009041
4409767 | 2015-04-30 00:49 | 2015-04-30 04:07 | 197.7667 | 1 | 197.7667 | 197.7667 | 194.7667 | 0.000598 | 194.7667 | 0.00058893 | 3.0238e-06 | Restore Supply on Device TD3-155 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses SD3 082 | Comleted under oms 4407210 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-04-30 | c | 0.00058893 | 3.024e-06 | 2016 | 2015-04-30 | C | 1 | 0.00058893 | 3.0238e-06
4410546 | 2015-04-30 07:11 | 2015-04-30 07:12 | 1 | 154 | 154 | 1 | -2 | 0.00046566 | 0 | 0 | 0.00046566 | Restore Supply on Device H41 | 6.6 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | H41 | Trees in line on load side of ABS 5275. Tree cutters coming out to trim trees. Asplundh cleared trees hv oh abs 5275 unknown ownership of trees | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0 | 0.00046566 | 2016 | 2015-04-30 | C | 154 | 0 | 0.00046566
4411170 | 2015-04-30 09:08 | 2015-04-30 10:47 | 99 | 5 | 495 | 99 | 96 | 0.0014968 | 480 | 0.0014514 | 1.5119e-05 | Restore Supply on Device 7610 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7610 | 2x 10amp HV Fuses replaced cause - bird strike goose has flown into lines. Sam worked through control. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.0014514 | 1.5119e-05 | 2016 | 2015-04-30 | C | 5 | 0.0014514 | 1.5119e-05
4411327 | 2015-04-30 09:11 | 2015-04-30 15:03 | 351.9167 | 79 | 22815.7167 | 288.8065 | 285.8065 | 0.068989 | 22578.7167 | 0.068273 | 0.00023888 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 838000 | Recloser C281 tripped on E/F flags.line waspatrolled and sectionalised and faultman found a tree had fallen through the lines and broken a pole 838000 and cross arms.Tree was outside of the notice zone 1 x 10meter pole replaced. 2 x cross arms & all hardw | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.068273 | 0.00023888 | 2016 | 2015-04-30 | C | 79 | 0.068273 | 0.00023888
4411876 | 2015-04-30 10:44 | 2015-04-30 11:31 | 47.2333 | 22 | 1039.1333 | 47.2333 | 44.2333 | 0.0031421 | 973.1333 | 0.0029425 | 6.6523e-05 | Restore Supply on Device SE7-005 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218000 | Faulty insulator identified on pole # 218000 while carrying out line patrol instigated from numerous recent trippings (OMS 4399455) Emergency shutdown between ABS IP515 & SE7-005 to replace pin & insulator. All supply restored following replacement & abno | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-04-30 | c | 0.0029425 | 6.6523e-05 | 2016 | 2015-04-30 | C | 22 | 0.0029425 | 6.6523e-05
4412836 | 2015-04-30 11:15 | 2015-04-30 12:03 | 48 | 123 | 5904 | 48 | 45 | 0.017852 | 5535 | 0.016737 | 0.00037192 | Restore Supply on Device I32 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | I32 | fm needs to patrol this line to check 3 sets of fuses. checked all fuses and could not find an issue I32 was open on arrival | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.016737 | 0.00037192 | 2016 | 2015-04-30 | C | 123 | 0.016737 | 0.00037192
4412846 | 2015-04-30 11:04 | 2015-04-30 12:03 | 59.4667 | 12 | 713.6 | 59.4667 | 56.4667 | 0.0021578 | 677.6 | 0.0020489 | 3.6285e-05 | Restore Supply on Device 528 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | Fuses 8421 | Please check if OMS 4412851 15 Kaitake Road is related & also OMS 4412886 42 Kaitake Road, Oakura Two Fuses found blown at Fuses 8421 - due to bamboo across lines past fuses 8471 refer OMS 4412851 replaced 2x 10 amp 11kv links. Cause: bamboo over the lin | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.0020489 | 3.6285e-05 | 2016 | 2015-04-30 | C | 12 | 0.0020489 | 3.6285e-05
4412856 | 2015-04-30 11:12 | 2015-04-30 14:46 | 214 | 95 | 20330 | 214 | 211 | 0.061473 | 20045 | 0.060611 | 0.00028726 | Restore Supply on Device T3560 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Links 7368 | Please check OMS 4412861 75 Ahiaruhe Road, affected no power also & also 15 Millars Road, Longbush. No power. Faultman go to 7368. Sam advised these fuses are out and will work through control after line patrol. Sam advised fuses blown asking for 2R for l | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.060611 | 0.00028726 | 2016 | 2015-04-30 | C | 95 | 0.060611 | 0.00028726
4414489 | 2015-05-13 10:00 | 2015-05-13 14:05 | 245 | 7 | 1715 | 245 | 242 | 0.0051857 | 1694 | 0.0051223 | 2.1166e-05 | NAPA ID:08978 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/143 | Upgrade 11KV trani T5/143 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-13 | b | 0.0025611 | 1.0583e-05 | 2016 | 2015-05-13 | B | 7 | 0.0051223 | 2.1166e-05
4414783 | 2015-05-20 09:08 | 2015-05-20 14:30 | 321.9667 | 40 | 12878.6667 | 321.9667 | 318.9667 | 0.038942 | 12758.6667 | 0.038579 | 0.00012095 | NAPA ID:08383 TP_HAWERA GXP > MANAIA SUB > AUROA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses MA112 | replace structures & tx's on rowan rd. Works location: Rowan Rd. WO 30007340 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-05-20 | b | 0.01929 | 6.0475e-05 | 2016 | 2015-05-20 | B | 40 | 0.038579 | 0.00012095
4415745 | 2015-04-30 19:43 | 2015-04-30 21:29 | 105.4167 | 108 | 78.0333 | 0.72253 | -2.2775 | 0.00023595 | 0 | 0 | 0.00032657 | Restore Supply on Device 4826W | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 4688 | RS2680 A/R, O/C B & C Phase. Patrolled with no fault found- Suspect Bird Strike. Repaced 2x 20Amp HV Links. Unable to find paperwork. Will audit when it is found. | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-04-30 | c | 0 | 0.00032657 | 2016 | 2015-04-30 | C | 108 | 0 | 0.00032657
4415766 | 2015-04-30 21:04 | 2015-04-30 22:41 | 96.7833 | 31 | 3000.2833 | 96.7833 | 93.7833 | 0.0090721 | 2907.2833 | 0.0087909 | 9.3737e-05 | Restore Supply on Device 798 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 8258 | Possibly part of 4415760. Patrolled, no fault found. Suspect bird strike. Replaced 2x 25A fuse links. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.0087909 | 9.3737e-05 | 2016 | 2015-04-30 | C | 31 | 0.0087909 | 9.3737e-05
4415808 | 2015-04-30 22:04 | 2015-04-30 23:50 | 106.4833 | 858 | 9551.05 | 11.1318 | 8.1318 | 0.02888 | 6977.05 | 0.021097 | 0.0025944 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 575 | CB 4 A/R, RS 575 L/O, No flags. Sectionalised & Partial Patrolled with no fault found. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-04-30 | c | 0.021097 | 0.0025944 | 2016 | 2015-04-30 | C | 858 | 0.021097 | 0.0025944
4417561 | 2015-04-30 22:28 | 2015-04-30 22:41 | 12.9333 | 1 | 12.9333 | 12.9333 | 9.9333 | 3.9107e-05 | 9.9333 | 3.0036e-05 | 3.0238e-06 | Restore Supply on Device X4129 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 736 PAPAITI ROAD | Part of Wanganui feeder fault - 4415808 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-04-30 | c | 3.0036e-05 | 3.024e-06 | 2016 | 2015-04-30 | C | 1 | 3.0036e-05 | 3.0238e-06
4418026 | 2015-05-01 04:25 | 2015-05-01 06:38 | 133.05 | 296 | 28095.95 | 94.9188 | 91.9188 | 0.084955 | 27207.95 | 0.08227 | 0.00089503 | Restore Supply on Device C917 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 799506 | Remove Opossum from pole 799506 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.08227 | 0.00089503 | 2016 | 2015-05-01 | C | 296 | 0.08227 | 0.00089503
4419469 | 2015-05-01 09:04 | 2015-05-01 15:14 | 369.8833 | 51 | 18864.05 | 369.8833 | 366.8833 | 0.05704 | 18711.05 | 0.056578 | 0.00015421 | Restore Supply on Device 7030 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 7030 | Treecutting by wairarapa treescaping. Works location: Mikimiki Rd Masterton. Parent Job OMS 4234932 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-01 | b | 0.028289 | 7.7106e-05 | 2016 | 2015-05-01 | B | 51 | 0.056578 | 0.00015421
4419524 | 2015-05-05 09:28 | 2015-05-05 15:23 | 354.9 | 8 | 2839.2 | 354.9 | 351.9 | 0.0085851 | 2815.2 | 0.0085125 | 2.419e-05 | NAPA ID:07968 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp ABS 91 | Replace poles and hardwear between TEMPABS 91 and ABS1118 Waotu Road | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-05 | b | 0.0042562 | 1.2095e-05 | 2016 | 2015-05-05 | B | 8 | 0.0085125 | 2.419e-05
4419527 | 2015-05-01 09:12 | 2015-05-01 12:22 | 189.8167 | 76 | 7279.7667 | 95.7864 | 92.7864 | 0.022012 | 7051.7667 | 0.021323 | 0.00022981 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 832166 | Cb 7417 ARC & trip A phase O/C & E/F (3 adv). Report received from Cory Winter of Horn Logging of tree through line @ pole 8232166 . Working on CAC 29840 at the time which was opened @ 06:01. Entered into Safeyt Manager on number 467004.Replaced 10m squir | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.021323 | 0.00022981 | 2016 | 2015-05-01 | C | 76 | 0.021323 | 0.00022981
4425886 | 2015-05-11 08:38 | 2015-05-11 09:07 | 28.85 | 166 | 4789.1 | 28.85 | 25.85 | 0.014481 | 4291.1 | 0.012975 | 0.00050194 | NAPA ID:08602 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C295 | Replace Existing Magnifix 4 way 11kv CB C297, C298, C299 C1005 with 3 way safe link CB "C1005 Deleted' Replace existing T1847 with new TF Install complete new concrete Pad. Works location: Waterhouse St Masterton. WO 10160113 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-11 | b | 0.0064876 | 0.00025097 | 2016 | 2015-05-11 | B | 166 | 0.012975 | 0.00050194
4426243 | 2015-05-01 17:52 | 2015-05-01 18:29 | 36.8333 | 1 | 36.8333 | 36.8333 | 33.8333 | 0.00011138 | 33.8333 | 0.0001023 | 3.0238e-06 | Restore Supply on Device X1072 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 14 WHITE STREET | No fault or hanging wires found. all surrounding customers still have power. | F2/F3 | WANGANUI EAST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.0001023 | 3.024e-06 | 2016 | 2015-05-01 | C | 1 | 0.0001023 | 3.0238e-06
4426267 | 2015-05-01 18:21 | 2015-05-01 19:36 | 74.9667 | 1128 | 82512.2333 | 73.1491 | 70.1491 | 0.2495 | 79128.2333 | 0.23926 | 0.0034108 | Restore Supply on Device 19 | 11 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | Beach Rd Sub | 11kV Temporary CB 19 tripped and locked out at 18:21. Loss of supply to both Kings Ave and Imlay Feeders. Both have priority customers, Open Country Dairy and Imlay meat works. Both Peter C and Dave D notified by ASW. *Sub technician Phil McQuiod dispatc | F2 | BEACH RD | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.23926 | 0.0034108 | 2016 | 2015-05-01 | C | 1128 | 0.23926 | 0.0034108
4427753 | 2015-05-01 20:18 | 2015-05-01 21:39 | 81.2 | 3 | 243.6 | 81.2 | 78.2 | 0.00073659 | 234.6 | 0.00070937 | 9.0713e-06 | Restore Supply on Device K4173 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | K4173 | 2R request to replace blown TX 3 Phase/30 kVA. 2x 3Amp HV Links | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.00070937 | 9.071e-06 | 2016 | 2015-05-01 | C | 3 | 0.00070937 | 9.0713e-06
4427779 | 2015-05-01 20:07 | 2015-05-01 21:06 | 59.0667 | 24 | 1417.6 | 59.0667 | 56.0667 | 0.0042865 | 1345.6 | 0.0040688 | 7.257e-05 | Restore Supply on Device 4119 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 4119 | Replace 2x 15Amp HV Fuse Links | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-05-01 | c | 0.0040688 | 7.257e-05 | 2016 | 2015-05-01 | C | 24 | 0.0040688 | 7.257e-05
4428368 | 2015-05-02 12:32 | 2015-05-02 14:09 | 96.6833 | 1 | 96.6833 | 96.6833 | 93.6833 | 0.00029235 | 93.6833 | 0.00028328 | 3.0238e-06 | Restore Supply on Device T1547 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 8189 | Advised Sammy at hub and Ian in control. Removed bark from the line with sticks and Replaced 2 X HV fuses. | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-05-02 | c | 0.00028328 | 3.024e-06 | 2016 | 2015-05-02 | C | 1 | 0.00028328 | 3.0238e-06
4428809 | 2015-05-02 15:00 | 2015-05-02 17:43 | 162.4167 | 327 | 18089.55 | 55.3197 | 52.3197 | 0.054698 | 17108.55 | 0.051732 | 0.00098877 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SD5-009 | 409 WAITAO ROAD tree online advised allen in control. CB 8 L/O on O/C. Backfeed via 9464 to RP09. Found lines twisted near ABS SD5-009 caused by goose. Untangled lines relivened. Reported tree in lines at 409 Waitao Rd. Found 3 lines broken at pole 220094 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-05-02 | c | 0.051732 | 0.00098877 | 2016 | 2015-05-02 | C | 327 | 0.051732 | 0.00098877
4429997 | 2015-05-02 15:08 | 2015-05-02 16:16 | 67.9833 | 1 | 67.9833 | 67.9833 | 64.9833 | 0.00020557 | 64.9833 | 0.00019649 | 3.0238e-06 | Restore Supply on Device T5165 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5165 | Replaced 2 X HV Fuses. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-02 | c | 0.00019649 | 3.024e-06 | 2016 | 2015-05-02 | C | 1 | 0.00019649 | 3.0238e-06
4430207 | 2015-05-02 18:23 | 2015-05-02 19:41 | 78.8 | 9 | 709.2 | 78.8 | 75.8 | 0.0021445 | 682.2 | 0.0020628 | 2.7214e-05 | Restore Supply on Device 957 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 8295 | 2x 10Amp Links | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-02 | c | 0.0020628 | 2.7214e-05 | 2016 | 2015-05-02 | C | 9 | 0.0020628 | 2.7214e-05
4430563 | 2015-05-03 07:22 | 2015-05-03 14:08 | 405.7833 | 306 | 16937 | 55.3497 | 52.3497 | 0.051213 | 16019 | 0.048438 | 0.00092527 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | M13077 | CB 4 auto reclosed E/F & O/C. reported car verse pole by Fire Services at 2693 SH1 Lichfield. Isolated between ABS 2561 & 2527. Backfeed rest of area. Replaced pole & 30 kva transformer TC382 & relivened NDR to be TBA | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-03 | c | 0.048438 | 0.00092527 | 2016 | 2015-05-03 | C | 306 | 0.048438 | 0.00092527
4432369 | 2015-05-03 17:02 | 2015-05-03 18:41 | 99.3167 | 5 | 496.5833 | 99.3167 | 96.3167 | 0.0015015 | 481.5833 | 0.0014562 | 1.5119e-05 | Restore Supply on Device TC4255 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4255 | 1 x 3 amp HV fuse replaced | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-05-03 | c | 0.0014562 | 1.5119e-05 | 2016 | 2015-05-03 | C | 5 | 0.0014562 | 1.5119e-05
4432738 | 2015-05-06 08:26 | 2015-05-06 09:50 | 84.3167 | 6 | 505.9 | 84.3167 | 81.3167 | 0.0015297 | 487.9 | 0.0014753 | 1.8143e-05 | NAPA ID:09103 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE6-135 | Replace cross arm and insulators. This is a Red Defect OMS No. 4422894. Works location: Browns Rd Te Puke. WO NA | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-06 | b | 0.00073765 | 9.071e-06 | 2016 | 2015-05-06 | B | 6 | 0.0014753 | 1.8143e-05
4432752 | 2015-05-04 09:10 | 2015-05-04 10:29 | 79.65 | 12 | 663.0167 | 55.2514 | 52.2514 | 0.0020048 | 627.0167 | 0.0018959 | 3.6285e-05 | Restore Supply on Device TE3-115 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Fuses SE2-020 | 04/05/15 10:26 - Mike Strange Attended. Inspected Pole & Associated equipment. All looked OK. Reloaded Relivened 2x 10A HV Fuses at Fuses SE2-020. All Power Restored On Completion. NDR 48468 His wife has hit a power pole, moved pole 100 mil - tripped fuse | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-04 | c | 0.0018959 | 3.6285e-05 | 2016 | 2015-05-04 | C | 12 | 0.0018959 | 3.6285e-05
4432830 | 2015-05-04 09:20 | 2015-05-04 10:40 | 80 | 9 | 720 | 80 | 77 | 0.0021771 | 693 | 0.0020955 | 2.7214e-05 | Restore Supply on Device 4201 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Pole 409720 | 11kV Line down at pole 409720. Replaced 4m 16mm copper, 3 x copper sleeves(crimps) 1x 11kV fuse and candle. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-05-04 | c | 0.0020955 | 2.7214e-05 | 2016 | 2015-05-04 | C | 9 | 0.0020955 | 2.7214e-05
4432953 | 2015-05-26 08:51 | 2015-05-26 15:30 | 399.6 | 104 | 41558.4 | 399.6 | 396.6 | 0.12566 | 41246.4 | 0.12472 | 0.00031447 | NAPA ID:08627 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S163 | 11KV ARM POLE REPLACEMENT. Works location: Kaka Amu Rd. WO 30001033 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-26 | b | 0.06236 | 0.00015724 | 2016 | 2015-05-26 | B | 104 | 0.12472 | 0.00031447
4432960 | 2015-05-28 08:30 | 2015-05-28 15:30 | 419.5667 | 104 | 43634.9333 | 419.5667 | 416.5667 | 0.13194 | 43322.9333 | 0.131 | 0.00031447 | NAPA ID:08628 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S163 | 11KV ARM POLE REPLACEMENT. Works location: Kaka Amu Rd. WO 30001033 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-28 | b | 0.065499 | 0.00015724 | 2016 | 2015-05-28 | B | 104 | 0.131 | 0.00031447
4433026 | 2015-05-19 08:49 | 2015-05-19 14:42 | 353.5 | 18 | 6363 | 353.5 | 350.5 | 0.01924 | 6309 | 0.019077 | 5.4428e-05 | NAPA ID:08827 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC796 | Replace Poles and X-arms. Works location: Tauranga Rd Te Poi. WO 30003315 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-05-19 | b | 0.0095385 | 2.7214e-05 | 2016 | 2015-05-19 | B | 18 | 0.019077 | 5.4428e-05
4433030 | 2015-05-26 09:36 | 2015-05-26 13:52 | 256 | 107 | 27392 | 256 | 253 | 0.082827 | 27071 | 0.081856 | 0.00032354 | NAPA ID:08322 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Recloser 4196/2 | A/P needed for tree cutting from pole 840960 to pole 789632. Works location: Koeke Rd. PPPD 53593 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-26 | b | 0.040928 | 0.00016177 | 2016 | 2015-05-26 | B | 107 | 0.081856 | 0.00032354
4433439 | 2015-05-13 09:03 | 2015-05-13 15:23 | 380 | 103 | 39140 | 380 | 377 | 0.11835 | 38831 | 0.11742 | 0.00031145 | NAPA ID:09139 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 792165 | Replace four 11kv poles 792165,792156,792155,792153 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-05-13 | b | 0.058708 | 0.00015572 | 2016 | 2015-05-13 | B | 103 | 0.11742 | 0.00031145
4433906 | 2015-05-04 19:07 | 2015-05-04 23:23 | 256.0667 | 1 | 256.0667 | 256.0667 | 253.0667 | 0.00077428 | 253.0667 | 0.00076521 | 3.0238e-06 | Restore Supply on Device TD4-049 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 203842 | Car vs pole - Police comms ref #P021084498 7:09PM - Advised tans at SMC Taken detail through to control 2r requested as pole and x arm to be replaced advised chorus telecom lines are down also ref 46317563 NDR No 51853 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-04 | c | 0.00076521 | 3.024e-06 | 2016 | 2015-05-04 | C | 1 | 0.00076521 | 3.0238e-06
4433938 | 2015-05-04 20:23 | 2015-05-04 22:48 | 145.1 | 1 | 145.1 | 145.1 | 142.1 | 0.00043875 | 142.1 | 0.00042968 | 3.0238e-06 | Restore Supply on Device T1162 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7043 | replaced 2 X HV fuses caused by large goose. No other assets repaired or replaced at site. Adjacent assets all up to Powerco Standard. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-05-04 | c | 0.00042968 | 3.024e-06 | 2016 | 2015-05-04 | C | 1 | 0.00042968 | 3.0238e-06
4433941 | 2015-05-04 20:23 | 2015-05-04 21:52 | 89.3167 | 1 | 89.3167 | 89.3167 | 86.3167 | 0.00027007 | 86.3167 | 0.000261 | 3.0238e-06 | Restore Supply on Device TC1098 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1666 | Found 2 x 10amp HT fuses blown. Checked line, re-livened. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-05-04 | c | 0.000261 | 3.024e-06 | 2016 | 2015-05-04 | C | 1 | 0.000261 | 3.0238e-06
4433980 | 2015-05-05 05:47 | 2015-05-05 07:42 | 115 | 7 | 805 | 115 | 112 | 0.0024341 | 784 | 0.0023706 | 2.1166e-05 | Restore Supply on Device TC339 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC339 | LV jumper burnt off , replaced connection at back of TX worked through control isolated tx to do this work No other assets repaired or replaced. Adjacent assets ok. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-05-05 | c | 0.0023706 | 2.1166e-05 | 2016 | 2015-05-05 | C | 7 | 0.0023706 | 2.1166e-05
4435136 | 2015-06-06 08:45 | 2015-06-06 15:45 | 420 | 16 | 6720 | 420 | 417 | 0.02032 | 6672 | 0.020175 | 4.838e-05 | NAPA ID:09166 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole LAKBRN099 | Replace 11/33kV Poles, crossarms and hardware between poles LAKBRN 099 and 115 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-06-06 | b | 0.010087 | 2.419e-05 | 2016 | 2015-06-06 | B | 16 | 0.020175 | 4.838e-05
4435142 | 2015-05-11 09:09 | 2015-05-11 15:25 | 377 | 4 | 1508 | 377 | 374 | 0.0045598 | 1496 | 0.0045235 | 1.2095e-05 | NAPA ID:09168 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LAKBRN121 | Replace 11/33kV Poles, crossarms and hardware between poles LAKBRN 118 and 143 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-05-11 | b | 0.0022618 | 6.048e-06 | 2016 | 2015-05-11 | B | 4 | 0.0045235 | 1.2095e-05
4435152 | 2015-05-15 09:19 | 2015-05-15 10:48 | 88.25 | 54 | 4765.5 | 88.25 | 85.25 | 0.01441 | 4603.5 | 0.01392 | 0.00016328 | NAPA ID:09169 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole 164 | Replace 11/33kV Poles, crossarms and hardware on pole LAKBRN 164 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-05-15 | b | 0.0069599 | 8.1642e-05 | 2016 | 2015-05-15 | B | 54 | 0.01392 | 0.00016328
4435174 | 2015-05-05 13:18 | 2015-05-05 14:00 | 41.5333 | 37 | 1535.2 | 41.4919 | 38.4919 | 0.0046421 | 1424.2 | 0.0043064 | 0.00011188 | Restore Supply on Device TC3112 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2111 | ADVISED JOANNE AT HUB' TAH 3 Emergency switching to replace burnt fuse holder at fuses FC2111. Isolations. between ABS's IC1222 & 837 ( no back feeds ). Fuse holder x 1 replaced all service restored Materials 1 x fuse holde, 1 x 10A H/V, O/H fuse link. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-05-05 | c | 0.0043064 | 0.00011188 | 2016 | 2015-05-05 | C | 37 | 0.0043064 | 0.00011188
4435427 | 2015-05-23 06:39 | 2015-05-23 06:59 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:09107 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-23 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-23 | B | 16 | 0.00082246 | 4.838e-05
4435457 | 2015-05-25 06:54 | 2015-05-25 07:14 | 20 | 16 | 320 | 20 | 17 | 0.0009676 | 272 | 0.00082246 | 4.838e-05 | NAPA ID:09108 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango. WO 10161206 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-25 | b | 0.00041123 | 2.419e-05 | 2016 | 2015-05-25 | B | 16 | 0.00082246 | 4.838e-05
4435467 | 2015-05-21 09:12 | 2015-05-21 13:11 | 238.7833 | 19 | 4536.8833 | 238.7833 | 235.7833 | 0.013718 | 4479.8833 | 0.013546 | 5.7451e-05 | NAPA ID:09147 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1350 | To install new 11kV ABS IP609 and replace 11kV conductors between Poles B12554 and B12534. Works location: Kokako Rd. WO 30000626 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-21 | b | 0.006773 | 2.8726e-05 | 2016 | 2015-05-21 | B | 19 | 0.013546 | 5.7451e-05
4437101 | 2015-05-19 13:11 | 2015-05-19 13:59 | 48.7333 | 12 | 584.8 | 48.7333 | 45.7333 | 0.0017683 | 548.8 | 0.0016594 | 3.6285e-05 | NAPA ID:08472 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC1460 | Replace x-arm at pole I0498. Works location: Graydon Rd Morrinsville. WO 30008268 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-05-19 | b | 0.00082972 | 1.8143e-05 | 2016 | 2015-05-19 | B | 12 | 0.0016594 | 3.6285e-05
4437159 | 2015-05-06 07:11 | 2015-05-06 07:48 | 37.2 | 6 | 223.2 | 37.2 | 34.2 | 0.0006749 | 205.2 | 0.00062048 | 1.8143e-05 | NAPA ID:09181 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P42450 | carry out switching to isolate piece of line so that we can carry out a live line break at P42450 as part of the pioneer hwy network change job. | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-06 | b | 0.00031024 | 9.071e-06 | 2016 | 2015-05-06 | B | 6 | 0.00062048 | 1.8143e-05
4437415 | 2015-05-05 17:28 | 2015-05-05 18:37 | 69.4833 | 5 | 347.4167 | 69.4833 | 66.4833 | 0.0010505 | 332.4167 | 0.0010051 | 1.5119e-05 | Restore Supply on Device X740 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 795527 | Lines down - 4:26PM spoke to SMC and taken detail through to control. HV line found down on Kaweka Rd, fuses 2625 open for isolation. Conductor rejoined OK and relivened. Suspect bird struike. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-05 | c | 0.0010051 | 1.5119e-05 | 2016 | 2015-05-05 | C | 5 | 0.0010051 | 1.5119e-05
4437562 | 2015-05-05 21:50 | 2015-05-06 02:43 | 292.55 | 765 | 43394.6667 | 56.7251 | 53.7251 | 0.13122 | 41099.6667 | 0.12428 | 0.0023132 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | o14182 | CB 1 L/O on E/F. auto backfeed scheme operated. Donnor feeder CB4 Tahuna Recloser RC27 tripped. Opened recloser 9668 and reclosed RC27. Reclosed CB1 after 15 minutes CB1 L/O on E/F. Reclosed backfeed recloser 9668. Repaired & relivened | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-05 | c | 0.12428 | 0.0023132 | 2016 | 2015-05-05 | C | 765 | 0.12428 | 0.0023132
4438875 | 2015-05-06 06:00 | 2015-05-06 09:36 | 216.0167 | 11 | 2368 | 215.2727 | 212.2727 | 0.0071603 | 2335 | 0.0070605 | 3.3261e-05 | Restore Supply on Device X1314 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 850107 | Fuses 2855 found tripped - patrolled during daylight hours with twisted wires found at pole 850107. Suspect bord strike. Unboud, relivened oK. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-05-06 | c | 0.0070605 | 3.3261e-05 | 2016 | 2015-05-06 | C | 11 | 0.0070605 | 3.3261e-05
4438883 | 2015-05-06 00:31 | 2015-05-06 01:52 | 81.3667 | 1 | 81.3667 | 81.3667 | 78.3667 | 0.00024603 | 78.3667 | 0.00023696 | 3.0238e-06 | Restore Supply on Device TC4-139 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9657/1 | Found CB 9657/1 Tripped. Check all OK Re-closed CB 9657/1. internal fault on motor, isolated in thier network. | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-05-06 | c | 0.00023696 | 3.024e-06 | 2016 | 2015-05-06 | C | 1 | 0.00023696 | 3.0238e-06
4438959 | 2015-05-06 08:04 | 2015-06-06 11:13 | 44829.2 | 1 | 44829.2 | 44829.2 | 44826.2 | 0.13555 | 44826.2 | 0.13554 | 3.0238e-06 | Restore Supply on Device TC395 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 1411 | x2 10amp HV fuse links due to ducks - link 1411 fed to TX TC6552. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED. 11:13 job would not Verify - so passed on to Richard. Associated with | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-06 | c | 0.13554 | 3.024e-06 | 2016 | 2015-05-06 | C | 1 | 0.13554 | 3.0238e-06
4440190 | 2015-05-07 09:02 | 2015-05-07 15:28 | 385.6667 | 19 | 7327.6667 | 385.6667 | 382.6667 | 0.022157 | 7270.6667 | 0.021985 | 5.7451e-05 | NAPA ID:09194 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | Pole B0527 | To install TEMP63 at Pole # B0527 and replace poles and cross arms in preparation for 11kV conductor upgrade. NC NOTE: RESTORATION NEW OPEN POINT IS TO BE 11kV ABS 1350 NOT SECTIONALISER 9916/2. PUT4 & BRD5 PARALELL WARNING FLAG TOBE ADDED TO SCADA TILE. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-07 | b | 0.010992 | 2.8726e-05 | 2016 | 2015-05-07 | B | 19 | 0.021985 | 5.7451e-05
4444261 | 2015-05-29 08:00 | 2015-05-29 08:20 | 20 | 2 | 40 | 20 | 17 | 0.00012095 | 34 | 0.00010281 | 6.0475e-06 | NAPA ID:09011 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7475 | ISOLATION OF SPUR LINE TO REPLACE 11 POLES THREE 11KV XARMS TO TRANSFORMERS OFF GOING TO INSTALL TO GENERATORS , WHICH WILL TAKE ONLY COUPLE OF MINUTES AT MOST AS WILL HAVE THEM SET UP DAY BEFORE ONLY MATTER PULLING FUSES PUT OTHERS IN. Works location: Ka | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-29 | b | 5.1404e-05 | 3.024e-06 | 2016 | 2015-05-29 | B | 2 | 0.00010281 | 6.0475e-06
4554858 | 2015-05-06 11:06 | 2015-05-06 19:18 | 491.5167 | 1 | 491.5167 | 491.5167 | 488.5167 | 0.0014862 | 488.5167 | 0.0014772 | 3.0238e-06 | Restore Supply on Device T3741 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t3741 | 12:47 2R TO REPLACE TRANSFORMER SAM LEAVING SITE. Tranformer 15 kv a single phase t3741 now replaced due to age. SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED. FULL POWER RESTORED. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2015-05-06 | c | 0.0014772 | 3.024e-06 | 2016 | 2015-05-06 | C | 1 | 0.0014772 | 3.0238e-06
4554863 | 2015-05-06 11:10 | 2015-05-06 11:13 | 2.6667 | 1 | 2.6667 | 2.6667 | -0.33333 | 8.0634e-06 | 0 | 0 | 3.0238e-06 | Restore Supply on Device FC1107 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuses 1107 | Related to OMS 4438959. This job records the outage information. No paperwork created. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-06 | c | 0 | 3.024e-06 | 2016 | 2015-05-06 | C | 1 | 0 | 3.0238e-06
4697750 | 2015-05-13 09:08 | 2015-05-13 15:23 | 375 | 6 | 2250 | 375 | 372 | 0.0068035 | 2232 | 0.006749 | 1.8143e-05 | NAPA ID:08231 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2759 | LLP1: Cut leads between OH line and the source side of the drop-out fuses for SWER Transformer TC2759. Before the Live Line Permit is issued the drop out fuses will need to be opened. AP1: Replace the supports for SWER transformer TC2759, replace the dro | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-05-13 | b | 0.0033745 | 9.071e-06 | 2016 | 2015-05-13 | B | 6 | 0.006749 | 1.8143e-05
4732937 | 2015-05-13 09:04 | 2015-05-13 13:50 | 286 | 13 | 3718 | 286 | 283 | 0.011242 | 3679 | 0.011124 | 3.9309e-05 | NAPA ID:07938 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1350 | To replace 11kV poles and cross arms between Poles B0527 and B0517 Kokako Road. Works location: Kokako Rd WO 30000626 Child Job locked in verified state, sent to project team to fix | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-13 | b | 0.0055622 | 1.9654e-05 | 2016 | 2015-05-13 | B | 13 | 0.011124 | 3.9309e-05
4733093 | 2015-05-07 12:00 | 2015-05-07 16:51 | 290.3167 | 265 | 244.6333 | 0.92314 | -2.0769 | 0.00073971 | 0 | 0 | 0.0008013 | NAPA ID:09217 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | O4144 | Install clamp top insulators. Work Location: River Road, Ngatea. Work Order 10189757. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-07 | b | 0 | 0.00040065 | 2016 | 2015-05-07 | B | 265 | 0 | 0.0008013
4733209 | 2015-05-06 17:15 | 2015-05-06 20:44 | 208.2333 | 1 | 208.2333 | 208.2333 | 205.2333 | 0.00062965 | 205.2333 | 0.00062058 | 3.0238e-06 | Restore Supply on Device T1319 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 823573 | 2x 11kv tx fuses 2amp due to possum on t1319 on pole 823573 did not work through control as fm thought that did not apply to tx fuses wich only feeds one property. SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED. FULL POWER RES | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-05-06 | c | 0.00062058 | 3.024e-06 | 2016 | 2015-05-06 | C | 1 | 0.00062058 | 3.0238e-06
4733309 | 2015-05-07 00:04 | 2015-05-07 00:22 | 18.0167 | 19 | 341.3 | 17.9632 | 14.9632 | 0.001032 | 284.3 | 0.00085966 | 5.7451e-05 | Restore Supply on Device 2763T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2788T | ADVISED LEANNE AT HUB. This was at transformer 2788T Not Transformer 2763T as in Header. Used Hot stick to Remove Lighting Arrestor from DDO | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.00085965 | 5.7451e-05 | 2016 | 2015-05-07 | C | 19 | 0.00085966 | 5.7451e-05
4734564 | 2015-05-26 10:00 | 2015-05-26 13:15 | 195 | 5 | 975 | 195 | 192 | 0.0029482 | 960 | 0.0029028 | 1.5119e-05 | NAPA ID:07993 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 6.6 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 2902T | Existing 20kva TX 2902T pole mount transformer to be upgraded on existing structure to new 100kva polemount TX | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-05-26 | b | 0.0014514 | 7.559e-06 | 2016 | 2015-05-26 | B | 5 | 0.0029028 | 1.5119e-05
4744732 | 2015-05-07 12:17 | 2015-05-07 15:16 | 179 | 1074 | 49055 | 45.675 | 42.675 | 0.14833 | 45833 | 0.13859 | 0.0032475 | Restore Supply on Device 8800/5 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Sw/Gear 6820 | CB 5 Tripped A,B,C Ph O/C G/F L/O - Car V Sw/Gear reported during Sectionlising - Installation of backfeeds held up by OSI failures - Isolated at Links 6811, ABS 6814, CB5 &, OCB4, issues getting isolation in place in Silver Fern Farms - Line Break made a | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.13859 | 0.0032475 | 2016 | 2015-05-07 | C | 1074 | 0.13859 | 0.0032475
4746081 | 2015-05-06 12:33 | 2015-05-07 16:54 | 1701 | 240 | 14244 | 59.35 | 56.35 | 0.04307 | 13524 | 0.040893 | 0.0007257 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 718419 | CB 7 Tripped O/C E/F L/O - Car V Pole reported - Isolated at ABS's MA453, MA448 &, 6440 - Back feed installed via ABS MA579 - Pole 718419 Replace including all Cross arms complete - Used 1 x pole, 1 HV Cross arm Complete 2 x Strainer arms Complete, 3 HV f | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-05-06 | c | 0.040893 | 0.0007257 | 2016 | 2015-05-06 | C | 240 | 0.040893 | 0.0007257
4746726 | 2015-05-07 13:22 | 2015-05-07 14:20 | 58 | 51 | 2958 | 58 | 55 | 0.0089443 | 2805 | 0.0084816 | 0.00015421 | Restore Supply on Device S151 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 827069 & 827072 | Faultman found 2 broken insulators on 2 different poles while on a line patrol, line was isolated at ABS's S64 & S151 to replace the broken insulators on poles 827072 & 827069. 2 x 11KV insulators replaced. 3 X binders. 12 X birdy begons installed on the | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.0084816 | 0.00015421 | 2016 | 2015-05-07 | C | 51 | 0.0084816 | 0.00015421
4747006 | 2015-05-15 09:30 | 2015-05-15 10:38 | 67.8167 | 258 | 17496.7 | 67.8167 | 64.8167 | 0.052906 | 16722.7 | 0.050565 | 0.00078013 | NAPA ID:09243 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC347 | Replace H. Structure crossarm at pole V13617. Works location: Kennedy Bay Rd Coromandel. WO NA. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-05-15 | b | 0.025283 | 0.00039006 | 2016 | 2015-05-15 | B | 258 | 0.050565 | 0.00078013
4747015 | 2015-05-07 14:58 | 2015-05-07 18:38 | 220.2 | 69 | 14717.7167 | 213.3002 | 210.3002 | 0.044503 | 14510.7167 | 0.043877 | 0.00020864 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 795068 | Recloser 4240 tripped on B & c phase O/C, line was patrolled and faultman found top of pole 795068 had burnt off and B phase was floating. Line was isolated at Links 4240/6 & ABS 4240/1to repair the line. 3 X 11KV insulators replaced. 4 X Binders. 10 mete | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.043877 | 0.00020864 | 2016 | 2015-05-07 | C | 69 | 0.043877 | 0.00020864
4750214 | 2015-05-07 16:10 | 2015-05-07 17:04 | 54 | 957 | 37909 | 39.6123 | 36.6123 | 0.11463 | 35038 | 0.10595 | 0.0028937 | Restore Supply on Device T8/314 | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 11kV CB 1at Sub | 11kV CB 1 tripped to Lock out, no flags. Loss of supply to Managamutu Sub BUS and feeders. Electrix working onsite conducting testing of 33kV CB XT70 via NAPA 9209. Electrix assisted in sorting CB 1 lock out as Downers fault crew unable to re-close CB 1. | F2 | PAHIATUA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.10595 | 0.0028937 | 2016 | 2015-05-07 | C | 957 | 0.10595 | 0.0028937
4750257 | 2015-05-07 16:32 | 2015-05-07 20:32 | 240.2 | 7 | 1681.4 | 240.2 | 237.2 | 0.0050842 | 1660.4 | 0.0050207 | 2.1166e-05 | Restore Supply on Device X1838 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4192 | Address is actually 22 not 220. High tension HV fuse replaced but it keeps blowing - Need to patrol line but its cross country so 2R requested. Patrol carried out with a broken Insulator replaced at Transformer Pole X4192. (Isolation from fuses 1043). R | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-05-07 | c | 0.0050207 | 2.1166e-05 | 2016 | 2015-05-07 | C | 7 | 0.0050207 | 2.1166e-05
4753831 | 2015-05-08 06:54 | 2015-05-08 07:01 | 6.25 | 1 | 6.25 | 6.25 | 3.25 | 1.8899e-05 | 3.25 | 9.8272e-06 | 3.0238e-06 | Restore Supply on Device L1055 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8804 | Part Power. 2 fuses founds Blown at fuses 8804 - Line Patrolled with no fault found - Used 2x amp fuses Parent job raised against wrong Transformer should of been 5548E | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-08 | c | 9.827e-06 | 3.024e-06 | 2016 | 2015-05-08 | C | 1 | 9.8272e-06 | 3.0238e-06
4779382 | 2015-05-08 05:09 | 2015-05-08 07:12 | 123 | 1 | 123 | 123 | 120 | 0.00037192 | 120 | 0.00036285 | 3.0238e-06 | Restore Supply on Device T1/162 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | L84 | 2 X HV FUSE LINKS CAUSE UNKNOWN | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-08 | c | 0.00036285 | 3.024e-06 | 2016 | 2015-05-08 | C | 1 | 0.00036285 | 3.0238e-06
4779437 | 2015-05-08 10:10 | 2015-05-08 13:37 | 207.1833 | 14 | 771.6 | 55.1143 | 52.1143 | 0.0023331 | 729.6 | 0.0022061 | 4.2333e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4927 | TPV 4 Suspected transformer T4927 faulty. Required isolation at ABS SE6 151 to isolate at link box SE6 021 ( no back feeds ) Faulty transformer T4927 isolated with rest of feeder returned to service via ABS SE6 151. Transformer T4927 (replaced reported n | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-08 | c | 0.0022061 | 4.2333e-05 | 2016 | 2015-05-08 | C | 14 | 0.0022061 | 4.2333e-05
4790136 | 2015-05-15 08:34 | 2015-05-15 15:01 | 387 | 1 | 387 | 387 | 384 | 0.0011702 | 384 | 0.0011611 | 3.0238e-06 | NAPA ID:09244 TP_WAIKINO GXP > WAIHI SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 1558 | Replace X-arms at various sites. Works location: Waihi Goldmine, Waihi. WO 30002377 | F1 | WAIHI GOLD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-05-15 | b | 0.00058056 | 1.512e-06 | 2016 | 2015-05-15 | B | 1 | 0.0011611 | 3.0238e-06
4790509 | 2015-05-08 13:20 | 2015-05-08 16:00 | 160 | 397 | 24913.75 | 62.755 | 59.755 | 0.075333 | 23722.75 | 0.071732 | 0.0012004 | Restore Supply on Device LI7 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 728749 | CB 7 Tripped O/C E/F L/O - Lines down reported by Public - Isolated at ABS's LI742, LI729 & Fuses LI710 - Lines Repaired, Bird strike caused lines to come down. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-08 | c | 0.071732 | 0.0012004 | 2016 | 2015-05-08 | C | 397 | 0.071732 | 0.0012004
4791821 | 2015-05-08 16:03 | 2015-05-08 17:08 | 65.15 | 1 | 65.15 | 65.15 | 62.15 | 0.000197 | 62.15 | 0.00018793 | 3.0238e-06 | Restore Supply on Device T5165 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5165 | 2x HV fuse Blown, working with ASW in NOC. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-08 | c | 0.00018793 | 3.024e-06 | 2016 | 2015-05-08 | C | 1 | 0.00018793 | 3.0238e-06
4793027 | 2015-05-08 21:38 | 2015-05-08 23:14 | 96.8667 | 1 | 96.8667 | 96.8667 | 93.8667 | 0.0002929 | 93.8667 | 0.00028383 | 3.0238e-06 | Restore Supply on Device W2445 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | WH277 | This job caused by 1 HT tripping at Fuses WH277. Unable to force up to fuses as job verified by dispatch. No loss of supply with one phase. (Fuse Rating 8a). | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-05-08 | c | 0.00028383 | 3.024e-06 | 2016 | 2015-05-08 | C | 1 | 0.00028383 | 3.0238e-06
4794637 | 2015-05-09 09:03 | 2015-05-09 09:15 | 11.7667 | 1366 | 15507.1 | 11.3522 | 8.3522 | 0.04689 | 11409.1 | 0.034498 | 0.0041305 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 215257 | at 09:03 Welcome Bay Sub, CB 3 Welcome Bay Feeder, Tripped, No Flags, L/O. Recloser 9412 Also Tripped, Ph B O/C, L/O. Faultmen were dispatched and investigation began. Downer Faultman Mike Strange lives in Welcome Bay and heard a loud bang. Called Control | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-05-09 | c | 0.034498 | 0.0041305 | 2016 | 2015-05-09 | C | 1366 | 0.034498 | 0.0041305
4796124 | 2015-05-09 11:29 | 2015-05-09 12:15 | 46.45 | 1 | 46.45 | 46.45 | 43.45 | 0.00014045 | 43.45 | 0.00013138 | 3.0238e-06 | Restore Supply on Device X4025 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 70566 | 11:30am called through hub - leanne ( used nearest ICP). intersection Fergusson St London St - Wanganui car /pole 11:34am ETA 15mins advised Belinda. checked HV pole all was good no damage to pole NDR # 30418 | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-09 | c | 0.00013138 | 3.024e-06 | 2016 | 2015-05-09 | C | 1 | 0.00013138 | 3.0238e-06
4796498 | 2015-05-10 00:53 | 2015-05-10 05:12 | 259.5 | 162 | 23052.35 | 142.2985 | 139.2985 | 0.069705 | 22566.35 | 0.068235 | 0.00048985 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784052 | CB 7 auto reclosed on A & B phase O/C flags, check and noticed Recloser 4004 had an AC fail alarm, sent faultman to Recloser 2032 to check if open as we have no comms with this Recloser, Recloser was found open, line was sectionalised and patrolled and a | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-10 | c | 0.068235 | 0.00048985 | 2016 | 2015-05-10 | C | 162 | 0.068235 | 0.00048985
4796897 | 2015-05-10 05:46 | 2015-05-10 06:20 | 34.0833 | 23 | 783.9167 | 34.0833 | 31.0833 | 0.0023704 | 714.9167 | 0.0021617 | 6.9546e-05 | Restore Supply on Device IC3159 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2877 | Isolation at Sw/gear IC3159 to replace 1X HV Fuse and Holder at Pole C1484/Transformer TC2877. Original job OMS 4796827 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-05-10 | c | 0.0021617 | 6.9546e-05 | 2016 | 2015-05-10 | C | 23 | 0.0021617 | 6.9546e-05
4798618 | 2015-05-10 11:11 | 2015-05-10 11:51 | 40.4333 | 86 | 3477.2667 | 40.4333 | 37.4333 | 0.010514 | 3219.2667 | 0.0097343 | 0.00026004 | Restore Supply on Device 5329 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5329 | reclosed with no fault found/reported | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-05-10 | c | 0.0097343 | 0.00026004 | 2016 | 2015-05-10 | C | 86 | 0.0097343 | 0.00026004
4799270 | 2015-05-10 17:33 | 2015-05-10 18:32 | 58.8833 | 1724 | 93907.8167 | 54.4709 | 51.4709 | 0.28395 | 88735.8167 | 0.26832 | 0.005213 | Restore Supply on Device 342 | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 720166 | 17:30. 33kV HWA GXP CB's 342 and 402 both tripped, Inverse time, L/O. Also Kapuni 33kV CB 3422 tripped O/C L/O. 18:10-18:22. 33kV Line down found at pole 720166 due to suspected bird strike btween KAP CB 3422 and HWA GXP CB 342. 18:21. Kapuni Sub re-liven | F1,F2,F3 | WAIMATE 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 2015-05-10 | c | 0.26832 | 0.005213 | 2016 | 2015-05-10 | C | 1724 | 0.26832 | 0.005213
4803316 | 2015-05-10 23:50 | 2015-05-11 13:31 | 821.05 | 2220 | 44267.7 | 19.9404 | 16.9404 | 0.13385 | 37607.7 | 0.11372 | 0.0067127 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P12872 | CB 5 tripped on E/F flags, received a call from Fire Services of a car vs pole P12872 on SH 2 at the Hamua Hall, line was isolated at ABS's S27 & S44.Fire Number F1841730. Pole P12872 been temperary held up with line truck until morning. NDR 19112 | F2 | PAHIATUA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-10 | c | 0.11372 | 0.0067127 | 2016 | 2015-05-10 | C | 2220 | 0.11372 | 0.0067127
4808169 | 2015-05-11 05:07 | 2015-05-11 15:22 | 614.85 | 702 | 98694.85 | 140.591 | 137.591 | 0.29843 | 96588.85 | 0.29206 | 0.0021227 | Restore Supply on Device SC4-514 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Transformer TC4-200 | at 05:07 Triton Sub, CB 7 Totara St North Feeder. Call came in for No Power. Faultman dispatched and investigation began. Found 1x Blown HV Fuse at Fuse/Sw SC4-514. Fuse/Sw was opened then earth/sw closed to investigate and replace fuse. On opening fuse c | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-05-11 | c | 0.29206 | 0.0021227 | 2016 | 2015-05-11 | C | 702 | 0.29206 | 0.0021227
4808894 | 2015-05-11 08:51 | 2015-05-11 10:02 | 70.7667 | 11 | 778.4333 | 70.7667 | 67.7667 | 0.0023538 | 745.4333 | 0.002254 | 3.3261e-05 | Restore Supply on Device MA404 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720166 | 11kV Fuses MA404 found to be blown on arrival to site. Lines twisted together mid span at Pole 720166 and bucket truck req for repair. Unknown cause. Materials used: 2x Ali Sleeves, 2x HV fuse holders, 3x 8Amp HV links | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.002254 | 3.3261e-05 | 2016 | 2015-05-11 | C | 11 | 0.002254 | 3.3261e-05
4808941 | 2015-05-17 09:32 | 2015-05-17 13:02 | 210 | 27 | 5670 | 210 | 207 | 0.017145 | 5589 | 0.0169 | 8.1642e-05 | NAPA ID:09052 TP_NEW PLYMOUTH GXP > MOTUROA SUB | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 226 | Replace ABS226 and Pole. Works location: Breakwater Rd, New Plymouth. WO 30006983. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-05-17 | b | 0.0084499 | 4.0821e-05 | 2016 | 2015-05-17 | B | 27 | 0.0169 | 8.1642e-05
4809458 | 2015-06-11 09:25 | 2015-06-11 14:52 | 327.5333 | 7 | 2292.7333 | 327.5333 | 324.5333 | 0.0069327 | 2271.7333 | 0.0068692 | 2.1166e-05 | NAPA ID:09043 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGAMAIRE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P45692 | To replace rotten H/W Pole | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-11 | b | 0.0034346 | 1.0583e-05 | 2016 | 2015-06-11 | B | 7 | 0.0068692 | 2.1166e-05
4809598 | 2015-05-11 12:07 | 2015-05-11 12:59 | 52.1833 | 14 | 730.5667 | 52.1833 | 49.1833 | 0.0022091 | 688.5667 | 0.0020821 | 4.2333e-05 | Restore Supply on Device 4965 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730931 | Emergency switching to replace faulty surge arrestors at pole 730931 ( KAA T11 ) . S/A lead fell & blew H/V fuse Isolations at Fuses 4965 ( no bak feeds ), surge arrestors replaced, all service restored. Materials 3 x 11kV surge arrestors, 1 x 3A H/V O/H | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.0020821 | 4.2333e-05 | 2016 | 2015-05-11 | C | 14 | 0.0020821 | 4.2333e-05
4809729 | 2015-05-15 12:30 | 2015-05-15 14:24 | 113.8833 | 404 | 33351.0333 | 82.5521 | 79.5521 | 0.10085 | 32139.0333 | 0.097181 | 0.0012216 | NAPA ID:09330 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses R58 | Replace damaged Switchgear 8620 (car vs pole)and cable to pole 846576. Methodology attached. Works location: Omata Rd. WO 30004481 | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-05-15 | b | 0.04859 | 0.0006108 | 2016 | 2015-05-15 | B | 404 | 0.097181 | 0.0012216
4810178 | 2015-05-27 08:51 | 2015-05-27 11:05 | 134.5667 | 5 | 672.8333 | 134.5667 | 131.5667 | 0.0020345 | 657.8333 | 0.0019891 | 1.5119e-05 | NAPA ID:09307 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV L53 | Install new D/A and strains on pole p33709. Works location: Himitangi Beach Rd. WO 10162444 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-27 | b | 0.00099456 | 7.559e-06 | 2016 | 2015-05-27 | B | 5 | 0.0019891 | 1.5119e-05
4810211 | 2015-05-11 16:17 | 2015-05-11 18:20 | 123.35 | 1 | 123.35 | 123.35 | 120.35 | 0.00037298 | 120.35 | 0.00036391 | 3.0238e-06 | Restore Supply on Device K73 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | K73 | Fuses found blown at Fuses K73 - line Patrolled with no fault found - Fuses closed used 2x 6 amp fuses | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.00036391 | 3.024e-06 | 2016 | 2015-05-11 | C | 1 | 0.00036391 | 3.0238e-06
4810232 | 2015-05-11 16:47 | 2015-05-12 12:45 | 1198.1667 | 608 | 87944.55 | 144.6456 | 141.6456 | 0.26592 | 86120.55 | 0.26041 | 0.0018384 | Restore Supply on Device 1 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TP1322 | MOV CB 1 tripped O/C, L/O Feeder sectionalized & patrolled. Fault found to be past fuses FP 157. Cable & transformer TP1322 tested, Transformer TP1322 found to be faulty. will be replaced on 12/05/15. Isolation at Fuses FP157. 12/05/15, ASW, Transformer t | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-05-11 | c | 0.26041 | 0.0018384 | 2016 | 2015-05-11 | C | 608 | 0.26041 | 0.0018384
4811110 | 2015-05-11 17:55 | 2015-05-11 20:19 | 143.95 | 1 | 143.95 | 143.95 | 140.95 | 0.00043527 | 140.95 | 0.0004262 | 3.0238e-06 | Restore Supply on Device T1162 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7043 | Replaced 2X hV Fuses | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.0004262 | 3.024e-06 | 2016 | 2015-05-11 | C | 1 | 0.0004262 | 3.0238e-06
4811148 | 2015-05-11 16:06 | 2015-05-11 18:15 | 129.2833 | 6 | 775.7 | 129.2833 | 126.2833 | 0.0023455 | 757.7 | 0.0022911 | 1.8143e-05 | Restore Supply on Device P4270 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P4270 | Replaced 2X 3a hV Fuses | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.0022911 | 1.8143e-05 | 2016 | 2015-05-11 | C | 6 | 0.0022911 | 1.8143e-05
4812609 | 2015-05-11 19:05 | 2015-05-11 21:05 | 119.6833 | 1 | 119.6833 | 119.6833 | 116.6833 | 0.00036189 | 116.6833 | 0.00035282 | 3.0238e-06 | Restore Supply on Device T8/233 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 10132 | Replaced 2X 6a hV Fuses | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-05-11 | c | 0.00035282 | 3.024e-06 | 2016 | 2015-05-11 | C | 1 | 0.00035282 | 3.0238e-06
4813881 | 2015-05-12 01:57 | 2015-05-12 15:58 | 840.75 | 86 | 24070.45 | 279.889 | 276.889 | 0.072783 | 23812.45 | 0.072003 | 0.00026004 | Restore Supply on Device 5329 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 355591 | Normal Substation: POHOKURA. Current Substation: POHOKURA. The above is incorect Should be 'Waitara East' Tripped on B&C phase O/C & E/F during high wind & heavy rain. During sectionalising and patrol found trees through lines at various sites on Piko Rd. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.072003 | 0.00026004 | 2016 | 2015-05-12 | C | 86 | 0.072003 | 0.00026004
4814898 | 2015-05-12 06:59 | 2015-05-12 11:00 | 241 | 278 | 44343 | 159.5072 | 156.5072 | 0.13408 | 43509 | 0.13156 | 0.00084061 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746382 | ( BBK 2 ) 11kV recloser 6610 Tripped E/F, A Ph O/C, L/O. Feeder sectionalised & fault isolated to between normal open point ABS 347 & ABS 355 ( rest of feeder returned to service ). At pole 746382 found blown H/V insulator & damaged conductor. All repai | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.13156 | 0.00084061 | 2016 | 2015-05-12 | C | 278 | 0.13156 | 0.00084061
4818022 | 2015-05-12 07:21 | 2015-05-12 08:46 | 85.1833 | 5 | 425.9167 | 85.1833 | 82.1833 | 0.0012879 | 410.9167 | 0.0012425 | 1.5119e-05 | Restore Supply on Device T5175 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA806 | Check to see if OMS 4818099 (32 Nopera Rd is related to this fault). Replaced 2 x 3A H/V O/H fuses at Fuses TA806 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.0012425 | 1.5119e-05 | 2016 | 2015-05-12 | C | 5 | 0.0012425 | 1.5119e-05
4818035 | 2015-05-12 07:32 | 2015-05-12 09:20 | 107.5833 | 1 | 107.5833 | 107.5833 | 104.5833 | 0.00032531 | 104.5833 | 0.00031623 | 3.0238e-06 | Restore Supply on Device 5012E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5012E | link 4818353 to this job. Replace 1 x 3A H/V, O/H fuse | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.00031623 | 3.024e-06 | 2016 | 2015-05-12 | C | 1 | 0.00031623 | 3.0238e-06
4818056 | 2015-05-12 11:27 | 2015-05-12 12:17 | 50.05 | 4 | 200.2 | 50.05 | 47.05 | 0.00060536 | 188.2 | 0.00056907 | 1.2095e-05 | Restore Supply on Device 5634 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5634 | Emergency switching to reload 1 x 2A H/V O/H fuse at transformer 4491T. Isolation at Fuses 5634 ( spur line no back feeds ). 1 X 10A Fuse blown at Fuses 5634 also ( suspect lightning ). All fuses re loaded all service restored. Materials 1 x 2A H/V O/H fu | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.00056907 | 1.2095e-05 | 2016 | 2015-05-12 | C | 4 | 0.00056907 | 1.2095e-05
4818092 | 2015-05-28 14:00 | 2015-05-28 15:08 | 68 | 61 | 4148 | 68 | 65 | 0.012543 | 3965 | 0.011989 | 0.00018445 | NAPA ID:08481 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2606 | Replace Poles & X-Arms. Works location: Gray Road, Morrinsville. WO 30001807. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-05-28 | b | 0.0059946 | 9.2225e-05 | 2016 | 2015-05-28 | B | 61 | 0.011989 | 0.00018445
4818099 | 2015-05-12 15:00 | 2015-05-12 16:20 | 80 | 1 | 80 | 80 | 77 | 0.0002419 | 77 | 0.00023283 | 3.0238e-06 | Restore Supply on Device T5165 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5165 | 11:10am 2 R request to replace blown TX T5165. 12pm email from Tallia - Dennis Embling aware of this and when the guys become available which will be later today the hub will be updated with whom attending. Transformer T5165 replaced & returned to servi | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.00023283 | 3.024e-06 | 2016 | 2015-05-12 | C | 1 | 0.00023283 | 3.0238e-06
4818583 | 2015-05-12 09:17 | 2015-05-12 16:39 | 442.2 | 65 | 11679.75 | 179.6885 | 176.6885 | 0.035317 | 11484.75 | 0.034727 | 0.00019654 | Restore Supply on Device V5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 11kV reclser V5 tripped L/O. Broken insulator at pole P49822 and a second fault at pole P06212 with a broken DDO holder at Tx Site T9/41. All work Complete. NOTE, All HV repairs are in OMS Job 4818936, ASW | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.034727 | 0.00019654 | 2016 | 2015-05-12 | C | 65 | 0.034727 | 0.00019654
4818814 | 2015-06-02 09:40 | 2015-06-02 13:53 | 252.2333 | 50 | 12171.1667 | 243.4233 | 240.4233 | 0.036803 | 12021.1667 | 0.036349 | 0.00015119 | NAPA ID:09275 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS WH284 | Install xarms replace DNO Abs WH203. Works location: Ohangai Rd Hawera. WO 30008737 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-06-02 | b | 0.018175 | 7.5594e-05 | 2016 | 2015-06-02 | B | 50 | 0.036349 | 0.00015119
4818815 | 2015-05-12 10:06 | 2015-05-12 17:45 | 458.7667 | 119 | 20297.8 | 170.5697 | 167.5697 | 0.061376 | 19940.8 | 0.060296 | 0.00035983 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8763 | Cloton Rd S61 Recloser 8763/2 tripped E/F, L/O. Feeder sectionalised & fault isolated to beyond Fuses 5566 on Stanley Rd ( no back feeds ) Temp fuses installed at pole 758389 between transformers 2678T & 4840T probable insulator fault yet to be found. Ma | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.060296 | 0.00035983 | 2016 | 2015-05-12 | C | 119 | 0.060296 | 0.00035983
4819314 | 2015-06-15 09:00 | 2015-06-15 16:58 | 478 | 66 | 31548 | 478 | 475 | 0.095394 | 31350 | 0.094795 | 0.00019957 | NAPA ID:09373 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC2-021 | CHANGE 33KV / 11KV POLES. Works location: Hwy 2 Omokoroa. IR 7180 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-06-15 | b | 0.047397 | 9.9784e-05 | 2016 | 2015-06-15 | B | 66 | 0.094795 | 0.00019957
4819879 | 2015-05-20 09:28 | 2015-05-20 15:02 | 334.3833 | 39 | 13040.95 | 334.3833 | 331.3833 | 0.039433 | 12923.95 | 0.039079 | 0.00011793 | NAPA ID:08029 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IP482 | Worksite 1: Northpower Dan Hardie: Replace 11kV poles, crossarms, conductors between ABS 956 and ABS 883. Worksite 2: Downers Malcolm Shield install new 11kV Recloser 9941/2, LINKS 9941/4, Re-label 11kV ABS 952 9941/1 as bypass ABS. (Commission once Supp | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-20 | b | 0.019539 | 5.8963e-05 | 2016 | 2015-05-20 | B | 39 | 0.039079 | 0.00011793
4819890 | 2015-05-12 14:58 | 2015-05-12 18:12 | 193.7333 | 2 | 387.4667 | 193.7333 | 190.7333 | 0.0011716 | 381.4667 | 0.0011535 | 6.0475e-06 | Restore Supply on Device 3327T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12006 | Replaced 2 x 3A H/V O/H fuses at Fuses 12006 ( would not force to these fuses ) | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-05-12 | c | 0.0011535 | 6.048e-06 | 2016 | 2015-05-12 | C | 2 | 0.0011535 | 6.0475e-06
4822919 | 2015-05-12 22:30 | 2015-05-12 23:05 | 35.1333 | 2383 | 83722.7333 | 35.1333 | 32.1333 | 0.25316 | 76573.7333 | 0.23154 | 0.0072056 | Restore Supply on Device 1072 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Taihape Sub | Supply restored via B line @23:05 various sites checked and appears ok Line patrol to be carried out in daylight Normal supply restored @23:59 | F1,F2,F3 | TAIHAPE A 33KV | MATAROA | Wanganui | TP_MATAROA | Western Electricity | POWERCO | 2015-05-12 | c | 0.23154 | 0.0072056 | 2016 | 2015-05-12 | C | 2383 | 0.23154 | 0.0072056
4825579 | 2015-05-13 11:38 | 2015-05-13 17:45 | 367 | 6 | 2202 | 367 | 364 | 0.0066583 | 2184 | 0.0066039 | 1.8143e-05 | Restore Supply on Device P4270 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P4270 | 30kva P4270 tx blown - has contact Brent Moratti to attend to replace tx. Warren leaving site. 3.25pm Allena from Genesis called for an update. Sammy at the svs hub advised FM in Enroute now (ETA approx 20 mins), Transformer replaced, relivened OK. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-05-13 | c | 0.0066039 | 1.8143e-05 | 2016 | 2015-05-13 | C | 6 | 0.0066039 | 1.8143e-05
4825590 | 2015-05-13 07:21 | 2015-05-13 09:11 | 109.7 | 527 | 24282.2 | 46.0763 | 43.0763 | 0.073424 | 22701.2 | 0.068643 | 0.0015935 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220326 | Protection review required for this. at 07:21 Papamoa Sub, CB 8 Reid Rd Feeder, Tripped, O/C, L/O. Recloser RP09 Also Tripped, Ph A + B O/C, E/F, L/O. Faultmen dispatched and investigation began. Calls came in of loud bang on Welcome Bay Rd. Faultman atte | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-05-13 | c | 0.068643 | 0.0015935 | 2016 | 2015-05-13 | C | 527 | 0.068643 | 0.0015935
4826772 | 2015-05-28 09:00 | 2015-05-28 15:30 | 390 | 13 | 5070 | 390 | 387 | 0.01533 | 5031 | 0.015213 | 3.9309e-05 | NAPA ID:07965 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IP609 | To replace 11kV conductors between IP609 and TEMP63 at Pole # B0527. Works location: Kokako Rd. WO 30000626 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-28 | b | 0.0076063 | 1.9654e-05 | 2016 | 2015-05-28 | B | 13 | 0.015213 | 3.9309e-05
4827335 | 2015-05-13 10:57 | 2015-05-13 12:41 | 103.7167 | 2 | 207.4333 | 103.7167 | 100.7167 | 0.00062723 | 201.4333 | 0.00060909 | 6.0475e-06 | Restore Supply on Device SF8-008 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SF8-008 | at 12:40, Pongakawa Sub, CB 2 Otamarakau Feeder. Faultman attended site, found 2x DDO's blown at Fuses SF8-008. Patrolled line, found bird had caused fault. Reloaded-Relivened fuses. All Power Restored on completion. Dave Ngatai Attended. 2x HV Fuses Repl | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-13 | c | 0.00060909 | 6.048e-06 | 2016 | 2015-05-13 | C | 2 | 0.00060909 | 6.0475e-06
4827825 | 2015-06-03 09:20 | 2015-06-03 12:01 | 161 | 2 | 322 | 161 | 158 | 0.00097365 | 316 | 0.00095551 | 6.0475e-06 | NAPA ID:08727 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse P27 | Replace HV xarms on poles P19770 & 19771. Works location: Forest Rd Kimbolton. WO 10160678 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-06-03 | b | 0.00047775 | 3.024e-06 | 2016 | 2015-06-03 | B | 2 | 0.00095551 | 6.0475e-06
4827900 | 2015-06-04 08:46 | 2015-06-04 15:04 | 378.15 | 72 | 27226.8 | 378.15 | 375.15 | 0.082327 | 27010.8 | 0.081674 | 0.00021771 | NAPA ID:08632 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S162 | 11KV ARM POLE REPLACEMENT. Works location: Kaka Amu Rd. WO 30001033 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-06-04 | b | 0.040837 | 0.00010886 | 2016 | 2015-06-04 | B | 72 | 0.081674 | 0.00021771
4827928 | 2015-05-13 14:49 | 2015-05-13 15:27 | 38 | 50 | 1890.4 | 37.808 | 34.808 | 0.0057161 | 1740.4 | 0.0052626 | 0.00015119 | Restore Supply on Device T9/344 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P26941 | Faultman found broken HV jumper at ABS I9. Backfeed put in at ABS 10169 & Isolated at ABS I40 & I7. Jumper replaced and new ampac connection used. | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-05-13 | c | 0.0052626 | 0.00015119 | 2016 | 2015-05-13 | C | 50 | 0.0052626 | 0.00015119
4834657 | 2015-06-02 09:04 | 2015-06-02 12:13 | 188.95 | 88 | 16627.6 | 188.95 | 185.95 | 0.050278 | 16363.6 | 0.04948 | 0.00026609 | NAPA ID:08324 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-014 | REPLACE POLE AND ARMS. INSTALL TEMP SW 23 FOR UP SHUTS. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-02 | b | 0.02474 | 0.00013305 | 2016 | 2015-06-02 | B | 88 | 0.04948 | 0.00026609
4834967 | 2015-05-19 09:03 | 2015-05-19 15:36 | 392.95 | 19 | 2578.1 | 135.6895 | 132.6895 | 0.0077956 | 2521.1 | 0.0076232 | 5.7451e-05 | NAPA ID:07959 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | between Pole 9916 and TEMP63 at Pole B0527. | To upgrade existing 11kV conductors between 9916 and TEMP63 at Pole B0527. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-19 | b | 0.0038116 | 2.8726e-05 | 2016 | 2015-05-19 | B | 19 | 0.0076232 | 5.7451e-05
4835981 | 2015-05-13 17:26 | 2015-05-13 22:49 | 323 | 119 | 7214.25 | 60.6239 | 57.6239 | 0.021814 | 6857.25 | 0.020735 | 0.00035983 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 75831 and 758392 | Tripping on recloser CB 8763/2. (Ongoing fault). Feeder patrolled. Restored again but tripped when temp fuses relivened. A total of 3 suspect Insulators then replaced, One at Pole 758391 and 2 at Pole 758392. Restored OK. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-05-13 | c | 0.020735 | 0.00035983 | 2016 | 2015-05-13 | C | 119 | 0.020735 | 0.00035983
4836299 | 2015-05-13 17:47 | 2015-05-13 22:44 | 296.3167 | 6353 | 1850405.4667 | 291.2648 | 288.2648 | 5.5952 | 1831346.4667 | 5.5376 | 0.01921 | Restore Supply on Device 40 | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | WHIWGM094 | * Waihi 33kV CB 40 Tripped A Ph O/C E/F. Loss of supply to Whangamata Sub. * Waihi, Feeder 1-Waihi North 11kV Recloser R/S 9604 (OMS 4836145) also tripped E/F, lock out. * Issue Escalated to NCTL and in turn communicated to regional Powerco project manage | F1,F2,F3 | WAIHI-WHANGAMATA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 2015-05-13 | c | 5.5376 | 0.01921 | 2016 | 2015-05-13 | C | 6353 | 5.5376 | 0.01921
4843775 | 2015-06-02 10:10 | 2015-06-02 12:45 | 155 | 9 | 1395 | 155 | 152 | 0.0042181 | 1368 | 0.0041365 | 2.7214e-05 | NAPA ID:09026 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV IC2586 | Stand over for treecutting (Asplundh). Works location: Coroglen Rd Whitianga. PPPD 45802 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-06-02 | b | 0.0020683 | 1.3607e-05 | 2016 | 2015-06-02 | B | 9 | 0.0041365 | 2.7214e-05
4843796 | 2015-06-02 08:50 | 2015-06-02 15:06 | 376 | 38 | 14288 | 376 | 373 | 0.043203 | 14174 | 0.042859 | 0.0001149 | NAPA ID:08654 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1152 | Replace 11kV Crossarms. Works location: Fisher Rd Netherton. WO 30008212 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-02 | b | 0.021429 | 5.7451e-05 | 2016 | 2015-06-02 | B | 38 | 0.042859 | 0.0001149
4843857 | 2015-06-05 08:31 | 2015-06-05 15:14 | 403.3167 | 38 | 15326.0333 | 403.3167 | 400.3167 | 0.046342 | 15212.0333 | 0.045998 | 0.0001149 | NAPA ID:08656 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1152 | Replace 11kV Crossarms. Works location: Fisher Rd Netherton. WO 30008212 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-05 | b | 0.022999 | 5.7451e-05 | 2016 | 2015-06-05 | B | 38 | 0.045998 | 0.0001149
4845243 | 2015-05-14 09:06 | 2015-05-14 13:57 | 291.2167 | 86 | 11555.0833 | 134.3614 | 131.3614 | 0.03494 | 11297.0833 | 0.03416 | 0.00026004 | Restore Supply on Device 5329 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763880 | Tripping on Recloser CB5329 on EF1. Patrol found a conductor resting on the crossarm on Piko Rd. Conductor rebound, relivened OK. (isolation from Fuses 5193). | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-05-14 | c | 0.03416 | 0.00026004 | 2016 | 2015-05-14 | C | 86 | 0.03416 | 0.00026004
4845994 | 2015-05-14 10:39 | 2015-05-14 15:15 | 276.65 | 8 | 2213.2 | 276.65 | 273.65 | 0.0066922 | 2189.2 | 0.0066196 | 2.419e-05 | Restore Supply on Device 6551 | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 737914 | Tripping on Recloser CB 6551 on E/F. Patrol found 4 conductors down from Poles 737913 and 737914. Ponga tree had fallen through conductors causing damage. Heavy rain, tree slipped away. Repairs carried out and relivened. 12 sleeves were used along with 40 | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-05-14 | c | 0.0066196 | 2.419e-05 | 2016 | 2015-05-14 | C | 8 | 0.0066196 | 2.419e-05
4846193 | 2015-06-08 08:30 | 2015-06-08 15:09 | 399 | 22 | 8778 | 399 | 396 | 0.026543 | 8712 | 0.026343 | 6.6523e-05 | NAPA ID:08997 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 965 | Upgrade 11KV Poles between tempary fuses 51 & ABS 965. Works location: Parapara Rd. WO 30002303 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-06-08 | b | 0.013172 | 3.3261e-05 | 2016 | 2015-06-08 | B | 22 | 0.026343 | 6.6523e-05
4846251 | 2015-06-02 09:46 | 2015-06-02 12:52 | 186.05 | 21 | 3907.05 | 186.05 | 183.05 | 0.011814 | 3844.05 | 0.011623 | 6.3499e-05 | NAPA ID:08711 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV KA763 | Replace K4142 replace pole 720033 and new cross arm pole 720095. Works location: Kokiri Rd Kapuni. WO 10161134 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-06-02 | b | 0.0058117 | 3.1749e-05 | 2016 | 2015-06-02 | B | 21 | 0.011623 | 6.3499e-05
4846269 | 2015-06-03 09:15 | 2015-06-03 10:50 | 95 | 3 | 285 | 95 | 92 | 0.00086177 | 276 | 0.00083456 | 9.0713e-06 | NAPA ID:08688 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-238 | Morning to replace TC2-238. Works location: Sargent Rd. WO 10147830 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-06-03 | b | 0.00041728 | 4.536e-06 | 2016 | 2015-06-03 | B | 3 | 0.00083456 | 9.0713e-06
4846286 | 2015-05-14 18:35 | 2015-05-14 18:54 | 18.75 | 149 | 2793.75 | 18.75 | 15.75 | 0.0084476 | 2346.75 | 0.007096 | 0.00045054 | Restore Supply on Device TD2-047 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD2-047 | at 18:35 Omokoroa Sub, CB 2 Whakamarama Feeder. Found broken jumper at Transformer Fuses TD2-047. Isolated Lines at ABS SC2-024 & SD4-004. Permit issued & repairs carried out. All Power Restored on completion. Dave Ngatai Attended. 1x Jumper & 1x HV Conne | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-05-14 | c | 0.007096 | 0.00045054 | 2016 | 2015-05-14 | C | 149 | 0.007096 | 0.00045054
4846292 | 2015-06-03 11:50 | 2015-06-03 12:40 | 50 | 3 | 150 | 50 | 47 | 0.00045356 | 141 | 0.00042635 | 9.0713e-06 | NAPA ID:09018 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-156 | To add extra LV arm on the transformer pole. Works location: Walford Rd. WO 10147830 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-06-03 | b | 0.00021317 | 4.536e-06 | 2016 | 2015-06-03 | B | 3 | 0.00042635 | 9.0713e-06
4846366 | 2015-05-14 14:18 | 2015-05-14 15:35 | 76.65 | 1 | 76.65 | 76.65 | 73.65 | 0.00023177 | 73.65 | 0.0002227 | 3.0238e-06 | Restore Supply on Device X1157 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuses X1157 | 2 x 5A links due to bird strike. Outage step on 4846239 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-14 | c | 0.0002227 | 3.024e-06 | 2016 | 2015-05-14 | C | 1 | 0.0002227 | 3.0238e-06
4846458 | 2015-05-14 17:57 | 2015-05-14 20:15 | 137.5167 | 28 | 3850.4667 | 137.5167 | 134.5167 | 0.011643 | 3766.4667 | 0.011389 | 8.4665e-05 | Restore Supply on Device WH272 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725720 | Replace 3X H/T Insulators at Pole 725720 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-05-14 | c | 0.011389 | 8.4665e-05 | 2016 | 2015-05-14 | C | 28 | 0.011389 | 8.4665e-05
4847237 | 2015-05-14 20:33 | 2015-05-14 23:53 | 199.5833 | 1080 | 111356.95 | 103.1083 | 100.1083 | 0.33672 | 108116.95 | 0.32692 | 0.0032657 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 214405 | at 20:33 Omanu Sub, CB 1 Concord Ave Feeder, Tripped, B + C O/C, L/O. CB 4 Bayfair Feeder, Tripped, A + B O/C, L/O. Faultmen dispatched and investigation began. Media reported of a tornado going through the area. Report came through of roof that had come | F3 | CONCORDE AVE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-05-14 | c | 0.32692 | 0.0032657 | 2016 | 2015-05-14 | C | 1080 | 0.32692 | 0.0032657
4848290 | 2015-05-14 21:04 | 2015-05-15 01:13 | 248.6833 | 1108 | 33127.2167 | 29.8982 | 26.8982 | 0.10017 | 29803.2167 | 0.090118 | 0.0033503 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228679 | at 21:04 Pongakawa Sub, CB 4 Old Coach Rd Feeder, Tripped, E/F, L/O. Faultman dispatched & investigation began. Feeder sectionalised & patrolled. Found tree through lines at Pole 228679. Isolated Lines at ABS SF6-014 & SF6-018. Backfeed supplied from TPV | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-14 | c | 0.090118 | 0.0033503 | 2016 | 2015-05-14 | C | 1108 | 0.090118 | 0.0033503
4849027 | 2015-05-14 21:48 | 2015-05-15 10:20 | 752 | 775 | 55184 | 71.2052 | 68.2052 | 0.16686 | 52859 | 0.15983 | 0.0023434 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 215124 | at 20:33 Omanu Sub, CB 1 Concord Ave Feeder, Tripped, B + C O/C, L/O. CB 4 Bayfair Feeder, Tripped, A + B O/C, L/O. Faultmen dispatched and investigation began. Media reported of a tornado going through the area. Report came through of roof that had come | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-05-14 | c | 0.15983 | 0.0023434 | 2016 | 2015-05-14 | C | 775 | 0.15983 | 0.0023434
4851849 | 2015-05-15 07:32 | 2015-05-15 13:36 | 364.05 | 279 | 18723 | 67.1075 | 64.1075 | 0.056614 | 17886 | 0.054083 | 0.00084363 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 747265 | Darryn spademan attending. nz fire require eta - 10-15mins - advised fire service of eta. Tripping Katere CB5 caused by Car / Pole on Egmont Rd. Extensive damage. Isolation between ABS 365 and 373. Pole and all associated hardware replaced. Relivened OK. | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-15 | c | 0.054083 | 0.00084363 | 2016 | 2015-05-15 | C | 279 | 0.054083 | 0.00084363
4852346 | 2015-06-03 09:33 | 2015-06-03 14:01 | 267.7 | 1 | 267.7 | 267.7 | 264.7 | 0.00080946 | 264.7 | 0.00080039 | 3.0238e-06 | NAPA ID:08937 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC910 | Replace pole and restrain conductor. Works location: Tairua Whitianga Rd. WO 30008612 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-06-03 | b | 0.00040019 | 1.512e-06 | 2016 | 2015-06-03 | B | 1 | 0.00080039 | 3.0238e-06
4852477 | 2015-05-15 10:08 | 2015-05-15 12:34 | 145.3 | 123 | 14877.75 | 120.9573 | 117.9573 | 0.044987 | 14508.75 | 0.043871 | 0.00037192 | Restore Supply on Device C936 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C936 | CB C936 tripped on B phase O/C & E/F flags, Line was patrolled and sectionalised and no fault was found. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-05-15 | c | 0.043871 | 0.00037192 | 2016 | 2015-05-15 | C | 123 | 0.043871 | 0.00037192
4853645 | 2015-05-15 11:45 | 2015-05-15 16:58 | 313.0333 | 348 | 41411.3333 | 118.9981 | 115.9981 | 0.12522 | 40367.3333 | 0.12206 | 0.0010523 | Restore Supply on Device RC22 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O312 | Tree through lines at pole o312 Broken xarm. Crossarm replaced. 3 pin insulators, 2 stays. Jumper off at Pole O311 jumper re-attached. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.12206 | 0.0010523 | 2016 | 2015-05-15 | C | 348 | 0.12206 | 0.0010523
4853995 | 2015-05-14 19:53 | 2015-05-15 14:08 | 1095.2667 | 17 | 3383.2667 | 199.0157 | 196.0157 | 0.01023 | 3332.2667 | 0.010076 | 5.1404e-05 | Restore Supply on Device T28 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P47208 | Faultman found a broken jumpers on pole P47208, line was isolated at ABS's T28, Q77 & ABS T42/1 & Limks T42/4 to replace the jumpers, this had to be accessed by motor bike to make the repair due to the very wet conditions. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-14 | c | 0.010076 | 5.1404e-05 | 2016 | 2015-05-14 | C | 17 | 0.010076 | 5.1404e-05
4854155 | 2015-05-15 12:15 | 2015-05-15 19:11 | 416.1333 | 3448 | 67692.35 | 19.6324 | 16.6324 | 0.20469 | 57348.35 | 0.17341 | 0.010426 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M1916 | at 12:14, Putaruru Sub, CB 3 Taumangi Rd Feeder, Recloser RC36, Tripped, A B C Ph O/C, E/F, L/O. at 12:17 Putaruru Sub, CB 3 Taumangi Rd Feeder, Tripped, A + B O/C. 2 Faults. RC36 Tripping was caused by trees in lines past Links IP526. Lines Isolated at L | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.17341 | 0.010426 | 2016 | 2015-05-15 | C | 3448 | 0.17341 | 0.010426
4854344 | 2015-05-21 09:32 | 2015-05-21 12:16 | 163.5833 | 146 | 23883.1667 | 163.5833 | 160.5833 | 0.072217 | 23445.1667 | 0.070893 | 0.00044147 | NAPA ID:09475 TP_STRATFORD GXP > ELTHAM SUB > RAWHITIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 736143 | Replace broken xarm @ pole 736143 & straghiten pole 736144. Works location: Rawhitiroa Rd. WO 10193246 | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-05-21 | b | 0.035446 | 0.00022074 | 2016 | 2015-05-21 | B | 146 | 0.070893 | 0.00044147
4854345 | 2015-05-15 12:22 | 2015-05-15 14:13 | 110.4833 | 187 | 16093.1167 | 86.0594 | 83.0594 | 0.048662 | 15532.1167 | 0.046965 | 0.00056544 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | M2003 | Tripping on CB9198 (Baird Rd 3) with no flags. Feeder patrolled with a downed tree found at Pole M2003. Tree had clashed lines and caused tripping. No damage, relivened OK. NOTE: Brief Storm through area at the time. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.046965 | 0.00056544 | 2016 | 2015-05-15 | C | 187 | 0.046965 | 0.00056544
4854541 | 2015-05-15 12:30 | 2015-05-15 16:10 | 219.6667 | 440 | 58683.9667 | 133.3727 | 130.3727 | 0.17745 | 57363.9667 | 0.17345 | 0.0013305 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217438 | Line down at Pole 217438. Conductor rehung. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.17345 | 0.0013305 | 2016 | 2015-05-15 | C | 440 | 0.17345 | 0.0013305
4855531 | 2015-05-15 12:34 | 2015-05-15 16:23 | 229.5667 | 522 | 59064.5667 | 113.1505 | 110.1505 | 0.1786 | 57498.5667 | 0.17386 | 0.0015784 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | M2211 | Tripping on CB8 on E/F. Feeder patrolled and sectionalised with fault proving difficult to locate. 2 samall branches found at Pole M2211, removed OK and relivened. Very Stormy conditions at the time. | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.17386 | 0.0015784 | 2016 | 2015-05-15 | C | 522 | 0.17386 | 0.0015784
4856113 | 2015-05-15 12:34 | 2015-05-15 18:16 | 341.3667 | 314 | 41908.2 | 133.4656 | 130.4656 | 0.12672 | 40966.2 | 0.12387 | 0.00094946 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - TORNADO | 222043 | RS 9168. 2.18pm - advised control of lines down at 148 burd road, fire comms are on site F1845130. 2.23pm - fire commms advised of 25min ETA. 1 X 11kV Pole 2 Xarms 6 Pin Insulators | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.12387 | 0.00094946 | 2016 | 2015-05-15 | C | 314 | 0.12387 | 0.00094946
4857533 | 2015-05-15 12:48 | 2015-05-15 15:14 | 145.6 | 200 | 22643.2 | 113.216 | 110.216 | 0.068468 | 22043.2 | 0.066653 | 0.00060475 | Restore Supply on Device RP10 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223289 | Line down at Pole 223289. Conductor re-strung. 1 mtr Namu and 1 link used. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.066653 | 0.00060475 | 2016 | 2015-05-15 | C | 200 | 0.066653 | 0.00060475
4858352 | 2015-05-15 12:54 | 2015-05-15 16:21 | 207.4833 | 678 | 79415.8667 | 117.1325 | 114.1325 | 0.24013 | 77381.8667 | 0.23398 | 0.0020501 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218314 | Line down at Pole 218314. Restrung | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.23398 | 0.0020501 | 2016 | 2015-05-15 | C | 678 | 0.23398 | 0.0020501
4859051 | 2015-05-15 12:59 | 2015-05-15 16:48 | 229.4833 | 159 | 22090.7667 | 138.9356 | 135.9356 | 0.066797 | 21613.7667 | 0.065355 | 0.00048078 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228998 | Line Down at Pole 228998. Line Restrung | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.065355 | 0.00048078 | 2016 | 2015-05-15 | C | 159 | 0.065355 | 0.00048078
4862770 | 2015-05-15 15:13 | 2015-05-15 15:33 | 19.5333 | 78 | 1523.6 | 19.5333 | 16.5333 | 0.004607 | 1289.6 | 0.0038994 | 0.00023585 | Restore Supply on Device TC583 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2235 | Possibly part of 4859249 Broken Jumper at Fuses FC2235 Re-connected | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.0038994 | 0.00023585 | 2016 | 2015-05-15 | C | 78 | 0.0038994 | 0.00023585
4867004 | 2015-05-15 16:31 | 2015-05-15 19:32 | 181.2167 | 6 | 347.7333 | 57.9556 | 54.9556 | 0.0010515 | 329.7333 | 0.00099703 | 1.8143e-05 | Restore Supply on Device TE3-030 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE3-030 | 1 HV Fuse Barrel. 2 X 3A HV Fuses Replaced | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.00099704 | 1.8143e-05 | 2016 | 2015-05-15 | C | 6 | 0.00099703 | 1.8143e-05
4868666 | 2015-05-15 16:09 | 2015-05-15 23:54 | 464.4167 | 332 | 32457.4167 | 97.7633 | 94.7633 | 0.098143 | 31461.4167 | 0.095132 | 0.0010039 | Restore Supply on Device IP424 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS SE5-139 | at 16:47, Te Puke Sub, CB 8 Te Matai Rd Feeder, Recloser 9502 Tripped, No Flags, L/O. Faultmen dispatched and investigation began. Feeder sectionalising began. Multiple faults found on this feeder. Found 1x Blown Fuse at SF5-004. Reloaded, Relivened. 2x B | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.095132 | 0.0010039 | 2016 | 2015-05-15 | C | 332 | 0.095132 | 0.0010039
4868762 | 2015-05-15 18:24 | 2015-05-16 01:41 | 436.3 | 1 | 436.3 | 436.3 | 433.3 | 0.0013193 | 433.3 | 0.0013102 | 3.0238e-06 | Restore Supply on Device TD3-315 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213130 | at 23:46, Bethlehem Sub, CB 1 Waipuna Feeder. Found broken crossarm at Pole 213130. Isolated lines at Fuses SD3-153. Permit Issued & Repairs carried out. All power restored on completion. Haden Beddgood attended. 4x Insulators, 2x HV Crossarms, 1x Binder, | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.0013102 | 3.024e-06 | 2016 | 2015-05-15 | C | 1 | 0.0013102 | 3.0238e-06
4869239 | 2015-05-15 20:32 | 2015-05-15 21:43 | 71.2333 | 11 | 783.5667 | 71.2333 | 68.2333 | 0.0023693 | 750.5667 | 0.0022695 | 3.3261e-05 | Restore Supply on Device TP2194 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1499 | Wayne Seath Attended. Replaced 2x DDO's at Fuses FC1499. Line Patrolled, Unknown cause.IS 4869236 RELATED | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.0022695 | 3.3261e-05 | 2016 | 2015-05-15 | C | 11 | 0.0022695 | 3.3261e-05
4869250 | 2015-05-15 20:48 | 2015-05-15 22:26 | 97.45 | 9 | 877.05 | 97.45 | 94.45 | 0.002652 | 850.05 | 0.0025703 | 2.7214e-05 | Restore Supply on Device FP1405 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FP1405 | Marty Keenan Attended. Reloaded-Relivened 2x DDO's. All Power Restored. Were high winds in this area today. Marty Believes was probably caused by line clash | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.0025703 | 2.7214e-05 | 2016 | 2015-05-15 | C | 9 | 0.0025703 | 2.7214e-05
4869490 | 2015-05-15 21:51 | 2015-05-16 05:05 | 434.2833 | 115 | 12917 | 112.3217 | 109.3217 | 0.039058 | 12572 | 0.038015 | 0.00034773 | Restore Supply on Device X393 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 784274 | RS 2032, A/R, L/O, E/F. Comms to recloser not working. Patrolled & Sectionalised with fault being found at Pole 784274. Due to pine tree falling through LV lines causing one line to sit on HV wires.LV removed from isolated HV lines and Transformer X1759 l | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-15 | c | 0.038015 | 0.00034773 | 2016 | 2015-05-15 | C | 115 | 0.038015 | 0.00034773
4869499 | 2015-05-16 09:53 | 2015-05-16 14:45 | 291.7333 | 8 | 2333.8667 | 291.7333 | 288.7333 | 0.0070571 | 2309.8667 | 0.0069845 | 2.419e-05 | Referral: Restore Supply on Device TE3-210 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 216859 | 173 BELK ROAD SOUTH. Isolated for safety low voltage , too dark to fault locate as is rural, Ted will attend 16/04. 8.23am extra kms travelled as he wasn't advised that this was Belk Road South and he went to Belk Road North. Tree through line at pole 216 | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-16 | c | 0.0069845 | 2.419e-05 | 2016 | 2015-05-16 | C | 8 | 0.0069845 | 2.419e-05
4869513 | 2015-05-15 22:09 | 2015-05-16 09:15 | 666 | 4 | 2664 | 666 | 663 | 0.0080553 | 2652 | 0.008019 | 1.2095e-05 | Restore Supply on Device FC2472 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2472 | 8.23am - Wayne called advising he needs assistance for patrolling line. Send through another 1R, this to be discussed at invoicing level. Line beyond Fuses FC2472 patrolled in morning with no obvious fault found although trees near line at pole 2114 need | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-05-15 | c | 0.008019 | 1.2095e-05 | 2016 | 2015-05-15 | C | 4 | 0.008019 | 1.2095e-05
4872971 | 2015-05-16 04:10 | 2015-05-16 11:26 | 436 | 2383 | 52572.1167 | 22.0613 | 19.0613 | 0.15897 | 45423.1167 | 0.13735 | 0.0072056 | Electric Job | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 779604 | 33kV CB 1072 Tripped, Phase to Phase Fault. Needs patrolling at first light, line was patrolled and a floating wire was found on pole 779604, line was isolated at ABS's 3023 & 307 on the 33KV line and at ABS's 221 & 521(TPE CB 6) on 11KV line. 1 x 33KV bi | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-16 | c | 0.13735 | 0.0072056 | 2016 | 2015-05-16 | C | 2383 | 0.13735 | 0.0072056
4873527 | 2015-05-16 12:04 | 2015-05-16 13:40 | 96 | 17 | 1632 | 96 | 93 | 0.0049348 | 1581 | 0.0047806 | 5.1404e-05 | Restore Supply on Device T1528 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 832945 | Please check if OMS4873664 2B Burnett Road LV related - on pole on corner of Burnetts Road & Upper plain road, pole # 7702 836196 circuit breaker broken on pole 836196 - advised Lucas. Faultman found line down at pole 832945, line was isolated at Fuses 7 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-16 | c | 0.0047806 | 5.1404e-05 | 2016 | 2015-05-16 | C | 17 | 0.0047806 | 5.1404e-05
4873688 | 2015-05-16 14:03 | 2015-05-16 18:00 | 237 | 1 | 237 | 237 | 234 | 0.00071663 | 234 | 0.00070756 | 3.0238e-06 | Restore Supply on Device 341 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 750394 | (1R) Check for safety - Trees growing in lines, contact Peter 0211172626. 10.52am - Called Glo at svs hub to advise. will need Asplundh to attend, power is still on but trees growing 10m through the line. 2.03pm temp line break on pole 750395 - Craig advi | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-16 | c | 0.00070756 | 3.024e-06 | 2016 | 2015-05-16 | C | 1 | 0.00070756 | 3.0238e-06
4873806 | 2015-05-16 13:27 | 2015-05-16 18:09 | 281.7833 | 1 | 281.7833 | 281.7833 | 278.7833 | 0.00085205 | 278.7833 | 0.00084297 | 3.0238e-06 | Restore Supply on Device T1791 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7345 | Faultman found blown fuses at Fuses 7345, suspect bird strike as line goes over a swamp. 2 x 3 amp fuses replaced. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-05-16 | c | 0.00084297 | 3.024e-06 | 2016 | 2015-05-16 | C | 1 | 0.00084297 | 3.0238e-06
4873919 | 2015-05-16 15:32 | 2015-05-16 16:30 | 58 | 7 | 406 | 58 | 55 | 0.0012276 | 385 | 0.0011641 | 2.1166e-05 | Restore Supply on Device T7/230 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses T4 | Line that runs along road, huge bang and sparking and now 2 fuses hanging down. 3.33 advised Sammy at SVS hub & control. Faultman found 2 blown fuses at Fuses T4, Line patrolled suspect bird strike. 2 X 6 Amp rewireable fuses replaced. | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-16 | c | 0.0011641 | 2.1166e-05 | 2016 | 2015-05-16 | C | 7 | 0.0011641 | 2.1166e-05
4874336 | 2015-05-17 02:10 | 2015-05-17 08:49 | 398.7 | 177 | 14514.5833 | 82.0033 | 79.0033 | 0.043889 | 13983.5833 | 0.042283 | 0.00053521 | Restore Supply on Device 2924 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843617 - 483620 | During sectionalising and patrol found line down in two places between poles 843617 & 483620 Isolated at links 2875 for repairs. Materials used 100m squirel conductor 3X sleves and 3 Forges | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-05-17 | c | 0.042283 | 0.00053521 | 2016 | 2015-05-17 | C | 177 | 0.042283 | 0.00053521
4874431 | 2015-05-17 03:07 | 2015-05-17 06:22 | 194.25 | 277 | 15106.7 | 54.5368 | 51.5368 | 0.045679 | 14275.7 | 0.043166 | 0.00083758 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 322178 | Car V Pole. 100 mtrs East of Kaituna Rd on Maketu Rd. Police Event # 21221987. Pole Replaced. + xarm 3 insulators. NDR 44862. | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-05-17 | c | 0.043166 | 0.00083758 | 2016 | 2015-05-17 | C | 277 | 0.043166 | 0.00083758
4876245 | 2015-05-17 10:00 | 2015-05-17 11:29 | 89 | 32 | 2848 | 89 | 86 | 0.0086117 | 2752 | 0.0083214 | 9.676e-05 | Restore Supply on Device 82W | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773718 | Report received of lines down found @ pole 773718 and isolated @ fuses 287 for repairs. Materials used =/- 5m copper wire | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-17 | c | 0.0083214 | 9.676e-05 | 2016 | 2015-05-17 | C | 32 | 0.0083214 | 9.676e-05
4876249 | 2015-05-17 08:11 | 2015-05-17 10:21 | 130 | 59 | 7651.6333 | 129.6887 | 126.6887 | 0.023137 | 7474.6333 | 0.022602 | 0.0001784 | Restore Supply on Device TEMP33 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC440 | 11kv line between ABS IC487 & Links temp33 isolated to repair burnt jumper at transformer TC440. All 3 fuse bases replaced as they were showing signs of corrosion | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-17 | c | 0.022602 | 0.0001784 | 2016 | 2015-05-17 | C | 59 | 0.022602 | 0.0001784
4876390 | 2015-05-17 11:13 | 2015-05-17 14:58 | 224.8167 | 1 | 224.8167 | 224.8167 | 221.8167 | 0.00067979 | 221.8167 | 0.00067072 | 3.0238e-06 | Restore Supply on Device 588 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 442644 | REPLACED CABLE CRUTCH DUE TO DETERIORATION. REPLACED 2 X 10 AMP HV FUSES & 2 X 60 AMP LV FUSES. No other assets repaired or replaced. Adjacent assets ok | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-17 | c | 0.00067072 | 3.024e-06 | 2016 | 2015-05-17 | C | 1 | 0.00067072 | 3.0238e-06
4877473 | 2015-05-17 19:04 | 2015-05-17 19:55 | 51 | 12 | 612 | 51 | 48 | 0.0018505 | 576 | 0.0017417 | 3.6285e-05 | Restore Supply on Device 7273P | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M6 | Faultman found 2 blown fuse at Fuses M6, line was patrolled, suspect lines struck by ducks. 2 X 10 amp HV fuses replaced. | F1 | SKYHAWK | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-17 | c | 0.0017417 | 3.6285e-05 | 2016 | 2015-05-17 | C | 12 | 0.0017417 | 3.6285e-05
4924898 | 2015-05-18 08:43 | 2015-05-18 09:48 | 65 | 91 | 5915 | 65 | 62 | 0.017886 | 5642 | 0.01706 | 0.00027516 | Restore Supply on Device 149 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/251 |  | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-18 | b | 0.00853 | 0.00013758 | 2016 | 2015-05-18 | B | 91 | 0.01706 | 0.00027516
4925400 | 2015-05-18 12:30 | 2015-05-18 13:16 | 45.9667 | 1 | 45.9667 | 45.9667 | 42.9667 | 0.00013899 | 42.9667 | 0.00012992 | 3.0238e-06 | Restore Supply on Device TC851 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | U12740 | *CHECK FOR SAFETY* insulator on power pole has come off and is now hanging. 10:21am called through to hub - Joanne. Polymer strain insulator has come off crossarm at pole u12740. Steve redrilled bolt hole to remount insulator. Isolation at Fuses FC4015. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-05-18 | c | 0.00012992 | 3.024e-06 | 2016 | 2015-05-18 | C | 1 | 0.00012992 | 3.0238e-06
4925847 | 2015-06-09 09:46 | 2015-06-09 13:58 | 252 | 41 | 10332 | 252 | 249 | 0.031241 | 10209 | 0.03087 | 0.00012397 | NAPA ID:08840 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Links2884 | Isolation of 11kv line needed for tree work. Works location: Turakina Valley Rd Taihape. PPPD 53476 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-09 | b | 0.015435 | 6.1987e-05 | 2016 | 2015-06-09 | B | 41 | 0.03087 | 0.00012397
4925865 | 2015-06-02 10:10 | 2015-06-02 14:16 | 246 | 44 | 10824 | 246 | 243 | 0.032729 | 10692 | 0.03233 | 0.00013305 | NAPA ID:08575 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC792 | To in stall new 11kV conductor from existing Pole # I13424 and liven new section of feeder up to new ABS IP616. As shown in attached line design. Works location: Bell Rd. WO 30001809 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-02 | b | 0.016165 | 6.6523e-05 | 2016 | 2015-06-02 | B | 44 | 0.03233 | 0.00013305
4925892 | 2015-05-18 11:00 | 2015-05-18 12:09 | 69 | 91 | 6279 | 69 | 66 | 0.018986 | 6006 | 0.018161 | 0.00027516 | Restore Supply on Device 304 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE |  | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-18 | b | 0.0090804 | 0.00013758 | 2016 | 2015-05-18 | B | 91 | 0.018161 | 0.00027516
4926095 | 2015-05-18 14:18 | 2015-05-18 16:58 | 159.6 | 10 | 1596 | 159.6 | 156.6 | 0.0048259 | 1566 | 0.0047352 | 3.0238e-05 | Restore Supply on Device SF5-001 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP 264/2 | Fuse FP264/2 blown. line patrolled unknown cause. fuse reloaded relivened voltage ok | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-18 | c | 0.0047352 | 3.0238e-05 | 2016 | 2015-05-18 | C | 10 | 0.0047352 | 3.0238e-05
4927444 | 2015-05-18 11:57 | 2015-05-18 14:01 | 123.5167 | 1 | 123.5167 | 123.5167 | 120.5167 | 0.00037348 | 120.5167 | 0.00036441 | 3.0238e-06 | Restore Supply on Device SE7-069 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7-069 | Dairy shed has no power as a truck has hit a power pole. The power pole is on a bit of a lean but still looks safe. 12:02 called through to hub - Lucy. 2 HV fuses blown at SE7-069 due to line clash from truck backing into pole. Fuses reloaded & livened Tr | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-18 | c | 0.00036441 | 3.024e-06 | 2016 | 2015-05-18 | C | 1 | 0.00036441 | 3.0238e-06
4927558 | 2015-05-18 14:48 | 2015-05-18 19:30 | 282.45 | 218 | 22855.4333 | 104.8414 | 101.8414 | 0.069109 | 22201.4333 | 0.067132 | 0.00065918 | Restore Supply on Device R11 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 737155 | Car vs Pole, line was isolated at ABS's 6179, 6191, 6070 & 6154 to replace pole .Chris Katene advised offsite 4.30. Denis Embling and Murray and Richard still at site. 1 x pole and allit's HV & LV hardware. 3 x 100amp fuse holders replaced. 3 x 63 amp H | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-05-18 | c | 0.067132 | 0.00065918 | 2016 | 2015-05-18 | C | 218 | 0.067132 | 0.00065918
4927776 | 2015-05-18 14:52 | 2015-05-18 15:39 | 47 | 3 | 141 | 47 | 44 | 0.00042635 | 132 | 0.00039914 | 9.0713e-06 | Restore Supply on Device FP656 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4206 | Broken Cross arm found during another job attended by Morris Doig - Cross arm Broken at Transformer TC4206 - Isolated at Fuses FP 656 _ Crossarm Replaced - Attended by Paul Cooper | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-18 | c | 0.00039914 | 9.071e-06 | 2016 | 2015-05-18 | C | 3 | 0.00039914 | 9.0713e-06
4927820 | 2015-06-12 08:45 | 2015-06-12 13:18 | 273.15 | 68 | 18574.2 | 273.15 | 270.15 | 0.056164 | 18370.2 | 0.055547 | 0.00020562 | NAPA ID:08857 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 823029 | Replace 11kV pole. Works location: Ahiaruhe Settlement Rd, Carterton. WO 30000799. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-12 | b | 0.027774 | 0.00010281 | 2016 | 2015-06-12 | B | 68 | 0.055547 | 0.00020562
4927845 | 2015-06-05 09:09 | 2015-06-05 12:45 | 216.0667 | 1 | 216.0667 | 216.0667 | 213.0667 | 0.00065333 | 213.0667 | 0.00064426 | 3.0238e-06 | NAPA ID:08940 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC849 | Replace DDO's and crossarms at TC6062. Works location: Manaia Rd Coromandel WO 3000226 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-06-05 | b | 0.00032213 | 1.512e-06 | 2016 | 2015-06-05 | B | 1 | 0.00064426 | 3.0238e-06
4927890 | 2015-06-03 09:49 | 2015-06-03 15:09 | 319.5 | 99 | 31630.5 | 319.5 | 316.5 | 0.095643 | 31333.5 | 0.094745 | 0.00029935 | NAPA ID:08482 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1345 | Replace poles & Cross Arms. Works location: Maungakawa Road. WO 30001807 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-03 | b | 0.047373 | 0.00014968 | 2016 | 2015-06-03 | B | 99 | 0.094745 | 0.00029935
4927896 | 2015-06-04 10:21 | 2015-06-04 11:48 | 86.7833 | 25 | 2169.5833 | 86.7833 | 83.7833 | 0.0065603 | 2094.5833 | 0.0063335 | 7.5594e-05 | NAPA ID:08486 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 841 | Replace poles & X-arms. Works location: Maungakawa Rd Morrinsville. WO 30001807 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-04 | b | 0.0031668 | 3.7797e-05 | 2016 | 2015-06-04 | B | 25 | 0.0063335 | 7.5594e-05
4927978 | 2015-05-18 18:22 | 2015-05-18 20:15 | 112.8667 | 1 | 112.8667 | 112.8667 | 109.8667 | 0.00034128 | 109.8667 | 0.00033221 | 3.0238e-06 | Restore Supply on Device L1205 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730062 | ADVISED CONTROL. 2x 3amp fuse elements - barrell was burnt out. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-18 | c | 0.00033221 | 3.024e-06 | 2016 | 2015-05-18 | C | 1 | 0.00033221 | 3.0238e-06
4928227 | 2015-06-27 09:02 | 2015-06-27 17:15 | 493.1 | 87 | 42899.7 | 493.1 | 490.1 | 0.12972 | 42638.7 | 0.12893 | 0.00026307 | NAPA ID:09286 TP_KINLEITH GXP > MARAETAI ROAD SUB > ARAWA ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9546 | Install RMU's to replace Magnefix switchgear. Works location: Grampian Rd Tokoroa. IR361 | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-06-27 | b | 0.064465 | 0.00013153 | 2016 | 2015-06-27 | B | 87 | 0.12893 | 0.00026307
4929537 | 2015-05-19 13:31 | 2015-05-19 19:06 | 335 | 5 | 1675 | 335 | 332 | 0.0050648 | 1660 | 0.0050194 | 1.5119e-05 | Restore Supply on Device X644 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 792008 | During Patrol located broken crossarm on pole which is remote and inaccessible in darkness . Jumpers broken @ pole 792008 and supply restored to transformer X643 . Transformer X718 is already running on a generator ??, so effectively all power is restored | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.0050194 | 1.5119e-05 | 2016 | 2015-05-19 | C | 5 | 0.0050194 | 1.5119e-05
4929544 | 2015-06-08 09:33 | 2015-06-08 13:20 | 227.05 | 53 | 12033.65 | 227.05 | 224.05 | 0.036387 | 11874.65 | 0.035906 | 0.00016026 | NAPA ID:08681 TP_WAIKINO GXP > WAIHI BEACH SUB > WILSON RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP308 | Repair 11kV Cables feeding TP451. Works location: Seaforth Rd Waihi Beach. WO 10162903 | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-06-08 | b | 0.017953 | 8.013e-05 | 2016 | 2015-06-08 | B | 53 | 0.035906 | 0.00016026
4930303 | 2015-06-09 09:31 | 2015-06-09 14:00 | 269.5333 | 39 | 10511.8 | 269.5333 | 266.5333 | 0.031785 | 10394.8 | 0.031431 | 0.00011793 | NAPA ID:09082 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV IC307 | Provide stand over for tree cutting (Asplundh). Works location: Main Rd Tairua. PPPD 45836 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-06-09 | b | 0.015716 | 5.8963e-05 | 2016 | 2015-06-09 | B | 39 | 0.031431 | 0.00011793
4932880 | 2015-05-19 11:02 | 2015-05-19 14:01 | 178.8167 | 1 | 178.8167 | 178.8167 | 175.8167 | 0.0005407 | 175.8167 | 0.00053163 | 3.0238e-06 | Restore Supply on Device G248 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P28273 | On pole P28273 there is a broken Cross arm. Has been entered as Amber 2 defect in SPA, Powerco deems this as RED DEFECT - 2R request to replace today. Unable to complete crossarm replacement today as the customer is on dialysis. Have organised with them | F3 | MAIN ST 21 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.00053163 | 3.024e-06 | 2016 | 2015-05-19 | C | 1 | 0.00053163 | 3.0238e-06
4932893 | 2015-06-04 10:15 | 2015-06-04 14:56 | 281 | 144 | 40464 | 281 | 278 | 0.12235 | 40032 | 0.12105 | 0.00043542 | NAPA ID:08582 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9561 | To install new 11kV ABS at Pole # I1459, install new pole at I1456 and run new 11kV conductors to new open switch # IP616. Once new conductors are in place cancel AP remove all operator earths and issue LLP to connect jumpers at new open ABS IP616. Once j | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-04 | b | 0.060524 | 0.00021771 | 2016 | 2015-06-04 | B | 144 | 0.12105 | 0.00043542
4932951 | 2015-05-19 12:13 | 2015-05-19 13:48 | 95.2167 | 7 | 666.5167 | 95.2167 | 92.2167 | 0.0020154 | 645.5167 | 0.0019519 | 2.1166e-05 | Restore Supply on Device 7241 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T995 | DDO hanging off crossarm, rehang. Used 1 X H/T Crossarm & 3 X DDO Fuses | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.0019519 | 2.1166e-05 | 2016 | 2015-05-19 | C | 7 | 0.0019519 | 2.1166e-05
4932977 | 2015-05-20 12:56 | 2015-05-20 15:35 | 159.4167 | 78 | 11820.5 | 151.5449 | 148.5449 | 0.035742 | 11586.5 | 0.035035 | 0.00023585 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 7592 OHURA ROAD 708518 | The customer advises a power pole of their street is leaning over approx 15 Degrees. No risk currently as is not touching anything. Power Pole Number 708518. Please go 7592 Ohura Road. Pole leaning badly and leaning into trees, f/m advised that will need | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-05-20 | c | 0.035035 | 0.00023585 | 2016 | 2015-05-20 | C | 78 | 0.035035 | 0.00023585
4938763 | 2015-05-19 15:36 | 2015-05-19 17:15 | 99 | 2 | 198 | 99 | 96 | 0.0005987 | 192 | 0.00058056 | 6.0475e-06 | Restore Supply on Device L4365 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4365 | 2.39pm advised hub of line down. Making safe 2 lv lines down on the road need to replace approx 15 meters on 2 phases requesting 2r also needs bucket truck | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.00058056 | 6.048e-06 | 2016 | 2015-05-19 | C | 2 | 0.00058056 | 6.0475e-06
4940138 | 2015-05-19 17:48 | 2015-05-19 18:24 | 35.6167 | 215 | 7556.8833 | 35.1483 | 32.1483 | 0.02285 | 6911.8833 | 0.0209 | 0.00065011 | Restore Supply on Device X4100 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Reg Set 4461 | Kevin Foley from Downers had a call from the public advising approx 6kms down Parewanui Road there is a tx leaking . plz check for safe. 5.23pm Roger called to advise he is having problems locating this transformer - who we got this job from and to call K | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.0209 | 0.00065011 | 2016 | 2015-05-19 | C | 215 | 0.0209 | 0.00065011
4940464 | 2015-05-19 20:22 | 2015-05-19 20:44 | 22 | 1 | 22 | 22 | 19 | 6.6523e-05 | 19 | 5.7451e-05 | 3.0238e-06 | Restore Supply on Device TE5-092 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE5-110 | Link box SE5-110 isolated to check for blown HV fuse. Isolations 9878/4 & Sw/gear 9926/1. 1x 20amp hv powder fuse in the switch - worked through control, cause age. No other assets repaired or replaced and all adjacent assets checked and are up to Powerc | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-19 | c | 5.7451e-05 | 3.024e-06 | 2016 | 2015-05-19 | C | 1 | 5.7451e-05 | 3.0238e-06
4944747 | 2015-05-19 18:33 | 2015-05-19 18:51 | 18.2 | 1613 | 23674 | 14.677 | 11.677 | 0.071585 | 18835 | 0.056953 | 0.0048773 | Restore Supply on Device C | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB G254/A | Found CB G254/A tripped Supply temp restored via G293/A from Main St 14 . Due to cable ratings being 120a and approximation of load exceeding 150a plug settings on CB G254/A temporary reset from 75% (150a) to 100% (200a) and backfeed restored to CB G254/A | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-05-19 | c | 0.056953 | 0.0048773 | 2016 | 2015-05-19 | C | 1613 | 0.056953 | 0.0048773
4947178 | 2015-05-20 09:26 | 2015-05-20 10:30 | 64.1167 | 4 | 256.4667 | 64.1167 | 61.1167 | 0.00077549 | 244.4667 | 0.00073921 | 1.2095e-05 | Restore Supply on Device L1270 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI270 | PART POWER TO PREMISE. HALF OF THE LIGHTS ARE WORKING AND SOME ARE NOT. SAME WITH THE APPLIANCES. THEY NOTICED AT MIDNIGHT. SOMEONE WILL BE ONSITE BUT SHE WILL BE SLEEPING AS SGE JUST FINISHED WORK SO ONLY KNOCK ON THE DOOR IF REQ, Broken Jumper Found at | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-05-20 | c | 0.00073921 | 1.2095e-05 | 2016 | 2015-05-20 | C | 4 | 0.00073921 | 1.2095e-05
4947183 | 2015-05-20 07:20 | 2015-05-20 12:17 | 296.9333 | 1 | 296.9333 | 296.9333 | 293.9333 | 0.00089786 | 293.9333 | 0.00088878 | 3.0238e-06 | Restore Supply on Device X2287 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X324 | No medical dependency, customer advised has not checked mains as neighbours are affected, advised possible callout charge. Power went off at 6.45 this morning. check to see if OMS 4948345 (5424 OMATANE SOUTH ROAD) is related to this job. Replaced 2x 6A HV | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-20 | c | 0.00088878 | 3.024e-06 | 2016 | 2015-05-20 | C | 1 | 0.00088878 | 3.0238e-06
4947192 | 2015-05-20 07:50 | 2015-05-20 12:36 | 286 | 468 | 110005.2667 | 235.054 | 232.054 | 0.33263 | 108601.2667 | 0.32838 | 0.0014151 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12553 | 11kV CB 1 tripped O/C N, Locked out. Lines Down Reported by Public During Sectionlising - Isolated at Fuses FP58 - Bucket truck required for repairs - Fault left Isolated until one could get on site - Replaced section of conductors as ruther warn - Used 3 | F3 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 2015-05-20 | c | 0.32838 | 0.0014151 | 2016 | 2015-05-20 | C | 468 | 0.32838 | 0.0014151
4948326 | 2015-05-21 09:49 | 2015-05-21 10:49 | 60 | 2 | 120 | 60 | 57 | 0.00036285 | 114 | 0.00034471 | 6.0475e-06 | NAPA ID:09583 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer X1937 | Replace Transformer X1937. 15 kVA, 3 Phase transformer replaced due to oil leak | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-05-21 | b | 0.00017235 | 3.024e-06 | 2016 | 2015-05-21 | B | 2 | 0.00034471 | 6.0475e-06
4948584 | 2015-06-17 08:31 | 2015-06-17 15:22 | 411.0333 | 19 | 7809.6333 | 411.0333 | 408.0333 | 0.023614 | 7752.6333 | 0.023442 | 5.7451e-05 | NAPA ID:08791 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse T24 | Replacing poles P45392, 394, 396, 397, 398, 399, 710 &702. Works location: Mangaramarama Rd WO 10147215 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-17 | b | 0.011721 | 2.8726e-05 | 2016 | 2015-06-17 | B | 19 | 0.023442 | 5.7451e-05
4948589 | 2015-06-16 09:30 | 2015-06-16 15:29 | 359 | 18 | 6462 | 359 | 356 | 0.01954 | 6408 | 0.019376 | 5.4428e-05 | NAPA ID:09046 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS Q63 | To Change 11kv H/W pole and 11kv conductor. Works location: Kohinui Rd. WO 30004481 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-16 | b | 0.0096881 | 2.7214e-05 | 2016 | 2015-06-16 | B | 18 | 0.019376 | 5.4428e-05
4949598 | 2015-06-09 09:15 | 2015-06-09 15:42 | 387 | 26 | 10062 | 387 | 384 | 0.030425 | 9984 | 0.030189 | 7.8618e-05 | NAPA ID:08587 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 11kV pole I1739 | To replace pole # I13474, replace 11kV cross arms and replace TC3576 in preparation for conductor upgrade. Works location: Starkey Rd. WO 30006975 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-09 | b | 0.015095 | 3.9309e-05 | 2016 | 2015-06-09 | B | 26 | 0.030189 | 7.8618e-05
4949621 | 2015-06-09 08:45 | 2015-06-09 15:05 | 379.8333 | 177 | 67083.5 | 379.0028 | 376.0028 | 0.20284 | 66552.5 | 0.20124 | 0.00053521 | NAPA ID:08330 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 432 | Replace various network poles in work area.Works location: Record St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-09 | b | 0.10062 | 0.0002676 | 2016 | 2015-06-09 | B | 177 | 0.20124 | 0.00053521
4950055 | 2015-06-16 08:46 | 2015-06-16 16:10 | 444.0167 | 49 | 21756.8167 | 444.0167 | 441.0167 | 0.065787 | 21609.8167 | 0.065343 | 0.00014816 | NAPA ID:08346 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8224 | Replace various network poles in work area. reconductor between abs 432 and line break at pole 749533. at completion close line break live line at pole 749533. Works location: Barriball St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-16 | b | 0.032671 | 7.4082e-05 | 2016 | 2015-06-16 | B | 49 | 0.065343 | 0.00014816
4950829 | 2015-06-10 09:30 | 2015-06-10 13:41 | 250.5 | 3 | 751.5 | 250.5 | 247.5 | 0.0022724 | 742.5 | 0.0022451 | 9.0713e-06 | NAPA ID:08698 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV SC2-104 | CUT TREES. Works location: Works Rd Apata. PPPD 37073 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-06-10 | b | 0.0011226 | 4.536e-06 | 2016 | 2015-06-10 | B | 3 | 0.0022451 | 9.0713e-06
4950830 | 2015-06-11 08:50 | 2015-06-11 14:22 | 332 | 61 | 20252 | 332 | 329 | 0.061237 | 20069 | 0.060684 | 0.00018445 | NAPA ID:08344 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 749565 | Cut jumpers on pole 749565 live line and Replace various network poles in work area and fuses 8359. Works location: Richmond St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-11 | b | 0.030342 | 9.2225e-05 | 2016 | 2015-06-11 | B | 61 | 0.060684 | 0.00018445
4950850 | 2015-06-18 08:59 | 2015-06-18 15:50 | 410.9167 | 98 | 40269.8333 | 410.9167 | 407.9167 | 0.12177 | 39975.8333 | 0.12088 | 0.00029633 | NAPA ID:08378 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8391 | Replace various network poles in work area. new tx 1372 and poles. Works location: Sackville St WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-18 | b | 0.060439 | 0.00014816 | 2016 | 2015-06-18 | B | 98 | 0.12088 | 0.00029633
4952165 | 2015-06-10 09:01 | 2015-06-10 14:23 | 321.8 | 4 | 1287.2 | 321.8 | 318.8 | 0.0038922 | 1275.2 | 0.0038559 | 1.2095e-05 | NAPA ID:08337 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-014 | REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-10 | b | 0.001928 | 6.048e-06 | 2016 | 2015-06-10 | B | 4 | 0.0038559 | 1.2095e-05
4952172 | 2015-06-11 09:01 | 2015-06-11 14:07 | 306.0167 | 46 | 14076.7667 | 306.0167 | 303.0167 | 0.042565 | 13938.7667 | 0.042147 | 0.00013909 | NAPA ID:08340 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD3-014 | REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-11 | b | 0.021074 | 6.9546e-05 | 2016 | 2015-06-11 | B | 46 | 0.042147 | 0.00013909
4952339 | 2015-05-21 03:36 | 2015-05-21 13:06 | 570 | 10 | 5700 | 570 | 567 | 0.017235 | 5670 | 0.017145 | 3.0238e-05 | Restore Supply on Device TF4-049 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223814 | at 03:36, Atuaroa Sub, CB 2 No. 3 Rd Feeder, Tripped, A Ph O/C, E/F, Auto Reclosed. Te Puke Sub, CB 1 Roads Feeder, Recloser 9146 Tripped, E/F, L/O. ATU 2 was partialling backfeeding TPV 1 at the time due to Transpower work at TMI GXP. Faultman dispatched | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-21 | c | 0.017145 | 3.0238e-05 | 2016 | 2015-05-21 | C | 10 | 0.017145 | 3.0238e-05
4954487 | 2015-05-21 07:32 | 2015-05-21 11:02 | 210.75 | 256 | 20883.2 | 81.575 | 78.575 | 0.063146 | 20115.2 | 0.060824 | 0.00077408 | Restore Supply on Device T2/19 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P03840 | Car vs Pole P03840. Work Area Isolated at ABS H127 & H129 and backfeed installed via Recloser 10041. Fm advised whole 11KV pole will need to be replaced including x-arms etc - crew request put through for him. NDR #30770 Replaced Pole P03840. 11m Pole w | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.060824 | 0.00077408 | 2016 | 2015-05-21 | C | 256 | 0.060824 | 0.00077408
4954852 | 2015-05-21 08:51 | 2015-05-21 10:31 | 100.1333 | 3 | 300.4 | 100.1333 | 97.1333 | 0.00090834 | 291.4 | 0.00088112 | 9.0713e-06 | Restore Supply on Device T7155 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TA998 | 2 HV Fuses tripped at TA998. (Bird Strike). Relivened OK, 8A rating. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.00088112 | 9.071e-06 | 2016 | 2015-05-21 | C | 3 | 0.00088112 | 9.0713e-06
4955003 | 2015-06-18 09:00 | 2015-06-18 15:52 | 411.5333 | 10 | 4115.3333 | 411.5333 | 408.5333 | 0.012444 | 4085.3333 | 0.012353 | 3.0238e-05 | NAPA ID:07489 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 999 | Project number IR6978 Rangikura Reconstruction Replace poles & cro9ss arms Main South Road beyond HT Fuses 999 poles 771571 to 771577. Works location: Main South Rd Waverley. IR 6978. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-18 | b | 0.0061765 | 1.5119e-05 | 2016 | 2015-06-18 | B | 10 | 0.012353 | 3.0238e-05
4955113 | 2015-06-17 09:18 | 2015-06-17 15:17 | 359.0667 | 26 | 9335.7333 | 359.0667 | 356.0667 | 0.028229 | 9257.7333 | 0.027993 | 7.8618e-05 | NAPA ID:08612 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP615 | To replace 11kV poles arms and hardware in preparation for 11kV conductor upgrade. Works location: Starkey Rd. WO 30006975 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-17 | b | 0.013997 | 3.9309e-05 | 2016 | 2015-06-17 | B | 26 | 0.027993 | 7.8618e-05
4955319 | 2015-05-21 09:51 | 2015-05-21 12:06 | 135 | 8 | 1079.3833 | 134.9229 | 131.9229 | 0.0032638 | 1055.3833 | 0.0031912 | 2.419e-05 | Restore Supply on Device 4826W | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 4147 | Replaced 2x 30Amp Links & 1x Holder | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-21 | c | 0.0031912 | 2.419e-05 | 2016 | 2015-05-21 | C | 8 | 0.0031912 | 2.419e-05
4961659 | 2015-05-21 10:23 | 2015-05-21 12:38 | 134.6 | 136 | 11039.05 | 81.1695 | 78.1695 | 0.033379 | 10631.05 | 0.032146 | 0.00041123 | Restore Supply on Device I51 | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB I51 | Initial Auto-recloses on CB I51 then tripped on E/F. Feeder patrolled / sectionalised but all restored. Many Magpies seen along Rimutuateka Rd, Suspect Bird strike. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.032146 | 0.00041123 | 2016 | 2015-05-21 | C | 136 | 0.032146 | 0.00041123
4973635 | 2015-06-11 10:12 | 2015-06-11 15:20 | 308.05 | 67 | 20639.35 | 308.05 | 305.05 | 0.062408 | 20438.35 | 0.061801 | 0.00020259 | NAPA ID:09173 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE7-025 | Replace pole, crossarms and conductor. Install ABS TEMP67. Works location: Old Coach Rd Paengaroa WO 30002518 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-11 | b | 0.0309 | 0.0001013 | 2016 | 2015-06-11 | B | 67 | 0.061801 | 0.00020259
4981291 | 2015-05-21 14:03 | 2015-05-21 16:46 | 163 | 9 | 1467 | 163 | 160 | 0.0044359 | 1440 | 0.0043542 | 2.7214e-05 | Restore Supply on Device 7149 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7149 | Replaced 1x 8Amp Fuse Link | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.0043542 | 2.7214e-05 | 2016 | 2015-05-21 | C | 9 | 0.0043542 | 2.7214e-05
4981414 | 2015-05-21 17:18 | 2015-05-21 23:07 | 349.2167 | 69 | 11698.9667 | 169.5502 | 166.5502 | 0.035375 | 11491.9667 | 0.034749 | 0.00020864 | Restore Supply on Device C223 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8181 | Sectioniser C223 found open. Patrolled Line found Fuses 8181 1 Fuse open & A bit of binder hanging on Line. Removed Binder Reloaded Fuse | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.034749 | 0.00020864 | 2016 | 2015-05-21 | C | 69 | 0.034749 | 0.00020864
4981658 | 2015-05-21 21:27 | 2015-05-21 22:51 | 83.7333 | 1 | 83.7333 | 83.7333 | 80.7333 | 0.00025319 | 80.7333 | 0.00024412 | 3.0238e-06 | Restore Supply on Device TC4-042 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | 202478 | ADVISED GLORIA AT HUB. Possibly salt build up on insulators. No fault found. F/M waited on site to check. | F3 | BEACH RD MATUA | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2015-05-21 | c | 0.00024412 | 3.024e-06 | 2016 | 2015-05-21 | C | 1 | 0.00024412 | 3.0238e-06
4981723 | 2015-05-22 04:47 | 2015-05-22 06:36 | 108.6333 | 11 | 1194.9667 | 108.6333 | 105.6333 | 0.0036133 | 1161.9667 | 0.0035135 | 3.3261e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7642 | Tree On Lines on Fire. Fuses 7642 opened for safety. | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0.0035135 | 3.3261e-05 | 2016 | 2015-05-22 | C | 11 | 0.0035135 | 3.3261e-05
4991924 | 2015-05-22 05:02 | 2015-05-22 09:12 | 250.6667 | 116 | 22815.7333 | 196.6874 | 193.6874 | 0.068989 | 22467.7333 | 0.067937 | 0.00035076 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 820625 | RS C409/2 Trip, E/F. Sectionalised & Patrolled. Found Broken Insulator & Line down at Pole 820625 Materials used: 2x Joints, 2x Lineguards, 2x binders, 1x Insulator. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0.067937 | 0.00035076 | 2016 | 2015-05-22 | C | 116 | 0.067937 | 0.00035076
5003395 | 2015-05-21 21:59 | 2015-05-22 10:59 | 779.35 | 17 | 1380.2 | 81.1882 | 78.1882 | 0.0041734 | 1329.2 | 0.0040192 | 5.1404e-05 | Restore Supply on Device T9/270 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | - | Phil Barnes is going to attend Taken back to assigned, Phil onsite, 2r 4981671 (90 Puketawa) which is related to this. To be repaired tomorrow. Replaced broken jumper at Pole P04291. Materials used: 4x Al Line Taps & 1 metre of ferret conductor | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-21 | c | 0.0040192 | 5.1404e-05 | 2016 | 2015-05-21 | C | 17 | 0.0040192 | 5.1404e-05
5003419 | 2015-05-22 08:32 | 2015-05-22 10:24 | 112.7833 | 1 | 112.7833 | 112.7833 | 109.7833 | 0.00034103 | 109.7833 | 0.00033196 | 3.0238e-06 | Restore Supply on Device 2098N | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 8072 | 2 HT Fuses found tripped at 8072. Suspect bird strike. Reloaded / Relivened OK. (Fuse Rating | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0.00033196 | 3.024e-06 | 2016 | 2015-05-22 | C | 1 | 0.00033196 | 3.0238e-06
5003428 | 2015-06-10 09:21 | 2015-06-10 12:18 | 177.4167 | 34 | 6032.1667 | 177.4167 | 174.4167 | 0.01824 | 5930.1667 | 0.017931 | 0.00010281 | NAPA ID:08805 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC2565 | Replace HV x-ams & straighten poles. Works location: Matuku Rd Tahuna. WO 30002272 | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-06-10 | b | 0.0089657 | 5.1404e-05 | 2016 | 2015-06-10 | B | 34 | 0.017931 | 0.00010281
5003445 | 2015-05-22 09:11 | 2015-05-22 11:44 | 153 | 655 | 32209.5833 | 49.1749 | 46.1749 | 0.097394 | 30244.5833 | 0.091452 | 0.0019806 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1 Te Puke | Trip. No Flags. Backfeed put in via Sectionaliser 9835 up to Recloser 9146 immediatly following tripping. Rest of feeder sectionalised but no fault found. Many reports from the public that when fault occurred that HV lines were seen swinging violently. | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-22 | c | 0.091452 | 0.0019806 | 2016 | 2015-05-22 | C | 655 | 0.091452 | 0.0019806
5005306 | 2015-05-22 10:49 | 2015-05-22 13:11 | 142.15 | 1 | 142.15 | 142.15 | 139.15 | 0.00042983 | 139.15 | 0.00042076 | 3.0238e-06 | Restore Supply on Device TP2477 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1 | Full power restored - Part of feeder fault | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-22 | c | 0.00042076 | 3.024e-06 | 2016 | 2015-05-22 | C | 1 | 0.00042076 | 3.0238e-06
5005318 | 2015-05-22 08:55 | 2015-05-22 11:15 | 139.5333 | 16 | 2232.5333 | 139.5333 | 136.5333 | 0.0067506 | 2184.5333 | 0.0066055 | 4.838e-05 | Restore Supply on Device 7856 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7856 | Replaced 2x 10Amp Fuse Links | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0.0066055 | 4.838e-05 | 2016 | 2015-05-22 | C | 16 | 0.0066055 | 4.838e-05
5005346 | 2015-06-09 09:01 | 2015-06-09 14:11 | 309.9833 | 1 | 309.9833 | 309.9833 | 306.9833 | 0.00093732 | 306.9833 | 0.00092824 | 3.0238e-06 | NAPA ID:09693 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-148 | REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. Works location: Crawford Rd WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-09 | b | 0.00046412 | 1.512e-06 | 2016 | 2015-06-09 | B | 1 | 0.00092824 | 3.0238e-06
5005369 | 2015-05-22 14:00 | 2015-05-22 18:10 | 250 | 80 | 20000 | 250 | 247 | 0.060475 | 19760 | 0.05975 | 0.0002419 | Restore Supply on Device 2669T | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 708518 | Power pole in a paddock has fallen over - customer is advising the power is still on. Pole is about 100m from this driveway towards Tahora on eastern side of the road. Tree contractors (Asplundh and Downer) were out there yesterday and knew about the pole | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0.05975 | 0.0002419 | 2016 | 2015-05-22 | C | 80 | 0.05975 | 0.0002419
5005416 | 2015-05-22 12:56 | 2015-05-22 13:01 | 5.4333 | 253 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00076501 | Restore Supply on Device C927 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | C927 | Tuhitarata CB C927 Kumenga - Auto reclosed E/F O/C A Phase. Patrol carried out - went down every spur line and couldn't find anything. Lots of geese around at the time. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-05-22 | c | 0 | 0.00076501 | 2016 | 2015-05-22 | C | 253 | 0 | 0.00076501
5006179 | 2015-06-03 09:30 | 2015-06-03 14:13 | 283 | 42 | 11886 | 283 | 280 | 0.03594 | 11760 | 0.035559 | 0.000127 | NAPA ID:08327 TP_TAURANGA 33 GXP > BETHLEHEM SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 213255 | LLWP GAP FOR SHUT AT POLE 213255. REPLACE POLE AND ARMS AND RECON FEEDER WIRE TO IODINE . Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-03 | b | 0.01778 | 6.3499e-05 | 2016 | 2015-06-03 | B | 42 | 0.035559 | 0.000127
5006223 | 2015-05-26 09:00 | 2015-05-26 15:39 | 399 | 11 | 4389 | 399 | 396 | 0.013271 | 4356 | 0.013172 | 3.3261e-05 | NAPA ID:09695 TP_PIAKO GXP > PIAKO SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC2529 | Change 11Kv arm on Both CB 8 and CB 5 feeder from Piako. Works location: Morrinsville-Walton Rd. IR6896 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-05-26 | b | 0.0065858 | 1.6631e-05 | 2016 | 2015-05-26 | B | 11 | 0.013172 | 3.3261e-05
5007717 | 2015-05-23 07:55 | 2015-05-23 11:50 | 234.7833 | 18 | 4226.1 | 234.7833 | 231.7833 | 0.012779 | 4172.1 | 0.012615 | 5.4428e-05 | Restore Supply on Device X717 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771558 | Faultman found line down at pole 771558, line was isolated at Fuses 663 to make the repairs. 1 meter 16mm copper conductor used. 2 x 16mm sleeves. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-23 | c | 0.012615 | 5.4428e-05 | 2016 | 2015-05-23 | C | 18 | 0.012615 | 5.4428e-05
5007724 | 2015-05-24 12:00 | 2015-05-24 15:01 | 180.9833 | 67 | 6694.9 | 99.9239 | 96.9239 | 0.020244 | 6493.9 | 0.019636 | 0.00020259 | Referral: Restore Supply on Device 538 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | X538 | follow up to return to site to repair UG cable fault. 24/5. Blair advised that he is not on stand down and he would do this job today, Darren did not advise dispatch of this when the original job was closed. 24/5 10.08am - email sent for update. Transform | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-24 | c | 0.019636 | 0.00020259 | 2016 | 2015-05-24 | C | 67 | 0.019636 | 0.00020259
5008985 | 2015-05-23 11:36 | 2015-05-23 16:19 | 283.2833 | 158 | 31768.7667 | 201.0681 | 198.0681 | 0.096061 | 31294.7667 | 0.094628 | 0.00047775 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 266965 | Replace Pole. 1 X LV Crossarm 1 X HV Crossarm and insulators for both. Stays and bolts. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-23 | c | 0.094628 | 0.00047775 | 2016 | 2015-05-23 | C | 158 | 0.094628 | 0.00047775
5009498 | 2015-05-23 16:53 | 2015-05-23 16:56 | 2.7 | 1583 | 2.05 | 0.001295 | -2.9987 | 6.1987e-06 | 0 | 0 | 0.0047866 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | A/R, no flags | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-05-23 | c | 0 | 0.0047866 | 2016 | 2015-05-23 | C | 1583 | 0 | 0.0047866
5013442 | 2015-05-24 06:08 | 2015-05-24 07:58 | 110.3667 | 29 | 3200.6333 | 110.3667 | 107.3667 | 0.0096779 | 3113.6333 | 0.0094149 | 8.7689e-05 | Restore Supply on Device P1290 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 6289 | Faultman found blown fuses at Fuses 6289, line patrolled suspect duck strike as customer reported lots off ducks flying around then power went off. 2 x 15 amp HV fuses replaced. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-05-24 | c | 0.0094149 | 8.7689e-05 | 2016 | 2015-05-24 | C | 29 | 0.0094149 | 8.7689e-05
5020971 | 2015-05-24 09:59 | 2015-05-24 11:40 | 101.4833 | 1 | 101.4833 | 101.4833 | 98.4833 | 0.00030686 | 98.4833 | 0.00029779 | 3.0238e-06 | Restore Supply on Device G141 | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | nn | scan power are onsite doing 11kv and LV jointing, customers not advised of planned outage. this will last until 2pm .planned outage ref 8652 | F2 | MAIN ST 23 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-05-24 | c | 0.00029779 | 3.024e-06 | 2016 | 2015-05-24 | C | 1 | 0.00029779 | 3.0238e-06
5021948 | 2015-05-24 13:57 | 2015-05-24 15:15 | 78 | 8 | 624 | 78 | 75 | 0.0018868 | 600 | 0.0018143 | 2.419e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2/67 Beach Rd | replaced 2x 8a HV fuse links at fuses 1198, OH due to unknown. nothing else repaired or replaced, adjacent assets up to powerco standard.was advised to close with dispatch after talking to control | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-05-24 | c | 0.0018143 | 2.419e-05 | 2016 | 2015-05-24 | C | 8 | 0.0018143 | 2.419e-05
5023202 | 2015-05-24 18:42 | 2015-05-24 21:00 | 138.2 | 5 | 691 | 138.2 | 135.2 | 0.0020894 | 676 | 0.0020441 | 1.5119e-05 | Restore Supply on Device T597 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7725 | HV Fuse Links blown. 2x 10Amp HV Fuse Links. Attended by Ben Taylor. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-05-24 | c | 0.0020441 | 1.5119e-05 | 2016 | 2015-05-24 | C | 5 | 0.0020441 | 1.5119e-05
5023261 | 2015-05-24 21:36 | 2015-05-25 02:04 | 268.3333 | 1210 | 105936.0333 | 87.5504 | 84.5504 | 0.32033 | 102306.0333 | 0.30935 | 0.0036588 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | W14117 | Car V Pole Pole W14117 Replaced X-arm 3 X Pin Insulators Binders. | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-05-24 | c | 0.30935 | 0.0036588 | 2016 | 2015-05-24 | C | 1210 | 0.30935 | 0.0036588
5025866 | 2015-05-25 00:41 | 2015-05-25 01:35 | 53.45 | 211 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00063801 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7 | A/R, O/C, Not patrolled, No fault found. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0 | 0.00063801 | 2016 | 2015-05-25 | C | 211 | 0 | 0.00063801
5026981 | 2015-05-25 01:00 | 2015-05-25 04:54 | 234.5 | 300 | 7892.6667 | 26.3089 | 23.3089 | 0.023866 | 6992.6667 | 0.021144 | 0.00090713 | Restore Supply on Device 6561-2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 379207 | RS 6561 A/R, O/C B & C Phase. Kept Reclosing so set to one shot & faultman sent out to patrol. Faultman noticed fire so isolated at ABS CA480 & Fire Brigade called. Temp Line break put in at Pole 379207 to isolate clashing lines between there & ABS CA412. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.021144 | 0.00090713 | 2016 | 2015-05-25 | C | 300 | 0.021144 | 0.00090713
5028737 | 2015-05-25 01:42 | 2015-05-25 05:58 | 256.1167 | 217 | 18580.0333 | 85.6223 | 82.6223 | 0.056182 | 17929.0333 | 0.054213 | 0.00065616 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | CB4 | CB 4 A/R and L/O. Possum on line removed by hot stick. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.054213 | 0.00065616 | 2016 | 2015-05-25 | C | 217 | 0.054213 | 0.00065616
5029377 | 2015-05-25 00:10 | 2015-05-25 11:21 | 670.7833 | 37 | 24818.9833 | 670.7833 | 667.7833 | 0.075047 | 24707.9833 | 0.074711 | 0.00011188 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789899 | Tree has come down over HV Lines across large gully causing SS2592 to trip. Pole 789899. Repair required to be started asap. See OMS 5025224 for outage information. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.074711 | 0.00011188 | 2016 | 2015-05-25 | C | 37 | 0.074711 | 0.00011188
5030945 | 2015-05-25 06:16 | 2015-05-25 08:34 | 137.9167 | 93 | 8455.9833 | 90.9246 | 87.9246 | 0.025569 | 8176.9833 | 0.024725 | 0.00028121 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844565 | Lines down, suspect high winds. | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.024725 | 0.00028121 | 2016 | 2015-05-25 | C | 93 | 0.024725 | 0.00028121
5031413 | 2015-05-25 06:36 | 2015-05-25 15:40 | 544.25 | 365 | 33557.6 | 91.9386 | 88.9386 | 0.10147 | 32462.6 | 0.098159 | 0.0011037 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - TORNADO | 782020 | 9.05am Shan called to request a CR. Broken 11kV pole from Kai Iwi sub. Replaced pole 782020 with crossarm and 90m 16mm copper at pole 782017 5m squirrel conductor and 3 sleeves. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.098159 | 0.0011037 | 2016 | 2015-05-25 | C | 365 | 0.098159 | 0.0011037
5032108 | 2015-05-25 06:55 | 2015-05-25 12:02 | 306.8167 | 1 | 306.8167 | 306.8167 | 303.8167 | 0.00092774 | 303.8167 | 0.00091867 | 3.0238e-06 | Restore Supply on Device T5/66 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 07812 | CHECK FOR SAFETY- LINES DOWN ON THE PROPERTY FROM THE TX INTO THE SITE TREE ON THE LINES. 574 Mangamako Road - Kimbolton. 6:58am Called through to hub and taken into control. ndr N300069 tree on network line blew 3 x 3mp hv fuses and 10 meter on conductor | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.00091867 | 3.024e-06 | 2016 | 2015-05-25 | C | 1 | 0.00091867 | 3.0238e-06
5032157 | 2015-05-25 07:30 | 2015-05-25 11:25 | 235 | 644 | 56476 | 87.6957 | 84.6957 | 0.17077 | 54544 | 0.16493 | 0.0019473 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745767 | Backfeed part of feeder from ABS 140 to recloser 499. Reported lined down beyound ABS 315. Isolated between ABS 315 & ABS 331. Repaired lines down caused by tree and relivened. NDR N100028. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.16493 | 0.0019473 | 2016 | 2015-05-25 | C | 644 | 0.16493 | 0.0019473
5032940 | 2015-05-25 08:33 | 2015-05-25 09:19 | 46 | 11 | 506 | 46 | 43 | 0.00153 | 473 | 0.0014302 | 3.3261e-05 | Restore Supply on Device 5502 | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760541 | Isolated 11kV to replace 33kV insulator on pole760541. Isolated between ABS 5496 & ABS 5502. Parent job OMS 5029374 | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.0014302 | 3.3261e-05 | 2016 | 2015-05-25 | C | 11 | 0.0014302 | 3.3261e-05
5057066 | 2015-06-11 09:06 | 2015-06-11 14:00 | 293.7667 | 26 | 7637.9333 | 293.7667 | 290.7667 | 0.023095 | 7559.9333 | 0.022859 | 7.8618e-05 | NAPA ID:08593 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9561 | To install new 11kV conductor between 9561 and Pole # I1506. Works location: Starkey Rd WO 30006975 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-11 | b | 0.01143 | 3.9309e-05 | 2016 | 2015-06-11 | B | 26 | 0.022859 | 7.8618e-05
5057115 | 2015-05-25 11:16 | 2015-05-25 14:04 | 168 | 510 | 42039 | 82.4294 | 79.4294 | 0.12712 | 40509 | 0.12249 | 0.0015421 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | pole 216538 | CURRENTLY WITH OSI AS IT APPEARS TO BE DUPLICATING ICP'S OVER MULTIPLE TIMES. DO NOT TOUCH UNTIL RETURNED TO RELEASE PLANNING BY ANDREW CURTIS. Recloser 9220/2 has tripped to L/O - E/F flag Line sectionalised & patrolled. LV line had contacted HV above | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-25 | c | 0.12249 | 0.0015421 | 2016 | 2015-05-25 | C | 510 | 0.12249 | 0.0015421
5057638 | 2015-07-04 09:11 | 2015-07-04 15:03 | 352.1833 | 195 | 68675.75 | 352.1833 | 349.1833 | 0.20766 | 68090.75 | 0.20589 | 0.00058963 | NAPA ID:09216 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS Q14 | To change red tagged poles. Works location: Cambridge St. WO 10161258 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-04 | b | 0.10295 | 0.00029482 | 2016 | 2015-07-04 | B | 195 | 0.20589 | 0.00058963
5058775 | 2015-05-25 11:23 | 2015-05-25 13:16 | 113.3 | 1 | 113.3 | 113.3 | 110.3 | 0.00034259 | 110.3 | 0.00033352 | 3.0238e-06 | Restore Supply on Device TC5881 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | pole k12889 | The is a broken x arm not a pole down as advised by lee at mercury fm will amber defect 93307 the xarm the pole is okay and also tree trimming is required pole k12889 this is lv road crossing pole unsure who owns the trees nothing repaired or replaced tod | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-05-25 | c | 0.00033352 | 3.024e-06 | 2016 | 2015-05-25 | C | 1 | 0.00033352 | 3.0238e-06
5058804 | 2015-05-25 11:15 | 2015-05-25 12:17 | 62 | 15 | 930 | 62 | 59 | 0.0028121 | 885 | 0.002676 | 4.5356e-05 | Restore Supply on Device PU303 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 846715 | Isolated at fuses PU303. Replaced 1 insulator and relivened. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.002676 | 4.5356e-05 | 2016 | 2015-05-25 | C | 15 | 0.002676 | 4.5356e-05
5059320 | 2015-05-25 11:57 | 2015-05-25 16:14 | 256.8167 | 2 | 268.95 | 134.475 | 131.475 | 0.00081324 | 262.95 | 0.0007951 | 6.0475e-06 | Restore Supply on Device T58 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7875, 7873 | Replaced 2X hv fuses | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.0007951 | 6.048e-06 | 2016 | 2015-05-25 | C | 2 | 0.0007951 | 6.0475e-06
5064896 | 2015-05-25 12:39 | 2015-05-25 14:54 | 134.8833 | 1 | 134.8833 | 134.8833 | 131.8833 | 0.00040785 | 131.8833 | 0.00039878 | 3.0238e-06 | Restore Supply on Device X554 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 781674 | 2x 6amp HV fuses cause weather - worked through control. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-05-25 | c | 0.00039878 | 3.024e-06 | 2016 | 2015-05-25 | C | 1 | 0.00039878 | 3.0238e-06
5064917 | 2015-05-18 14:32 | 2015-05-18 14:36 | 4 | 2 | 8 | 4 | 1 | 2.419e-05 | 2 | 6.0475e-06 | 6.0475e-06 | Restore Supply on Device X1435 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1435 | Off Load transformer to tap up due to customer complaint. Complaint Number 6301 (refer to Greg Turner). | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-05-18 | c | 6.048e-06 | 6.048e-06 | 2016 | 2015-05-18 | C | 2 | 6.0475e-06 | 6.0475e-06
5065036 | 2015-05-19 18:27 | 2015-05-19 18:42 | 15 | 5 | 75 | 15 | 12 | 0.00022678 | 60 | 0.00018143 | 1.5119e-05 | Restore Supply on Device S4670 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4601 | Tap up transformer T4601 due to high voltage. | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-05-19 | c | 0.00018143 | 1.5119e-05 | 2016 | 2015-05-19 | C | 5 | 0.00018143 | 1.5119e-05
5065634 | 2015-05-25 10:03 | 2015-05-25 18:53 | 529.6667 | 143 | 75640.1333 | 528.952 | 525.952 | 0.22872 | 75211.1333 | 0.22742 | 0.0004324 | Restore Supply on Device 1297 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 846290 | Repaired lines @ pole 846290 brought down by trees. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.22742 | 0.0004324 | 2016 | 2015-05-25 | C | 143 | 0.22742 | 0.0004324
5065686 | 2015-05-25 14:50 | 2015-05-25 16:58 | 127.7333 | 7 | 894.1333 | 127.7333 | 124.7333 | 0.0027036 | 873.1333 | 0.0026401 | 2.1166e-05 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 83385 STATE HIGHWAY 2 | URGENT PLS ATTEND ASAP - MAN STUCK UP ON CHERRY PICKER CANT GET DOWN - LINES SNAPPED AND ON THE GROUND 2.15pm advised Tans at svs hub 2:43am 1 r request for assistance to help rehang HV lines. 10.09pm - smc advise Andrew also left site but Control only s | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.0026401 | 2.1166e-05 | 2016 | 2015-05-25 | C | 7 | 0.0026401 | 2.1166e-05
5070780 | 2015-06-17 09:15 | 2015-06-17 17:56 | 521 | 57 | 29697 | 521 | 518 | 0.089797 | 29526 | 0.08928 | 0.00017235 | NAPA ID:09305 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 825593 | Replacement of Magnifix units C291, C292, C293 with ABB Safelink CFC unit. Replacement of G/L Transformer T809. Works location: Rewa Place Masterton. WO 10160113 | F3/F4 | GORDON ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-06-17 | b | 0.04464 | 8.6177e-05 | 2016 | 2015-06-17 | B | 57 | 0.08928 | 0.00017235
5070935 | 2015-05-25 17:18 | 2015-05-25 20:46 | 208.4833 | 1 | 208.4833 | 208.4833 | 205.4833 | 0.0006304 | 205.4833 | 0.00062133 | 3.0238e-06 | Restore Supply on Device T9/302 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | T9/302 | FM not sure why he was called out again as he replaced a 6 amp pole fuse previously. cause: unsure. 8.05pm - insufficient permissions to verify transformer (eastern dispatch desk), sent e-mail to Wayne Hosking. 8.43pm - tried to verify transformer at gas | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.00062133 | 3.024e-06 | 2016 | 2015-05-25 | C | 1 | 0.00062133 | 3.0238e-06
5071111 | 2015-05-26 14:35 | 2015-05-26 15:40 | 65 | 1 | 65 | 65 | 62 | 0.00019654 | 62 | 0.00018747 | 3.0238e-06 | Restore Supply on Device X1535 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1535 | broken tx x1535. pole # 788236. control advised. 2 x house and woolshed have part power. FM advise tx will not be replace tonight as still snowy. Transformer required Changing - Off at 14:35, on 15:40. relivened OK. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-05-26 | c | 0.00018747 | 3.024e-06 | 2016 | 2015-05-26 | C | 1 | 0.00018747 | 3.0238e-06
5071143 | 2015-05-25 18:24 | 2015-05-26 16:00 | 1296 | 2 | 2592 | 1296 | 1293 | 0.0078376 | 2586 | 0.0078194 | 6.0475e-06 | Restore Supply on Device W2230 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725785 | left fuse WH212 open for now. 2 of the isolation fuses to line keeps blowing. Line is 5km long and going cross country and through a forestry block. Need to check line during day light. FM worked through control. Found damage pole 725785. Leaving power of | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.0078194 | 6.048e-06 | 2016 | 2015-05-25 | C | 2 | 0.0078194 | 6.0475e-06
5071672 | 2015-06-16 08:45 | 2015-06-16 14:36 | 351 | 43 | 4597.7667 | 106.9248 | 103.9248 | 0.013903 | 4468.7667 | 0.013512 | 0.00013002 | NAPA ID:08645 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 218187 | 1 / MAKE 11KV BREAK AT POLE 218187 SEE NOTES FOR DETAILS. 2/ AP TO RECON 3 SPANS OF FEEDER WIRE TO IODINE AND RE POLE. 3/ RE MAKE 11KV BREAK AT POLE 218187 SEE NOTES FOR DETAILS. Works location: Hwy 33 WO IR7777 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-16 | b | 0.0067562 | 6.5011e-05 | 2016 | 2015-06-16 | B | 43 | 0.013512 | 0.00013002
5073141 | 2015-06-17 09:03 | 2015-06-17 14:48 | 344.9833 | 34 | 11622.3 | 341.8324 | 338.8324 | 0.035143 | 11520.3 | 0.034835 | 0.00010281 | NAPA ID:08341 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 200364 | MAKE GAP AT POLE 200364. REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. RE MAKE GAP AT POLE 200364. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-17 | b | 0.017417 | 5.1404e-05 | 2016 | 2015-06-17 | B | 34 | 0.034835 | 0.00010281
5083524 | 2015-05-26 08:30 | 2015-05-26 11:35 | 185 | 3 | 555 | 185 | 182 | 0.0016782 | 546 | 0.001651 | 9.0713e-06 | Restore Supply on Device 8471 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756173 | Repaired Lines dowm caused by tree contractor NDR N100029, Isolated at fuses 8471 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-05-26 | c | 0.001651 | 9.071e-06 | 2016 | 2015-05-26 | C | 3 | 0.001651 | 9.0713e-06
5085236 | 2015-05-26 14:10 | 2015-05-26 14:33 | 22.35 | 37 | 826.95 | 22.35 | 19.35 | 0.0025005 | 715.95 | 0.0021649 | 0.00011188 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22896 | Outage required between ABS I36 and I39 to replace a broken Insulator. (Backfeed at ABS S26 - Alfredton, Rongomai feeder). Relivened OK. (Damaged Insulator seen by DOWNER Contractor when driving in area). | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-05-26 | c | 0.0021649 | 0.00011188 | 2016 | 2015-05-26 | C | 37 | 0.0021649 | 0.00011188
5088360 | 2015-05-26 13:43 | 2015-05-26 15:26 | 103 | 1 | 103 | 103 | 100 | 0.00031145 | 100 | 0.00030238 | 3.0238e-06 | Restore Supply on Device T2/366 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C31 | NOTE: Original OMS job (This one) is incorrect address. (Refer Child attached). Fuses C31 foound tripped ( X 2). Reloaded / relivened OK. Suspect Bird strike. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-05-26 | c | 0.00030238 | 3.024e-06 | 2016 | 2015-05-26 | C | 1 | 0.00030238 | 3.0238e-06
5090370 | 2015-05-26 14:05 | 2015-05-26 15:40 | 94.6333 | 53 | 5015.5667 | 94.6333 | 91.6333 | 0.015166 | 4856.5667 | 0.014685 | 0.00016026 | Restore Supply on Device 5814 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 85814 | 2:08pm advised hub of 999. Found 2 HT fuses blown Isolated at fuses 5814 and cut away lightening arrestors, Relivened | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-05-26 | c | 0.014685 | 0.00016026 | 2016 | 2015-05-26 | C | 53 | 0.014685 | 0.00016026
5090820 | 2015-06-19 09:30 | 2015-06-19 10:45 | 75 | 3 | 225 | 75 | 72 | 0.00068035 | 216 | 0.00065313 | 9.0713e-06 | NAPA ID:09123 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1630 | To install a 3 phase 400V disconnection unit & re terminate sun damaged cables. Works location: Old Te Aroha Rd, Matamata. WO 10162450 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-19 | b | 0.00032657 | 4.536e-06 | 2016 | 2015-06-19 | B | 3 | 0.00065313 | 9.0713e-06
5090831 | 2015-05-25 12:14 | 2015-05-25 15:23 | 189 | 489 | 39279 | 80.3252 | 77.3252 | 0.11877 | 37812 | 0.11433 | 0.0014786 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 6 L/O on E/F. Sectionalised & found lines down between ABS 252 & ABS 407. Backfeed rest of area. Repaired lines & relivened. Bird strike. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-05-25 | c | 0.11433 | 0.0014786 | 2016 | 2015-05-25 | C | 489 | 0.11433 | 0.0014786
5091820 | 2015-06-29 09:56 | 2015-06-29 14:40 | 284.3667 | 10 | 2843.6667 | 284.3667 | 281.3667 | 0.0085986 | 2813.6667 | 0.0085079 | 3.0238e-05 | NAPA ID:09245 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5380 | to change existing trany 2716t to new 11m pole plus new 15kva trany and upgrade earths. Works location: Makara Rd. WO 30001676 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-06-29 | b | 0.0042539 | 1.5119e-05 | 2016 | 2015-06-29 | B | 10 | 0.0085079 | 3.0238e-05
5092627 | 2015-05-27 09:25 | 2015-05-27 12:42 | 196.6833 | 1 | 196.6833 | 196.6833 | 193.6833 | 0.00059472 | 193.6833 | 0.00058565 | 3.0238e-06 | Restore Supply on Device TE5-221 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | TE5-221 | Replaced 2x 3A hv fuses. Due to a possum on the lines. Nothing else repaired or replaced. All surrounding assets up to Powerco standard | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-05-27 | c | 0.00058565 | 3.024e-06 | 2016 | 2015-05-27 | C | 1 | 0.00058565 | 3.0238e-06
5092629 | 2015-05-27 09:23 | 2015-05-27 09:24 | 1 | 722 | 722 | 1 | -2 | 0.0021832 | 0 | 0 | 0.0021832 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB5 | CB 5 Tripped A Ph O/C A/R - Not Patrolled | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-05-27 | c | 0 | 0.0021832 | 2016 | 2015-05-27 | C | 722 | 0 | 0.0021832
5104258 | 2015-05-27 11:14 | 2015-05-27 11:33 | 19.3667 | 310 | 6003.6667 | 19.3667 | 16.3667 | 0.018154 | 5073.6667 | 0.015342 | 0.00093737 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 9736/2 | Tree branch contacted line during planned work. NAPA 9155-01. Safety Manager 472254. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-05-27 | c | 0.015342 | 0.00093737 | 2016 | 2015-05-27 | C | 310 | 0.015342 | 0.00093737
5104610 | 2015-05-27 14:30 | 2015-05-27 16:38 | 128 | 4 | 512 | 128 | 125 | 0.0015482 | 500 | 0.0015119 | 1.2095e-05 | Restore Supply on Device 3317T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3317T | Found fault at transformer 3317T. Isolated at fuses 5751. Replaced 1 set of DDO units & 1 set of polymars. Relivened | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-05-27 | c | 0.0015119 | 1.2095e-05 | 2016 | 2015-05-27 | C | 4 | 0.0015119 | 1.2095e-05
5104676 | 2015-07-08 08:46 | 2015-07-08 15:34 | 408.3333 | 225 | 91875 | 408.3333 | 405.3333 | 0.27781 | 91200 | 0.27577 | 0.00068035 | NAPA ID:08379 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 11kV ABS 432 | Replace various network poles in work area. Works location: Barriball St. CIW 119439 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-07-08 | b | 0.13788 | 0.00034017 | 2016 | 2015-07-08 | B | 225 | 0.27577 | 0.00068035
5104772 | 2015-06-16 08:40 | 2015-06-16 13:27 | 287 | 28 | 8036 | 287 | 284 | 0.024299 | 7952 | 0.024045 | 8.4665e-05 | NAPA ID:09638 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 299 | Replace pole and install 30kVA transformer. Works location: Frankton Rd Waihi. WO 30009544 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-06-16 | b | 0.012022 | 4.2333e-05 | 2016 | 2015-06-16 | B | 28 | 0.024045 | 8.4665e-05
5104777 | 2015-05-27 17:35 | 2015-05-27 18:30 | 55.7 | 78 | 4344.6 | 55.7 | 52.7 | 0.013137 | 4110.6 | 0.012429 | 0.00023585 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 53 TE ORE ORE ROAD Pole 830002 | 2.52pm - advise smc. 33kv Insulator on Pole 830002 found arcing - Isolated 33kv at ABS's S187, S190 & S726, 11kV Isolated at ABS's S73 & 7937 Sw/Gear 7415/3 and CB C821 - Insulator Replaced - Used 1 x 33kV insulator | F3 | TOTARA ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-05-27 | c | 0.012429 | 0.00023585 | 2016 | 2015-05-27 | C | 78 | 0.012429 | 0.00023585
5104811 | 2015-05-29 09:02 | 2015-05-29 15:00 | 358 | 68 | 24344 | 358 | 355 | 0.07361 | 24140 | 0.072994 | 0.00020562 | NAPA ID:09473 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 846481 | L/L Cut live line break at pole 846481. A/P Replace various network poles in work area. L/L Close live line break | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-05-29 | b | 0.036497 | 0.00010281 | 2016 | 2015-05-29 | B | 68 | 0.072994 | 0.00020562
5104867 | 2015-05-27 16:15 | 2015-05-27 16:42 | 27.2833 | 72 | 1964.4 | 27.2833 | 24.2833 | 0.0059399 | 1748.4 | 0.0052867 | 0.00021771 | Restore Supply on Device F2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P17072 | Broken Strain reported by Powerco Staff to Downers - Isolated at ABS's E23 & F2 - Strainer repaired - used 1x M12 bolt | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-05-27 | c | 0.0052867 | 0.00021771 | 2016 | 2015-05-27 | C | 72 | 0.0052867 | 0.00021771
5105085 | 2015-05-27 18:14 | 2015-05-27 18:22 | 8.3833 | 334 | 2800.0333 | 8.3833 | 5.3833 | 0.0084666 | 1798.0333 | 0.0054368 | 0.0010099 | Restore Supply on Device C822 | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | C822 | CB C822 Opened by Faultman during Switching for OMS 5104777 - Once Faultman contacted to Confirm wrong CB operated, CB Closed. Safety Manager 472476. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-05-27 | c | 0.0054368 | 0.0010099 | 2016 | 2015-05-27 | C | 334 | 0.0054368 | 0.0010099
5105435 | 2015-05-27 21:33 | 2015-05-27 21:50 | 17 | 38 | 621.4 | 16.3526 | 13.3526 | 0.001879 | 507.4 | 0.0015343 | 0.0001149 | Restore Supply on Device TC3-008 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC3-071 | Advised Tans that shannon at Trustpower advised that the whole of Matakana Island is out plz check if oms 5105582 53 Opureora road affected fed from different tx No power 2 x fuses replaced at SC3-071 | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-05-27 | c | 0.0015343 | 0.0001149 | 2016 | 2015-05-27 | C | 38 | 0.0015343 | 0.0001149
5105679 | 2015-05-28 06:22 | 2015-05-28 08:37 | 135.1833 | 18 | 2433.3 | 135.1833 | 132.1833 | 0.0073577 | 2379.3 | 0.0071944 | 5.4428e-05 | Restore Supply on Device T9/293 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | v83 | 2 fuses blown unknown cause | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-05-28 | c | 0.0071944 | 5.4428e-05 | 2016 | 2015-05-28 | C | 18 | 0.0071944 | 5.4428e-05
5105684 | 2015-05-28 06:35 | 2015-05-28 09:19 | 164 | 2 | 327.3833 | 163.6917 | 160.6917 | 0.00098993 | 321.3833 | 0.00097179 | 6.0475e-06 | Restore Supply on Device T4007 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7384 | Jo advised he is leaving site and Brad is to attend - as the hub told him to call dispatch duck caused 2 fuses to blow address wrong icp changed in data manager actual fault at fuses 7348 | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-05-28 | c | 0.00097179 | 6.048e-06 | 2016 | 2015-05-28 | C | 2 | 0.00097179 | 6.0475e-06
5105720 | 2015-05-25 07:58 | 2015-05-28 10:00 | 4442.0167 | 676 | 96529.35 | 142.7949 | 139.7949 | 0.29188 | 94501.35 | 0.28575 | 0.0020441 | Restore Supply on Device 2 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-516 | At 07:58, Tauranga Sub, CB 13 Oropi Rd Feeder, Recloser 9517 Tripped, E/F, L/O. Faultmen dispatched and investigation began. Feeder sectionalised. Found 11kV Cable had faulted beyond Fuses SD4-136. Generator was supplied to TD4-516 at 11:35 and supplied t | F3 | OROPI RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-05-25 | c | 0.28575 | 0.0020441 | 2016 | 2015-05-25 | C | 676 | 0.28575 | 0.0020441
5106970 | 2015-05-26 09:15 | 2015-05-26 15:40 | 385 | 200 | 77000 | 385 | 382 | 0.23283 | 76400 | 0.23102 | 0.00060475 | Restore Supply on Device 2605 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2608 |  | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-05-26 | b | 0.11551 | 0.00030238 | 2016 | 2015-05-26 | B | 200 | 0.23102 | 0.00060475
5107221 | 2015-05-28 10:58 | 2015-05-28 11:20 | 22.4667 | 6 | 134.8 | 22.4667 | 19.4667 | 0.0004076 | 116.8 | 0.00035318 | 1.8143e-05 | Restore Supply on Device TC3165 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F1515 | No LT fuses on transformer. Isolated HT side to carry out repairs on LT wire down | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-05-28 | c | 0.00035318 | 1.8143e-05 | 2016 | 2015-05-28 | C | 6 | 0.00035318 | 1.8143e-05
5107918 | 2015-05-28 14:16 | 2015-05-28 14:31 | 15 | 7 | 105 | 15 | 12 | 0.00031749 | 84 | 0.000254 | 2.1166e-05 | Restore Supply on Device T8/207 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | S7 | Possibly part of 5104961 Fuses Found Blown At Fuses S7 and 10178 - Suspected bird strike - used 2x 6amp fuses and 2x3 amp | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-05-28 | c | 0.000254 | 2.1166e-05 | 2016 | 2015-05-28 | C | 7 | 0.000254 | 2.1166e-05
5108855 | 2015-06-25 08:45 | 2015-06-25 14:28 | 343 | 75 | 25725 | 343 | 340 | 0.077786 | 25500 | 0.077106 | 0.00022678 | NAPA ID:08770 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 342 | Replace pole 751052 and 11kv U/G cable and pothead. Upgarde knife links 6116. Works location: Nobs line. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-25 | b | 0.038553 | 0.00011339 | 2016 | 2015-06-25 | B | 75 | 0.077106 | 0.00022678
5109151 | 2015-05-28 18:07 | 2015-05-28 18:25 | 17.8667 | 5 | 89.3333 | 17.8667 | 14.8667 | 0.00027012 | 74.3333 | 0.00022477 | 1.5119e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5643 | At 28/05/15 Kerepehi Sub, CB 5 Mangatarata Feeder. Found a broken Jumper on the LV of Transformer TC5643. Own Isolation & AP. Repairs carried out. All Power restored on completion. James Brier Attended. 1x Quick Lug Replaced. Isolating tx 5643 to fix loos | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-05-28 | c | 0.00022477 | 1.5119e-05 | 2016 | 2015-05-28 | C | 5 | 0.00022477 | 1.5119e-05
5111647 | 2015-05-28 20:25 | 2015-05-28 22:58 | 152.7167 | 1026 | 17509.0833 | 17.0654 | 14.0654 | 0.052943 | 14431.0833 | 0.043636 | 0.0031024 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 776517 | Valley Road, near intersection of King Street, Raetihi. eta required. Event Number F1853276. Fire Comms Wellington 048010812 - Jill. 7.29am - Advise Jill at Fire Comms of 5min ETA. Line isolated @ ABS 652 to replace pole 776517 NDR to follow | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-05-28 | c | 0.043636 | 0.0031024 | 2016 | 2015-05-28 | C | 1026 | 0.043636 | 0.0031024
5117007 | 2015-05-29 07:48 | 2015-05-29 09:52 | 124.3333 | 5 | 621.6667 | 124.3333 | 121.3333 | 0.0018798 | 606.6667 | 0.0018344 | 1.5119e-05 | Restore Supply on Device SE7-004 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | SE7-004 | Shay Deegan Attended. Reloaded-Relivened 2x DDO's at Fuses SE7-004. Unknown Cause, Possibly Bird or Line Clash. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-29 | c | 0.0018344 | 1.5119e-05 | 2016 | 2015-05-29 | C | 5 | 0.0018344 | 1.5119e-05
5117035 | 2015-05-29 08:45 | 2015-05-29 14:44 | 359.2 | 44 | 15804.8 | 359.2 | 356.2 | 0.04779 | 15672.8 | 0.047391 | 0.00013305 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2479 | TRansformer TC2479 needs to be replaced - working through control. Replaced transformer TC2479. Relivened, Tested all OK | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-05-29 | c | 0.047391 | 0.00013305 | 2016 | 2015-05-29 | C | 44 | 0.047391 | 0.00013305
5117240 | 2015-06-14 07:05 | 2015-06-14 15:51 | 525.8167 | 57 | 29971.55 | 525.8167 | 522.8167 | 0.090627 | 29800.55 | 0.09011 | 0.00017235 | NAPA ID:09861 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB2162 | isolate 33kv and 11kv so that new poles, new conductor and new underground 11kv cables can be installed. cable will come down new pole installed between 828623 & 828622 then go up and back down pole 374908 to feed towards s108 and then go back up pole 82 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-06-14 | b | 0.045055 | 8.6177e-05 | 2016 | 2015-06-14 | B | 57 | 0.09011 | 0.00017235
5117567 | 2015-06-18 08:17 | 2015-06-18 15:36 | 438.85 | 19 | 8338.15 | 438.85 | 435.85 | 0.025213 | 8281.15 | 0.02504 | 5.7451e-05 | NAPA ID:09800 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse T24 | Replacing poles P45378, 380, 381, 382, 383, 384, 385, 390 & 391. Works location: Mangaramarama Rd WO 10147215 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-18 | b | 0.01252 | 2.8726e-05 | 2016 | 2015-06-18 | B | 19 | 0.02504 | 5.7451e-05
5118071 | 2015-09-29 09:46 | 2015-09-29 09:50 | 4 | 471 | 1884 | 4 | 1 | 0.0056968 | 471 | 0.0014242 | 0.0014242 | Restore Supply on Device RC15 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RC15 | Unknown fault line not patrolled No flags | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-09-29 | c | 0.0014242 | 0.0014242 | 2016 | 2015-09-29 | C | 471 | 0.0014242 | 0.0014242
5121491 | 2015-05-30 06:42 | 2015-05-30 12:50 | 367.8833 | 365 | 36373.8333 | 99.6543 | 96.6543 | 0.10999 | 35278.8333 | 0.10667 | 0.0011037 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 361332 | CB 8 A/R, L/O, E/F, O/C. Car vs Pole. Isolated at ABS 235 & ABS 338. Backfeed installed via ABS 52. NDR# 43667 Materials: 11m Pole, 1x 11kV Arm & associated hardware. Traffic Management, Excavation Contractor | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-05-30 | c | 0.10667 | 0.0011037 | 2016 | 2015-05-30 | C | 365 | 0.10667 | 0.0011037
5132748 | 2015-05-30 07:11 | 2015-05-30 08:59 | 108.65 | 19 | 268.0833 | 14.1096 | 11.1096 | 0.00081062 | 211.0833 | 0.00063827 | 5.7451e-05 | Restore Supply on Device R48 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | R48 | Replaced 2x 10Amp HV Links | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-30 | c | 0.00063826 | 5.7451e-05 | 2016 | 2015-05-30 | C | 19 | 0.00063827 | 5.7451e-05
5132815 | 2015-05-30 11:06 | 2015-05-30 13:41 | 154.8833 | 22 | 3406.55 | 154.8432 | 151.8432 | 0.010301 | 3340.55 | 0.010101 | 6.6523e-05 | Restore Supply on Device 8436 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701395 | Pole on Fire due to faulty Kidney Strain Insulator. Replaced 2x HV Crossarms, 3x Polymers, & 1x Insulator | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-05-30 | c | 0.010101 | 6.6523e-05 | 2016 | 2015-05-30 | C | 22 | 0.010101 | 6.6523e-05
5133015 | 2015-05-30 18:10 | 2015-05-30 19:00 | 50 | 5 | 250 | 50 | 47 | 0.00075594 | 235 | 0.00071058 | 1.5119e-05 | Restore Supply on Device TC4729 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | F13007 | at 18:10 Lake Rd Sub, CB 3 Rangitanuku Rd Feeder. Call came in of Digger hitting lines. Faultman dispatched. Own Isolation & AP carried out at Transformer TC4729. LV Lines repaired and all power restored. NDR 048030. Poles F13007 & F1323. 4x LV Connectors | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-05-30 | c | 0.00071058 | 1.5119e-05 | 2016 | 2015-05-30 | C | 5 | 0.00071058 | 1.5119e-05
5139649 | 2015-05-30 20:16 | 2015-05-31 03:22 | 426 | 704 | 152329 | 216.3764 | 213.3764 | 0.46061 | 150217 | 0.45422 | 0.0021287 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 769457 | Feeder Fault. CB 5 Tripped @ Taupo Quay Sub. No OMS job was created on tripping. Job created manually (due GIS not being up to date due to GXP upgrade works last week). Report of car v pole cnr Alma Rd & Moore Ave reported by fire service. Ref F1854444. 1 | F3 | CARLTON | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2015-05-30 | c | 0.45422 | 0.0021287 | 2016 | 2015-05-30 | C | 704 | 0.45422 | 0.0021287
5139652 | 2015-05-30 20:33 | 2015-05-30 23:35 | 182 | 196 | 22299.3667 | 113.7723 | 110.7723 | 0.067428 | 21711.3667 | 0.06565 | 0.00059266 | Restore Supply on Device Q61 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Q61 | 11kV Recloser Q61 feeder tripped, no flags. (Mangamutu CB 5) Report of car v pole at 261 Kohinui Rd Mangatinoka, reported by fire service. Broken 11kV pole (P18042) has not been replaced, will do via a planned shut at a later date. 11kV lines have been le | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-30 | c | 0.06565 | 0.00059266 | 2016 | 2015-05-30 | C | 196 | 0.06565 | 0.00059266
5140260 | 2015-05-30 20:43 | 2015-05-30 21:17 | 33.95 | 1 | 33.95 | 33.95 | 30.95 | 0.00010266 | 30.95 | 9.3585e-05 | 3.0238e-06 | Restore Supply on Device T3/517 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/517 | Chris Naylor Attended. Replaced 2x 3A HV fuses at Transformer T3/517. Unknown Cause. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-05-30 | c | 9.3585e-05 | 3.024e-06 | 2016 | 2015-05-30 | C | 1 | 9.3585e-05 | 3.0238e-06
5140497 | 2015-05-30 22:40 | 2015-05-31 01:17 | 156.6 | 1 | 156.6 | 156.6 | 153.6 | 0.00047352 | 153.6 | 0.00046445 | 3.0238e-06 | Restore Supply on Device TE7-109 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | FP892 | Steve Doran Attended. Found 2x Blown HV Fuses. Replaced 2x DDO's at FP892. Pole 855921. Patrolled - Cause Unknown. Do not believe there are any customers fed from this? Transformer TE7-063 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-05-30 | c | 0.00046445 | 3.024e-06 | 2016 | 2015-05-30 | C | 1 | 0.00046445 | 3.0238e-06
5140658 | 2015-05-31 04:59 | 2015-05-31 05:07 | 8 | 18 | 144 | 8 | 5 | 0.00043542 | 90 | 0.00027214 | 5.4428e-05 | Restore Supply on Device Q61 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Q58 | 1 link at Q58 had fallen out. Recloser Q61 opened while link reclosed | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-05-31 | c | 0.00027214 | 5.4428e-05 | 2016 | 2015-05-31 | C | 18 | 0.00027214 | 5.4428e-05
5141149 | 2015-05-31 21:00 | 2015-05-31 22:49 | 109 | 134 | 784 | 5.8507 | 2.8507 | 0.0023706 | 382 | 0.0011551 | 0.00040518 | Restore Supply on Device X2170 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4462/2 | Numerous properties with part power after Auto Reclose on RS4659. Fault tracked down to open circuit at Regulator 4462/2. Regulator isolated & bypassed. DNO Tag applied | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-05-31 | c | 0.0011551 | 0.00040518 | 2016 | 2015-05-31 | C | 134 | 0.0011551 | 0.00040518
5141402 | 2015-06-01 06:49 | 2015-06-01 08:10 | 80.95 | 1 | 80.95 | 80.95 | 77.95 | 0.00024477 | 77.95 | 0.0002357 | 3.0238e-06 | Restore Supply on Device 5292E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 363350 | Replaced 2 x 3amp fuses and replaced holder and 60a fuse, OH due to deterioration | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-01 | c | 0.0002357 | 3.024e-06 | 2016 | 2015-06-01 | C | 1 | 0.0002357 | 3.0238e-06
5141495 | 2015-06-01 16:12 | 2015-06-01 22:44 | 392.3 | 950 | 9945.1833 | 10.4686 | 7.4686 | 0.030072 | 7095.1833 | 0.021454 | 0.0028726 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 320013 | HEAD TOWARDS PAREOA CAR V POLE LINES ON CAR PEOPLE TRAPPED IN CAR. NZ FIRE 09 486 7948 F1855314 ETA PLEASE. ORCHARD EAST ROAD 2 K FROM PAEROA. 1626 ADVISED FIRE SERVICE 15 MINUTES AS PER SERVICE HUB TANIA Pole replaced. LV Crossarm, 4 LV Pin Insulators | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-01 | c | 0.021454 | 0.0028726 | 2016 | 2015-06-01 | C | 950 | 0.021454 | 0.0028726
5142468 | 2015-06-01 17:32 | 2015-06-01 21:16 | 223.6833 | 177 | 29177.5167 | 164.8447 | 161.8447 | 0.088226 | 28646.5167 | 0.08662 | 0.00053521 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809521 | Recloser 4659/2 tripped on A phase E/F flags, Line Down. Materials used: 3x Sleeves. 20mtrs of squirrel conductor | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-06-01 | c | 0.08662 | 0.00053521 | 2016 | 2015-06-01 | C | 177 | 0.08662 | 0.00053521
5143800 | 2015-05-01 23:00 | 2015-06-02 00:26 | 44725.9667 | 4 | 340.8 | 85.2 | 82.2 | 0.0010305 | 328.8 | 0.00099421 | 1.2095e-05 | Restore Supply on Device SE6-168 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE6-168 | Opossum on Lines at Transformer SE6-273. Removed with Fuse Stick. Line Fuses SE6-168 Blown as well as Two HV Fuses at Transformer SE6-273. 2 X 16A HV Line Fuses and 2 X HV Transformer Fuses Replaced. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-05-01 | c | 0.00099421 | 1.2095e-05 | 2016 | 2015-05-01 | C | 4 | 0.00099421 | 1.2095e-05
5147258 | 2015-06-02 12:02 | 2015-06-02 16:25 | 262.9833 | 477 | 4268.8 | 8.9493 | 5.9493 | 0.012908 | 2837.8 | 0.0085808 | 0.0014423 | Restore Supply on Device T4595 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 263499 | hv cable blown up. requesting 2R to fix the cable. Reloading & closing blown fuse x 1 ( FP808 ) tripped Sectionaliser 9870/2 Fuses FP808 opened & Sectionaliser 9870/2 closed. Repaired 3 x single 11kV cable terminations at pole 263499, all service restored | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-06-02 | c | 0.0085808 | 0.0014423 | 2016 | 2015-06-02 | C | 477 | 0.0085808 | 0.0014423
5149658 | 2015-06-02 13:23 | 2015-06-03 11:49 | 1345.9833 | 60 | 80759 | 1345.9833 | 1342.9833 | 0.2442 | 80579 | 0.24365 | 0.00018143 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2835 | 11kV recloser 4230 tripped L/O. Large Span of conductor down past fuses 2835 due to a broken conductor. Unable to repair on the night, had to leave off and repair next day (03/06) Unable to provide generators due to sizes and remote locations, was discuss | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.24365 | 0.00018143 | 2016 | 2015-06-02 | C | 60 | 0.24365 | 0.00018143
5149962 | 2015-06-02 15:54 | 2015-06-02 17:00 | 65.9833 | 22 | 1405.65 | 63.8932 | 60.8932 | 0.0042503 | 1339.65 | 0.0040508 | 6.6523e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC5-011 | HV jumper blown off bottom of ddo. Requires 2r and bucket truck. Will work through control | F3 | ARATAKI | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-06-02 | c | 0.0040508 | 6.6523e-05 | 2016 | 2015-06-02 | C | 22 | 0.0040508 | 6.6523e-05
5150343 | 2015-06-02 15:48 | 2015-06-02 16:43 | 55.1667 | 1 | 55.1667 | 55.1667 | 52.1667 | 0.00016681 | 52.1667 | 0.00015774 | 3.0238e-06 | Restore Supply on Device TA2-012 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 263499 | FM check with #120 and #124 on tx ta2-012 and the power is back on. These customers were part of oms 5147258 (signed off in same manner as oms 5147258. Outage step included in 5149359/5147258/5148837 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-06-02 | c | 0.00015774 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00015774 | 3.0238e-06
5150940 | 2015-06-02 18:07 | 2015-06-02 21:15 | 188 | 12 | 2256 | 188 | 185 | 0.0068216 | 2220 | 0.0067127 | 3.6285e-05 | Restore Supply on Device NG4 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses NG406, Tfr N1095 | Faultman fuse broken fuse holders and blown fuses at transformer N1095, faultman also found the fuse at Fuses NG406 blown all due to lightning, line was isolated at Fuses NG406 to replace the 3 fuse holder and fuses at transformer N1095 on pole 711778. 3 | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.0067127 | 3.6285e-05 | 2016 | 2015-06-02 | C | 12 | 0.0067127 | 3.6285e-05
5151689 | 2015-06-02 18:16 | 2015-06-02 18:17 | 1 | 154 | 154 | 1 | -2 | 0.00046566 | 0 | 0 | 0.00046566 | Restore Supply on Device H41 | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | H41 | 1x A/R on CB h41 - lightning in area | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0 | 0.00046566 | 2016 | 2015-06-02 | C | 154 | 0 | 0.00046566
5151861 | 2015-06-02 18:29 | 2015-06-02 20:32 | 122.6 | 2 | 245.2 | 122.6 | 119.6 | 0.00074143 | 239.2 | 0.00072328 | 6.0475e-06 | Restore Supply on Device 1309 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x1305 | *** check if oms 5151926 - tx X534 - 334 WAITARA ROAD is part of this outage *** confirmed with Blair that this is a separate job. 2x 3amp hv fuses & 2x candle sticks - worked through control. No other assets repaired or replaced and all adjacent assets c | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.00072328 | 6.048e-06 | 2016 | 2015-06-02 | C | 2 | 0.00072328 | 6.0475e-06
5151923 | 2015-06-02 19:06 | 2015-06-02 23:38 | 271.7 | 1 | 271.7 | 271.7 | 268.7 | 0.00082156 | 268.7 | 0.00081248 | 3.0238e-06 | Restore Supply on Device P4429 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P4429 | *** check if oms 5152063 - tx p4430 - 50 Mid Puniho Rd is part of this outage *** Faultman found a blown fuse on transformer P4429. 1 X 3amp HV fuse replaced. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.00081249 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00081248 | 3.0238e-06
5151949 | 2015-06-02 19:31 | 2015-06-02 21:40 | 129 | 1 | 129 | 129 | 126 | 0.00039007 | 126 | 0.00038099 | 3.0238e-06 | Restore Supply on Device 1200 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1200 | 3x 3amp DDO Fuses ( only fuses not fuse holders) - worked through control. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.00038099 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00038099 | 3.0238e-06
5152067 | 2015-06-02 20:14 | 2015-06-02 22:46 | 152.1167 | 162 | 24449.4167 | 150.9223 | 147.9223 | 0.073929 | 23963.4167 | 0.07246 | 0.00048985 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 7 | CB 7 tripped on A phase O/C flags, line was sectionalised and patrolled no fault was found, When the faultman was leaving control received a call from the Wanganui Council faultman to report a blown fuse to the No:3 water pump, fault fault check the trans | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.07246 | 0.00048985 | 2016 | 2015-06-02 | C | 162 | 0.07246 | 0.00048985
5152690 | 2015-06-02 20:30 | 2015-06-02 23:05 | 155 | 3 | 429.6 | 143.2 | 140.2 | 0.001299 | 420.6 | 0.0012718 | 9.0713e-06 | Restore Supply on Device 3587T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3587T, 2259T, 4193T | Faultman foun blown fuses on transformer 3587T. 2 X 3amp HV fuse replaced. Faultman also found fuses blown on transformers 2259T & 4193T they were also replaced under this job. 2 X 2 amp HV fuse replaced (transformer 2259T). 2 X 2amp HV fuse replaced (tra | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.0012718 | 9.071e-06 | 2016 | 2015-06-02 | C | 3 | 0.0012718 | 9.0713e-06
5152754 | 2015-06-02 20:41 | 2015-06-02 22:17 | 96.1667 | 1 | 96.1667 | 96.1667 | 93.1667 | 0.00029078 | 93.1667 | 0.00028171 | 3.0238e-06 | Restore Supply on Device TC1578 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1578 | 2 X 2A HV Fuses. Lightning | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-06-02 | c | 0.00028171 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00028171 | 3.0238e-06
5152766 | 2015-06-02 20:47 | 2015-06-02 23:29 | 161.4 | 1 | 161.4 | 161.4 | 158.4 | 0.00048803 | 158.4 | 0.00047896 | 3.0238e-06 | Restore Supply on Device X1697 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1697 | Faultman found blown fuse on transformer X1697. 1 X 3 amp HV fuse replaced | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-06-02 | c | 0.00047896 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00047896 | 3.0238e-06
5152780 | 2015-06-02 20:56 | 2015-06-02 23:46 | 170.1833 | 1 | 170.1833 | 170.1833 | 167.1833 | 0.00051459 | 167.1833 | 0.00050552 | 3.0238e-06 | Restore Supply on Device 1118 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer 1118 | Faultman found blown fuse on transformer 1118. 1 X 3 amp HV fuse replaced. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.00050552 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00050552 | 3.0238e-06
5155520 | 2015-06-02 21:17 | 2015-06-02 23:15 | 118.2333 | 1 | 118.2333 | 118.2333 | 115.2333 | 0.00035751 | 115.2333 | 0.00034844 | 3.0238e-06 | Restore Supply on Device TC1160 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1160 | 2 X 3A HV Fuses Lightning | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-06-02 | c | 0.00034844 | 3.024e-06 | 2016 | 2015-06-02 | C | 1 | 0.00034844 | 3.0238e-06
5155528 | 2015-06-02 21:28 | 2015-06-02 23:20 | 112.2 | 4 | 448.8 | 112.2 | 109.2 | 0.0013571 | 436.8 | 0.0013208 | 1.2095e-05 | Restore Supply on Device 939 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 939 | Lightning strike then pwer out, 10 homes affectd on street. Faultman found blown fuse at transformer 939. 2 x 3 amp HV fuses replaced. Email to Jo to check SAIDI. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.0013208 | 1.2095e-05 | 2016 | 2015-06-02 | C | 4 | 0.0013208 | 1.2095e-05
5155916 | 2015-06-02 21:31 | 2015-06-02 21:42 | 10.7333 | 2 | 21.4667 | 10.7333 | 7.7333 | 6.491e-05 | 15.4667 | 4.6767e-05 | 6.0475e-06 | Restore Supply on Device 6942 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 6942 | Recloser 6942 tripped on A & B phase O/C & E/F flags, contacted they were happy to reliven, lightning striking in the area. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-06-02 | c | 4.6767e-05 | 6.048e-06 | 2016 | 2015-06-02 | C | 2 | 4.6767e-05 | 6.0475e-06
5156672 | 2015-06-02 23:04 | 2015-06-03 00:15 | 71.1333 | 2 | 142.2667 | 71.1333 | 68.1333 | 0.00043018 | 136.2667 | 0.00041204 | 6.0475e-06 | Restore Supply on Device T7/303 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/303 | Faultman found blown fuses on transformer T7/303 after lightning strike. 3 x 3amp HV fuses replaced. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-02 | c | 0.00041204 | 6.048e-06 | 2016 | 2015-06-02 | C | 2 | 0.00041204 | 6.0475e-06
5159654 | 2015-06-03 06:17 | 2015-06-03 13:21 | 424.3833 | 1 | 424.3833 | 424.3833 | 421.3833 | 0.0012832 | 421.3833 | 0.0012742 | 3.0238e-06 | Restore Supply on Device P4095 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1871 Wiremu Road, Rahotu P4095 | Pls also check OMS 5159794. 2 x 3 amp HV fuses caused by lightning. checked adjacent assets and all good | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0012742 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.0012742 | 3.0238e-06
5159657 | 2015-06-03 08:10 | 2015-06-03 08:55 | 45 | 4 | 150 | 37.5 | 34.5 | 0.00045356 | 138 | 0.00041728 | 1.2095e-05 | Restore Supply on Device TD5-168 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-086 | Jumper off at fuses SD5-086. Transformer TD5-208 (5159952) Offloaded so that FM can climb up through the LV Lines. Jumper Repaired. Transformer TD5-208 isolated so that FM can work above the De Energised LV conductors. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-06-03 | c | 0.00041728 | 1.2095e-05 | 2016 | 2015-06-03 | C | 4 | 0.00041728 | 1.2095e-05
5159660 | 2015-06-03 06:28 | 2015-06-03 09:01 | 153.6667 | 1 | 153.6667 | 153.6667 | 150.6667 | 0.00046465 | 150.6667 | 0.00045558 | 3.0238e-06 | Restore Supply on Device 3758T | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 735001 | 2x 2amp fuses, due to lightning - adjacent assets fine. | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00045558 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00045558 | 3.0238e-06
5159681 | 2015-06-03 07:03 | 2015-06-03 08:36 | 93.1 | 1 | 93.1 | 93.1 | 90.1 | 0.00028151 | 90.1 | 0.00027244 | 3.0238e-06 | Restore Supply on Device 485 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 485 | Advised hub of 999 burnt out HV fuse holder due to lightning and 2 x 2 amp fuses - 1x due to lightning, 1 x due to over load | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00027244 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00027244 | 3.0238e-06
5159729 | 2015-06-03 07:25 | 2015-06-03 14:16 | 410.55 | 11 | 4516.05 | 410.55 | 407.55 | 0.013655 | 4483.05 | 0.013556 | 3.3261e-05 | Restore Supply on Device N3375 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3375 | 12.52pm - Lucy from svs hub called to ask for a CR. Replace 3 x 3A Fuse. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.013556 | 3.3261e-05 | 2016 | 2015-06-03 | C | 11 | 0.013556 | 3.3261e-05
5159736 | 2015-06-03 05:57 | 2015-06-03 07:31 | 93.85 | 3 | 281.55 | 93.85 | 90.85 | 0.00085134 | 272.55 | 0.00082413 | 9.0713e-06 | Restore Supply on Device 5583E | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 373226 | Replaced 2x 3A HT fuses. Due to weather. Nothing else repaired or replaced. All surrounding assets up to Powerco standard | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00082413 | 9.071e-06 | 2016 | 2015-06-03 | C | 3 | 0.00082413 | 9.0713e-06
5159789 | 2015-06-03 09:50 | 2015-06-03 12:50 | 180 | 2 | 360 | 180 | 177 | 0.0010886 | 354 | 0.0010704 | 6.0475e-06 | Referral: Restore Supply on Device TC1141 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1185 | On another fault FM found blown fuse on TX: TC1185 when replaced, the TX blew and needs to be replaced. 2R requested by Marty. Replaced 15KVA dual phase TX - Added seismic bracket. 2x 3A HV fuses | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-06-03 | c | 0.0010704 | 6.048e-06 | 2016 | 2015-06-03 | C | 2 | 0.0010704 | 6.0475e-06
5159794 | 2015-06-03 07:39 | 2015-06-03 16:40 | 541.3 | 1 | 541.3 | 541.3 | 538.3 | 0.0016368 | 538.3 | 0.0016277 | 3.0238e-06 | Restore Supply on Device P4097 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P4097 | Check if OMS 5160442 is linked. 1:21pm FM advises checked this up pole and no fault found - advised Fm to contact SMC as he is only assigned to this job, not on site. 1:38pm FM signed off wrong job - this is a blown tx P4097 - had to create referral 5166 | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0016277 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.0016277 | 3.0238e-06
5159808 | 2015-06-03 10:15 | 2015-06-03 12:27 | 132 | 14 | 1848 | 132 | 129 | 0.0055879 | 1806 | 0.0054609 | 4.2333e-05 | Restore Supply on Device TC2710 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WHUTAH185 | Line isolated between ABS 1361, 1370, & CB 3 to repair 11kv jumper ar pole WHUTAH185. All supply restored following repairs. 1 metre conductor, 2 x sleeves, 2 x connectors material required. spoke to Maurice in control room but he is doing switching so Pe | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-06-03 | c | 0.0054609 | 4.2333e-05 | 2016 | 2015-06-03 | C | 14 | 0.0054609 | 4.2333e-05
5159815 | 2015-06-03 07:53 | 2015-06-03 07:55 | 2 | 3 | 6 | 2 | -1 | 1.8143e-05 | 0 | 0 | 9.0713e-06 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC2398 | 2 Fuses blown at FC 2398 possibly due to lightning in the area. line patrolled. 2x6amp fuses | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-06-03 | c | 0 | 9.071e-06 | 2016 | 2015-06-03 | C | 3 | 0 | 9.0713e-06
5159881 | 2015-06-03 08:13 | 2015-06-03 12:28 | 254.5667 | 3 | 763.7 | 254.5667 | 251.5667 | 0.0023092 | 754.7 | 0.002282 | 9.0713e-06 | Restore Supply on Device 1060 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1060 | Replaced 3 x 3A Fuses Lightening | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.002282 | 9.071e-06 | 2016 | 2015-06-03 | C | 3 | 0.002282 | 9.0713e-06
5159889 | 2015-06-03 06:48 | 2015-06-03 08:56 | 127.8833 | 5 | 639.4167 | 127.8833 | 124.8833 | 0.0019334 | 624.4167 | 0.0018881 | 1.5119e-05 | Restore Supply on Device 797 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 797 | Has had no power since 6pm last night due to lightning, thinks it's just his road, 3ks of the road and he's down the end. Transformer 797 3x HV fuses replaced HV OH caused by lightning worked through Control. No other assets repaired or replaced, all adj | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0018881 | 1.5119e-05 | 2016 | 2015-06-03 | C | 5 | 0.0018881 | 1.5119e-05
5159962 | 2015-06-06 11:02 | 2015-06-06 11:33 | 30.9833 | 68 | 2106.8667 | 30.9833 | 27.9833 | 0.0063707 | 1902.8667 | 0.0057538 | 0.00020562 | NAPA ID:09932 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 846481 | close line break at pole 846481 Outage may not be correct. Only affected Transformer 1374 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-06 | b | 0.0028769 | 0.00010281 | 2016 | 2015-06-06 | B | 68 | 0.0057538 | 0.00020562
5160447 | 2015-06-03 07:27 | 2015-06-03 09:27 | 120.4667 | 6 | 722.8 | 120.4667 | 117.4667 | 0.0021856 | 704.8 | 0.0021311 | 1.8143e-05 | Restore Supply on Device N1185 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N1185 | 2 X 2AMP HV FUSES BLOWN DUE TO LIGHTNING = ADJACENT ASSETS ALL GOOD | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0021311 | 1.8143e-05 | 2016 | 2015-06-03 | C | 6 | 0.0021311 | 1.8143e-05
5160474 | 2015-06-03 09:22 | 2015-06-03 12:10 | 167.6333 | 1 | 167.6333 | 167.6333 | 164.6333 | 0.00050688 | 164.6333 | 0.00049781 | 3.0238e-06 | Restore Supply on Device 1288 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1336 | Ask if OMS 5160465 linked and 5161625. Different Feeder. Replace 3 x 3A Fuse | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00049781 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00049781 | 3.0238e-06
5160638 | 2015-06-03 09:56 | 2015-06-03 13:38 | 222 | 2 | 370.15 | 185.075 | 182.075 | 0.0011192 | 364.15 | 0.0011011 | 6.0475e-06 | Restore Supply on Device X1566 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1566 | 2 x 2 amp HV fuse and 1 x carrier - due to lightning at tx X1566 - adjacent assets checked and replaced more fuses: * 199 Makakaho Rd replaced 3x 2amp fuses and 2 x DDO carriers - due to lightning - TX X1565 * 151 Makakao Rd 2 x 2 amp HV fuses due to ligh | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-03 | c | 0.0011011 | 6.048e-06 | 2016 | 2015-06-03 | C | 2 | 0.0011011 | 6.0475e-06
5160693 | 2015-06-25 09:00 | 2015-06-25 14:18 | 318.3667 | 34 | 10824.4667 | 318.3667 | 315.3667 | 0.032731 | 10722.4667 | 0.032422 | 0.00010281 | NAPA ID:09213 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF7-031 | Replace poles, crossarms and conductor. Works location: Old Coach Rd Paengaroa. WO 30002518 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-25 | b | 0.016211 | 5.1404e-05 | 2016 | 2015-06-25 | B | 34 | 0.032422 | 0.00010281
5160737 | 2015-06-03 10:42 | 2015-06-03 17:03 | 381.2833 | 5 | 1906.4167 | 381.2833 | 378.2833 | 0.0057645 | 1891.4167 | 0.0057192 | 1.5119e-05 | Restore Supply on Device 3779T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3779T | Replace 2 x 2A Fuse | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0057192 | 1.5119e-05 | 2016 | 2015-06-03 | C | 5 | 0.0057192 | 1.5119e-05
5160768 | 2015-06-03 10:55 | 2015-06-03 18:01 | 426.7667 | 9 | 3840.9 | 426.7667 | 423.7667 | 0.011614 | 3813.9 | 0.011532 | 2.7214e-05 | Restore Supply on Device N3150 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N3150 | Part power to dairy shed. 2r created to replace transformer as damaged via lightning. Transformer replaced via self permitting. All power restored at 1734, all works etc complete just after 18:00, all tested fine. Still an internal fault at shed, owner S | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.011532 | 2.7214e-05 | 2016 | 2015-06-03 | C | 9 | 0.011532 | 2.7214e-05
5160843 | 2015-06-03 11:25 | 2015-06-03 21:16 | 591.0167 | 768 | 43969.9667 | 57.2526 | 54.2526 | 0.13295 | 41665.9667 | 0.12599 | 0.0023222 | Restore Supply on Device U20 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 384851 | CB U20 tripped, Locked out, no flags. Downstream Recloser RS 4989 tripped by NOC. Steve from Downer - 0274457250 - has advised that one of his trucks has hit a power pole and has brought two (2) lines down. He is on his way to investigate. No further info | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.12599 | 0.0023222 | 2016 | 2015-06-03 | C | 768 | 0.12599 | 0.0023222
5161616 | 2015-06-29 09:16 | 2015-06-29 14:24 | 308.1167 | 34 | 10475.9667 | 308.1167 | 305.1167 | 0.031677 | 10373.9667 | 0.031368 | 0.00010281 | NAPA ID:09220 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF8-005 | Replace poles, crossarms and conductor. Works location; Old Coach Rd Paengaroa. WO 30002518 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-29 | b | 0.015684 | 5.1404e-05 | 2016 | 2015-06-29 | B | 34 | 0.031368 | 0.00010281
5161625 | 2015-06-03 11:32 | 2015-06-03 12:42 | 69.9833 | 1 | 69.9833 | 69.9833 | 66.9833 | 0.00021161 | 66.9833 | 0.00020254 | 3.0238e-06 | Restore Supply on Device 1366 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | check if linked 5160474 | This job was related to 5160474 - 3x 3A fuses replaced. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00020254 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00020254 | 3.0238e-06
5163303 | 2015-06-03 13:01 | 2015-06-03 13:18 | 17.1833 | 2825 | 45461.55 | 16.0926 | 13.0926 | 0.13746 | 36986.55 | 0.11184 | 0.0085421 | Restore Supply on Device 19 | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB19 | 11kV CB 19 tripped, lock out, NO flags. Loss of supply to all ICP's at 13:01. Protection review required please Jo. Electrix working onsite on 33kV Cb XT60 protection at time. Downers to site promptly, found no flags on any CB's. NOC relivened 11kV BUS th | F1,F2,F3 | MANGAMUTU 2 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2015-06-03 | c | 0.11184 | 0.0085421 | 2016 | 2015-06-03 | C | 2825 | 0.11184 | 0.0085421
5166230 | 2015-06-03 09:14 | 2015-06-03 16:44 | 449.3 | 1 | 449.3 | 449.3 | 446.3 | 0.0013586 | 446.3 | 0.0013495 | 3.0238e-06 | Referral: Restore Supply on Device P4097 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1752 WIREMU ROAD, RAHOTU | 2R request to replace blown TX. P4100 (FM signed off the wrong job). *** please check if oms 5160442 - 1750 WIREMU ROAD is part of this outage *** fm confirmed 1750 5160442 is related so linked now. Transformer replaced and service restored at 16:40 | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0013495 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.0013495 | 3.0238e-06
5166235 | 2015-06-03 13:43 | 2015-06-03 13:58 | 15.6 | 2 | 31.2 | 15.6 | 12.6 | 9.4341e-05 | 25.2 | 7.6199e-05 | 6.0475e-06 | Restore Supply on Device 466 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 466 | Replace 2 x 3A Fuse | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-03 | c | 7.6199e-05 | 6.048e-06 | 2016 | 2015-06-03 | C | 2 | 7.6199e-05 | 6.0475e-06
5168792 | 2015-06-03 14:04 | 2015-06-03 16:10 | 125.9 | 1 | 125.9 | 125.9 | 122.9 | 0.00038069 | 122.9 | 0.00037162 | 3.0238e-06 | Restore Supply on Device P1402 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P1402 | Replace Transformer P1402 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00037162 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00037162 | 3.0238e-06
5169084 | 2015-06-03 08:31 | 2015-06-03 14:37 | 365.7333 | 6 | 2194.4 | 365.7333 | 362.7333 | 0.0066353 | 2176.4 | 0.0065809 | 1.8143e-05 | Restore Supply on Device 4425T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4425T | Faulty transformer 4425T replaced. Lightning damage. Own AP issued on site. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0065809 | 1.8143e-05 | 2016 | 2015-06-03 | C | 6 | 0.0065809 | 1.8143e-05
5169112 | 2015-06-03 14:54 | 2015-06-03 16:45 | 111.15 | 211 | 8844.2333 | 41.9158 | 38.9158 | 0.026743 | 8211.2333 | 0.024829 | 0.00063801 | Restore Supply on Device 7 | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Cb 7 | Circuit breaker faulted DNO 150602 Feeder reconfigured with backfeeds until breaker repaired | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.024829 | 0.00063801 | 2016 | 2015-06-03 | C | 211 | 0.024829 | 0.00063801
5170245 | 2015-06-03 14:55 | 2015-06-08 16:45 | 7309.8667 | 919 | 63378.4833 | 68.9646 | 65.9646 | 0.19164 | 60621.4833 | 0.1833 | 0.0027788 | Restore Supply on Device 5329 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 5329 | 11kV Recloser 5329 (out of Waitara East Sub, CB U30) tripped O/C E/F L/O. Trees down through lines past fuses 5193. Near transformer 2999T. Forestry crew has dropped a tree through lines, pole and transformer site, major rebuild required. Unable to repair | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.1833 | 0.0027788 | 2016 | 2015-06-03 | C | 919 | 0.1833 | 0.0027788
5170811 | 2015-06-03 15:19 | 2015-06-03 18:38 | 199.0833 | 1 | 199.0833 | 199.0833 | 196.0833 | 0.00060198 | 196.0833 | 0.00059291 | 3.0238e-06 | Restore Supply on Device T7/302 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/302 | Replaced 25kva 3 phase transformer T7/302 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00059291 | 3.024e-06 | 2016 | 2015-06-03 | C | 1 | 0.00059291 | 3.0238e-06
5170824 | 2015-06-20 06:05 | 2015-06-20 08:03 | 117.95 | 24 | 2830.8 | 117.95 | 114.95 | 0.0085597 | 2758.8 | 0.008342 | 7.257e-05 | NAPA ID:09741 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 4 | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G9C | Replace cable between G149T and transformer due to cable break down on Magnefix. Works location; Spotlight. WO 30001663. | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-06-20 | b | 0.004171 | 3.6285e-05 | 2016 | 2015-06-20 | B | 24 | 0.008342 | 7.257e-05
5170832 | 2015-06-03 15:42 | 2015-06-03 19:07 | 204.8167 | 417 | 32956.1833 | 79.0316 | 76.0316 | 0.099652 | 31705.1833 | 0.095869 | 0.0012609 | Restore Supply on Device RC27 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | K1501 | TAH 4 Recloser RC27 tripped E/F, O/C , L/O. Feeder sectionalised & fault isolated to between ABS IC473 & Sectionaliser 9668/2. Branch found on line at pole K1501, branch removed all service restored. Materials: Nil. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-03 | c | 0.095869 | 0.0012609 | 2016 | 2015-06-03 | C | 417 | 0.095869 | 0.0012609
5171540 | 2015-06-03 16:15 | 2015-06-03 21:03 | 288.4833 | 305 | 20095.1167 | 65.8856 | 62.8856 | 0.060763 | 19180.1167 | 0.057996 | 0.00092225 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 745328 | Received report of tree on the lines on Mountain Road. Feeder was de- energised at Recloser 8667 and then line was isolated at ABS's 97 & 239, Tree contractor was contacted to remove the tree from the line between poles 745328 & 745330. NDR: 38187 | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.057996 | 0.00092225 | 2016 | 2015-06-03 | C | 305 | 0.057996 | 0.00092225
5171862 | 2015-06-03 15:00 | 2015-06-03 16:35 | 95.3333 | 3 | 286 | 95.3333 | 92.3333 | 0.0008648 | 277 | 0.00083758 | 9.0713e-06 | Restore Supply on Device P1380 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1380 | Replace 3 x 2A Fuse | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.00083758 | 9.071e-06 | 2016 | 2015-06-03 | C | 3 | 0.00083758 | 9.0713e-06
5172504 | 2015-06-03 19:14 | 2015-06-03 21:45 | 151 | 597 | 51953 | 87.0235 | 84.0235 | 0.15709 | 50162 | 0.15168 | 0.0018052 | Restore Supply on Device 32:52 | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 712004 | CB 3252& CB 3232 and CB NG 2 all tripped. alarms received were CB NG2 A, B &C phase fault, CB 3232no flags, CB 3252 Bus Trip flags, & T1 A, B & C phase fault flags, sub was checked by faultman and no fault found at the sub, suspect fault on CB NG2 caused | F1,F2,F3 | RAHOTU 33KV | OPUNAKE | Taranaki | TP_OPUNAKE | Western Electricity | POWERCO | 2015-06-03 | c | 0.15168 | 0.0018052 | 2016 | 2015-06-03 | C | 597 | 0.15168 | 0.0018052
5175247 | 2015-06-03 19:19 | 2015-06-03 21:50 | 151.2833 | 712 | 27960.8833 | 39.2709 | 36.2709 | 0.084547 | 25824.8833 | 0.078088 | 0.0021529 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 788312 | All part of OMS | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.078088 | 0.0021529 | 2016 | 2015-06-03 | C | 712 | 0.078088 | 0.0021529
5177894 | 2015-06-03 21:42 | 2015-06-03 22:08 | 26 | 358 | 9308 | 26 | 23 | 0.028145 | 8234 | 0.024898 | 0.0010825 | Restore Supply on Device M1293 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 5 | CB 5 tripped on O/C flags, line was not patrolled, CB was not livened as there was a job for sparking lines on the feeder, after contacting the faultman, the faultman confirmed the job had nothing to do with the tripping as it was just a safety disconnec | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.024898 | 0.0010825 | 2016 | 2015-06-03 | C | 358 | 0.024898 | 0.0010825
5179054 | 2015-06-03 21:41 | 2015-06-03 23:16 | 95 | 5 | 475 | 95 | 92 | 0.0014363 | 460 | 0.0013909 | 1.5119e-05 | Restore Supply on Device T5175 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA806 | Faultman found fuses blown at Fuses TA806. 2 x 3 amp HV fuses replaced. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.0013909 | 1.5119e-05 | 2016 | 2015-06-03 | C | 5 | 0.0013909 | 1.5119e-05
5180198 | 2015-06-03 11:19 | 2015-06-04 01:38 | 858.5333 | 681 | 89874 | 131.9736 | 128.9736 | 0.27176 | 87831 | 0.26558 | 0.0020592 | Restore Supply on Device L34 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P32864 | Recloser L34 tripped on A & B phase O/C flags, line was sectionalised and patrolled and a dead tree was found touching the line at pole P32864. Dead tree was remove with hot line sticks.Tree outside zone. NDR: N300072. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-03 | c | 0.26558 | 0.0020592 | 2016 | 2015-06-03 | C | 681 | 0.26558 | 0.0020592
5181252 | 2015-06-04 08:33 | 2015-06-04 09:24 | 50.65 | 640 | 32242.9 | 50.3795 | 47.3795 | 0.097495 | 30322.9 | 0.091689 | 0.0019352 | Restore Supply on Device 2172 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 824726 | Advised by NGOC CB 2172 had Tripped on O/C - Backfeeds install via ABS S364 - 33kv line Patrolled Dead Bird found at Pole 824726 - 33kv Line returned to Service then sub returned to normal configuration | F1,F2,F3 | GLADSTONE 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 2015-06-04 | c | 0.091689 | 0.0019352 | 2016 | 2015-06-04 | C | 640 | 0.091689 | 0.0019352
5181914 | 2015-06-04 08:43 | 2015-06-04 10:09 | 86.3333 | 1 | 86.3333 | 86.3333 | 83.3333 | 0.00026105 | 83.3333 | 0.00025198 | 3.0238e-06 | Restore Supply on Device X1536 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1536 | Two fuses for Transformer X1536 found blown due to lightening - Fuses replaced - used 2 x 2amp fuses | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-04 | c | 0.00025198 | 3.024e-06 | 2016 | 2015-06-04 | C | 1 | 0.00025198 | 3.0238e-06
5182050 | 2015-06-04 09:23 | 2015-06-04 18:45 | 562 | 364 | 31568 | 86.7253 | 83.7253 | 0.095454 | 30476 | 0.092152 | 0.0011006 | Restore Supply on Device WH2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 725807 | CB WH2 tripped. No flags. Replaced pole 725807 and repaired conductors damaged by tree as a result of a land slip. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-06-04 | c | 0.092152 | 0.0011006 | 2016 | 2015-06-04 | C | 364 | 0.092152 | 0.0011006
5184101 | 2015-06-04 11:19 | 2015-06-04 15:19 | 240 | 1 | 240 | 240 | 237 | 0.0007257 | 237 | 0.00071663 | 3.0238e-06 | Restore Supply on Device TC1365 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TC1365 | 11:22 advised control and hub police called to advise power pole is down and ripped power line off house also - police and fire enroute. 09 571 2801 P021416822 11:26 advised fire & police eta 15 minutes 1.04pm - FM isolated power. no tag as team arrived t | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-04 | c | 0.00071663 | 3.024e-06 | 2016 | 2015-06-04 | C | 1 | 0.00071663 | 3.0238e-06
5184831 | 2015-06-04 14:16 | 2015-06-04 17:17 | 181.3667 | 2 | 362.7333 | 181.3667 | 178.3667 | 0.0010968 | 356.7333 | 0.0010787 | 6.0475e-06 | Restore Supply on Device 3788T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3788T | 2 HV fuses blown at transfomer 3788T. reloaded & livened voltages al correct. 2x3amp fuses | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-04 | c | 0.0010787 | 6.048e-06 | 2016 | 2015-06-04 | C | 2 | 0.0010787 | 6.0475e-06
5187050 | 2015-06-04 23:45 | 2015-06-05 01:02 | 76.7833 | 1 | 76.7833 | 76.7833 | 73.7833 | 0.00023217 | 73.7833 | 0.0002231 | 3.0238e-06 | Restore Supply on Device 1269 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8221 | replaced 2X 10a HV fuses | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-04 | c | 0.0002231 | 3.024e-06 | 2016 | 2015-06-04 | C | 1 | 0.0002231 | 3.0238e-06
5187053 | 2015-06-05 00:14 | 2015-06-05 05:25 | 310.9667 | 240 | 63762.8 | 265.6783 | 262.6783 | 0.1928 | 63042.8 | 0.19063 | 0.0007257 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 776952 | Recloser 4232 ARC (3adv) & trip B phase O/C & E/F During sectioalising and patrol found lines down between poles 776952 & 373137 .repaired conductor used 10m squirel and 2 sleves | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-06-05 | c | 0.19063 | 0.0007257 | 2016 | 2015-06-05 | C | 240 | 0.19063 | 0.0007257
5188142 | 2015-06-05 05:36 | 2015-06-05 08:43 | 186.7667 | 1 | 186.7667 | 186.7667 | 183.7667 | 0.00056474 | 183.7667 | 0.00055567 | 3.0238e-06 | Restore Supply on Device 2292T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4982 | HV links out, line patrol required to find cause. 2 X 8 Amp HT Fuses | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-05 | c | 0.00055567 | 3.024e-06 | 2016 | 2015-06-05 | C | 1 | 0.00055567 | 3.0238e-06
5188145 | 2015-06-05 06:10 | 2015-06-05 06:14 | 4.3167 | 87 | 375.55 | 4.3167 | 1.3167 | 0.0011356 | 114.55 | 0.00034637 | 0.00026307 | Restore Supply on Device SE6-012 | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | IP446 | at 05:47 Te Puke Sub, CB 4 Paengaroa Feeder. While moving high load in the area, it was found that they needed to isolate a section of 11kV Lines to get the load under safely. No where load could park up so had to moved under lines. Lines isolated at ABS | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-06-05 | c | 0.00034637 | 0.00026307 | 2016 | 2015-06-05 | C | 87 | 0.00034637 | 0.00026307
5188235 | 2015-06-05 07:15 | 2015-06-05 08:35 | 80.2167 | 38 | 3048.2333 | 80.2167 | 77.2167 | 0.0092171 | 2934.2333 | 0.0088724 | 0.0001149 | Restore Supply on Device 994 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8420 | Replaced 2 X 10 Amp HT Fuses | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-06-05 | c | 0.0088724 | 0.0001149 | 2016 | 2015-06-05 | C | 38 | 0.0088724 | 0.0001149
5188328 | 2015-06-05 08:39 | 2015-06-05 10:54 | 135.2 | 1 | 135.2 | 135.2 | 132.2 | 0.00040881 | 132.2 | 0.00039974 | 3.0238e-06 | Restore Supply on Device X2636 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x2636 | 2 x fuses found blown at Transformer X2636 caused by Lightnening - Used 2 x 2amp fuses | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-05 | c | 0.00039974 | 3.024e-06 | 2016 | 2015-06-05 | C | 1 | 0.00039974 | 3.0238e-06
5188732 | 2015-06-05 11:27 | 2015-06-05 11:47 | 20.6333 | 25 | 515.8333 | 20.6333 | 17.6333 | 0.0015598 | 440.8333 | 0.001333 | 7.5594e-05 | Restore Supply on Device S582 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7257 | Part of NAPA 9406. Original Isolation point has failed on relivening due to age (fuses 7257) Requiring unplanned Shut to replace full set of fuse holders. Lucas Grant on site ASW. - Isolated at ABS S582 DDO's replaced - Used 2x ddo's and 2x 10amp fuses | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-05 | c | 0.001333 | 7.5594e-05 | 2016 | 2015-06-05 | C | 25 | 0.001333 | 7.5594e-05
5188947 | 2015-06-29 09:00 | 2015-06-29 12:08 | 187.7833 | 60 | 11267 | 187.7833 | 184.7833 | 0.034069 | 11087 | 0.033524 | 0.00018143 | NAPA ID:08745 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TAWA ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S5475 | Change over transformer TC4-207 from fuse-switch S5475 to new fuse-switch 9944-4. Works location: Banks Ave. WO 30000872 | F3 | TAWA ST | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-06-29 | b | 0.016762 | 9.0713e-05 | 2016 | 2015-06-29 | B | 60 | 0.033524 | 0.00018143
5188975 | 2015-06-29 12:31 | 2015-06-29 16:34 | 243.3833 | 101 | 24581.7167 | 243.3833 | 240.3833 | 0.074329 | 24278.7167 | 0.073413 | 0.0003054 | NAPA ID:08747 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TAWA ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-275 | Change-over transformer TC4-275 from fuse-switch S5467 to fuse-switch 9944-2 | F3 | TAWA ST | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-06-29 | b | 0.036707 | 0.0001527 | 2016 | 2015-06-29 | B | 101 | 0.073413 | 0.0003054
5202105 | 2015-06-06 17:36 | 2015-06-10 19:18 | 5862 | 2505 | 108495 | 43.3114 | 40.3114 | 0.32806 | 100980 | 0.30534 | 0.0075745 | Restore Supply on Device 5 | 11 | Unplanned | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | CB5 | Feeder fault. Line sectionalized & patrolled. Cable found damaged by UFB thrusting. DNO 100031. | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-06-06 | c | 0.30534 | 0.0075745 | 2016 | 2015-06-06 | C | 2505 | 0.30534 | 0.0075745
5222438 | 2015-06-06 23:09 | 2015-06-07 00:34 | 84.7167 | 486 | 41172.3 | 84.7167 | 81.7167 | 0.1245 | 39714.3 | 0.12009 | 0.0014695 | Restore Supply on Device TC4-187 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213761 | arching power lines outside ppty - called in by fire service plz adv dispatch eta. 8.22pm adv Sammy of job - eta 15mins advised fire ( Donna) Replaced double crossarm & insulators at pole 213761. Isolation at Sw/Gear 9564/1 & ABS SD4-097 no Back feeds ava | F3 | CENTRAL PARADE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-06-06 | c | 0.12009 | 0.0014695 | 2016 | 2015-06-06 | C | 486 | 0.12009 | 0.0014695
5239375 | 2015-06-06 23:00 | 2015-06-07 03:20 | 260.1 | 744 | 97904.65 | 131.5923 | 128.5923 | 0.29604 | 95672.65 | 0.28929 | 0.0022497 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 200988 | CB 1 trip due to Car accident at pole 200988. Flags E/F. Jumper also blown off at pole 200653 Reported by Fire service a sparking pole. Isolated at ABS's SD3-112, SD3-009, SD3-010 9678/1 & Links 9768/4. No Back feeds available due to Recloser 9803/2 out | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-06 | c | 0.28929 | 0.0022497 | 2016 | 2015-06-06 | C | 744 | 0.28929 | 0.0022497
5240609 | 2015-06-06 23:44 | 2015-06-07 01:07 | 83.0167 | 721 | 42918.7833 | 59.5267 | 56.5267 | 0.12978 | 40755.7833 | 0.12324 | 0.0021801 | Restore Supply on Device 5 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | CB 5 | Faulty Cable between CB 5 and ABS L1 found during sectionlising - Cable Isolated - Backfeeds installed via ABS's M2 and M43 - Cable to be tested on Monday Referral job created | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-06 | c | 0.12324 | 0.0021801 | 2016 | 2015-06-06 | C | 721 | 0.12324 | 0.0021801
5244173 | 2015-06-07 10:20 | 2015-06-07 11:30 | 69.9 | 1 | 69.9 | 69.9 | 66.9 | 0.00021136 | 66.9 | 0.00020229 | 3.0238e-06 | Restore Supply on Device 8203 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 8203 | Replaced 2x 20Amp HV Links | F2 | KATERE 11 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-06-07 | c | 0.00020229 | 3.024e-06 | 2016 | 2015-06-07 | C | 1 | 0.00020229 | 3.0238e-06
5244216 | 2015-06-07 11:39 | 2015-06-07 12:35 | 56.3 | 66 | 3715.8 | 56.3 | 53.3 | 0.011236 | 3517.8 | 0.010637 | 0.00019957 | Restore Supply on Device 1014 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O14117 | Blown Jumper at Transformer TC3530, Pole O14117. 1 X 25mm Crimp Lug. ! X 25mm Crimp Sleeve. 1m 25mm Cable Lead. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-07 | c | 0.010637 | 0.00019957 | 2016 | 2015-06-07 | C | 66 | 0.010637 | 0.00019957
5245687 | 2015-06-08 13:50 | 2015-06-08 15:11 | 81.4 | 49 | 3988.6 | 81.4 | 78.4 | 0.012061 | 3841.6 | 0.011616 | 0.00014816 | Restore Supply on Device N2200 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 712011 | Brett is getting traffic management out for the 2R. Used hv fuse arm, 3 hv fuses (units complete) and 1 x 16mm bare conductor, 3 x 16mm copper sleeves. pole # 712011. tx n2205. cause: age and deterioration, screws rusted off. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-08 | c | 0.011616 | 0.00014816 | 2016 | 2015-06-08 | C | 49 | 0.011616 | 0.00014816
5246203 | 2015-06-23 09:25 | 2015-06-23 14:20 | 295 | 6 | 1770 | 295 | 292 | 0.0053521 | 1752 | 0.0052976 | 1.8143e-05 | NAPA ID:10050 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE3-052 | Remove pole mount 50kva TX, Install new ground mount 100kva TX and liven from existing DDOs. (pole no 216496). Re-label existing transformer fuses TE3-052 to FP1695. Works location: Pyes Pa. WO 30008719 | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-06-23 | b | 0.0026488 | 9.071e-06 | 2016 | 2015-06-23 | B | 6 | 0.0052976 | 1.8143e-05
5328954 | 2015-06-08 14:30 | 2015-06-08 17:05 | 155.1833 | 29 | 4500.3167 | 155.1833 | 152.1833 | 0.013608 | 4413.3167 | 0.013345 | 8.7689e-05 | Restore Supply on Device T4948 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208488 | part of oms 5326129. Jumper replaced at Pole 208488. 1 mtr Namu Conductor 2 x Namu Joints | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-06-08 | c | 0.013345 | 8.7689e-05 | 2016 | 2015-06-08 | C | 29 | 0.013345 | 8.7689e-05
5330019 | 2015-06-09 07:03 | 2015-06-09 11:54 | 291 | 255 | 30073 | 117.9333 | 114.9333 | 0.090934 | 29308 | 0.08862 | 0.00077106 | Restore Supply on Device S6031 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 231308 | TPV CB4 Recloser S6031 tripped E/F, A & B Ph O/C, L/O. Feeder sectionalised with fault found to be beyond ABS S6011 & normal open point ABS SF6 039 ( no back feeds ) Recloser S6031 closed to restore supply. Lines down X 2 at pole 231308 found ( bird stri | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-06-09 | c | 0.08862 | 0.00077106 | 2016 | 2015-06-09 | C | 255 | 0.08862 | 0.00077106
5351964 | 2015-06-09 13:06 | 2015-06-09 14:41 | 95 | 6 | 570 | 95 | 92 | 0.0017235 | 552 | 0.0016691 | 1.8143e-05 | Restore Supply on Device T9/190 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22914 | Trevor fm advsied 11 kv line down requesting 2r but unsure how much cable will need to be replaced so will put another 1r for assistance to replace 11kv line can be 2r if over 3 meters or more than one conductor. Faultman found line down at pole P22914 , | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-09 | c | 0.0016691 | 1.8143e-05 | 2016 | 2015-06-09 | C | 6 | 0.0016691 | 1.8143e-05
5351979 | 2015-06-09 06:54 | 2015-06-09 14:40 | 466 | 147 | 39427 | 268.2109 | 265.2109 | 0.11922 | 38986 | 0.11788 | 0.00044449 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Tairua CB3 tripped on O/C C phase and E/F. Line was patrolled and no fault found. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-06-09 | c | 0.11788 | 0.00044449 | 2016 | 2015-06-09 | C | 147 | 0.11788 | 0.00044449
5373359 | 2015-06-10 03:03 | 2015-06-10 03:54 | 51.3833 | 307 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00092829 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C627 | RS C627 A/R, O/C A & B Phase.Not patrolled, No fault found | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-06-10 | c | 0 | 0.00092829 | 2016 | 2015-06-10 | C | 307 | 0 | 0.00092829
5375464 | 2015-06-10 12:24 | 2015-06-10 14:00 | 96.0667 | 343 | 20157.6167 | 58.7686 | 55.7686 | 0.060952 | 19128.6167 | 0.05784 | 0.0010371 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Mangamutu | Tripping on Mangamutu CB6 on O/C R-Y-B, INVT. Feeder patrolled / sectionalised but nothing found. Restored OK. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-10 | c | 0.05784 | 0.0010371 | 2016 | 2015-06-10 | C | 343 | 0.05784 | 0.0010371
5388136 | 2015-06-11 09:39 | 2015-06-11 10:01 | 21.5667 | 19 | 409.7667 | 21.5667 | 18.5667 | 0.001239 | 352.7667 | 0.0010667 | 5.7451e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773500 | 1R Investigate broken binder at Pole 773500. Ben advised looks OK at the moment. Will arrange outage Thursday. Isolation carried out from Fuses 772 to rebind 2 Insulators. However, there was a large inductance generated from nearby Transpower Lines. Cons | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0010667 | 5.7451e-05 | 2016 | 2015-06-11 | C | 19 | 0.0010667 | 5.7451e-05
5388183 | 2015-06-10 16:45 | 2015-06-10 18:10 | 84.9833 | 2 | 169.9667 | 84.9833 | 81.9833 | 0.00051394 | 163.9667 | 0.0004958 | 6.0475e-06 | Restore Supply on Device TP556 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 268888 | 4.47pm - advise smc. 4.54pm - smc advise eta of 25 min. Advised Helen at Fire Comms. 5.04pm - Fire Comms advise leaving site as fuses have blown, sparking has stopped. pole 268888. advise smc. Replaced 2 x 15A H/V, O/H Fuses at FP518 possible bird strike | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-06-10 | c | 0.0004958 | 6.048e-06 | 2016 | 2015-06-10 | C | 2 | 0.0004958 | 6.0475e-06
5389263 | 2015-06-10 17:25 | 2015-06-10 19:15 | 110 | 1023 | 12727 | 12.4409 | 9.4409 | 0.038483 | 9658 | 0.029203 | 0.0030933 | Restore Supply on Device T6/158 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P35189 | broke crossarm at pole p35189 materuials crossarm and 3 insulators | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-06-10 | c | 0.029203 | 0.0030933 | 2016 | 2015-06-10 | C | 1023 | 0.029203 | 0.0030933
5394049 | 2015-06-10 23:10 | 2015-06-11 01:27 | 137.3167 | 9 | 1235.85 | 137.3167 | 134.3167 | 0.0037369 | 1208.85 | 0.0036553 | 2.7214e-05 | Restore Supply on Device T3163 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 821011 | Advised hub and control of lines down. Faultman found pole down at pole 821011, line was isolated at Fuses 7146 after pole was hit by a car. 1 X 10 metre pole replaced. 1 X cross arm with all it's hardware replaced. NDR: 37923 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-10 | c | 0.0036553 | 2.7214e-05 | 2016 | 2015-06-10 | C | 9 | 0.0036553 | 2.7214e-05
5394135 | 2015-06-10 22:11 | 2015-06-11 10:16 | 724.5 | 77 | 19456.1667 | 252.6775 | 249.6775 | 0.058831 | 19225.1667 | 0.058132 | 0.00023283 | Restore Supply on Device 4832 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736273 | Recloser 4832/2 tripped on E/F flags, line was patrolled and sectionalised, faultman found a damaged insulator on pole 736273, line was isolated at Fuses 4946 to replace the insulator.Faultman to return in morning to locate 2 fault. 1 x 11KV insulator rep | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-10 | c | 0.058132 | 0.00023283 | 2016 | 2015-06-10 | C | 77 | 0.058132 | 0.00023283
5394527 | 2015-06-11 00:55 | 2015-06-11 17:07 | 972 | 76 | 18892.95 | 248.5914 | 245.5914 | 0.057128 | 18664.95 | 0.056438 | 0.00022981 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 832163 | Recloser 7417 tripped on A & B phase O/C & E/F flags, line was patrolled and sectionalised and faultman found trees across the line between poles 832163 & 367737, line was isolated at Fuses 7993.This has been an on going problem with the forestry about th | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.056438 | 0.00022981 | 2016 | 2015-06-11 | C | 76 | 0.056438 | 0.00022981
5394864 | 2015-06-11 08:09 | 2015-06-11 09:45 | 96.1833 | 63 | 6059.55 | 96.1833 | 93.1833 | 0.018323 | 5870.55 | 0.017751 | 0.0001905 | Restore Supply on Device TD6-018 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD6-003 | Please check OMS 5394872 if related . Fuse blown at SD6-003. Fuse is in 2 pieces. Isolated at fuses sd6-003 so that testing of the cable & transformer can be carried out to determine if a fault is present. Cable & transformer tested No Fault found, Suppl | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-06-11 | c | 0.017751 | 0.0001905 | 2016 | 2015-06-11 | C | 63 | 0.017751 | 0.0001905
5394886 | 2015-06-11 09:18 | 2015-06-11 09:42 | 24 | 35 | 840 | 24 | 21 | 0.00254 | 735 | 0.0022225 | 0.00010583 | Restore Supply on Device TC2326 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC 2326 | Requesting 2r to replace burnt out 1x ddo taking customers off will work through control 1x ddo is only 1r so 2r no requested. fm going to depot to get the fuse and will then work through control | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-06-11 | c | 0.0022225 | 0.00010583 | 2016 | 2015-06-11 | C | 35 | 0.0022225 | 0.00010583
5395420 | 2015-06-11 08:39 | 2015-06-11 12:11 | 211.85 | 1 | 211.85 | 211.85 | 208.85 | 0.00064058 | 208.85 | 0.00063151 | 3.0238e-06 | Restore Supply on Device N3110 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3110 | Replaced 2X 3a hV Fuses & 3X 60a HRC lV fuses | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00063151 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00063151 | 3.0238e-06
5395424 | 2015-06-11 08:39 | 2015-06-11 10:14 | 94.8667 | 2 | 189.7333 | 94.8667 | 91.8667 | 0.00057371 | 183.7333 | 0.00055557 | 6.0475e-06 | Restore Supply on Device T1882 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T1182 | CHECK FOR SAFETY- branch has fallen on the pole which has landed on the tx on the pole, causing no power onsite. no access issues. On the mailbox shows #95. cut tree away NDR 21911 no damage to tx need to replace 3x 11kv fuses 2amp fuses will work throu | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00055557 | 6.048e-06 | 2016 | 2015-06-11 | C | 2 | 0.00055557 | 6.0475e-06
5395620 | 2015-06-11 11:01 | 2015-06-11 16:22 | 320.75 | 2 | 641.5 | 320.75 | 317.75 | 0.0019397 | 635.5 | 0.0019216 | 6.0475e-06 | Disconnection for Safety on Device NA | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 834941 | Advised hub and control. 546 BLUFF RANGITUMAU ROAD Masterton. Outage required from Fuses 7479 to replace a broken Pole with full crossarm components (High winds, Rotten Pole). Also straightened another pole. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.0019216 | 6.048e-06 | 2016 | 2015-06-11 | C | 2 | 0.0019216 | 6.0475e-06
5396524 | 2015-06-19 09:00 | 2015-06-19 12:30 | 210.3833 | 13 | 2734.9833 | 210.3833 | 207.3833 | 0.0082699 | 2695.9833 | 0.008152 | 3.9309e-05 | NAPA ID:10198 TP_MASTERTON GXP > AWATOITOI SUB > BLAIRLOGIE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 838126 | Repair badly spragged 11kV conductor and cut tree at pole 838126. Works location: Kaiwhata Rd, Masterton. WO 10156579. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-06-19 | b | 0.004076 | 1.9654e-05 | 2016 | 2015-06-19 | B | 13 | 0.008152 | 3.9309e-05
5396679 | 2015-06-11 13:50 | 2015-06-11 14:52 | 62 | 7 | 434 | 62 | 59 | 0.0013123 | 413 | 0.0012488 | 2.1166e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5396679 | Isolation required from Fuses 7551 to repair 2 broken binders. Also replaced 1 HT fus and Fuse Holder. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.0012488 | 2.1166e-05 | 2016 | 2015-06-11 | C | 7 | 0.0012488 | 2.1166e-05
5396707 | 2015-06-11 13:00 | 2015-06-11 13:36 | 35.5167 | 1047 | 36264.5833 | 34.6367 | 31.6367 | 0.10966 | 33123.5833 | 0.10016 | 0.0031659 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB8 | CB8 Trip on O/C B-C Phase. Lightning seen in area at the time. Feeder sectionalised / patrolled. NZ FIRE REPORT CLOSE TO 2 MIRO ST TX HIT BY LIGHTNING. ALSO TREES ON LINE AT BACK OF 26 RUAPEHU ST AS ADVISED BY RETAILER. All checked out OK. Relivened. | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.10016 | 0.0031659 | 2016 | 2015-06-11 | C | 1047 | 0.10016 | 0.0031659
5397986 | 2015-06-11 13:27 | 2015-06-11 17:01 | 213.8833 | 5 | 1069.4167 | 213.8833 | 210.8833 | 0.0032337 | 1054.4167 | 0.0031883 | 1.5119e-05 | Restore Supply on Device X574 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 775, 684, X574 | check if related to 5402508. Fuses Blown (2) at 775. Reloaded OK. Lightning. Fuses also tripped on circuit at 684 and X574. 5.31pm - smc advise FM has attended this job but Control did not sign him off. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0031883 | 1.5119e-05 | 2016 | 2015-06-11 | C | 5 | 0.0031883 | 1.5119e-05
5397996 | 2015-06-11 13:33 | 2015-06-12 06:51 | 1038.6833 | 1 | 1038.6833 | 1038.6833 | 1035.6833 | 0.0031407 | 1035.6833 | 0.0031317 | 3.0238e-06 | Restore Supply on Device X545 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708 | Trpping on 2HT fuses at 708. Reloaded OK. Lightning. Job redesignated 2R to enable reclosing of many fuses due to lightning. Tripping on 1 Fuse X4485 / reloaded 16:50. 3 Trippings on Fuses Transformer X1061 - reloaded 17:10. 1 Tripping Fuses Tran | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0031317 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.0031317 | 3.0238e-06
5398003 | 2015-06-11 13:37 | 2015-06-11 15:17 | 99.9333 | 5 | 499.6667 | 99.9333 | 96.9333 | 0.0015109 | 484.6667 | 0.0014655 | 1.5119e-05 | Restore Supply on Device X686 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2628 | advised joanne at hub low lines. Replaced 2x hv 3amp at t2628 advised paul to work through control - Lightning in area | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0014655 | 1.5119e-05 | 2016 | 2015-06-11 | C | 5 | 0.0014655 | 1.5119e-05
5398006 | 2015-06-11 13:37 | 2015-06-11 16:12 | 155 | 4 | 620 | 155 | 152 | 0.0018747 | 608 | 0.0018384 | 1.2095e-05 | Restore Supply on Device X690 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuse #119 | 2 x hv fuses replaced. less than 100amp - as per Paul Douglas. This customer is actually fed off tx X691. FM replaced fuses at Fuse #119. Sent e-mail to Kasey Chadwick. Transformer amended in outage to reflect the X691. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0018384 | 1.2095e-05 | 2016 | 2015-06-11 | C | 4 | 0.0018384 | 1.2095e-05
5398193 | 2015-06-11 13:52 | 2015-06-11 21:30 | 457.6167 | 3 | 1372.85 | 457.6167 | 454.6167 | 0.0041512 | 1363.85 | 0.004124 | 9.0713e-06 | Restore Supply on Device Y164 | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Y164 | Also check 5403004 - 16 TOKOMARU WEST ROAD also off tx Y164. Replaced 3x 3A HV fuses - Worked through control. Due to lightning strike. Nothing else repaired or replaced. All surrounding assets up to Powerco standard | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.004124 | 9.071e-06 | 2016 | 2015-06-11 | C | 3 | 0.004124 | 9.0713e-06
5398208 | 2015-06-11 13:54 | 2015-06-11 16:12 | 137.75 | 1 | 137.75 | 137.75 | 134.75 | 0.00041652 | 134.75 | 0.00040745 | 3.0238e-06 | Restore Supply on Device X2707 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 155B VALLEY ROAD WAITOTARA | FM advise: did a line patrol. nothing repaired or replaced. job turned out to be part of oms 5398006. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.00040745 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00040745 | 3.0238e-06
5398217 | 2015-06-11 13:57 | 2015-06-11 16:00 | 123.1333 | 1 | 123.1333 | 123.1333 | 120.1333 | 0.00037233 | 120.1333 | 0.00036325 | 3.0238e-06 | Restore Supply on Device X4155 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4155 | check if 5398569 is related2 Fuses tripped - reloaded OK. Lightning. 2 x 2 amp hv fuses. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00036325 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00036325 | 3.0238e-06
5402401 | 2015-06-30 09:08 | 2015-06-30 15:32 | 383.65 | 69 | 26471.85 | 383.65 | 380.65 | 0.080045 | 26264.85 | 0.079419 | 0.00020864 | NAPA ID:09306 TP_HINUERA GXP > TOWER ROAD SUB > BURWOOD RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9475/3 | Replace SD unit with Safelink - Generation supplied for School. Works location; Burwood Rd Matamata IR6462 | F3 | TAINUI ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-06-30 | b | 0.039709 | 0.00010432 | 2016 | 2015-06-30 | B | 69 | 0.079419 | 0.00020864
5402747 | 2015-06-11 15:05 | 2015-06-11 17:47 | 161.5167 | 77 | 12037.6667 | 156.3333 | 153.3333 | 0.036399 | 11806.6667 | 0.035701 | 0.00023283 | Restore Supply on Device 4832 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4832 |  | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.035701 | 0.00023283 | 2016 | 2015-06-11 | C | 77 | 0.035701 | 0.00023283
5406700 | 2015-06-11 15:48 | 2015-06-11 20:20 | 271.85 | 1 | 271.85 | 271.85 | 268.85 | 0.00082201 | 268.85 | 0.00081294 | 3.0238e-06 | Restore Supply on Device X1538 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1538 | faultman found blown fuse at transformer X1538 due to lightning. 3 X 3 amp HV fuses replaced. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.00081294 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00081294 | 3.0238e-06
5406711 | 2015-06-11 16:05 | 2015-06-11 16:55 | 50 | 2 | 100 | 50 | 47 | 0.00030238 | 94 | 0.00028423 | 6.0475e-06 | Restore Supply on Device X2708 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X708 | 3 HT Fuses tripped at Transformer X708. Reloaded. Lightning in area. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.00028423 | 6.048e-06 | 2016 | 2015-06-11 | C | 2 | 0.00028423 | 6.0475e-06
5406771 | 2015-06-11 16:54 | 2015-06-11 18:10 | 75.75 | 2 | 151.5 | 75.75 | 72.75 | 0.0004581 | 145.5 | 0.00043996 | 6.0475e-06 | Restore Supply on Device X1465 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1465 | 2 Fuses found tripped at Transformer X1465. Lightning strike - reloaded OK | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.00043996 | 6.048e-06 | 2016 | 2015-06-11 | C | 2 | 0.00043996 | 6.0475e-06
5406789 | 2015-06-11 17:04 | 2015-06-11 22:15 | 311.0833 | 1 | 311.0833 | 311.0833 | 308.0833 | 0.00094064 | 308.0833 | 0.00093157 | 3.0238e-06 | Restore Supply on Device Y17 | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 782439 | 2x 2A HV fuses and 1x DDO fuse. Due to lightning strike. Nothing else repaired or replaced. All surrounding assets up to Powerco standard | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00093157 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00093157 | 3.0238e-06
5406798 | 2015-06-11 17:10 | 2015-06-11 19:25 | 135.5 | 1 | 135.5 | 135.5 | 132.5 | 0.00040972 | 132.5 | 0.00040065 | 3.0238e-06 | Restore Supply on Device X4153 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x4153 | replace 2 x 2 amp fuses. cause: lightning. tx x4153 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00040065 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00040065 | 3.0238e-06
5407709 | 2015-06-11 18:34 | 2015-06-12 01:35 | 420.9333 | 189 | 33609.1 | 177.8259 | 174.8259 | 0.10163 | 33042.1 | 0.099911 | 0.00057149 | Restore Supply on Device D21 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 739530 | Car vs pole. black toyota alteza with reg # gmp 487. event # P021497064. eta required. Intersection of Douglas Road and SH43, Stratford. 50 m down Douglas Road, opposite engineering shop. tel: 0800 115 019. 7.44pm - FM advise eta of 15 min. Line was isola | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.099911 | 0.00057149 | 2016 | 2015-06-11 | C | 189 | 0.099911 | 0.00057149
5408330 | 2015-06-11 19:23 | 2015-06-11 20:23 | 59.6333 | 1 | 59.6333 | 59.6333 | 56.6333 | 0.00018032 | 56.6333 | 0.00017125 | 3.0238e-06 | Restore Supply on Device X2477 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2477 | replace 2 x 3 amp ht fuses. tx X2477. cause: lightning. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00017125 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00017125 | 3.0238e-06
5408612 | 2015-06-11 19:55 | 2015-06-12 11:52 | 957.2 | 77 | 10591.35 | 137.55 | 134.55 | 0.032026 | 10360.35 | 0.031327 | 0.00023283 | Restore Supply on Device 4832 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4832/2 | Recloser 4832/2 tripped on E/F flags, faultman cannot find fault on the line, this has been tripping since 10/06/15, faultman will be out in the morning with a thermal camera to see if they can locate the fault.Follow up job has been made OMS 5407687. Whe | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.031327 | 0.00023283 | 2016 | 2015-06-11 | C | 77 | 0.031327 | 0.00023283
5408868 | 2015-06-11 20:23 | 2015-06-11 21:25 | 62.35 | 1 | 62.35 | 62.35 | 59.35 | 0.00018853 | 59.35 | 0.00017946 | 3.0238e-06 | Restore Supply on Device T1/99 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T20487 | Replaced 2x 2A HV DDO fuses. Due to lightning strike. Noting else repaired or replaced. All surrounding assets up to Powerco standard | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.00017946 | 3.024e-06 | 2016 | 2015-06-11 | C | 1 | 0.00017946 | 3.0238e-06
5409472 | 2015-06-12 08:27 | 2015-06-12 08:57 | 30 | 1 | 30 | 30 | 27 | 9.0713e-05 | 27 | 8.1642e-05 | 3.0238e-06 | Restore Supply on Device X417 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771410 | 2x 2amp HV Fuses and 1x DDO at pole 771410. Worked through Control. No other assets repaired or replaced, all adjacent assets checked and are up to Powerco Standard. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-12 | c | 8.1642e-05 | 3.024e-06 | 2016 | 2015-06-12 | C | 1 | 8.1642e-05 | 3.0238e-06
5420999 | 2015-06-12 09:03 | 2015-06-12 09:46 | 43 | 46 | 1978 | 43 | 40 | 0.005981 | 1840 | 0.0055637 | 0.00013909 | Restore Supply on Device N3260 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713188 | May be related to OMS 5409468 2R requested - repairing HV jumper isloated, bucket truck required, advised only 1R work - and to go to the hub to request bucket truck. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.0055637 | 0.00013909 | 2016 | 2015-06-12 | C | 46 | 0.0055637 | 0.00013909
5421006 | 2015-06-12 08:24 | 2015-06-12 10:35 | 131.0667 | 7 | 917.4667 | 131.0667 | 128.0667 | 0.0027742 | 896.4667 | 0.0027107 | 2.1166e-05 | Restore Supply on Device T8/335 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P26159 | Tree through lines. 10.19am - 2R requested as extra man required to help remove pretty large tree from lines, Andrew advises they would get a contractor for this usually but apparently they don't like coming out to the location where this fault is. Andre | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.0027107 | 2.1166e-05 | 2016 | 2015-06-12 | C | 7 | 0.0027107 | 2.1166e-05
5421273 | 2015-06-11 16:59 | 2015-06-12 00:05 | 426.2667 | 2 | 852.5333 | 426.2667 | 423.2667 | 0.0025779 | 846.5333 | 0.0025597 | 6.0475e-06 | Restore Supply on Device X2981 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2981 | replaced TX : X2981. Cause:was hit by lightning. Nothing else repaired or replaced. Adjacent assets up to Powerco standard. 12.05pm Ben called to sign off job was not onsite, will call svs hub to get put onsite | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-11 | c | 0.0025597 | 6.048e-06 | 2016 | 2015-06-11 | C | 2 | 0.0025597 | 6.0475e-06
5421289 | 2015-06-12 11:40 | 2015-06-12 15:14 | 213.7167 | 23 | 4915.4833 | 213.7167 | 210.7167 | 0.014863 | 4846.4833 | 0.014655 | 6.9546e-05 | Restore Supply on Device T7/112 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P44089 | advised shan at hub line blowing in wind at pump at back of farm. 11kv line down - take out whole area to fix. Requesting a 2R approx 200 mtrs of 11kv conductor needed. *** oms 5431487 and oms 5421047 are part of this outage *** Isolated at Fuses R29 - L | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.014655 | 6.9546e-05 | 2016 | 2015-06-12 | C | 23 | 0.014655 | 6.9546e-05
5421341 | 2015-06-12 09:00 | 2015-06-12 11:58 | 178 | 59 | 10502 | 178 | 175 | 0.031756 | 10325 | 0.03122 | 0.0001784 | Restore Supply on Device TC564 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC 564 | Remount transformer TC564 due to slipping off steel mounts. Emergency shutdown. Issued own AP. | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.03122 | 0.0001784 | 2016 | 2015-06-12 | C | 59 | 0.03122 | 0.0001784
5421360 | 2015-06-12 10:30 | 2015-06-12 12:43 | 132.8 | 5 | 664 | 132.8 | 129.8 | 0.0020078 | 649 | 0.0019624 | 1.5119e-05 | Restore Supply on Device TP1784 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | S5947 | 2 HV fuses blown at S5947. Line Patrolled dead Magpie found in area. Suspect bird strike. reloaded & livened. Materials Used: 2 x 10 Amp. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.0019624 | 1.5119e-05 | 2016 | 2015-06-12 | C | 5 | 0.0019624 | 1.5119e-05
5431367 | 2015-06-12 10:41 | 2015-06-12 10:42 | 1 | 118 | 118 | 1 | -2 | 0.0003568 | 0 | 0 | 0.0003568 | Restore Supply on Device V61 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | V61 | Flags A, B, C O/C Line Not Patrolled. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0 | 0.0003568 | 2016 | 2015-06-12 | C | 118 | 0 | 0.0003568
5432107 | 2015-06-12 15:20 | 2015-06-12 17:23 | 123 | 3 | 369 | 123 | 120 | 0.0011158 | 360 | 0.0010886 | 9.0713e-06 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | TC4545 | Advised Tallia at Hub. 11:25am Customer is also advising they are experiencing no power to the cow shed and part power to the house. 11:41am advised Wayne of updated fault information. 12.03pm tahllia advised this was issued to Waihi fault man, CR put in | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.0010886 | 9.071e-06 | 2016 | 2015-06-12 | C | 3 | 0.0010886 | 9.0713e-06
5432113 | 2015-06-11 13:51 | 2015-06-12 20:44 | 1853.5833 | 77 | 972.25 | 12.6266 | 9.6266 | 0.0029399 | 741.25 | 0.0022414 | 0.00023283 | Restore Supply on Device 4832 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6194 | Monday, 15/05/15- 11kV Recloser 4832 has tripped numerous times over the last week. Discussed issue with Powerco Protection engineer, requested a physical check of CT leads done and download events, ASW. Recloser 4832 back in service. Faultmen waited arou | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-11 | c | 0.0022414 | 0.00023283 | 2016 | 2015-06-11 | C | 77 | 0.0022414 | 0.00023283
5432661 | 2015-06-12 12:15 | 2015-06-12 13:59 | 103.6333 | 921 | 23886.85 | 25.9358 | 22.9358 | 0.072228 | 21123.85 | 0.063873 | 0.0027849 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TD4 576 | CB 1 Trip No Flags from CB 1 at Welcome Bay. Flags from Recloser 9182. This recloser failed to open while operating under the auto back scheme, thus feeding into a possible fault. This recloser will need a protection review. Public reported to the FM a sm | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.063873 | 0.0027849 | 2016 | 2015-06-12 | C | 921 | 0.063873 | 0.0027849
5433923 | 2015-06-12 12:23 | 2015-06-12 13:04 | 41.5167 | 3 | 124.55 | 41.5167 | 38.5167 | 0.00037661 | 115.55 | 0.0003494 | 9.0713e-06 | Restore Supply on Device X687 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X687 | Transformer found with all fuses blown due to lightning overnight. Fault man found when driving to another job so wanted to resolve promptly. ASW | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-12 | c | 0.0003494 | 9.071e-06 | 2016 | 2015-06-12 | C | 3 | 0.0003494 | 9.0713e-06
5434618 | 2015-06-12 14:10 | 2015-06-12 14:11 | 1 | 64 | 64 | 1 | -2 | 0.00019352 | 0 | 0 | 0.00019352 | Restore Supply on Device V5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | V5 | RS V 5 Tripped C Ph O/C E/F A/R - Not Patrolled. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0 | 0.00019352 | 2016 | 2015-06-12 | C | 64 | 0 | 0.00019352
5434747 | 2015-06-12 14:37 | 2015-06-12 15:50 | 73.5 | 1 | 73.5 | 73.5 | 70.5 | 0.00022225 | 70.5 | 0.00021318 | 3.0238e-06 | Restore Supply on Device T2013 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7105 | 2 Fuses found blown at Fuses 7105 - Line Patrolled with no fault found - used 2 x 10 amp fuses | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.00021317 | 3.024e-06 | 2016 | 2015-06-12 | C | 1 | 0.00021318 | 3.0238e-06
5434763 | 2015-06-12 15:42 | 2015-06-12 17:15 | 92.7333 | 84 | 7789.6 | 92.7333 | 89.7333 | 0.023554 | 7537.6 | 0.022792 | 0.000254 | Restore Supply on Device 7208P | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20115 | 15 GLASGOW TERRACE FEILDING. 2.49pm called through svs hub and taken to control. Lines down found at Pole P20115 - Isolated at ABS J9 - Lines repaired Used 4x sleeves and 4 mtrs of conductor | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.022792 | 0.000254 | 2016 | 2015-06-12 | C | 84 | 0.022792 | 0.000254
5435051 | 2015-06-12 15:46 | 2015-06-12 19:25 | 219.05 | 31 | 6790.55 | 219.05 | 216.05 | 0.020533 | 6697.55 | 0.020252 | 9.3737e-05 | Restore Supply on Device TC1693 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 9397/4 | *** check if oms 5435671 - 7138 WAHAROA RD WEST is part of this outage *** On Arrival found switch 9397/4 in the open position Closed on load . Suspect due to switching earlier to restore network to normal configuration after upgrade work at Waharoa Sub. | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.020252 | 9.3737e-05 | 2016 | 2015-06-12 | C | 31 | 0.020252 | 9.3737e-05
5435266 | 2015-06-12 15:52 | 2015-06-13 10:39 | 1127.0333 | 103 | 91027 | 883.7573 | 880.7573 | 0.27524 | 90718 | 0.27431 | 0.00031145 | Restore Supply on Device CB1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04883 | Fault Between Fuses V16 and the Sub Line Cross coutry and weather making it impossible to access - work to continue in morning - Back feed installed via ABS V19 up to Fuses V16. Phil Barnes attended in morning - Isolations Completed, Isolated at ABS's V2, | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.27431 | 0.00031145 | 2016 | 2015-06-12 | C | 103 | 0.27431 | 0.00031145
5435388 | 2015-06-12 19:28 | 2015-06-12 23:05 | 217 | 6 | 1302 | 217 | 214 | 0.0039369 | 1284 | 0.0038825 | 1.8143e-05 | Restore Supply on Device 807 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 700847 | Outage required from ABS 4802 to replace a broken pole (Car accident). Pole replaced along with LV crossarm and associated hardware. Relivened OK. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.0038825 | 1.8143e-05 | 2016 | 2015-06-12 | C | 6 | 0.0038825 | 1.8143e-05
5435953 | 2015-06-12 18:31 | 2015-06-12 21:16 | 164.4 | 1183 | 75022.8 | 63.4174 | 60.4174 | 0.22685 | 71473.8 | 0.21612 | 0.0035771 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 800895 | HV line had gone through the LV line and also blown all streetlights. HV line replaced but LV will need to be replaced tomorrow with an electrician as he will need to check all properties to make sure there is no damage from high voltage. Tripping on CB | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.21612 | 0.0035771 | 2016 | 2015-06-12 | C | 1183 | 0.21612 | 0.0035771
5437601 | 2015-06-12 18:52 | 2015-06-13 15:20 | 1228.7667 | 115 | 35276.3667 | 306.751 | 303.751 | 0.10667 | 34931.3667 | 0.10562 | 0.00034773 | Restore Supply on Device 564 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 843691 | Tripping on Recloser CB 564 on B Phase O/C. Feeder patrolled and sectionalised with a conductor found down (across a big Gully) at Pole 843691. Impractical to repair during stormy conditions at night so a temp line break was installed at Pole 843691 to re | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.10562 | 0.00034773 | 2016 | 2015-06-12 | C | 115 | 0.10562 | 0.00034773
5437855 | 2015-06-12 19:05 | 2015-06-13 13:55 | 1129.4167 | 110 | 2258.5667 | 20.5324 | 17.5324 | 0.0068294 | 1928.5667 | 0.0058315 | 0.00033261 | Restore Supply on Device 6942 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Tripping on recloser CB6942 during storm. (Supplying Cheal Generation). Cheal advise happy to "Island" until daylight hours and weather calms down. Line Patrolled with no fault found. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.0058315 | 0.00033261 | 2016 | 2015-06-12 | C | 110 | 0.0058315 | 0.00033261
5438043 | 2015-06-12 19:26 | 2015-06-13 01:49 | 382.5167 | 278 | 29798.45 | 107.1887 | 104.1887 | 0.090103 | 28964.45 | 0.087582 | 0.00084061 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6610 | Line Down Clarke Road. span replaced along with broken LC cross arm. (Possible tornado). | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.087582 | 0.00084061 | 2016 | 2015-06-12 | C | 278 | 0.087582 | 0.00084061
5438934 | 2015-06-12 19:45 | 2015-06-12 22:50 | 185.45 | 764 | 52184.6 | 68.3045 | 65.3045 | 0.15779 | 49892.6 | 0.15086 | 0.0023102 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752692 | BKL CB7 tripped on E/F, B Phase. High winds in area caused a tree branch to break a conductor. Rejointed OK, 2 sleeves used. Relivened. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.15086 | 0.0023102 | 2016 | 2015-06-12 | C | 764 | 0.15086 | 0.0023102
5440437 | 2015-06-12 20:06 | 2015-06-12 23:25 | 199.1833 | 18 | 3585.3 | 199.1833 | 196.1833 | 0.010841 | 3531.3 | 0.010678 | 5.4428e-05 | Restore Supply on Device 2811 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 883 | Advised hub and control of 999 - Lines on fire due to trees. Fire comms F1862563. 2 HT fuses reloaded at 883. (20A). High winds | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.010678 | 5.4428e-05 | 2016 | 2015-06-12 | C | 18 | 0.010678 | 5.4428e-05
5440511 | 2015-06-12 20:42 | 2015-06-13 13:51 | 1028.6 | 371 | 83420.1 | 224.852 | 221.852 | 0.25224 | 82307.1 | 0.24888 | 0.0011218 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782655 | Cb 8 Tripped C Ph O/C E/F - Line down found during sectionlising - Isolated at Fuses 109, repairs to be carried out tomorrow. Line repaired between Pole 782655 & 782656 - Used 5mtrs of Conductor and 4 sleeves | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.24888 | 0.0011218 | 2016 | 2015-06-12 | C | 371 | 0.24888 | 0.0011218
5440887 | 2015-06-12 20:28 | 2015-06-12 20:32 | 3.9 | 66 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00019957 | Restore Supply on Device 266 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Taihape CB8 Recloser 266 tripped A Ph O/C, A/R not patrolled. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0 | 0.00019957 | 2016 | 2015-06-12 | C | 66 | 0 | 0.00019957
5441267 | 2015-06-12 20:44 | 2015-06-14 12:15 | 2370.5333 | 77 | 10450.3 | 135.7182 | 132.7182 | 0.031599 | 10219.3 | 0.030901 | 0.00023283 | Restore Supply on Device 4832 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4832 | Tripping on Recloser 4832 on O/C, E/F during stormy conditions. (Ongoing fault). Feeder sectionalised but only managed to liven to Fuses 4946. Unable to locate fault - to be fully patrolled during daylight hours. 13/6 6.36pm - FM advise: power remains off | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.030901 | 0.00023283 | 2016 | 2015-06-12 | C | 77 | 0.030901 | 0.00023283
5441570 | 2015-06-12 21:06 | 2015-06-13 04:27 | 441.0333 | 252 | 106989.1 | 424.5599 | 421.5599 | 0.32351 | 106233.1 | 0.32122 | 0.00076199 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | U12683 | Tairua CB 3 Recloser 9643 tripped A Ph O/C, L/O. Feeder sectionalised with fault isolated to between ABS's IC352, IC2115 & IC333 ( no back feeds ). Turns out branch found on line at pole U12683 just beyond ABS IC333. Branch removed all service restored, w | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.32122 | 0.00076199 | 2016 | 2015-06-12 | C | 252 | 0.32122 | 0.00076199
5445032 | 2015-06-12 21:34 | 2015-06-13 02:29 | 294.6 | 282 | 36252.9167 | 128.5564 | 125.5564 | 0.10962 | 35406.9167 | 0.10706 | 0.0008527 | Restore Supply on Device RC01 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12812 | TWR CB1 Recloser RC01 ( no flags ) tripped L/O. Feeder sectionalised & blown H/V fuse x 1 found at Fuses FP668. Isolation at fuses FP668 ( no back feeds ) with all other service restored. Patrol found stay wire on H/V bushing of transformer TC2416, stay | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.10706 | 0.0008527 | 2016 | 2015-06-12 | C | 282 | 0.10706 | 0.0008527
5445788 | 2015-06-12 23:18 | 2015-06-13 02:16 | 177.5833 | 18 | 3196.5 | 177.5833 | 174.5833 | 0.0096655 | 3142.5 | 0.0095022 | 5.4428e-05 | Restore Supply on Device TE3-007 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 217630 | Advised hub of 999 - Found line down behind house in the bushes that is sparking. Line 1 x down at pole 217630, brought down by tree, isolation at fuses SE3 034 ( no back feed ). Line repaired, service restored. NOTE Transformer TE3 007 L/V fuses left is | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-06-12 | c | 0.0095022 | 5.4428e-05 | 2016 | 2015-06-12 | C | 18 | 0.0095022 | 5.4428e-05
5446004 | 2015-06-12 23:22 | 2015-06-13 01:22 | 119.7833 | 20 | 2395.6667 | 119.7833 | 116.7833 | 0.0072439 | 2335.6667 | 0.0070625 | 6.0475e-05 | Restore Supply on Device MA574 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718388 | Broken conductor repaired beyond fuses MA574. Cause unknown. 2 Sleeves used. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.0070625 | 6.0475e-05 | 2016 | 2015-06-12 | C | 20 | 0.0070625 | 6.0475e-05
5446065 | 2015-06-12 19:16 | 2015-06-13 15:53 | 1236.8333 | 143 | 74848.8667 | 523.4186 | 520.4186 | 0.22633 | 74419.8667 | 0.22503 | 0.0004324 | Restore Supply on Device 1297 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784217 | Tripping on CB2032 Waterworks Recloser. (Some delay in patrolling as no Comms to CB). Feeder patrolled / sectionalised and livened up to Fuses 838. Impractical to patrol any further during stormy conditions at night. (Majority line cross country). To be | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-12 | c | 0.22503 | 0.0004324 | 2016 | 2015-06-12 | C | 143 | 0.22503 | 0.0004324
5446289 | 2015-06-13 01:39 | 2015-06-13 01:41 | 1.2167 | 530 | 644.8333 | 1.2167 | -1.7833 | 0.0019498 | 0 | 0 | 0.0016026 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 5 | at 01:39 Kerepehi Sub, CB 5 Managatarata Feeder, Tripped, A + B O/C, Auto Reclosed. Line Patrol carried out. No fault found. Suspect line clash due to high winds last night. Grant Jordan Attended. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-13 | c | 0 | 0.0016026 | 2016 | 2015-06-13 | C | 530 | 0 | 0.0016026
5447937 | 2015-06-13 02:50 | 2015-06-13 15:29 | 759.0167 | 347 | 68064.55 | 196.1514 | 193.1514 | 0.20581 | 67023.55 | 0.20266 | 0.0010492 | Restore Supply on Device 2 | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761302 | Tripping on CB6616 on Phase B-C O/C, E/F. Feeder patrolled with broken crossarm found down York Rd. (Isolation made at Fuses 5525. Remainder feeder restored. Repairs to be carried out during daylight hours (too dangerous during storm). Broken Cross arm fo | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.20266 | 0.0010492 | 2016 | 2015-06-13 | C | 347 | 0.20266 | 0.0010492
5448430 | 2015-06-13 05:04 | 2015-06-13 14:28 | 564.2 | 441 | 132352.8 | 300.1197 | 297.1197 | 0.4002 | 131029.8 | 0.3962 | 0.0013335 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 217445 | at 05:04, Tauranga GXP, CB 11 Kaimai Drive Feeder, Recloser 9275 Tripped, O/C, E/F, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Found tree through lines at Pole 217445. Isolated Lines at ABS SE3-004, SE3-016, SE3-034, 9270/1 & 92 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-06-13 | c | 0.3962 | 0.0013335 | 2016 | 2015-06-13 | C | 441 | 0.3962 | 0.0013335
5450631 | 2015-06-13 11:40 | 2015-06-13 13:00 | 80.2167 | 42 | 3369.1 | 80.2167 | 77.2167 | 0.010187 | 3243.1 | 0.0098064 | 0.000127 | Restore Supply on Device 5303E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 723988 | check 5450640 240 Rakaupiko Road & 545609 371 Rakaupiko Road part powers & 5450652 264 Rakaupiko Road & 5450655 285 Rakaupiko Road and 5451179. Damaged Cross arm found at Pole 723988 - Isolated at Fuses LI708 - Crossarm replaced - Used 1x Complete HV Cros | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.0098064 | 0.000127 | 2016 | 2015-06-13 | C | 42 | 0.0098064 | 0.000127
5451049 | 2015-06-13 09:20 | 2015-06-13 17:29 | 489.4167 | 1 | 489.4167 | 489.4167 | 486.4167 | 0.0014799 | 486.4167 | 0.0014708 | 3.0238e-06 | Restore Supply on Device 2222W | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4727 | 2 fuses found blown at Fuses 4551 - used 2 x 8 amp fuses | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.0014708 | 3.024e-06 | 2016 | 2015-06-13 | C | 1 | 0.0014708 | 3.0238e-06
5451152 | 2015-06-13 09:51 | 2015-06-13 17:15 | 444.3667 | 3 | 1333.1 | 444.3667 | 441.3667 | 0.004031 | 1324.1 | 0.0040038 | 9.0713e-06 | Restore Supply on Device X1266 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2934 | 2 fuses found blown at Fuses 2934 - line patrolled with no fault found - used 2 x 6amp fuses | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-13 | c | 0.0040038 | 9.071e-06 | 2016 | 2015-06-13 | C | 3 | 0.0040038 | 9.0713e-06
5451219 | 2015-06-13 08:16 | 2015-06-13 16:47 | 511.0167 | 11 | 5621.1833 | 511.0167 | 508.0167 | 0.016997 | 5588.1833 | 0.016897 | 3.3261e-05 | Restore Supply on Device X2848 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4172 | 1 fuse found blown at FABS 4172 - used 1 x 15 amp HV fuse. FM advise: 5 x transformers from this fuse would have been affected and those customer would have been without power. FM did sign job off with Control. Dispatch clicked FM offsite. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.016897 | 3.3261e-05 | 2016 | 2015-06-13 | C | 11 | 0.016897 | 3.3261e-05
5451642 | 2015-06-13 12:41 | 2015-06-13 13:18 | 37.0833 | 15 | 556.25 | 37.0833 | 34.0833 | 0.001682 | 511.25 | 0.0015459 | 4.5356e-05 | Restore Supply on Device 708 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 708 | Damaged Dead End Found at Fuses 708 - Isolated at Fuses 708 - Dead end replaced - used 1 x 16mm copper dead end. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-13 | c | 0.0015459 | 4.5356e-05 | 2016 | 2015-06-13 | C | 15 | 0.0015459 | 4.5356e-05
5452338 | 2015-06-13 13:20 | 2015-06-13 17:59 | 278.8333 | 606 | 4480 | 7.3927 | 4.3927 | 0.013546 | 2662 | 0.0080493 | 0.0018324 | Restore Supply on Device TD2-040 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209715 | at 13:20, Omokoroa Sub, CB 2 Whakamarama Feeder, Tripped, A + B O/C, Auto Reclosed. Call came in of loud bang. Faultmen dispatched. Found broken jumper at Pole 209715. Isolated Lines at ABS SD3-043, SD3-095 & OMO CB 5. Backfeed supplied from OMO 3, Closed | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-06-13 | c | 0.0080493 | 0.0018324 | 2016 | 2015-06-13 | C | 606 | 0.0080493 | 0.0018324
5452825 | 2015-06-13 18:56 | 2015-06-13 19:39 | 43.4 | 96 | 4166.4 | 43.4 | 40.4 | 0.012598 | 3878.4 | 0.011727 | 0.00029028 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 814533 | Also -20, 9, 6 & 2 Hardie Grove. HV outage required between CB C911, ABS S593 and S563 to reapir a blown Jumper. Backfeed at ABS S589. Relivened OK. | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.011727 | 0.00029028 | 2016 | 2015-06-13 | C | 96 | 0.011727 | 0.00029028
5453365 | 2015-06-13 17:34 | 2015-06-13 20:38 | 183.65 | 5 | 918.25 | 183.65 | 180.65 | 0.0027766 | 903.25 | 0.0027312 | 1.5119e-05 | Restore Supply on Device 4260T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733889 | Check to see if 5453527 - 75 Neill Rd is related to this job. Outage required from Fuses 4955 to replace a broken crossarm at Pole 733889. Associated crossarm hardware replaced along with 3 X 16A Transformer Fuses. Relivened OK. Windy conditions. Alte | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-13 | c | 0.0027312 | 1.5119e-05 | 2016 | 2015-06-13 | C | 5 | 0.0027312 | 1.5119e-05
5453471 | 2015-06-13 18:06 | 2015-06-13 20:35 | 148.7 | 9 | 1336.6333 | 148.5148 | 145.5148 | 0.0040417 | 1309.6333 | 0.00396 | 2.7214e-05 | Restore Supply on Device X2707 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2708 | Short outage required from fuses 119 to cutaway live wires (Make safe) from transformer X2708 which had a broken Fuse Crossarm. Repairs to be carried out during daylight hours. Referral job requested. 5453882. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-13 | c | 0.00396 | 2.7214e-05 | 2016 | 2015-06-13 | C | 9 | 0.00396 | 2.7214e-05
5453882 | 2015-06-15 13:05 | 2015-06-15 15:10 | 125 | 10 | 1250 | 125 | 122 | 0.0037797 | 1220 | 0.003689 | 3.0238e-05 | Referral: Restore Supply on Device X2707 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2708 | 2R Transformer X2708 has been cutaway due to broken fuse arm. To be repaired during daylight hours. Refer B.Englebretsen. Replaced HV Arm, 3x HV Fuse Holders with 2Amp links, Arm Brace, Connectors, & Conductor | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-15 | c | 0.003689 | 3.0238e-05 | 2016 | 2015-06-15 | C | 10 | 0.003689 | 3.0238e-05
5454050 | 2015-06-14 00:15 | 2015-06-14 01:05 | 50.7167 | 72 | 3651.6 | 50.7167 | 47.7167 | 0.011042 | 3435.6 | 0.010388 | 0.00021771 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7438401 | Report from Sarah Fleming 06 7554650. Lines sparking when wind gusts. 284 Corbett Rd. Inspection found problem caused by broken Insulator. Isolation required O/H HV between ABS 292 and 371 with backfeed at CB8819/2. Insulator replaced, rebound and livene | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-06-14 | c | 0.010388 | 0.00021771 | 2016 | 2015-06-14 | C | 72 | 0.010388 | 0.00021771
5454229 | 2015-06-14 01:16 | 2015-06-14 03:29 | 133.2 | 750 | 67886.05 | 90.5147 | 87.5147 | 0.20527 | 65636.05 | 0.19847 | 0.0022678 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB6 | A/R of CB 6 A, B, C O/C. This was the precurser to OMS outage 5454984 Tree through line at pole 208599. CB 6 Trip E/F Tree through the line at pole 208599 braking crossarm. moved insulator in on crossarm to get power restored. Isolation at ABS SB2-047, AB | F3 | MURAL TOWN | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-06-14 | c | 0.19847 | 0.0022678 | 2016 | 2015-06-14 | C | 750 | 0.19847 | 0.0022678
5464256 | 2015-06-14 04:36 | 2015-06-14 06:19 | 103.8833 | 302 | 19543.8667 | 64.7148 | 61.7148 | 0.059096 | 18637.8667 | 0.056356 | 0.00091318 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9606 | Recloser 9606 Trip Flags B, C O/C LFI's flashing up Busby Rd. Line Patrolled No Fault found. FM also looking at a possible fault on the 33kV line from AON to KPT subs. Faultmen did find a tree that had fallen and looked as if it would have hit the 11kV Li | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-06-14 | c | 0.056356 | 0.00091318 | 2016 | 2015-06-14 | C | 302 | 0.056356 | 0.00091318
5464567 | 2015-06-14 05:57 | 2015-06-14 05:58 | 1.5 | 8475 | 12712.5 | 1.5 | -1.5 | 0.03844 | 0 | 0 | 0.025626 | Restore Supply on Device 202 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 122 | at 05:56 Greerton Sub, CB 122 Tripped, Ph B O/C, E/F, L/O. CB 202 Tripped, E/F, Auto Reclosed. Kauri Point Sub, CB 62 Flagged with Ph B & C O/C. Aongatete Sub CB 42 Flagged with Ph A O/C. Faultmen dispatched & investigation began on CB 122 33kV Line. Patr | F1,F2,F3 | GREERTON202-AONGATETE82 33KV | TAURANGA 31 | Tauranga | GREERTON | Eastern Electricity | POWERCO | 2015-06-14 | c | 0 | 0.025626 | 2016 | 2015-06-14 | C | 8475 | 0 | 0.025626
5473050 | 2015-06-14 07:05 | 2015-06-14 09:03 | 117.7833 | 849 | 69931.05 | 82.3687 | 79.3687 | 0.21145 | 67384.05 | 0.20375 | 0.0025672 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 4650/5 Trip, E/F, O/C A,B,C Phase Sectionalised and Patrolled. No fault found. 1x 10Amp fuse link was found blown at Fuses 4146 and was replaced | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-06-14 | c | 0.20375 | 0.0025672 | 2016 | 2015-06-14 | C | 849 | 0.20375 | 0.0025672
5474581 | 2015-06-14 08:01 | 2015-06-14 10:40 | 158.8667 | 299 | 29366.8167 | 98.2168 | 95.2168 | 0.088798 | 28469.8167 | 0.086086 | 0.0009041 | Restore Supply on Device 6561-2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720880 | Repaced 11kV Insulator, Pin, & 2 metres bare Cu. Binder. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-06-14 | c | 0.086086 | 0.0009041 | 2016 | 2015-06-14 | C | 299 | 0.086086 | 0.0009041
5475395 | 2015-06-14 14:20 | 2015-06-14 14:24 | 4 | 1 | 4 | 4 | 1 | 1.2095e-05 | 1 | 3.0238e-06 | 3.0238e-06 | Restore Supply on Device 2173T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 6194 | ABS switch 6194 cnr Rawhitiroa & Oru road, the voltage is fluctuating all the time, has put red tag on switch and spoken to control and this will get looked into this week customer has opened back feed & closed back feed and checked switch and power is al | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-14 | c | 3.024e-06 | 3.024e-06 | 2016 | 2015-06-14 | C | 1 | 3.0238e-06 | 3.0238e-06
5475421 | 2015-06-14 12:05 | 2015-06-14 12:08 | 3 | 252 | 756 | 3 | 0 | 0.002286 | 0 | 0 | 0.00076199 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 751645 | Waratah standards on HV Lines. Also attended by Craig Wellington to minimise shutdown time. Plastic waratah removed with hotstick after backfeed and isolation carried out. NDR #2015N00033 | F3 | BROOKLANDS 10 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-14 | c | 0 | 0.00076199 | 2016 | 2015-06-14 | C | 252 | 0 | 0.00076199
5475868 | 2015-06-15 02:06 | 2015-06-15 02:51 | 44.7833 | 3 | 134.35 | 44.7833 | 41.7833 | 0.00040624 | 125.35 | 0.00037903 | 9.0713e-06 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731487 | 12.33pm - advise smc. Insulator redrilled in crossarm & re attached 1x 5Amp Link replaced. 3:18pm left site 1/2 hour ago | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.00037903 | 9.071e-06 | 2016 | 2015-06-15 | C | 3 | 0.00037903 | 9.0713e-06
5475969 | 2015-06-14 14:13 | 2015-06-14 15:12 | 58.5333 | 2 | 117.0667 | 58.5333 | 55.5333 | 0.00035398 | 111.0667 | 0.00033584 | 6.0475e-06 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 806372 | Repaired corroded jumper. Used 2x conductor joints | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-14 | c | 0.00033584 | 6.048e-06 | 2016 | 2015-06-14 | C | 2 | 0.00033584 | 6.0475e-06
5476295 | 2015-06-14 15:48 | 2015-06-14 18:12 | 144.3167 | 25 | 3607.6 | 144.304 | 141.304 | 0.010909 | 3532.6 | 0.010682 | 7.5594e-05 | Restore Supply on Device 2292T | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 738505 | Broken Crossarm & Lines Down. Materials used: HV crossarm, 3x Pins & Insulators, 3x HV Fuses, 3x 3Amp HV Links, Associated connectors & Hardware | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-14 | c | 0.010682 | 7.5594e-05 | 2016 | 2015-06-14 | C | 25 | 0.010682 | 7.5594e-05
5476740 | 2015-06-15 03:57 | 2015-06-15 04:31 | 33.1833 | 1 | 33.1833 | 33.1833 | 30.1833 | 0.00010034 | 30.1833 | 9.1267e-05 | 3.0238e-06 | Restore Supply on Device T7/424 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-15 | c | 9.1267e-05 | 3.024e-06 | 2016 | 2015-06-15 | C | 1 | 9.1267e-05 | 3.0238e-06
5476750 | 2015-06-15 05:42 | 2015-06-15 08:25 | 163 | 161 | 16387 | 101.7826 | 98.7826 | 0.04955 | 15904 | 0.04809 | 0.00048683 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P17214 | Recloser O10 A/R, L/O, E/F, O/C. Sectionalised & Patrolled. Broken Insulator found at Pole P17214. Pin, Insulator, & Binder replaced. Crossarm burnt and will be defected. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.04809 | 0.00048682 | 2016 | 2015-06-15 | C | 161 | 0.04809 | 0.00048683
5477035 | 2015-06-15 06:46 | 2015-06-15 10:00 | 194.2 | 209 | 619.8 | 2.9656 | -0.03445 | 0.0018741 | 0 | 0 | 0.00063197 | Restore Supply on Device NG376 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712440 | Blown Lightning arrestor at Pole 712440. Cut away and power restored. To be defected and repaired at a later date | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0 | 0.00063197 | 2016 | 2015-06-15 | C | 209 | 0 | 0.00063197
5477268 | 2015-06-15 07:56 | 2015-06-15 15:32 | 456.1667 | 73 | 33300.1667 | 456.1667 | 453.1667 | 0.10069 | 33081.1667 | 0.10003 | 0.00022073 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 1942 Parewanui Road | is 5477288 AND 5479097 linked. 2x Blown fuse links at Fuses 4203. Replaced to 2x fuse carriers and 2x 30Amp Links. Farmer reported seeing bird hit power lines | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.10003 | 0.00022074 | 2016 | 2015-06-15 | C | 73 | 0.10003 | 0.00022073
5477271 | 2015-06-15 07:40 | 2015-06-15 10:56 | 195.55 | 1 | 195.55 | 195.55 | 192.55 | 0.0005913 | 192.55 | 0.00058223 | 3.0238e-06 | Restore Supply on Device T2/99 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | E90 | 2x 6Amp Fuse Links found blown. Suspect Bird Strike where line crosses river. | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.00058223 | 3.024e-06 | 2016 | 2015-06-15 | C | 1 | 0.00058223 | 3.0238e-06
5477279 | 2015-06-15 07:45 | 2015-06-15 08:49 | 64.3 | 2 | 128.6 | 64.3 | 61.3 | 0.00038886 | 122.6 | 0.00037071 | 6.0475e-06 | Restore Supply on Device TC2993 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP580 | 2 X 6A Fuses replaced Suspect Bird Strike | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-06-15 | c | 0.00037071 | 6.048e-06 | 2016 | 2015-06-15 | C | 2 | 0.00037071 | 6.0475e-06
5477854 | 2015-06-15 08:05 | 2015-06-15 10:24 | 139.0333 | 545 | 42541.3667 | 78.0576 | 75.0576 | 0.12863 | 40906.3667 | 0.12369 | 0.0016479 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 767922 | CB2 Trip, No flags. Broken Insulator had burnt crossarm. Materials used: HV Crossarm, 3Pins & Insulators, 2x Arm Braces, Cu. Binder, Misc Bolts. | F3 | DURIE HILL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.12369 | 0.001648 | 2016 | 2015-06-15 | C | 545 | 0.12369 | 0.0016479
5478734 | 2015-06-26 09:20 | 2015-06-26 15:39 | 379 | 52 | 19708 | 379 | 376 | 0.059592 | 19552 | 0.059121 | 0.00015724 | NAPA ID:10090 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse Link 893 | IR6981 Moawhango Reconstruction. Install new pole to replace pole 786804 (11kV DDO 2835). Replace pole 786805 with a new H-Pole structure. Run new conductor from this H-pole to another across the gully (see plans). Works location: Taihape Napier Rd Moawha | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-26 | b | 0.02956 | 7.8618e-05 | 2016 | 2015-06-26 | B | 52 | 0.059121 | 0.00015724
5478840 | 2015-06-15 09:40 | 2015-06-15 17:26 | 466 | 3 | 1398 | 466 | 463 | 0.0042272 | 1389 | 0.0042 | 9.0713e-06 | Restore Supply on Device SA2-022 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC2-022 | Found 2 fuses blowen. Tested & repaired faulty cable Relivened | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-06-15 | c | 0.0042 | 9.071e-06 | 2016 | 2015-06-15 | C | 3 | 0.0042 | 9.0713e-06
5479539 | 2015-07-01 09:33 | 2015-07-01 13:15 | 222.05 | 13 | 2886.65 | 222.05 | 219.05 | 0.0087285 | 2847.65 | 0.0086106 | 3.9309e-05 | NAPA ID:09434 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV L77 | Remove 1pole of 2pole structure replace transformer. Works location; Tangimoana Rd. WO 10159772 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0043053 | 1.9654e-05 | 2016 | 2015-07-01 | B | 13 | 0.0086106 | 3.9309e-05
5479541 | 2015-07-01 09:03 | 2015-07-01 15:51 | 408.0667 | 28 | 11425.8667 | 408.0667 | 405.0667 | 0.034549 | 11341.8667 | 0.034295 | 8.4665e-05 | NAPA ID:07500 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 412 | Project number IR6978 Rangikura Reconstruction Replace poles Karakahi Road poles 772757 to 772802. Works location: Karakahi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-01 | b | 0.017148 | 4.2333e-05 | 2016 | 2015-07-01 | B | 28 | 0.034295 | 8.4665e-05
5479568 | 2015-07-01 08:46 | 2015-07-01 14:45 | 358.9833 | 13 | 4666.7833 | 358.9833 | 355.9833 | 0.014111 | 4627.7833 | 0.013993 | 3.9309e-05 | NAPA ID:09797 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7116 | tree work near overhead lines between pole numbers 827602 and 827620. Works location: Ngaumu Rd Masterton. PPPD 43228 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0069967 | 1.9654e-05 | 2016 | 2015-07-01 | B | 13 | 0.013993 | 3.9309e-05
5479688 | 2015-06-18 09:30 | 2015-06-18 12:18 | 168.2 | 30 | 5046 | 168.2 | 165.2 | 0.015258 | 4956 | 0.014986 | 9.0713e-05 | NAPA ID:10331 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 782415 | Replace 11kv pole 784215 broken when a tree fell onto the line pole is being held up with ropes and a stay wire. Works location: Rangitautau East Rd Kai Iwi. WO 10200995 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-06-18 | b | 0.0074929 | 4.5356e-05 | 2016 | 2015-06-18 | B | 30 | 0.014986 | 9.0713e-05
5479992 | 2015-06-01 09:45 | 2015-06-01 13:00 | 195 | 40 | 7800 | 195 | 192 | 0.023585 | 7680 | 0.023222 | 0.00012095 | NAPA ID:09995 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1256 | Replace H/V Crossarms and T/X. Works location: Hwy 27. WO 10147831 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-01 | b | 0.011611 | 6.0475e-05 | 2016 | 2015-06-01 | B | 40 | 0.023222 | 0.00012095
5480070 | 2015-06-15 17:06 | 2015-06-15 17:07 | 1 | 210 | 210 | 1 | -2 | 0.00063499 | 0 | 0 | 0.00063499 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | A/R, E/F, O/C. Not patrolled, No fault found | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0 | 0.00063499 | 2016 | 2015-06-15 | C | 210 | 0 | 0.00063499
5480286 | 2015-06-15 23:35 | 2015-06-16 00:38 | 62.8167 | 8 | 496.1667 | 62.0208 | 59.0208 | 0.0015003 | 472.1667 | 0.0014277 | 2.419e-05 | Restore Supply on Device TC5570 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc4165 | at 23:35, Thames Sub, CB 2 Totara Feeder. Faultman was called to no power calls. Found Fuse had blown at FC4165. upon inspection looked OK. called control to reload reliven. On trying to close the fuse in, it blew again, and the jumper on the next fuse ca | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-06-15 | c | 0.0014277 | 2.419e-05 | 2016 | 2015-06-15 | C | 8 | 0.0014277 | 2.419e-05
5480370 | 2015-06-15 17:48 | 2015-06-15 19:56 | 128.1333 | 6 | 768.8 | 128.1333 | 125.1333 | 0.0023247 | 750.8 | 0.0022702 | 1.8143e-05 | Restore Supply on Device FC2111 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2111 | Marty Keenan Attended. Reloaded, Relivened 2x 15A Fuses at Fuses FC2111. All OK. 2x HV Fuses Replaced | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-06-15 | c | 0.0022702 | 1.8143e-05 | 2016 | 2015-06-15 | C | 6 | 0.0022702 | 1.8143e-05
5480641 | 2015-06-15 21:59 | 2015-06-16 01:11 | 191.75 | 47 | 6632.5333 | 141.1177 | 138.1177 | 0.020055 | 6491.5333 | 0.019629 | 0.00014212 | Restore Supply on Device X1747 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1747 | 136 Concord Line, Wanganui. 8.47pm - called through to svshub. taken to control. 10.11pm - requesting 2R - broken crossarm on the tx 11kv, needs to be replaced tonight. Isolated at ABS's 680 and 606 with back feed via ABS 716 Cross arm replaced - Used 1x | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.019629 | 0.00014212 | 2016 | 2015-06-15 | C | 47 | 0.019629 | 0.00014212
5480917 | 2015-06-30 09:00 | 2015-06-30 14:25 | 325.0167 | 42 | 13650.7 | 325.0167 | 322.0167 | 0.041276 | 13524.7 | 0.040895 | 0.000127 | NAPA ID:10010 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP 610 | REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-06-30 | b | 0.020448 | 6.3499e-05 | 2016 | 2015-06-30 | B | 42 | 0.040895 | 0.000127
5480952 | 2015-07-02 10:00 | 2015-07-02 11:29 | 88.5333 | 128 | 11332.2667 | 88.5333 | 85.5333 | 0.034266 | 10948.2667 | 0.033105 | 0.00038704 | NAPA ID:07493 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 726 | Project number IR6978 Rangikura Reconstruction Replace cross arms Koihi Road between Recloser 573 ,links 836 & fuses 090 Koihi Rd & 412 Karakahi Rd. Works location: Main South Rd Waverley. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-02 | b | 0.016552 | 0.00019352 | 2016 | 2015-07-02 | B | 128 | 0.033105 | 0.00038704
5480959 | 2015-07-01 09:24 | 2015-07-01 15:14 | 350.2833 | 38 | 13310.7667 | 350.2833 | 347.2833 | 0.040249 | 13196.7667 | 0.039904 | 0.0001149 | NAPA ID:09598 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS 662 | Tree trimming between poles 774988 and 774972 and near pole 773003. Works location; Ridge Rd Waitotara. PPPD 53712 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-01 | b | 0.019952 | 5.7451e-05 | 2016 | 2015-07-01 | B | 38 | 0.039904 | 0.0001149
5480965 | 2015-07-02 09:38 | 2015-07-02 14:52 | 314 | 121 | 36725.2 | 303.514 | 300.514 | 0.11105 | 36362.2 | 0.10995 | 0.00036588 | NAPA ID:09949 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1376 | Remove temp ABS 15, replace crossarms various locations. Works location: Hwy 1 Tokoroa. WO 10163039 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-07-02 | b | 0.054975 | 0.00018294 | 2016 | 2015-07-02 | B | 121 | 0.10995 | 0.00036588
5481695 | 2015-07-03 09:01 | 2015-07-03 14:01 | 300.1 | 28 | 8402.8 | 300.1 | 297.1 | 0.025408 | 8318.8 | 0.025154 | 8.4665e-05 | NAPA ID:07501 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 412 | Project number IR6978 Rangikura Reconstruction Replace poles Karakahi Road poles 772802 to 7722813. Works location: Karakahi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-03 | b | 0.012577 | 4.2333e-05 | 2016 | 2015-07-03 | B | 28 | 0.025154 | 8.4665e-05
5481698 | 2015-07-01 10:30 | 2015-07-01 12:51 | 140.6333 | 42 | 5246.6 | 124.919 | 121.919 | 0.015864 | 5120.6 | 0.015483 | 0.000127 | NAPA ID:09825 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 355 | to change badly spalled pole reported by consumer at 1135 richmond rd. spalled from top to bottom. Works location: Richmond Rd Inglewood. WO 10146070 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0077417 | 6.3499e-05 | 2016 | 2015-07-01 | B | 42 | 0.015483 | 0.000127
5481701 | 2015-07-01 09:00 | 2015-07-01 14:25 | 325 | 46 | 14950 | 325 | 322 | 0.045205 | 14812 | 0.044788 | 0.00013909 | NAPA ID:10012 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-014 | REPLACE POLES AND ARMS AND RECON FEEDER WIRE TO IODINE. Works location: Crawford Rd. WO 10166701 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-07-01 | b | 0.022394 | 6.9546e-05 | 2016 | 2015-07-01 | B | 46 | 0.044788 | 0.00013909
5481814 | 2015-07-01 10:50 | 2015-07-01 15:11 | 260.5167 | 5 | 1302.5833 | 260.5167 | 257.5167 | 0.0039387 | 1287.5833 | 0.0038933 | 1.5119e-05 | NAPA ID:09470 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4119T | Replace all xarms fuse's & upgrade earths on Tx 4119T structure, put existing single phase Tx back up | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0019467 | 7.559e-06 | 2016 | 2015-07-01 | B | 5 | 0.0038933 | 1.5119e-05
5481835 | 2015-07-03 09:15 | 2015-07-03 10:38 | 83.2 | 3 | 249.6 | 83.2 | 80.2 | 0.00075473 | 240.6 | 0.00072752 | 9.0713e-06 | NAPA ID:09487 TP_STRATFORD GXP > ELTHAM SUB > NGAERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6259 | Increase height of HV spur line between poles 738563 &738562. Works location: Wingrove Rd Stratford WO 30002186. Job was cancelled due to hydrolics failure on the truck, will reapply to do the work. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-03 | b | 0.00036376 | 4.536e-06 | 2016 | 2015-07-03 | B | 3 | 0.00072752 | 9.0713e-06
5481839 | 2015-06-16 09:41 | 2015-06-16 10:45 | 64.2 | 13 | 834.6 | 64.2 | 61.2 | 0.0025236 | 795.6 | 0.0024057 | 3.9309e-05 | Restore Supply on Device WH831 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH831 | 2 X HV Fuses Replaced | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-06-16 | c | 0.0024057 | 3.9309e-05 | 2016 | 2015-06-16 | C | 13 | 0.0024057 | 3.9309e-05
5482205 | 2015-06-16 11:22 | 2015-06-16 14:32 | 190.2667 | 1 | 190.2667 | 190.2667 | 187.2667 | 0.00057532 | 187.2667 | 0.00056625 | 3.0238e-06 | Restore Supply on Device 3116T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | unknown as only sited broken jumper with binoculars | Chris advised that he has found that a High Tension Jumper has come off the pot head at mountain house. This will need to be fixed tomorrow Wed 17/6 as needing to find access to this jumper & pot head. Mountain Club happy to have part power over night. H | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-06-16 | c | 0.00056625 | 3.024e-06 | 2016 | 2015-06-16 | C | 1 | 0.00056625 | 3.0238e-06
5482212 | 2015-07-03 09:12 | 2015-07-03 13:00 | 228 | 2 | 456 | 228 | 225 | 0.0013788 | 450 | 0.0013607 | 6.0475e-06 | NAPA ID:10210 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5333 | Replace xarms on P121345 (T5/212). Existing Tx to be reinstalled. Works location; Vera Rd Stratford WO 30002672. Off at 09/12. On at 13 00 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-07-03 | b | 0.00068035 | 3.024e-06 | 2016 | 2015-07-03 | B | 2 | 0.0013607 | 6.0475e-06
5482238 | 2015-07-01 09:21 | 2015-07-01 14:58 | 337.4333 | 16 | 5398.9333 | 337.4333 | 334.4333 | 0.016325 | 5350.9333 | 0.01618 | 4.838e-05 | NAPA ID:09036 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1333 | To replace poles and cross arms as required beyond IC1333. Works location: Livingstone Rd Te Poi WO 30006868. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-07-01 | b | 0.00809 | 2.419e-05 | 2016 | 2015-07-01 | B | 16 | 0.01618 | 4.838e-05
5482264 | 2015-07-01 09:30 | 2015-07-01 12:35 | 184.9 | 29 | 5362.1 | 184.9 | 181.9 | 0.016214 | 5275.1 | 0.015951 | 8.7689e-05 | NAPA ID:10096 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 6537 | Replace hardwood pole 725681 with 12.5 metre busck. Works location: Meremere Rd Hawera. WO 10160655 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0079753 | 4.3845e-05 | 2016 | 2015-07-01 | B | 29 | 0.015951 | 8.7689e-05
5482266 | 2015-07-06 04:31 | 2015-07-10 06:08 | 5856.8333 | 225 | 37706.25 | 167.5833 | 164.5833 | 0.11401 | 37031.25 | 0.11197 | 0.00068035 | NAPA ID:09556 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 302 | Make line breaks at transformers T3/353 T3/363 and T3/365, cut in new safelink 10231, liven and commission. Works location: Beattie St Fielding. WO 10157269 | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-07-06 | b | 0.055987 | 0.00034017 | 2016 | 2015-07-06 | B | 225 | 0.11197 | 0.00068035
5482267 | 2015-07-02 09:07 | 2015-07-02 14:49 | 342 | 59 | 20178 | 342 | 339 | 0.061013 | 20001 | 0.060478 | 0.0001784 | NAPA ID:09829 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 8 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 333 | Replace Pole 753308 NDR N100026. Works location: Carrington St. NDR N100026 | F3 | BROOKLANDS 8 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-07-02 | b | 0.030239 | 8.9201e-05 | 2016 | 2015-07-02 | B | 59 | 0.060478 | 0.0001784
5482403 | 2015-07-03 10:30 | 2015-07-03 11:30 | 60 | 4 | 240 | 60 | 57 | 0.0007257 | 228 | 0.00068942 | 1.2095e-05 | NAPA ID:10167 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TC2843 | To replace & Upgrade the existing pole mount transformer from a 3 phase 15kVA to a 3 Phase 30kVA. Works location: Lake Arapuni Rd. WO 30010726 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-03 | b | 0.00034471 | 6.048e-06 | 2016 | 2015-07-03 | B | 4 | 0.00068942 | 1.2095e-05
5482472 | 2015-07-06 09:24 | 2015-07-06 16:38 | 434.6 | 112 | 48675.2 | 434.6 | 431.6 | 0.14718 | 48339.2 | 0.14617 | 0.00033866 | NAPA ID:09735 TP_MARTON GXP > BULLS SUB > RACECOURSE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 834 | Work as part of Bulls township Tender, LV poles and xarms, HV poles and Xarms. Works location: Taumahi St. WO 30001091 | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-07-06 | b | 0.073083 | 0.00016933 | 2016 | 2015-07-06 | B | 112 | 0.14617 | 0.00033866
5482484 | 2015-07-08 09:00 | 2015-07-08 15:39 | 399 | 47 | 18753 | 399 | 396 | 0.056705 | 18612 | 0.056278 | 0.00014212 | NAPA ID:09767 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 803425 | Work as part of Bulls township Tender, LV poles and xarms, HV poles and Xarms | F3 | OXFORD ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-07-08 | b | 0.028139 | 7.1058e-05 | 2016 | 2015-07-08 | B | 47 | 0.056278 | 0.00014212
5482554 | 2015-07-07 09:56 | 2015-07-07 15:46 | 349.4833 | 19 | 6640.1833 | 349.4833 | 346.4833 | 0.020078 | 6583.1833 | 0.019906 | 5.7451e-05 | NAPA ID:09929 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 2621 | isolation of 11 kv line for tree cutting , treescape. Works location; Turakina Valley Rd Taihape. PPPD 53596 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-07-07 | b | 0.009953 | 2.8726e-05 | 2016 | 2015-07-07 | B | 19 | 0.019906 | 5.7451e-05
5482555 | 2015-07-07 09:23 | 2015-07-07 12:41 | 198.2333 | 42 | 8011.8667 | 190.7587 | 187.7587 | 0.024226 | 7885.8667 | 0.023845 | 0.000127 | NAPA ID:09447 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI742 | Replace 11kv poles and conductor from pole 730038 to fuses LI774 and any extra poles to the end of the line at pole 728749. Works location: Garsed Rd Kakaramea. WO 30001089 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-07 | b | 0.011922 | 6.3499e-05 | 2016 | 2015-07-07 | B | 42 | 0.023845 | 0.000127
5482582 | 2015-07-08 10:00 | 2015-07-08 10:17 | 17 | 1 | 17 | 17 | 14 | 5.1404e-05 | 14 | 4.2333e-05 | 3.0238e-06 | NAPA ID:10168 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4597 | To install a 400V Fuse /Disconector. Works location: Roach Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 2.1166e-05 | 1.512e-06 | 2016 | 2015-07-08 | B | 1 | 4.2333e-05 | 3.0238e-06
5484803 | 2015-07-07 09:00 | 2015-07-07 15:08 | 367.75 | 28 | 10297 | 367.75 | 364.75 | 0.031136 | 10213 | 0.030882 | 8.4665e-05 | NAPA ID:07496 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 412 | Project number IR6978 Rangikura Reconstruction Replace poles Karakahi Road poles 772786 to 772757. Works location: Karakahi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-07 | b | 0.015441 | 4.2333e-05 | 2016 | 2015-07-07 | B | 28 | 0.030882 | 8.4665e-05
5484817 | 2015-07-07 08:47 | 2015-07-07 14:26 | 338.5167 | 33 | 11171.05 | 338.5167 | 335.5167 | 0.033779 | 11072.05 | 0.033479 | 9.9784e-05 | NAPA ID:09980 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T842 | replace transformer pole t842 and transformer. Works location: Woodlands Rd Carterton. WO 10162028 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-07-07 | b | 0.01674 | 4.9892e-05 | 2016 | 2015-07-07 | B | 33 | 0.033479 | 9.9784e-05
5484833 | 2015-07-09 08:45 | 2015-07-09 14:55 | 369.8667 | 225 | 83220 | 369.8667 | 366.8667 | 0.25164 | 82545 | 0.2496 | 0.00068035 | NAPA ID:08381 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 432 | Replace various network poles in work area. Works location: Barriball St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-07-09 | b | 0.1248 | 0.00034017 | 2016 | 2015-07-09 | B | 225 | 0.2496 | 0.00068035
5484961 | 2015-06-16 18:15 | 2015-06-16 19:02 | 46.8333 | 3 | 137.7333 | 45.9111 | 42.9111 | 0.00041647 | 128.7333 | 0.00038926 | 9.0713e-06 | Restore Supply on Device TC2643 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M1301 | at 18:15 Putaruru Sub, CB 5 Waotu Feeder. Found low hanging wire caused by broken polymer insulator. Isolated lines at Fuses FC4254. Permit issued & repairs carried out. All Power Restored on completion. Paul Cooper Attended. 1x Insulator replaced. Pole M | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-06-16 | c | 0.00038926 | 9.071e-06 | 2016 | 2015-06-16 | C | 3 | 0.00038926 | 9.0713e-06
5485066 | 2015-06-16 18:44 | 2015-06-16 19:47 | 62.9167 | 17 | 1069.5833 | 62.9167 | 59.9167 | 0.0032342 | 1018.5833 | 0.00308 | 5.1404e-05 | Restore Supply on Device X298 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 802384 | Repaired floating conductor using 1x Copper Binder 5.10pm called through to svs hub. Also check 5485199 - 1150 WANGANUI ROAD. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-16 | c | 0.00308 | 5.1404e-05 | 2016 | 2015-06-16 | C | 17 | 0.00308 | 5.1404e-05
5485879 | 2015-06-15 20:09 | 2015-06-16 23:48 | 1659.25 | 358 | 27138 | 75.8045 | 72.8045 | 0.082059 | 26064 | 0.078811 | 0.0010825 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 717744 | O/C, E/F. Car vs Pole, Lines down. Isolated at ABS MA191. NDR #43429 Car had left scene of accident. Police attended. Transformer 5319E was isolated at LV fuses due to HV line contacting LV neutral. To be inspected before relivening. See OMS 5487575. Mat | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-15 | c | 0.078811 | 0.0010825 | 2016 | 2015-06-15 | C | 358 | 0.078811 | 0.0010825
5486242 | 2015-06-16 20:10 | 2015-06-16 21:29 | 79.0667 | 240 | 13492 | 56.2167 | 53.2167 | 0.040797 | 12772 | 0.038619 | 0.0007257 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 717744 | See OMS 5485609. Outage links with OMS 5485879 (Manaia CB5).E/F, O/C. Tripped at exact same time as CB 5 which was caused by car vs pole. Partial patrol with no fault found. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-16 | c | 0.038619 | 0.0007257 | 2016 | 2015-06-16 | C | 240 | 0.038619 | 0.0007257
5487461 | 2015-06-17 03:00 | 2015-06-17 04:09 | 68.9167 | 37 | 2531.6 | 68.4216 | 65.4216 | 0.007655 | 2420.6 | 0.0073193 | 0.00011188 | Restore Supply on Device TC2894 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B12470 | at 03:00, Baird Rd Sub, CB 5 Harris Block Feeder. Found broken 11kV Transformer Fuse Crossarm at Pole B12470 (Transformer TC2894). Isolated Lines at ABS 1008. Permit issued & repairs carried out. All power restored on completion. 1x Crossarm replaced, 3x | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-06-17 | c | 0.0073193 | 0.00011188 | 2016 | 2015-06-17 | C | 37 | 0.0073193 | 0.00011188
5488717 | 2015-06-17 01:50 | 2015-06-17 02:06 | 16.4833 | 1134 | 1829.65 | 1.6134 | -1.3866 | 0.0055324 | 0 | 0 | 0.0034289 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C634 | RS C634 A/R, L/O, E/F, O/C B & C Phase. Successful reclose tried after 15 minutes. Patrolled, No fault found | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-17 | c | 0 | 0.0034289 | 2016 | 2015-06-17 | C | 1134 | 0 | 0.0034289
5489179 | 2015-06-17 03:39 | 2015-06-17 06:26 | 166.6833 | 235 | 39059.2333 | 166.2095 | 163.2095 | 0.11811 | 38354.2333 | 0.11597 | 0.00071058 | Restore Supply on Device TE7-111 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227222 | at 05:04, Pongakawa Sub, CB 1 Tainui Feeder. Police reported lines down on Pukehina Parade and believed they were still alive. Faultmen dispatched. Found 11kV line down that was still alive (had blown DDO but line was still alive through transformers). Is | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-17 | c | 0.11597 | 0.00071058 | 2016 | 2015-06-17 | C | 235 | 0.11597 | 0.00071058
5489436 | 2015-06-17 08:10 | 2015-06-17 08:58 | 48 | 5 | 238.6667 | 47.7333 | 44.7333 | 0.00072167 | 223.6667 | 0.00067631 | 1.5119e-05 | Restore Supply on Device T1044 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798282 | Faultman found a broken jumper on pole 798282, line was isolated at Fuses 7276 & ABS S526 to repair the jumper. 2 X line taps used. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-17 | c | 0.00067631 | 1.5119e-05 | 2016 | 2015-06-17 | C | 5 | 0.00067631 | 1.5119e-05
5490876 | 2015-07-08 12:00 | 2015-07-08 12:26 | 26 | 7 | 182 | 26 | 23 | 0.00055032 | 161 | 0.00048683 | 2.1166e-05 | NAPA ID:10169 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4596 | To install a 400V Fuse/Disconector. Works location: Roach Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 0.00024341 | 1.0583e-05 | 2016 | 2015-07-08 | B | 7 | 0.00048683 | 2.1166e-05
5490896 | 2015-07-08 13:50 | 2015-07-08 14:36 | 46 | 4 | 184 | 46 | 43 | 0.00055637 | 172 | 0.00052009 | 1.2095e-05 | NAPA ID:10170 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4499 | To install a 400V Fuse / Disconector. Works location: Bolton Rd Morrinsville. WO 10148449 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 0.00026004 | 6.048e-06 | 2016 | 2015-07-08 | B | 4 | 0.00052009 | 1.2095e-05
5490925 | 2015-07-10 10:00 | 2015-07-10 10:35 | 35 | 11 | 385 | 35 | 32 | 0.0011641 | 352 | 0.0010644 | 3.3261e-05 | NAPA ID:10171 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3959 | To install a 400V Fuse /Disconector. Works location: Bolton Rd Morrinsville WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-10 | b | 0.00053218 | 1.6631e-05 | 2016 | 2015-07-10 | B | 11 | 0.0010644 | 3.3261e-05
5490978 | 2015-07-10 12:30 | 2015-07-10 14:56 | 145.5167 | 2 | 291.0333 | 145.5167 | 142.5167 | 0.00088002 | 285.0333 | 0.00086187 | 6.0475e-06 | NAPA ID:10172 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1521 | Replace 11kV & 400V arms on pole TC1993. Works location: Kereone Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-10 | b | 0.00043094 | 3.024e-06 | 2016 | 2015-07-10 | B | 2 | 0.00086187 | 6.0475e-06
5491012 | 2015-07-13 10:00 | 2015-07-13 10:35 | 35 | 9 | 315 | 35 | 32 | 0.00095248 | 288 | 0.00087084 | 2.7214e-05 | NAPA ID:10173 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC759 | To install a 400V Fuse/Disconnector. Works location: Scott Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0.00043542 | 1.3607e-05 | 2016 | 2015-07-13 | B | 9 | 0.00087084 | 2.7214e-05
5491024 | 2015-07-13 13:27 | 2015-07-13 13:29 | 1.45 | 7 | 10.15 | 1.45 | -1.55 | 3.0691e-05 | 0 | 0 | 2.1166e-05 | NAPA ID:10174 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC236 | Install a 400V Fuse Disconector. Works location: Kuranui Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0 | 1.0583e-05 | 2016 | 2015-07-13 | B | 7 | 0 | 2.1166e-05
5491213 | 2015-07-13 14:05 | 2015-07-13 14:30 | 25 | 5 | 125 | 25 | 22 | 0.00037797 | 110 | 0.00033261 | 1.5119e-05 | NAPA ID:10175 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1214 | Ibnstall a 400V Fuse/Disconnector. Works location: Kuranui Rd Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0.00016631 | 7.559e-06 | 2016 | 2015-07-13 | B | 5 | 0.00033261 | 1.5119e-05
5491377 | 2015-07-08 09:15 | 2015-07-08 15:20 | 365 | 10 | 3650 | 365 | 362 | 0.011037 | 3620 | 0.010946 | 3.0238e-05 | NAPA ID:09808 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV V85 | tree work near overhead lines between pole p02604 and p02613. Works location: Route 52 Tiraumean PPPD 47127. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-08 | b | 0.005473 | 1.5119e-05 | 2016 | 2015-07-08 | B | 10 | 0.010946 | 3.0238e-05
5492167 | 2015-06-17 10:16 | 2015-06-17 11:19 | 63.75 | 4 | 255 | 63.75 | 60.75 | 0.00077106 | 243 | 0.00073477 | 1.2095e-05 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737997 | Attend and find access to Jumper & Pot Head at Stratford Mountain Club. Jumper has come off pot head, not sure if pot head needs to be replaced also. 2.37pm advised Tallia at svs hub that i have put through 1R request for jumper but if pot head needs to | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-06-17 | c | 0.00073477 | 1.2095e-05 | 2016 | 2015-06-17 | C | 4 | 0.00073477 | 1.2095e-05
5492177 | 2015-07-15 09:45 | 2015-07-15 12:45 | 180 | 9 | 1620 | 180 | 177 | 0.0048985 | 1593 | 0.0048169 | 2.7214e-05 | NAPA ID:10176 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2151 | To replace the 400V arm and install a 400V Fuse/Disconnector. Works location: Kuranui Rd Morrinsville WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-15 | b | 0.0024084 | 1.3607e-05 | 2016 | 2015-07-15 | B | 9 | 0.0048169 | 2.7214e-05
5492256 | 2015-07-02 09:46 | 2015-07-02 10:07 | 21.5667 | 107 | 2199.1333 | 20.5526 | 17.5526 | 0.0066497 | 1878.1333 | 0.005679 | 0.00032354 | NAPA ID:09191 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC2-124 | CHANGE 33KV Cross arms and poles, also need 11KV Isolated & Earthed as both are on the same pole being changed. Works location: Hwy 2 Omokoroa. IR7180. Job cancelled problem with crane, also crews turned up late | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-07-02 | b | 0.0028395 | 0.00016177 | 2016 | 2015-07-02 | B | 107 | 0.005679 | 0.00032354
5492270 | 2015-06-17 11:29 | 2015-06-17 14:48 | 198.7667 | 1 | 198.7667 | 198.7667 | 195.7667 | 0.00060102 | 195.7667 | 0.00059195 | 3.0238e-06 | Restore Supply on Device T9/81 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P23311 | Pole P23311 needs replacing - spur line from fuses B25 on Waioni feeder. Pole Down Pole P23311 and two either side will need re straightening. Left off overnight as only feeds woolshed. Switching written to be completed on 18/06/15. Offloaded transformer | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-17 | c | 0.00059195 | 3.024e-06 | 2016 | 2015-06-17 | C | 1 | 0.00059195 | 3.0238e-06
5492308 | 2015-06-17 15:38 | 2015-06-17 15:58 | 20.4 | 40 | 816 | 20.4 | 17.4 | 0.0024674 | 696 | 0.0021045 | 0.00012095 | Restore Supply on Device TP2144 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | W13317 | Digger at the quarry knocked a pole W13317 and caused the lines to spark and smoke. Pole is now on a lean. No power, 11.59pm advised Joanne at svs hub of job 1337 2r request to straighten pole and replace stay wire, has isolated ht fuses through Control | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-06-17 | c | 0.0021045 | 0.00012095 | 2016 | 2015-06-17 | C | 40 | 0.0021045 | 0.00012095
5492328 | 2015-07-02 12:35 | 2015-07-02 13:40 | 65 | 1 | 65 | 65 | 62 | 0.00019654 | 62 | 0.00018747 | 3.0238e-06 | NAPA ID:09984 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4792 | Replace Transformer TC4792. Works location: Manaia Rd Coromandel WO 30002265 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-07-02 | b | 9.3737e-05 | 1.512e-06 | 2016 | 2015-07-02 | B | 1 | 0.00018747 | 3.0238e-06
5492398 | 2015-07-08 11:36 | 2015-07-08 16:14 | 278 | 162 | 36618.1 | 226.0377 | 223.0377 | 0.11072 | 36132.1 | 0.10925 | 0.00048985 | NAPA ID:09591 TP_MARTON GXP > ARAHINA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2838 | Replace double curcuit 11kv pole hit by Vehicle. Works location: Wanganui Rd Marton. NDR 30416 | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-07-08 | b | 0.054627 | 0.00024493 | 2016 | 2015-07-08 | B | 162 | 0.10925 | 0.00048985
5492410 | 2015-07-03 09:40 | 2015-07-03 14:38 | 298.4167 | 64 | 19098.6667 | 298.4167 | 295.4167 | 0.05775 | 18906.6667 | 0.057169 | 0.00019352 | NAPA ID:09962 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC482 | Replace H/V Crossarms and T/X's at Various Sites. Works location: Kaihere Rd. WO 10147831 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-03 | b | 0.028585 | 9.676e-05 | 2016 | 2015-07-03 | B | 64 | 0.057169 | 0.00019352
5492418 | 2015-07-01 10:16 | 2015-07-01 12:10 | 113.9833 | 51 | 5813.15 | 113.9833 | 110.9833 | 0.017578 | 5660.15 | 0.017115 | 0.00015421 | NAPA ID:09340 TP_CARRINGTON GXP > OAKURA SUB > INLAND COAST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 412 | change 11kv xarms on pole 755604 as xrms burnt after previous fault,16mm wire. Works location: Carrington Rd New Plymouth. WO 30003349 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-07-01 | b | 0.0085575 | 7.7106e-05 | 2016 | 2015-07-01 | B | 51 | 0.017115 | 0.00015421
5495646 | 2015-06-18 06:00 | 2015-06-18 12:31 | 391.1 | 92 | 12147.9333 | 132.0428 | 129.0428 | 0.036732 | 11871.9333 | 0.035898 | 0.00027819 | Restore Supply on Device T396 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 817059 | Initial tripping on CB C890 on O/C, E/F. Reports of no power found sectionaliser CB C637/2 had tripped. Feeder sectionalised / patrolled with a broken conductor found beyond ABS S1204. Conductor rejoined with about 3m of 16mm CU. Relivened OK. High winds | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.035898 | 0.00027819 | 2016 | 2015-06-18 | C | 92 | 0.035898 | 0.00027819
5495738 | 2015-06-18 07:46 | 2015-06-18 07:58 | 11.85 | 85 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00025702 | Restore Supply on Device C630 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C630 | CB C630 Auto-reclosed a number of times in quick succession - Area patrolled but nothing found (Some uneven spans / trees in area but nothing obvious). 3 Temp Fault Locaters fitted. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0 | 0.00025702 | 2016 | 2015-06-18 | C | 85 | 0 | 0.00025702
5496614 | 2015-07-06 09:30 | 2015-07-06 13:20 | 230 | 12 | 2760 | 230 | 227 | 0.0083456 | 2724 | 0.0082367 | 3.6285e-05 | NAPA ID:09670 TP_TAURANGA 33 GXP > OMOKOROA SUB > OMOKOROA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3-074 | Replace Tx cross arm. Works location: Omokoroa Rd. WO 30002379 | F3 | OMOKOROA RD | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-06 | b | 0.0041184 | 1.8143e-05 | 2016 | 2015-07-06 | B | 12 | 0.0082367 | 3.6285e-05
5496638 | 2015-07-06 09:42 | 2015-07-06 12:42 | 180 | 1 | 180 | 180 | 177 | 0.00054428 | 177 | 0.00053521 | 3.0238e-06 | NAPA ID:09998 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC968 | Replace Transformer at TC968. Works location: Ferry Rd Kerepehi. WO 10147831 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-06 | b | 0.0002676 | 1.512e-06 | 2016 | 2015-07-06 | B | 1 | 0.00053521 | 3.0238e-06
5496664 | 2015-06-18 09:11 | 2015-06-18 09:12 | 1 | 64 | 64 | 1 | -2 | 0.00019352 | 0 | 0 | 0.00019352 | Restore Supply on Device V5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | V5 | Auto-reclose on CB V5 on Phase A-C E/F. Windy in area. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0 | 0.00019352 | 2016 | 2015-06-18 | C | 64 | 0 | 0.00019352
5496729 | 2015-07-06 09:15 | 2015-07-06 11:12 | 117 | 4 | 468 | 117 | 114 | 0.0014151 | 456 | 0.0013788 | 1.2095e-05 | NAPA ID:09784 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 208963 | Replace Cross Arms. Works location: Omokoroa Rd WO 30002379 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-06 | b | 0.00068942 | 6.048e-06 | 2016 | 2015-07-06 | B | 4 | 0.0013788 | 1.2095e-05
5496979 | 2015-06-18 12:00 | 2015-06-18 18:06 | 365.5667 | 6 | 2193.4 | 365.5667 | 362.5667 | 0.0066323 | 2175.4 | 0.0065779 | 1.8143e-05 | Restore Supply on Device T9/24 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P06293 | Trevor advised that pole P06293 has burnt down and will need replacing, this will need helicopter to change this pole, also tree trimming contractor needed to cut away pine tree from lines. once trees have been cut power should be able to be restored. T | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.0065779 | 1.8143e-05 | 2016 | 2015-06-18 | C | 6 | 0.0065779 | 1.8143e-05
5497188 | 2015-06-18 00:51 | 2015-06-18 15:48 | 896.8167 | 64 | 4426 | 69.1562 | 66.1562 | 0.013383 | 4234 | 0.012803 | 0.00019352 | Restore Supply on Device V5 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06272 | Initially received a number of Auto-recloses on CB V5 then trip. (Flags Phase A-C O/C, E/F). Feeder sectionalised / patrolled with a floating conductor found on the main line. (Isolation from recloser CB V5). Rebound OK, relivened. Windy in area. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.012803 | 0.00019352 | 2016 | 2015-06-18 | C | 64 | 0.012803 | 0.00019352
5497916 | 2015-07-07 08:45 | 2015-07-07 14:15 | 329.6333 | 9 | 2966.7 | 329.6333 | 326.6333 | 0.0089706 | 2939.7 | 0.0088889 | 2.7214e-05 | NAPA ID:09725 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole S0384 | Replace 11kV poles and crossarms. Works location: Paeroa Kopu Rd Paeroa. WO 30009300. Unable to close. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-07-07 | b | 0.0044445 | 1.3607e-05 | 2016 | 2015-07-07 | B | 9 | 0.0088889 | 2.7214e-05
5497919 | 2015-07-06 09:30 | 2015-07-06 11:43 | 133 | 2 | 266 | 133 | 130 | 0.00080432 | 260 | 0.00078618 | 6.0475e-06 | NAPA ID:09992 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4124 | Replace two phaseTransformer TC4124. Works location: Manaia Rd Coromandel. WO 30002265 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-07-06 | b | 0.00039309 | 3.024e-06 | 2016 | 2015-07-06 | B | 2 | 0.00078618 | 6.0475e-06
5497932 | 2015-07-07 09:09 | 2015-07-07 12:29 | 200.1167 | 9 | 1801.05 | 200.1167 | 197.1167 | 0.0054459 | 1774.05 | 0.0053643 | 2.7214e-05 | NAPA ID:09996 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2104 | Replace Two phaseTransformer TC3649 and crossarms at various sites. Works location: Manaia Rd Coromandel. WO 30002265 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-07-07 | b | 0.0026822 | 1.3607e-05 | 2016 | 2015-07-07 | B | 9 | 0.0053643 | 2.7214e-05
5498162 | 2015-06-18 15:20 | 2015-06-18 16:30 | 70 | 38 | 2660 | 70 | 67 | 0.0080432 | 2546 | 0.0076985 | 0.0001149 | Restore Supply on Device 2903T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2903T | Please check if 5505901 is related. Isolated from ABS 5515 to repair jumper on drop out at transformer 2903T | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.0076985 | 0.0001149 | 2016 | 2015-06-18 | C | 38 | 0.0076985 | 0.0001149
5507373 | 2015-06-18 19:21 | 2015-06-18 20:55 | 94.3333 | 3 | 283 | 94.3333 | 91.3333 | 0.00085572 | 274 | 0.00082851 | 9.0713e-06 | Restore Supply on Device TE6-107 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP896 | Advised hub of 999 Found 2 fuses blowen at FP896. Caused by duck. Reloaded Relivened | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-06-18 | c | 0.00082851 | 9.071e-06 | 2016 | 2015-06-18 | C | 3 | 0.00082851 | 9.0713e-06
5507382 | 2015-06-18 19:46 | 2015-06-18 20:40 | 54 | 100 | 5400 | 54 | 51 | 0.016328 | 5100 | 0.015421 | 0.00030238 | Restore Supply on Device 5531 | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5490 | Faultman found damaged fuse holders at Fuses 5490, line was isolated at ABS 5531 to replace the full set of fuse holders and fuses. 1 X Full set of fuse holders. 3 X 20 amp HV fuses replaced. | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.015421 | 0.00030238 | 2016 | 2015-06-18 | C | 100 | 0.015421 | 0.00030238
5507856 | 2015-06-18 21:58 | 2015-06-18 23:32 | 93.6 | 1 | 93.6 | 93.6 | 90.6 | 0.00028302 | 90.6 | 0.00027395 | 3.0238e-06 | Restore Supply on Device T3651 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T3651 | Faultman check lines around area of the flickering power but did not find anything, earlier in the evening there was an auto recloser on this feeder at Recloser C408, faultman reported that they have had problems on this feeder and have not found any faul | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.00027395 | 3.024e-06 | 2016 | 2015-06-18 | C | 1 | 0.00027395 | 3.0238e-06
5508607 | 2015-06-19 04:19 | 2015-06-19 06:25 | 125.7833 | 234 | 19124.7 | 81.7295 | 78.7295 | 0.057829 | 18422.7 | 0.055706 | 0.00070756 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7 | Recloser 499 tripped on A phase O/C & E/F flags. Line was patrolled and sectionalised and no fault was found. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.055706 | 0.00070756 | 2016 | 2015-06-19 | C | 234 | 0.055706 | 0.00070756
5509861 | 2015-06-18 04:32 | 2015-06-19 06:28 | 1556 | 240 | 18423.0333 | 76.7626 | 73.7626 | 0.055707 | 17703.0333 | 0.05353 | 0.0007257 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7 | CB 7 tripped on A phase O/C & E/F flags, line was patrolled and sectionalised and no fault was found. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-06-18 | c | 0.05353 | 0.0007257 | 2016 | 2015-06-18 | C | 240 | 0.05353 | 0.0007257
5510917 | 2015-06-19 05:14 | 2015-06-19 07:22 | 128.45 | 233 | 20653.95 | 88.6436 | 85.6436 | 0.062453 | 19954.95 | 0.060339 | 0.00070454 | Restore Supply on Device T21 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T21 | Feeder sectionalised, and patrolled, no fault found. Suspect line clash from high winds. | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.060339 | 0.00070454 | 2016 | 2015-06-19 | C | 233 | 0.060339 | 0.00070454
5511479 | 2015-06-19 06:51 | 2015-06-19 06:52 | 1 | 239 | 239 | 1 | -2 | 0.00072268 | 0 | 0 | 0.00072268 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | N/A - NOT APPLICABLE | Line patrolled and found tree branch on lines at Pole C774. Removed with hot sticks. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-06-19 | c | 0 | 0.00072268 | 2016 | 2015-06-19 | C | 239 | 0 | 0.00072268
5514008 | 2015-06-19 07:47 | 2015-06-19 11:34 | 227.4833 | 1 | 227.4833 | 227.4833 | 224.4833 | 0.00068786 | 224.4833 | 0.00067878 | 3.0238e-06 | Other Request on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7376 | Customer also reporting pole down on farm. Advised hub. (no pole down at all). 2 X HT fuses (10A) reloaded at fuses 7376. Child job made as this was put in as a schedulled (5516179). | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.00067878 | 3.024e-06 | 2016 | 2015-06-19 | C | 1 | 0.00067878 | 3.0238e-06
5514035 | 2015-06-26 12:45 | 2015-06-26 13:49 | 64 | 193 | 11914 | 61.7306 | 58.7306 | 0.036025 | 11335 | 0.034274 | 0.00058359 | NAPA ID:10446 TP_STRATFORD GXP > ELTHAM SUB > RAWHITIROA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4951 | Replace centre contacts on Abs 6194 DNO 150608. Works location: Rawhitiroa Rd Eltham. WO 30010908 | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-26 | b | 0.017137 | 0.00029179 | 2016 | 2015-06-26 | B | 193 | 0.034274 | 0.00058359
5514208 | 2015-06-19 10:16 | 2015-06-19 15:00 | 283.3 | 2 | 566.6 | 283.3 | 280.3 | 0.0017133 | 560.6 | 0.0016951 | 6.0475e-06 | Restore Supply on Device T45 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7873 | 2 HT fuses reloaded at Fuses 7873. (10A) | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.0016951 | 6.048e-06 | 2016 | 2015-06-19 | C | 2 | 0.0016951 | 6.0475e-06
5514252 | 2015-07-13 10:35 | 2015-07-13 17:03 | 387.8167 | 94 | 36406.05 | 387.2984 | 384.2984 | 0.11008 | 36124.05 | 0.10923 | 0.00028423 | NAPA ID:08836 TP_MARTON GXP > BULLS SUB > RACECOURSE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4466 | Work as part of Bulls township Tender, LV poles and xarms, HV poles and Xarms. Works location: Hwy 1 and Criterion St Bulls. WO 30001091. Delay in restoration due to late downer attendance for switching. AP issued at 1051 should been issued 0900. Scanpow | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-07-13 | b | 0.054615 | 0.00014212 | 2016 | 2015-07-13 | B | 94 | 0.10923 | 0.00028423
5515707 | 2015-06-19 09:24 | 2015-06-19 12:24 | 179.4 | 116 | 13990.1333 | 120.6046 | 117.6046 | 0.042303 | 13642.1333 | 0.041251 | 0.00035076 | Restore Supply on Device T1608 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 820169 | Initial Tripping on OYT recloser C409/2. Fault caused by 2 spans of conductor down (same phase) beyond fuses 7308. Fuses open for isolation and CB409/2 reclosed. Conductor rehung / jointed /rebound and livened OK. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.041251 | 0.00035076 | 2016 | 2015-06-19 | C | 116 | 0.041251 | 0.00035076
5516159 | 2015-07-13 10:00 | 2015-07-13 13:33 | 213.4167 | 28 | 5975.6667 | 213.4167 | 210.4167 | 0.018069 | 5891.6667 | 0.017815 | 8.4665e-05 | NAPA ID:07502 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 412 | Project number IR6978 Rangikura Reconstruction Replace poles Karakahi Road poles 7722813 to 772889. Works location; Karakahi Rd. IR6978. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-13 | b | 0.0089075 | 4.2333e-05 | 2016 | 2015-07-13 | B | 28 | 0.017815 | 8.4665e-05
5516172 | 2015-06-19 16:42 | 2015-06-19 16:54 | 12.0333 | 19 | 228.6333 | 12.0333 | 9.0333 | 0.00069133 | 171.6333 | 0.00051898 | 5.7451e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1322 | Replace 11kV fuses elements in fuses 1322 to 20A links, currently under rated and causing relibility issues. Fuses are on the Waverley Sub, Feeder 242- Waitotara Feeder. Please work through NOC control. ASW- NCTL. Fuses upgraded to 20A. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-19 | c | 0.00051898 | 5.7451e-05 | 2016 | 2015-06-19 | C | 19 | 0.00051898 | 5.7451e-05
5516899 | 2015-06-19 11:04 | 2015-06-19 13:31 | 147 | 234 | 25883 | 110.6111 | 107.6111 | 0.078264 | 25181 | 0.076141 | 0.00070756 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Brookelands 5 Mangorei Junction Road RS499 tripped A phase E/F. Line sectionalised and patrolled. No fault found. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.076141 | 0.00070756 | 2016 | 2015-06-19 | C | 234 | 0.076141 | 0.00070756
5522010 | 2015-06-19 12:04 | 2015-06-19 12:20 | 15.9833 | 20 | 319.6667 | 15.9833 | 12.9833 | 0.0009666 | 259.6667 | 0.00078517 | 6.0475e-05 | Restore Supply on Device LI146 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 727165 | Replace king bolt and nuts | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.00078517 | 6.0475e-05 | 2016 | 2015-06-19 | C | 20 | 0.00078517 | 6.0475e-05
5522849 | 2015-07-09 08:41 | 2015-07-09 16:11 | 450 | 242 | 89546.6833 | 370.0276 | 367.0276 | 0.27077 | 88820.6833 | 0.26857 | 0.00073175 | NAPA ID:09303 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC223 | To replace 11kV and LV cross arms along Station Road Matamata. Works location: Station Rd. WO 30002943 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-09 | b | 0.13429 | 0.00036587 | 2016 | 2015-07-09 | B | 242 | 0.26857 | 0.00073175
5523084 | 2015-06-19 17:30 | 2015-06-19 22:48 | 317.75 | 211 | 33396.7167 | 158.2783 | 155.2783 | 0.10098 | 32763.7167 | 0.09907 | 0.00063801 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 358773 | Tripping on recloser CB 4261 on Phase A-B O/C, E/F. Feeder sectionalised / patrolled. Faultman found a tree through the lines at pole 358773, Line was isolated at ABS's 716 & 2667 to repair the lines. 40 meters rabbit conductor used. 10 X rabbit sleeves u | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.09907 | 0.00063801 | 2016 | 2015-06-19 | C | 211 | 0.09907 | 0.00063801
5523477 | 2015-06-19 20:30 | 2015-06-19 22:06 | 95.4167 | 1 | 95.4167 | 95.4167 | 92.4167 | 0.00028852 | 92.4167 | 0.00027945 | 3.0238e-06 | Restore Supply on Device TP2161 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TP2161 | 8.35pm advised svs hub of 999. branch hit 11kV, caught fire, fire has been out for a while now. Fm advises site is safe. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-06-19 | c | 0.00027945 | 3.024e-06 | 2016 | 2015-06-19 | C | 1 | 0.00027945 | 3.0238e-06
5523499 | 2015-06-19 21:00 | 2015-06-19 21:01 | 1 | 303 | 303 | 1 | -2 | 0.0009162 | 0 | 0 | 0.0009162 | Restore Supply on Device XT40 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | XT40 | CB XT40 auto reclosed on no flags, line was not patrolled. Cause of fault unknown. | F1,F2,F3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0 | 0.0009162 | 2016 | 2015-06-19 | C | 303 | 0 | 0.0009162
5524583 | 2015-06-19 21:30 | 2015-06-19 23:49 | 138.6667 | 234 | 11296.6333 | 48.2762 | 45.2762 | 0.034158 | 10594.6333 | 0.032036 | 0.00070756 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745180 | Check for safety - cross arm shorting (2 poles up from #387). After receiving a call from a customer fault man found a cracked 11kV insulator on pole 745180, line was isolated at ABS's 349 & 483. 1 X 11kV insulator replaced. 1,5 meters Namu conductor used | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.032036 | 0.00070756 | 2016 | 2015-06-19 | C | 234 | 0.032036 | 0.00070756
5525127 | 2015-06-19 22:01 | 2015-06-29 16:17 | 14056 | 363 | 199550 | 549.7245 | 546.7245 | 0.60339 | 198461 | 0.6001 | 0.0010976 | Restore Supply on Device WH2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6863 | 29/06/15 - Paul Fitzpatrick attended. Carried out repairs beyond fuses 6863. Multiple assets repaired/replaced. Downer to provide materials list to billing. Believe all power has been restored on this feeder. CB WH2 tripped no flags, line was sectionalise | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0.6001 | 0.0010976 | 2016 | 2015-06-19 | C | 363 | 0.6001 | 0.0010976
5526236 | 2015-06-19 22:24 | 2015-06-19 22:25 | 1 | 303 | 303 | 1 | -2 | 0.0009162 | 0 | 0 | 0.0009162 | Restore Supply on Device XT40 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | XT40 | CB XT 40 auto reclosed no flags, Line was not patrolled. Suspect line clash as fault man reported high winds in area. | F1,F2,F3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0 | 0.0009162 | 2016 | 2015-06-19 | C | 303 | 0 | 0.0009162
5526554 | 2015-06-19 23:35 | 2015-06-19 23:36 | 1 | 64 | 64 | 1 | -2 | 0.00019352 | 0 | 0 | 0.00019352 | Restore Supply on Device V5 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | V5 | Recloser V5 auto reclosed on B & C phase O/C flags, Line was not patrolled. Suspect line clash as fault man report high winds in the area. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0 | 0.00019352 | 2016 | 2015-06-19 | C | 64 | 0 | 0.00019352
5526986 | 2015-06-20 02:55 | 2015-06-20 07:25 | 270.3167 | 44 | 11893.9333 | 270.3167 | 267.3167 | 0.035964 | 11761.9333 | 0.035565 | 0.00013305 | Restore Supply on Device Y4 | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Y4 | Faultman found blown fuses on transfomer Y4 , line was isolated at ABS 2577 and Links 4012 to replaced the fuses on closer inspection faultman found transformer Y4 was damaged and needs to be replaced. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.035565 | 0.00013305 | 2016 | 2015-06-20 | C | 44 | 0.035565 | 0.00013305
5527162 | 2015-06-20 02:25 | 2015-06-20 11:48 | 563.15 | 224 | 126145.6 | 563.15 | 560.15 | 0.38143 | 125473.6 | 0.3794 | 0.00067732 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T0483 | Car V Pole T0483 ( THS 3 ) Emergency isolation at ABS IC2729 ( Spur no back feeds ). Pole replaced all service restored. NDR No 31058. Materials 1x11m concrete pole, 1x HV crossarm + insulators, 2x LV crossarms & insulators. | F2/F3 | QUEEN ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.3794 | 0.00067732 | 2016 | 2015-06-20 | C | 224 | 0.3794 | 0.00067732
5533027 | 2015-06-20 05:44 | 2015-06-26 14:21 | 9156.8667 | 8635 | 2975220.4667 | 344.5536 | 341.5536 | 8.9964 | 2949315.4667 | 8.918 | 0.02611 | Restore Supply on Device 3092 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 3092 | CB 1092 tripped on E/F and O/C due to severe flooding and slip taking out Kelvin Grove and Peat St Substations. Initial backfeed via Roberts Ave. This failed when large slip occurred behind sub taking out 3 33kV poles. Due to rising water fault restoratio | F1,F2,F3 | PEAT ST 33KV | BRUNSWICK | Wanganui | TP_BRUNSWICK | Western Electricity | POWERCO | 2015-06-20 | c | 8.918 | 0.02611 | 2016 | 2015-06-20 | C | 8635 | 8.918 | 0.02611
5534313 | 2015-06-20 08:16 | 2015-06-23 12:50 | 4593.7833 | 4 | 18375.1333 | 4593.7833 | 4590.7833 | 0.055562 | 18363.1333 | 0.055526 | 1.2095e-05 | Restore Supply on Device X406 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | X406 | FM advise: tx x406 has blown. Not sure when tx will be replaced, need to wait for weather to improve. Transformer Replaced by Alan Cox on 23/06/15. Materials used: 3Phase/15kVA Transformer, 2x 2Amp HV Links, 1x 60Amp LV Link | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-20 | c | 0.055526 | 1.2095e-05 | 2016 | 2015-06-20 | C | 4 | 0.055526 | 1.2095e-05
5534355 | 2015-06-20 08:34 | 2015-06-20 17:10 | 515.8333 | 4 | 2063.3333 | 515.8333 | 512.8333 | 0.006239 | 2051.3333 | 0.0062027 | 1.2095e-05 | Restore Supply on Device 7574 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7574 | 7574 fuses found blown bark on line cleared nby hot stick | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.0062027 | 1.2095e-05 | 2016 | 2015-06-20 | C | 4 | 0.0062027 | 1.2095e-05
5534358 | 2015-06-19 08:35 | 2015-06-19 08:37 | 2.1667 | 1420 | 3076.6667 | 2.1667 | -0.83333 | 0.0093031 | 0 | 0 | 0.0042937 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | Unknown | Unknown | cb5 | Momentary Loss of Supply - Line not Patrolled. Cause of fault unknown. | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-06-19 | c | 0 | 0.0042937 | 2016 | 2015-06-19 | C | 1420 | 0 | 0.0042937
5535795 | 2015-06-20 08:41 | 2015-06-22 15:06 | 3264.7833 | 86 | 70694 | 822.0233 | 819.0233 | 0.21376 | 70436 | 0.21298 | 0.00026004 | Restore Supply on Device 5329 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 763959 | NDR: N1039 Will need to return to site tomorrow, clear trees and restore power 21/06/15 Temp line break made at Pole 763939 and power restored up to there, multiple damage past this pole. Work to continue once access sorted 1 x 11 mtr pole 2 x crossarms c | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.21298 | 0.00026004 | 2016 | 2015-06-20 | C | 86 | 0.21298 | 0.00026004
5536103 | 2015-06-20 09:06 | 2015-06-20 11:54 | 168 | 3322 | 199532.7167 | 60.064 | 57.064 | 0.60334 | 189566.7167 | 0.5732 | 0.010045 | Restore Supply on Device 2212 | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2212 | Cross arms were rotten and king pin had come loose causing cross arm brace to contact 33kV resulting in tripping of CB2212. | F1,F2,F3 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.5732 | 0.010045 | 2016 | 2015-06-20 | C | 3322 | 0.5732 | 0.010045
5539561 | 2015-06-20 09:41 | 2015-06-20 11:14 | 92.8 | 592 | 28590.15 | 48.2942 | 45.2942 | 0.08645 | 26814.15 | 0.08108 | 0.0017901 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9182 | Line sectionalised & patrolled no fault found. No flags operated. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.08108 | 0.0017901 | 2016 | 2015-06-20 | C | 592 | 0.08108 | 0.0017901
5540239 | 2015-06-20 12:26 | 2015-06-23 17:09 | 4603.4 | 17 | 78257.8 | 4603.4 | 4600.4 | 0.23663 | 78206.8 | 0.23648 | 5.1404e-05 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | UNDERGROUND CABLE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | X3243 | 10.50am - eta of 10-15 min. Isolated transformer X3243 due to flooding affecting half of road from # 12 upwards. 23/6 5.01pm - Inspected all boxes and put fuses back in. Power should now be restored to the street. Ben and crew attended. | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.23648 | 5.1404e-05 | 2016 | 2015-06-20 | C | 17 | 0.23648 | 5.1404e-05
5541072 | 2015-06-20 10:52 | 2015-06-20 13:15 | 142.9667 | 1 | 142.9667 | 142.9667 | 139.9667 | 0.0004323 | 139.9667 | 0.00042323 | 3.0238e-06 | Restore Supply on Device T2841 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2841 | 12.53pm - FM requested additional FM for safety. replace 2 amp fuse at tx 2841. reload, re-liven. cause: wind. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.00042323 | 3.024e-06 | 2016 | 2015-06-20 | C | 1 | 0.00042323 | 3.0238e-06
5541077 | 2015-06-20 10:56 | 2015-06-26 15:00 | 8884 | 142 | 350458.0333 | 2468.0143 | 2465.0143 | 1.0597 | 350032.0333 | 1.0584 | 0.00042937 | Restore Supply on Device 575 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 784695 | 15/07/15. JOb Stuck, escalated by Paul D. Tripping on Recloser CB 575B-C Phase. Feeder restored to Links 440 but unable to gain access to MABS 2995 due to closed roads. (Storm damage due to floods). Request changed to 2R due to network network damage. ASW | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-20 | c | 1.0584 | 0.00042937 | 2016 | 2015-06-20 | C | 142 | 1.0584 | 0.00042937
5542481 | 2015-06-20 10:40 | 2015-06-23 11:32 | 4371.75 | 408 | 145430.1167 | 356.4464 | 353.4464 | 0.43975 | 144206.1167 | 0.43604 | 0.0012337 | Restore Supply on Device D11 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5483 | Two different fault 1 past Fuses 5483 and the other past ABS 5479 - unable to access either work area due to slips. Lines repaired and power restored beyond ABS 5479 on CB 7121. Replaced 2 x crossarms and pulled up 2 spans of conductors beyond Fuses 5483. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.43604 | 0.0012337 | 2016 | 2015-06-20 | C | 408 | 0.43604 | 0.0012337
5542812 | 2015-06-20 11:59 | 2015-06-22 16:24 | 3145 | 6 | 18870 | 3145 | 3142 | 0.057058 | 18852 | 0.057004 | 1.8143e-05 | Restore Supply on Device 4556W | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 400 Beamish Road | 11kV HV Fuses 4248 and 4468 both Open and Tagged at by Ben Englebretsen. Flooding past these fusing points. NOTE the two jobs linked together as both jobs cover the same area and section of line, ASW 22/06. Revisit site (if Possible) ascertain damage an | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.057004 | 1.8143e-05 | 2016 | 2015-06-20 | C | 6 | 0.057004 | 1.8143e-05
5543637 | 2015-06-20 12:22 | 2015-06-21 10:44 | 1342 | 212 | 116581 | 549.9104 | 546.9104 | 0.35251 | 115945 | 0.35059 | 0.00064104 | Restore Supply on Device 2 | 22 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 808218 | Glen has found the fault but the tree trimmer can not gain access to the fault due to the road being closed - Glen will call the tree trimmers in the morning. NDR 047052 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.35059 | 0.00064104 | 2016 | 2015-06-20 | C | 212 | 0.35059 | 0.00064104
5543977 | 2015-06-20 12:48 | 2015-06-20 14:02 | 73.7167 | 592 | 14462.6167 | 24.4301 | 21.4301 | 0.043731 | 12686.6167 | 0.038361 | 0.0017901 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9182/2 | Line sectionalised & patrolled no fault found. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.038361 | 0.0017901 | 2016 | 2015-06-20 | C | 592 | 0.038361 | 0.0017901
5548956 | 2015-06-20 13:21 | 2015-06-20 18:21 | 299.6167 | 255 | 60710.0667 | 238.0787 | 235.0787 | 0.18357 | 59945.0667 | 0.18126 | 0.00077106 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | n/a | Line Patrolled & sectionalised unknown fault. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.18126 | 0.00077106 | 2016 | 2015-06-20 | C | 255 | 0.18126 | 0.00077106
5555468 | 2015-06-20 14:11 | 2015-06-20 19:30 | 319 | 466 | 65798 | 141.1974 | 138.1974 | 0.19896 | 64400 | 0.19473 | 0.0014091 | Electric Job | 11 | Unplanned | DISTRIBUTION EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 11kV Switchgear CNR HOBSON & GILL ST NEW PLYMOUTH | TX ON FIRE EVENT NUMBER F1867324 , ETA PLEASE 04 801 0812 ALANA AT HUB ADVISED CONTROL ADVISED ADVISED FIRE 10 MINUTES ETA Installed 3 generators to feed 3 LV tx's & put in some LV backfeeds. 11kV switchgear exploded. Blair to speak to Trent T about getti | F3 | CITY 3 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.19473 | 0.0014091 | 2016 | 2015-06-20 | C | 466 | 0.19473 | 0.0014091
5556060 | 2015-06-20 15:14 | 2015-06-21 11:14 | 1199.8167 | 302 | 57585.0833 | 190.6791 | 187.6791 | 0.17412 | 56679.0833 | 0.17138 | 0.00091318 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 204762 | KPT CB1 Recloser 9606 tripped E/F, L/O fedder sectionalised and fault isolated to beyond ABS SB1 022. Line break cut at pole 204762 ( TX TB1 145 ) & ABS SB1 022 closed. Beyond line break remained offloaded overnight due to terrain & bad weather. To be pa | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.17138 | 0.00091318 | 2016 | 2015-06-20 | C | 302 | 0.17138 | 0.00091318
5557209 | 2015-06-20 15:50 | 2015-06-20 19:18 | 208.1333 | 74 | 15401.8667 | 208.1333 | 205.1333 | 0.046572 | 15179.8667 | 0.0459 | 0.00022376 | Restore Supply on Device TC3499 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12384 | Emergency switching to repair broken Fuse holder FC2177. Isolations between ABS IC1301, Links 9852/6, ABS IC1058 & ABS IC1050 with back feeds via ABS 1356 & ABS IC1274. Fuse holder replaced all service restored. Materials 1 x H/V Fuse Holder & 1 x 15A O/H | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.0459 | 0.00022376 | 2016 | 2015-06-20 | C | 74 | 0.0459 | 0.00022376
5557380 | 2015-06-20 14:17 | 2015-06-24 14:55 | 5798.2 | 91 | 308726.8 | 3392.6022 | 3389.6022 | 0.93352 | 308453.8 | 0.93269 | 0.00027516 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 11kV Recloser 693 tripped L/O. All works being managed off OMS 5557384 due to GIS error (error has been escalated, due to ABS 4442 not in GIS causing job to go to resotredd state. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-20 | c | 0.93269 | 0.00027516 | 2016 | 2015-06-20 | C | 91 | 0.93269 | 0.00027516
5557769 | 2015-06-20 15:46 | 2015-06-20 15:54 | 8.0167 | 154 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00046566 | Restore Supply on Device 5258E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711776 | 107 Upper Ngariki Road - Rohotu Crossarm on the power pole outside is arcing -4:17pm Called Tarn. Changed to 2R after the fact due to workload at NOC, ASW. Replace entire cross arm assembly due to failed insulator and burnt cross arm . | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0 | 0.00046566 | 2016 | 2015-06-20 | C | 154 | 0 | 0.00046566
5557891 | 2015-06-20 14:57 | 2015-06-27 15:55 | 10138.1333 | 111 | 988573.8 | 8906.0703 | 8903.0703 | 2.9892 | 988240.8 | 2.9882 | 0.00033564 | Restore Supply on Device 513 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | Numerous | 11kV Recloser 513 tripped E/F L/O. Downers advise there is no access to the road, let alone the network to effect patrolling etc due to excessive flooding at Waitotara. DO NOT include in KPI's please, ASW. Major storm and flooding with slips in area. Ex | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-06-20 | c | 2.9882 | 0.00033564 | 2016 | 2015-06-20 | C | 111 | 2.9882 | 0.00033564
5558809 | 2015-06-20 17:12 | 2015-06-21 15:37 | 1344.35 | 181 | 78433.8667 | 433.3363 | 430.3363 | 0.23717 | 77890.8667 | 0.23552 | 0.0005473 | Restore Supply on Device RC26 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | H1961 | WLN CB3 Recloser RC26 tripped ( no flags ) feeder sectionalised with fault isolated to beyond ABS 769. Found at pole H1961 1 x line down at compresion sleeve. Sleeve replaced, service restored. Materials 3 meters conductor, 2 x comp sleeves. NOTE Fuses F | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.23552 | 0.0005473 | 2016 | 2015-06-20 | C | 181 | 0.23552 | 0.0005473
5561723 | 2015-06-20 18:12 | 2015-06-20 21:19 | 186.2333 | 2 | 372.4667 | 186.2333 | 183.2333 | 0.0011263 | 366.4667 | 0.0011081 | 6.0475e-06 | Restore Supply on Device TC3368 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP23 | Replace 2 x 6 A H/V, O/H Fuses at FP23 suspect line clash with high wind | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.0011081 | 6.048e-06 | 2016 | 2015-06-20 | C | 2 | 0.0011081 | 6.0475e-06
5564147 | 2015-06-20 18:39 | 2015-06-23 16:30 | 4190.5333 | 186 | 106728.8333 | 573.8109 | 570.8109 | 0.32272 | 106170.8333 | 0.32104 | 0.00056242 | Restore Supply on Device 1133 | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Temp break at pole 805157 | 22kV CB 1133 Triped A, B, C, O/C L/O. Lines down at 379 Onepuhi Rd, yet to ascertain damage etc. Have cut a temp line brak at pole 805157 (just before tx Z149). Temp break applied to emap model by ASW, Follow /refferal job to effect repairs for downed lin | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.32104 | 0.00056242 | 2016 | 2015-06-20 | C | 186 | 0.32104 | 0.00056242
5564364 | 2015-06-20 19:00 | 2015-06-21 00:41 | 340.1167 | 147 | 31008.4167 | 210.9416 | 207.9416 | 0.093762 | 30567.4167 | 0.092429 | 0.00044449 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 248289 | PKW CB4 Recloser RS9463 tripped E/F, L/O. Feeder sectionalised with trees through line at pole 248289. ( high wind & rain caused slip to bring trees down ) Isolation between ABS SF6 014 & ABS SF6 018 with back feed via ABS SF6 039. Lines repaired all | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.092429 | 0.00044449 | 2016 | 2015-06-20 | C | 147 | 0.092429 | 0.00044449
5564526 | 2015-06-20 19:20 | 2015-06-21 14:14 | 1134.3667 | 27 | 3610.6833 | 133.729 | 130.729 | 0.010918 | 3529.6833 | 0.010673 | 8.1642e-05 | Restore Supply on Device Y67 | 6.6 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 795 | Fault restoration due to severe weather conditions. Fuses 795 opened and 481 untagged and closed. Fuses 795 then reclosed. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-06-20 | c | 0.010673 | 8.1642e-05 | 2016 | 2015-06-20 | C | 27 | 0.010673 | 8.1642e-05
5567100 | 2015-06-20 22:17 | 2015-06-24 15:06 | 5329 | 190 | 14733.6667 | 77.5456 | 74.5456 | 0.044551 | 14163.6667 | 0.042828 | 0.00057451 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 279 TE MATAI ROAD | Fuses E90 found tripped due to major flooding issue. All conductors had come down into the river. Isolation from ABS E78 and E69 where a Temp line break was installed (Pole P02115). Re-livened area OK. Referral OMS issued for repairs. No.5578941. 22/6, wo | F3 | KEITH ST 12 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.042828 | 0.00057452 | 2016 | 2015-06-20 | C | 190 | 0.042828 | 0.00057451
5567280 | 2015-06-20 21:59 | 2015-06-21 15:10 | 1031 | 858 | 179337 | 209.0175 | 206.0175 | 0.54227 | 176763 | 0.53449 | 0.0025944 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 14465 | Tripping on CB8 E/F. Feeder sectionalised / patrolled with a pole found down due to a slip. Isolation from ABS E46. To be repaired during daylight hours.Pole replaced P14920 replaced. Referral job OMS 5578848 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.53449 | 0.0025944 | 2016 | 2015-06-20 | C | 858 | 0.53449 | 0.0025944
5568475 | 2015-06-20 22:27 | 2015-06-21 21:12 | 1365 | 606 | 498230 | 822.1617 | 819.1617 | 1.5065 | 496412 | 1.501 | 0.0018324 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB4 | Blink Bonnie CB4 tripped on E/F, Neg Sequence O/C. Power restored to ABS 704 but unable to continue due to slip on road. Area patrolled by Hellicopter but nothing seen. Feeder restored OK. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-06-20 | c | 1.501 | 0.0018324 | 2016 | 2015-06-20 | C | 606 | 1.501 | 0.0018324
5571324 | 2015-06-20 23:01 | 2015-06-21 09:35 | 634.4333 | 1 | 634.4333 | 634.4333 | 631.4333 | 0.0019184 | 631.4333 | 0.0019093 | 3.0238e-06 | Restore Supply on Device TC354 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 219 Piakoiti Rd, Richmond Downs | power off at 5pm back on 9:30pm, then off again and customer phoned it through and then power came back on just after 11:00pm. When FM arrived onsite this morning, the power was on. FM tried to contact customer before hand but due to the location there is | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-06-20 | c | 0.0019093 | 3.024e-06 | 2016 | 2015-06-20 | C | 1 | 0.0019093 | 3.0238e-06
5575920 | 2015-06-21 00:43 | 2015-06-21 03:04 | 141.0667 | 41 | 5617.9833 | 137.024 | 134.024 | 0.016987 | 5494.9833 | 0.016616 | 0.00012397 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | H38 | Tripping on recloser CB10050 on Phase B O/C. Fault caused by large tree through lines with isolation at ABS H38 and Links 10051. Backfed at ABS 10098. Referral Job put in for repairs - OMS 5578945 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.016616 | 0.00012397 | 2016 | 2015-06-21 | C | 41 | 0.016616 | 0.00012397
5576254 | 2015-06-22 11:45 | 2015-06-22 14:07 | 142.25 | 50 | 7112.5 | 142.25 | 139.25 | 0.021506 | 6962.5 | 0.021053 | 0.00015119 | Referral: Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Paraonui Road, Tokoroa . B0040 | At pole B0040 cracked insulator & burnt x arm to be replaced in morning. 7.35am - Brad. crew request as per control Crew to attend at first light tomorrow | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-06-22 | c | 0.021053 | 0.00015119 | 2016 | 2015-06-22 | C | 50 | 0.021053 | 0.00015119
5577058 | 2015-06-21 01:28 | 2015-06-21 03:52 | 143.6667 | 396 | 30392.4667 | 76.7487 | 73.7487 | 0.0919 | 29204.4667 | 0.088307 | 0.0011974 | Restore Supply on Device K13 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | CB K13 | Tripping on Recloser K13 on Phase A O/C. Feeder sectionalised / patrolled but nothing found. Restored OK. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.088307 | 0.0011974 | 2016 | 2015-06-21 | C | 396 | 0.088307 | 0.0011974
5577906 | 2015-06-21 03:39 | 2015-06-21 07:37 | 237.85 | 930 | 139734.1 | 150.2517 | 147.2517 | 0.42252 | 136944.1 | 0.41409 | 0.0028121 | Restore Supply on Device 11 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 767742 | Line break made and power restored to line break | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.41409 | 0.0028121 | 2016 | 2015-06-21 | C | 930 | 0.41409 | 0.0028121
5578952 | 2015-06-21 07:03 | 2015-06-22 16:20 | 1997 | 2 | 3994 | 1997 | 1994 | 0.012077 | 3988 | 0.012059 | 6.0475e-06 | Restore Supply on Device X536 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 367183 | This was affected by job 5599501. Notes from that job:"Line down across river. River flooded and caused slip bringing down trees. Materials Used: HV 70 mtrs squirrel conductor & 6 sleeves. LV: 130 metres 16mm Cu. covered conductor & 8x 16mm sleeves. NDR 0 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.012059 | 6.048e-06 | 2016 | 2015-06-21 | C | 2 | 0.012059 | 6.0475e-06
5578964 | 2015-06-21 07:33 | 2015-06-21 12:39 | 305.7167 | 1 | 305.7167 | 305.7167 | 302.7167 | 0.00092441 | 302.7167 | 0.00091534 | 3.0238e-06 | Restore Supply on Device T3/532 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | T3/352 | REPLACED HV FUSE IN TX T3/532. Will need to replace the transformer tomorrow as blown transformer but the customer has enough power for overnight. 3 Phase 30kVA transformer replaced by Bruce Mehrtens | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.00091534 | 3.024e-06 | 2016 | 2015-06-21 | C | 1 | 0.00091534 | 3.0238e-06
5578975 | 2015-06-21 09:11 | 2015-06-23 14:32 | 3201 | 1 | 3201 | 3201 | 3198 | 0.0096791 | 3198 | 0.00967 | 3.0238e-06 | Restore Supply on Device C6805 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CA465 | FM advise: needs to replace full set of hv fuses but can only patrol 2km up road because road inaccessible. will need to go back when road opens. Has numerous slips in area, strongly suspected we have sustained network damage. Currently Isolated at 11kV | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.00967 | 3.024e-06 | 2016 | 2015-06-21 | C | 1 | 0.00967 | 3.0238e-06
5579016 | 2015-06-21 08:03 | 2015-06-22 11:08 | 1625.8333 | 67 | 108930.8333 | 1625.8333 | 1622.8333 | 0.32938 | 108729.8333 | 0.32877 | 0.00020259 | Restore Supply on Device T6/181 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | T6/181 | 2 x hv tx still under water. tx t6-181 and tx t6-200. 5:09pm Tracey reliven at T6/181 she will check TX T6/200. Transformers relivened last night. Nothing repaired or replaced. | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.32877 | 0.00020259 | 2016 | 2015-06-21 | C | 67 | 0.32877 | 0.00020259
5579150 | 2015-06-21 09:00 | 2015-06-21 11:15 | 135 | 237 | 31995 | 135 | 132 | 0.096745 | 31284 | 0.094595 | 0.00071663 | Restore Supply on Device LI1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI179 | 11kV CB LI6 tripped L/O. Lines in river between Sub and ABS LI179. Cannot repair until flood waters recede, May be able to sort on Mon, Tues dependent on water level. Does not affect any customers. Bruce Kerr attended originally, he will have additional d | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.094595 | 0.00071663 | 2016 | 2015-06-21 | C | 237 | 0.094595 | 0.00071663
5579401 | 2015-06-21 09:07 | 2015-06-21 12:04 | 177 | 217 | 18736 | 86.341 | 83.341 | 0.056653 | 18085 | 0.054685 | 0.00065616 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P09820 | Repaired lines down @ pole P09820 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.054685 | 0.00065616 | 2016 | 2015-06-21 | C | 217 | 0.054685 | 0.00065616
5580311 | 2015-06-21 09:16 | 2015-06-23 18:08 | 3411.7167 | 4 | 13646.8667 | 3411.7167 | 3408.7167 | 0.041265 | 13634.8667 | 0.041229 | 1.2095e-05 | Restore Supply on Device CA465 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CA465 | 11kV Fuses CA 465 Tripped, unknow fault, no access due to slips and trees. Inspected by Henry Hood. Awaiting access once road cleared, ASW. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.041229 | 1.2095e-05 | 2016 | 2015-06-21 | C | 4 | 0.041229 | 1.2095e-05
5580393 | 2015-06-21 09:58 | 2015-06-21 17:59 | 480.7833 | 2 | 961.5667 | 480.7833 | 477.7833 | 0.0029075 | 955.5667 | 0.0028894 | 6.0475e-06 | Restore Supply on Device 2185T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2185T | Transformer 2185T found to be faulty - Isolated at own fuses - Transformer replaced - used 1x 30kVA Transformer | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.0028894 | 6.048e-06 | 2016 | 2015-06-21 | C | 2 | 0.0028894 | 6.0475e-06
5580522 | 2015-06-21 11:48 | 2015-06-23 14:58 | 3070 | 19 | 32265 | 1698.1579 | 1695.1579 | 0.097562 | 32208 | 0.097389 | 5.7451e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847617 | Road taken out as well as power poles and lines. Back of farm, Mt Curl Road, Hunterville. It is about 2km up the road as you turn off SH1. Brian Wilson on 027 22 99 135 or 06 3228 621. 21/6 12.19pm - isolated at fuse # 748 - all the houses beyond this poi | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.097389 | 5.7451e-05 | 2016 | 2015-06-21 | C | 19 | 0.097389 | 5.7451e-05
5580815 | 2015-06-21 13:02 | 2015-06-21 13:49 | 46.45 | 1 | 46.45 | 46.45 | 43.45 | 0.00014045 | 43.45 | 0.00013138 | 3.0238e-06 | Restore Supply on Device T3/206 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 182 MINGAROA ROAD, HALCOMBE | power back on. part of feeder | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.00013138 | 3.024e-06 | 2016 | 2015-06-21 | C | 1 | 0.00013138 | 3.0238e-06
5580935 | 2015-06-21 13:41 | 2015-06-21 15:04 | 82.5667 | 3 | 247.7 | 82.5667 | 79.5667 | 0.00074899 | 238.7 | 0.00072177 | 9.0713e-06 | Restore Supply on Device 868 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 868 | Lines down past Fuses 868 - Isolated at Fuses 868 - lines repaired - used 2 x Sleeves and 1 binder - cause unknown (weather). | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.00072177 | 9.071e-06 | 2016 | 2015-06-21 | C | 3 | 0.00072177 | 9.0713e-06
5580970 | 2015-06-21 16:53 | 2015-06-21 17:29 | 35.5333 | 166 | 5804.5333 | 34.9671 | 31.9671 | 0.017552 | 5306.5333 | 0.016046 | 0.00050194 | Restore Supply on Device TC4-361 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213827 | Repair broken DDO at TX TC4-361. Can field staff also please talk with Control about this job. Believe this issue may be affecting the power supplying recloser 9881. linked to 5581836. | F2 | PORTSIDE | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-06-21 | c | 0.016046 | 0.00050194 | 2016 | 2015-06-21 | C | 166 | 0.016046 | 0.00050194
5581149 | 2015-06-21 15:30 | 2015-06-21 15:58 | 28 | 91 | 2548 | 28 | 25 | 0.0077045 | 2275 | 0.0068791 | 0.00027516 | Restore Supply on Device K15 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P38033 | Repaired jumper on pole P38033. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.0068791 | 0.00027516 | 2016 | 2015-06-21 | C | 91 | 0.0068791 | 0.00027516
5589242 | 2015-06-21 17:39 | 2015-06-21 20:02 | 143.15 | 1 | 143.15 | 143.15 | 140.15 | 0.00043285 | 140.15 | 0.00042378 | 3.0238e-06 | Restore Supply on Device T8/113 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/113 | Replaced 2 x 2A HV fuses (2 out of 3). All other assets okay; nothing else replaced. Crew didn't call through control, as was 5km out of comms. Tried to get restoration time from crew but RT was not available again. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.00042378 | 3.024e-06 | 2016 | 2015-06-21 | C | 1 | 0.00042378 | 3.0238e-06
5589248 | 2015-06-20 17:40 | 2015-06-21 20:42 | 1622.1167 | 2372 | 2976148.0333 | 1254.6998 | 1251.6998 | 8.9992 | 2969032.0333 | 8.9776 | 0.0071724 | Restore Supply on Device 5 | 11 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | cb5 | CB5 tripped due to load transfer to Peat St Sub. | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-06-20 | c | 8.9776 | 0.0071724 | 2016 | 2015-06-20 | C | 2372 | 8.9776 | 0.0071724
5594021 | 2015-06-21 21:44 | 2015-06-22 14:08 | 983.9333 | 18 | 17710.8 | 983.9333 | 980.9333 | 0.053553 | 17656.8 | 0.05339 | 5.4428e-05 | Restore Supply on Device X2018 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 598 | Initially received auto-recloses on CB4566 on E/F. Fault caused by large span down, to dangerous to repair at night. To be repaired during daylight hours. Temp line break cut at Pole 802935 and referral job created to have repairs done once resources are | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.05339 | 5.4428e-05 | 2016 | 2015-06-21 | C | 18 | 0.05339 | 5.4428e-05
5597188 | 2015-06-21 20:53 | 2015-06-21 21:09 | 16.9 | 212 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00064104 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 4566 A/R on E/F | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0 | 0.00064104 | 2016 | 2015-06-21 | C | 212 | 0 | 0.00064104
5597668 | 2015-06-21 22:10 | 2015-06-22 14:50 | 999.4167 | 2 | 1998.8333 | 999.4167 | 996.4167 | 0.006044 | 1992.8333 | 0.0060259 | 6.0475e-06 | Restore Supply on Device 4266 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 707548 | Fused ABS 4266 Opened and Tagged, suspected 11kV cable fault. Requires investigation, testing and possible repairs. Attended by Pa Koro. Replaced 2x Lightning Arrestors. Chil Outage relates to the customer who called in for his neighbour. Outage removed f | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.0060259 | 6.048e-06 | 2016 | 2015-06-21 | C | 2 | 0.0060259 | 6.0475e-06
5598159 | 2015-07-14 08:45 | 2015-07-14 13:46 | 300.55 | 224 | 67323.2 | 300.55 | 297.55 | 0.20357 | 66651.2 | 0.20154 | 0.00067732 | NAPA ID:08382 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 432 | Reconductor from abs 432 to pole 749588. Works location: Barriball St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-07-14 | b | 0.10077 | 0.00033866 | 2016 | 2015-07-14 | B | 224 | 0.20154 | 0.00067732
5598213 | 2015-07-14 09:01 | 2015-07-14 15:48 | 407.4 | 118 | 48073.2 | 407.4 | 404.4 | 0.14536 | 47719.2 | 0.14429 | 0.0003568 | NAPA ID:09928 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Stuck child | Replace ABS IC1347 & crossarms at various locations.Works location: Scotsman Valley Rd Kiwitahi. WO 30003283 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-14 | b | 0.072146 | 0.0001784 | 2016 | 2015-07-14 | B | 118 | 0.14429 | 0.0003568
5598327 | 2015-07-15 09:30 | 2015-07-15 12:55 | 205.0833 | 47 | 9638.9167 | 205.0833 | 202.0833 | 0.029146 | 9497.9167 | 0.028719 | 0.00014212 | NAPA ID:10057 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5968 | Replace ABS 6012 + xarms & upgrade Earths. Works location: ELtham Rd Kaponga. WO 10159896 | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-07-15 | b | 0.01436 | 7.1058e-05 | 2016 | 2015-07-15 | B | 47 | 0.028719 | 0.00014212
5598350 | 2015-06-22 09:39 | 2015-06-22 09:51 | 12 | 714 | 8209 | 11.4972 | 8.4972 | 0.024822 | 6067 | 0.018345 | 0.002159 | Restore Supply on Device 18 | 11 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | Tahuna Sub | CB 18, CB1 & CB3 tripped while work was being carried out on T1. When the Bucholz was bled on the Isolated and Earthed T1, the transformer's protection saw this as a fault and as the 11kV CB17 was showing Closed (Circuit Earth) it opened the BUS Coupler C | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-06-22 | c | 0.018345 | 0.002159 | 2016 | 2015-06-22 | C | 714 | 0.018345 | 0.002159
5599174 | 2015-06-22 12:51 | 2015-06-22 16:55 | 244.4 | 19 | 4643.6 | 244.4 | 241.4 | 0.014041 | 4586.6 | 0.013869 | 5.7451e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 739562 | Pole on a severe lean by overhead rail bridge on Douglas Road. Contact is Neil Smiley @ 06 765 7783. 5.55 phoned hub for update tarn is calling Alan. Two Poles installed either side of subsidence. See outage for this Job. OMS 5600495 | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.013869 | 5.7451e-05 | 2016 | 2015-06-22 | C | 19 | 0.013869 | 5.7451e-05
5599290 | 2015-06-21 07:03 | 2015-06-21 11:04 | 241 | 40 | 9640 | 241 | 238 | 0.029149 | 9520 | 0.028786 | 0.00012095 | Restore Supply on Device U41 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | U39 | Faultman directed to recloser U39. Found recloser open, Patrolled line nothing obvious found and supply restored | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.028786 | 0.00012095 | 2016 | 2015-06-21 | C | 40 | 0.028786 | 0.00012095
5599501 | 2015-06-22 11:36 | 2015-06-22 16:20 | 284 | 14 | 3976 | 284 | 281 | 0.012022 | 3934 | 0.011895 | 4.2333e-05 | Restore Supply on Device 840 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 367183 | Line down across river. River flooded and caused slip bringing down trees. Materials Used: HV 70 mtrs squirrel conductor & 6 sleeves. LV: 130 metres 16mm Cu. covered conductor & 8x 16mm sleeves NDR 047054 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.011895 | 4.2333e-05 | 2016 | 2015-06-22 | C | 14 | 0.011895 | 4.2333e-05
5599523 | 2015-07-07 09:16 | 2015-07-07 15:26 | 369.9833 | 54 | 19979.1 | 369.9833 | 366.9833 | 0.060412 | 19817.1 | 0.059922 | 0.00016328 | NAPA ID:09819 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP506 | Replace poles, crossarms and conductors. Install DOF's TEMP 68 pole227244. Works location; Pukehina Parade WO 30003712 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-07 | b | 0.029961 | 8.1642e-05 | 2016 | 2015-07-07 | B | 54 | 0.059922 | 0.00016328
5599524 | 2015-07-14 09:30 | 2015-07-14 15:10 | 340 | 12 | 4080 | 340 | 337 | 0.012337 | 4044 | 0.012228 | 3.6285e-05 | NAPA ID:09304 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1690 | Live Line: To install new 11kV fuses FP1690 complete with termination arms at Pole # G0548. Access permit: To replace 11kV cross arms etc; at poles G0549 and G12349. Works location: Hwy 27 Matamata. WO 30002943 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-14 | b | 0.006114 | 1.8143e-05 | 2016 | 2015-07-14 | B | 12 | 0.012228 | 3.6285e-05
5599660 | 2015-06-22 12:32 | 2015-06-22 15:37 | 185.2667 | 1 | 185.2667 | 185.2667 | 182.2667 | 0.0005602 | 182.2667 | 0.00055113 | 3.0238e-06 | Restore Supply on Device 5203E | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 846031 | Transformer Faulty and will need to be replaced. Farmer happy to leave for a couple of days for the paddock to dry out. Feeds Irrigation Pump. Farmer notified faultman he does not want fault crew driving over the water ground to his irrigation pumps where | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.00055113 | 3.024e-06 | 2016 | 2015-06-22 | C | 1 | 0.00055113 | 3.0238e-06
5600131 | 2015-06-23 10:34 | 2015-06-23 12:29 | 115 | 2 | 230 | 115 | 112 | 0.00069546 | 224 | 0.00067732 | 6.0475e-06 | Restore Supply on Device T3/81 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | P28438 | 1061 Makino Road, Feilding Nearest ICP - Customer at 1060 Makino Rd advises a pole is fully exposed due to the makino river flooding - please check for safety. 2nd pole in off the road. 1.39pm advised Joanne at svs hub & control this pole has 11kv line on | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.00067732 | 6.048e-06 | 2016 | 2015-06-23 | C | 2 | 0.00067732 | 6.0475e-06
5600148 | 2015-06-22 11:58 | 2015-06-22 14:00 | 122.4333 | 2 | 131.0167 | 65.5083 | 62.5083 | 0.00039616 | 125.0167 | 0.00037802 | 6.0475e-06 | Restore Supply on Device 7296 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7296 | Replace 2 x 10A Fuses | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.00037802 | 6.048e-06 | 2016 | 2015-06-22 | C | 2 | 0.00037802 | 6.0475e-06
5600172 | 2015-06-23 09:50 | 2015-06-23 12:04 | 133.5833 | 4 | 534.3333 | 133.5833 | 130.5833 | 0.0016157 | 522.3333 | 0.0015794 | 1.2095e-05 | Referral: Restore Supply on Device T2214 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 7398 | to remove vine from structure, will need shutdown will only affect this customer, treescape to liaise with Jason as to time. Switching carried out by Downer. Trees and Vines cleared by Treescape | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.0015794 | 1.2095e-05 | 2016 | 2015-06-23 | C | 4 | 0.0015794 | 1.2095e-05
5600176 | 2015-06-23 20:00 | 2015-06-23 20:20 | 20 | 170 | 3400 | 20 | 17 | 0.010281 | 2890 | 0.0087387 | 0.00051404 | NAPA ID:10515 TP_CARRINGTON GXP > CITY SUB > CITY 3 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch 429 | Magnefix 297 failed on Sat 20 June. Currently work to replace switchgear with Safelink CFCF is under permit. Three transformers is currently running on generators. Tx 2005N, 487 & 1151. This application is to allow generators to be switched off and discon | F3 | CITY 3 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2015-06-23 | b | 0.0043693 | 0.00025702 | 2016 | 2015-06-23 | B | 170 | 0.0087387 | 0.00051404
5600422 | 2015-06-22 16:34 | 2015-06-23 11:53 | 1159 | 1 | 1159 | 1159 | 1156 | 0.0035045 | 1156 | 0.0034955 | 3.0238e-06 | Restore Supply on Device X1382 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 802846 | 5804 Tutaenui Road, Marton - lines down - trees have fallen onto lines. 4.00pm called svs hub to advise 999 and taken into control. 8.38pm email sent to Sandy for update. 7.40am 23/6 email update from Sandy - Adam was there yesterday but has to go back to | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.0034955 | 3.024e-06 | 2016 | 2015-06-22 | C | 1 | 0.0034955 | 3.0238e-06
5600965 | 2015-06-22 15:21 | 2015-06-22 19:16 | 234.65 | 7 | 296.9333 | 42.419 | 39.419 | 0.00089786 | 275.9333 | 0.00083436 | 2.1166e-05 | Restore Supply on Device 1043 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 1043 | two Fuses at fuses 1043 found blown - line patroled with no fault found - used 2x 20 amp fuses | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0.00083436 | 2.1166e-05 | 2016 | 2015-06-22 | C | 7 | 0.00083436 | 2.1166e-05
5601648 | 2015-06-22 22:49 | 2015-06-22 22:51 | 1.75 | 283 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00085572 | Restore Supply on Device TA9 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | TA9 | CB TA 9 Tripped E/F, A/R - Not Patrolled | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-06-22 | c | 0 | 0.00085572 | 2016 | 2015-06-22 | C | 283 | 0 | 0.00085572
5602399 | 2015-07-08 08:48 | 2015-07-08 14:20 | 331.7 | 50 | 16585 | 331.7 | 328.7 | 0.050149 | 16435 | 0.049696 | 0.00015119 | NAPA ID:09823 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP423 | Replace poles, crossarms and conductors. Works location: Pukehina Parade. WO 30003712 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 0.024848 | 7.5594e-05 | 2016 | 2015-07-08 | B | 50 | 0.049696 | 0.00015119
5602418 | 2015-07-14 09:01 | 2015-07-14 15:01 | 359.8333 | 87 | 31305.5 | 359.8333 | 356.8333 | 0.09466 | 31044.5 | 0.093871 | 0.00026307 | NAPA ID:09824 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 227244 | Replace poles, crossarms and conductors. Works location: Pukehina Parade. WO 30003712 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-14 | b | 0.046936 | 0.00013153 | 2016 | 2015-07-14 | B | 87 | 0.093871 | 0.00026307
5602864 | 2015-06-23 09:28 | 2015-06-23 09:32 | 4.3333 | 438 | 1898 | 4.3333 | 1.3333 | 0.0057391 | 584 | 0.0017659 | 0.0013244 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | CB3 | Tower Road CB3 Te Poi Tripped O/C L/O. Trippng caused due to line clash whilst pole F1990 being straightened. See also OMS 5602463. Safety Manager Incident 478767 Raised. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.0017659 | 0.0013244 | 2016 | 2015-06-23 | C | 438 | 0.0017659 | 0.0013244
5603306 | 2015-07-15 09:00 | 2015-07-15 14:03 | 302.3 | 87 | 26300.1 | 302.3 | 299.3 | 0.079525 | 26039.1 | 0.078736 | 0.00026307 | NAPA ID:09827 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 227244 | Replace poles, crossarms and conductors. Works location: Pukehina Parade. WO 30003712 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-15 | b | 0.039368 | 0.00013153 | 2016 | 2015-07-15 | B | 87 | 0.078736 | 0.00026307
5603312 | 2015-06-23 09:34 | 2015-06-23 10:54 | 79.5 | 1 | 79.5 | 79.5 | 76.5 | 0.00024039 | 76.5 | 0.00023132 | 3.0238e-06 | Restore Supply on Device FP512 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP512 | 2 x 6A HV Fuses Replaced. Caused by Pukeko flying into Lines. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.00023132 | 3.024e-06 | 2016 | 2015-06-23 | C | 1 | 0.00023132 | 3.0238e-06
5603415 | 2015-07-08 09:45 | 2015-07-08 15:16 | 331.05 | 83 | 27477.15 | 331.05 | 328.05 | 0.083084 | 27228.15 | 0.082331 | 0.00025097 | NAPA ID:09965 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1256 | Replace H/V Crossarms and T/X's at Various Sites. Works location: Hwy 27 Mangatarata. WO 10147831 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 0.041166 | 0.00012549 | 2016 | 2015-07-08 | B | 83 | 0.082331 | 0.00025097
5603883 | 2015-06-23 11:18 | 2015-06-23 14:03 | 165.55 | 1 | 165.55 | 165.55 | 162.55 | 0.00050058 | 162.55 | 0.00049151 | 3.0238e-06 | Restore Supply on Device Y95 | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | Y95 | Replaced 2x 3Amp HV Links | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-06-23 | c | 0.00049151 | 3.024e-06 | 2016 | 2015-06-23 | C | 1 | 0.00049151 | 3.0238e-06
5604255 | 2015-06-23 11:17 | 2015-06-23 13:30 | 133 | 474 | 61122 | 128.9494 | 125.9494 | 0.18482 | 59700 | 0.18052 | 0.0014333 | Restore Supply on Device IC2718 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IC2717 | Insulator cracked while carrying out LLP 9551-01. Isolated area between ABS IC2716 & ABS IC2718. Replaced insulator and completed part of work which was to be carried out on LLP. Relivened | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.18052 | 0.0014333 | 2016 | 2015-06-23 | C | 474 | 0.18052 | 0.0014333
5605300 | 2015-07-08 09:15 | 2015-07-08 14:20 | 304.7833 | 48 | 14629.6 | 304.7833 | 301.7833 | 0.044236 | 14485.6 | 0.043801 | 0.00014514 | NAPA ID:09772 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC3-016 | Replace Poles and cross arms. Works location: Prole Rd. WO 30002379 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-08 | b | 0.0219 | 7.257e-05 | 2016 | 2015-07-08 | B | 48 | 0.043801 | 0.00014514
5605353 | 2015-06-23 11:35 | 2015-06-23 14:27 | 171.9833 | 9 | 1547.85 | 171.9833 | 168.9833 | 0.0046803 | 1520.85 | 0.0045987 | 2.7214e-05 | Restore Supply on Device FP552 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F1990 | 5605568 & 5605655 are linked to this. Part of Outage to resag conductors after Northpower caused a line clash See Incident # 478767. | F4 | BANKS ST | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.0045987 | 2.7214e-05 | 2016 | 2015-06-23 | C | 9 | 0.0045987 | 2.7214e-05
5605566 | 2015-06-23 22:38 | 2015-06-23 23:31 | 53.3833 | 726 | 12501.3167 | 17.2194 | 14.2194 | 0.037801 | 10323.3167 | 0.031215 | 0.0021953 | Electric Job | 11 | Unplanned | ZONE SUB EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | Reconfigure Roberts Ave sub back feeds | NOC require the 11kV Back feeds for Roberts Ave Sub reconfigured to mitigate the phase shift issues. Currently fed from WGE Sub, requires changing to PST. Cause has been the flooding and loss of 33kV line to ROB and oss of PST sub last weekend. Has been d | F3 | PEAT ST INLAND | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.031215 | 0.0021953 | 2016 | 2015-06-23 | C | 726 | 0.031215 | 0.0021953
5605602 | 2015-06-30 13:33 | 2015-06-30 15:23 | 110 | 3 | 330 | 110 | 107 | 0.00099784 | 321 | 0.00097063 | 9.0713e-06 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5825 | at 13:33, Waihapa Sub, CB 5841 Origin 2 Feeder. Report came in from production station on the 23/06/15 that they had low voltage on one phase. Called Control on 30/06/15 for follow up with this issue. Duty NC did not know of any issues but dispatched faul | F1 | ORIGIN 2 | STRATFORD | Taranaki | WAIHAPA SUB | Western Electricity | POWERCO | 2015-06-30 | c | 0.00097063 | 9.071e-06 | 2016 | 2015-06-30 | C | 3 | 0.00097063 | 9.0713e-06
5605616 | 2015-06-23 13:19 | 2015-06-23 15:31 | 132.0167 | 1 | 132.0167 | 132.0167 | 129.0167 | 0.00039919 | 129.0167 | 0.00039012 | 3.0238e-06 | Restore Supply on Device X2264 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2264 | Replaced 3x 8 Amp fuses. See OMS 5558803 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.00039012 | 3.024e-06 | 2016 | 2015-06-23 | C | 1 | 0.00039012 | 3.0238e-06
5605644 | 2015-07-16 08:43 | 2015-07-16 15:16 | 393 | 1 | 393 | 393 | 390 | 0.0011883 | 390 | 0.0011793 | 3.0238e-06 | NAPA ID:10000 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 369693 | to cut jumpers live line at pole 369693 to isolate for pole change at pole 829936 then reinstate jumpers live line at pole 369693. Works location: Cockburn St and South Rd. WO 30000781 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-07-16 | b | 0.00058963 | 1.512e-06 | 2016 | 2015-07-16 | B | 1 | 0.0011793 | 3.0238e-06
5605655 | 2015-06-23 11:22 | 2015-06-23 14:45 | 203.4167 | 3 | 610.25 | 203.4167 | 200.4167 | 0.0018452 | 601.25 | 0.001818 | 9.0713e-06 | Restore Supply on Device TC3157 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2934, TC3157 |  | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.001818 | 9.071e-06 | 2016 | 2015-06-23 | C | 3 | 0.001818 | 9.0713e-06
5605875 | 2015-07-13 09:31 | 2015-07-13 11:53 | 141.8833 | 304 | 43132.5333 | 141.8833 | 138.8833 | 0.13042 | 42220.5333 | 0.12766 | 0.00091922 | NAPA ID:10546 TP_CARRINGTON GXP > KATERE SUB > KATERE 8 | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 454 | Installing new cables and switchgear for new road layout on SH 3 done in several stages. This is stage 2 of 3. To change over Queens Rd feed to new Safelink CCC 454/2. This application replaces NAPA 9915. Stage 1 is NAPA 10544 & Stage 3 is NAPA 10547 | F3 | KATERE 8 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-07-13 | b | 0.063832 | 0.00045961 | 2016 | 2015-07-13 | B | 304 | 0.12766 | 0.00091922
5605894 | 2015-06-20 14:29 | 2015-06-23 15:19 | 4370.25 | 5 | 21851.25 | 4370.25 | 4367.25 | 0.066073 | 21836.25 | 0.066028 | 1.5119e-05 | Restore Supply on Device 1362 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803587 | Replace 3 x Insulators, 3 x binders & 1 x center bolt | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-20 | c | 0.066028 | 1.5119e-05 | 2016 | 2015-06-20 | C | 5 | 0.066028 | 1.5119e-05
5605920 | 2015-06-21 16:35 | 2015-06-23 14:55 | 2780.3167 | 2 | 5560.6333 | 2780.3167 | 2777.3167 | 0.016814 | 5554.6333 | 0.016796 | 6.0475e-06 | Restore Supply on Device X4124 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1433 | Removed branch from lines & replaced 2x 10Amp Links at fuses 1433 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-06-21 | c | 0.016796 | 6.048e-06 | 2016 | 2015-06-21 | C | 2 | 0.016796 | 6.0475e-06
5605969 | 2015-07-13 22:05 | 2015-07-14 02:40 | 274.05 | 30 | 8221.5 | 274.05 | 271.05 | 0.02486 | 8131.5 | 0.024588 | 9.0713e-05 | NAPA ID:09331 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CRANE SUPPLY | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G S4630 | Find and repair faulty Mech on Fuse/Sw FP440. Works location: Taiato Place. WO 30008663 | F1 | CRANE SUPPLY | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0.012294 | 4.5356e-05 | 2016 | 2015-07-13 | B | 30 | 0.024588 | 9.0713e-05
5606004 | 2015-06-23 15:44 | 2015-06-23 17:00 | 76 | 5 | 380 | 76 | 73 | 0.001149 | 365 | 0.0011037 | 1.5119e-05 | Restore Supply on Device TC1002 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1002 | 2 x 2A HV Fuses. Suspect Line Clash | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.0011037 | 1.5119e-05 | 2016 | 2015-06-23 | C | 5 | 0.0011037 | 1.5119e-05
5606267 | 2015-06-23 19:40 | 2015-06-23 23:05 | 204.5167 | 38 | 5885.7667 | 154.8886 | 151.8886 | 0.017797 | 5771.7667 | 0.017452 | 0.0001149 | Restore Supply on Device 1092 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1092 | Faulty Fuse carrier and base found at Transformer 1092 - Isolated at ABS's 363, 537, & 561 back feed installed via ABS 8717 - used 3x DDO's 3x 8amp fuses, 3x sleeves and 1 mtr of conductor | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.017452 | 0.0001149 | 2016 | 2015-06-23 | C | 38 | 0.017452 | 0.0001149
5606547 | 2015-06-23 17:15 | 2015-06-23 17:35 | 20 | 3 | 60 | 20 | 17 | 0.00018143 | 51 | 0.00015421 | 9.0713e-06 | Restore Supply on Device X2178 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer X2178 | 24/6 8.55am - Retailer called for an update. Wanganui depot advise it will be attended today. 24/6 11.37am - Retailer called again for an update. Sandy at Wanganui advise the job should be attended shortly as FM is just on a close approach and this should | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-06-23 | c | 0.00015421 | 9.071e-06 | 2016 | 2015-06-23 | C | 3 | 0.00015421 | 9.0713e-06
5606604 | 2015-06-23 23:22 | 2015-06-24 03:31 | 249.4667 | 1141 | 69963.3333 | 61.3176 | 58.3176 | 0.21155 | 66540.3333 | 0.2012 | 0.0034501 | Restore Supply on Device 7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 213275 | at 23:21, Triton Sub, CB 5 Wharf Feeder Tripped, No Flags, L/O. CB 7 Totara St North Feeder, Tripped, No Flags, L/O. Faultmen dispatched & investigation began. Call came in of lines brought down due to crane driving incident on CB 5 feeder at Pole 213275. | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-06-23 | c | 0.2012 | 0.0034501 | 2016 | 2015-06-23 | C | 1141 | 0.2012 | 0.0034501
5608927 | 2015-06-24 11:15 | 2015-06-24 14:58 | 223.3667 | 114 | 25463.8 | 223.3667 | 220.3667 | 0.076996 | 25121.8 | 0.075962 | 0.00034471 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole KINMAR078 (A12629) | Broken 11KV cross arm reported by Henry Rovers 027 278 6248 (Kinleith Electrician). Faultman found on arrival that there was 2 broken 11KV cross arms on pole KINMAR078 (A12629), line was isolated at ABS's 984, 997 & 1020 to replace the cross arms. 2 X 11K | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-06-24 | c | 0.075962 | 0.00034471 | 2016 | 2015-06-24 | C | 114 | 0.075962 | 0.00034471
5608952 | 2015-06-24 10:20 | 2015-06-24 10:37 | 17 | 2 | 34 | 17 | 14 | 0.00010281 | 28 | 8.4665e-05 | 6.0475e-06 | Restore Supply on Device Z198 | 22 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Links 2708 | 3 X HT Fuses | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-06-24 | c | 8.4665e-05 | 6.048e-06 | 2016 | 2015-06-24 | C | 2 | 8.4665e-05 | 6.0475e-06
5609440 | 2015-06-24 10:07 | 2015-06-24 11:52 | 105.2667 | 245 | 25619.2667 | 104.5684 | 101.5684 | 0.077467 | 24884.2667 | 0.075244 | 0.00074082 | Restore Supply on Device C206 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 834614 | Truck hit Pole 834614 NDR 21813 Used 1 X Pole 1 X Crossarm HT 3 X HT Insulators | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-06-24 | c | 0.075244 | 0.00074082 | 2016 | 2015-06-24 | C | 245 | 0.075244 | 0.00074082
5609999 | 2015-06-24 11:07 | 2015-07-02 18:41 | 11974.0833 | 7 | 83818.5833 | 11974.0833 | 11971.0833 | 0.25345 | 83797.5833 | 0.25338 | 2.1166e-05 | Restore Supply on Device 2697 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789970 | Lines Down After Transformer X644 Cut temp Line Break at Transformer X644. 3.02 made lines safe, trees through the lines NDR 47055 - will need to get tree cutters in and helicopter to hang conductor - spoke with Glenn in control and he advised oked to cl | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-24 | c | 0.25338 | 2.1166e-05 | 2016 | 2015-06-24 | C | 7 | 0.25338 | 2.1166e-05
5610209 | 2015-07-09 09:20 | 2015-07-09 12:07 | 167 | 1 | 167 | 167 | 164 | 0.00050497 | 164 | 0.0004959 | 3.0238e-06 | NAPA ID:09976 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1276 | Replace H/V Crossarm and T/X. Works location: Awaiti Canal Rd. WO 10147831 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-09 | b | 0.00024795 | 1.512e-06 | 2016 | 2015-07-09 | B | 1 | 0.0004959 | 3.0238e-06
5610241 | 2015-07-14 10:35 | 2015-07-14 14:15 | 220 | 3 | 660 | 220 | 217 | 0.0019957 | 651 | 0.0019685 | 9.0713e-06 | NAPA ID:10550 TP_LINTON GXP > KAIRANGA SUB > BAINESSE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/501 | Change existing 50kva transformer for a new 100kva pole mount transformer, upgrade earths and HV fuse link to 10 amp. Transformer Off at 10:35 and on at 14:15 | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-07-14 | b | 0.00098423 | 4.536e-06 | 2016 | 2015-07-14 | B | 3 | 0.0019685 | 9.0713e-06
5610296 | 2015-06-24 09:58 | 2015-06-24 16:02 | 363.8833 | 16 | 1342.9333 | 83.9333 | 80.9333 | 0.0040607 | 1294.9333 | 0.0039156 | 4.838e-05 | Restore Supply on Device 598 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 598 | Closing Temp Line Break at Pole Transformer X2018. Was another Job to put in Temp line Break but not sure what Happened to it SORRY | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-06-24 | c | 0.0039156 | 4.838e-05 | 2016 | 2015-06-24 | C | 16 | 0.0039156 | 4.838e-05
5610349 | 2015-06-24 16:09 | 2015-06-24 17:13 | 63.7333 | 9 | 573.6 | 63.7333 | 60.7333 | 0.0017344 | 546.6 | 0.0016528 | 2.7214e-05 | Restore Supply on Device 1481 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 374011 | Replace Pole washed away In Flood. Used 1 X Pole 1 X Crossarm 3 X H/T Insulators | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-24 | c | 0.0016528 | 2.7214e-05 | 2016 | 2015-06-24 | C | 9 | 0.0016528 | 2.7214e-05
5612293 | 2015-06-25 07:33 | 2015-06-25 08:38 | 64.9 | 1 | 64.9 | 64.9 | 61.9 | 0.00019624 | 61.9 | 0.00018717 | 3.0238e-06 | Restore Supply on Device TC3018 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TC3018 | Replace 15 KVA transformer fuses TC3018. Replaced 3 x 100 amp fuses and cutout. Cause: bird clash lv. Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-25 | c | 0.00018717 | 3.024e-06 | 2016 | 2015-06-25 | C | 1 | 0.00018717 | 3.0238e-06
5612320 | 2015-07-10 09:00 | 2015-07-10 13:05 | 244.7 | 48 | 11745.6 | 244.7 | 241.7 | 0.035516 | 11601.6 | 0.03508 | 0.00014514 | NAPA ID:09774 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC3-016 | Replace Poles and cross arms. Works location: Prole Rd. WO 30002379 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-10 | b | 0.01754 | 7.257e-05 | 2016 | 2015-07-10 | B | 48 | 0.03508 | 0.00014514
5612789 | 2015-06-25 11:15 | 2015-06-25 15:02 | 226.6 | 214 | 3399 | 15.8832 | 12.8832 | 0.010278 | 2757 | 0.0083365 | 0.00064708 | Restore Supply on Device 3276T | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 847271 | Car vs pole, fire service require eta plz call dispatch with eta thanks 04 801 0812 F1870515 - ETA 15 mins, advised fire comms and police. 1182 Auroa Road, Manaia. 11.16am advised Tallia at svs hub & control. Brett advising pole needs to be replaced broke | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-06-25 | c | 0.0083365 | 0.00064709 | 2016 | 2015-06-25 | C | 214 | 0.0083365 | 0.00064708
5612830 | 2015-06-25 11:35 | 2015-06-25 12:50 | 75 | 23 | 1725 | 75 | 72 | 0.005216 | 1656 | 0.0050073 | 6.9546e-05 | Restore Supply on Device 495 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 805660 | Replace Pole 805660 | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-25 | c | 0.0050073 | 6.9546e-05 | 2016 | 2015-06-25 | C | 23 | 0.0050073 | 6.9546e-05
5612974 | 2015-07-13 09:30 | 2015-07-13 12:30 | 180 | 2 | 360 | 180 | 177 | 0.0010886 | 354 | 0.0010704 | 6.0475e-06 | NAPA ID:10017 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer TC556 | Replace Transformer at TC556. Works location: Rangiora Rd Komata. WO 10147831 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0.00053521 | 3.024e-06 | 2016 | 2015-07-13 | B | 2 | 0.0010704 | 6.0475e-06
5613025 | 2015-07-15 12:00 | 2015-07-15 13:45 | 105 | 3 | 315 | 105 | 102 | 0.00095248 | 306 | 0.00092527 | 9.0713e-06 | NAPA ID:10036 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3317 | Replace Transformer at TC3317. Works location: Robinson Rd Hikutaia. WO 10147831 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-15 | b | 0.00046263 | 4.536e-06 | 2016 | 2015-07-15 | B | 3 | 0.00092527 | 9.0713e-06
5613077 | 2015-07-13 12:30 | 2015-07-13 15:23 | 173 | 2 | 346 | 173 | 170 | 0.0010462 | 340 | 0.0010281 | 6.0475e-06 | NAPA ID:10120 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF7-045 | Replace 11kv crossarms and LA's pole 230798. Works location: Maniatutu Rd. WO 30010396 | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-13 | b | 0.00051404 | 3.024e-06 | 2016 | 2015-07-13 | B | 2 | 0.0010281 | 6.0475e-06
5613121 | 2015-06-25 15:15 | 2015-06-26 16:10 | 1495 | 12 | 2089.1833 | 174.0986 | 171.0986 | 0.0063172 | 2053.1833 | 0.0062083 | 3.6285e-05 | Restore Supply on Device V64 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 356327 | Floating conductor at pole 356327. Isolated at V64 to rebind | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-25 | c | 0.0062083 | 3.6285e-05 | 2016 | 2015-06-25 | C | 12 | 0.0062083 | 3.6285e-05
5613384 | 2015-06-25 18:40 | 2015-06-25 21:00 | 140.1167 | 2 | 280.2333 | 140.1167 | 137.1167 | 0.00084736 | 274.2333 | 0.00082922 | 6.0475e-06 | Restore Supply on Device 6231 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 6231 | 2x 2Amp Fuses & 1x candle replaced | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-06-25 | c | 0.00082922 | 6.048e-06 | 2016 | 2015-06-25 | C | 2 | 0.00082922 | 6.0475e-06
5616728 | 2015-06-26 06:58 | 2015-06-26 11:31 | 272.6833 | 24 | 6544.4 | 272.6833 | 269.6833 | 0.019789 | 6472.4 | 0.019571 | 7.257e-05 | Restore Supply on Device 997 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 997 | 8.05am advised Tallia at svs hub of job -151 Mangahoe Road, lights and appliances affected , heard a big bang last night. Patrol carried out, nothing found. (3 fuses tripped, reloaded OK - 20A Rating). | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-06-26 | c | 0.019571 | 7.257e-05 | 2016 | 2015-06-26 | C | 24 | 0.019571 | 7.257e-05
5617670 | 2015-06-26 11:40 | 2015-06-26 11:48 | 8 | 2 | 16 | 8 | 5 | 4.838e-05 | 10 | 3.0238e-05 | 6.0475e-06 | Restore Supply on Device TC2071 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC2071 | jumper broken of back of TX - de-energised TX HV side and went through control. Power off 11:40am Power on 11:48am. Worked through Todd in Control. Repaired LV jumper - full power back on. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-06-26 | c | 3.0238e-05 | 6.048e-06 | 2016 | 2015-06-26 | C | 2 | 3.0238e-05 | 6.0475e-06
5617722 | 2015-07-15 10:37 | 2015-07-15 13:35 | 178.2167 | 10 | 1782.1667 | 178.2167 | 175.2167 | 0.0053888 | 1752.1667 | 0.0052981 | 3.0238e-05 | NAPA ID:10023 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP346 | REPLACE HV POLE / ARMS # 221388. Works location: Rangiuru Rd Te Puke. WO 10162942 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-07-15 | b | 0.0026491 | 1.5119e-05 | 2016 | 2015-07-15 | B | 10 | 0.0052981 | 3.0238e-05
5617971 | 2015-06-26 11:16 | 2015-06-26 13:12 | 116 | 237 | 19662 | 82.962 | 79.962 | 0.059453 | 18951 | 0.057303 | 0.00071663 | Restore Supply on Device T21 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T21 | CB T21 tripped on B phase O/C & E/F flags,line was patrolled and sectionalised and no fault was found. Control has arranged for closer inspection with a camera due to repeat tripping with no fault found. | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-06-26 | c | 0.057303 | 0.00071663 | 2016 | 2015-06-26 | C | 237 | 0.057303 | 0.00071663
5618609 | 2015-07-15 08:46 | 2015-07-15 12:24 | 218.9167 | 112 | 24518.6667 | 218.9167 | 215.9167 | 0.074139 | 24182.6667 | 0.073123 | 0.00033866 | NAPA ID:09777 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC3-069 | Replace poles and cross arms. Install 2 X fused ABS at Pole 208955 to replace fuses SC3-024 & SC3-023. Works location: Kayelene Place. WO 30002379 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-15 | b | 0.036561 | 0.00016933 | 2016 | 2015-07-15 | B | 112 | 0.073123 | 0.00033866
5622154 | 2015-06-26 14:44 | 2015-06-26 17:01 | 137.1333 | 7 | 959.9333 | 137.1333 | 134.1333 | 0.0029026 | 938.9333 | 0.0028391 | 2.1166e-05 | Restore Supply on Device X1035 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 914 | Trippinmg on 2 HT fuses at 914. (Suspect line clash). Reclosed OK (5A Rating) | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-06-26 | c | 0.0028391 | 2.1166e-05 | 2016 | 2015-06-26 | C | 7 | 0.0028391 | 2.1166e-05
5622440 | 2015-06-26 17:30 | 2015-06-26 18:15 | 45 | 17 | 757.8 | 44.5765 | 41.5765 | 0.0022914 | 706.8 | 0.0021372 | 5.1404e-05 | Restore Supply on Device 113 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 113 | 2 HT Fuses tripped at 113 (2 X 6A). Reloaded OK, suspect line clash. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-06-26 | c | 0.0021372 | 5.1404e-05 | 2016 | 2015-06-26 | C | 17 | 0.0021372 | 5.1404e-05
5622724 | 2015-06-26 20:45 | 2015-06-26 22:42 | 117 | 233 | 10388.7333 | 44.5868 | 41.5868 | 0.031413 | 9689.7333 | 0.029299 | 0.00070454 | Restore Supply on Device T21 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730600 | Replace blown insulator on pole 730600 | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-06-26 | c | 0.029299 | 0.00070454 | 2016 | 2015-06-26 | C | 233 | 0.029299 | 0.00070454
5623341 | 2015-06-27 05:45 | 2015-06-27 09:06 | 201.45 | 283 | 32868.9 | 116.1445 | 113.1445 | 0.099388 | 32019.9 | 0.096821 | 0.00085572 | Restore Supply on Device TA9 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715955 | Tripping on CBTA9 on DEF E/F. Feeder sectionalised / patrolled with a floating Conductor found on Watino Rd. Isolation between ABS TA916, TA914 and TA875 with backfeed at ABS TA115. One 11kV Insulator and binder replaced, relivened OK. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-06-27 | c | 0.096821 | 0.00085572 | 2016 | 2015-06-27 | C | 283 | 0.096821 | 0.00085572
5629961 | 2015-06-27 09:28 | 2015-06-27 16:33 | 425.15 | 639 | 46618.9833 | 72.9562 | 69.9562 | 0.14096 | 44701.9833 | 0.13517 | 0.0019322 | Restore Supply on Device 2172 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | GLADSTONE | Tripping on MST GXP 33kV CB2172 on O/C. (Loss of supply to Gladstone). 11kV Initially backfed via ABS S364 then 33kV patrol carried out. Nothing found, all restored OK. (NOTE: some delay in restoration of Kourarau feeder as unable to contact Station contr | F1,F2,F3 | GLADSTONE 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 2015-06-27 | c | 0.13517 | 0.0019322 | 2016 | 2015-06-27 | C | 639 | 0.13517 | 0.0019322
5630694 | 2015-06-27 09:34 | 2015-06-27 16:17 | 403.2833 | 151 | 36471.5167 | 241.5332 | 238.5332 | 0.11028 | 36018.5167 | 0.10891 | 0.00045659 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | C2180 | Car vs pole - advised hub and control. Reclose 9707/2 Tripped. Isolation at Links 9707/6 ABS 617 ABS 571. Back feed from ABS 599 TAH CB 3. HV repairs carried out to get Power restored. Transforner 2898 Isolated for LV repairs. Pole C2180. NDR 48174. Mater | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-06-27 | c | 0.10891 | 0.00045659 | 2016 | 2015-06-27 | C | 151 | 0.10891 | 0.00045659
5639469 | 2015-06-27 12:11 | 2015-06-27 13:42 | 91 | 3281 | 185607.8 | 56.5705 | 53.5705 | 0.56123 | 175764.8 | 0.53147 | 0.009921 | Restore Supply on Device 2182 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N/A | Tripping on Wanganui GXP CB2812 on Neutral Time O/C. (Loss of supply to Wanganui East Sub). 11kV Backfed initially from ABS 998 and 702. Some delay as CB7 failed to close on site. (CB Fault - DNO 150618). CB7 backfed via ABS111 instead. 33kV Patrolled as | F1,F2,F3 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 2015-06-27 | c | 0.53147 | 0.009921 | 2016 | 2015-06-27 | C | 3281 | 0.53147 | 0.009921
5644235 | 2015-06-27 12:51 | 2015-06-27 12:53 | 2.7333 | 595 | 1626.3333 | 2.7333 | -0.26667 | 0.0049176 | 0 | 0 | 0.0017991 | Restore Supply on Device 6 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | CB 6 | Switching error while carrying out NAPA 10648 caused tripping of CB 6 Otumoetai S/M 479516 | F3 | SUMMIT | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-06-27 | c | 0 | 0.0017991 | 2016 | 2015-06-27 | C | 595 | 0 | 0.0017991
5646065 | 2015-06-27 21:40 | 2015-06-28 09:10 | 689.35 | 859 | 192447.2833 | 224.0364 | 221.0364 | 0.58191 | 189870.2833 | 0.57412 | 0.0025974 | Restore Supply on Device 1 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | N1041 | POA CB1 tripped E/F, A Ph O/C, L/O. Feeder sectionalised with fault bounded by ABS 2512, & Links LC500. CB1 returned to service & back feed via Sw/Gear 9210/2. 11kV U/G cables tested & faulted section disconnected & earthed for repair ( ABS 2512 - Source | F2 | WILLOUGHBY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-06-27 | c | 0.57412 | 0.0025974 | 2016 | 2015-06-27 | C | 859 | 0.57412 | 0.0025974
5648125 | 2015-06-28 13:20 | 2015-06-28 13:42 | 22.4333 | 41 | 919.3333 | 22.4228 | 19.4228 | 0.0027798 | 796.3333 | 0.0024079 | 0.00012397 | Restore Supply on Device T7/102 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/102 | Found Blown Jumper at Transformer T7/102 - Isolated at Fuses R28 - Remade jumper at replaced 2 blown Fuses - used 2x 3 amp fuses | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-28 | c | 0.0024079 | 0.00012397 | 2016 | 2015-06-28 | C | 41 | 0.0024079 | 0.00012397
5648254 | 2015-06-28 15:09 | 2015-06-28 18:17 | 188.2833 | 111 | 13113.15 | 118.1365 | 115.1365 | 0.039651 | 12780.15 | 0.038644 | 0.00033564 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798524 | Recloser C634 Tripped E/F, L/O - Floater found at Pole 798524 during sectionalising - Isolated at ABS S505, ABS C634/1, and links C634/6 - back feed via VS 11035 - Rebind Floater at Pole 798524. Refer OMS 5648391 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-28 | c | 0.038644 | 0.00033564 | 2016 | 2015-06-28 | C | 111 | 0.038644 | 0.00033564
5648380 | 2015-06-28 15:33 | 2015-06-28 16:39 | 65.7333 | 1 | 65.7333 | 65.7333 | 62.7333 | 0.00019876 | 62.7333 | 0.00018969 | 3.0238e-06 | Restore Supply on Device T1893 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/103 | 2 fuse found blown at Transformer T2/103, due to tin foil - used 2 x 6 amp fuses | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-06-28 | c | 0.00018969 | 3.024e-06 | 2016 | 2015-06-28 | C | 1 | 0.00018969 | 3.0238e-06
5649671 | 2015-06-28 17:47 | 2015-06-28 19:45 | 118.7167 | 635 | 2534.4 | 3.9912 | 0.99118 | 0.0076634 | 0 | 0 | 0.0019201 | Restore Supply on Device LI7 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727271 | Outage required between ABS LI146 and ABS LI185 to replace one HV insulator. Backfeed at ABS LI170. Relivened OK. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-06-28 | c | 0 | 0.0019201 | 2016 | 2015-06-28 | C | 635 | 0 | 0.0019201
5650323 | 2015-06-28 17:45 | 2015-06-28 18:54 | 68.6833 | 28 | 1923.1333 | 68.6833 | 65.6833 | 0.0058151 | 1839.1333 | 0.0055611 | 8.4665e-05 | Restore Supply on Device T31 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46999 | Outage required on Kaharoa Rd to replace one HV jumper. Isolation Between Links T31 and ABS T35 with backfeed at ABS V19. Relivened OK. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-06-28 | c | 0.0055611 | 8.4665e-05 | 2016 | 2015-06-28 | C | 28 | 0.0055611 | 8.4665e-05
5650386 | 2015-06-28 19:10 | 2015-06-28 20:11 | 60.8667 | 562 | 21660.5667 | 38.5419 | 35.5419 | 0.065496 | 19974.5667 | 0.060398 | 0.0016994 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M12658 | PUT CB6 tripped A, B & C Ph O/C, L/O. Recloser 9636 opened & back fed closed via sectionaliser 9704 ( PUT 5 ) Report of car v pole M12658 which caused line clash & broken stay wire, pole & conductor checked out all ok CB6 returned to service with all serv | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-06-28 | c | 0.060398 | 0.0016994 | 2016 | 2015-06-28 | C | 562 | 0.060398 | 0.0016994
5652324 | 2015-06-29 07:33 | 2015-06-29 12:15 | 282.0167 | 16 | 3968.5167 | 248.0323 | 245.0323 | 0.012 | 3920.5167 | 0.011855 | 4.838e-05 | Restore Supply on Device T9/104 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01075 | Plz check if oms 5652340 49 Kaituna Road & 5652343 146 Kaituna Road are related both No power 2 X fuses found blown at fuses V33 - during patrol ,damaged line found past fuses 10148 - Isolated at Fuses 10148 and fuses V33 reloaded and closed - unable to | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-29 | c | 0.011855 | 4.838e-05 | 2016 | 2015-06-29 | C | 16 | 0.011855 | 4.838e-05
5652405 | 2015-07-16 09:53 | 2015-07-16 14:04 | 251.5 | 1 | 251.5 | 251.5 | 248.5 | 0.00076048 | 248.5 | 0.0007514 | 3.0238e-06 | NAPA ID:10020 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF6-054 | REPLACE ALL HV AND LV ARMS AT TF6-052. Works location: Rangiuru Rd. WO 10162942 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-07-16 | b | 0.0003757 | 1.512e-06 | 2016 | 2015-07-16 | B | 1 | 0.0007514 | 3.0238e-06
5652761 | 2015-07-09 09:30 | 2015-07-09 10:09 | 38.2833 | 16 | 612.5333 | 38.2833 | 35.2833 | 0.0018522 | 564.5333 | 0.001707 | 4.838e-05 | NAPA ID:09602 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 758389 | Remove temp HV links @ pole 758389 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-07-09 | b | 0.00085351 | 2.419e-05 | 2016 | 2015-07-09 | B | 16 | 0.001707 | 4.838e-05
5652909 | 2015-07-16 09:09 | 2015-07-16 15:25 | 376.2667 | 107 | 40260.5333 | 376.2667 | 373.2667 | 0.12174 | 39939.5333 | 0.12077 | 0.00032354 | NAPA ID:09930 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1347 | Replace crossarms various locations. Works location: Scotsman Valley Rd Kiwitahi. WO 30002383 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-16 | b | 0.060384 | 0.00016177 | 2016 | 2015-07-16 | B | 107 | 0.12077 | 0.00032354
5652944 | 2015-06-29 09:29 | 2015-06-29 11:10 | 100.1333 | 12 | 210.9833 | 17.5819 | 14.5819 | 0.00063796 | 174.9833 | 0.00052911 | 3.6285e-05 | Restore Supply on Device SE2-020 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217356 | pole 217356 is glowing and sparking. 9.30am advised at svs hub & control. 230 Soldiers Road, Tauranga. Fuses SE2-020 opened & closed on approval from NOC to check source of arcing. Cause identified to be fuse carrier had become marginally detached from ba | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-06-29 | c | 0.00052911 | 3.6285e-05 | 2016 | 2015-06-29 | C | 12 | 0.00052911 | 3.6285e-05
5653095 | 2015-06-29 08:48 | 2015-06-30 07:32 | 1363.55 | 130 | 5694.55 | 43.8042 | 40.8042 | 0.017219 | 5304.55 | 0.01604 | 0.00039309 | Restore Supply on Device CB4 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P22830 | CB Tripped E/F when Fuses V86 Closed - Fuses V86 Opened and Line Patrolled - broken pole found at P22830, unable to replace due to weather - line break made at Pole P22830 and Fuses V86 Closed Generators to be installed at transformers T9/300 & T9/304. Re | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-06-29 | c | 0.01604 | 0.00039309 | 2016 | 2015-06-29 | C | 130 | 0.01604 | 0.00039309
5653637 | 2015-07-16 09:15 | 2015-07-16 15:09 | 353.8667 | 13 | 4600.2667 | 353.8667 | 350.8667 | 0.01391 | 4561.2667 | 0.013792 | 3.9309e-05 | NAPA ID:09457 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses L1774 | Replacing 11kv poles and conductors between fuses L1774 and pole 728702 at the end of the line. Works location: Garsed Rd Kakaramea. WO 30001089 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-16 | b | 0.0068961 | 1.9654e-05 | 2016 | 2015-07-16 | B | 13 | 0.013792 | 3.9309e-05
5654159 | 2015-06-29 14:32 | 2015-06-29 15:38 | 65.55 | 35 | 2232.5833 | 63.7881 | 60.7881 | 0.0067508 | 2127.5833 | 0.0064333 | 0.00010583 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD4-060 | Advice received from faultman of blown jumper on links SC4-060. Part power to all of feeder. CB 5 opened by NOC to protect from low voltage. Supply restored to feeder via back feeds from Sw/gear S4651 & SC4-079. Feeder was split at Sw/gear SC4-136 prior. | F1 | WHARF | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-06-29 | c | 0.0064333 | 0.00010583 | 2016 | 2015-06-29 | C | 35 | 0.0064333 | 0.00010583
5654167 | 2015-07-17 11:03 | 2015-07-17 13:28 | 145.0667 | 43 | 6237.8667 | 145.0667 | 142.0667 | 0.018862 | 6108.8667 | 0.018472 | 0.00013002 | NAPA ID:09920 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 118 | to change 11kv xrm and 400v xrms on pole 745009 in bad condition. Works location: Ackworth Rd, New Plymouth. WO 30009505 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-07-17 | b | 0.0092359 | 6.5011e-05 | 2016 | 2015-07-17 | B | 43 | 0.018472 | 0.00013002
5654178 | 2015-06-29 06:40 | 2015-06-29 06:41 | 1.15 | 1126 | 1294.9 | 1.15 | -1.85 | 0.0039155 | 0 | 0 | 0.0034048 | Restore Supply on Device 18 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB | Cb Temp 18 Tripped no flags - A/R | F2 | KINGS AVENUE | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 2015-06-29 | c | 0 | 0.0034048 | 2016 | 2015-06-29 | C | 1126 | 0 | 0.0034048
5656670 | 2015-06-29 15:10 | 2015-06-29 20:22 | 312 | 2684 | 162330 | 60.4806 | 57.4806 | 0.49085 | 154278 | 0.4665 | 0.0081158 | Restore Supply on Device 1092 | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 801615 | Initial tripping on 33kV CB1092 MTN GXP on E/F, O/C. (Loss of supply to Bulls Sub). Fault caused by Car / Pole on SH3. Isolation required on 33kV and 11kV between ABS 1075 and 959. Bulls backfeed via ABS 852, ABS 4241 and recloser 912. 3:28pm advised by P | F1,F2,F3 | BULLS 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-06-29 | c | 0.4665 | 0.0081158 | 2016 | 2015-06-29 | C | 2684 | 0.4665 | 0.0081158
5658131 | 2015-06-29 16:43 | 2015-06-29 20:39 | 236.1 | 1065 | 82992.7 | 77.9274 | 74.9274 | 0.25095 | 79797.7 | 0.24129 | 0.0032203 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P33815 | Tripping on CB6 on Phase A-B-C Overcurrent. Fault caused by tree falling across lines (High winds). Isolation required between ABS L5 and L7 with backfeed at ABS L96. Repairs included new crossarm and associated hardware and 6 metres conductor.. Relivene | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-06-29 | c | 0.24129 | 0.0032203 | 2016 | 2015-06-29 | C | 1065 | 0.24129 | 0.0032203
5659929 | 2015-06-30 11:40 | 2015-06-30 13:37 | 117 | 38 | 4446 | 117 | 114 | 0.013444 | 4332 | 0.013099 | 0.0001149 | Restore Supply on Device X121 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792074 | Problem with Transformer X121 - Difficult to locate during the night. To be investigated during daylight hours. 8.39am customer called from 721 - fault is at pole on top of hill, wire has come loose - customer advised poss will be need quad bike access wh | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-06-30 | c | 0.013099 | 0.0001149 | 2016 | 2015-06-30 | C | 38 | 0.013099 | 0.0001149
5661683 | 2015-06-30 07:43 | 2015-06-30 09:40 | 117.3 | 1 | 117.3 | 117.3 | 114.3 | 0.00035469 | 114.3 | 0.00034562 | 3.0238e-06 | Restore Supply on Device X1068 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 785605 | replace 3 x 2 amp hv fuses. tx x1068. pole 785605. cause: bird strike. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-06-30 | c | 0.00034562 | 3.024e-06 | 2016 | 2015-06-30 | C | 1 | 0.00034562 | 3.0238e-06
5673781 | 2015-06-30 11:35 | 2015-06-30 14:38 | 183 | 325 | 5075 | 15.6154 | 12.6154 | 0.015346 | 4100 | 0.012397 | 0.00098272 | Restore Supply on Device TC3189 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3189 | at 11:40, Piako Sub, CB 6 Kereone Feeder, Recloser 9121 Tripped, E/F, L/O. This happened during an LV shut Downers were having at Transformer TC3189. While working on the LV fed from this transformer, 1 HV Fuse at the transformer began to smoke. Downer st | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-06-30 | c | 0.012397 | 0.00098272 | 2016 | 2015-06-30 | C | 325 | 0.012397 | 0.00098272
5675165 | 2015-06-30 12:47 | 2015-06-30 14:56 | 129.0833 | 22 | 2839.8333 | 129.0833 | 126.0833 | 0.008587 | 2773.8333 | 0.0083874 | 6.6523e-05 | Restore Supply on Device IC404 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | O2349 | Powerco requested to isolate lines for safety to remove vehicle from under line. 11kV line beyond ABS IC404 isolated for safety to remove damaged vehicle from under the line with crane. Road verge subsided from under Downer vehicle 29/06/15, vehicle rolle | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-06-30 | c | 0.0083874 | 6.6523e-05 | 2016 | 2015-06-30 | C | 22 | 0.0083874 | 6.6523e-05
5675433 | 2015-07-14 09:15 | 2015-07-14 14:45 | 329.4 | 13 | 4282.2 | 329.4 | 326.4 | 0.012948 | 4243.2 | 0.01283 | 3.9309e-05 | NAPA ID:09456 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses L1774 | replaceing poles and conductor between fuses L1774 and pole 728702 at the end of the line. Works location: Garsed Rd Kakaramea. WO 30001089 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-14 | b | 0.0064152 | 1.9654e-05 | 2016 | 2015-07-14 | B | 13 | 0.01283 | 3.9309e-05
5677673 | 2015-07-01 02:05 | 2015-07-01 04:43 | 157.6 | 1 | 157.6 | 157.6 | 154.6 | 0.00047654 | 154.6 | 0.00046747 | 3.0238e-06 | Restore Supply on Device X4082 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 287 | Found one DDO fuse carrier burnt off at the top of carrier at Fuses 287 - Carrier and fuse replaced with temp repairs being done - used 1x DDO carrier and 2 x 15amp fuses | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-07-01 | c | 0.00046747 | 3.024e-06 | 2016 | 2015-07-01 | C | 1 | 0.00046747 | 3.0238e-06
5678297 | 2015-07-01 05:59 | 2015-07-01 10:45 | 285.6333 | 23 | 6569.5667 | 285.6333 | 282.6333 | 0.019865 | 6500.5667 | 0.019656 | 6.9546e-05 | Restore Supply on Device R29 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | r29 | 2 fuses replaced 10 amp suspect wind cause | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-01 | c | 0.019656 | 6.9546e-05 | 2016 | 2015-07-01 | C | 23 | 0.019656 | 6.9546e-05
5690933 | 2015-07-17 09:35 | 2015-07-17 14:45 | 310 | 145 | 44950 | 310 | 307 | 0.13592 | 44515 | 0.1346 | 0.00043845 | NAPA ID:10040 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC400 | Replace H/V Crossarms and T/X's at Various Sites. Works location: Hwy 26 Hikutaia. WO 10147831 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-17 | b | 0.067301 | 0.00021922 | 2016 | 2015-07-17 | B | 145 | 0.1346 | 0.00043845
5701987 | 2015-07-01 22:43 | 2015-07-02 03:16 | 273.3333 | 438 | 58050.6667 | 132.5358 | 129.5358 | 0.17553 | 56736.6667 | 0.17156 | 0.0013244 | Restore Supply on Device X194 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 768113 | CB 9 Tripped B,C Ph O/C E/F A/R - Car V Pole at Pole 768113 - Isolated at ABS's 533, 1108 & 004 - Backfeed via ABS 039 - Pole replaced - used 1x pole, 2x LV crossarms complete, 1x HV crossarm Complete. Service lines still to be repaired. | F3 | KIWI ST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-07-01 | c | 0.17156 | 0.0013244 | 2016 | 2015-07-01 | C | 438 | 0.17156 | 0.0013244
5704016 | 2015-07-20 14:00 | 2015-07-20 14:45 | 45 | 4 | 180 | 45 | 42 | 0.00054428 | 168 | 0.00050799 | 1.2095e-05 | NAPA ID:10180 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2460 | To install a 400V Fuse/Disconnector. Works location: Hwy 26 Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-20 | b | 0.000254 | 6.048e-06 | 2016 | 2015-07-20 | B | 4 | 0.00050799 | 1.2095e-05
5704995 | 2015-07-21 09:03 | 2015-07-21 13:59 | 295.75 | 7 | 2070.25 | 295.75 | 292.75 | 0.0062599 | 2049.25 | 0.0061964 | 2.1166e-05 | NAPA ID:09875 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole LAKBRN158 | To install 11kV break and replace 11kV cross arms at poles F12384 and TC3499. Works location: Hinuera Rd WO 30002943 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-21 | b | 0.0030982 | 1.0583e-05 | 2016 | 2015-07-21 | B | 7 | 0.0061964 | 2.1166e-05
5705052 | 2015-07-21 10:00 | 2015-07-21 10:45 | 45 | 4 | 180 | 45 | 42 | 0.00054428 | 168 | 0.00050799 | 1.2095e-05 | NAPA ID:10183 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4133 | To install a 3 phase fues/disconnector. Works location: Harbottle Rd, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-21 | b | 0.000254 | 6.048e-06 | 2016 | 2015-07-21 | B | 4 | 0.00050799 | 1.2095e-05
5705056 | 2015-07-27 09:01 | 2015-07-27 15:39 | 398.0167 | 98 | 39005.6333 | 398.0167 | 395.0167 | 0.11794 | 38711.6333 | 0.11705 | 0.00029633 | NAPA ID:07506 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 090 | Project number IR6978 Rangikura Reconstruction Replace poles Koihi Road poles 772893 to 772910 & install tempory line break & HT fuses TMP 3 at pole 781120. Works location: Karakahi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-27 | b | 0.058527 | 0.00014816 | 2016 | 2015-07-27 | B | 98 | 0.11705 | 0.00029633
5705131 | 2015-07-20 10:00 | 2015-07-20 11:36 | 95.45 | 122 | 11644.9 | 95.45 | 92.45 | 0.035211 | 11278.9 | 0.034105 | 0.0003689 | NAPA ID:09941 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5207 | Replace 11KV Insulators at pole 764278 and 764349. Works location: Inland North Rd, Waitara. WO 30006647 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-20 | b | 0.017052 | 0.00018445 | 2016 | 2015-07-20 | B | 122 | 0.034105 | 0.0003689
5705175 | 2015-07-17 10:10 | 2015-07-17 13:12 | 182 | 3 | 546 | 182 | 179 | 0.001651 | 537 | 0.0016238 | 9.0713e-06 | NAPA ID:10181 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TC299 | LLP: to replace 11kV Fuses TC299. AP: To replace the 400V arm & install 400V Fuse Disconnector. Works location: Hwy 26 Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-17 | b | 0.00081188 | 4.536e-06 | 2016 | 2015-07-17 | B | 3 | 0.0016238 | 9.0713e-06
5705178 | 2015-07-29 09:00 | 2015-07-29 14:55 | 355 | 98 | 34790 | 355 | 352 | 0.1052 | 34496 | 0.10431 | 0.00029633 | NAPA ID:07510 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 090 | Project number IR6978 Rangikura Reconstruction Replace poles Koihi Road poles 772912 to 772936. Works location: Koihi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-29 | b | 0.052154 | 0.00014816 | 2016 | 2015-07-29 | B | 98 | 0.10431 | 0.00029633
5705242 | 2015-07-20 12:55 | 2015-07-20 14:00 | 65 | 11 | 715 | 65 | 62 | 0.002162 | 682 | 0.0020622 | 3.3261e-05 | NAPA ID:10182 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TC4286 | To replace the transformer & install a 400V Fuse/Disconnector. Works location: Harbottle Rd, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-20 | b | 0.0010311 | 1.6631e-05 | 2016 | 2015-07-20 | B | 11 | 0.0020622 | 3.3261e-05
5705259 | 2015-07-20 09:45 | 2015-07-20 10:35 | 50 | 6 | 300 | 50 | 47 | 0.00090713 | 282 | 0.0008527 | 1.8143e-05 | NAPA ID:10178 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2241 | To install a 400V Fuse/Disconnector | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-20 | b | 0.00042635 | 9.071e-06 | 2016 | 2015-07-20 | B | 6 | 0.0008527 | 1.8143e-05
5705361 | 2015-07-02 17:16 | 2015-07-02 18:46 | 90 | 661 | 12989 | 19.6505 | 16.6505 | 0.039276 | 11006 | 0.03328 | 0.0019987 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 268679 | CB 3 tripped to L/O. O/C & E/F flags. Line sectionalised & patrolled. Back feed established by opening Sw/gear 9637/1 & closing sectionaliser following report of arcing on line beyond ABS 2106 at time of trip. Line patrolled beyond ABS 2106 & evidence fou | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-07-02 | c | 0.03328 | 0.0019987 | 2016 | 2015-07-02 | C | 661 | 0.03328 | 0.0019987
5707219 | 2015-07-03 07:30 | 2015-07-03 11:16 | 226 | 359 | 23346.5833 | 65.0323 | 62.0323 | 0.070594 | 22269.5833 | 0.067338 | 0.0010855 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 1391 | customer at #67 No 8 Road Extension advise line down outside his property. 7.50am - advise control. CB 3 tripped on A, B & C phase O/C & E/F flags, received a call from customer of lines down,faultman found broken jumpers at ABS 1391, line was isolated at | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-07-03 | c | 0.067338 | 0.0010855 | 2016 | 2015-07-03 | C | 359 | 0.067338 | 0.0010855
5708689 | 2015-07-03 10:06 | 2015-07-03 12:06 | 120.25 | 594 | 71428.5 | 120.25 | 117.25 | 0.21598 | 69646.5 | 0.21059 | 0.0017961 | Restore Supply on Device L39 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Assorted Poles | Replaced FABS 10151 with Set of Fuses Replace assorted Crossarms & Insulators | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-03 | c | 0.21059 | 0.0017961 | 2016 | 2015-07-03 | C | 594 | 0.21059 | 0.0017961
5709301 | 2015-08-05 09:24 | 2015-08-05 15:03 | 338.8333 | 13 | 4404.8333 | 338.8333 | 335.8333 | 0.013319 | 4365.8333 | 0.013201 | 3.9309e-05 | NAPA ID:09453 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 728702 | Replacing 11kV poles and conductor between fuses L1774 and pole 728702. Garsed Road, Kakaramea. Work Order 30001089. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-08-05 | b | 0.0066006 | 1.9654e-05 | 2016 | 2015-08-05 | B | 13 | 0.013201 | 3.9309e-05
5709419 | 2015-07-27 09:00 | 2015-07-27 10:50 | 109.9333 | 1 | 109.9333 | 109.9333 | 106.9333 | 0.00033241 | 106.9333 | 0.00032334 | 3.0238e-06 | NAPA ID:09885 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F12381 | To replace 11kV cross arms at pole # F12381. Work Location: Hinuera Road, Matamata. Work Order 30002943. | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-27 | b | 0.00016167 | 1.512e-06 | 2016 | 2015-07-27 | B | 1 | 0.00032334 | 3.0238e-06
5709435 | 2015-07-27 12:20 | 2015-07-27 14:13 | 112.85 | 3 | 338.55 | 112.85 | 109.85 | 0.0010237 | 329.55 | 0.00099648 | 9.0713e-06 | NAPA ID:09888 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6368, TP1204 | To replace 11kV cross arms at pole TC6368. Work Location: Hinuera Road. Work Order 30002943. | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-27 | b | 0.00049824 | 4.536e-06 | 2016 | 2015-07-27 | B | 3 | 0.00099648 | 9.0713e-06
5709532 | 2015-07-24 10:00 | 2015-07-24 10:50 | 50 | 1 | 50 | 50 | 47 | 0.00015119 | 47 | 0.00014212 | 3.0238e-06 | NAPA ID:10188 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5708 | To install a 400V Fuse/Disconnector. Works location: Hwy 26 Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-24 | b | 7.1058e-05 | 1.512e-06 | 2016 | 2015-07-24 | B | 1 | 0.00014212 | 3.0238e-06
5709536 | 2015-07-24 12:00 | 2015-07-24 12:45 | 45 | 3 | 135 | 45 | 42 | 0.00040821 | 126 | 0.00038099 | 9.0713e-06 | NAPA ID:10189 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP523 | To install a 400V Fuse/Disconector. Works location; Hwy 26 Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-24 | b | 0.0001905 | 4.536e-06 | 2016 | 2015-07-24 | B | 3 | 0.00038099 | 9.0713e-06
5709538 | 2015-07-27 12:00 | 2015-07-27 12:40 | 40 | 7 | 280 | 40 | 37 | 0.00084665 | 259 | 0.00078315 | 2.1166e-05 | NAPA ID:10192 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2847 | To install a 400V Fuse/Disconnector. Works location: Piako Rd, Morrinsville. WO 10147849. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-27 | b | 0.00039158 | 1.0583e-05 | 2016 | 2015-07-27 | B | 7 | 0.00078315 | 2.1166e-05
5709539 | 2015-07-27 10:00 | 2015-07-27 10:40 | 40 | 3 | 120 | 40 | 37 | 0.00036285 | 111 | 0.00033564 | 9.0713e-06 | NAPA ID:10191 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2958 | To replace the 400V arm & install a 400V Fuse/Disconnector. Works location: Piako Rd, Morrinsville. WO 10147849. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-27 | b | 0.00016782 | 4.536e-06 | 2016 | 2015-07-27 | B | 3 | 0.00033564 | 9.0713e-06
5709672 | 2015-07-25 11:30 | 2015-07-25 13:50 | 140 | 9 | 1260 | 140 | 137 | 0.0038099 | 1233 | 0.0037283 | 2.7214e-05 | NAPA ID:10179 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2888 | To install a 400V Fuse Disconnector. Works location: Hwy 26 Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-25 | b | 0.0018641 | 1.3607e-05 | 2016 | 2015-07-25 | B | 9 | 0.0037283 | 2.7214e-05
5709680 | 2015-07-03 16:25 | 2015-07-03 16:26 | 1 | 224 | 224 | 1 | -2 | 0.00067732 | 0 | 0 | 0.00067732 | Restore Supply on Device H41 | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB H41 | CB H41 auto reclosed on B & C phase O/C flags, line was not patrolled. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-07-03 | c | 0 | 0.00067732 | 2016 | 2015-07-03 | C | 224 | 0 | 0.00067732
5709975 | 2015-07-03 18:04 | 2015-07-03 23:39 | 334.9167 | 250 | 30804 | 123.216 | 120.216 | 0.093144 | 30054 | 0.090876 | 0.00075594 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D1521 | Sectioaliser SS9396 L/O on E/F. Sectionalised and found fault beyond ABS 821. Replaced 3 faulty insulators at pole D1521. Relivened | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-07-03 | c | 0.090876 | 0.00075594 | 2016 | 2015-07-03 | C | 250 | 0.090876 | 0.00075594
5710880 | 2015-07-04 10:17 | 2015-07-04 14:17 | 240.6167 | 2 | 481.2333 | 240.6167 | 237.6167 | 0.0014551 | 475.2333 | 0.001437 | 6.0475e-06 | Restore Supply on Device T714 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T714 | Replaced 30kva transformer with a 50kva (no 30 available) | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-07-04 | c | 0.001437 | 6.048e-06 | 2016 | 2015-07-04 | C | 2 | 0.001437 | 6.0475e-06
5710887 | 2015-07-04 10:20 | 2015-07-04 12:02 | 101.9667 | 4 | 407.8667 | 101.9667 | 98.9667 | 0.0012333 | 395.8667 | 0.001197 | 1.2095e-05 | Restore Supply on Device TD5-304 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219966 | Replace 2 x 10 A H/V, O/H Fuses possible bird strike | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.001197 | 1.2095e-05 | 2016 | 2015-07-04 | C | 4 | 0.001197 | 1.2095e-05
5712067 | 2015-07-04 11:54 | 2015-07-04 14:46 | 172.3833 | 1 | 172.3833 | 172.3833 | 169.3833 | 0.00052125 | 169.3833 | 0.00051217 | 3.0238e-06 | Restore Supply on Device 4938T | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731554 | 2R replace TX. TX replaced and power restored | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-07-04 | c | 0.00051218 | 3.024e-06 | 2016 | 2015-07-04 | C | 1 | 0.00051217 | 3.0238e-06
5712095 | 2015-07-04 12:25 | 2015-07-04 16:18 | 233.45 | 302 | 29031.4667 | 96.1307 | 93.1307 | 0.087784 | 28125.4667 | 0.085045 | 0.00091318 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 204527 | KPT 1 recloser 9606 tripped E/F, L/O. Feeder sectionalised & faulty insulator at pole 204527. Isolation at Fuses SB1 047 ( no back feeds ) with rest of feeder returned to service. Insulator replaced, all service restored. Materials 1 x H/V Insulator, 2 x | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.085045 | 0.00091318 | 2016 | 2015-07-04 | C | 302 | 0.085045 | 0.00091318
5716296 | 2015-07-04 15:02 | 2015-07-04 20:24 | 322.4667 | 1645 | 44722.8833 | 27.1872 | 24.1872 | 0.13523 | 39787.8833 | 0.12031 | 0.0049741 | Restore Supply on Device TE4-035 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 212722 | ICP included in 5714285 | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.12031 | 0.0049741 | 2016 | 2015-07-04 | C | 1645 | 0.12031 | 0.0049741
5716603 | 2015-07-04 19:56 | 2015-07-04 21:48 | 112.1333 | 7 | 298.1333 | 42.5905 | 39.5905 | 0.00090148 | 277.1333 | 0.00083798 | 2.1166e-05 | Restore Supply on Device TC3-174 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3-174 | Isolated transformer to carry out repiars to bottom of DDO | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.00083798 | 2.1166e-05 | 2016 | 2015-07-04 | C | 7 | 0.00083798 | 2.1166e-05
5716649 | 2015-07-04 21:05 | 2015-07-04 21:36 | 31 | 75 | 2325 | 31 | 28 | 0.0070302 | 2100 | 0.0063499 | 0.00022678 | Restore Supply on Device FP1092 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3-174 |  | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.0063499 | 0.00022678 | 2016 | 2015-07-04 | C | 75 | 0.0063499 | 0.00022678
5716733 | 2015-07-04 21:55 | 2015-07-04 23:20 | 84.7 | 2 | 169.4 | 84.7 | 81.7 | 0.00051223 | 163.4 | 0.00049408 | 6.0475e-06 | Restore Supply on Device T2/637 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P99 | two fuses found blown at Fuses P99 - no fault found - used 2x 10amp fuses and 1x holder | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-07-04 | c | 0.00049408 | 6.048e-06 | 2016 | 2015-07-04 | C | 2 | 0.00049408 | 6.0475e-06
5716737 | 2015-07-04 23:47 | 2015-07-05 00:21 | 34 | 5 | 170 | 34 | 31 | 0.00051404 | 155 | 0.00046868 | 1.5119e-05 | Restore Supply on Device TC6291 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc6291 | Found faulty DDO unit at TC6291. Isolated at ABS IC328. Replaced DDO & relivened | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.00046868 | 1.5119e-05 | 2016 | 2015-07-04 | C | 5 | 0.00046868 | 1.5119e-05
5716757 | 2015-07-04 23:48 | 2015-07-05 00:21 | 33.6667 | 127 | 4275.6667 | 33.6667 | 30.6667 | 0.012929 | 3894.6667 | 0.011777 | 0.00038402 | Restore Supply on Device IC328 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6291 | Found faulty DDO unit at TC6291. Isolated at ABS IC328. Replaced DDO & relivened | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-07-04 | c | 0.011777 | 0.00038402 | 2016 | 2015-07-04 | C | 127 | 0.011777 | 0.00038402
5717128 | 2015-07-05 08:19 | 2015-07-05 10:52 | 153.3833 | 25 | 2012.4 | 80.496 | 77.496 | 0.006085 | 1937.4 | 0.0058582 | 7.5594e-05 | Restore Supply on Device 2285T | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758844 | Repaired lines @ pole 758844 used 4m 6mm conductor and 2 sleeves. Patrolled balance of line with nothing obvious found | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-07-05 | c | 0.0058582 | 7.5594e-05 | 2016 | 2015-07-05 | C | 25 | 0.0058582 | 7.5594e-05
5717229 | 2015-07-05 10:13 | 2015-07-05 13:29 | 196 | 1 | 196 | 196 | 193 | 0.00059266 | 193 | 0.00058359 | 3.0238e-06 | Restore Supply on Device 4042T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763678 | 2R line down - Need to be replaced Replaced 1x 10A, 60A, 3A fuses and 2 spans of conductor Noting else repaired or replaced All surrounding assets up to Powerco standard | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-05 | c | 0.00058359 | 3.024e-06 | 2016 | 2015-07-05 | C | 1 | 0.00058359 | 3.0238e-06
5717246 | 2015-07-05 15:15 | 2015-07-05 16:19 | 64 | 24 | 1536 | 64 | 61 | 0.0046445 | 1464 | 0.0044268 | 7.257e-05 | Restore Supply on Device T9/216 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04847 |  | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-05 | c | 0.0044268 | 7.257e-05 | 2016 | 2015-07-05 | C | 24 | 0.0044268 | 7.257e-05
5719403 | 2015-07-06 03:36 | 2015-07-06 06:31 | 174.85 | 2 | 268.7167 | 134.3583 | 131.3583 | 0.00081253 | 262.7167 | 0.00079439 | 6.0475e-06 | Restore Supply on Device TE4-020 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE4 020 | Replace 2 x 15A H/V Fuses at Fuses SE4 020 ( bird strike ). Fuses Closed 06:07 | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-07-06 | c | 0.00079439 | 6.048e-06 | 2016 | 2015-07-06 | C | 2 | 0.00079439 | 6.0475e-06
5719656 | 2015-07-06 06:27 | 2015-07-06 06:47 | 19.9333 | 96 | 1913.6 | 19.9333 | 16.9333 | 0.0057863 | 1625.6 | 0.0049154 | 0.00029028 | Restore Supply on Device SE4-020 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE4-020 | Part Of OMS 5719403 2 15amp HV Fuses blown unknown cause | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-07-06 | c | 0.0049154 | 0.00029028 | 2016 | 2015-07-06 | C | 96 | 0.0049154 | 0.00029028
5720063 | 2015-07-06 08:55 | 2015-07-06 10:32 | 96.4667 | 1 | 96.4667 | 96.4667 | 93.4667 | 0.00029169 | 93.4667 | 0.00028262 | 3.0238e-06 | Restore Supply on Device T4/39 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/197 | Blown Fuse found at Transformer T4/197 - On relivening Transformer found to be Faulty refer OMS 5720284 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-07-06 | c | 0.00028262 | 3.024e-06 | 2016 | 2015-07-06 | C | 1 | 0.00028262 | 3.0238e-06
5720132 | 2015-07-21 09:40 | 2015-07-21 15:18 | 337.2167 | 1 | 337.2167 | 337.2167 | 334.2167 | 0.0010197 | 334.2167 | 0.0010106 | 3.0238e-06 | NAPA ID:10141 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole V0321 | Replace Pole V12581 (sectionaliser 9839). Works location: Manaia Rd, Coromandel. WO 30002265 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-07-21 | b | 0.0005053 | 1.512e-06 | 2016 | 2015-07-21 | B | 1 | 0.0010106 | 3.0238e-06
5720284 | 2015-07-06 10:28 | 2015-07-06 13:38 | 190.0167 | 2 | 380.0333 | 190.0167 | 187.0167 | 0.0011491 | 374.0333 | 0.001131 | 6.0475e-06 | Restore Supply on Device T4/197 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/197 | Transformer T4/197 found to be faulty - Isolated at Transformer fuses - Transformer replaced - Used 1 x 15 kVA transformer | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-07-06 | c | 0.001131 | 6.048e-06 | 2016 | 2015-07-06 | C | 2 | 0.001131 | 6.0475e-06
5720446 | 2015-07-06 12:04 | 2015-07-06 12:43 | 39 | 132 | 5148 | 39 | 36 | 0.015566 | 4752 | 0.014369 | 0.00039914 | Restore Supply on Device X2139 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | OMS 5720419 possibly related | OMS 5720419 possibly relate Damaged DDO found at Transformer X2140 - isolated at ABS's 523 & 506 - all DDO's replaced - Used 3x DDO's and 3 X 30 amp fuses | F2 | TAIHAPE TOWN NORTH | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-07-06 | c | 0.014369 | 0.00039914 | 2016 | 2015-07-06 | C | 132 | 0.014369 | 0.00039914
5720897 | 2015-07-07 09:13 | 2015-07-07 13:18 | 245 | 86 | 21070 | 245 | 242 | 0.063711 | 20812 | 0.062931 | 0.00026004 | NAPA ID:10856 TP_MANGAMAIRE GXP > MANGAMUTU SUB > KONINI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Make repairs to lines and poles damaged by slips needs investigation to see if done | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-07 | b | 0.031465 | 0.00013002 | 2016 | 2015-07-07 | B | 86 | 0.062931 | 0.00026004
5720985 | 2015-07-23 09:15 | 2015-07-23 15:18 | 362.5 | 53 | 2189.4 | 41.3094 | 38.3094 | 0.0066202 | 2030.4 | 0.0061394 | 0.00016026 | NAPA ID:10030 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 221721 | REPLACE ROTTEN TX - TE7-087 AND ARMS. Works location: Black Rd, Te Puke. WO 30010387 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-07-23 | b | 0.0030697 | 8.013e-05 | 2016 | 2015-07-23 | B | 53 | 0.0061394 | 0.00016026
5724084 | 2015-07-07 09:24 | 2015-07-07 15:45 | 380.7333 | 102 | 38834.8 | 380.7333 | 377.7333 | 0.11743 | 38528.8 | 0.1165 | 0.00030842 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 776341 | Car vs pole. 4km north of Raetihi. Valley Road (SH 4). Event # F1876866. ETA required. Chris from Fire Comms Wellington on 048010812. 9.03am - advise smc. 9.06am - eta of 5-10 min. advise chris at fire comms. Car V Pole at pole 776341 - isolated at ABS 27 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-07 | c | 0.1165 | 0.00030842 | 2016 | 2015-07-07 | C | 102 | 0.1165 | 0.00030842
5724345 | 2015-07-31 09:00 | 2015-07-31 13:24 | 264 | 98 | 25872 | 264 | 261 | 0.078231 | 25578 | 0.077342 | 0.00029633 | NAPA ID:07515 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 090 | Project number IR6978 Rangikura Reconstruction Replace poles Koihi Road poles 772937 to 781152. Works location: Koihi Rd. IR6978 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-31 | b | 0.038671 | 0.00014816 | 2016 | 2015-07-31 | B | 98 | 0.077342 | 0.00029633
5724655 | 2015-07-17 09:16 | 2015-07-17 13:13 | 237 | 108 | 25596 | 237 | 234 | 0.077396 | 25272 | 0.076416 | 0.00032657 | NAPA ID:10862 TP_WANGANUI GXP > BLINK BONNIE SUB > UNION LINE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 680 | Replace pole 793251 moving in a slip and leaning towards the road. Works location: Hwy 3 Kaitoki WO 30007436 | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-07-17 | b | 0.038208 | 0.00016328 | 2016 | 2015-07-17 | B | 108 | 0.076416 | 0.00032657
5724677 | 2015-07-25 11:10 | 2015-07-25 11:38 | 28 | 2 | 56 | 28 | 25 | 0.00016933 | 50 | 0.00015119 | 6.0475e-06 | NAPA ID:10826 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP523 | To install a 400V Fuse/Disconnector. Works locatioN: Hwy 26, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-25 | b | 7.5594e-05 | 3.024e-06 | 2016 | 2015-07-25 | B | 2 | 0.00015119 | 6.0475e-06
5725426 | 2015-07-08 02:47 | 2015-07-08 06:41 | 234.6833 | 239 | 56067.3167 | 234.5913 | 231.5913 | 0.16953 | 55350.3167 | 0.16737 | 0.00072268 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 777258 | Conductor down at pole 777258 Recloser tripped on C Phase O/C E/F | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-08 | c | 0.16737 | 0.00072268 | 2016 | 2015-07-08 | C | 239 | 0.16737 | 0.00072268
5726227 | 2015-07-08 06:44 | 2015-07-08 13:29 | 405.1333 | 239 | 80705.75 | 337.681 | 334.681 | 0.24403 | 79988.75 | 0.24187 | 0.00072268 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 373110 | Line sectionalised and patrolled found floating conductor @ pole 373110 and repaired | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-08 | c | 0.24187 | 0.00072268 | 2016 | 2015-07-08 | C | 239 | 0.24187 | 0.00072268
5726474 | 2015-07-08 06:59 | 2015-07-08 11:05 | 246.2 | 10 | 2459.4667 | 245.9467 | 242.9467 | 0.0074368 | 2429.4667 | 0.0073461 | 3.0238e-05 | Restore Supply on Device T2276 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7543 | replace 2 x 10 amp fuses. cause: unknown. pole 817189. fuse 7543. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-07-08 | c | 0.0073461 | 3.0238e-05 | 2016 | 2015-07-08 | C | 10 | 0.0073461 | 3.0238e-05
5726743 | 2015-07-08 08:07 | 2015-07-08 10:58 | 171.5 | 298 | 48065.8833 | 161.2949 | 158.2949 | 0.14534 | 47171.8833 | 0.14264 | 0.00090108 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210104 | at 08:06, Omokoroa Sub, CB 2 Whakamarama Feeder, Recloser 9560 Tripped, E/F, L/O. Faultmen dispatched and investigation began. Call came in of crossarm on fire. Faultman confirmed broken insulator and crossarm at Pole 210104. Isolated Lines at ABS 9560/1, | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-08 | c | 0.14264 | 0.00090108 | 2016 | 2015-07-08 | C | 298 | 0.14264 | 0.00090108
5729341 | 2015-07-10 09:50 | 2015-07-10 14:10 | 260 | 72 | 18712.1167 | 259.8905 | 256.8905 | 0.056581 | 18496.1167 | 0.055928 | 0.00021771 | NAPA ID:09982 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1038 | Replace H/V Crossarms and T/X's at Various Sites | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-10 | b | 0.027964 | 0.00010886 | 2016 | 2015-07-10 | B | 72 | 0.055928 | 0.00021771
5730984 | 2015-07-08 08:55 | 2015-07-08 12:27 | 212 | 1250 | 80942.6167 | 64.7541 | 61.7541 | 0.24475 | 77192.6167 | 0.23341 | 0.0037797 | Restore Supply on Device C855 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | During planned switching for NAPA 9973 a tripping occurred on CB C855 3phase O/C & E/F line sectionalised and patrolled with no apparent cause found and supply restored. Planned work proceeded with no other issues | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-07-08 | c | 0.23341 | 0.0037797 | 2016 | 2015-07-08 | C | 1250 | 0.23341 | 0.0037797
5732462 | 2015-07-08 17:39 | 2015-07-08 19:48 | 128.7833 | 1 | 128.7833 | 128.7833 | 125.7833 | 0.00038941 | 125.7833 | 0.00038034 | 3.0238e-06 | Restore Supply on Device N30 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N30 | 2x 10amp 11kv fuses N30 cause poss bird strike - spoke to Ian and he advised ok for me to clear job. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-07-08 | c | 0.00038034 | 3.024e-06 | 2016 | 2015-07-08 | C | 1 | 0.00038034 | 3.0238e-06
5732790 | 2015-07-08 20:45 | 2015-07-09 00:06 | 200.7 | 3 | 602.1 | 200.7 | 197.7 | 0.0018206 | 593.1 | 0.0017934 | 9.0713e-06 | Restore Supply on Device T1/125 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P33291 | Sparking at the power pole and cross arm is broken. 7.41pm advised Sammy at svs hub & control 950 Kellow Road, Palmerston North. Pole and crossarm on fire - isolated at fuses L24 - Temp repairs carried out (New Cross arm fixed lower on pole - pole will ne | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-08 | c | 0.0017934 | 9.071e-06 | 2016 | 2015-07-08 | C | 3 | 0.0017934 | 9.0713e-06
5733824 | 2015-07-09 10:28 | 2015-07-09 11:41 | 72.85 | 7 | 509.95 | 72.85 | 69.85 | 0.001542 | 488.95 | 0.0014785 | 2.1166e-05 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3084 | HV Jumper blown on top of Fuses at Transformer TC3084. Isolation at Fuses 2218 to repair | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-07-09 | c | 0.0014785 | 2.1166e-05 | 2016 | 2015-07-09 | C | 7 | 0.0014785 | 2.1166e-05
5733830 | 2015-07-09 09:09 | 2015-07-09 13:13 | 243.85 | 34 | 8290.9 | 243.85 | 240.85 | 0.02507 | 8188.9 | 0.024761 | 0.00010281 | Restore Supply on Device TE3-063 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 390638 | 7.55am - advise smc. Car vs pole, pole on car, person still in car. 100m from the crematorium. Event # F1877986. ETA required. 403 PYES PA ROAD, Tauranga. 8.00am - advise Fire Comms of 20-30 min eta, depending on traffic. Isolated between ABS IP581 & SE3- | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-07-09 | c | 0.024761 | 0.00010281 | 2016 | 2015-07-09 | C | 34 | 0.024761 | 0.00010281
5734335 | 2015-07-09 09:59 | 2015-07-09 12:55 | 175.5667 | 12 | 2106.8 | 175.5667 | 172.5667 | 0.0063705 | 2070.8 | 0.0062616 | 3.6285e-05 | Restore Supply on Device P54 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P03542 | Replaced Pole P03542. NDR N300084 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-07-09 | c | 0.0062616 | 3.6285e-05 | 2016 | 2015-07-09 | C | 12 | 0.0062616 | 3.6285e-05
5734364 | 2015-07-09 10:23 | 2015-07-09 12:39 | 135.5 | 82 | 11111 | 135.5 | 132.5 | 0.033597 | 10865 | 0.032853 | 0.00024795 | Restore Supply on Device X1697 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 182 | Replaced 2 x fuse links | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-09 | c | 0.032853 | 0.00024795 | 2016 | 2015-07-09 | C | 82 | 0.032853 | 0.00024795
5738365 | 2015-07-28 08:47 | 2015-07-28 16:10 | 442.7167 | 418 | 8153.2167 | 19.5053 | 16.5053 | 0.024653 | 6899.2167 | 0.020862 | 0.0012639 | NAPA ID:10108 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 11kV SA2-003 | Reconductor. Works location: Emerton Rd, Waihi Beach. WO 30002363 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-07-28 | b | 0.010431 | 0.00063197 | 2016 | 2015-07-28 | B | 418 | 0.020862 | 0.0012639
5739005 | 2015-07-09 15:58 | 2015-07-09 16:29 | 31.1 | 46 | 1430.6 | 31.1 | 28.1 | 0.0043258 | 1292.6 | 0.0039085 | 0.00013909 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuse 153 | Replace 2 x Fuse | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-09 | c | 0.0039085 | 0.00013909 | 2016 | 2015-07-09 | C | 46 | 0.0039085 | 0.00013909
5739015 | 2015-07-17 10:40 | 2015-07-17 13:12 | 152 | 3 | 456 | 152 | 149 | 0.0013788 | 447 | 0.0013516 | 9.0713e-06 | Referral: Referral: Restore Supply on Device T1/125 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | P33291 | this job is to replace pole on Fri 10/7 original referral 5733735 job was completed by mistake 2R to replace pole is already on the above oms. 4.04pm called svs hub and advised Sammy that this is a crew replacement because there was already a 2R request p | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-17 | c | 0.0013516 | 9.071e-06 | 2016 | 2015-07-17 | C | 3 | 0.0013516 | 9.0713e-06
5739970 | 2015-07-09 19:19 | 2015-07-09 23:35 | 256.4333 | 3 | 769.3 | 256.4333 | 253.4333 | 0.0023262 | 760.3 | 0.002299 | 9.0713e-06 | Restore Supply on Device N2060 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2060 | Transformer found to be faulty causing part powers , lv left on until replacement on site - isolated at transformer fuses and transformer replaced - used 1 x 50 kVA transformer to replaced a 30 kVA transformer | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-07-09 | c | 0.002299 | 9.071e-06 | 2016 | 2015-07-09 | C | 3 | 0.002299 | 9.0713e-06
5740936 | 2015-07-10 03:51 | 2015-07-10 04:21 | 30.65 | 209 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00063197 | Restore Supply on Device NG3 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB3 |  | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-07-10 | c | 0 | 0.00063197 | 2016 | 2015-07-10 | C | 209 | 0 | 0.00063197
5741846 | 2015-07-10 12:37 | 2015-07-10 13:51 | 73.9 | 232 | 10813.9 | 46.6116 | 43.6116 | 0.032699 | 10117.9 | 0.030594 | 0.00070151 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9146 | Recloser 9146 L/O on E/F. Contacted live line gang ( Jason Deans ) working on LLP 10778-01. Confirmed they did not cause tripping. Used Jason Deans to carry out switching untill Downer turned up on site. Patrolled rest of area found no fault relivened | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-07-10 | c | 0.030594 | 0.00070151 | 2016 | 2015-07-10 | C | 232 | 0.030594 | 0.00070151
5742588 | 2015-07-10 13:03 | 2015-07-10 18:04 | 300.7333 | 209 | 601.4667 | 2.8778 | -0.12217 | 0.0018187 | 0 | 0 | 0.00063197 | Restore Supply on Device N3220 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3220 | Transformer N3220 Replaced. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-07-10 | c | 0 | 0.00063197 | 2016 | 2015-07-10 | C | 209 | 0 | 0.00063197
5742907 | 2015-07-10 13:37 | 2015-07-10 14:47 | 69.8333 | 67 | 4678.8333 | 69.8333 | 66.8333 | 0.014148 | 4477.8333 | 0.01354 | 0.00020259 | Restore Supply on Device IC757 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H0011 | Replace Broken xarm complete | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-07-10 | c | 0.01354 | 0.00020259 | 2016 | 2015-07-10 | C | 67 | 0.01354 | 0.00020259
5742999 | 2015-07-10 13:16 | 2015-07-10 14:46 | 89.3833 | 2 | 178.7667 | 89.3833 | 86.3833 | 0.00054055 | 172.7667 | 0.00052241 | 6.0475e-06 | Restore Supply on Device PU202 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU202 | 2 X 6A Fuses Replaced. Bird Strike | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-07-10 | c | 0.0005224 | 6.048e-06 | 2016 | 2015-07-10 | C | 2 | 0.00052241 | 6.0475e-06
5743943 | 2015-07-27 22:00 | 2015-07-27 22:58 | 58 | 278 | 16124 | 58 | 55 | 0.048755 | 15290 | 0.046233 | 0.00084061 | NAPA ID:10703 TP_MT MAUNGANUI 33 GXP > OMANU SUB > CONCORDE AVE | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9730-2 | Repair 11KV cable lug that is getting hot. Works location: Concord Ave. WO 10179373 | F3 | CONCORDE AVE | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-07-27 | b | 0.023117 | 0.0004203 | 2016 | 2015-07-27 | B | 278 | 0.046233 | 0.00084061
5744691 | 2015-07-10 23:04 | 2015-07-11 06:58 | 474.3667 | 1 | 474.3667 | 474.3667 | 471.3667 | 0.0014344 | 471.3667 | 0.0014253 | 3.0238e-06 | Restore Supply on Device X2461 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773912 | Used 1 x 3 M H/T Arm 3 X Insulators 1 XFusearm 2 X Fuses | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-07-10 | c | 0.0014253 | 3.024e-06 | 2016 | 2015-07-10 | C | 1 | 0.0014253 | 3.0238e-06
5744812 | 2015-07-11 10:39 | 2015-07-11 11:19 | 40.7167 | 1 | 40.7167 | 40.7167 | 37.7167 | 0.00012312 | 37.7167 | 0.00011405 | 3.0238e-06 | Restore Supply on Device TC4-004 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC4-004 | FM was unable to find any fault - buzzing possible due to the cold morning weather | F3 | PILLANS POINT | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-07-11 | c | 0.00011405 | 3.024e-06 | 2016 | 2015-07-11 | C | 1 | 0.00011405 | 3.0238e-06
5744884 | 2015-07-11 12:50 | 2015-07-11 13:05 | 15.1167 | 8 | 120.9333 | 15.1167 | 12.1167 | 0.00036567 | 96.9333 | 0.0002931 | 2.419e-05 | Restore Supply on Device V86 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | P22830 | Replace pole P22830. Part of Job to Close up Temp Line Break After Flooding a bit Back. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-11 | c | 0.0002931 | 2.419e-05 | 2016 | 2015-07-11 | C | 8 | 0.0002931 | 2.419e-05
5745262 | 2015-07-11 19:16 | 2015-07-12 02:18 | 421.5833 | 680 | 147810.9 | 217.369 | 214.369 | 0.44694 | 145770.9 | 0.44078 | 0.0020562 | Restore Supply on Device I31 | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 707737 | Car vs pole near the high school Fire comms reference F1879648. Replaced pole 707737 and crossarm complete. NDR No 045661 | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-07-11 | c | 0.44078 | 0.0020562 | 2016 | 2015-07-11 | C | 680 | 0.44078 | 0.0020562
5745954 | 2015-07-11 19:46 | 2015-07-13 12:37 | 2450.8 | 8 | 600.3833 | 75.0479 | 72.0479 | 0.0018154 | 576.3833 | 0.0017428 | 2.419e-05 | Restore Supply on Device TC2955 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc2955 | Found trany faulty needs replacing 30kVA | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-07-11 | c | 0.0017428 | 2.419e-05 | 2016 | 2015-07-11 | C | 8 | 0.0017428 | 2.419e-05
5746604 | 2015-07-11 20:23 | 2015-07-11 22:44 | 141.3 | 1 | 141.3 | 141.3 | 138.3 | 0.00042726 | 138.3 | 0.00041819 | 3.0238e-06 | Restore Supply on Device W1327 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH184 | Replaced 2X 20a HV fuses and one holder | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-07-11 | c | 0.00041819 | 3.024e-06 | 2016 | 2015-07-11 | C | 1 | 0.00041819 | 3.0238e-06
5746639 | 2015-07-11 21:59 | 2015-07-11 22:24 | 24.8 | 30 | 744 | 24.8 | 21.8 | 0.0022497 | 654 | 0.0019775 | 9.0713e-05 | Other Request on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 214741 | Found jumper broken on TC4-144 Isolated transformer, repiared jumper & relivened | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-07-11 | c | 0.0019775 | 9.0713e-05 | 2016 | 2015-07-11 | C | 30 | 0.0019775 | 9.0713e-05
5746771 | 2015-07-12 09:20 | 2015-07-12 12:11 | 171 | 16 | 2736 | 171 | 168 | 0.008273 | 2688 | 0.0081279 | 4.838e-05 | Restore Supply on Device TB3-017 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201761 | ( AON 1) 1 x Burnt fuse holder required replacement at Fuses SB3 004. Fuses opened while replacements sourced from mainland. Further isolation required to replace fuse holder at Recloser S6040 ( no back feeds ) Fuse holder replaced, all service restored. | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-07-12 | c | 0.0081279 | 4.838e-05 | 2016 | 2015-07-12 | C | 16 | 0.0081279 | 4.838e-05
5746904 | 2015-07-12 09:50 | 2015-07-12 09:53 | 3 | 493 | 1479 | 3 | 0 | 0.0044721 | 0 | 0 | 0.0014907 | Restore Supply on Device XT30 | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P28597 | Tripping on Mangamaire-Pongaroa 33kV Line (Loss of supply to Pongaroa). Flags E/F, Deft Time, O/C. Supply restored via CB XT50 at Pongaroa Sub. Patrol carried out with Helicopter and a Dead Magpie found. Bird strike had caused a 33kV Insulator above to bl | F1,F2,F3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2015-07-12 | c | 0 | 0.0014907 | 2016 | 2015-07-12 | C | 493 | 0 | 0.0014907
5747452 | 2015-07-12 10:44 | 2015-07-12 12:35 | 111.2833 | 43 | 4785.1833 | 111.2833 | 108.2833 | 0.014469 | 4656.1833 | 0.014079 | 0.00013002 | Restore Supply on Device 426 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 426 | 2 HT fuses at 426. Line patrol found bird strike (Dead Swan). relivened OK with 2 X 15A Fuses. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-07-12 | c | 0.014079 | 0.00013002 | 2016 | 2015-07-12 | C | 43 | 0.014079 | 0.00013002
5747933 | 2015-07-12 16:18 | 2015-07-12 17:36 | 77.9333 | 4 | 311.7333 | 77.9333 | 74.9333 | 0.00094261 | 299.7333 | 0.00090632 | 1.2095e-05 | Restore Supply on Device X1219 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 4171 | Advised hub of 999. 2 HT fuses found tripped due to bird strike. Relivened OK (8A rating) | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-07-12 | c | 0.00090632 | 1.2095e-05 | 2016 | 2015-07-12 | C | 4 | 0.00090632 | 1.2095e-05
5748466 | 2015-07-13 02:05 | 2015-07-13 07:41 | 336.1333 | 1 | 336.1333 | 336.1333 | 333.1333 | 0.0010164 | 333.1333 | 0.0010073 | 3.0238e-06 | Restore Supply on Device T2/17 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/17 | Pls check if 5749116 is also related - yes related. Replaced 2 x 3amp ht fuses. Cause:unknown - birds FM did not go through control - advise needs too. Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-07-13 | c | 0.0010073 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 0.0010073 | 3.0238e-06
5748474 | 2015-07-13 06:56 | 2015-07-13 08:35 | 99.7167 | 217 | 15307.7667 | 70.5427 | 67.5427 | 0.046287 | 14656.7667 | 0.044319 | 0.00065616 | Restore Supply on Device R11 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | R11 | Line sectionalized & Patrolled no Fault found | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-13 | c | 0.044319 | 0.00065616 | 2016 | 2015-07-13 | C | 217 | 0.044319 | 0.00065616
5749116 | 2015-07-13 07:27 | 2015-07-13 07:55 | 27.85 | 1 | 27.85 | 27.85 | 24.85 | 8.4212e-05 | 24.85 | 7.514e-05 | 3.0238e-06 | Restore Supply on Device T2/18 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | poss related to 5748466 | related to 5748466 - yes related. Replaced 2 x 3amp ht fuses. Cause:unknown - birds. FM did not go through control - advise needs too. Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-07-13 | c | 7.514e-05 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 7.514e-05 | 3.0238e-06
5749162 | 2015-07-13 16:20 | 2015-07-13 17:22 | 62 | 3 | 186 | 62 | 59 | 0.00056242 | 177 | 0.00053521 | 9.0713e-06 | Restore Supply on Device TC2955 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2955 | Joanne advised that they are calling Metering Solutions to attend as they have no Electrical Inspectors available. 13/7 9am - Andrew Wilson to speak to PM. 09:24am Coops advises customer is paying for 3 phase 3 x 60amp fuses. There are 3 x 200amp fuses | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0.00053521 | 9.071e-06 | 2016 | 2015-07-13 | C | 3 | 0.00053521 | 9.0713e-06
5749512 | 2015-07-13 08:46 | 2015-07-13 10:55 | 129.5833 | 1 | 129.5833 | 129.5833 | 126.5833 | 0.00039183 | 126.5833 | 0.00038276 | 3.0238e-06 | Restore Supply on Device TC4-139 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9657/2 | CB 9657/2 Tripped. Overload. Closed OK | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0.00038276 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 0.00038276 | 3.0238e-06
5749528 | 2015-07-21 06:00 | 2015-07-21 06:44 | 43.9667 | 96 | 3776.1333 | 39.3347 | 36.3347 | 0.011418 | 3488.1333 | 0.010547 | 0.00029028 | NAPA ID:09403 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CENTRAL TRITON | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9942 | Remove rusted out series 2 switchgear S5449>S5463 and replace with Safelink2 CFCF switchgear 9942 Generators installed at transformers TC4-237 & TC4-319 under AP | F2 | CENTRAL TRITON | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-07-21 | b | 0.0052736 | 0.00014514 | 2016 | 2015-07-21 | B | 96 | 0.010547 | 0.00029028
5750513 | 2015-07-13 09:35 | 2015-07-13 12:20 | 165.1333 | 703 | 42398.25 | 60.3105 | 57.3105 | 0.1282 | 40289.25 | 0.12183 | 0.0021257 | Restore Supply on Device RC27 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | RC22 | Part of KPE CB1 tripping on 5750513. Recloser RC22 Failed causing CB1 KPE to trip. Recloser removed and jumpered through | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0.12183 | 0.0021257 | 2016 | 2015-07-13 | C | 703 | 0.12183 | 0.0021257
5751462 | 2015-07-13 09:38 | 2015-07-13 09:41 | 2.6 | 1385 | 3568.7333 | 2.5767 | -0.4233 | 0.010791 | 0 | 0 | 0.0041879 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 3 | A/R not patrolled. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0 | 0.0041879 | 2016 | 2015-07-13 | C | 1385 | 0 | 0.0041879
5752879 | 2015-07-13 12:02 | 2015-07-13 17:30 | 328 | 1 | 328 | 328 | 325 | 0.00099179 | 325 | 0.00098272 | 3.0238e-06 | Restore Supply on Device TC5186 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC466 | Transformer TC466 Blown Up. Replaced. This Should have been OMS 5753331 | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0.00098272 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 0.00098272 | 3.0238e-06
5752882 | 2015-07-20 09:17 | 2015-07-20 17:11 | 474.3333 | 47 | 15194.4667 | 323.2865 | 320.2865 | 0.045944 | 15053.4667 | 0.045518 | 0.00014212 | NAPA ID:11072 TP_MARTON GXP > PUKEPAPA SUB > LEEDSTOWN 22KV | 22 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | ABS 475 | Drop 22kv lines between poles 805157 and 805158 ( create line break at pole 505157)so a crane can install new concrete bridge supports washed out by recent flooding. Reinstate line at pole 805157. NOTE: delay in restoration as contractor took longer than | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-07-20 | b | 0.022759 | 7.1058e-05 | 2016 | 2015-07-20 | B | 47 | 0.045518 | 0.00014212
5753324 | 2015-07-18 09:09 | 2015-07-18 09:41 | 32.6333 | 1 | 32.6333 | 32.6333 | 29.6333 | 9.8675e-05 | 29.6333 | 8.9604e-05 | 3.0238e-06 | NAPA ID:11074 TP_HUIRANGI GXP > WAITARA WEST SUB > AFFCO-QUEEN ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB F61 | 11kV CB maintenance. Outage requested from ANZCO foods due to CB F51 being dedicated feeder. Outage time is for the outage. The other two CB's F61 and F05 can be done afterwards. The CB to be racked out of service, reason being F51 will restore supply and | F1 | AFFCO-QUEEN ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 2015-07-18 | b | 4.4802e-05 | 1.512e-06 | 2016 | 2015-07-18 | B | 1 | 8.9604e-05 | 3.0238e-06
5753516 | 2015-07-27 09:16 | 2015-07-27 11:58 | 162.0167 | 11 | 1782.1833 | 162.0167 | 159.0167 | 0.0053889 | 1749.1833 | 0.0052891 | 3.3261e-05 | NAPA ID:09604 TP_HAWERA GXP > MANAIA SUB > OKAIAWA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 720163 | Replace damaged pole 720163. Works location: Inaha Road, Kapuni. Work Order: 30007226. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-07-27 | b | 0.0026446 | 1.6631e-05 | 2016 | 2015-07-27 | B | 11 | 0.0052891 | 3.3261e-05
5753644 | 2015-07-13 10:35 | 2015-07-13 13:25 | 170.2667 | 32 | 5448.5333 | 170.2667 | 167.2667 | 0.016475 | 5352.5333 | 0.016185 | 9.676e-05 | Restore Supply on Device T31 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46600 | Replaced 2 x 2.7 c rossarms 11kv, 6 x 11kV clamp top insulators and 2 x arm braces at pole P46600 HV O/H. Unplanned outage damage originally seen by helicopter pilot and advised to Phil Barnes. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-13 | c | 0.016185 | 9.676e-05 | 2016 | 2015-07-13 | C | 32 | 0.016185 | 9.676e-05
5753932 | 2015-07-13 12:58 | 2015-07-13 16:09 | 190.6667 | 1 | 190.6667 | 190.6667 | 187.6667 | 0.00057653 | 187.6667 | 0.00056746 | 3.0238e-06 | Restore Supply on Device M3145 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | M3145 | Blown tx needs replacing - has spoken to Dave in NOC in regards to a 2R. M3145. Replaced 15kv tx m3145. pole 721076. cause: deterioration. also replaced 3 x 2 amp fuses and 3 x hv jumpers. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-07-13 | c | 0.00056746 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 0.00056746 | 3.0238e-06
5754241 | 2015-07-13 12:02 | 2015-07-13 17:30 | 328 | 6 | 1968 | 328 | 325 | 0.0059508 | 1950 | 0.0058963 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC466 |  | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-13 | c | 0.0058963 | 1.8143e-05 | 2016 | 2015-07-13 | C | 6 | 0.0058963 | 1.8143e-05
5755396 | 2015-07-13 14:43 | 2015-07-13 20:03 | 319.3667 | 1 | 319.3667 | 319.3667 | 316.3667 | 0.00096569 | 316.3667 | 0.00095662 | 3.0238e-06 | Restore Supply on Device T7/594 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer T7/594 | 2 HT fuses tripped on T7/594. Tripped on reclose. Faulty transformer requires changing. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-13 | c | 0.00095662 | 3.024e-06 | 2016 | 2015-07-13 | C | 1 | 0.00095662 | 3.0238e-06
5755439 | 2015-07-31 09:07 | 2015-07-31 15:57 | 410.0667 | 102 | 16685.5 | 163.5833 | 160.5833 | 0.050453 | 16379.5 | 0.049528 | 0.00030842 | NAPA ID:10880 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC765 | Break jumpers at pole I2026. Replace pole H3611(Recloser 9720). Reinstate jumpers at pole I2026.Works location: Morrinsville/Walton Rd. WO 30009816 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-07-31 | b | 0.024764 | 0.00015421 | 2016 | 2015-07-31 | B | 102 | 0.049528 | 0.00030842
5756518 | 2015-07-14 03:42 | 2015-07-14 05:23 | 101 | 103 | 10403 | 101 | 98 | 0.031456 | 10094 | 0.030522 | 0.00031145 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 214835 | Car V Pole, Police comms report. Pole ok but conductor has unbound on pole 214835 & conductor making contact with trees. Em switching to isolate pole 214835 between ABS IP530, ABS SD4 094, Fuses SD4 542 & CB2 with recloser 9503 closed for back feed. Cond | F3 | MATAPIHI RD | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-07-14 | c | 0.030522 | 0.00031145 | 2016 | 2015-07-14 | C | 103 | 0.030522 | 0.00031145
5756743 | 2015-07-14 10:30 | 2015-07-14 10:48 | 18.1167 | 232 | 4082.8333 | 17.5984 | 14.5984 | 0.012346 | 3386.8333 | 0.010241 | 0.00070151 | Restore Supply on Device TC4-031 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4-031 | Jayden on his way and Josh leaving site - replacing 200amp fuse and holder at TX. HV Isolation Between Sw/gear SC4-420 and SD4-285 to repair broken LV Jumper at Transformer TC4-031. Backfeed via Sw/gear 9618. blown tx fuse and case. needs a 200amp fuse. | F3 | CHERRYWOOD DRIVE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-07-14 | c | 0.010241 | 0.00070151 | 2016 | 2015-07-14 | C | 232 | 0.010241 | 0.00070151
5756878 | 2015-07-30 08:46 | 2015-07-30 13:18 | 272.0167 | 43 | 3691.55 | 85.85 | 82.85 | 0.011162 | 3562.55 | 0.010772 | 0.00013002 | NAPA ID:10927 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11klV pole 218187 | 1 / MAKE 11KV BREAK AT POLE 218187 SEE NOTES FOR DETAILS.2/ AP TO REPLACE POLE & RECON SPAN OVER RAILWAY TRACKS UNDER RAIL PERMIT TO IODINE TO COMPLETE JOB AND CONNECTIONS . 3/ RE MAKE 11KV BREAK AT POLE 218187 SEE NOTES FOR DETAILS.Works location: Hwy | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-30 | b | 0.0053861 | 6.5011e-05 | 2016 | 2015-07-30 | B | 43 | 0.010772 | 0.00013002
5757298 | 2015-07-30 08:48 | 2015-07-30 14:31 | 342.7667 | 477 | 26724.1 | 56.0254 | 53.0254 | 0.080807 | 25293.1 | 0.07648 | 0.0014423 | NAPA ID:10101 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SA2-003 | 11kV Reconductor. Works location: Emerton Rd, Waihi Beach. WO 30002363 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-07-30 | b | 0.03824 | 0.00072117 | 2016 | 2015-07-30 | B | 477 | 0.07648 | 0.0014423
5762773 | 2015-08-04 09:31 | 2015-08-04 14:52 | 320.7833 | 224 | 61982.9167 | 276.7094 | 273.7094 | 0.18742 | 61310.9167 | 0.18539 | 0.00067732 | NAPA ID:08972 TP_PIAKO GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | n/a | Paul Cooper: Replace 33kV & 11kV crossarms & 1 pole various locations. Brent Williams: Repair to MABS 34 (DNO 140821). Guy Sharp: Change RTU over for Morrinsville 11kV CB2 & Test. (CB will be racked down and NOT in service). Guy Sharp: Move controls for 3 | F1 | NZDC A | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-08-04 | b | 0.092695 | 0.00033866 | 2016 | 2015-08-04 | B | 224 | 0.18539 | 0.00067732
5765379 | 2015-08-03 08:46 | 2015-08-03 12:00 | 194.1167 | 1 | 194.1167 | 194.1167 | 191.1167 | 0.00058696 | 191.1167 | 0.00057789 | 3.0238e-06 | NAPA ID:10953 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI721 | Replace transformer pole and arms; re use transformer. Works location: Wilson Rd, Kakaramea. WO 30009387. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-08-03 | b | 0.00028895 | 1.512e-06 | 2016 | 2015-08-03 | B | 1 | 0.00057789 | 3.0238e-06
5765383 | 2015-07-15 08:30 | 2015-07-15 10:18 | 108 | 1 | 108 | 108 | 105 | 0.00032657 | 105 | 0.00031749 | 3.0238e-06 | NAPA ID:11160 TP_MASTERTON GXP > CHAPEL SUB > HEAD OFFICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 11053 | REPAIR WORK TO GROUND LEVEL TRANSFORMER AND PAD APPEARS TO BEEN RUN OVER CAUSING PAD AND TRANSFORMER TO SINK ON 11KV SIDE PUTTING PRESSURE ON 11KV CABLE. Works location; DIxon St | F2 | HEAD OFFICE | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-07-15 | b | 0.00015875 | 1.512e-06 | 2016 | 2015-07-15 | B | 1 | 0.00031749 | 3.0238e-06
5765621 | 2015-07-14 18:13 | 2015-07-14 18:18 | 5 | 1 | 5 | 5 | 2 | 1.5119e-05 | 2 | 6.0475e-06 | 3.0238e-06 | Restore Supply on Device L1057 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI762 | called customer to confirm address, customer advised their address is 2 Powerhouse Road, Patea 2 fuses blown. Line patrolled fuses LI762 reloaded relivened. Possibly bird strike. 2x10amp HV fuses | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-14 | c | 6.048e-06 | 3.024e-06 | 2016 | 2015-07-14 | C | 1 | 6.0475e-06 | 3.0238e-06
5766814 | 2015-07-14 18:14 | 2015-07-14 18:18 | 4.6667 | 4 | 18.6667 | 4.6667 | 1.6667 | 5.6444e-05 | 6.6667 | 2.0158e-05 | 1.2095e-05 | Restore Supply on Device LI762 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | li 762 | called customer to confirm address, customer advised their address is 2 Powerhouse Road, Patea 2 fuses blown. Line patrolled fuses LI762 reloaded relivened. Possibly bird strike. 2x10amp HV fuses48pm spoke with David S and asked if ok to complete Bevan fr | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-14 | c | 2.0158e-05 | 1.2095e-05 | 2016 | 2015-07-14 | C | 4 | 2.0158e-05 | 1.2095e-05
5766904 | 2015-07-15 09:45 | 2015-07-15 11:35 | 110.2 | 11 | 1212.2 | 110.2 | 107.2 | 0.0036654 | 1179.2 | 0.0035656 | 3.3261e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P19196 | cnr Halcombe Road and Mingaroa Road, Halcolmbe. car vs pole, lines down, sparking. Event # P021844042. Steve from Police on 04 381 2000 ext 40017. 7.53pm - advise smc. 7.58pm - advised Shellie from Police of eta of 20 min. and also Fire Comms. pole # p191 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-15 | c | 0.0035656 | 3.3261e-05 | 2016 | 2015-07-15 | C | 11 | 0.0035656 | 3.3261e-05
5767855 | 2015-08-03 09:50 | 2015-08-03 13:36 | 226 | 33 | 7458 | 226 | 223 | 0.022551 | 7359 | 0.022252 | 9.9784e-05 | NAPA ID:10450 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 195 | Trimming trees between poles 844671 and 844672. Works location: Makaho Valley Rd, Waitotara. PPPD 53383. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-03 | b | 0.011126 | 4.9892e-05 | 2016 | 2015-08-03 | B | 33 | 0.022252 | 9.9784e-05
5767856 | 2015-08-03 09:55 | 2015-08-03 14:30 | 275 | 3 | 825 | 275 | 272 | 0.0024946 | 816 | 0.0024674 | 9.0713e-06 | NAPA ID:10232 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M12395 | LLP: Replace the 11kV Pin Arm & 11kV D.O.Fuse arm Plus Fuses. AP: Replace the 400V Pin Arm & Install 400V Fuse/Disconnector. Works location: Lichfield Rd, Putaruru. WO 30010392. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.0012337 | 4.536e-06 | 2016 | 2015-08-03 | B | 3 | 0.0024674 | 9.0713e-06
5770306 | 2015-08-04 10:06 | 2015-08-04 11:22 | 75.3333 | 24 | 1808 | 75.3333 | 72.3333 | 0.005467 | 1736 | 0.0052492 | 7.257e-05 | NAPA ID:11075 TP_BRUNSWICK GXP > ROBERTS AVE SUB > BRUNSWICK | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 952 | Repair broken dead end at pole 782569. Works location: Western Line, Wanganui. WO 10161766. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-08-04 | b | 0.0026246 | 3.6285e-05 | 2016 | 2015-08-04 | B | 24 | 0.0052492 | 7.257e-05
5771072 | 2015-08-03 09:00 | 2015-08-03 11:30 | 150 | 8 | 1200 | 150 | 147 | 0.0036285 | 1176 | 0.0035559 | 2.419e-05 | NAPA ID:10744 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC518 | Replace crossarms at TC518. Works location: Fisher Rd, Paeroa. WO 30008212. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.001778 | 1.2095e-05 | 2016 | 2015-08-03 | B | 8 | 0.0035559 | 2.419e-05
5771074 | 2015-07-15 10:02 | 2015-07-15 10:04 | 2 | 3 | 6 | 2 | -1 | 1.8143e-05 | 0 | 0 | 9.0713e-06 | Restore Supply on Device TC5058 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5058 | Tranformer TC5058 isolated for tapping down. Customer getting high voltages & damage to electonic equipment because of this. Transformer was on +2.5% voltages measured by electician at 250Volts. Voltage now 239V. Safety Manager 484291 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0 | 9.071e-06 | 2016 | 2015-07-15 | C | 3 | 0 | 9.0713e-06
5771079 | 2015-08-03 09:00 | 2015-08-03 12:21 | 201.0667 | 17 | 3418.1333 | 201.0667 | 198.0667 | 0.010336 | 3367.1333 | 0.010181 | 5.1404e-05 | NAPA ID:11008 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7702 | Replace defective 11kV pole 832924. Works location: Burnetts Rd, Masterton. WO 30000980. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-08-03 | b | 0.0050907 | 2.5702e-05 | 2016 | 2015-08-03 | B | 17 | 0.010181 | 5.1404e-05
5771083 | 2015-07-15 08:38 | 2015-07-15 10:42 | 124.2167 | 5 | 621.0833 | 124.2167 | 121.2167 | 0.001878 | 606.0833 | 0.0018327 | 1.5119e-05 | Restore Supply on Device X677 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1362 | Found 2 x fuses blown at fuses 1362 - no cause found - used 2x 6 amp uses and holders | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-07-15 | c | 0.0018327 | 1.5119e-05 | 2016 | 2015-07-15 | C | 5 | 0.0018327 | 1.5119e-05
5771085 | 2015-08-03 12:00 | 2015-08-03 12:45 | 45 | 7 | 315 | 45 | 42 | 0.00095248 | 294 | 0.00088899 | 2.1166e-05 | NAPA ID:10688 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3416 | To install 400V Fuses on the Transformer LV. Works location: Morrinsville Walton Road. WO 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.00044449 | 1.0583e-05 | 2016 | 2015-08-03 | B | 7 | 0.00088899 | 2.1166e-05
5771090 | 2015-08-04 09:16 | 2015-08-04 10:05 | 49.6667 | 201 | 9983 | 49.6667 | 46.6667 | 0.030186 | 9380 | 0.028363 | 0.00060778 | NAPA ID:10453 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 4064 | Trimming trees around poles 773473 and 773474 SH3 Waitotara. Works location: State Highway 3 Waitotara. PPPD 53535. Job Cancelled due to not being able to get Road side Link out at Links 4060. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-04 | b | 0.014181 | 0.00030389 | 2016 | 2015-08-04 | B | 201 | 0.028363 | 0.00060778
5771105 | 2015-08-03 14:00 | 2015-08-03 14:35 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 | NAPA ID:10689 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3077 | Install 400V Fuses on transformer LV. Works location: Morrinsville Walton Rd. WO 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.00019352 | 6.048e-06 | 2016 | 2015-08-03 | B | 4 | 0.00038704 | 1.2095e-05
5771222 | 2015-08-04 09:17 | 2015-08-04 12:48 | 210.6833 | 4 | 842.7333 | 210.6833 | 207.6833 | 0.0025482 | 830.7333 | 0.0025119 | 1.2095e-05 | NAPA ID:10272 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X944 | Remove 11kV jumpers to transformer X944 by g/b methods. Change Fuse arm, transformer and hardware pole 786321. Works location: Moehau Rd, Taihape. WO 30001682. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-04 | b | 0.001256 | 6.048e-06 | 2016 | 2015-08-04 | B | 4 | 0.0025119 | 1.2095e-05
5771559 | 2015-08-04 09:24 | 2015-08-04 16:45 | 441.1 | 222 | 97924.2 | 441.1 | 438.1 | 0.2961 | 97258.2 | 0.29409 | 0.00067127 | NAPA ID:09765 TP_MARTON GXP > BULLS SUB > RACECOURSE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1318 | Work as part of Bulls township Tender, LV poles and xarms, HV poles and Crossarms.Works location: Taumahi St, Bulls.WO 30001091 | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-08-04 | b | 0.14704 | 0.00033564 | 2016 | 2015-08-04 | B | 222 | 0.29409 | 0.00067127
5771742 | 2015-08-05 09:05 | 2015-08-05 12:43 | 217.8 | 25 | 5445 | 217.8 | 214.8 | 0.016464 | 5370 | 0.016238 | 7.5594e-05 | NAPA ID:10426 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L19 | Replace 11kV pole & transformer. Works location: Rosina Rd, Tangimoana. WO 30003249. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-05 | b | 0.0081188 | 3.7797e-05 | 2016 | 2015-08-05 | B | 25 | 0.016238 | 7.5594e-05
5771766 | 2015-08-10 10:22 | 2015-08-10 12:00 | 98 | 3 | 294 | 98 | 95 | 0.00088899 | 285 | 0.00086177 | 9.0713e-06 | NAPA ID:10754 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2347 | Replace Crossarms and Hardware at TC2347. Works location: Highway 29, Te Poi. WO 30003315. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-08-10 | b | 0.00043089 | 4.536e-06 | 2016 | 2015-08-10 | B | 3 | 0.00086177 | 9.0713e-06
5771789 | 2015-08-05 08:51 | 2015-08-05 13:00 | 248.6833 | 16 | 3978.9333 | 248.6833 | 245.6833 | 0.012031 | 3930.9333 | 0.011886 | 4.838e-05 | NAPA ID:10773 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2835 | Install new conductor across gully between sites 786805(new H-Pole) and 786807/786806(new H-Pole). See plans for details. Works location: Taihape-Napier Rd, Taihape. WO 10161206. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-05 | b | 0.0059431 | 2.419e-05 | 2016 | 2015-08-05 | B | 16 | 0.011886 | 4.838e-05
5772503 | 2015-07-21 09:02 | 2015-07-21 15:31 | 389.3 | 508 | 221.2 | 0.43543 | -2.5646 | 0.00066886 | 0 | 0 | 0.0015361 | NAPA ID:11226 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SA2-003 | Reconductor. Works location: Emerton Rd, Waihi Beach. WO 30002363 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-07-21 | b | 0 | 0.00076804 | 2016 | 2015-07-21 | B | 508 | 0 | 0.0015361
5772511 | 2015-08-06 09:15 | 2015-08-06 16:07 | 411.5167 | 21 | 8641.85 | 411.5167 | 408.5167 | 0.026131 | 8578.85 | 0.02594 | 6.3499e-05 | NAPA ID:11172 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726697 | Shutdown on LI6 to change twin circuit pole 726697 (LI1 is already de-energised), and Hardware Removal & Preparation work, for the reinstatement of the Livingstone Substation's LI 1 feeder. Works location: Livingstone Sub. WO 30011733. | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-08-06 | b | 0.01297 | 3.1749e-05 | 2016 | 2015-08-06 | B | 21 | 0.02594 | 6.3499e-05
5772515 | 2015-08-03 10:00 | 2015-08-03 13:30 | 210 | 9 | 1890 | 210 | 207 | 0.0057149 | 1863 | 0.0056333 | 2.7214e-05 | NAPA ID:10791 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC675 | Replace Transformer and L.V arms at TC675. Works location: Tapu Coroglen Rd, Thames. WO 30010652. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.0028166 | 1.3607e-05 | 2016 | 2015-08-03 | B | 9 | 0.0056333 | 2.7214e-05
5773245 | 2015-07-16 18:10 | 2015-07-16 20:00 | 110 | 3 | 330 | 110 | 107 | 0.00099784 | 321 | 0.00097063 | 9.0713e-06 | Referral: Restore Supply on Device TC5058 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5058 | follow up due to excessive Voltage issues and further investigation to prove network status. A fault person to carry out the following please. Check up stream/ Down stream Transformers for Tap position, Voltage phase to Earth and Ph to Ph for the followin | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.00097063 | 9.071e-06 | 2016 | 2015-07-16 | C | 3 | 0.00097063 | 9.0713e-06
5773403 | 2015-07-15 20:15 | 2015-07-15 21:58 | 102.3333 | 1 | 102.3333 | 102.3333 | 99.3333 | 0.00030943 | 99.3333 | 0.00030036 | 3.0238e-06 | Restore Supply on Device TF7-141 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | TF7-141 | 8.18pm - advise smc. Inspected and found to be salt spray tracking | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.00030036 | 3.024e-06 | 2016 | 2015-07-15 | C | 1 | 0.00030036 | 3.0238e-06
5774001 | 2015-07-15 21:16 | 2015-07-15 23:15 | 118.6167 | 2 | 237.2333 | 118.6167 | 115.6167 | 0.00071734 | 231.2333 | 0.00069919 | 6.0475e-06 | Restore Supply on Device TC510 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC510 | 2 X 3 A HV Fuses | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.00069919 | 6.048e-06 | 2016 | 2015-07-15 | C | 2 | 0.00069919 | 6.0475e-06
5774011 | 2015-07-16 21:26 | 2015-07-17 04:07 | 401 | 4 | 1604 | 401 | 398 | 0.0048501 | 1592 | 0.0048138 | 1.2095e-05 | Restore Supply on Device TC1660 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1660 | 3 X 3A Fuses Lightning | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0048138 | 1.2095e-05 | 2016 | 2015-07-16 | C | 4 | 0.0048138 | 1.2095e-05
5774949 | 2015-07-15 21:28 | 2015-07-16 00:13 | 165.5667 | 934 | 71098.9333 | 76.1231 | 73.1231 | 0.21499 | 68296.9333 | 0.20651 | 0.0028242 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C3493 | 1 x 11kV Poly Insulator. Lightning | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.20651 | 0.0028242 | 2016 | 2015-07-15 | C | 934 | 0.20651 | 0.0028242
5775889 | 2015-07-15 21:30 | 2015-07-16 03:25 | 354.5167 | 1 | 354.5167 | 354.5167 | 351.5167 | 0.001072 | 351.5167 | 0.0010629 | 3.0238e-06 | Restore Supply on Device TC5780 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC4-233 | 3 X 6A HV Fuses Lightning | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.0010629 | 3.024e-06 | 2016 | 2015-07-15 | C | 1 | 0.0010629 | 3.0238e-06
5775891 | 2015-07-15 21:31 | 2015-07-16 05:10 | 459.55 | 659 | 165751.4833 | 251.5197 | 248.5197 | 0.50119 | 163774.4833 | 0.49521 | 0.0019927 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 248632 | 2 x sleeves 2 x Binders 2 x HV Pins, 3mtrs Racoon Conductor | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.49521 | 0.0019927 | 2016 | 2015-07-15 | C | 659 | 0.49521 | 0.0019927
5776580 | 2015-07-15 22:00 | 2015-07-16 01:26 | 206.1 | 5 | 1030.5 | 206.1 | 203.1 | 0.003116 | 1015.5 | 0.0030706 | 1.5119e-05 | Restore Supply on Device TC856 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC856 | 3 X 3A HV Fuses Replaced | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-15 | c | 0.0030706 | 1.5119e-05 | 2016 | 2015-07-15 | C | 5 | 0.0030706 | 1.5119e-05
5781571 | 2015-07-16 04:34 | 2015-07-16 08:46 | 252.3 | 2 | 263.55 | 131.775 | 128.775 | 0.00079691 | 257.55 | 0.00077877 | 6.0475e-06 | Restore Supply on Device TC6321 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC 925 | 2x 3Amp HV Links | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.00077877 | 6.048e-06 | 2016 | 2015-07-16 | C | 2 | 0.00077877 | 6.0475e-06
5781736 | 2015-07-16 07:00 | 2015-07-16 13:50 | 409.6667 | 6 | 2458 | 409.6667 | 406.6667 | 0.0074324 | 2440 | 0.007378 | 1.8143e-05 | Restore Supply on Device TC2680 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2680 | Completed while OMS was down - unable to verify or restore when completing the crew onsite. Replaced 3x 3A HT fuses. Due to lightning strike. Nothing else repaired or replaced. All surrounding assets up to Powerco standard | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.007378 | 1.8143e-05 | 2016 | 2015-07-16 | C | 6 | 0.007378 | 1.8143e-05
5781738 | 2015-07-16 07:00 | 2015-07-16 11:00 | 240 | 849 | 45030 | 53.0389 | 50.0389 | 0.13616 | 42483 | 0.12846 | 0.0025672 | Restore Supply on Device 8 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40100 | Flash reported between number 86 & 72 Grove Rd Ashhurst. Repaired lines @ poles P40100 & P39966 Suspect due to bird strike. Transformer T4/15 lV Isolated due to possible clash between 11kV & 400v Transformer restored with , 1301 Colyton road Disconnecti | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.12846 | 0.0025672 | 2016 | 2015-07-16 | C | 849 | 0.12846 | 0.0025672
5783807 | 2015-07-16 07:10 | 2015-07-16 09:40 | 149.85 | 3 | 447.4667 | 149.1556 | 146.1556 | 0.001353 | 438.4667 | 0.0013258 | 9.0713e-06 | Restore Supply on Device TC4215 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4215 | 3 x HV fuses replaced on transformer | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0013258 | 9.071e-06 | 2016 | 2015-07-16 | C | 3 | 0.0013258 | 9.0713e-06
5783854 | 2015-07-16 07:36 | 2015-07-16 10:31 | 174.8167 | 2 | 174.8167 | 87.4083 | 84.4083 | 0.0005286 | 168.8167 | 0.00051046 | 6.0475e-06 | Restore Supply on Device TB1-155 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TB1-155 | 2 x HV fuses replaced - did not work through control, when asked FM replied "no I did not know I had to? , I transferred him to Maurice in Control for sign off. | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.00051046 | 6.048e-06 | 2016 | 2015-07-16 | C | 2 | 0.00051046 | 6.0475e-06
5787095 | 2015-07-16 08:27 | 2015-07-16 09:13 | 46.6 | 1 | 46.6 | 46.6 | 43.6 | 0.00014091 | 43.6 | 0.00013184 | 3.0238e-06 | Restore Supply on Device T4/157 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | called customer at 305 midland road and confirmed power is on | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.00013184 | 3.024e-06 | 2016 | 2015-07-16 | C | 1 | 0.00013184 | 3.0238e-06
5787142 | 2015-07-16 08:51 | 2015-07-16 15:32 | 401.35 | 3 | 1062.4833 | 354.1611 | 351.1611 | 0.0032127 | 1053.4833 | 0.0031855 | 9.0713e-06 | Restore Supply on Device TC2195 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2195 | Replace 3 x 3amp ddo fuses at tx tc2195 due to lightning. FM was offsite at 3:30pm. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0031855 | 9.071e-06 | 2016 | 2015-07-16 | C | 3 | 0.0031855 | 9.0713e-06
5787168 | 2015-07-16 07:15 | 2015-07-16 09:03 | 107.5833 | 6 | 645.5 | 107.5833 | 104.5833 | 0.0019518 | 627.5 | 0.0018974 | 1.8143e-05 | Restore Supply on Device TC220 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC220 | Replaced 2x 3Amp Links | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0018974 | 1.8143e-05 | 2016 | 2015-07-16 | C | 6 | 0.0018974 | 1.8143e-05
5787180 | 2015-07-15 22:58 | 2015-07-16 01:19 | 141 | 2507 | 135513 | 54.0538 | 51.0538 | 0.40976 | 127992 | 0.38702 | 0.0075806 | Restore Supply on Device 5 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 750711 | Tripping on Moturoa CB5 on E/F protection. Attempt to close VS8760 failed from NOC. Carried out locally (control box fault). Feeder patrolled. Found 3 insulators broken at pole 750711 isolated at abs 329 &144. BRENT MORRATTI AND C VIVIER ATTENDED THIS IS | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-07-15 | c | 0.38702 | 0.0075806 | 2016 | 2015-07-15 | C | 2507 | 0.38702 | 0.0075806
5789898 | 2015-07-16 15:20 | 2015-07-16 17:50 | 150 | 8 | 1200 | 150 | 147 | 0.0036285 | 1176 | 0.0035559 | 2.419e-05 | Restore Supply on Device TC2885 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2885 | 2.07pm - don watson leaving site, 2R requested as transformer is blown and needs to be replaced Materials used: 1x 30kva/3 phase transformer, 1x Q3 Quiklug connector, 3x 6Amp lugs Attended by B Fisher, Ferdinand, J Briar also. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0035559 | 2.419e-05 | 2016 | 2015-07-16 | C | 8 | 0.0035559 | 2.419e-05
5789914 | 2015-08-06 10:00 | 2015-08-06 10:50 | 50 | 5 | 250 | 50 | 47 | 0.00075594 | 235 | 0.00071058 | 1.5119e-05 | NAPA ID:10690 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3019 | To install 400V Fuses on the Transformer LV. Works location: Haynes Rd. WO 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-06 | b | 0.00035529 | 7.559e-06 | 2016 | 2015-08-06 | B | 5 | 0.00071058 | 1.5119e-05
5789924 | 2015-08-06 14:00 | 2015-08-06 14:45 | 45 | 2 | 90 | 45 | 42 | 0.00027214 | 84 | 0.000254 | 6.0475e-06 | NAPA ID:10692 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4209 | To install 400V fuses on the transformer LV. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-06 | b | 0.000127 | 3.024e-06 | 2016 | 2015-08-06 | B | 2 | 0.000254 | 6.0475e-06
5789931 | 2015-08-06 12:00 | 2015-08-06 12:45 | 45 | 9 | 405 | 45 | 42 | 0.0012246 | 378 | 0.001143 | 2.7214e-05 | NAPA ID:10691 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC405 | To install 400V Fuses on the Transformer LV. Works location: Waikuku Rd. WO 10147849. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-06 | b | 0.00057149 | 1.3607e-05 | 2016 | 2015-08-06 | B | 9 | 0.001143 | 2.7214e-05
5790060 | 2015-08-13 09:20 | 2015-08-13 14:36 | 316.2667 | 25 | 7906.6667 | 316.2667 | 313.2667 | 0.023908 | 7831.6667 | 0.023681 | 7.5594e-05 | NAPA ID:10235 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 841 | Replace poles & arms various locations. Works location: Te Miro. WO 300018074. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-13 | b | 0.011841 | 3.7797e-05 | 2016 | 2015-08-13 | B | 25 | 0.023681 | 7.5594e-05
5790083 | 2015-08-06 09:30 | 2015-08-06 14:08 | 278.45 | 26 | 7239.7 | 278.45 | 275.45 | 0.021891 | 7161.7 | 0.021655 | 7.8618e-05 | NAPA ID:10943 TP_HAWERA GXP > KAPUNI SUB > KAPUNI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | KA116 | Replace existing network pole 719356 with new 11m busck pole fitted with Temporary Regulator structure 12092 ABS 12092 will be closed for 11kV supply of feeder. Works location: Skeet Rd, Kapuni. WO 30001919. | F4 | KAPUNI | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-08-06 | b | 0.010828 | 3.9309e-05 | 2016 | 2015-08-06 | B | 26 | 0.021655 | 7.8618e-05
5790662 | 2015-07-16 10:55 | 2015-07-16 12:05 | 69.7667 | 782 | 53951.6333 | 68.9919 | 65.9919 | 0.16314 | 51605.6333 | 0.15604 | 0.0023646 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | F1326 | oms 5791452 line down could be cause advised Pete Senior in control. Tower Rd CB3 Trip, E/F, O/C A-B-C Phase. Neutral wire crossing road appears to have been hit by truck and has flicked up and onto HV lines. Repaired using 15mtrs of 7/052 bare Cu. and 3x | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.15604 | 0.0023646 | 2016 | 2015-07-16 | C | 782 | 0.15604 | 0.0023646
5791499 | 2015-07-16 06:22 | 2015-07-16 11:17 | 295.4 | 3 | 886.2 | 295.4 | 292.4 | 0.0026797 | 877.2 | 0.0026524 | 9.0713e-06 | Restore Supply on Device TC1004 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1004 | Replaced 3x 3Amp HV Links | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.0026524 | 9.071e-06 | 2016 | 2015-07-16 | C | 3 | 0.0026524 | 9.0713e-06
5791520 | 2015-07-16 11:30 | 2015-07-16 12:58 | 88 | 1003 | 70899.1667 | 70.6871 | 67.6871 | 0.21438 | 67890.1667 | 0.20528 | 0.0030328 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | S5505 | Trip to L/O on CB 1. CB 1 was also donor feeder for outage on CB 2 for protection maintenance. Bus split was created at CB 38 Waihi Rd sub to limit fault levels during sectionalising. Cables sectionalised & supply restored gradually. LFI at sw/gear found | F3 | 11TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.20528 | 0.0030328 | 2016 | 2015-07-16 | C | 1003 | 0.20528 | 0.0030328
5792536 | 2015-07-16 11:51 | 2015-07-16 14:06 | 134.55 | 1 | 134.55 | 134.55 | 131.55 | 0.00040685 | 131.55 | 0.00039778 | 3.0238e-06 | Restore Supply on Device TC361 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13418 | Replaced 2x 2A fuse. Due to unknown cause. Nothing else repaired or replaced. All surrounding assets up to Powerco standard. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.00039778 | 3.024e-06 | 2016 | 2015-07-16 | C | 1 | 0.00039778 | 3.0238e-06
5794618 | 2015-07-16 10:47 | 2015-07-16 14:26 | 219.0333 | 684 | 46605 | 68.136 | 65.136 | 0.14092 | 44553 | 0.13472 | 0.0020683 | Restore Supply on Device 9 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P36733 | Repaired lines @ pole P36733 brought down by a digger on a truck. NDR 046912 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.13472 | 0.0020683 | 2016 | 2015-07-16 | C | 684 | 0.13472 | 0.0020683
6128416 | 2015-08-03 09:30 | 2015-08-03 17:28 | 478 | 61 | 29158 | 478 | 475 | 0.088167 | 28975 | 0.087613 | 0.00018445 | NAPA ID:10821 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227130 | REPLACE POLE 227130 LIVE LINE DFT 101- 40821. 13 Pukehina Parade. W/O 30007289. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.043807 | 9.2225e-05 | 2016 | 2015-08-03 | B | 61 | 0.087613 | 0.00018445
6128422 | 2015-08-03 11:15 | 2015-08-03 13:30 | 135 | 5 | 675 | 135 | 132 | 0.002041 | 660 | 0.0019957 | 1.5119e-05 | NAPA ID:10800 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1268 | Replace Transformer TC1268. Thames Coast Road, Thames. W/O 30010653. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.00099784 | 7.559e-06 | 2016 | 2015-08-03 | B | 5 | 0.0019957 | 1.5119e-05
6128428 | 2015-08-03 05:00 | 2015-08-07 05:30 | 5789.8333 | 131 | 3269.6167 | 24.9589 | 21.9589 | 0.0098865 | 2876.6167 | 0.0086982 | 0.00039611 | NAPA ID:10882 TP_WAIKINO GXP > WAIHI SUB > GILMOUR ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ground mounted switchgear 2073,2075, 2077 & 1238 - T1238 | Replace existing 11kV GEC ground mounted switchgear 2073,2075, 2077 & 1238 with new Siemens 8DJH switchgear. T1238 Kiosk in service lane off Haszard Street, Waihi. W/O 10148246. | F3 | GILMOUR ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.0043491 | 0.00019806 | 2016 | 2015-08-03 | B | 131 | 0.0086982 | 0.00039611
6128434 | 2015-08-18 09:01 | 2015-08-18 15:04 | 363 | 9 | 3267 | 363 | 360 | 0.0098786 | 3240 | 0.009797 | 2.7214e-05 | NAPA ID:11068 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 557 | Replace H/V Crossarms at Various Sites. Station Rd, Te Aroha. WO 30002440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-18 | b | 0.0048985 | 1.3607e-05 | 2016 | 2015-08-18 | B | 9 | 0.009797 | 2.7214e-05
6128436 | 2015-08-03 09:05 | 2015-08-03 17:15 | 490 | 215 | 27305 | 127 | 124 | 0.082564 | 26660 | 0.080613 | 0.00065011 | NAPA ID:10771 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-278, TD4-134, 9963/2 | Disconnect Transformer TD4-278 from TD4-134 and transfer to new Fuse/Sw 9963/2. Connect new HV cable at TD4-134 and liven two new CFC Sw/gear 9963 and 9964. Second part of job on NAPA 10772. Both sets of SCADA Tiles included. Leave Sw/gear 9964/1 OPEN & e | F3 | MAUNGATAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-08-03 | b | 0.040307 | 0.00032505 | 2016 | 2015-08-03 | B | 215 | 0.080613 | 0.00065011
6128448 | 2015-08-04 09:41 | 2015-08-04 10:36 | 54.7667 | 2 | 109.5333 | 54.7667 | 51.7667 | 0.0003312 | 103.5333 | 0.00031306 | 6.0475e-06 | NAPA ID:10128 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP384 | Install LV Frame, 160 amp disconnector, reconfigure neutrals and earths . Install covers on LV Bushings. 764 Maniatutu Road. W/O 30010396. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-04 | b | 0.00015653 | 3.024e-06 | 2016 | 2015-08-04 | B | 2 | 0.00031306 | 6.0475e-06
6128486 | 2015-08-05 09:30 | 2015-08-05 10:23 | 52.85 | 40 | 2114 | 52.85 | 49.85 | 0.0063922 | 1994 | 0.0060294 | 0.00012095 | NAPA ID:10649 TP_TE MATAI GXP > TE PUKE SUB > CENTRAL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9729/4 | Replace 11kV cross arms. Stock Road, Te Puke. W/O 30002376. | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-05 | b | 0.0030147 | 6.0475e-05 | 2016 | 2015-08-05 | B | 40 | 0.0060294 | 0.00012095
6128490 | 2015-08-05 04:30 | 2015-08-05 07:00 | 150.3 | 239 | 18123.9 | 75.8322 | 72.8322 | 0.054802 | 17406.9 | 0.052634 | 0.00072268 | NAPA ID:10650 TP_TE MATAI GXP > TE PUKE SUB > CENTRAL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-033 | Replace 11kV Cross Arms. Boucher Avenue, Te Puke. W/O 30002376. | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-05 | b | 0.026317 | 0.00036134 | 2016 | 2015-08-05 | B | 239 | 0.052634 | 0.00072268
6128501 | 2015-08-05 10:43 | 2015-08-05 13:50 | 187.2 | 7 | 1310.4 | 187.2 | 184.2 | 0.0039623 | 1289.4 | 0.0038988 | 2.1166e-05 | NAPA ID:10995 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 221289 | Replace Termination Arms on Pole 221289. 852 Rangiuru Road, Te Puke. W/O 30002275. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-05 | b | 0.0019494 | 1.0583e-05 | 2016 | 2015-08-05 | B | 7 | 0.0038988 | 2.1166e-05
6128504 | 2015-08-07 08:46 | 2015-08-07 15:20 | 394.1333 | 120 | 8809.6 | 73.4133 | 70.4133 | 0.026638 | 8449.6 | 0.02555 | 0.00036285 | NAPA ID:10651 TP_TE MATAI GXP > TE PUKE SUB > CENTRAL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-080 | Replace 11kV poles & cross arms. Work Location: King Street, Te Puke. W/O 30002376. | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.012775 | 0.00018143 | 2016 | 2015-08-07 | B | 120 | 0.02555 | 0.00036285
6128507 | 2015-08-06 09:15 | 2015-08-06 13:00 | 225 | 76 | 17100 | 225 | 222 | 0.051706 | 16872 | 0.051017 | 0.00022981 | NAPA ID:10677 TP_KOPU GXP > WHITIANGA SUB > COOK DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole W0040 | Replace pole W0040 and L.V arms at W0035. Hamilton Crescent, Whitianga. W/O 10148313. | F3 | COOK DRIVE | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-08-06 | b | 0.025508 | 0.0001149 | 2016 | 2015-08-06 | B | 76 | 0.051017 | 0.00022981
6128515 | 2015-08-07 08:35 | 2015-08-07 11:59 | 203.2667 | 34 | 6911.0667 | 203.2667 | 200.2667 | 0.020897 | 6809.0667 | 0.020589 | 0.00010281 | NAPA ID:10772 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-648 | Transferring TD4-648 onto 9964/2, then jointing the cable that use to go to TD4-648 onto 9964/3 This is part 2 of the job, installation of switch gear is on NAPA Number is 10771.Hammond Street, Tauranga. W/O 10147844. | F3 | MAUNGATAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.010294 | 5.1404e-05 | 2016 | 2015-08-07 | B | 34 | 0.020589 | 0.00010281
6128518 | 2015-08-10 08:47 | 2015-08-10 15:02 | 375 | 107 | 6580.5 | 61.5 | 58.5 | 0.019898 | 6259.5 | 0.018927 | 0.00032354 | NAPA ID:10872 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 86 | CHANGE 33kV Cross arms and poles, also need 11kV Isolated & Earthed as both are on the same pole being changed. State Highway 2, Omokoroa. Thermal Upgrade. W/O 12345678. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-10 | b | 0.0094636 | 0.00016177 | 2016 | 2015-08-10 | B | 107 | 0.018927 | 0.00032354
6128556 | 2015-08-10 10:00 | 2015-08-10 13:30 | 210 | 4 | 840 | 210 | 207 | 0.00254 | 828 | 0.0025037 | 1.2095e-05 | NAPA ID:10919 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE7-115 | To replace the 400V Termination arm and 6 cutouts on the transformer pole. 71 Pongakawa Station Road. W/O 10161617. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-10 | b | 0.0012518 | 6.048e-06 | 2016 | 2015-08-10 | B | 4 | 0.0025037 | 1.2095e-05
6128563 | 2015-08-11 09:45 | 2015-08-11 14:56 | 311.4667 | 53 | 16507.7333 | 311.4667 | 308.4667 | 0.049915 | 16348.7333 | 0.049435 | 0.00016026 | NAPA ID:10987 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-037 | Replace HV Cross arms and Poles.. Maketu, Tainui. W/O 30002362. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-11 | b | 0.024717 | 8.013e-05 | 2016 | 2015-08-11 | B | 53 | 0.049435 | 0.00016026
6128565 | 2015-08-11 08:57 | 2015-08-11 14:13 | 316 | 20 | 6320 | 316 | 313 | 0.01911 | 6260 | 0.018929 | 6.0475e-05 | NAPA ID:10797 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1614 | Replace H.V arms at T1614 and T13173. Thames Coast Road, Thames. W/O 30007302. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-11 | b | 0.0094644 | 3.0238e-05 | 2016 | 2015-08-11 | B | 20 | 0.018929 | 6.0475e-05
6128568 | 2015-08-12 09:15 | 2015-08-12 10:33 | 78.2833 | 4 | 313.1333 | 78.2833 | 75.2833 | 0.00094684 | 301.1333 | 0.00091056 | 1.2095e-05 | NAPA ID:10801 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5023 | Replace H.V crossarms at TC5023. Manaia, Coromandel. W/O 30010651. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-12 | b | 0.00045528 | 6.048e-06 | 2016 | 2015-08-12 | B | 4 | 0.00091056 | 1.2095e-05
6128571 | 2015-08-12 09:30 | 2015-08-12 15:18 | 348.4167 | 22 | 7665.1667 | 348.4167 | 345.4167 | 0.023178 | 7599.1667 | 0.022978 | 6.6523e-05 | NAPA ID:10974 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE2-021 | Replace poles and arms and reconductor 11kV Spur line. Old Kaimai Road. W/O 30002432. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-08-12 | b | 0.011489 | 3.3261e-05 | 2016 | 2015-08-12 | B | 22 | 0.022978 | 6.6523e-05
6128574 | 2015-08-12 09:01 | 2015-08-12 14:58 | 356.7667 | 176 | 62790.9333 | 356.7667 | 353.7667 | 0.18986 | 62262.9333 | 0.18827 | 0.00053218 | NAPA ID:10923 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 221756 | Replace poles, hardware and conductor. Install ABS TEMP63 on pole 221793. LL Permit to connect new conductor onto SF6-009 once AP returned to NOC. State Highway 33 Paengaroa. W/O 30008668. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-12 | b | 0.094134 | 0.00026609 | 2016 | 2015-08-12 | B | 176 | 0.18827 | 0.00053218
6128576 | 2015-08-13 21:33 | 2015-08-14 04:19 | 406.1167 | 268 | 59471.4 | 221.9082 | 218.9082 | 0.17983 | 58667.4 | 0.1774 | 0.00081037 | NAPA ID:10981 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 18TH AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP425 | Replace poles and HV arms plus reconductor feeder. Fraser Street/Oxford Street, Tauranga. W/O 30002446. | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-08-13 | b | 0.088698 | 0.00040518 | 2016 | 2015-08-13 | B | 268 | 0.1774 | 0.00081037
6128588 | 2015-08-14 11:05 | 2015-08-14 14:45 | 219.9667 | 83 | 18257.2333 | 219.9667 | 216.9667 | 0.055206 | 18008.2333 | 0.054453 | 0.00025097 | NAPA ID:10804 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T13032 | Replace pole T13032 and replace crossarms at T13082. Te Mata Creek Road, Thames. W/O 30010653. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-14 | b | 0.027226 | 0.00012549 | 2016 | 2015-08-14 | B | 83 | 0.054453 | 0.00025097
6128592 | 2015-08-17 10:02 | 2015-08-17 13:30 | 208 | 20 | 4160 | 208 | 205 | 0.012579 | 4100 | 0.012397 | 6.0475e-05 | NAPA ID:10802 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC808 | Replace Transformer TC808. Thames Coast Road, Thames. W/O 30010652. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-08-17 | b | 0.0061987 | 3.0238e-05 | 2016 | 2015-08-17 | B | 20 | 0.012397 | 6.0475e-05
6128694 | 2015-08-07 08:45 | 2015-08-07 12:55 | 250 | 2 | 500 | 250 | 247 | 0.0015119 | 494 | 0.0014937 | 6.0475e-06 | NAPA ID:11044 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11058 | Tree cutting around 11kV lines. Te Ore Ore Bideford Road, Masterton. PPPD 47427. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-07 | b | 0.00074687 | 3.024e-06 | 2016 | 2015-08-07 | B | 2 | 0.0014937 | 6.0475e-06
6128701 | 2015-08-07 09:30 | 2015-08-07 13:28 | 238 | 4 | 952 | 238 | 235 | 0.0028786 | 940 | 0.0028423 | 1.2095e-05 | NAPA ID:11040 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | T2303 | Remove vine from t2303. Bideford Road, Masterton. PPPD 47093. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-07 | b | 0.0014212 | 6.048e-06 | 2016 | 2015-08-07 | B | 4 | 0.0028423 | 1.2095e-05
6128704 | 2015-08-09 08:45 | 2015-08-09 11:03 | 138 | 29 | 4002 | 138 | 135 | 0.012101 | 3915 | 0.011838 | 8.7689e-05 | NAPA ID:11518 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | J30 | Change 4 Rotten 11kv cross arms. Lees Road, Feilding. W/O 10162062. | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-08-09 | b | 0.005919 | 4.3845e-05 | 2016 | 2015-08-09 | B | 29 | 0.011838 | 8.7689e-05
6128712 | 2015-08-10 09:05 | 2015-08-10 11:50 | 165 | 2 | 330 | 165 | 162 | 0.00099784 | 324 | 0.0009797 | 6.0475e-06 | NAPA ID:10479 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer T4/209 | Replace 11KV trani T4/209. Pohongina East Road, Pohanginga. W/O 10162062. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-10 | b | 0.00048985 | 3.024e-06 | 2016 | 2015-08-10 | B | 2 | 0.0009797 | 6.0475e-06
6128729 | 2015-08-12 09:20 | 2015-08-12 12:20 | 180 | 4 | 720 | 180 | 177 | 0.0021771 | 708 | 0.0021408 | 1.2095e-05 | NAPA ID:10484 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T4/331 | Replace 11KV Transformer T4/331. Forlongs Road, Pohongina. W/O 10162783. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-12 | b | 0.0010704 | 6.048e-06 | 2016 | 2015-08-12 | B | 4 | 0.0021408 | 1.2095e-05
6128734 | 2015-08-13 09:10 | 2015-08-13 12:15 | 185 | 3 | 555 | 185 | 182 | 0.0016782 | 546 | 0.001651 | 9.0713e-06 | NAPA ID:10486 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/102 | Replace 11KV Transformer T2/102. Water Shed Road, Pohongina. W/O 10161950. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-13 | b | 0.00082549 | 4.536e-06 | 2016 | 2015-08-13 | B | 3 | 0.001651 | 9.0713e-06
6128740 | 2015-08-14 09:00 | 2015-08-14 12:57 | 236.9167 | 6 | 1421.5 | 236.9167 | 233.9167 | 0.0042983 | 1403.5 | 0.0042438 | 1.8143e-05 | NAPA ID:07561 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 781113 | Project number IR6978 Rangikura Reconstruction, Hughes Road beyond 11kV Fuse 292 replace poles 781113 to 781130. Hughes Road, Rangikura. W/O 30001953. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-14 | b | 0.0021219 | 9.071e-06 | 2016 | 2015-08-14 | B | 6 | 0.0042438 | 1.8143e-05
6128744 | 2015-08-15 08:00 | 2015-08-15 16:05 | 485.0667 | 283 | 68780.8 | 243.0417 | 240.0417 | 0.20798 | 67931.8 | 0.20541 | 0.00085572 | NAPA ID:11020 TP_BUNNYTHORPE GXP > MILSON SUB > GEMINI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/476 | Remove Platform transformer T6/476 and install new 11m pole with new DDO Fuses. New groundmount Transformer (7317P) to be installed within the next week under separate switching. Transformers T6/459, T6/460 & T6/461 to be on Generators half an hour after | F3 | GEMINI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-08-15 | b | 0.1027 | 0.00042786 | 2016 | 2015-08-15 | B | 283 | 0.20541 | 0.00085572
6128748 | 2015-08-18 09:06 | 2015-08-18 15:32 | 386 | 8 | 3088 | 386 | 383 | 0.0093374 | 3064 | 0.0092648 | 2.419e-05 | NAPA ID:10652 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 965 | Replace poles & Hardware. Parapara Road, Parapara. W/O 30002303. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-18 | b | 0.0046324 | 1.2095e-05 | 2016 | 2015-08-18 | B | 8 | 0.0092648 | 2.419e-05
6128753 | 2015-08-19 09:16 | 2015-08-19 15:05 | 349.35 | 50 | 17467.5 | 349.35 | 346.35 | 0.052818 | 17317.5 | 0.052364 | 0.00015119 | NAPA ID:11022 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L52 | Replace 11kv Poles, cross arms and conductor between ABS L52 and M76 and install two temp ABSs' pole P21916, ABS 28. P21768, ABS 29. Mt Stewart-Halcombe Road, Fielding. W/O 30002718. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-19 | b | 0.026182 | 7.5594e-05 | 2016 | 2015-08-19 | B | 50 | 0.052364 | 0.00015119
6128755 | 2015-08-20 09:04 | 2015-08-20 15:19 | 374.4333 | 98 | 36694.4667 | 374.4333 | 371.4333 | 0.11096 | 36400.4667 | 0.11007 | 0.00029633 | NAPA ID:10653 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4045 | Replacing HV cross arms. Grey Street/Ballance Street, Raetihi. W/O 10162395. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-20 | b | 0.055033 | 0.00014816 | 2016 | 2015-08-20 | B | 98 | 0.11007 | 0.00029633
6128757 | 2015-09-23 08:30 | 2015-09-23 13:30 | 300 | 5 | 1500 | 300 | 297 | 0.0045356 | 1485 | 0.0044903 | 1.5119e-05 | NAPA ID:10992 TP_MASTERTON GXP > NORFOLK SUB > WAINGAWA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 826464 | Replace 33kv,11kv poles 826464,826463,826455 and 826454. also remove temp links 76. State Highway 2, Masterton. W/O 30000973. | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2015-09-23 | b | 0.0022451 | 7.559e-06 | 2016 | 2015-09-23 | B | 5 | 0.0044903 | 1.5119e-05
6128760 | 2015-08-24 09:00 | 2015-08-24 15:10 | 370 | 12 | 4440 | 370 | 367 | 0.013425 | 4404 | 0.013317 | 3.6285e-05 | NAPA ID:07562 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 772974 | Project number IR6978 Rangikura Reconstruction, Medlicott Road replace 772974 to 772955 beyond 11kv fuses 070. Medlicott Road, Rangikura. W/O 30001953. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-24 | b | 0.0066583 | 1.8143e-05 | 2016 | 2015-08-24 | B | 12 | 0.013317 | 3.6285e-05
6128849 | 2015-08-07 09:32 | 2015-08-07 13:20 | 228.1333 | 12 | 2737.6 | 228.1333 | 225.1333 | 0.0082778 | 2701.6 | 0.008169 | 3.6285e-05 | NAPA ID:10749 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1255 | Replace H/V Crossarms at Various Sites. Hanga Road, Te Poi. W/O 30003315. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.0040845 | 1.8143e-05 | 2016 | 2015-08-07 | B | 12 | 0.008169 | 3.6285e-05
6128862 | 2015-08-07 10:00 | 2015-08-07 13:15 | 194.5 | 44 | 8558 | 194.5 | 191.5 | 0.025877 | 8426 | 0.025478 | 0.00013305 | NAPA ID:09923 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 3 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 743566 | Replace cross arms and DDOs on 743566. Paraite Road, Bell Block. W/O 10163078. | F1 | BELL BLOCK 3 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-08-07 | b | 0.012739 | 6.6523e-05 | 2016 | 2015-08-07 | B | 44 | 0.025478 | 0.00013305
6128874 | 2015-08-07 09:15 | 2015-08-07 10:30 | 75 | 2 | 150 | 75 | 72 | 0.00045356 | 144 | 0.00043542 | 6.0475e-06 | NAPA ID:10608 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4495 | Isolate transformer TC 4495 to carry out LV work on transformer pole and LV service main pole. 262 Taotaoroa Road, Karapiro, Matamata. W/O 30010937. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.00021771 | 3.024e-06 | 2016 | 2015-08-07 | B | 2 | 0.00043542 | 6.0475e-06
6128884 | 2015-08-07 09:45 | 2015-08-07 14:16 | 270.8333 | 29 | 7854.1667 | 270.8333 | 267.8333 | 0.023749 | 7767.1667 | 0.023486 | 8.7689e-05 | NAPA ID:09891 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1085 | To replace 11kV cross arms and hardware between ABS IC1085 and 1356. Hopkins Road, Matamata. W/O 30002943. | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.011743 | 4.3845e-05 | 2016 | 2015-08-07 | B | 29 | 0.023486 | 8.7689e-05
6128903 | 2015-08-07 09:53 | 2015-08-07 13:50 | 237.0167 | 3 | 711.05 | 237.0167 | 234.0167 | 0.00215 | 702.05 | 0.0021228 | 9.0713e-06 | NAPA ID:10695 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3415 | To replace the 11kV Fuse arm & Fuses. Plus install a 400V fuse unit on the Transformer LV. Walton Road, Morrinsville. W/O 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-07 | b | 0.0010614 | 4.536e-06 | 2016 | 2015-08-07 | B | 3 | 0.0021228 | 9.0713e-06
6128923 | 2015-08-12 09:30 | 2015-08-12 13:25 | 235 | 75 | 17625 | 235 | 232 | 0.053294 | 17400 | 0.052613 | 0.00022678 | NAPA ID:10799 TP_CARRINGTON GXP > OAKURA SUB > INLAND COAST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 414 | We are replacing all strain insulators on both sides of ABS 414 and replacing double arms and 11kv fuses 8410. 325 Upper Pitone Road, Okato. W/O 10162044. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-08-12 | b | 0.026307 | 0.00011339 | 2016 | 2015-08-12 | B | 75 | 0.052613 | 0.00022678
6128938 | 2015-08-14 08:46 | 2015-08-14 14:01 | 315.1 | 19 | 5986.9 | 315.1 | 312.1 | 0.018103 | 5929.9 | 0.017931 | 5.7451e-05 | NAPA ID:11067 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 550 | Replace H/V Crossarms at Various Sites. Rawhiti Road, Te Aroha. W/O 30002440. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-14 | b | 0.0089653 | 2.8726e-05 | 2016 | 2015-08-14 | B | 19 | 0.017931 | 5.7451e-05
6128941 | 2015-08-13 13:30 | 2015-08-13 14:20 | 50 | 7 | 350 | 50 | 47 | 0.0010583 | 329 | 0.00099482 | 2.1166e-05 | NAPA ID:10694 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses TC278 | To install 400V fuses on the transformer LV. Taharoa Road, Kiwitahi. W/O 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-13 | b | 0.00049741 | 1.0583e-05 | 2016 | 2015-08-13 | B | 7 | 0.00099482 | 2.1166e-05
6128944 | 2015-08-17 12:00 | 2015-08-17 12:30 | 30 | 5 | 150 | 30 | 27 | 0.00045356 | 135 | 0.00040821 | 1.5119e-05 | NAPA ID:10949 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3918 | To install 400V Fuse/Disconnector. 3172 State Highway 26, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-17 | b | 0.0002041 | 7.559e-06 | 2016 | 2015-08-17 | B | 5 | 0.00040821 | 1.5119e-05
6128947 | 2015-08-17 10:00 | 2015-08-17 10:30 | 30 | 7 | 210 | 30 | 27 | 0.00063499 | 189 | 0.00057149 | 2.1166e-05 | NAPA ID:10948 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3420 | To install 400V 3 phase Fuse/Diconector. 8 Murray Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-17 | b | 0.00028575 | 1.0583e-05 | 2016 | 2015-08-17 | B | 7 | 0.00057149 | 2.1166e-05
6128950 | 2015-08-17 14:00 | 2015-08-17 14:37 | 37 | 4 | 148 | 37 | 34 | 0.00044752 | 136 | 0.00041123 | 1.2095e-05 | NAPA ID:10950 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5039 | Install a 400V Fuse/Disconector. 11 Brown Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-17 | b | 0.00020562 | 6.048e-06 | 2016 | 2015-08-17 | B | 4 | 0.00041123 | 1.2095e-05
6129002 | 2015-08-26 08:53 | 2015-08-26 13:42 | 289.4333 | 13 | 3762.6333 | 289.4333 | 286.4333 | 0.011377 | 3723.6333 | 0.011259 | 3.9309e-05 | NAPA ID:11070 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC865 | Replace H/V Crossarms at Various Sites. Rawhiti Road, Te Aroha. W/O 30002440. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-26 | b | 0.0056297 | 1.9654e-05 | 2016 | 2015-08-26 | B | 13 | 0.011259 | 3.9309e-05
6130219 | 2015-08-06 09:01 | 2015-08-06 14:16 | 315.0333 | 12 | 3780.4 | 315.0333 | 312.0333 | 0.011431 | 3744.4 | 0.011322 | 3.6285e-05 | NAPA ID:10589 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE6 121 | Replace poles, hardware and conductor.. LL Permit to connect new conductor onto IP125 once AP returned to NOC. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-06 | b | 0.0056611 | 1.8143e-05 | 2016 | 2015-08-06 | B | 12 | 0.011322 | 3.6285e-05
6130221 | 2015-08-04 09:08 | 2015-08-04 15:16 | 368.3667 | 17 | 6262.2333 | 368.3667 | 365.3667 | 0.018935 | 6211.2333 | 0.018781 | 5.1404e-05 | NAPA ID:10587 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace poles, hardware and conductor. State Highway 33, Paengaroa. Work Order 30008668 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-04 | b | 0.0093906 | 2.5702e-05 | 2016 | 2015-08-04 | B | 17 | 0.018781 | 5.1404e-05
6130262 | 2015-08-03 12:30 | 2015-08-03 14:16 | 106.0833 | 30 | 3182.5 | 106.0833 | 103.0833 | 0.0096231 | 3092.5 | 0.009351 | 9.0713e-05 | NAPA ID:11480 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 268 | Replace 11kV Broken pole. Works location: Matahiwi River Rd. WO 30012313. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-03 | b | 0.0046755 | 4.5356e-05 | 2016 | 2015-08-03 | B | 30 | 0.009351 | 9.0713e-05
6131763 | 2015-08-18 09:00 | 2015-08-18 14:24 | 324 | 50 | 16200 | 324 | 321 | 0.048985 | 16050 | 0.048531 | 0.00015119 | NAPA ID:10924 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP125 | Replace poles, hardware and conductor. LL Permit to connect new conductor onto TEMP63 once AP returned to NOC. Works location: Highway 33 Paengaroa. WO 30008668 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-18 | b | 0.024266 | 7.5594e-05 | 2016 | 2015-08-18 | B | 50 | 0.048531 | 0.00015119
6131873 | 2015-08-01 09:01 | 2015-08-01 14:21 | 319.8 | 101 | 32299.8 | 319.8 | 316.8 | 0.097667 | 31996.8 | 0.096751 | 0.0003054 | NAPA ID:09295 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | To replace 11kV and LV cross arms on Smith Street, Matamata. Work Order 30002943. | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-08-01 | b | 0.048375 | 0.0001527 | 2016 | 2015-08-01 | B | 101 | 0.096751 | 0.0003054
6132092 | 2015-07-30 17:19 | 2015-07-30 19:00 | 101.25 | 230 | 17864.5 | 77.6717 | 74.6717 | 0.054018 | 17174.5 | 0.051932 | 0.00069546 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M0484 | at 17:18, Putaruru Sub, CB 6 Horahora Feeder, Recloser 9636 Tripped, No Flags, L/O. Faultmen dispatched and investigation began. Feeder sectionalised. Fire Service called in to report Car vs Pole near 1270 Lake Arapuni Rd. Found car had hit pole at Pole | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-30 | c | 0.051932 | 0.00069547 | 2016 | 2015-07-30 | C | 230 | 0.051932 | 0.00069546
6133387 | 2015-07-30 20:14 | 2015-07-30 22:08 | 114.1833 | 35 | 3996.4167 | 114.1833 | 111.1833 | 0.012084 | 3891.4167 | 0.011767 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5214 | 2 HT fuses found tripped at 5214. Patrol carried out, reloaded OK. Cause unknown. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-30 | c | 0.011767 | 0.00010583 | 2016 | 2015-07-30 | C | 35 | 0.011767 | 0.00010583
6365322 | 2015-07-31 08:06 | 2015-07-31 11:45 | 218.8667 | 441 | 23043.6 | 52.2531 | 49.2531 | 0.069678 | 21720.6 | 0.065678 | 0.0013335 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 9275 | Recloser 9275 tripped on E/F. Line sectionalised and patrolled but no fault found. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-07-31 | c | 0.065678 | 0.0013335 | 2016 | 2015-07-31 | C | 441 | 0.065678 | 0.0013335
6397851 | 2015-08-18 09:10 | 2015-08-18 13:11 | 241 | 69 | 16629 | 241 | 238 | 0.050282 | 16422 | 0.049656 | 0.00020864 | NAPA ID:10886 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2622 | Replace section fuses FP1104 with ABS IP622. Works location: Totmans Rd, Hinuera. WO 30003457 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-08-18 | b | 0.024828 | 0.00010432 | 2016 | 2015-08-18 | B | 69 | 0.049656 | 0.00020864
6398212 | 2015-08-20 09:15 | 2015-08-20 14:01 | 286.2667 | 53 | 15137 | 285.6038 | 282.6038 | 0.045771 | 14978 | 0.04529 | 0.00016026 | NAPA ID:10892 TP_HINUERA GXP > LAKE ROAD SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | Connect 11kV link between CB 1 & CB 5. Works location: Totmans Rd, Hinuera. WO 30003457 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-08-20 | b | 0.022645 | 8.013e-05 | 2016 | 2015-08-20 | B | 53 | 0.04529 | 0.00016026
6398360 | 2015-08-29 09:20 | 2015-08-29 15:39 | 378.3333 | 59 | 22321.6667 | 378.3333 | 375.3333 | 0.067495 | 22144.6667 | 0.06696 | 0.0001784 | NAPA ID:11605 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS Q8 | To replace 11kv poles and install new 200kv overhead transformer. Works location: Albert St. WO: 10147560 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-29 | b | 0.03348 | 8.9201e-05 | 2016 | 2015-08-29 | B | 59 | 0.06696 | 0.0001784
6398434 | 2015-08-18 07:08 | 2015-08-18 07:25 | 17.1333 | 18 | 308.4 | 17.1333 | 14.1333 | 0.00093253 | 254.4 | 0.00076924 | 5.4428e-05 | NAPA ID:10511 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 13TH AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TK5-0158 | 1. Install generators at TP301 & T4663 2. Spike & cut from SK5-068 & SK5-070 joint to new cable from new CFCF 9959-1&3 3. Remove old Magnefix switchgear SK5-068/069/070 4. Cut cable to TP301 joint to new cable from CFCF 9959-4 5. Test cables 6. Liven new | F3 | 13TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-08-18 | b | 0.00038462 | 2.7214e-05 | 2016 | 2015-08-18 | B | 18 | 0.00076924 | 5.4428e-05
6535787 | 2015-08-19 10:05 | 2015-08-19 10:37 | 32 | 6 | 192 | 32 | 29 | 0.00058056 | 174 | 0.00052613 | 1.8143e-05 | NAPA ID:10952 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2050 | Install a 400V Fuse/Disconector. WOrks location: 105 Brown Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-19 | b | 0.00026307 | 9.071e-06 | 2016 | 2015-08-19 | B | 6 | 0.00052613 | 1.8143e-05
6535901 | 2015-08-19 12:00 | 2015-08-19 12:27 | 27 | 3 | 81 | 27 | 24 | 0.00024492 | 72 | 0.00021771 | 9.0713e-06 | NAPA ID:10954 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3692 | To install a 400V Fuse/Disconector. Works location: 3258 Hwy 26, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-19 | b | 0.00010886 | 4.536e-06 | 2016 | 2015-08-19 | B | 3 | 0.00021771 | 9.0713e-06
6535946 | 2015-08-19 14:00 | 2015-08-19 14:17 | 17 | 9 | 153 | 17 | 14 | 0.00046264 | 126 | 0.00038099 | 2.7214e-05 | NAPA ID:10962 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1805 | To install a 400V Fuse/Disconnector. Works location: 124 Horrels Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-19 | b | 0.0001905 | 1.3607e-05 | 2016 | 2015-08-19 | B | 9 | 0.00038099 | 2.7214e-05
6536851 | 2015-08-25 09:06 | 2015-08-25 13:27 | 261 | 23 | 6003 | 261 | 258 | 0.018152 | 5934 | 0.017943 | 6.9546e-05 | NAPA ID:07564 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 070 | Project number IR6978 Rangikura Reconstruction. Work Location: Medlicott Road. Replace poles 772974 to 772955 beyond 11kV Fuses 070. WO 30001953. | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-25 | b | 0.0089715 | 3.4773e-05 | 2016 | 2015-08-25 | B | 23 | 0.017943 | 6.9546e-05
6540840 | 2015-07-31 14:36 | 2015-07-31 16:34 | 118.55 | 414 | 23497.4333 | 56.7571 | 53.7571 | 0.071051 | 22255.4333 | 0.067295 | 0.0012518 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E0261 | CB 3 tripped on CPL E/F. NOC disable AR after 5 fails as faultman not familiar with equipment. Patrol found loose M16 nuts at Pole E0261. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-07-31 | c | 0.067295 | 0.0012518 | 2016 | 2015-07-31 | C | 414 | 0.067295 | 0.0012518
6541258 | 2015-08-25 08:30 | 2015-08-25 15:35 | 425 | 19 | 8075 | 425 | 422 | 0.024417 | 8018 | 0.024245 | 5.7451e-05 | NAPA ID:10666 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 2621 | isolation of 11kV line for tree cutting. Works location: Turakina Valley Rd, Taihape. PPPD 53596 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-25 | b | 0.012122 | 2.8726e-05 | 2016 | 2015-08-25 | B | 19 | 0.024245 | 5.7451e-05
6542471 | 2015-07-31 11:51 | 2015-07-31 13:25 | 94.35 | 19 | 1792.65 | 94.35 | 91.35 | 0.0054205 | 1735.65 | 0.0052482 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 364742 |  | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-31 | c | 0.0052482 | 5.7451e-05 | 2016 | 2015-07-31 | C | 19 | 0.0052482 | 5.7451e-05
6542724 | 2015-07-31 21:04 | 2015-07-31 22:20 | 75.4333 | 66 | 4978.6 | 75.4333 | 72.4333 | 0.015054 | 4780.6 | 0.014455 | 0.00019957 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 797683 | Aprox 2539 LAKE FERRY ROAD, Pirinoa. Car vs Pole - pole # 797683. Pole damaged, required changing (No trippings). Isolation between ABS S553 and S529 with backfeed at ABS S576. Pole changed along with crossarm and associated hardware. Relivened OK. NDR | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-07-31 | c | 0.014455 | 0.00019957 | 2016 | 2015-07-31 | C | 66 | 0.014455 | 0.00019957
6542749 | 2015-07-31 18:23 | 2015-07-31 19:19 | 56.15 | 2 | 112.3 | 56.15 | 53.15 | 0.00033957 | 106.3 | 0.00032143 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2793 | 7607 VALLEY ROAD - RAETIHI - advised Shanon. Bad LV Connection repaired at back of Transformer. Relivened OK. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-31 | c | 0.00032143 | 6.048e-06 | 2016 | 2015-07-31 | C | 2 | 0.00032143 | 6.0475e-06
6621791 | 2015-07-31 23:19 | 2015-07-31 23:41 | 21.2167 | 608 | 6301.35 | 10.3641 | 7.3641 | 0.019054 | 4477.35 | 0.013538 | 0.0018384 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9560 | CB2 tripped - unknown cause. Closed in OK. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-31 | c | 0.013538 | 0.0018384 | 2016 | 2015-07-31 | C | 608 | 0.013538 | 0.0018384
6622525 | 2015-08-01 06:29 | 2015-08-01 10:33 | 244.75 | 255 | 49352.55 | 193.5394 | 190.5394 | 0.14923 | 48587.55 | 0.14692 | 0.00077106 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 221794 | Line Down at Pole 221794. Broken at joint. HV has clashed with LV some inspections are required. Properties that were effected were inspected & livened by inspector. Isolation at Links IP125 ABS SE6-042, ABS SF6-009. Back feed from Pongakawa CB 4 via ABS | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-01 | c | 0.14692 | 0.00077106 | 2016 | 2015-08-01 | C | 255 | 0.14692 | 0.00077106
6624011 | 2015-08-01 08:26 | 2015-08-01 11:40 | 194.7833 | 1 | 194.7833 | 194.7833 | 191.7833 | 0.00058898 | 191.7833 | 0.00057991 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1338 | Replace Blown Transformer X1338. 3 Phase, 15 kVA Transformer & 4x 2Amp HV Links. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-08-01 | c | 0.00057991 | 3.024e-06 | 2016 | 2015-08-01 | C | 1 | 0.00057991 | 3.0238e-06
6624283 | 2015-08-01 10:00 | 2015-08-01 11:36 | 96 | 13 | 1248 | 96 | 93 | 0.0037737 | 1209 | 0.0036557 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P16662 | Andrew Tahura noticed this Larch pole was burnt and on closer investigation, also rotten. Decision made to change it with agreement of Network Co-ordinator. Replaced Pole with 11mtr Busck pole, 2.7 metre arm, 3x Clamptop insulators, & associated hardware | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-01 | c | 0.0036557 | 3.9309e-05 | 2016 | 2015-08-01 | C | 13 | 0.0036557 | 3.9309e-05
6624346 | 2015-08-01 10:24 | 2015-08-01 14:10 | 225.95 | 1 | 225.95 | 225.95 | 222.95 | 0.00068322 | 222.95 | 0.00067415 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1741 | 15kVA 11kV Single Phase Transformer needs replacing. Own Isolation & AP. Transformer changed & Tested Voltages. Reset flags at CB 2 Omokoroa. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-08-01 | c | 0.00067415 | 3.024e-06 | 2016 | 2015-08-01 | C | 1 | 0.00067415 | 3.0238e-06
6625916 | 2015-08-01 17:24 | 2015-08-01 18:55 | 91 | 45 | 4095 | 91 | 88 | 0.012382 | 3960 | 0.011974 | 0.00013607 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V43 | Faultman found blown fuses at Fuses V43. 2 X 10 amp HV fuses replaced. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-08-01 | c | 0.011974 | 0.00013607 | 2016 | 2015-08-01 | C | 45 | 0.011974 | 0.00013607
6626138 | 2015-08-01 21:07 | 2015-08-02 14:02 | 1014.55 | 165 | 89683.5667 | 543.5368 | 540.5368 | 0.27118 | 89188.5667 | 0.26968 | 0.00049892 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708493 | Recloser 4897 tripped on B phase E/F flags, line was patrolled and sectionalised, the faultman cannot see the line between ABS 6494 and Recloser 4915 where we suspect fault is. Faultman will return in morning.Line sectionalised and patrolled found broken | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-01 | c | 0.26968 | 0.00049892 | 2016 | 2015-08-01 | C | 165 | 0.26968 | 0.00049892
6627882 | 2015-08-02 14:45 | 2015-08-02 15:50 | 65.4333 | 1 | 65.4333 | 65.4333 | 62.4333 | 0.00019785 | 62.4333 | 0.00018878 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5433E | Replaced 30kvA transformer 5433E | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-02 | c | 0.00018878 | 3.024e-06 | 2016 | 2015-08-02 | C | 1 | 0.00018878 | 3.0238e-06
6628719 | 2015-08-03 01:02 | 2015-08-03 14:59 | 837 | 147 | 17211 | 117.0816 | 114.0816 | 0.052042 | 16770 | 0.050708 | 0.00044449 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 339583 | CB 6 tripped on A, B & C phase O/C, Matapihi 33kV CB 3042 on A, B & C phase O/C, Triton CB 72 on E/F & O/C BF flags & CB 37, Fire Services report of Car vs Pole on Matapihi Rd, Fire Comms no: F1892373. 10.02am Tallia called to advise that Paul & Dennis h | F2/F3 | AERODROME | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-08-03 | c | 0.050708 | 0.00044449 | 2016 | 2015-08-03 | C | 147 | 0.050708 | 0.00044449
6629811 | 2015-08-03 06:38 | 2015-08-03 09:03 | 144.8167 | 404 | 19974.0333 | 49.4407 | 46.4407 | 0.060397 | 18762.0333 | 0.056732 | 0.0012216 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | na | WLN CB3 tripped E/F, L/O Feeder sectionalised with Recloser RC26 opened & back feed placed via Sectionaliser 9720. Rest of feeder sectionalised with no fault found. Possum guards missing Lansdown Rd. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-08-03 | c | 0.056732 | 0.0012216 | 2016 | 2015-08-03 | C | 404 | 0.056732 | 0.0012216
6639179 | 2015-08-20 09:46 | 2015-08-20 14:19 | 272.8167 | 241 | 27947.2167 | 115.9636 | 112.9636 | 0.084506 | 27224.2167 | 0.08232 | 0.00072873 | NAPA ID:11206 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 432 | Cut line break. Reconductor between ABS 432 and line break at pole 749533. Also replace low voltage poles 749614, 749612 feed from transformer 1111. Close line break at completion of work. Works location: Barriball St, Newton St. WO 30002060 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-08-20 | b | 0.04116 | 0.00036436 | 2016 | 2015-08-20 | B | 241 | 0.08232 | 0.00072873
6639616 | 2015-08-03 14:59 | 2015-08-03 17:27 | 148 | 1 | 148 | 148 | 145 | 0.00044752 | 145 | 0.00043845 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X512 | Broken HV jumper - unable to repair so have to replace HV Transformer. Off at 14:59 On at 17:27. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-08-03 | c | 0.00043844 | 3.024e-06 | 2016 | 2015-08-03 | C | 1 | 0.00043845 | 3.0238e-06
6639820 | 2015-08-03 12:50 | 2015-08-04 14:59 | 1568.6333 | 1 | 1568.6333 | 1568.6333 | 1565.6333 | 0.0047432 | 1565.6333 | 0.0047341 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses 7597 | 2R requested as 11kv UG cable fault onsite, cable faulters required. 21:38 03/08 - FM called to be taken offsite - Located cable fault and will be returning tomorrow to repair - CR requested for 04/08. | F2 | WYNDHAM ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-08-03 | c | 0.0047341 | 3.024e-06 | 2016 | 2015-08-03 | C | 1 | 0.0047341 | 3.0238e-06
6640681 | 2015-08-19 08:50 | 2015-08-19 13:10 | 260.0167 | 22 | 5720.3667 | 260.0167 | 257.0167 | 0.017297 | 5654.3667 | 0.017097 | 6.6523e-05 | NAPA ID:10977 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE2-021 | Replace poles and cross arms and reconductor 11kV Spur Line. Works location: Old Kaimai Rd. WO 30002432 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-08-19 | b | 0.0085487 | 3.3261e-05 | 2016 | 2015-08-19 | B | 22 | 0.017097 | 6.6523e-05
6640970 | 2015-08-03 15:49 | 2015-08-03 18:26 | 157.5167 | 1 | 157.5167 | 157.5167 | 154.5167 | 0.00047629 | 154.5167 | 0.00046722 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1452 | Replaced x 2 6amp DDO Fuses (2 from 3) and replaced the candle as well. Cause - unknown (possible bird strike - ducks). No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok. Full Power Restored. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-08-03 | c | 0.00046722 | 3.024e-06 | 2016 | 2015-08-03 | C | 1 | 0.00046722 | 3.0238e-06
6641292 | 2015-08-03 16:18 | 2015-08-03 20:50 | 272 | 26 | 7072 | 272 | 269 | 0.021384 | 6994 | 0.021148 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11390 | Found floating conductor @ pole P11390. Repaired and replaced 2X 10a Fuses @ S11. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-08-03 | c | 0.021148 | 7.8618e-05 | 2016 | 2015-08-03 | C | 26 | 0.021148 | 7.8618e-05
6641329 | 2015-08-03 16:10 | 2015-08-03 16:31 | 20.9333 | 6 | 125.6 | 20.9333 | 17.9333 | 0.00037978 | 107.6 | 0.00032536 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9612/2 | Found Fuse switch 9612/2 tripped. Isolated between SD4-026 & 9827/3. Replaced 2 x 16 amp Fuses. Relivened. | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-08-03 | c | 0.00032536 | 1.8143e-05 | 2016 | 2015-08-03 | C | 6 | 0.00032536 | 1.8143e-05
6642517 | 2015-08-03 03:58 | 2015-08-04 04:54 | 1495.6333 | 427 | 46356.2667 | 108.5627 | 105.5627 | 0.14017 | 45075.2667 | 0.1363 | 0.0012911 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4 | Castlecliff CB4 tripped A & B Phase O/C. Line patrolled with nothing obvious found & supply restored. | F2 | POLSON ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-08-03 | c | 0.1363 | 0.0012911 | 2016 | 2015-08-03 | C | 427 | 0.1363 | 0.0012911
6643045 | 2015-08-04 06:09 | 2015-08-04 09:20 | 191 | 1277 | 185014 | 144.8818 | 141.8818 | 0.55944 | 181183 | 0.54785 | 0.0038613 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 737272 | 33kV CB 2862 tripped E/F, O/C inverse time, locked out. Loss of Kaponga and Cardiff Substations at 06:08. Sub's offloaded, via SCADA, Kaponga relivened at 08:02. Delays in relivening: 1. Busy in NOC with large shut for Piako, Morrinsville on 8972, this wa | F1,F2,F3 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2015-08-04 | c | 0.54785 | 0.0038613 | 2016 | 2015-08-04 | C | 1277 | 0.54785 | 0.0038613
6644347 | 2015-08-03 08:00 | 2015-08-03 09:30 | 90 | 52 | 4680 | 90 | 87 | 0.014151 | 4524 | 0.013679 | 0.00015724 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761308 | York Road (Halfway between Derby Road and the top of York Road). Driving up York Road its on the right hand side. Please call customer if any issues. 4 m conductor, 2 sleeves. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-03 | c | 0.013679 | 0.00015724 | 2016 | 2015-08-03 | C | 52 | 0.013679 | 0.00015724
6644391 | 2015-08-04 07:30 | 2015-08-04 07:56 | 26 | 36 | 936 | 26 | 23 | 0.0028302 | 828 | 0.0025037 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | A48 | Big bang came from P40979 - found a dead bird. Taken to control. Replaced 2x 15a HV fuses at A48, OH due to bird strike. Worked through control. Nothing else repaired or replaced, adjacent assets up to Powerco standard. | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.0025037 | 0.00010886 | 2016 | 2015-08-04 | C | 36 | 0.0025037 | 0.00010886
6644468 | 2015-08-04 07:29 | 2015-08-04 12:52 | 322.5167 | 1 | 322.5167 | 322.5167 | 319.5167 | 0.00097521 | 319.5167 | 0.00096614 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 29032 | replaced 2x 3a hv fuse links, OH due trees, worked through to control. nothing else repaired or replaced, adjacent assets up to powerco standard. | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.00096614 | 3.024e-06 | 2016 | 2015-08-04 | C | 1 | 0.00096614 | 3.0238e-06
6645023 | 2015-08-04 09:06 | 2015-08-04 12:30 | 204.4 | 190 | 27854.8333 | 146.6044 | 143.6044 | 0.084226 | 27284.8333 | 0.082503 | 0.00057451 |  | 6.6 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 758929 | Lines down HV - due to wind. Tony called to close off job - spoke to control - said ok to complete job, however unable to. Completed FM from site MOK CB H11 tripped (no flags) report of lines x 1 down at pole 758929. (High wind & rain). Isolations betwee | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.082503 | 0.00057452 | 2016 | 2015-08-04 | C | 190 | 0.082503 | 0.00057451
6646480 | 2015-08-11 09:07 | 2015-08-11 15:58 | 410.8333 | 127 | 22230.3333 | 175.042 | 172.042 | 0.067219 | 21849.3333 | 0.066067 | 0.00038402 | NAPA ID:11545 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/281 | Replace Transformer T3/133 with new city pad. Terminate new 11kV cable onto transformer after 11kV cable fault DNO 150718 return feeder to normal. Works location: 201 Kimbolton Rd, Feilding. WO 30002202 | F3 | RESIDENTIAL | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-08-11 | b | 0.033034 | 0.00019201 | 2016 | 2015-08-11 | B | 127 | 0.066067 | 0.00038402
6646997 | 2015-08-04 10:32 | 2015-08-04 12:42 | 130 | 430 | 36608 | 85.1349 | 82.1349 | 0.11069 | 35318 | 0.10679 | 0.0013002 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11003 | Mangamutu CB6 tripped A & B Phase - Ground Fault. Line patrolled and faultman located conductor down at pole P11003.Rehang 50m of 16mm Conductor. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.10679 | 0.0013002 | 2016 | 2015-08-04 | C | 430 | 0.10679 | 0.0013002
6649408 | 2015-08-04 11:13 | 2015-08-04 12:56 | 103.05 | 85 | 4178.85 | 49.1629 | 46.1629 | 0.012636 | 3923.85 | 0.011865 | 0.00025702 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C630 | Tuhitarata C630 tripped. Unknown cause. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.011865 | 0.00025702 | 2016 | 2015-08-04 | C | 85 | 0.011865 | 0.00025702
6651338 | 2015-08-21 10:50 | 2015-08-21 11:08 | 18 | 4 | 72 | 18 | 15 | 0.00021771 | 60 | 0.00018143 | 1.2095e-05 | NAPA ID:10964 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2250 | To install a 400V Fuse/Disconnector. 222 Horrell Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 9.0713e-05 | 6.048e-06 | 2016 | 2015-08-21 | B | 4 | 0.00018143 | 1.2095e-05
6651342 | 2015-08-04 13:31 | 2015-08-04 17:36 | 244.6 | 44 | 3650.4 | 82.9636 | 79.9636 | 0.011038 | 3518.4 | 0.010639 | 0.00013305 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709424 | DUG D21 Emergency switching to check/repair fuses 5514. Isolation required at links 6290 (no back feeds). Jumper x 1 repaired at fuses 5514 with all service restored. Materials Nil. | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.010639 | 0.00013305 | 2016 | 2015-08-04 | C | 44 | 0.010639 | 0.00013305
6651354 | 2015-08-04 14:40 | 2015-08-04 15:27 | 47 | 1 | 47 | 47 | 44 | 0.00014212 | 44 | 0.00013305 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 355746 | ADVISED SHANNON AT HUB. Re bolted Crossarm to Pole 355746. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.00013305 | 3.024e-06 | 2016 | 2015-08-04 | C | 1 | 0.00013305 | 3.0238e-06
6651414 | 2015-08-04 16:28 | 2015-08-04 17:17 | 49 | 95 | 4655 | 49 | 46 | 0.014076 | 4370 | 0.013214 | 0.00028726 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5248 | at 1628, Thames Sub, CB 3 Queen St Feeder. Found 2x burnt up LV fuses & holders at Transformer TC5248. Isolation using the T-Blade Switch at TC5248 was required to repair LV Fuses. TC5248 OFF at 16:28, ON at 17:17. All Power Restored on Completion. Stu Si | F2/F3 | QUEEN ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-08-04 | c | 0.013214 | 0.00028726 | 2016 | 2015-08-04 | C | 95 | 0.013214 | 0.00028726
6651423 | 2015-08-21 14:25 | 2015-08-21 14:40 | 15 | 4 | 60 | 15 | 12 | 0.00018143 | 48 | 0.00014514 | 1.2095e-05 | NAPA ID:10966 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC 3642 | To install a 400V fuse/disconnector. 19 Newman Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 7.257e-05 | 6.048e-06 | 2016 | 2015-08-21 | B | 4 | 0.00014514 | 1.2095e-05
6651443 | 2015-08-21 12:38 | 2015-08-21 13:00 | 22 | 3 | 66 | 22 | 19 | 0.00019957 | 57 | 0.00017235 | 9.0713e-06 | NAPA ID:10965 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4154 | To install a 400V fuse/disconnector. 369 Horrells Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 8.6177e-05 | 4.536e-06 | 2016 | 2015-08-21 | B | 3 | 0.00017235 | 9.0713e-06
6651480 | 2015-08-21 09:03 | 2015-08-21 16:16 | 432.5 | 71 | 30164.75 | 424.8556 | 421.8556 | 0.091211 | 29951.75 | 0.090567 | 0.00021469 | NAPA ID:10902 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-043 | Replace 11kV Poles and Crossarms at Various Sites. Works location: Morton Rd/Prestidge Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 0.045283 | 0.00010734 | 2016 | 2015-08-21 | B | 71 | 0.090567 | 0.00021469
6651535 | 2015-08-25 09:00 | 2015-08-25 15:37 | 396.9 | 106 | 42071.4 | 396.9 | 393.9 | 0.12721 | 41753.4 | 0.12625 | 0.00032052 | NAPA ID:10909 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-012 | Replace 11kV Poles and Crossarms at Various Sites. Works location: Work Rd, Aongatete. WO 30003302. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-25 | b | 0.063126 | 0.00016026 | 2016 | 2015-08-25 | B | 106 | 0.12625 | 0.00032052
6654037 | 2015-08-04 19:30 | 2015-08-05 00:28 | 297.9333 | 404 | 12516.3167 | 30.981 | 27.981 | 0.037846 | 11304.3167 | 0.034182 | 0.0012216 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H1657 | Walton CB 3 L/O on E/F. Reported pole on fire. Checked & found strain insulator faulty. Isolated between ABS IC508 & links IP177. Replaced & relivened. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-08-04 | c | 0.034182 | 0.0012216 | 2016 | 2015-08-04 | C | 404 | 0.034182 | 0.0012216
6655018 | 2015-08-04 20:20 | 2015-08-05 14:24 | 1083.95 | 78 | 10757.85 | 137.9212 | 134.9212 | 0.032529 | 10523.85 | 0.031822 | 0.00023585 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 838173 | Line sectionalised and patrolled. Fault appears to be beyond fuses 7139 and isolated to be further investigated in daylight. Line down at Pole 838173 through scrub. Crew returned 05/08/15 found this and repaired. Materials used: 4mtrs of Ali conductor, 2 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-08-04 | c | 0.031822 | 0.00023585 | 2016 | 2015-08-04 | C | 78 | 0.031822 | 0.00023585
6656761 | 2015-08-05 07:41 | 2015-08-05 08:33 | 51.95 | 2 | 22.5667 | 11.2833 | 8.2833 | 6.8236e-05 | 16.5667 | 5.0094e-05 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Kaponga Sub | 33kV CB 2782 tripped L/O E/F O/C. No Loss of Supply due to back fed via ELT Sub. 11kV back livening (Protection issue). NOC Requested Transpower close CB 2782, successfully done. NOC requested an urgent line patrol of the 33kV line. Downers promptly on th | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-05 | c | 5.0094e-05 | 6.048e-06 | 2016 | 2015-08-05 | C | 2 | 5.0094e-05 | 6.0475e-06
6656833 | 2015-08-05 08:08 | 2015-08-05 08:27 | 19 | 3 | 57 | 19 | 16 | 0.00017235 | 48 | 0.00014514 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7714 | Fuses 7717 - 2 x 10 amp. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-08-05 | c | 0.00014514 | 9.071e-06 | 2016 | 2015-08-05 | C | 3 | 0.00014514 | 9.0713e-06
6662487 | 2015-08-25 09:30 | 2015-08-25 15:31 | 361.0667 | 8 | 2888.5333 | 361.0667 | 358.0667 | 0.0087342 | 2864.5333 | 0.0086617 | 2.419e-05 | NAPA ID:10520 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP620 | Replacing 11kV conductor between IP620 and TC661. Pouarua Road. W/O 30002562. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-25 | b | 0.0043308 | 1.2095e-05 | 2016 | 2015-08-25 | B | 8 | 0.0086617 | 2.419e-05
6662999 | 2015-08-05 13:43 | 2015-08-05 15:42 | 119.5 | 1 | 119.5 | 119.5 | 116.5 | 0.00036134 | 116.5 | 0.00035227 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC820 | Loose connection ug pillar box re-tightened TC820 cause: age Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-08-05 | c | 0.00035227 | 3.024e-06 | 2016 | 2015-08-05 | C | 1 | 0.00035227 | 3.0238e-06
6663069 | 2015-08-26 12:27 | 2015-08-26 13:55 | 87.6333 | 3 | 262.9 | 87.6333 | 84.6333 | 0.00079495 | 253.9 | 0.00076773 | 9.0713e-06 | NAPA ID:11717 TP_STRATFORD GXP > CARDIFF SUB > CLIMIE RD | 11 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Q31 | LLP Repair 11Kv ABS 5891 jumper. AP Replace faulty lightning arrestors. Cardiff Substation. W/O 10203193. | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-08-26 | b | 0.00038387 | 4.536e-06 | 2016 | 2015-08-26 | B | 3 | 0.00076773 | 9.0713e-06
6665828 | 2015-08-05 19:01 | 2015-08-06 04:16 | 554.9667 | 298 | 43226.2167 | 145.0544 | 142.0544 | 0.13071 | 42332.2167 | 0.128 | 0.00090108 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 216720 | Fire comms have confirmed this is a car vs pole at 555 Wright Street, KATIKATI - Have advised hub and control. Found fault & isolated at ABS IP559. ReStored rest of power. 2 poles broken at pole 216720 & 205003 and 1 crossarm at pole 205002 & lines down. | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-05 | c | 0.128 | 0.00090108 | 2016 | 2015-08-05 | C | 298 | 0.128 | 0.00090108
6668140 | 2015-08-06 06:28 | 2015-08-06 09:00 | 152 | 520 | 23883.45 | 45.9297 | 42.9297 | 0.072218 | 22323.45 | 0.067501 | 0.0015724 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217058 | TGA 17 sectionaliser 9220/2 tripped E/F, L/O. Feeder sectionalised & line down found at pole 217058. Isolation at ABS IP558 ( no back feeds ) Line repaired all service restored. High wind & rain at time of fault branch broken from tree 20 meters from line | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.067501 | 0.0015724 | 2016 | 2015-08-06 | C | 520 | 0.067501 | 0.0015724
6669207 | 2015-08-06 06:54 | 2015-08-06 08:35 | 101.0167 | 7 | 707.1167 | 101.0167 | 98.0167 | 0.0021382 | 686.1167 | 0.0020747 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | B0219 | Tree branch found across lines (2 HT fuses tripped). Branch removed OK and fuses relivened. (All 3 checked - 2 X 10A replaced). | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.0020747 | 2.1166e-05 | 2016 | 2015-08-06 | C | 7 | 0.0020747 | 2.1166e-05
6669356 | 2015-08-06 09:30 | 2015-08-06 10:51 | 80.7833 | 21 | 1696.45 | 80.7833 | 77.7833 | 0.0051297 | 1633.45 | 0.0049392 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 223873 | TPV 1 Emergency switching to isolate H/V with tree fallen into L/V at pole 223873. Isolation at Fuses SF5 047. Tree removed all service restored. High wind & rain at time of outage, re sag L/V straighten pole. NDR No 44158.Materials Nil. | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.0049392 | 6.3499e-05 | 2016 | 2015-08-06 | C | 21 | 0.0049392 | 6.3499e-05
6669773 | 2015-08-06 08:29 | 2015-08-06 15:00 | 391.4333 | 920 | 114781.6667 | 124.7627 | 121.7627 | 0.34707 | 112021.6667 | 0.33873 | 0.0027819 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207138, 207137 | 8:42AM ADVISED CONTROL OF CAR V POLE, THEY ARE GOING TO CONTACT FM AND LET HIM KNOW. KPT CB 1 tripped A, B & C O/C L/O ( at time of tripping was feeding KPT 2 ) Car V poles 207138 &207137. Isolations between ABS's SA2 009 & SA2 052 (no back feeds). Poles | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.33873 | 0.0027819 | 2016 | 2015-08-06 | C | 920 | 0.33873 | 0.0027819
6670748 | 2015-08-12 10:00 | 2015-08-12 12:07 | 127 | 22 | 2794 | 127 | 124 | 0.0084484 | 2728 | 0.0082488 | 6.6523e-05 | NAPA ID:11783 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M0484 | Replace pole M0484 hit by car. Works location: Lake Arapuni Rd, Putaruru. WO 30007220 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-08-12 | b | 0.0041244 | 3.3261e-05 | 2016 | 2015-08-12 | B | 22 | 0.0082488 | 6.6523e-05
6671018 | 2015-08-06 08:48 | 2015-08-11 10:45 | 7316.7 | 12 | 40235.4 | 3352.95 | 3349.95 | 0.12166 | 40199.4 | 0.12155 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 6863 | Tripping on Fuses 6863 Tangahoe Valley Rd. Torrential rain causing floods and slips. (Road Closed). Extensive damage suspected with parts of hills slipping away - One tree seen through conductors. Generators supplied to occupied houses at 4 Transformer s | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-06 | c | 0.12155 | 3.6285e-05 | 2016 | 2015-08-06 | C | 12 | 0.12155 | 3.6285e-05
6677384 | 2015-08-06 12:57 | 2015-08-06 13:16 | 18.95 | 1 | 18.95 | 18.95 | 15.95 | 5.73e-05 | 15.95 | 4.8229e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | F1036 | Short outage required from Fuses 1469 to repair a tipped crossarm. One Brace bolt replaced. Relivened OK. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-08-06 | c | 4.8229e-05 | 3.024e-06 | 2016 | 2015-08-06 | C | 1 | 4.8229e-05 | 3.0238e-06
6678454 | 2015-08-06 10:30 | 2015-08-06 20:20 | 590 | 2 | 1180 | 590 | 587 | 0.003568 | 1174 | 0.0035499 | 6.0475e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | X756, 770853 | Replace section of cable 11kV feeding Transformer X756. | F1 | BRYCE ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-08-06 | c | 0.0035499 | 6.048e-06 | 2016 | 2015-08-06 | C | 2 | 0.0035499 | 6.0475e-06
6678855 | 2015-08-26 10:20 | 2015-08-26 12:24 | 124.4 | 8 | 995.2 | 124.4 | 121.4 | 0.0030092 | 971.2 | 0.0029367 | 2.419e-05 | NAPA ID:10522 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP620 | (1) Carry out phase checks at pole O4336. (2) Isolate TC661 and TC4971 and IP620. (3) Install Jumpers on pole O4336. (4) Reliven TC661 and TC4971. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-26 | b | 0.0014683 | 1.2095e-05 | 2016 | 2015-08-26 | B | 8 | 0.0029367 | 2.419e-05
6682019 | 2015-08-10 13:19 | 2015-08-10 14:10 | 51 | 3 | 153 | 51 | 48 | 0.00046264 | 144 | 0.00043542 | 9.0713e-06 | NAPA ID:10752 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP 15 | Re-sag H/V Conductors. State Highway, Te Poi. W/O 30003315. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-08-10 | b | 0.00021771 | 4.536e-06 | 2016 | 2015-08-10 | B | 3 | 0.00043542 | 9.0713e-06
6682047 | 2015-08-06 15:54 | 2015-08-07 00:08 | 493.4333 | 1306 | 23128.2667 | 17.7092 | 14.7092 | 0.069934 | 19210.2667 | 0.058087 | 0.003949 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 853508 | at 18:18, Waihi Beach Sub, CB 5 Athenree Feeder. Faultman was dispatched to No Power call. Found blown jumper at 853508. Isolated Lines at ABS SA2-010, 9225/1 & Links 9225/6. Backfeed supplied from KPT 1 via KPT 2, Sectionaliser 9405 Closed. Permit issued | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.058087 | 0.003949 | 2016 | 2015-08-06 | C | 1306 | 0.058087 | 0.003949
6682454 | 2015-08-06 20:07 | 2015-08-06 21:08 | 61.1667 | 36 | 1911.2667 | 53.0907 | 50.0907 | 0.0057792 | 1803.2667 | 0.0054526 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12815 | at 19:19, Kerepehi Sub, CB 6 Ngatea Feeder. Lineman from Counties Power was driving through and noticed a floating conductor at Pole O12815. Reported it into Powerco. Faultman dispatched to investigate. Floating conductor confirmed. Backfeeds supplied fro | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-06 | c | 0.0054526 | 0.00010886 | 2016 | 2015-08-06 | C | 36 | 0.0054526 | 0.00010886
6685351 | 2015-08-06 23:30 | 2015-08-07 02:43 | 193 | 380 | 27626 | 72.7 | 69.7 | 0.083534 | 26486 | 0.080087 | 0.001149 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 703926 | Replaced 1 H/T Insulator & Pin at Pole 703926. Had trouble finding fault as was cross country. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-08-06 | c | 0.080087 | 0.001149 | 2016 | 2015-08-06 | C | 380 | 0.080087 | 0.001149
6690885 | 2015-08-25 09:00 | 2015-08-25 15:27 | 387.0333 | 50 | 19351.6667 | 387.0333 | 384.0333 | 0.058515 | 19201.6667 | 0.058061 | 0.00015119 | NAPA ID:10926 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 221755, 221793 | Replace poles, hardware and conductor. LL Permit to connect new conductor onto IP125 once AP returned to NOC. SH 33 Paengaroa, Te Puke. W/O 30008668. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-25 | b | 0.029031 | 7.5594e-05 | 2016 | 2015-08-25 | B | 50 | 0.058061 | 0.00015119
6692261 | 2015-08-07 12:32 | 2015-08-07 13:10 | 38 | 839 | 9797 | 11.677 | 8.677 | 0.029624 | 7280 | 0.022013 | 0.0025369 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 267787 | PMA CB3 tripped L/O (no flags). Rain & wind squall at time of tripping. Recloser 9488 opened with back feed via Sectionaliser 9675. Branch found on ground at pole 267787 likely cause. CB 3 closed & held line patrol carried out on feeder no other causes | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-08-07 | c | 0.022013 | 0.0025369 | 2016 | 2015-08-07 | C | 839 | 0.022013 | 0.0025369
6728304 | 2015-08-17 09:03 | 2015-08-17 14:55 | 352.15 | 307 | 20322.55 | 66.1972 | 63.1972 | 0.061451 | 19401.55 | 0.058666 | 0.00092829 | NAPA ID:11076 TP_PIAKO GXP > MORRINSVILLE SUB > ALEXANDRA AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4378 | STAGE 1: 1: Switching to bring in backfeeds. 2: Replace 11kV TX TC4378. 3: Cable from IC3162 to be disconnected and left disconnected from TX TC4378 but connected at IC3162 and in circuit earth. 4: Re-liven New Replacement TX TC4378 complete with Tblade. | F3 | ALEXANDRA AVE | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-08-17 | b | 0.029333 | 0.00046415 | 2016 | 2015-08-17 | B | 307 | 0.058666 | 0.00092829
6728317 | 2015-08-18 14:02 | 2015-08-18 15:09 | 67 | 250 | 16712 | 66.848 | 63.848 | 0.050533 | 15962 | 0.048265 | 0.00075594 | NAPA ID:11671 TP_PIAKO GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | PKOMOV018 | 1: LLP Connect new Temprary Line between 11kV Pole PKOMOV018 (11kV Line from Piako CB2) and 11kV Pole PKOMOV019 complete with 11kV Temporary Links TEMP53. 2:AP: Cut cable away from Pole PKOMOV034. (Cable earthed from 11kV SwGear IC3161 in circuit earth. N | F3 | ALEXANDRA AVE | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-08-18 | b | 0.024133 | 0.00037797 | 2016 | 2015-08-18 | B | 250 | 0.048265 | 0.00075594
6728337 | 2015-08-20 09:01 | 2015-08-20 15:43 | 402 | 38 | 15276 | 402 | 399 | 0.046191 | 15162 | 0.045846 | 0.0001149 | NAPA ID:11672 TP_PIAKO GXP > MORRINSVILLE SUB > ALEXANDRA AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4372 | Isolate old SD1 switch gear and install new CFCC RMU. 9981/1, 9981/2, 9981/3, 9981/4. Connect TC4372 to (RMU FUSE 9981/2). Connect Feeder to 9981/4 Connect cable that was IC3162 to 9981/3. Connect Cable that was IC3161 to 9981/1. NOTE: Cable from 9981/1 | F3 | ALEXANDRA AVE | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-08-20 | b | 0.022923 | 5.7451e-05 | 2016 | 2015-08-20 | B | 38 | 0.045846 | 0.0001149
6728348 | 2015-08-21 12:00 | 2015-08-21 12:40 | 40 | 57 | 2280 | 40 | 37 | 0.0068942 | 2109 | 0.0063771 | 0.00017235 | NAPA ID:11673 TP_PIAKO GXP > MORRINSVILLE SUB > ALEXANDRA AVE | 11 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4378 | 1: TP to test phasing between New RMU, Cable and Overhead. 2: Short outage to connect Cable from new RMU 9981/1 to Over head at pole PKOMOV034. (Note TS's to be offloaded before LINKS 53 opened). 2: AP Isolate TX TC 4378 and close cable break between new | F3 | ALEXANDRA AVE | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 0.0031886 | 8.6177e-05 | 2016 | 2015-08-21 | B | 57 | 0.0063771 | 0.00017235
6728663 | 2015-08-07 17:47 | 2015-08-07 21:57 | 249.8 | 467 | 63672.1667 | 136.343 | 133.343 | 0.19253 | 62271.1667 | 0.18829 | 0.0014121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 7 tripped on B & C phase O/C & E/F flags. Sectionalised & patrolled with no fault found. | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-08-07 | c | 0.18829 | 0.0014121 | 2016 | 2015-08-07 | C | 467 | 0.18829 | 0.0014121
6729537 | 2015-08-07 19:12 | 2015-08-07 20:01 | 49.2167 | 157 | 2380.2333 | 15.1607 | 12.1607 | 0.0071973 | 1909.2333 | 0.0057731 | 0.00047473 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE5-029 | at 19:12, Atuaroa Sub, CB 6 Te Puke Quarry Rd Feeder. Found 2x Blown HV Fuses at SE5-029. Faultman requested to isolate line and carry out line patrol beyond these Fuses. This is a difficult line to patrol - patrolled what was easily accessible. Requested | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-08-07 | c | 0.0057731 | 0.00047473 | 2016 | 2015-08-07 | C | 157 | 0.0057731 | 0.00047473
6729608 | 2015-08-07 18:39 | 2015-08-09 12:16 | 2496.6333 | 24 | 1756.8667 | 73.2028 | 70.2028 | 0.0053123 | 1684.8667 | 0.0050946 | 7.257e-05 |  | 33 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | z200 | CB Z200 Trip, O/C A-B-C Phase, RS 10060 Trip (Intertrip). O/H Line patrolled between Z200 & RS10060 with no fault found. Attempted Reclose on Z200 Tripped. E/F, O/C A & B Phase. Cable fault suspected. Cable Isolated to be tested next day. Passed to DNO. R | F2 | MILSON | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-08-07 | c | 0.0050946 | 7.257e-05 | 2016 | 2015-08-07 | C | 24 | 0.0050946 | 7.257e-05
6730440 | 2015-08-07 22:17 | 2015-08-07 22:53 | 36.1667 | 26 | 940.3333 | 36.1667 | 33.1667 | 0.0028433 | 862.3333 | 0.0026075 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850559 | Floating conductor due to insulator unscrewing from pin. Insulator screwed back on. Nil materials used. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-07 | c | 0.0026075 | 7.8618e-05 | 2016 | 2015-08-07 | C | 26 | 0.0026075 | 7.8618e-05
6730646 | 2015-08-07 22:34 | 2015-08-07 23:30 | 55.9333 | 3 | 167.8 | 55.9333 | 52.9333 | 0.00050739 | 158.8 | 0.00048017 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1133 | 3x 3Amp Links | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-07 | c | 0.00048017 | 9.071e-06 | 2016 | 2015-08-07 | C | 3 | 0.00048017 | 9.0713e-06
6731756 | 2015-08-07 22:05 | 2015-08-08 03:59 | 354 | 14 | 2973.8 | 212.4143 | 209.4143 | 0.0089921 | 2931.8 | 0.0088651 | 4.2333e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1460 | Transformer 1460 hit by lightning and needs to be replaced. 3 Phase, 30kVA, 11kV. Also installed 3x100Amp LV Fuseholders Complete & 3x 3Amp HV Links. Replaced by Brent Moratti & Craig Wellington. Single Fuses changed at Transformers 857, 1022 | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-07 | c | 0.0088651 | 4.2333e-05 | 2016 | 2015-08-07 | C | 14 | 0.0088651 | 4.2333e-05
6731922 | 2015-08-08 01:16 | 2015-08-08 03:04 | 108.2333 | 1 | 108.2333 | 108.2333 | 105.2333 | 0.00032727 | 105.2333 | 0.0003182 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Carrington Rd | Replaced Fuses due to Lightning on the Brooklands 7 feeder Also changed 1 transformer Fuse 939. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.0003182 | 3.024e-06 | 2016 | 2015-08-08 | C | 1 | 0.0003182 | 3.0238e-06
6732039 | 2015-08-08 03:29 | 2015-08-08 09:42 | 373 | 96 | 33004.5 | 343.7969 | 340.7969 | 0.099798 | 32716.5 | 0.098927 | 0.00029028 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4849 | Recloser 4835 tripped on C phase O/C & E/F flags. Line was sectionalised and patrolled. Faultman found a blown lightning arrestor on Links 4849. Line was isolated at Temp Links 48 to cut away blown arrestor. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.098927 | 0.00029028 | 2016 | 2015-08-08 | C | 96 | 0.098927 | 0.00029028
6733071 | 2015-08-08 07:30 | 2015-08-08 11:02 | 212 | 767 | 72374.5 | 94.3605 | 91.3605 | 0.21884 | 70073.5 | 0.21189 | 0.0023192 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 701530 | CB 7 tripped on A, B & C phase O/C flags received a Report of car v pole at 850 Carrington Rd Reported by fire service, ref number F1895698 - phone number 04 8010812. Line was isolated at ABS"s 33, 44 & 6806. 2 Temp Line Breaks were made each side of tran | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.21189 | 0.0023192 | 2016 | 2015-08-08 | C | 767 | 0.21189 | 0.0023192
6734772 | 2015-08-08 17:58 | 2015-08-08 18:52 | 53.8667 | 105 | 5656 | 53.8667 | 50.8667 | 0.017102 | 5341 | 0.01615 | 0.00031749 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5220 | Replaced 3x HV Fuse Holders Complete, 3x 3Amp Links, 1x 15kVA Transformer 3451T | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.01615 | 0.00031749 | 2016 | 2015-08-08 | C | 105 | 0.01615 | 0.00031749
6734845 | 2015-08-08 08:39 | 2015-08-08 16:18 | 458.1667 | 1 | 458.1667 | 458.1667 | 455.1667 | 0.0013854 | 455.1667 | 0.0013763 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2375T | Faultman replaced blown transformer 2375T, suspect lightning strike. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.0013763 | 3.024e-06 | 2016 | 2015-08-08 | C | 1 | 0.0013763 | 3.0238e-06
6735322 | 2015-08-08 09:33 | 2015-08-08 15:20 | 347 | 1573 | 146885 | 93.3789 | 90.3789 | 0.44415 | 142166 | 0.42988 | 0.0047564 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Peat St Sub CB 7 | CB 7 tripped at Peat St Sub on E/F flags. Line was sectionalised and patrolled and a line down was found. Line was isolated at ABS 2846 & Links 2536 to repair the line. At time of tripping CB 7 at Peat St Sub is back feeding CB 4 & 5 out of Roberts Ave Su | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.42988 | 0.0047564 | 2016 | 2015-08-08 | C | 1573 | 0.42988 | 0.0047564
6736304 | 2015-08-08 11:42 | 2015-08-08 14:55 | 193.6 | 2 | 387.2 | 193.6 | 190.6 | 0.0011708 | 381.2 | 0.0011527 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7/612 | Faultman found blown fuse at Fuses Q100. Faultman tested transformer T7/612 and found it to be faulty. Line was isolated at Fuses Q100 to replace the transformer and replace the LV jumpers and LV crutches. This job did not affect transformer T7/611. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.0011527 | 6.048e-06 | 2016 | 2015-08-08 | C | 2 | 0.0011527 | 6.0475e-06
6739362 | 2015-08-08 12:14 | 2015-08-08 16:12 | 238 | 52 | 6459.4 | 124.2192 | 121.2192 | 0.019532 | 6303.4 | 0.01906 | 0.00015724 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11900 | Recloser 4443/2 tripped on B phase O/C flags. Line was sectionalised and patrolled and a floating wire was found at pole P11900, line was isolated at ABS K41 & N12 to rebind the conductor. Replace nut on clamp top. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.01906 | 0.00015724 | 2016 | 2015-08-08 | C | 52 | 0.01906 | 0.00015724
6739739 | 2015-08-08 12:33 | 2015-08-08 14:02 | 89.0167 | 2067 | 64285.7167 | 31.101 | 28.101 | 0.19438 | 58084.7167 | 0.17563 | 0.0062501 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WHOPKO183 | CB 402 at TP Waihou sub & CB 60 Waitoa sub tripped to L/O. Flags on 402 were O/C Time & Neutral Time O/C & E/F on CB 60. Loss of supply to Farmers Rd & Tatua subs as Tatua supplied via CB 42 @ Farmers Rd sub at time. Sectionalising carried out by isolati | F1,F2,F3 | PC199-WAITOA 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 2015-08-08 | c | 0.17563 | 0.0062501 | 2016 | 2015-08-08 | C | 2067 | 0.17563 | 0.0062501
6742791 | 2015-08-08 14:00 | 2015-08-08 15:21 | 81 | 629 | 33771.4 | 53.6906 | 50.6906 | 0.10212 | 31884.4 | 0.096411 | 0.0019019 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 7 | CB 7 tripped on O/C & E/F flags line was sectionalised and patrolled and no fault was found. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.096411 | 0.0019019 | 2016 | 2015-08-08 | C | 629 | 0.096411 | 0.0019019
6744812 | 2015-08-08 15:22 | 2015-08-08 18:09 | 166.65 | 6 | 999.9 | 166.65 | 163.65 | 0.0030235 | 981.9 | 0.002969 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7776 | Faultman found blown fuses at Fuses 7776, line was patrolled no fault found. 2 x 10 amp HV replaced. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.002969 | 1.8143e-05 | 2016 | 2015-08-08 | C | 6 | 0.002969 | 1.8143e-05
6745623 | 2015-08-08 19:09 | 2015-08-08 23:52 | 282.6333 | 1 | 282.6333 | 282.6333 | 279.6333 | 0.00085462 | 279.6333 | 0.00084554 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Due to lines down. OMS 6745636 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.00084554 | 3.024e-06 | 2016 | 2015-08-08 | C | 1 | 0.00084554 | 3.0238e-06
6745636 | 2015-08-08 20:03 | 2015-08-08 23:49 | 226 | 143 | 32318 | 226 | 223 | 0.097722 | 31889 | 0.096425 | 0.0004324 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784790 | Report of lines on fire. Palm trees growing into lines, burnt lines down. Used 35mtrs of squirrel & 4 tension sleeves. NDR #41349. BEING RECREATED WITHIN OMS | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-08-08 | c | 0.096425 | 0.0004324 | 2016 | 2015-08-08 | C | 143 | 0.096425 | 0.0004324
6746872 | 2015-08-09 07:31 | 2015-08-09 08:46 | 74.55 | 60 | 4473 | 74.55 | 71.55 | 0.013525 | 4293 | 0.012981 | 0.00018143 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4230 | Line patrolled beyond Recloser 4230 and nothing found susspect line clashing due to snow melting and falling off causing lines to bounce together | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-09 | c | 0.012981 | 0.00018143 | 2016 | 2015-08-09 | C | 60 | 0.012981 | 0.00018143
6748410 | 2015-08-09 14:46 | 2015-08-09 15:57 | 71.3333 | 3 | 214 | 71.3333 | 68.3333 | 0.00064708 | 205 | 0.00061987 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | sf7029 | 11kV line patrol. re-loaded 2 x 40 amp HRC Fuses at Fuse SF7029. Cause: Unknown, may be bird. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. I confirmed again with FM about the 40 amp HRC Fuses. H | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-09 | c | 0.00061987 | 9.071e-06 | 2016 | 2015-08-09 | C | 3 | 0.00061987 | 9.0713e-06
6748680 | 2015-08-09 16:04 | 2015-08-09 23:26 | 442 | 1 | 442 | 442 | 439 | 0.0013365 | 439 | 0.0013274 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Part of HV fault refer OMS 6749679 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-09 | c | 0.0013274 | 3.024e-06 | 2016 | 2015-08-09 | C | 1 | 0.0013274 | 3.0238e-06
6748927 | 2015-08-09 17:05 | 2015-08-09 19:10 | 125.1833 | 1 | 125.1833 | 125.1833 | 122.1833 | 0.00037852 | 122.1833 | 0.00036945 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4058 | Replace 2 x 6A H/V, O/H fuses ( Lightning ) at Fuses FC4058. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-09 | c | 0.00036945 | 3.024e-06 | 2016 | 2015-08-09 | C | 1 | 0.00036945 | 3.0238e-06
6749482 | 2015-08-09 18:26 | 2015-08-10 12:42 | 1095.7167 | 1 | 1095.7167 | 1095.7167 | 1092.7167 | 0.0033132 | 1092.7167 | 0.0033041 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC3405 | Transformer TC3405 suspected faulty & requires replacement in morning. Fog & lightning in area not replaced due to safety. 4 customers advised 2 not. Transformer TC3405 replaced by Brian Fisher, all voltages correct 12.42. 30kVA 3 phase 11kV/400V. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-09 | c | 0.0033041 | 3.024e-06 | 2016 | 2015-08-09 | C | 1 | 0.0033041 | 3.0238e-06
6749679 | 2015-08-09 16:40 | 2015-08-09 20:53 | 252.3667 | 148 | 26932.2 | 181.9743 | 178.9743 | 0.081437 | 26488.2 | 0.080094 | 0.00044752 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | RS 248 | Recloser 284 found tripped, no comms so trip not recorded - lines patrolled with no fault found - two faultman reqiured as one had to operate recloser | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-09 | c | 0.080094 | 0.00044752 | 2016 | 2015-08-09 | C | 148 | 0.080094 | 0.00044752
6752686 | 2015-08-09 22:24 | 2015-08-09 23:25 | 61.35 | 1 | 61.35 | 61.35 | 58.35 | 0.00018551 | 58.35 | 0.00017644 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1525 | Replace 3 x 3A H/V, O/H fuses (lightning) at transformer TC6221. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-09 | c | 0.00017644 | 3.024e-06 | 2016 | 2015-08-09 | C | 1 | 0.00017644 | 3.0238e-06
6753148 | 2015-08-10 02:51 | 2015-08-10 13:55 | 663.5333 | 122 | 21743.4 | 178.2246 | 175.2246 | 0.065747 | 21377.4 | 0.06464 | 0.0003689 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 839976 | CB C936 Tripped B,C Ph O/C E/F L/O - during line patrol Pole 839984 found broken (rotten) - Isolated at ABS' S708 & S12, Line Break made at Pole 839976 - Power Restored to Feeder. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0.06464 | 0.0003689 | 2016 | 2015-08-10 | C | 122 | 0.06464 | 0.0003689
6754206 | 2015-08-10 07:22 | 2015-08-10 08:20 | 58 | 1015 | 54858.4333 | 54.0477 | 51.0477 | 0.16588 | 51813.4333 | 0.15667 | 0.0030691 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Te Ore Ore | 33kV CB C809 tripped on E/F line sectionalised and supply restored with no apparent cause found. | F1,F2,F3 | AWATOITOI 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 2015-08-10 | c | 0.15667 | 0.0030691 | 2016 | 2015-08-10 | C | 1015 | 0.15667 | 0.0030691
6755359 | 2015-08-10 08:06 | 2015-08-10 09:39 | 93 | 1 | 93 | 93 | 90 | 0.00028121 | 90 | 0.00027214 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TP985 | Fuses Blown at Transformer TP985 due to Bird strike (Swan). 2x6Amp HV Fuses links | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-10 | c | 0.00027214 | 3.024e-06 | 2016 | 2015-08-10 | C | 1 | 0.00027214 | 3.0238e-06
6756589 | 2015-08-10 11:16 | 2015-08-10 13:58 | 161.8833 | 125 | 6656.25 | 53.25 | 50.25 | 0.020127 | 6281.25 | 0.018993 | 0.00037797 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA2-083 | Broken DDO at transformer TA2-083. The top of the DDO broke when isolation of this tranformer TA2-083 for new earth mat installation. Isolation at ABS SA2-052 ABS SA2-009. No back feeds available. Power Isolated only once all gear on site & ready to go. J | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-08-10 | c | 0.018993 | 0.00037797 | 2016 | 2015-08-10 | C | 125 | 0.018993 | 0.00037797
6756985 | 2015-08-27 08:45 | 2015-08-27 17:20 | 514.5333 | 269 | 13212.9 | 49.1186 | 46.1186 | 0.039953 | 12405.9 | 0.037512 | 0.00081339 | NAPA ID:10774 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD4-288 | Replace Series One with Safe Link CCFC | F3 | MAUNGATAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-08-27 | b | 0.018756 | 0.0004067 | 2016 | 2015-08-27 | B | 269 | 0.037512 | 0.00081339
6759122 | 2015-08-10 14:23 | 2015-08-10 14:55 | 32 | 95 | 3040 | 32 | 29 | 0.0091922 | 2755 | 0.0083305 | 0.00028726 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 701529 | Close Line Breaks at Poles 701529 and 701533. TLB installed following tree car vs pole. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0.0083305 | 0.00028726 | 2016 | 2015-08-10 | C | 95 | 0.0083305 | 0.00028726
6759140 | 2015-08-10 13:20 | 2015-08-10 15:13 | 113 | 6 | 678 | 113 | 110 | 0.0020501 | 660 | 0.0019957 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7776 | Replaced 2X HV insulators and replaced 2X HV Fuses | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0.0019957 | 1.8143e-05 | 2016 | 2015-08-10 | C | 6 | 0.0019957 | 1.8143e-05
6759145 | 2015-08-10 14:17 | 2015-08-10 18:42 | 265 | 689 | 104354 | 151.4572 | 148.4572 | 0.31554 | 102287 | 0.30929 | 0.0020834 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9152/3 | Feeder trip B OC E/F. Feeder sectionalized & patrolled. Sw/Gear 9152/3 had a cable termination fail in the switch unit. Sw/Gear 9152/1,2,3 checked no damage to insulators, hole in steel base plate from fault. Cable isolated & back feeds from BHM CB 3 via | F3/F4 | SHERWOOD ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-08-10 | c | 0.30929 | 0.0020834 | 2016 | 2015-08-10 | C | 689 | 0.30929 | 0.0020834
6760120 | 2015-08-31 09:15 | 2015-08-31 12:33 | 198 | 7 | 1386 | 198 | 195 | 0.0041909 | 1365 | 0.0041274 | 2.1166e-05 | NAPA ID:11845 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M0972 | LLP1: To install a line Br on pole M0971. AP: To repair the lines between poles M0967 & M12377. LLP2: To replace line Br on pole M0971. Works location: Waotu Rd, Putaruru. WO 30010392. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-08-31 | b | 0.0020637 | 1.0583e-05 | 2016 | 2015-08-31 | B | 7 | 0.0041274 | 2.1166e-05
6760890 | 2015-08-10 15:44 | 2015-08-10 18:08 | 143.5833 | 677 | 66239.15 | 97.8422 | 94.8422 | 0.20029 | 64208.15 | 0.19415 | 0.0020471 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1 | CB S61 L/O on E/F. Sectionalised and found no fault | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0.19415 | 0.0020471 | 2016 | 2015-08-10 | C | 677 | 0.19415 | 0.0020471
6762825 | 2015-08-10 18:37 | 2015-08-10 21:31 | 173.7167 | 23 | 3995.4833 | 173.7167 | 170.7167 | 0.012081 | 3926.4833 | 0.011873 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 858359 | Check OMS 6762891 - 293 Pipiroa Road. 5.30pm advised SVS hub. 1 x broken 11kv conductor repaired. 2 x 16mm Cu sleeves & 1 metre 16mm Cu conductor only materials used. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-10 | c | 0.011873 | 6.9546e-05 | 2016 | 2015-08-10 | C | 23 | 0.011873 | 6.9546e-05
6766642 | 2015-08-10 21:40 | 2015-08-11 09:15 | 695.2667 | 927 | 14310 | 15.4369 | 12.4369 | 0.04327 | 11529 | 0.034861 | 0.002803 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 4 PAUL DRIVE | at 07:15, Kerepehi Sub, CB 6 Ngatea Feeder. Faultman was called to multiple part power calls. 02:15. Brent Williams confirmed part power only to transformers TC2823, TP1411, TC3751. Caused by possible cable fault or Sw/Gear fault beyond Sw/Gear IC1985. He | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-10 | c | 0.034861 | 0.002803 | 2016 | 2015-08-10 | C | 927 | 0.034861 | 0.002803
6769383 | 2015-08-10 10:01 | 2015-08-11 10:04 | 1442.9167 | 979 | 2382.9833 | 2.4341 | -0.5659 | 0.0072056 | 0 | 0 | 0.0029603 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S181 | A Tripping occurred on both CBs C818 (Akura, Coradine feeder) and C862 (Chapel, Essex St Feeder). Flags C818 Deft E/F, CB C865 Phase A-C O/C. Switching was being carried out on NAPA 10299 and ABS S181 had just been closed (paralleling feeders) when the tr | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0 | 0.0029603 | 2016 | 2015-08-10 | C | 979 | 0 | 0.0029603
6770466 | 2015-08-11 14:15 | 2015-08-11 14:50 | 35.2667 | 10 | 352.6667 | 35.2667 | 32.2667 | 0.0010664 | 322.6667 | 0.00097567 | 3.0238e-05 | NAPA ID:12013 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/465 | 30kVA tx with a 50kVA due to gross loading now has ten houses on it. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-08-11 | b | 0.00048783 | 1.5119e-05 | 2016 | 2015-08-11 | B | 10 | 0.00097567 | 3.0238e-05
6770846 | 2015-08-28 09:33 | 2015-08-28 14:01 | 267.9667 | 30 | 8039 | 267.9667 | 264.9667 | 0.024308 | 7949 | 0.024036 | 9.0713e-05 | NAPA ID:11983 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 784215 | Replace 11kV pole 784215 broken when a tree fell onto the line pole is being held up with ropes and a stay wire. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-08-28 | b | 0.012018 | 4.5356e-05 | 2016 | 2015-08-28 | B | 30 | 0.024036 | 9.0713e-05
6770902 | 2015-08-12 10:45 | 2015-08-12 13:10 | 145 | 1 | 145 | 145 | 142 | 0.00043845 | 142 | 0.00042937 | 3.0238e-06 | NAPA ID:12014 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5760 | Repair faulty 11kV jumpers. Works location: East Rd. WO 10210839 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-12 | b | 0.00021469 | 1.512e-06 | 2016 | 2015-08-12 | B | 1 | 0.00042937 | 3.0238e-06
6771071 | 2015-08-11 09:20 | 2015-08-11 12:15 | 175 | 6 | 1050 | 175 | 172 | 0.0031749 | 1032 | 0.0031205 | 1.8143e-05 | NAPA ID:10482 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/363 | Replace 11KV Tranformer T1/363 planned | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-11 | b | 0.0015603 | 9.071e-06 | 2016 | 2015-08-11 | B | 6 | 0.0031205 | 1.8143e-05
6808066 | 2015-08-11 18:36 | 2015-08-12 11:45 | 1028.5833 | 9 | 2238.1833 | 248.687 | 245.687 | 0.0067677 | 2211.1833 | 0.0066861 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2372 | Line isolated at fuses FC2372 to isolate faulty transformer TC1138. Line restored, transformer left isolated to replace in morning. Paul James has been in contact with customer who agreed to morning change. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-11 | c | 0.0066861 | 2.7214e-05 | 2016 | 2015-08-11 | C | 9 | 0.0066861 | 2.7214e-05
6811115 | 2015-08-12 10:56 | 2015-08-12 12:22 | 86.4167 | 76 | 5603.7667 | 73.7338 | 70.7338 | 0.016944 | 5375.7667 | 0.016255 | 0.00022981 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | N/A - NOT APPLICABLE | 11kV Recloser 7417 tripped E/F L/O. Close Approach Consent 32872 issued to Horn Logging. NOC Duty NC attempted to contact the consent holder, unable to do so. Downers dispatched to investigate. Cause of tripping was due to Horn Logging actions, a digger b | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-08-12 | c | 0.016255 | 0.00022981 | 2016 | 2015-08-12 | C | 76 | 0.016255 | 0.00022981
6811228 | 2015-08-10 14:34 | 2015-08-10 15:45 | 71 | 49 | 3479 | 71 | 68 | 0.01052 | 3332 | 0.010075 | 0.00014816 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731411 | Fuses replaced at Transformer 3362T. 3 x DDOs. isolated beyond Recloser 5961. | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-08-10 | c | 0.010075 | 0.00014816 | 2016 | 2015-08-10 | C | 49 | 0.010075 | 0.00014816
6812005 | 2015-09-02 09:44 | 2015-09-02 13:32 | 228 | 19 | 4332 | 228 | 225 | 0.013099 | 4275 | 0.012927 | 5.7451e-05 | NAPA ID:09633 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP 781 | From 9am - 12noon, Replace pole H3694. 11kV Outage. From 12:00 noon to 3pm, Replace Transformer TC394 and re install LV service lines. 1031 Piakoiti Road, Walton. W/O 30010085. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.0064633 | 2.8726e-05 | 2016 | 2015-09-02 | B | 19 | 0.012927 | 5.7451e-05
6812226 | 2015-09-14 09:09 | 2015-09-14 15:37 | 387.7333 | 57 | 22100.8 | 387.7333 | 384.7333 | 0.066828 | 21929.8 | 0.06631 | 0.00017235 | NAPA ID:11633 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 731073 | Replacing conductor between poles 731073 & 731015. Ball Road, Alton. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-14 | b | 0.033155 | 8.6177e-05 | 2016 | 2015-09-14 | B | 57 | 0.06631 | 0.00017235
6812254 | 2015-09-17 09:01 | 2015-09-17 14:50 | 348.6167 | 6 | 2091.7 | 348.6167 | 345.6167 | 0.0063248 | 2073.7 | 0.0062704 | 1.8143e-05 | NAPA ID:11647 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS L1730 | Replace ABS LI730 , Tx L4455 and as many other poles we can during the shutdown period. Ball Road, Patea. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-17 | b | 0.0031352 | 9.071e-06 | 2016 | 2015-09-17 | B | 6 | 0.0062704 | 1.8143e-05
6812328 | 2015-09-01 22:01 | 2015-09-01 22:23 | 21.8167 | 264 | 5759.6 | 21.8167 | 18.8167 | 0.017416 | 4967.6 | 0.015021 | 0.00079827 | NAPA ID:11715 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 824181 | Make a temp line break on 01/08 so that a temp live line cut can be made on 02/08 so that abs pole S330 can be replaced. Carters Line, Carterton. W/O 10159903. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-01 | b | 0.0075104 | 0.00039914 | 2016 | 2015-09-01 | B | 264 | 0.015021 | 0.00079827
6812374 | 2015-09-02 09:08 | 2015-09-02 12:06 | 178 | 7 | 1246 | 178 | 175 | 0.0037676 | 1225 | 0.0037041 | 2.1166e-05 | NAPA ID:11177 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1219 | To install a 40V Fuse Disconnector on pole TC482. To replace the arms, Hardware & install a fuse Disconnector on TC2490. Te Mimi Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.0018521 | 1.0583e-05 | 2016 | 2015-09-02 | B | 7 | 0.0037041 | 2.1166e-05
6812380 | 2015-09-02 11:00 | 2015-09-02 11:55 | 55 | 4 | 220 | 55 | 52 | 0.00066523 | 208 | 0.00062894 | 1.2095e-05 | NAPA ID:11178 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4057 | To install a 400V Fuse/Disconector. 496 Tahuna Road. Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.00031447 | 6.048e-06 | 2016 | 2015-09-02 | B | 4 | 0.00062894 | 1.2095e-05
6812487 | 2015-09-01 09:19 | 2015-09-01 15:17 | 358 | 19 | 6802 | 358 | 355 | 0.020568 | 6745 | 0.020395 | 5.7451e-05 | NAPA ID:11372 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuse T24 | Replace poles: P45378, P45380, P45381, P45382, P45384, P45385, P45394, P45396. Mangaramarama Road, Pahiatua. W/O 10147215. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-01 | b | 0.010198 | 2.8726e-05 | 2016 | 2015-09-01 | B | 19 | 0.020395 | 5.7451e-05
6812542 | 2015-09-02 14:00 | 2015-09-02 14:21 | 21 | 6 | 126 | 21 | 18 | 0.00038099 | 108 | 0.00032657 | 1.8143e-05 | NAPA ID:11180 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1374 | To install a 400V Fuse Disconnector. Tahuna Road, Piako. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.00016328 | 9.071e-06 | 2016 | 2015-09-02 | B | 6 | 0.00032657 | 1.8143e-05
6812582 | 2015-09-01 13:00 | 2015-09-01 14:10 | 70 | 3 | 210 | 70 | 67 | 0.00063499 | 201 | 0.00060778 | 9.0713e-06 | NAPA ID:11731 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2606 | Replace broken crossarms. Work Location: 78 Miki Miki Road, Masterton. Work Order: 10162207. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-09-01 | b | 0.00030389 | 4.536e-06 | 2016 | 2015-09-01 | B | 3 | 0.00060778 | 9.0713e-06
6812638 | 2015-08-13 08:27 | 2015-08-13 16:31 | 484 | 157 | 3898 | 24.828 | 21.828 | 0.011787 | 3427 | 0.010362 | 0.00047473 | NAPA ID:12040 TP_TAURANGA 33 GXP > OTUMOETAI SUB > SHERWOOD ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9152 | Replace Ringmain unit 9152 due to faulty bushing. Note; 1 Hour outage at beginning & end of work to connect/disconnect generators . | F3/F4 | SHERWOOD ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-08-13 | b | 0.0051812 | 0.00023736 | 2016 | 2015-08-13 | B | 157 | 0.010362 | 0.00047473
6812780 | 2015-09-08 09:15 | 2015-09-08 15:49 | 394 | 2 | 788 | 394 | 391 | 0.0023827 | 782 | 0.0023646 | 6.0475e-06 | NAPA ID:11425 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1707 | Replace poles and Xarms on ball rd from pole 729068 ...to pole 729105. Ball Road, Alton. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-08 | b | 0.0011823 | 3.024e-06 | 2016 | 2015-09-08 | B | 2 | 0.0023646 | 6.0475e-06
6812803 | 2015-09-10 09:05 | 2015-09-10 12:08 | 183.3833 | 26 | 4767.9667 | 183.3833 | 180.3833 | 0.014417 | 4689.9667 | 0.014181 | 7.8618e-05 | NAPA ID:11477 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1716 | Replacing HV poles on Ball rd Alton. Ball Road, Patea. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-10 | b | 0.0070907 | 3.9309e-05 | 2016 | 2015-09-10 | B | 26 | 0.014181 | 7.8618e-05
6812864 | 2015-09-01 09:39 | 2015-09-01 14:10 | 270.75 | 73 | 19764.75 | 270.75 | 267.75 | 0.059764 | 19545.75 | 0.059102 | 0.00022073 | NAPA ID:11366 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1730 | Hv line reconstruction and reconductoring on Ball rd Alton. Ball Road, Patea. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-01 | b | 0.029551 | 0.00011037 | 2016 | 2015-09-01 | B | 73 | 0.059102 | 0.00022073
6813113 | 2015-08-12 16:25 | 2015-08-12 16:35 | 9.85 | 15 | 147.75 | 9.85 | 6.85 | 0.00044676 | 102.75 | 0.00031069 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I44 | 2 Fuses found blown at Fuses I44 - used 2 x 10 amp fuses. | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-08-12 | c | 0.00031069 | 4.5356e-05 | 2016 | 2015-08-12 | C | 15 | 0.00031069 | 4.5356e-05
6819888 | 2015-09-25 09:00 | 2015-09-25 14:38 | 338.1333 | 37 | 12443.2333 | 336.3036 | 333.3036 | 0.037625 | 12332.2333 | 0.03729 | 0.00011188 | NAPA ID:11960 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp links 72 - L1790 | Replace ABS LI872 plus other poles in area. Ball Road, Alton. W/O 30010887. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-25 | b | 0.018645 | 5.594e-05 | 2016 | 2015-09-25 | B | 37 | 0.03729 | 0.00011188
6819959 | 2015-08-21 09:20 | 2015-08-21 11:25 | 124.7833 | 2 | 249.5667 | 124.7833 | 121.7833 | 0.00075463 | 243.5667 | 0.00073649 | 6.0475e-06 | NAPA ID:12060 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1209 | Replace HV poles and arms. Maketu, Pongakawa. W/O 30002362. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 0.00036824 | 3.024e-06 | 2016 | 2015-08-21 | B | 2 | 0.00073649 | 6.0475e-06
6820825 | 2015-09-01 08:30 | 2015-09-01 14:26 | 356 | 2 | 712 | 356 | 353 | 0.0021529 | 706 | 0.0021348 | 6.0475e-06 | NAPA ID:07565 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 685 | Project number IR6978 Rangikura Reconstruction, SH3 Waverly Racecourse beyound 11kv fuses 658 replace poles 771389 to 771388. SH 3 Waverly Racecourse, Waverley. PPPD 55555. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-09-01 | b | 0.0010674 | 3.024e-06 | 2016 | 2015-09-01 | B | 2 | 0.0021348 | 6.0475e-06
6820827 | 2015-08-13 10:12 | 2015-08-13 11:52 | 100 | 1 | 100 | 100 | 97 | 0.00030238 | 97 | 0.0002933 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46878 | Andrew Tahura and Guy Herbert were carrying out Transformer Inspections. Found HV Lines were extremely low requiring immediate attention due to Pole P46878 leaning over. Work started via control room at 10am but not immediately requested on OMS. Isolated | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-13 | c | 0.0002933 | 3.024e-06 | 2016 | 2015-08-13 | C | 1 | 0.0002933 | 3.0238e-06
6820838 | 2015-09-03 09:34 | 2015-09-03 16:40 | 425.85 | 205 | 29547.4333 | 144.1338 | 141.1338 | 0.089344 | 28932.4333 | 0.087485 | 0.00061987 | NAPA ID:11612 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 1376 | Replace 11kV crossarms various locations. SH 1 Tokoroa, Harris Block. W/O 10163039. Note Linked Jobs: Protection review required. When parallel made via device 9595, Device 9198 tripped on O/C and Locked out, seen 155 Amps on this device. Reclosed 9198, o | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.043742 | 0.00030994 | 2016 | 2015-09-03 | B | 205 | 0.087485 | 0.00061987
6820953 | 2015-09-02 09:16 | 2015-09-02 14:21 | 305.3167 | 5 | 1526.5833 | 305.3167 | 302.3167 | 0.004616 | 1511.5833 | 0.0045707 | 1.5119e-05 | NAPA ID:10842 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P21768 | Run new Weta conductor between poles P21768 and Pole P21781. Sandon Road, Halcomb, Sanson. W/O 30002718. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-02 | b | 0.0022853 | 7.559e-06 | 2016 | 2015-09-02 | B | 5 | 0.0045707 | 1.5119e-05
6820971 | 2015-09-02 09:35 | 2015-09-02 14:41 | 305.85 | 16 | 4893.6 | 305.85 | 302.85 | 0.014797 | 4845.6 | 0.014652 | 4.838e-05 | NAPA ID:11897 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T27 | To replace burnt of soft wood pole with helicotor. Hinemoa Valley Road, Mangamutu. W/O 30001378. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-02 | b | 0.007326 | 2.419e-05 | 2016 | 2015-09-02 | B | 16 | 0.014652 | 4.838e-05
6821026 | 2015-09-02 09:09 | 2015-09-02 12:25 | 196.6667 | 13 | 2556.6667 | 196.6667 | 193.6667 | 0.0077307 | 2517.6667 | 0.0076128 | 3.9309e-05 | NAPA ID:11915 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 795278 | Replace poles 795278 /795265. Poles in poor condition. Wairepu East Road, Taihape. W/O 10161734. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-02 | b | 0.0038064 | 1.9654e-05 | 2016 | 2015-09-02 | B | 13 | 0.0076128 | 3.9309e-05
6821656 | 2015-09-04 08:45 | 2015-09-04 14:50 | 364.7 | 19 | 6929.3 | 364.7 | 361.7 | 0.020953 | 6872.3 | 0.02078 | 5.7451e-05 | NAPA ID:11373 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T24 | Replace poles: P45701, P45395, P45702, P45390, P45389. Mangaramarama Road, Pahiatua. W/O 10147215. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.01039 | 2.8726e-05 | 2016 | 2015-09-04 | B | 19 | 0.02078 | 5.7451e-05
6821658 | 2015-09-09 09:30 | 2015-09-09 13:40 | 250 | 4 | 1000 | 250 | 247 | 0.0030238 | 988 | 0.0029875 | 1.2095e-05 | NAPA ID:11893 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P46002 | To cut in live line gap at pole P46002 and replace damaged 11kV conductor. Ruawhata Road, Mangamutu. W/O 10161172. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-09 | b | 0.0014937 | 6.048e-06 | 2016 | 2015-09-09 | B | 4 | 0.0029875 | 1.2095e-05
6821725 | 2015-09-03 09:30 | 2015-09-03 15:30 | 360 | 11 | 3960 | 360 | 357 | 0.011974 | 3927 | 0.011874 | 3.3261e-05 | NAPA ID:11250 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC 861 | Replace H/V Crossarms at Various Sites. Thompsons Road, Manawaru, Mikkelsen Road. W/O 30000841. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.0059372 | 1.6631e-05 | 2016 | 2015-09-03 | B | 11 | 0.011874 | 3.3261e-05
6821728 | 2015-09-04 09:06 | 2015-09-04 12:14 | 188.5333 | 2 | 377.0667 | 188.5333 | 185.5333 | 0.0011402 | 371.0667 | 0.001122 | 6.0475e-06 | NAPA ID:11919 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 22 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 849 | Replace, pole 808400 due to poor condition. 5604 SH 1, Mangawekea, Taihape. W/O 30011403. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.00056101 | 3.024e-06 | 2016 | 2015-09-04 | B | 2 | 0.001122 | 6.0475e-06
6821741 | 2015-09-04 09:32 | 2015-09-04 13:12 | 220.05 | 9 | 1980.45 | 220.05 | 217.05 | 0.0059884 | 1953.45 | 0.0059068 | 2.7214e-05 | NAPA ID:11879 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R46 | To replace burnt 11kV cross arms. Ridge Road, Central, Mangamutu. W/O 10163076. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.0029534 | 1.3607e-05 | 2016 | 2015-09-04 | B | 9 | 0.0059068 | 2.7214e-05
6821806 | 2015-08-13 14:25 | 2015-08-13 18:18 | 233 | 149 | 9199.8833 | 61.7442 | 58.7442 | 0.027818 | 8752.8833 | 0.026467 | 0.00045054 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 778354 | RS284 A/R, E/F, O/C at 14:06hrs. Tripped to Lockout at 14:25 hrs. Due to digger hitting pole.Isolated at ABS 014 & Links Temp 46. Backfed via RS 4621. NDR #41854. Materials Used: 8 mtrs of squirrel conductor & 5 sleeves. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-08-13 | c | 0.026467 | 0.00045054 | 2016 | 2015-08-13 | C | 149 | 0.026467 | 0.00045054
6822266 | 2015-09-03 08:45 | 2015-09-03 15:06 | 381 | 28 | 10668 | 381 | 378 | 0.032257 | 10584 | 0.032003 | 8.4665e-05 | NAPA ID:11751 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 857 | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title. IR7453 Cambridge Rd Pole Renewal. Paparaum Road, Tirau. W/O 30002577. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.016002 | 4.2333e-05 | 2016 | 2015-09-03 | B | 28 | 0.032003 | 8.4665e-05
6822307 | 2015-09-08 10:29 | 2015-09-08 15:15 | 285.6333 | 22 | 6283.9333 | 285.6333 | 282.6333 | 0.019001 | 6217.9333 | 0.018802 | 6.6523e-05 | NAPA ID:11755 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 272 | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title ?IR7453 Cambridge Rd Pole Renewal?. Puketirau Road, Tirau. W/O 30002577. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 0.0094008 | 3.3261e-05 | 2016 | 2015-09-08 | B | 22 | 0.018802 | 6.6523e-05
6822316 | 2015-09-10 08:19 | 2015-09-10 13:53 | 333.35 | 16 | 5333.6 | 333.35 | 330.35 | 0.016128 | 5285.6 | 0.015982 | 4.838e-05 | NAPA ID:11757 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP51, D12467 | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title ?IR7453 Cambridge Rd Pole Renewal?. Off SH 1, 1.3km northwest of Puketirau Road, Tirau. W/O 30002577. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.0079912 | 2.419e-05 | 2016 | 2015-09-10 | B | 16 | 0.015982 | 4.838e-05
6822425 | 2015-09-06 08:32 | 2015-09-06 15:16 | 404.65 | 74 | 12144.2667 | 164.1117 | 161.1117 | 0.036721 | 11922.2667 | 0.03605 | 0.00022376 | NAPA ID:10294 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 821685 | LIVE LINE CUT AT POLE 821685 TO REPLACE LOAD BREAKING FUSES WITH NEW FUSED ABS STRUCTURE REPLACE OLD 11KV CABLE WITH NEW 185 3 CORE CABLE INTO T1444. Nelson Crescent, Clareville. W/O 10159932. | F2 | WYNDHAM ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-06 | b | 0.018025 | 0.00011188 | 2016 | 2015-09-06 | B | 74 | 0.03605 | 0.00022376
6825370 | 2015-08-14 05:35 | 2015-08-14 10:15 | 280.2833 | 297 | 4910.3167 | 16.5331 | 13.5331 | 0.014848 | 4019.3167 | 0.012153 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 818728 | Car Vs Pole State Highway 2 & No 1 line. Advised SMC ETA Required. Fire on the way F1899176 Adrian called and adviesd NDR # 37762. Isolated at Fuses 7215. Feeder opened for 10mins until isolated at Fuses due to lines sitting across car. 10m busk pole, com | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-08-14 | c | 0.012153 | 0.00089806 | 2016 | 2015-08-14 | C | 297 | 0.012153 | 0.00089806
6827799 | 2015-09-03 09:50 | 2015-09-03 11:40 | 110 | 4 | 440 | 110 | 107 | 0.0013305 | 428 | 0.0012942 | 1.2095e-05 | NAPA ID:11181 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4962 | To install a 400V Fuse/Disconnector. 43 Horrells Road, Morrinsville. W/O 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.00064709 | 6.048e-06 | 2016 | 2015-09-03 | B | 4 | 0.0012942 | 1.2095e-05
6828028 | 2015-09-07 09:30 | 2015-09-07 13:02 | 212.1 | 18 | 3817.8 | 212.1 | 209.1 | 0.011544 | 3763.8 | 0.011381 | 5.4428e-05 | NAPA ID:11885 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V83 | To replace 11kVconductor 270m and replace 11kV Fuses V84. Works location: Haunui Rd. WO 30007281 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-09-07 | b | 0.0056904 | 2.7214e-05 | 2016 | 2015-09-07 | B | 18 | 0.011381 | 5.4428e-05
6828216 | 2015-09-05 09:00 | 2015-09-05 12:38 | 218.1667 | 147 | 32070.5 | 218.1667 | 215.1667 | 0.096974 | 31629.5 | 0.09564 | 0.00044449 | NAPA ID:11650 TP_BUNNYTHORPE GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 414 | Change 5 x 33kv xarms and 3 x 11kv xarms and hardware. Works location: Roberts Line. WO 30001119 Job ran over by 30 min | F3 | KARAMEA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-05 | b | 0.04782 | 0.00022225 | 2016 | 2015-09-05 | B | 147 | 0.09564 | 0.00044449
6828316 | 2015-09-02 09:00 | 2015-09-02 14:38 | 337.7667 | 131 | 44247.4333 | 337.7667 | 334.7667 | 0.13379 | 43854.4333 | 0.13261 | 0.00039611 | NAPA ID:10989 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE7-031 | REPLACE HV POLES AND ARMS. Maketu, Pongakawa. W/O 30002362. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.066303 | 0.00019806 | 2016 | 2015-09-02 | B | 131 | 0.13261 | 0.00039611
6829082 | 2015-09-03 09:01 | 2015-09-03 14:19 | 318.3333 | 131 | 41701.6667 | 318.3333 | 315.3333 | 0.1261 | 41308.6667 | 0.12491 | 0.00039611 | NAPA ID:10990 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE7-031 | REPLACE HV POLES AND ARMS. Maketu, Pongakawa. W/O 30002362. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.062454 | 0.00019806 | 2016 | 2015-09-03 | B | 131 | 0.12491 | 0.00039611
6873754 | 2015-08-14 14:57 | 2015-08-14 15:09 | 11.6833 | 268 | 3131.1333 | 11.6833 | 8.6833 | 0.0094678 | 2327.1333 | 0.0070367 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Line patrolled an no fault found. | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-14 | c | 0.0070367 | 0.00081037 | 2016 | 2015-08-14 | C | 268 | 0.0070367 | 0.00081037
6874030 | 2015-08-15 15:05 | 2015-08-15 18:32 | 207.1333 | 124 | 10096.6833 | 81.4249 | 78.4249 | 0.03053 | 9724.6833 | 0.029405 | 0.00037495 | NAPA ID:12103 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1985 | AP to terminate cable on IC1985 TC2823 9264/1. Safety Issue with IC1985. IC1985 requiring switch to be shut down. Work Authority to remove Gensets off TC2823 TP1411 TC3751 LV Outage requried. Cable overlay IC1985-TC2823-9264/1 due to HV Cable fault - G | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-15 | b | 0.014703 | 0.00018747 | 2016 | 2015-08-15 | B | 124 | 0.029405 | 0.00037495
6874662 | 2015-08-15 22:43 | 2015-08-16 00:30 | 107 | 3 | 321 | 107 | 104 | 0.00097063 | 312 | 0.00094341 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | FP896 | Outage shows as being created at ABS SE6-003. This is an error as the substation was being upgraded and GIS had not reflected this. Outage was at Fuses FP896. | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-08-15 | c | 0.00094341 | 9.071e-06 | 2016 | 2015-08-15 | C | 3 | 0.00094341 | 9.0713e-06
6875229 | 2015-08-14 14:30 | 2015-08-14 14:31 | 1 | 239 | 239 | 1 | -2 | 0.00072268 | 0 | 0 | 0.00072268 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N/A - NOT APPLICABLE | Silver Fern Farms fed off Mikkelsen Sub, CB 4 have reported a direct lightning strike on network equipment. At this stage it is presumed to be 11kV ABS IP42 and may have damaged the Earthing and or the lightning arrestor on this asset. Can Downer inspect | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-14 | c | 0 | 0.00072268 | 2016 | 2015-08-14 | C | 239 | 0 | 0.00072268
6875981 | 2015-08-14 18:15 | 2015-08-14 19:31 | 75.6333 | 4 | 302.5333 | 75.6333 | 72.6333 | 0.00091479 | 290.5333 | 0.0008785 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | SD2-041 | Hilton Gardiner Attended. Reloaded, Relivened 4x DDO's. 2x DDO's & DDO carriers replaced at Transformer TD2-122, 2x DDO's Replaced at Fuses SD2-041. 6.51pm - retailer had call from customer advising a car has hit a pole which caused no power here, advise | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-08-14 | c | 0.0008785 | 1.2095e-05 | 2016 | 2015-08-14 | C | 4 | 0.0008785 | 1.2095e-05
6877563 | 2015-08-14 20:49 | 2015-08-14 22:50 | 121.4167 | 2 | 242.8333 | 121.4167 | 118.4167 | 0.00073427 | 236.8333 | 0.00071613 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716051 | Blown Insulator found at Pole 716051 - Isolated at fuses at Pole 716050 - used 1 x HV insulator 2x binders. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-08-14 | c | 0.00071613 | 6.048e-06 | 2016 | 2015-08-14 | C | 2 | 0.00071613 | 6.0475e-06
6879171 | 2015-08-15 03:11 | 2015-08-15 10:13 | 422.1833 | 415 | 127499.3667 | 307.2274 | 304.2274 | 0.38553 | 126254.3667 | 0.38176 | 0.0012549 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 838590 | Recloser C225/2 tripped on B & C phase O/C flags, line was patrolled and sectionalised and a tree was found on the line at pole 838590, line was isolated at ABS C225/1 and Links C225/6 so tree contractor could cut away the tree between poles 838590 & 8385 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-08-15 | c | 0.38176 | 0.0012549 | 2016 | 2015-08-15 | C | 415 | 0.38176 | 0.0012549
6880679 | 2015-08-15 12:06 | 2015-08-15 15:47 | 220.9167 | 113 | 3701.1167 | 32.7532 | 29.7532 | 0.011191 | 3362.1167 | 0.010166 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C217/2 | Recloser C217/2 auto reclosed on B & C phase O/C flags. Line was patrolled and faultman found Sectionaliser C218/2 to be open. Line was patrolled and sectionalised and no fault was found. This job may be a 2 R job due to the time doing the line patrol. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-15 | c | 0.010166 | 0.00034168 | 2016 | 2015-08-15 | C | 113 | 0.010166 | 0.00034168
6892066 | 2015-08-15 16:11 | 2015-08-15 17:22 | 71.5 | 1453 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0043935 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4 | Contacts checked and cleaned. CB4 restored to service | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-15 | c | 0 | 0.0043935 | 2016 | 2015-08-15 | C | 1453 | 0 | 0.0043935
6899981 | 2015-08-15 19:58 | 2015-08-15 22:34 | 155.8333 | 235 | 19935.7333 | 84.8329 | 81.8329 | 0.060281 | 19230.7333 | 0.058149 | 0.00071058 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711274 | CB NG2 A/R, Trip to Lockout. Sectionalised & Patrolled. Floating Conductor found at Pole 711274 Materials used: 1x Ali Binder | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-08-15 | c | 0.058149 | 0.00071058 | 2016 | 2015-08-15 | C | 235 | 0.058149 | 0.00071058
6900794 | 2015-08-16 05:53 | 2015-08-18 12:00 | 3247 | 3820 | 179953.0167 | 47.1081 | 44.1081 | 0.54413 | 168493.0167 | 0.50948 | 0.011551 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 707090 | CB 3102/1 tripped,(Castlecliff Sub), CB 3042 tripped (Peat St Sub) on A, B & C phase O/C & E/F flags & CB 5 tripped (Castlecliff Sub) A & C phase O/C flags, received a call of car vs pole. Pole 707090 that was hit had 33kV,11kV & 400V on it, 33kV line wa | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-08-16 | c | 0.50948 | 0.011551 | 2016 | 2015-08-16 | C | 3820 | 0.50948 | 0.011551
6914835 | 2015-08-17 07:48 | 2015-08-17 10:04 | 135.9833 | 365 | 22666.3667 | 62.0996 | 59.0996 | 0.068538 | 21571.3667 | 0.065227 | 0.0011037 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Line patrolled nothing found. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-17 | c | 0.065227 | 0.0011037 | 2016 | 2015-08-17 | C | 365 | 0.065227 | 0.0011037
6915693 | 2015-08-20 09:24 | 2015-08-20 16:55 | 450.55 | 8 | 3604.4 | 450.55 | 447.55 | 0.010899 | 3580.4 | 0.010826 | 2.419e-05 | NAPA ID:12132 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | O2626 | Job cannot be closed out due to OMS Issue (Fuses FP1170 have been removed and replaced with ABS IP620). (1) Replace 7 poles between O2626 and O4336. (2) Replace conductor between poles O2626 and new IP620. (3) New conductor between poles O4336 and TC661 ( | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-20 | b | 0.0054131 | 1.2095e-05 | 2016 | 2015-08-20 | B | 8 | 0.010826 | 2.419e-05
6916663 | 2015-08-21 11:10 | 2015-08-21 11:30 | 20 | 3 | 60 | 20 | 17 | 0.00018143 | 51 | 0.00015421 | 9.0713e-06 | NAPA ID:12099 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2402 | Change Tap setting on TC2402 to resolve PQI issue | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-21 | b | 7.7106e-05 | 4.536e-06 | 2016 | 2015-08-21 | B | 3 | 0.00015421 | 9.0713e-06
6916678 | 2015-08-21 09:20 | 2015-08-21 11:10 | 110 | 7 | 770 | 110 | 107 | 0.0023283 | 749 | 0.0022648 | 2.1166e-05 | NAPA ID:12118 TP_BRUNSWICK GXP > PEAT ST SUB > WESTMERE PEAT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2266 | Replace transformer X2266 customer complaint voltage and fluctuating power issues | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-08-21 | b | 0.0011324 | 1.0583e-05 | 2016 | 2015-08-21 | B | 7 | 0.0022648 | 2.1166e-05
6918884 | 2015-09-02 13:35 | 2015-09-02 14:39 | 64 | 2 | 128 | 64 | 61 | 0.00038704 | 122 | 0.0003689 | 6.0475e-06 | NAPA ID:11179 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC947 | To install a 400V Fuise/Disconnector. Works location: Maungateparu Loop Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.00018445 | 3.024e-06 | 2016 | 2015-09-02 | B | 2 | 0.0003689 | 6.0475e-06
6919019 | 2015-09-08 09:34 | 2015-09-08 11:58 | 143.9833 | 69 | 9934.85 | 143.9833 | 140.9833 | 0.030041 | 9727.85 | 0.029415 | 0.00020864 | NAPA ID:11925 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 795108 | Resag 11 kv wires at pole 795108 remove trees burning in 11 kv lines. Works location: Tiriwakawa Rd, Taihape. WO 30007515 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-08 | b | 0.014707 | 0.00010432 | 2016 | 2015-09-08 | B | 69 | 0.029415 | 0.00020864
6919156 | 2015-09-07 13:00 | 2015-09-07 15:09 | 129.15 | 2 | 258.3 | 129.15 | 126.15 | 0.00078104 | 252.3 | 0.00076289 | 6.0475e-06 | NAPA ID:11182 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 2173 | To install a 400V Fuse/Disconector & Replace the 400V Arms. Works location: Tahuna Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-07 | b | 0.00038145 | 3.024e-06 | 2016 | 2015-09-07 | B | 2 | 0.00076289 | 6.0475e-06
6919188 | 2015-09-03 10:22 | 2015-09-03 11:54 | 92 | 28 | 2576 | 92 | 89 | 0.0077892 | 2492 | 0.0075352 | 8.4665e-05 | NAPA ID:11554 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8293 | Replace Pole 745953 hit by Lightning Strike. Works location: Upland Rd, Egmont Village. WO 30012151 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-03 | b | 0.0037676 | 4.2333e-05 | 2016 | 2015-09-03 | B | 28 | 0.0075352 | 8.4665e-05
6919236 | 2015-09-03 10:31 | 2015-09-03 13:50 | 199 | 7 | 1393 | 199 | 196 | 0.0042121 | 1372 | 0.0041486 | 2.1166e-05 | NAPA ID:11588 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3308 | LLP: To replace the 11kV Pin Arm. 11kV Fuses. AP: To Replace the 400V pin arm & Install a 400V Fuse Unit. Works location: Bell Rd. WO 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-03 | b | 0.0020743 | 1.0583e-05 | 2016 | 2015-09-03 | B | 7 | 0.0041486 | 2.1166e-05
6919406 | 2015-08-17 12:42 | 2015-08-17 18:28 | 346 | 695 | 91420.1167 | 131.5397 | 128.5397 | 0.27643 | 89335.1167 | 0.27013 | 0.0021015 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 781187 | Fire Event # F1900802. Truck vs pole. CB 242 tripped on E/F flags, received a call of truck vs pole 781187, line was isolated at ABS 029, ABS 4192/1 and Links 4192/4 to replace the pole and hardware. NDR:047204 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-17 | c | 0.27013 | 0.0021015 | 2016 | 2015-08-17 | C | 695 | 0.27013 | 0.0021015
6920583 | 2015-08-17 14:08 | 2015-08-17 15:56 | 107.9833 | 1 | 107.9833 | 107.9833 | 104.9833 | 0.00032652 | 104.9833 | 0.00031744 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1088 | Low 11KV line which FM will defect for it to be done live line - not non reg | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-08-17 | c | 0.00031744 | 3.024e-06 | 2016 | 2015-08-17 | C | 1 | 0.00031744 | 3.0238e-06
6920716 | 2015-09-09 09:15 | 2015-09-09 15:04 | 348.7167 | 29 | 10112.7833 | 348.7167 | 345.7167 | 0.030579 | 10025.7833 | 0.030316 | 8.7689e-05 | NAPA ID:11719 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L52 | Replace cross arms, poles P21764,P21763, P21761, P21759, P21760, P21930, P21925. Works location: Mt Stewart Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-09 | b | 0.015158 | 4.3845e-05 | 2016 | 2015-09-09 | B | 29 | 0.030316 | 8.7689e-05
6920751 | 2015-09-16 09:24 | 2015-09-16 14:42 | 318.3 | 29 | 9230.7 | 318.3 | 315.3 | 0.027911 | 9143.7 | 0.027648 | 8.7689e-05 | NAPA ID:11860 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS L52 | replacing poles, X arms and conductor between poles P21916 and pole P21766. Works location: Mt Stewart Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-16 | b | 0.013824 | 4.3845e-05 | 2016 | 2015-09-16 | B | 29 | 0.027648 | 8.7689e-05
6920766 | 2015-09-23 09:03 | 2015-09-23 15:01 | 357.7333 | 29 | 10374.2667 | 357.7333 | 354.7333 | 0.031369 | 10287.2667 | 0.031106 | 8.7689e-05 | NAPA ID:11864 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L52 | Replacing poles, cross arms and conductor between poles P21916 and P21766. Works location: Mt Stewart Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-23 | b | 0.015553 | 4.3845e-05 | 2016 | 2015-09-23 | B | 29 | 0.031106 | 8.7689e-05
6920819 | 2015-09-29 09:12 | 2015-09-29 15:21 | 368.75 | 16 | 5900 | 368.75 | 365.75 | 0.01784 | 5852 | 0.017695 | 4.838e-05 | NAPA ID:11869 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P21916 | Replace 11kv poles, X arms and reconductor between poles P21916 and P21768. Works location: Mt Stewart-Halcomb Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-29 | b | 0.0088475 | 2.419e-05 | 2016 | 2015-09-29 | B | 16 | 0.017695 | 4.838e-05
6920897 | 2015-09-09 08:45 | 2015-09-09 12:20 | 215.3333 | 7 | 1507.3333 | 215.3333 | 212.3333 | 0.0045578 | 1486.3333 | 0.0044943 | 2.1166e-05 | NAPA ID:11378 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | U43 | Tree cutting near 11kV lines. Works location: Opaki Kaiparoro Rd, Masterton. PPPD 46954. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-09-09 | b | 0.0022472 | 1.0583e-05 | 2016 | 2015-09-09 | B | 7 | 0.0044943 | 2.1166e-05
6920911 | 2015-09-04 09:36 | 2015-09-04 14:49 | 313 | 13 | 4069 | 313 | 310 | 0.012304 | 4030 | 0.012186 | 3.9309e-05 | NAPA ID:11803 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI774 | Run new conductor from pole 728722 to pole 728702. Works location: Garsed Rd, Kakaramea. WO 30001089 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.0060929 | 1.9654e-05 | 2016 | 2015-09-04 | B | 13 | 0.012186 | 3.9309e-05
6921164 | 2015-09-04 10:09 | 2015-09-04 12:17 | 128 | 60 | 7680 | 128 | 125 | 0.023222 | 7500 | 0.022678 | 0.00018143 | NAPA ID:11024 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 173 | Replacing 11kV Fuses on transformer 752 as they are faulty. Works location: Walsh Rd, New Plymouth. WO 30008631 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.011339 | 9.0713e-05 | 2016 | 2015-09-04 | B | 60 | 0.022678 | 0.00018143
6921366 | 2015-09-02 09:15 | 2015-09-02 10:45 | 90 | 4 | 360 | 90 | 87 | 0.0010886 | 348 | 0.0010523 | 1.2095e-05 | NAPA ID:11323 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2923 | Replace transformer at TC2923. Works location: Old Maratoto Rd, Hikutaia. WO 10147831 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-09-02 | b | 0.00052613 | 6.048e-06 | 2016 | 2015-09-02 | B | 4 | 0.0010523 | 1.2095e-05
6923620 | 2015-08-17 23:35 | 2015-08-18 04:41 | 306.25 | 177 | 9742 | 55.0395 | 52.0395 | 0.029457 | 9211 | 0.027852 | 0.00053521 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K0275 | 1 x Pin and insulator. 16 mtrs 16mm copper conductor. 2 sleeves. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-08-17 | c | 0.027852 | 0.00053521 | 2016 | 2015-08-17 | C | 177 | 0.027852 | 0.00053521
6924785 | 2015-08-18 07:48 | 2015-08-18 09:32 | 103.9667 | 723 | 62272.4 | 86.1306 | 83.1306 | 0.1883 | 60103.4 | 0.18174 | 0.0021862 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 861227 | CB 5 Trip B Phase E/F. Feeder sectionalized & Patrolled. U/Ground sections livened up one section at a time. Small branch found below pole 861227. LFI's checked at Sw/Gear IC1591. | F2/F3 | PORT RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-08-18 | c | 0.18174 | 0.0021862 | 2016 | 2015-08-18 | C | 723 | 0.18174 | 0.0021862
6925637 | 2015-09-04 10:35 | 2015-09-04 12:10 | 95 | 4 | 380 | 95 | 92 | 0.001149 | 368 | 0.0011127 | 1.2095e-05 | NAPA ID:11510 TP_HUIRANGI GXP > MCKEE SUB > MCKEE 1 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8603 | Remove ABS5163 [Leave 11kV Fuses same number 5163 ]. Works location: McKee Production. WO 10159896 | F1 | MCKEE 1 | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.00055637 | 6.048e-06 | 2016 | 2015-09-04 | B | 4 | 0.0011127 | 1.2095e-05
6925694 | 2015-09-08 09:00 | 2015-09-08 11:56 | 176 | 33 | 5808 | 176 | 173 | 0.017562 | 5709 | 0.017263 | 9.9784e-05 | NAPA ID:11440 TP_KOPU GXP > WHITIANGA SUB > COOK DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole W12956 | live line break at pole W12956 to enable crossarm change at TC3660. Works location: Cook Drive, Whitianga. WO 30007314 | F3 | COOK DRIVE | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 0.0086313 | 4.9892e-05 | 2016 | 2015-09-08 | B | 33 | 0.017263 | 9.9784e-05
6925808 | 2015-09-10 09:07 | 2015-09-10 15:04 | 357.55 | 8 | 2860.4 | 357.55 | 354.55 | 0.0086492 | 2836.4 | 0.0085766 | 2.419e-05 | NAPA ID:11471 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T44 | Replace poles P45736, P45739, P45740, P45741 and P45742. Replace and install new 11kV conductor between poles P27039 and P27043. Works location: Kaitawa Rd, Pahiatua. WO 10147215 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-10 | b | 0.0042883 | 1.2095e-05 | 2016 | 2015-09-10 | B | 8 | 0.0085766 | 2.419e-05
6925925 | 2015-09-07 13:30 | 2015-09-07 15:06 | 96 | 4 | 384 | 96 | 93 | 0.0011611 | 372 | 0.0011248 | 1.2095e-05 | NAPA ID:11184 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5983 | To install a 400V Fuse/Disconnector. Works location: Tahuna Rd. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-07 | b | 0.00056242 | 6.048e-06 | 2016 | 2015-09-07 | B | 4 | 0.0011248 | 1.2095e-05
6926024 | 2015-09-10 08:30 | 2015-09-10 14:01 | 330.6667 | 23 | 7605.3333 | 330.6667 | 327.6667 | 0.022997 | 7536.3333 | 0.022788 | 6.9546e-05 | NAPA ID:11747 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7148 | Replace x 7 11kV poles. Works location: Flat Point Rd, Masterton. WO 30011007 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-09-10 | b | 0.011394 | 3.4773e-05 | 2016 | 2015-09-10 | B | 23 | 0.022788 | 6.9546e-05
6926243 | 2015-08-19 09:25 | 2015-08-19 14:52 | 327 | 8 | 2616 | 327 | 324 | 0.0079102 | 2592 | 0.0078376 | 2.419e-05 | NAPA ID:12160 TP_TAURANGA 33 GXP > AONGATETE SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-072 | Replace 11kV Poles and Crossarms at Various Sites. Works location: Hwy 2 Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-19 | b | 0.0039188 | 1.2095e-05 | 2016 | 2015-08-19 | B | 8 | 0.0078376 | 2.419e-05
6926434 | 2015-09-07 09:30 | 2015-09-07 12:10 | 160 | 4 | 640 | 160 | 157 | 0.0019352 | 628 | 0.0018989 | 1.2095e-05 | NAPA ID:11183 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4722 | LLP: To replace the 11kv fuses TC4722 (With them open). AP: To replace the 400V Cross arm & install a 400V Fuse/Disconnector. Works location: Horrells Rd. WO 10147849. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-07 | b | 0.00094946 | 6.048e-06 | 2016 | 2015-09-07 | B | 4 | 0.0018989 | 1.2095e-05
6928590 | 2015-08-18 12:41 | 2015-08-18 15:50 | 189 | 365 | 30469 | 83.4767 | 80.4767 | 0.092131 | 29374 | 0.08882 | 0.0011037 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB WH 2 L/O.No Flags Sectionalised and found no fault | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.08882 | 0.0011037 | 2016 | 2015-08-18 | C | 365 | 0.08882 | 0.0011037
6932065 | 2015-09-15 09:00 | 2015-09-15 15:08 | 367.9167 | 16 | 5886.6667 | 367.9167 | 364.9167 | 0.0178 | 5838.6667 | 0.017655 | 4.838e-05 | NAPA ID:11808 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T27 | Replace poles or install new crossarms on the following list of poles: P46926, P46927, P46928, P46929, P46945, P46246, P46950, P46956, P46336, P46353. See plans for details. Hinemoa Valley Road, Pahiatua. W/O 10147215. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.0088274 | 2.419e-05 | 2016 | 2015-09-15 | B | 16 | 0.017655 | 4.838e-05
6984082 | 2015-08-18 14:59 | 2015-08-18 19:02 | 243.4833 | 2 | 486.9667 | 243.4833 | 240.4833 | 0.0014725 | 480.9667 | 0.0014543 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/357t | 3.02pm - Advise SMC that this is a cowshed. Replaced 2X HV fuses and blown. Own AP to replace transformer T7/357. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.0014543 | 6.048e-06 | 2016 | 2015-08-18 | C | 2 | 0.0014543 | 6.0475e-06
6984110 | 2015-08-18 13:31 | 2015-08-18 14:41 | 70 | 91 | 6370 | 70 | 67 | 0.019261 | 6097 | 0.018436 | 0.00027516 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | Reported DDO hanging by jumper at transformer N3310. Isolated between ABS NG310 & NG326. Resecured fuse holder and relivened | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.018436 | 0.00027516 | 2016 | 2015-08-18 | C | 91 | 0.018436 | 0.00027516
6985248 | 2015-08-18 11:31 | 2015-08-18 14:29 | 178.2333 | 2 | 356.4667 | 178.2333 | 175.2333 | 0.0010779 | 350.4667 | 0.0010597 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5033 | Replaced 2x 2Amp HV fuses at transformer T5033. Due to burnt out 400V main switch at 348 Lees Rd. Installation has been disconnected for safety tag A3825, is going to speak to customer. NOTE Fault man did not work through NOC control for authorisation to | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-08-18 | c | 0.0010597 | 6.048e-06 | 2016 | 2015-08-18 | C | 2 | 0.0010597 | 6.0475e-06
6986947 | 2015-08-18 17:06 | 2015-08-18 21:45 | 279 | 365 | 19155 | 52.4795 | 49.4795 | 0.05792 | 18060 | 0.054609 | 0.0011037 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 725771 | CB WH 2 tripped no flags, line was sectionalised and patrolled. The faultman found a big bird stuck between the conductor and the arm brace on pole 725771. Line was isolated at Fuses WH 270 and the bird was removed with hot line sticks. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.054609 | 0.0011037 | 2016 | 2015-08-18 | C | 365 | 0.054609 | 0.0011037
6988477 | 2015-08-18 19:42 | 2015-08-18 22:45 | 183 | 6 | 1098 | 183 | 180 | 0.0033201 | 1080 | 0.0032657 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | M1010 | Has blown transformer. Requesting 2r to replace transformer M1010. | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.0032657 | 1.8143e-05 | 2016 | 2015-08-18 | C | 6 | 0.0032657 | 1.8143e-05
6988964 | 2015-08-18 23:40 | 2015-08-19 00:25 | 45.35 | 18 | 815.95 | 45.3306 | 42.3306 | 0.0024672 | 761.95 | 0.002304 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740179 | Faultman found a broken jumper at pole 740179, line was isolated at ABS's 5629 & 5723 to repair the jumper. 1 x clamp used. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.002304 | 5.4428e-05 | 2016 | 2015-08-18 | C | 18 | 0.002304 | 5.4428e-05
6988975 | 2015-08-18 18:51 | 2015-08-18 21:44 | 173.3333 | 278 | 25532 | 91.8417 | 88.8417 | 0.077203 | 24698 | 0.074681 | 0.00084061 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 746345 | Recloser 6610 tripped on C phase O/C & E/F flags. Line was patrolled and sectionalised and faultman found a line down at pole 746345. Line was isolated at ABS's 347 & 355 to repair the line. 5 metres of 16mm copper conductor used. 4 X 16mm sleeves used. F | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-08-18 | c | 0.074681 | 0.00084061 | 2016 | 2015-08-18 | C | 278 | 0.074681 | 0.00084061
6990207 | 2015-08-18 20:08 | 2015-08-19 00:13 | 245.2833 | 97 | 19979.5167 | 205.9744 | 202.9744 | 0.060413 | 19688.5167 | 0.059533 | 0.0002933 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE4-020 | Check if OMS 6990228 and 6990232 are related. 31 and 1 Warner and 597 Oropi Road. Andy requested another 1r for voltage issues on TE4-016 TE4-017 TE4-169. 2 blown fuses at SE4-020. Last of fuses opened & line patrolled. Nothing found. 2 x blown 15amp fuse | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-08-18 | c | 0.059533 | 0.0002933 | 2016 | 2015-08-18 | C | 97 | 0.059533 | 0.0002933
6991694 | 2015-08-19 06:28 | 2015-08-19 15:01 | 513.2167 | 187 | 722.8 | 3.8652 | 0.86524 | 0.0021856 | 0 | 0 | 0.00056544 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 811506 | Initial Auto-reclose on 33kV CB C885 Martinborough and trip on Bidwells CB 3141/2 (C Phase O/C, EF). CB 3141/2 reclosed OK. Patrol carried out later and a burnt / tipped 11kV Crossarm was found down stream of Fuses 7395. Isolation carried out and a repla | F1,F2,F3 | PAHAUTEA 33KV TIE | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2015-08-19 | c | 0 | 0.00056544 | 2016 | 2015-08-19 | C | 187 | 0 | 0.00056544
6992257 | 2015-08-19 19:08 | 2015-08-19 20:53 | 105 | 3 | 315 | 105 | 102 | 0.00095248 | 306 | 0.00092527 | 9.0713e-06 | NAPA ID:12167 TP_CARRINGTON GXP > KATERE SUB > KATERE 8 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1016 | We have to replace transformer 1016 for safety and environmental reasons!! oil is leaking out of it and may cause a fault at any time. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-19 | b | 0.00046263 | 4.536e-06 | 2016 | 2015-08-19 | B | 3 | 0.00092527 | 9.0713e-06
6992319 | 2015-08-31 09:05 | 2015-08-31 14:09 | 304.2667 | 58 | 17647.4667 | 304.2667 | 301.2667 | 0.053362 | 17473.4667 | 0.052836 | 0.00017538 | NAPA ID:12185 TP_MASTERTON GXP > CHAPEL SUB > HIGH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Block and Tag C865 | Make a live line cut at pole 828553 so that 11kv pole 828190 can be replaced. Fleet Street, Masterton. W/O 30007227. | F3 | HIGH ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-08-31 | b | 0.026418 | 8.7689e-05 | 2016 | 2015-08-31 | B | 58 | 0.052836 | 0.00017538
6992339 | 2015-08-19 08:13 | 2015-08-19 10:26 | 133.05 | 19 | 2527.95 | 133.05 | 130.05 | 0.0076439 | 2470.95 | 0.0074716 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | D4 | 2 fuses found blown at Fuses D4 due to magpie, all fuses opened to clear Magpie using hot sticks - blown fuses replaced - Used 2x 10 amp fuses | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.0074716 | 5.7451e-05 | 2016 | 2015-08-19 | C | 19 | 0.0074716 | 5.7451e-05
6993354 | 2015-08-19 08:11 | 2015-08-19 11:55 | 224.7833 | 3 | 674.35 | 224.7833 | 221.7833 | 0.0020391 | 665.35 | 0.0020119 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1142 | Replace Transformer TC1142 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-08-19 | c | 0.0020119 | 9.071e-06 | 2016 | 2015-08-19 | C | 3 | 0.0020119 | 9.0713e-06
6993525 | 2015-08-19 09:53 | 2015-08-19 10:49 | 55.9333 | 704 | 33901.0333 | 48.1549 | 45.1549 | 0.10251 | 31789.0333 | 0.096122 | 0.0021287 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9516 | Recloser 9516/2 Trip P Trip E/F. Line Patrolled & Sectionalised. No fault found | F3 | TETLEY ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-08-19 | c | 0.096122 | 0.0021287 | 2016 | 2015-08-19 | C | 704 | 0.096122 | 0.0021287
7002148 | 2015-08-19 13:48 | 2015-08-19 14:04 | 16.3167 | 704 | 11486.9333 | 16.3167 | 13.3167 | 0.034734 | 9374.9333 | 0.028348 | 0.0021287 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9516 | Rec 9516 tripped. Line patrolled. No fault found. | F3 | TETLEY ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-08-19 | c | 0.028348 | 0.0021287 | 2016 | 2015-08-19 | C | 704 | 0.028348 | 0.0021287
7017097 | 2015-08-19 16:52 | 2015-08-19 18:40 | 108.1667 | 39 | 4218.5 | 108.1667 | 105.1667 | 0.012756 | 4101.5 | 0.012402 | 0.00011793 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4135 | Replaced 2X 10a HV Fuses | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.012402 | 0.00011793 | 2016 | 2015-08-19 | C | 39 | 0.012402 | 0.00011793
7018209 | 2015-08-19 21:46 | 2015-08-20 02:24 | 278.2167 | 111 | 15395.3 | 138.6964 | 135.6964 | 0.046552 | 15062.3 | 0.045545 | 0.00033564 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 798318 & 9 | CB C634 ARC & Tripped B&C Phase O/C line sectionalised and backfed and section between ABS S505 and Fuses 7276 patrolled and found lines tangled together between poles 798318 & 9 untangled with fuse stick and supply restored . | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.045545 | 0.00033564 | 2016 | 2015-08-19 | C | 111 | 0.045545 | 0.00033564
7020307 | 2015-08-19 22:03 | 2015-08-20 00:20 | 137.0833 | 61 | 8362.0833 | 137.0833 | 134.0833 | 0.025285 | 8179.0833 | 0.024732 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Sec C641 found open. No fault found. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.024732 | 0.00018445 | 2016 | 2015-08-19 | C | 61 | 0.024732 | 0.00018445
7023710 | 2015-09-07 09:46 | 2015-09-07 14:31 | 285.1833 | 42 | 11977.7 | 285.1833 | 282.1833 | 0.036218 | 11851.7 | 0.035837 | 0.000127 | NAPA ID:10912 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 347 | We are replacing Transformer 811. New pole, hardware and 30kVA and upgrading earths.1225 Richmond Road, Everett Park, Inglewood. W/O 30010500. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-09-07 | b | 0.017918 | 6.3499e-05 | 2016 | 2015-09-07 | B | 42 | 0.035837 | 0.000127
7024556 | 2015-08-20 09:16 | 2015-08-20 10:31 | 75.55 | 5 | 377.75 | 75.55 | 72.55 | 0.0011422 | 362.75 | 0.0010969 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758 | Job 7023865 Rolled in. Reload Reliven 2x6A Fuses | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-08-20 | c | 0.0010969 | 1.5119e-05 | 2016 | 2015-08-20 | C | 5 | 0.0010969 | 1.5119e-05
7024673 | 2015-08-20 10:25 | 2015-08-20 14:03 | 217.75 | 920 | 17825.75 | 19.3758 | 16.3758 | 0.053901 | 15065.75 | 0.045555 | 0.0027819 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P07269 | Cracked 11kV Insulator on Pole P07269. Material Used: replaced 1x HV insulator OH due to deterioration. Nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-08-20 | c | 0.045555 | 0.0027819 | 2016 | 2015-08-20 | C | 920 | 0.045555 | 0.0027819
7029023 | 2015-09-04 09:43 | 2015-09-04 13:45 | 242.4833 | 128 | 31037.8667 | 242.4833 | 239.4833 | 0.093851 | 30653.8667 | 0.09269 | 0.00038704 | NAPA ID:11327 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC377 | Replace H/V Crossarms and Transformers at Various Sites. TC2918; TC2707; TC2865; TC2866 & TC2867. Various Sites, Puriri. W/O 10147831. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-09-04 | b | 0.046345 | 0.00019352 | 2016 | 2015-09-04 | B | 128 | 0.09269 | 0.00038704
7031703 | 2015-09-22 09:01 | 2015-09-22 15:00 | 359.1 | 56 | 20109.6 | 359.1 | 356.1 | 0.060807 | 19941.6 | 0.060299 | 0.00016933 | NAPA ID:11838 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T25 | Replace crossarms only on pole P45775. Poles for complete replacement are: P45778, P45779, P45783, P45784, P47106, P47107, P47108, P47109, P47110. Works location: Hinemoa Valley Rd & Mangaone Valley Rd, Pahiatua. WO 10147215 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-22 | b | 0.030149 | 8.4665e-05 | 2016 | 2015-09-22 | B | 56 | 0.060299 | 0.00016933
7034528 | 2015-08-19 12:41 | 2015-08-19 13:13 | 32 | 170 | 5440 | 32 | 29 | 0.016449 | 4930 | 0.014907 | 0.00051404 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 7 Tripped C ph O/C E/F L/O - no fault found while sectionalising even with another trip after feeder reinstated - feeder left partly offloaded to help isolate fault. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.014907 | 0.00051404 | 2016 | 2015-08-19 | C | 170 | 0.014907 | 0.00051404
7039806 | 2015-08-19 14:47 | 2015-08-19 16:07 | 80 | 826 | 37424 | 45.3075 | 42.3075 | 0.11316 | 34946 | 0.10567 | 0.0024976 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 7 tripped. This was possibly due to lightning. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-08-19 | c | 0.10567 | 0.0024976 | 2016 | 2015-08-19 | C | 826 | 0.10567 | 0.0024976
7040751 | 2015-09-07 22:04 | 2015-09-08 00:40 | 156.2833 | 278 | 41437.1833 | 149.0546 | 146.0546 | 0.1253 | 40603.1833 | 0.12277 | 0.00084061 | NAPA ID:12065 TP_WAIKINO GXP > PAEROA SUB > WILLOUGHBY ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2512 | TO RE ATTACH REPAIRED 11KV CABLE TO "T" BLADE TRANSF TC3719. Works location: Towers St, Paeroa. WO 10210882 | F2 | WILLOUGHBY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-09-07 | b | 0.061387 | 0.0004203 | 2016 | 2015-09-07 | B | 278 | 0.12277 | 0.00084061
7042673 | 2015-08-20 17:24 | 2015-08-20 19:40 | 136.4 | 1 | 136.4 | 136.4 | 133.4 | 0.00041244 | 133.4 | 0.00040337 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6354 | 2nd 1 R to be sorted out at invoicing. HV Fuse blew on reliving. LV removed from transformer reloaded HV fuses in & holding. All LV restored and fuses holding. 2x3amp HV fuse elements. Old piggery still connected to supply, 20years old may need to be disc | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-20 | c | 0.00040337 | 3.024e-06 | 2016 | 2015-08-20 | C | 1 | 0.00040337 | 3.0238e-06
7043129 | 2015-08-20 19:57 | 2015-08-20 21:09 | 71.8667 | 2 | 143.7333 | 71.8667 | 68.8667 | 0.00043462 | 137.7333 | 0.00041647 | 6.0475e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4348T | 1 HV fuse blown at Transformer Reloaded & Livened. 2AMP HV FUSE 4348 T POLE 730436. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-20 | c | 0.00041647 | 6.048e-06 | 2016 | 2015-08-20 | C | 2 | 0.00041647 | 6.0475e-06
7044431 | 2015-08-20 03:36 | 2015-08-20 06:20 | 164 | 664 | 46605 | 70.1883 | 67.1883 | 0.14092 | 44613 | 0.1349 | 0.0020078 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P33198 | Line sectionalised and patrolled found lines down @ pole P33198 section of Sanson 8 and Sanson 6 being back fed due to network constraints at time of tripping. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-08-20 | c | 0.1349 | 0.0020078 | 2016 | 2015-08-20 | C | 664 | 0.1349 | 0.0020078
7046568 | 2015-09-07 08:51 | 2015-09-07 16:01 | 429.95 | 477 | 34034.85 | 71.3519 | 68.3519 | 0.10291 | 32603.85 | 0.098586 | 0.0014423 | NAPA ID:11551 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SA2-003 | 11kV Reconductor. Works location: Emerton Rd, Waihi Beach. WO 30002363 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-09-07 | b | 0.049293 | 0.00072117 | 2016 | 2015-09-07 | B | 477 | 0.098586 | 0.0014423
7047034 | 2015-09-08 14:05 | 2015-09-08 14:45 | 40 | 4 | 160 | 40 | 37 | 0.0004838 | 148 | 0.00044752 | 1.2095e-05 | NAPA ID:11187 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC208 | Install a 400V Fuse/Disconnector. Works location: Taukoro Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 0.00022376 | 6.048e-06 | 2016 | 2015-09-08 | B | 4 | 0.00044752 | 1.2095e-05
7047063 | 2015-09-16 08:45 | 2015-09-16 11:45 | 180 | 6 | 1080 | 180 | 177 | 0.0032657 | 1062 | 0.0032112 | 1.8143e-05 | NAPA ID:11758 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV links T33 | tree cutting near 11kv lines. Works location: Woodville Aohanga Rd. PPPD 46954 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-16 | b | 0.0016056 | 9.071e-06 | 2016 | 2015-09-16 | B | 6 | 0.0032112 | 1.8143e-05
7047156 | 2015-08-21 10:50 | 2015-08-21 12:25 | 94.7333 | 2 | 189.4667 | 94.7333 | 91.7333 | 0.0005729 | 183.4667 | 0.00055476 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1903 | 2x HV 11A Transformer Fuses | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-08-21 | c | 0.00055476 | 6.048e-06 | 2016 | 2015-08-21 | C | 2 | 0.00055476 | 6.0475e-06
7048216 | 2015-09-08 18:00 | 2015-09-08 20:52 | 171.55 | 137 | 23168.6 | 169.1139 | 166.1139 | 0.070056 | 22757.6 | 0.068814 | 0.00041426 | NAPA ID:12274 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | U0489 | Install Temporary links at pole U0489. Works location: Tairua Rd, Hikuai. WO 10148351 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 0.034407 | 0.00020713 | 2016 | 2015-09-08 | B | 137 | 0.068814 | 0.00041426
7049062 | 2015-09-09 14:00 | 2015-09-09 14:14 | 14 | 6 | 84 | 14 | 11 | 0.000254 | 66 | 0.00019957 | 1.8143e-05 | NAPA ID:11190 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5287 | To install a 400V Fuse/Disconnector. Works location: Taukoro Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-09 | b | 9.9784e-05 | 9.071e-06 | 2016 | 2015-09-09 | B | 6 | 0.00019957 | 1.8143e-05
7049207 | 2015-09-08 12:20 | 2015-09-08 12:40 | 20 | 1 | 20 | 20 | 17 | 6.0475e-05 | 17 | 5.1404e-05 | 3.0238e-06 | NAPA ID:11186 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC849 | To install a 400V Fuse/Disconnector. Works location: Taukoro Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 2.5702e-05 | 1.512e-06 | 2016 | 2015-09-08 | B | 1 | 5.1404e-05 | 3.0238e-06
7049322 | 2015-09-08 10:30 | 2015-09-08 10:56 | 26 | 8 | 208 | 26 | 23 | 0.00062894 | 184 | 0.00055637 | 2.419e-05 | NAPA ID:11185 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2227 | To install av 400V Fuse/Disconnector. Works location: Tahuna Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-08 | b | 0.00027819 | 1.2095e-05 | 2016 | 2015-09-08 | B | 8 | 0.00055637 | 2.419e-05
7049350 | 2015-09-09 08:45 | 2015-09-09 10:07 | 82 | 9 | 738 | 82 | 79 | 0.0022315 | 711 | 0.0021499 | 2.7214e-05 | NAPA ID:11986 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2229 | Replace faulty low voltage cross arm and install L/V Isolators. Works location: Hwy 27. WO 30002943 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-09-09 | b | 0.0010749 | 1.3607e-05 | 2016 | 2015-09-09 | B | 9 | 0.0021499 | 2.7214e-05
7049471 | 2015-09-09 10:00 | 2015-09-09 10:18 | 18 | 1 | 18 | 18 | 15 | 5.4428e-05 | 15 | 4.5356e-05 | 3.0238e-06 | NAPA ID:11188 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC817 | Install a 400V Fuse/Disconector. Works location: Taukoro Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-09 | b | 2.2678e-05 | 1.512e-06 | 2016 | 2015-09-09 | B | 1 | 4.5356e-05 | 3.0238e-06
7049816 | 2015-09-09 12:00 | 2015-09-09 12:21 | 21 | 6 | 126 | 21 | 18 | 0.00038099 | 108 | 0.00032657 | 1.8143e-05 | NAPA ID:11189 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC705 | Install a 400V Fuse/Disconnector. Works location: Taukoro Rd. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-09 | b | 0.00016328 | 9.071e-06 | 2016 | 2015-09-09 | B | 6 | 0.00032657 | 1.8143e-05
7051132 | 2015-08-21 17:01 | 2015-08-21 17:05 | 3.4 | 1 | 3.4 | 3.4 | 0.4 | 1.0281e-05 | 0 | 0 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 10012 | Faultman out on other call out also found 2x HT Fuses down at Fuses 10012, Authorised to reload, reliven. Outage due to big bird. Unknown how long fuses were blown for, found by chance. ASW | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-08-21 | c | 0 | 3.024e-06 | 2016 | 2015-08-21 | C | 1 | 0 | 3.0238e-06
7051947 | 2015-08-22 01:06 | 2015-08-22 04:22 | 196.5833 | 163 | 32043.0833 | 196.5833 | 193.5833 | 0.096891 | 31554.0833 | 0.095412 | 0.00049287 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 388443 | Fire comms reporting car vs pole, police also onsite F1903737 P022257048. ETA required for fire comms - 09 486 7948. Svs hub advise 20min ETA, fire comms advised. Pole replaced. Isolated at Recloser 9503/2, links 9503/6 ABS 9503/1 ABS IP530. No Back feeds | F3 | MATAPIHI RD | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-08-22 | c | 0.095412 | 0.00049287 | 2016 | 2015-08-22 | C | 163 | 0.095412 | 0.00049287
7052322 | 2015-08-22 06:36 | 2015-08-22 09:05 | 149.0333 | 108 | 9522.6667 | 88.1728 | 85.1728 | 0.028794 | 9198.6667 | 0.027815 | 0.00032657 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771834 | Reports of part power found fuses 1257 tripped. (Supplies Waverley Beach / Waipipi Subdivision). One Conductor found down and a broken jumper at Pole 771835. Repairs carried out with conductor rejoined and one Jumper repaired - relivened OK. (Isolation fr | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-08-22 | c | 0.027815 | 0.00032657 | 2016 | 2015-08-22 | C | 108 | 0.027815 | 0.00032657
7052752 | 2015-08-21 15:58 | 2015-08-22 16:00 | 1442.05 | 418 | 19033.1167 | 45.5338 | 42.5338 | 0.057552 | 17779.1167 | 0.05376 | 0.0012639 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | C025 | Car vs pole ETA Required People trapped. Feeder Opened under instruction from Fire Service. F1903799. Isolation at ABS 2111, ABS 649. Back feed from sectionalizer 9705 WLN CB 4 Transformer TC174 isolated to isolate LV, Pole Pulled clear of HV. Feeder Rel | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-21 | c | 0.05376 | 0.0012639 | 2016 | 2015-08-21 | C | 418 | 0.05376 | 0.0012639
7053823 | 2015-08-22 12:16 | 2015-08-22 13:04 | 47.6833 | 26 | 1239.7667 | 47.6833 | 44.6833 | 0.0037488 | 1161.7667 | 0.0035129 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X4001 | Outage required on transformer X4001 to replace a broken DDO holder. Isolation between ABS 1078, 1499 and 184 with backfeed at ABS 2590. Relivened OK. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-22 | c | 0.0035129 | 7.8618e-05 | 2016 | 2015-08-22 | C | 26 | 0.0035129 | 7.8618e-05
7054097 | 2015-08-22 11:04 | 2015-08-22 12:04 | 59.75 | 1 | 59.75 | 59.75 | 56.75 | 0.00018067 | 56.75 | 0.0001716 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | p21382 | 11.05am called hub to advise 999 p21382 make safe a stay wire - tied it up on the stud pole. close to 11kv will need to repaired amber defecting - FM advised will get back to it when there is a 11 kv shutdown in the area. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-08-22 | c | 0.0001716 | 3.024e-06 | 2016 | 2015-08-22 | C | 1 | 0.0001716 | 3.0238e-06
7054545 | 2015-08-22 08:17 | 2015-08-22 08:55 | 38.2667 | 1 | 38.2667 | 38.2667 | 35.2667 | 0.00011571 | 35.2667 | 0.00010664 | 3.0238e-06 |  | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TP2326 | NAPA ID 11791 to remove redundant transformer | F2 | PAPAMOA JUNCTION | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-08-22 | b | 5.3319e-05 | 1.512e-06 | 2016 | 2015-08-22 | B | 1 | 0.00010664 | 3.0238e-06
7054831 | 2015-08-22 19:58 | 2015-08-23 12:50 | 1012 | 2 | 2024 | 1012 | 1009 | 0.0061201 | 2018 | 0.0061019 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6354 | James Kennerley attended this fault earlier in the week. There is an old circuit that feeds an old piggery which is not being used. It crosses over a waterway where there are some ducks in the area. He has talked to the owners of the old piggery and they | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-22 | c | 0.0061019 | 6.048e-06 | 2016 | 2015-08-22 | C | 2 | 0.0061019 | 6.0475e-06
7055642 | 2015-08-23 09:36 | 2015-08-23 10:39 | 63.2 | 677 | 34985.6833 | 51.6775 | 48.6775 | 0.10579 | 32954.6833 | 0.099647 | 0.0020471 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | S61 | CB S61 tripped on E/F flags, line patrolled and sectionalised and no fault was found, faultman suspect duck strike. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-23 | c | 0.099647 | 0.0020471 | 2016 | 2015-08-23 | C | 677 | 0.099647 | 0.0020471
7057495 | 2015-08-23 11:53 | 2015-08-23 11:54 | 1 | 322 | 322 | 1 | -2 | 0.00097365 | 0 | 0 | 0.00097365 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 23 | CB 23 auto reclosed on A, B & C phase O/C flags, line was patrolled and no fault was found by faultman. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-08-23 | c | 0 | 0.00097365 | 2016 | 2015-08-23 | C | 322 | 0 | 0.00097365
7058071 | 2015-08-23 15:26 | 2015-08-23 18:05 | 158.7667 | 16 | 2540.2667 | 158.7667 | 155.7667 | 0.0076812 | 2492.2667 | 0.007536 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738475 | Faultman found a broken conductor at Fuses 6113, line was isolated at Fuses 4943 to repair the conductor at pole 738475. 1 X squirrel sleeve used. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-08-23 | c | 0.007536 | 4.838e-05 | 2016 | 2015-08-23 | C | 16 | 0.007536 | 4.838e-05
7058863 | 2015-08-23 17:47 | 2015-08-23 18:58 | 70.8167 | 2 | 141.6333 | 70.8167 | 67.8167 | 0.00042827 | 135.6333 | 0.00041012 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5683 | Reloaded-Relivened 2x DDO's at Transformer TC5683. Caused by Magpie - was sitting on top of transformer. Perry Hicks Attended. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-08-23 | c | 0.00041012 | 6.048e-06 | 2016 | 2015-08-23 | C | 2 | 0.00041012 | 6.0475e-06
7058897 | 2015-08-23 17:50 | 2015-08-23 18:44 | 53.65 | 30 | 1609.5 | 53.65 | 50.65 | 0.0048667 | 1519.5 | 0.0045946 | 9.0713e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224216 | Jumper found blown off at Pole 224216. Rejoined 1 x connector. Isolation between ABS's SE5-021 and SE6-052. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-23 | c | 0.0045946 | 9.0713e-05 | 2016 | 2015-08-23 | C | 30 | 0.0045946 | 9.0713e-05
7058932 | 2015-08-23 18:08 | 2015-08-23 19:40 | 91.65 | 13 | 1191.45 | 91.65 | 88.65 | 0.0036027 | 1152.45 | 0.0034847 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | E93 | 2 HT Fuses reloaded at E93. Bird Strike. | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-23 | c | 0.0034847 | 3.9309e-05 | 2016 | 2015-08-23 | C | 13 | 0.0034847 | 3.9309e-05
7058986 | 2015-08-23 18:34 | 2015-08-24 01:59 | 444.55 | 25 | 6976.7833 | 279.0713 | 276.0713 | 0.021096 | 6901.7833 | 0.020869 | 7.5594e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758863 | Initially found one HT fuse blown at 5348. Tripped on relivenmeing. Unable to locate any obvious faults beyond these fuse. (2 Lightning arrestors were cut away but fuse still tripped). All transformers offloaded but fuse trippeed once again. A temp line | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-08-23 | c | 0.020869 | 7.5594e-05 | 2016 | 2015-08-23 | C | 25 | 0.020869 | 7.5594e-05
7059500 | 2015-08-24 00:34 | 2015-08-24 05:15 | 281.3333 | 6 | 1688 | 281.3333 | 278.3333 | 0.0051041 | 1670 | 0.0050497 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC265 | at 00:33, Farmer Rd Sub, CB 6 Tatuanui Feeder. Faultman called to no power and loud bang outside house. Found transformer TC265 had faulted. Own Isolation & AP issued. Transformer Replaced. All Power Restored on Completion. Perry Hicks Attended. 1x Transf | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-08-24 | c | 0.0050497 | 1.8143e-05 | 2016 | 2015-08-24 | C | 6 | 0.0050497 | 1.8143e-05
7059641 | 2015-08-24 08:07 | 2015-08-24 11:36 | 208.8167 | 25 | 5220.4167 | 208.8167 | 205.8167 | 0.015785 | 5145.4167 | 0.015559 | 7.5594e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5348 | 7059636 & 7059629 & 7063928- plz check if related. Ongoing intermittant fault. 1 fuse blown again at 5348. Suspected possibly faulty insulator or likely given amount of recent rain. Line isolated at 5348, AP issued to erect new set of fuses at pole 758833 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-08-24 | c | 0.015559 | 7.5594e-05 | 2016 | 2015-08-24 | C | 25 | 0.015559 | 7.5594e-05
7064125 | 2015-09-09 09:53 | 2015-09-09 15:34 | 341.35 | 30 | 10230.7 | 341.0233 | 338.0233 | 0.030935 | 10140.7 | 0.030663 | 9.0713e-05 | NAPA ID:11949 TP_OPUNAKE GXP > TASMAN SUB > OPUNAKE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6681 | Install cross arms and replace rusty ABS TA232. Works location: Beach Rd, Opunake. WO 10195568 | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-09-09 | b | 0.015332 | 4.5356e-05 | 2016 | 2015-09-09 | B | 30 | 0.030663 | 9.0713e-05
7064824 | 2015-08-24 08:41 | 2015-08-24 08:43 | 1.8 | 775 | 1395 | 1.8 | -1.2 | 0.0042181 | 0 | 0 | 0.0023434 |  | 11 | Unplanned | UNDERGROUND CABLE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 6 | during planned switching ( napa 11264 ) an operation ( item 5 ) was missed which lead to TMA CB6 tripping. After discussion with field staff all service restored. | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-08-24 | c | 0 | 0.0023434 | 2016 | 2015-08-24 | C | 775 | 0 | 0.0023434
7065658 | 2015-09-11 10:15 | 2015-09-11 10:36 | 21 | 2 | 42 | 21 | 18 | 0.000127 | 36 | 0.00010886 | 6.0475e-06 | NAPA ID:11191 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2207 | To install a 400V Fuse/Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-11 | b | 5.4428e-05 | 3.024e-06 | 2016 | 2015-09-11 | B | 2 | 0.00010886 | 6.0475e-06
7065926 | 2015-09-11 12:00 | 2015-09-11 12:22 | 22 | 6 | 132 | 22 | 19 | 0.00039914 | 114 | 0.00034471 | 1.8143e-05 | NAPA ID:11192 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6000 | To install a 400V Fuse/Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-11 | b | 0.00017235 | 9.071e-06 | 2016 | 2015-09-11 | B | 6 | 0.00034471 | 1.8143e-05
7065958 | 2015-09-11 14:07 | 2015-09-11 14:27 | 20 | 7 | 140 | 20 | 17 | 0.00042333 | 119 | 0.00035983 | 2.1166e-05 | NAPA ID:11193 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2563 | To install a 400V Fues/Disconnector. Works location: Grayden Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-11 | b | 0.00017991 | 1.0583e-05 | 2016 | 2015-09-11 | B | 7 | 0.00035983 | 2.1166e-05
7065966 | 2015-09-10 09:40 | 2015-09-10 11:43 | 123 | 6 | 738 | 123 | 120 | 0.0022315 | 720 | 0.0021771 | 1.8143e-05 | NAPA ID:12240 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2070 | Raise Transformer & cross arms to meet Powerco Standards - Safety issue. Works location: Scotsman Valley Rd, Kiwitahi. WO 30003283 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.0010886 | 9.071e-06 | 2016 | 2015-09-10 | B | 6 | 0.0021771 | 1.8143e-05
7074116 | 2015-09-15 10:00 | 2015-09-15 10:35 | 35 | 6 | 210 | 35 | 32 | 0.00063499 | 192 | 0.00058056 | 1.8143e-05 | NAPA ID:11194 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1892 | To,install a 400V Fuse/Disconnector. Works location: Taukoro Rd, Morrisnville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00029028 | 9.071e-06 | 2016 | 2015-09-15 | B | 6 | 0.00058056 | 1.8143e-05
7074135 | 2015-09-15 12:00 | 2015-09-15 12:35 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 | NAPA ID:11195 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4218 | To install a 400V Fuse Disconnector. Works location: Grayden Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00019352 | 6.048e-06 | 2016 | 2015-09-15 | B | 4 | 0.00038704 | 1.2095e-05
7075309 | 2015-09-09 09:05 | 2015-09-09 15:10 | 365.2167 | 35 | 12782.5833 | 365.2167 | 362.2167 | 0.038651 | 12677.5833 | 0.038334 | 0.00010583 | NAPA ID:11601 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-042 | Replace H/V crossarms at various locations. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-09-09 | b | 0.019167 | 5.2916e-05 | 2016 | 2015-09-09 | B | 35 | 0.038334 | 0.00010583
7075841 | 2015-09-15 14:00 | 2015-09-15 14:35 | 35 | 13 | 455 | 35 | 32 | 0.0013758 | 416 | 0.0012579 | 3.9309e-05 | NAPA ID:11196 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC564 | To install a 400V Fuse/Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00062894 | 1.9654e-05 | 2016 | 2015-09-15 | B | 13 | 0.0012579 | 3.9309e-05
7075859 | 2015-09-15 10:00 | 2015-09-15 10:16 | 16 | 6 | 96 | 16 | 13 | 0.00029028 | 78 | 0.00023585 | 1.8143e-05 | NAPA ID:11197 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC730 | To install a 400V Fuse Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00011793 | 9.071e-06 | 2016 | 2015-09-15 | B | 6 | 0.00023585 | 1.8143e-05
7075871 | 2015-09-15 12:00 | 2015-09-15 12:19 | 19 | 4 | 76 | 19 | 16 | 0.00022981 | 64 | 0.00019352 | 1.2095e-05 | NAPA ID:11198 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1363 | to install a 400V Fuse/Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 9.676e-05 | 6.048e-06 | 2016 | 2015-09-15 | B | 4 | 0.00019352 | 1.2095e-05
7075881 | 2015-09-15 14:00 | 2015-09-15 14:19 | 19 | 4 | 76 | 19 | 16 | 0.00022981 | 64 | 0.00019352 | 1.2095e-05 | NAPA ID:11199 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC292 | To install a 400V Fuse/Disconnector. Works location: Hangawera Rd, Morrinsville. WO 10147849 | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 9.676e-05 | 6.048e-06 | 2016 | 2015-09-15 | B | 4 | 0.00019352 | 1.2095e-05
7076078 | 2015-09-13 09:30 | 2015-09-13 13:31 | 241 | 26 | 6266 | 241 | 238 | 0.018947 | 6188 | 0.018711 | 7.8618e-05 | NAPA ID:11753 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 4 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 182 | Replace ABS427 Pole & Xarms. Replace ABS217 & Xarms. Works location: Breakwater Rd, New Plymouth. WO 10179679 | F4 | MOTUROA 4 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-13 | b | 0.0093555 | 3.9309e-05 | 2016 | 2015-09-13 | B | 26 | 0.018711 | 7.8618e-05
7076270 | 2015-09-15 09:24 | 2015-09-15 13:12 | 228 | 57 | 12996 | 228 | 225 | 0.039297 | 12825 | 0.03878 | 0.00017235 | NAPA ID:11517 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV NG202 | Replace ABS NG240 and Xarms at pole 711460. Works location: South Rd, Opunake. WO 10159896 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.01939 | 8.6177e-05 | 2016 | 2015-09-15 | B | 57 | 0.03878 | 0.00017235
7076464 | 2015-09-15 08:45 | 2015-09-15 15:20 | 395.3 | 75 | 29647.5 | 395.3 | 392.3 | 0.089647 | 29422.5 | 0.088967 | 0.00022678 | NAPA ID:11944 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5538 | Pole & cross arm replacement as part of the PowerCo IR750 Mountain Road pole renewal w/o 523369 . Shudown 1 ]Will be starting work from pole 761638 to pole 761616. Works location: Mountain Rd, Inglewood. WO 30001178. | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.044483 | 0.00011339 | 2016 | 2015-09-15 | B | 75 | 0.088967 | 0.00022678
7076533 | 2015-09-17 08:45 | 2015-09-17 15:13 | 387.8 | 75 | 29085 | 387.8 | 384.8 | 0.087946 | 28860 | 0.087266 | 0.00022678 | NAPA ID:11958 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5538 | Pole & cross arm replacement as part of the PowerCo IR750 Mountain Road pole renewal w/o 523369 . Shudown 2 ]Will be starting work from pole 761616 to pole 761604. Works location: Mountain Rd, Inglewood. WO 30001178 | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-09-17 | b | 0.043633 | 0.00011339 | 2016 | 2015-09-17 | B | 75 | 0.087266 | 0.00022678
7076571 | 2015-09-30 08:53 | 2015-09-30 15:24 | 390.8667 | 75 | 29315 | 390.8667 | 387.8667 | 0.088642 | 29090 | 0.087961 | 0.00022678 | NAPA ID:11961 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5538 | Pole & cross arm replacement as part of the PowerCo IR750 Mountain Road pole renewal w/o 523369 . Shudown 3 Will be starting work from pole 761602 to pole 761574. Works location: Mountain Rd, Inglewood. WO 30001178 | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-09-30 | b | 0.043981 | 0.00011339 | 2016 | 2015-09-30 | B | 75 | 0.087961 | 0.00022678
7076650 | 2015-09-16 14:00 | 2015-09-16 14:45 | 45 | 6 | 270 | 45 | 42 | 0.00081642 | 252 | 0.00076199 | 1.8143e-05 | NAPA ID:11557 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2210 | To install a 400V Fuse/Disconnector. Works location: Morrinsville Walton Rd, Morrinsville. WO 10147849 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-16 | b | 0.00038099 | 9.071e-06 | 2016 | 2015-09-16 | B | 6 | 0.00076199 | 1.8143e-05
7076675 | 2015-09-11 12:30 | 2015-09-11 13:00 | 30 | 3 | 90 | 30 | 27 | 0.00027214 | 81 | 0.00024492 | 9.0713e-06 | NAPA ID:11561 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1936 | To install a 400V Fuse/Disconnector. Works location: Bolton Rd, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-11 | b | 0.00012246 | 4.536e-06 | 2016 | 2015-09-11 | B | 3 | 0.00024492 | 9.0713e-06
7076810 | 2015-09-10 08:46 | 2015-09-10 14:57 | 370.7 | 42 | 15569.4 | 370.7 | 367.7 | 0.047078 | 15443.4 | 0.046697 | 0.000127 | NAPA ID:11398 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP183 | Replace poles hardware and conductor between poles 212269 - 212233. Works location: OManawa Rd. WO 30002540 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.023349 | 6.3499e-05 | 2016 | 2015-09-10 | B | 42 | 0.046697 | 0.000127
7086448 | 2015-08-24 14:52 | 2015-08-24 18:12 | 199.5167 | 1259 | 74354.65 | 59.0585 | 56.0585 | 0.22483 | 70577.65 | 0.21341 | 0.0038069 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/180 | CB 8 tripped on O/C flags, at time of tripping Recloser F48 close this is part of CB 8's auto backfeed system but Recloser F26 did not trip open it should this will be investigated on 25/08/15 by Tracey Hall, Recloser F26 was opened by NOC Control, receiv | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-24 | c | 0.21341 | 0.0038069 | 2016 | 2015-08-24 | C | 1259 | 0.21341 | 0.0038069
7090562 | 2015-08-25 08:43 | 2015-08-25 12:46 | 243.3 | 74 | 10135.6 | 136.9676 | 133.9676 | 0.030648 | 9913.6 | 0.029976 | 0.00022376 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780 | Main Line down broken off insulator - hanging over driveway and hedge. 8.43am advised Tallia at svs hub & control. Please check if OMS7090653 664 Upper Pitone Road affected. 7090585, 7090653, 7090699, 7090733,7090767.7090928,7090943. 11kV line down at pol | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-08-25 | c | 0.029976 | 0.00022376 | 2016 | 2015-08-25 | C | 74 | 0.029976 | 0.00022376
7091777 | 2015-09-01 08:49 | 2015-09-01 17:05 | 496 | 63 | 12429 | 197.2857 | 194.2857 | 0.037582 | 12240 | 0.037011 | 0.0001905 | NAPA ID:11636 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB 11 | Change 20 x 11kv and 33kv xarms, change transformer T6/572. Job had a over run as weather was causing problems. | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-01 | b | 0.018505 | 9.5248e-05 | 2016 | 2015-09-01 | B | 63 | 0.037011 | 0.0001905
7092042 | 2015-09-04 09:01 | 2015-09-04 11:35 | 154.0333 | 17 | 2618.5667 | 154.0333 | 151.0333 | 0.0079179 | 2567.5667 | 0.0077637 | 5.1404e-05 | NAPA ID:11487 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | J56 | Replace DDO fuses J56 using live line. Repair damaged cable termination at T3/291. Please note transformer T3/291 will need to be off for the full 2hrs. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.0038819 | 2.5702e-05 | 2016 | 2015-09-04 | B | 17 | 0.0077637 | 5.1404e-05
7092091 | 2015-08-25 12:20 | 2015-08-25 18:31 | 371.05 | 163 | 60481.15 | 371.05 | 368.05 | 0.18288 | 59992.15 | 0.1814 | 0.00049287 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 708091 | Recloser 4897/2 tripped to L/O. O/C & E/F flags. 1 r requested initially then 2 r. Tree across line located at pole 708091. Line isolated at ABS 5288 & Links 4914 for repairs. Permission given to fault man to carry out isolation/earthing/issue self A/P du | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-08-25 | c | 0.1814 | 0.00049287 | 2016 | 2015-08-25 | C | 163 | 0.1814 | 0.00049287
7092587 | 2015-08-31 09:30 | 2015-08-31 15:56 | 386 | 80 | 30880 | 386 | 383 | 0.093374 | 30640 | 0.092648 | 0.0002419 | NAPA ID:12421 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V35 | Tree cutting near 11kV lines . Downer to replace 11kV cross arms and poles. Work location: Route 52, Pongaroa. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-08-31 | b | 0.046324 | 0.00012095 | 2016 | 2015-08-31 | B | 80 | 0.092648 | 0.0002419
7093134 | 2015-08-25 15:43 | 2015-08-25 17:07 | 84.3167 | 1 | 84.3167 | 84.3167 | 81.3167 | 0.00025495 | 81.3167 | 0.00024588 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7644 | replaced 2X10a HV fuses | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-08-25 | c | 0.00024588 | 3.024e-06 | 2016 | 2015-08-25 | C | 1 | 0.00024588 | 3.0238e-06
7093578 | 2015-08-25 18:30 | 2015-08-26 06:02 | 691.7833 | 95 | 26544.2833 | 279.4135 | 276.4135 | 0.080264 | 26259.2833 | 0.079402 | 0.00028726 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | K1006 | Corner of Matuku Road and Hangawera Road a truck hit the powerpole. (No tripping). 6.33pm advised Dianne at svs hub & control. Isolation required from ABS IC585 and recloser 9778/2. Repairs were carried out during the night with a pole and all associated | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-08-25 | c | 0.079402 | 0.00028726 | 2016 | 2015-08-25 | C | 95 | 0.079402 | 0.00028726
7093999 | 2015-08-25 22:40 | 2015-08-26 08:31 | 590.95 | 40 | 23638 | 590.95 | 587.95 | 0.071476 | 23518 | 0.071113 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P15962 | Faultman found Recloser U39 open, closed in once tripped, line could not be patrolled all, will return in morning as faultman can not see a large part of the line in the dark, goes cross country. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-08-25 | c | 0.071113 | 0.00012095 | 2016 | 2015-08-25 | C | 40 | 0.071113 | 0.00012095
7094337 | 2015-08-26 07:39 | 2015-08-26 13:50 | 370.95 | 340 | 36902.7667 | 108.5375 | 105.5375 | 0.11159 | 35882.7667 | 0.1085 | 0.0010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P3183 | Power lines down in forestry block, - tree has fallen and taken out lines P21380, 027 442 1100 Matt Nelson 11kV line- 7.49am 26/8 advised Ian control about this *** check if oms 7094773 - 16 Harrison Hill Road is part of this issue - Nick Lake knows abou | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-08-26 | c | 0.1085 | 0.0010281 | 2016 | 2015-08-26 | C | 340 | 0.1085 | 0.0010281
7095195 | 2015-08-26 09:53 | 2015-08-26 10:37 | 44.6833 | 1 | 44.6833 | 44.6833 | 41.6833 | 0.00013511 | 41.6833 | 0.00012604 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8295 | replace 2 x 10 hv links. cause: bird strike. link # 8295. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-26 | c | 0.00012604 | 3.024e-06 | 2016 | 2015-08-26 | C | 1 | 0.00012604 | 3.0238e-06
7095269 | 2015-08-26 10:10 | 2015-08-26 15:46 | 336.3667 | 647 | 70573.5 | 109.0781 | 106.0781 | 0.2134 | 68632.5 | 0.20753 | 0.0019564 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | G12433 | 11kV Recloser 9780 Opened for public safety due to Car V Pole on linked Job 7095149. Copied data from linked job for direct reference. Dallas from Fire Comms Auckland on 094867949. Car vs concrete pole, pole on a 45 degree lean.No lines down. Event # F190 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-08-26 | c | 0.20753 | 0.0019564 | 2016 | 2015-08-26 | C | 647 | 0.20753 | 0.0019564
7097006 | 2015-08-26 11:07 | 2015-08-26 15:36 | 268.7167 | 604 | 56080.4333 | 92.8484 | 89.8484 | 0.16957 | 54268.4333 | 0.16409 | 0.0018264 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 851600 | 11kV CB R21, Tripped E/F L/O. Truck V Pole, Bridge Place. Pole 851600 hit by vehicle. Pole not broken but broken crossarm & assembly replaced & 3 x damaged conductors restrained. 3 x 16mm Cu sleeves required and 2 x LV fuse bases also replaced. Isolation' | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-08-26 | c | 0.16409 | 0.0018264 | 2016 | 2015-08-26 | C | 604 | 0.16409 | 0.0018264
7098202 | 2015-08-26 13:00 | 2015-08-26 13:25 | 25.4 | 100 | 2540 | 25.4 | 22.4 | 0.0076804 | 2240 | 0.0067732 | 0.00030238 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C268/6 | oms 7097790 possibly relates. 1.28pm worked through control - sectionaliser 268 - replacing set of 3 DDO fuses & holders. 1.31pm 26/8 checked with Ian if ok to put 2R request on job as this is a mainline job now. all ok have sent through request. 2.51pm | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-08-26 | c | 0.0067732 | 0.00030238 | 2016 | 2015-08-26 | C | 100 | 0.0067732 | 0.00030238
7105619 | 2015-08-27 00:27 | 2015-08-27 09:24 | 537.3167 | 536 | 60392.1167 | 112.6719 | 109.6719 | 0.18261 | 58784.1167 | 0.17775 | 0.0016207 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | E1194 | LAK CB5 tripped A, B & C Ph O/C. Report of car v pole E1194, SH29. Isolation between ABS 2526 & ABS 803 ( lines down on car no back feeds in place until passengers clear ) CB5 returned to service & back feed via ABS 1356 ( BRN9 ) | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-08-27 | c | 0.17775 | 0.0016207 | 2016 | 2015-08-27 | C | 536 | 0.17775 | 0.0016207
7107884 | 2015-08-27 08:36 | 2015-08-27 14:11 | 335 | 110 | 18836 | 171.2364 | 168.2364 | 0.056956 | 18506 | 0.055958 | 0.00033261 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 3203 | Plz check if oms 7107896 20 Waiotahi Road no power affected tx TC5210. 8.33am advised Stewart - tree leaning on lines, up hill just onto waiotahi road on right hand side. Tree has come over and touched the 11KV ? needing electrical fitter to replace some | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-08-27 | c | 0.055958 | 0.00033261 | 2016 | 2015-08-27 | C | 110 | 0.055958 | 0.00033261
7107903 | 2015-08-27 06:26 | 2015-08-27 07:10 | 43.7 | 4 | 174.8 | 43.7 | 40.7 | 0.00052855 | 162.8 | 0.00049227 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7161 | No Power. Heard loud bang than power went out could be transformer. 6.30am advsied Joanne at svs hub of job & control. replace 2 x 10 amp hv fuses. suspect birds. fuse # 7161. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-08-27 | c | 0.00049227 | 1.2095e-05 | 2016 | 2015-08-27 | C | 4 | 0.00049227 | 1.2095e-05
7108176 | 2015-09-11 08:49 | 2015-09-11 15:13 | 384 | 3 | 1152 | 384 | 381 | 0.0034834 | 1143 | 0.0034562 | 9.0713e-06 | NAPA ID:11746 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Open & Tag SA2-003 | Re-conductor. Emerton Road, Waihi Beach. W/O 30002363. | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-09-11 | b | 0.0017281 | 4.536e-06 | 2016 | 2015-09-11 | B | 3 | 0.0034562 | 9.0713e-06
7108374 | 2015-09-24 08:46 | 2015-09-24 16:00 | 434.8 | 47 | 20435.6 | 434.8 | 431.8 | 0.061792 | 20294.6 | 0.061366 | 0.00014212 | NAPA ID:11521 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 726857 | Replacing pole's from 726857 to 726900. Wilson Road, Kakaramea. W/O 30001088. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-24 | b | 0.030683 | 7.1058e-05 | 2016 | 2015-09-24 | B | 47 | 0.061366 | 0.00014212
7112984 | 2015-09-10 10:43 | 2015-09-10 16:29 | 346.3167 | 12 | 4155.8 | 346.3167 | 343.3167 | 0.012566 | 4119.8 | 0.012457 | 3.6285e-05 | NAPA ID:12475 TP_HINUERA GXP > TIRAU SUB | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2092 | Gang 1: To replace SD3 2092, 2089, 2091. Gang 2: To replace 11kV Cross arms. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.0062286 | 1.8143e-05 | 2016 | 2015-09-10 | B | 12 | 0.012457 | 3.6285e-05
7113124 | 2015-09-29 14:14 | 2015-09-29 14:30 | 16 | 1 | 16 | 16 | 13 | 4.838e-05 | 13 | 3.9309e-05 | 3.0238e-06 | NAPA ID:11820 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TP 1725 | To install a 400V Fuse/Disconector. Paratu Road, Walton. W/O 10147849. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 1.9654e-05 | 1.512e-06 | 2016 | 2015-09-29 | B | 1 | 3.9309e-05 | 3.0238e-06
7113267 | 2015-08-27 14:00 | 2015-08-27 16:00 | 120.3 | 1 | 120.3 | 120.3 | 117.3 | 0.00036376 | 117.3 | 0.00035469 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/349 | 2.01pm - e-map update. 2x10 Amp Fuses and Carrier at Transformer T1/349. Reload Reliven | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-27 | c | 0.00035469 | 3.024e-06 | 2016 | 2015-08-27 | C | 1 | 0.00035469 | 3.0238e-06
7115824 | 2015-08-27 18:37 | 2015-08-27 20:17 | 99.5833 | 1 | 99.5833 | 99.5833 | 96.5833 | 0.00030112 | 96.5833 | 0.00029204 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7381 | replaced 2X 6a HV fuses | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-08-27 | c | 0.00029204 | 3.024e-06 | 2016 | 2015-08-27 | C | 1 | 0.00029204 | 3.0238e-06
7116177 | 2015-08-28 06:11 | 2015-08-28 07:25 | 73.7 | 9 | 663.3 | 73.7 | 70.7 | 0.0020057 | 636.3 | 0.001924 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7919 | 2 x 10 Amp fuses At FUSES 7919. Suspected duck Strike.Reload Reliven | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-08-28 | c | 0.001924 | 2.7214e-05 | 2016 | 2015-08-28 | C | 9 | 0.001924 | 2.7214e-05
7116407 | 2015-08-27 09:19 | 2015-08-27 14:51 | 332.3167 | 29 | 9637.1833 | 332.3167 | 329.3167 | 0.029141 | 9550.1833 | 0.028877 | 8.7689e-05 |  | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-057 | 7116407 was a recreation of OMS # 7108763 which was lost during an OMS fail over to Auckland. The Parent of this OMS 3# is 6651572. Napa10910 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-27 | b | 0.014439 | 4.3845e-05 | 2016 | 2015-08-27 | B | 29 | 0.028877 | 8.7689e-05
7116507 | 2015-08-28 11:35 | 2015-08-28 13:40 | 125.25 | 3 | 375.75 | 125.25 | 122.25 | 0.0011362 | 366.75 | 0.001109 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF5-003 | at 11:32, Atuaroa Sub, CB 2 No. 3 Rd. Found decommissioned O/H lines that had been tied off but were still in very close proximity to live 11kV Lines. Crossarms were also badly rotten at transformer structure TF5-003. Isolated Lines at Fuses SF5-055. Perm | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-08-28 | c | 0.001109 | 9.071e-06 | 2016 | 2015-08-28 | C | 3 | 0.001109 | 9.0713e-06
7116532 | 2015-09-29 09:40 | 2015-09-29 13:00 | 200 | 3 | 600 | 200 | 197 | 0.0018143 | 591 | 0.001787 | 9.0713e-06 | NAPA ID:11809 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC 781 | To replace 11kV Fuses TC1079. Install a 400V Fuse Disconector. Morrinsville-Walton Road, Piako. W/O 10147849. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 0.00089352 | 4.536e-06 | 2016 | 2015-09-29 | B | 3 | 0.001787 | 9.0713e-06
7117839 | 2015-08-28 13:18 | 2015-08-28 18:05 | 286.8667 | 1 | 286.8667 | 286.8667 | 283.8667 | 0.00086742 | 283.8667 | 0.00085834 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2227T and 733458 | Actually Tawhiti Road North. transformer blew up. 15kv transformer. tx 2227T. pole 733458. only feeds a pump. man on line sign, did not disconnect. will be replaced today or tomorrow. Replaced Transformer All back on at 18:05 | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-08-28 | c | 0.00085835 | 3.024e-06 | 2016 | 2015-08-28 | C | 1 | 0.00085834 | 3.0238e-06
7121513 | 2015-08-28 19:49 | 2015-08-28 23:31 | 221.7667 | 1 | 221.7667 | 221.7667 | 218.7667 | 0.00067057 | 218.7667 | 0.0006615 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 795346 | Found 3 fuses blown checked transformer and all appeared to be ok Terain not conducive to line patrol in the dark so replaced two fuses and they blew. Customer advised the faultman he was happy for the power to remain off until daylight when a patrol can | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-08-28 | c | 0.0006615 | 3.024e-06 | 2016 | 2015-08-28 | C | 1 | 0.0006615 | 3.0238e-06
7121946 | 2015-08-29 09:56 | 2015-08-29 11:03 | 67.2667 | 19 | 1278.0667 | 67.2667 | 64.2667 | 0.0038646 | 1221.0667 | 0.0036922 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7-064 | at 09:56, Pongakawa Sub, CB 1 Tainui Feeder. Faulman called out to No Power Job. Found blown jumper and broken DOO at Fuses SE7-064. Isolated lines at Fuses SE7-032. Permit issued & repairs carried out. All Power Restored on Completion. Replaced 1x DDO Ho | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-08-29 | c | 0.0036922 | 5.7451e-05 | 2016 | 2015-08-29 | C | 19 | 0.0036922 | 5.7451e-05
7121963 | 2015-08-29 08:02 | 2015-08-29 09:20 | 77.5833 | 10 | 775.8333 | 77.5833 | 74.5833 | 0.0023459 | 745.8333 | 0.0022552 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | FC2464 | Stu Simpson Attended. Reloaded, Relivened 2x HV Fuses at Fuses FC2464. Unknown Cause (Did not find anything but suspects maybe a bird). All OK. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-08-29 | c | 0.0022552 | 3.0238e-05 | 2016 | 2015-08-29 | C | 10 | 0.0022552 | 3.0238e-05
7122724 | 2015-08-29 11:54 | 2015-08-29 13:31 | 96.9167 | 9 | 872.25 | 96.9167 | 93.9167 | 0.0026375 | 845.25 | 0.0025558 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8295 | Replaced 2x 8 Amp Links. Dead Goose found | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-29 | c | 0.0025558 | 2.7214e-05 | 2016 | 2015-08-29 | C | 9 | 0.0025558 | 2.7214e-05
7124920 | 2015-08-29 21:55 | 2015-08-29 23:11 | 76.0333 | 348 | 18745.1833 | 53.8655 | 50.8655 | 0.056681 | 17701.1833 | 0.053524 | 0.0010523 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6616 | RS 6616 tripped and locked out on E/F. No Fault found while sectionalising.Paul Comes up as Eltham sub. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-29 | c | 0.053524 | 0.0010523 | 2016 | 2015-08-29 | C | 348 | 0.053524 | 0.0010523
7125276 | 2015-08-29 22:05 | 2015-08-29 22:25 | 20.2667 | 414 | 2605.35 | 6.2931 | 3.2931 | 0.007878 | 1363.35 | 0.0041224 | 0.0012518 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 205277 | Reload at fuses SC2-126 caused feeder to trip. Line patrolled & possum found on top of double arms at pole 205277. Removed possum by hot stick, fuses SC2-126 reloaded. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-08-29 | c | 0.0041224 | 0.0012518 | 2016 | 2015-08-29 | C | 414 | 0.0041224 | 0.0012518
7126140 | 2015-08-29 23:21 | 2015-08-30 01:10 | 109.4333 | 348 | 6982.7667 | 20.0654 | 17.0654 | 0.021114 | 5938.7667 | 0.017957 | 0.0010523 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761655 | Broken Isolator found at Pole 761655 during sectionlising - Isolated at Fuses 5516 - Isolator replaced - used 1 x pin & insulator. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-08-29 | c | 0.017957 | 0.0010523 | 2016 | 2015-08-29 | C | 348 | 0.017957 | 0.0010523
7126879 | 2015-08-30 02:18 | 2015-08-30 05:33 | 195.45 | 291 | 17080.45 | 58.6957 | 55.6957 | 0.051647 | 16207.45 | 0.049007 | 0.00087991 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844107 | Floating Conductor found at Pole 844107 during sectionlising - Isolated at ABS 2846 & Links 2536 - Floater repaired - used 1x binder | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-08-30 | c | 0.049007 | 0.00087991 | 2016 | 2015-08-30 | C | 291 | 0.049007 | 0.00087991
7129834 | 2015-08-30 05:36 | 2015-08-30 10:16 | 279.3833 | 3 | 838.15 | 279.3833 | 276.3833 | 0.0025344 | 829.15 | 0.0025072 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2-084 | Transformer TC2-084 faulty. Replaced | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-08-30 | c | 0.0025072 | 9.071e-06 | 2016 | 2015-08-30 | C | 3 | 0.0025072 | 9.0713e-06
7129874 | 2015-08-30 06:37 | 2015-08-30 07:32 | 55.1833 | 8 | 441.4667 | 55.1833 | 52.1833 | 0.0013349 | 417.4667 | 0.0012623 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8181 | Replaced 2x 15Amp Links. Suspect Birdstrike | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-08-30 | c | 0.0012623 | 2.419e-05 | 2016 | 2015-08-30 | C | 8 | 0.0012623 | 2.419e-05
7130001 | 2015-08-30 08:18 | 2015-08-30 08:33 | 15 | 704 | 10560 | 15 | 12 | 0.031931 | 8448 | 0.025545 | 0.0021287 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 9516 | Recloser 9516 Trip. E/F. L/O. Recloser after 15min ok. Lines patrolled nothing found. Lots of pigeons around. Suspect bird strike. | F3 | TETLEY ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-08-30 | c | 0.025545 | 0.0021287 | 2016 | 2015-08-30 | C | 704 | 0.025545 | 0.0021287
7131365 | 2015-08-30 16:47 | 2015-08-30 19:15 | 147.8333 | 113 | 4690.8333 | 41.5118 | 38.5118 | 0.014184 | 4351.8333 | 0.013159 | 0.00034168 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/678 | CB 13 Tripped E/F - Cable between Sw/Gear 350 and Transformer T6/678 found to be faulty during sectionlising and testing - Refer DNO 150818 | F2 | ARMSTRONG ST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-08-30 | c | 0.013159 | 0.00034168 | 2016 | 2015-08-30 | C | 113 | 0.013159 | 0.00034168
7131701 | 2015-08-30 17:38 | 2015-08-30 19:59 | 141 | 741 | 78331.8 | 105.7109 | 102.7109 | 0.23686 | 76108.8 | 0.23013 | 0.0022406 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sansun Sub | CB * Tripped B,C Ph O/C - Cable out of Sub appears to be faulty, found during sectionlising - Isolated at ABS O48 and feeder offloaded via ABS's L3,L96, O53 &, B8 - cable to be tested in morning refer DNO 150817 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-30 | c | 0.23013 | 0.0022406 | 2016 | 2015-08-30 | C | 741 | 0.23013 | 0.0022406
7133144 | 2015-08-30 18:41 | 2015-08-30 20:21 | 100.2167 | 1 | 100.2167 | 100.2167 | 97.2167 | 0.00030303 | 97.2167 | 0.00029396 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 79 KOPUTARA ROAD | All Power on on arrival possible power issues due to fault in Sanson. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-08-30 | c | 0.00029396 | 3.024e-06 | 2016 | 2015-08-30 | C | 1 | 0.00029396 | 3.0238e-06
7134222 | 2015-09-08 10:30 | 2015-09-08 14:36 | 245.9 | 3 | 737.7 | 245.9 | 242.9 | 0.0022306 | 728.7 | 0.0022034 | 9.0713e-06 | NAPA ID:12336 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 6 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Omata Tank Farm | Shutdown 1 replace poles & upgrade wire from ABS 448 to pole 756650 ready for shut down 2 to install tempory 11kv lines Omata tank Farm | F3 | MOTUROA 6 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-08 | b | 0.0011017 | 4.536e-06 | 2016 | 2015-09-08 | B | 3 | 0.0022034 | 9.0713e-06
7134861 | 2015-10-13 10:16 | 2015-10-13 10:31 | 15 | 3 | 45 | 15 | 12 | 0.00013607 | 36 | 0.00010886 | 9.0713e-06 | NAPA ID:12252 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP2030 | To install a 400V Fuse Disconnector. 244 Tower Road, Matamata. W/O 10147849. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 5.4428e-05 | 4.536e-06 | 2016 | 2015-10-13 | B | 3 | 0.00010886 | 9.0713e-06
7135820 | 2015-08-31 14:52 | 2015-08-31 15:04 | 12.6167 | 13 | 164.0167 | 12.6167 | 9.6167 | 0.00049595 | 125.0167 | 0.00037802 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228041 | Crossarm in need of replacing. Ready to fall off Urgent. Reported by Ron Borrie. Crossarm re-stayed. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-08-31 | c | 0.00037802 | 3.9309e-05 | 2016 | 2015-08-31 | C | 13 | 0.00037802 | 3.9309e-05
7135828 | 2015-08-31 11:19 | 2015-08-31 12:28 | 69.3167 | 9 | 623.85 | 69.3167 | 66.3167 | 0.0018864 | 596.85 | 0.0018047 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC853 | customer reporting that an insulator has come away from transformer pole, TX#853. check for safety required. 11kV Fuses TC853 Opened for Own Isolation. Restored 12:28 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-08-31 | c | 0.0018047 | 2.7214e-05 | 2016 | 2015-08-31 | C | 9 | 0.0018047 | 2.7214e-05
7135837 | 2015-08-31 11:00 | 2015-08-31 16:46 | 346.4167 | 704 | 58583.3667 | 83.215 | 80.215 | 0.17714 | 56471.3667 | 0.17076 | 0.0021287 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201466 | 11.45am - Call from Trustpower to report a customer noticing sparking pole on the corner of Park Road and Poly Crescent, 1st pole on Beach Road. Could not find Poly Crescent on Google maps. Has advised Murray in Control. Cracked Insulator found at pole 2 | F3 | TETLEY ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-08-31 | c | 0.17076 | 0.0021287 | 2016 | 2015-08-31 | C | 704 | 0.17076 | 0.0021287
7136856 | 2015-09-15 09:35 | 2015-09-15 11:48 | 133 | 2 | 266 | 133 | 130 | 0.00080432 | 260 | 0.00078618 | 6.0475e-06 | NAPA ID:11891 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-199 | REPLACE HV ARMS AT POLE 224814. Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00039309 | 3.024e-06 | 2016 | 2015-09-15 | B | 2 | 0.00078618 | 6.0475e-06
7136920 | 2015-08-31 11:50 | 2015-08-31 13:26 | 96 | 3 | 288 | 96 | 93 | 0.00087084 | 279 | 0.00084363 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1120 | Emergency Isolation to replace LV Crossarm at Pole | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-08-31 | c | 0.00084363 | 9.071e-06 | 2016 | 2015-08-31 | C | 3 | 0.00084363 | 9.0713e-06
7137271 | 2015-09-15 12:08 | 2015-09-15 13:22 | 74 | 2 | 148 | 74 | 71 | 0.00044752 | 142 | 0.00042937 | 6.0475e-06 | NAPA ID:11894 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-081 | REPLACE HV ARMS AT POLE 224797. Te Matai Road, Te Puke. W/O 30002443 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.00021469 | 3.024e-06 | 2016 | 2015-09-15 | B | 2 | 0.00042937 | 6.0475e-06
7137305 | 2015-09-15 09:15 | 2015-09-15 12:59 | 224 | 15 | 3360 | 224 | 221 | 0.01016 | 3315 | 0.010024 | 4.5356e-05 | NAPA ID:11887 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-133 | REPLACE HV POLE 224951 AND HV ARMS. Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.0050119 | 2.2678e-05 | 2016 | 2015-09-15 | B | 15 | 0.010024 | 4.5356e-05
7137329 | 2015-09-15 09:15 | 2015-09-15 15:15 | 360 | 42 | 15120 | 360 | 357 | 0.045719 | 14994 | 0.045338 | 0.000127 | NAPA ID:11571 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1445 | Replacing poles and crossarms at various sites. Taup/Coroglen Road, Thames. W/O 30002382. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.022669 | 6.3499e-05 | 2016 | 2015-09-15 | B | 42 | 0.045338 | 0.000127
7142071 | 2015-09-07 13:05 | 2015-09-07 13:47 | 42.15 | 15 | 632.25 | 42.15 | 39.15 | 0.0019118 | 587.25 | 0.0017757 | 4.5356e-05 | NAPA ID:12543 TP_GREYTOWN GXP > TUHITARATA SUB > KUMENGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S508 | Replace defective terminator on C11035 which has slipped causing badly uneven sag on 11kV center phase. Western Lake Road, Featherston. W/O 30010412. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-09-07 | b | 0.00088785 | 2.2678e-05 | 2016 | 2015-09-07 | B | 15 | 0.0017757 | 4.5356e-05
7142091 | 2015-09-15 10:20 | 2015-09-15 15:14 | 294 | 67 | 19698 | 294 | 291 | 0.059562 | 19497 | 0.058954 | 0.00020259 | NAPA ID:12430 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | U12686 | Replace defected conductor and replace pole#U12686. Hikuai Settlement Road, Hikuai. W/O 30013484. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-09-15 | b | 0.029477 | 0.0001013 | 2016 | 2015-09-15 | B | 67 | 0.058954 | 0.00020259
7144462 | 2015-09-01 01:15 | 2015-09-01 02:29 | 74 | 168 | 11595.65 | 69.0217 | 66.0217 | 0.035062 | 11091.65 | 0.033538 | 0.00050799 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P0108 | at 01:15, Waihi Sub, CB 2 Waihi Beach Rd Feeder, Recloser 9713, Tripped, Ph A + C O/C, E/F, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Found small tree branch on lines at Pole P0108. Removed with hot stick while line was de-ener | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.033538 | 0.00050799 | 2016 | 2015-09-01 | C | 168 | 0.033538 | 0.00050799
7145286 | 2015-09-01 03:07 | 2015-09-01 04:05 | 57.95 | 1 | 57.95 | 57.95 | 54.95 | 0.00017523 | 54.95 | 0.00016616 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IP42 | at 03:07, Mikkelsen Rd Sub, CB 4 McCabes Rd. Silver Fern Farms called in to report part power. Faultmen dispatched to investigate. Found that a jumper had blown at ABS IP42 due to lightning arrestor failure. Isolated cable at ABS IP42. Permit issued and r | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.00016616 | 3.024e-06 | 2016 | 2015-09-01 | C | 1 | 0.00016616 | 3.0238e-06
7145915 | 2015-09-01 05:19 | 2015-09-01 05:40 | 21.3 | 385 | 7635 | 19.8312 | 16.8312 | 0.023086 | 6480 | 0.019594 | 0.0011641 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Feeder patrolled on fault found | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.019594 | 0.0011641 | 2016 | 2015-09-01 | C | 385 | 0.019594 | 0.0011641
7148219 | 2015-09-01 06:13 | 2015-09-01 10:52 | 278.85 | 34 | 4650.8167 | 136.7887 | 133.7887 | 0.014063 | 4548.8167 | 0.013755 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | ABS 694 | Found a Possum and a Hawk on the lines, removed with hot sticks. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.013755 | 0.00010281 | 2016 | 2015-09-01 | C | 34 | 0.013755 | 0.00010281
7149065 | 2015-09-01 07:21 | 2015-09-01 12:34 | 312.5667 | 19 | 5938.7667 | 312.5667 | 309.5667 | 0.017957 | 5881.7667 | 0.017785 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 6293 | Pls check if 7149926/ 7149992/ 7149083 are related to this job. Replace 2 x Fuses caused by high winds. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.017785 | 5.7451e-05 | 2016 | 2015-09-01 | C | 19 | 0.017785 | 5.7451e-05
7150007 | 2015-09-01 06:36 | 2015-09-01 08:28 | 111.15 | 16 | 1778.4 | 111.15 | 108.15 | 0.0053775 | 1730.4 | 0.0052323 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD4-444 | 2 x 10 Amp Fuses. Reload and Reliven at Fuses SD4-444. Very Windy. Susp Line Clash. *** please check if oms 7150007 - 62 Shady Lane off tx TD4-720 is related *** | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.0052323 | 4.838e-05 | 2016 | 2015-09-01 | C | 16 | 0.0052323 | 4.838e-05
7150274 | 2015-09-01 08:15 | 2015-09-01 10:29 | 133.9 | 4 | 535.6 | 133.9 | 130.9 | 0.0016195 | 523.6 | 0.0015832 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | Repair Lines Down past Fuses PU424. Nick Webby and Craig Wellington attended but the crew requests may be have been lost in the system due to multiple faults on the same feeder. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.0015832 | 1.2095e-05 | 2016 | 2015-09-01 | C | 4 | 0.0015832 | 1.2095e-05
7150308 | 2015-09-01 08:36 | 2015-09-01 13:57 | 320.3833 | 21 | 4809.2333 | 229.0111 | 226.0111 | 0.014542 | 4746.2333 | 0.014351 | 6.3499e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2254 | need to replace TX - Tp 2254 - 50 kVA A crew will on there way to replace the TX. Transformer TP2254 replaced, but voltage variations still found. Appears fuse blown at Fused/Sw 9579/2. (wrong size fuse which never activated trip bar ) fuse replace a | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.014351 | 6.3499e-05 | 2016 | 2015-09-01 | C | 21 | 0.014351 | 6.3499e-05
7150538 | 2015-09-01 08:50 | 2015-09-01 09:51 | 61 | 357 | 10240 | 28.6835 | 25.6835 | 0.030963 | 9169 | 0.027725 | 0.0010795 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 754770 | Sparking lines just down from the *Super shed on Ngatumru Rd * called in by Shay 027 224 48098. 9:02am Called through to hub - Joanne 33kV Earth dropped down onto 11kV Lines at Pole 754770. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.027725 | 0.0010795 | 2016 | 2015-09-01 | C | 357 | 0.027725 | 0.0010795
7151853 | 2015-09-01 09:02 | 2015-09-01 11:18 | 135.7833 | 58 | 7875.4333 | 135.7833 | 132.7833 | 0.023813 | 7701.4333 | 0.023287 | 0.00017538 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-042 | Repair broken fuse holder | F2 | GRAVATT RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.023287 | 0.00017538 | 2016 | 2015-09-01 | C | 58 | 0.023287 | 0.00017538
7151998 | 2015-09-01 06:40 | 2015-09-01 16:19 | 579.5667 | 313 | 15497.3333 | 49.5122 | 46.5122 | 0.04686 | 14558.3333 | 0.044021 | 0.00094644 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 710460 | CB 4 opened for safety. Remove tree through lines at Pole 710460. Tree bought down in high winds | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.044021 | 0.00094644 | 2016 | 2015-09-01 | C | 313 | 0.044021 | 0.00094644
7152329 | 2015-09-01 09:11 | 2015-09-01 11:50 | 159 | 631 | 32040.8 | 50.7778 | 47.7778 | 0.096884 | 30147.8 | 0.09116 | 0.001908 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 807864 | CB 5 tripped on A & B phase O/C falgs, line was sectionalised and patrolled and faultman found tree across the line at pole 807864, line was isolated at ABS's 610 & 880 to remove the tree. This is now a 2 R job. NDR:600001 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.09116 | 0.001908 | 2016 | 2015-09-01 | C | 631 | 0.09116 | 0.001908
7154890 | 2015-09-01 10:00 | 2015-09-01 10:47 | 46.5667 | 146 | 6798.7333 | 46.5667 | 43.5667 | 0.020558 | 6360.7333 | 0.019233 | 0.00044147 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/46 | Replace 3x 11kV Fuse holders on Tranforemer T1/46 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.019233 | 0.00044147 | 2016 | 2015-09-01 | C | 146 | 0.019233 | 0.00044147
7155394 | 2015-09-01 10:26 | 2015-09-01 16:13 | 347.05 | 132 | 28555.0833 | 216.3264 | 213.3264 | 0.086344 | 28159.0833 | 0.085146 | 0.00039914 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 724972 | 12:35 - Report from passerby (Mark @ 06 278 4021) of line down at Ararata Hall on Ararata Road. Advised Phil to check before relivening. pole # 724972. 11kv line broken in the middle. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.085146 | 0.00039914 | 2016 | 2015-09-01 | C | 132 | 0.085146 | 0.00039914
7155617 | 2015-09-01 10:40 | 2015-09-01 14:20 | 219.45 | 3 | 658.35 | 219.45 | 216.45 | 0.0019907 | 649.35 | 0.0019635 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 218096 | NDR51858. Tree leant into lines during high wind & rain at pole 218096. Isolation at Fuses SE7 043 (no back feeds). Tree removed all service restored, no damage to lines. Materials 3 x 6A H/V, O/H fuses. 4.16pm Shay advised signed off with control at 2.24 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.0019635 | 9.071e-06 | 2016 | 2015-09-01 | C | 3 | 0.0019635 | 9.0713e-06
7155737 | 2015-09-01 10:56 | 2015-09-01 15:33 | 276.9833 | 634 | 49125.7167 | 77.4854 | 74.4854 | 0.14854 | 47223.7167 | 0.14279 | 0.0019171 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - FLOOD | 12937 | Pole in River. Now a 2R Job 11:47 01/09/15. 1.21pm - Wayne leaving now to attend another job. Recloser 9603 tripped O/C, L/O. Feeder sectionalised with pole 12937 found to be subsided into river. Isolations between ABS 345, 228 IP587 & Links 9714/6 to cut | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.14279 | 0.0019171 | 2016 | 2015-09-01 | C | 634 | 0.14279 | 0.0019171
7156905 | 2015-09-01 11:24 | 2015-09-01 14:57 | 213.0167 | 47 | 10011.7833 | 213.0167 | 210.0167 | 0.030273 | 9870.7833 | 0.029847 | 0.00014212 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715257 | Replace king bolt in crossarm at pole 715257 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.029847 | 0.00014212 | 2016 | 2015-09-01 | C | 47 | 0.029847 | 0.00014212
7157727 | 2015-09-12 01:01 | 2015-09-14 01:28 | 2907.5 | 23 | 882.05 | 38.35 | 35.35 | 0.0026671 | 813.05 | 0.0024585 | 6.9546e-05 | NAPA ID:12576 TP_CARRINGTON GXP > CITY SUB > CITY 7 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Switch 585/3 | Urgent replacement of DNO150813 magnefix. LV circuits outside Hotel will be backfeed from tx 48 and 1106. First shut on Sat morning is to disconnect tx jumpers from LV panel and Plymouth Hotel main switch and to connect generator to Hotel main switch. THE | F2 | CITY 7 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2015-09-12 | b | 0.0012292 | 3.4773e-05 | 2016 | 2015-09-12 | B | 23 | 0.0024585 | 6.9546e-05
7158157 | 2015-09-01 10:41 | 2015-09-01 18:40 | 478.85 | 364 | 75266.6 | 206.7764 | 203.7764 | 0.22759 | 74174.6 | 0.22429 | 0.0011006 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725955 | 12.52pm - Travis in Control advise to leave this job as it is a HV job, they are taking care of it. 8.49pm Paul called to get completed from site. Repaired lines LV & HV overhead conductor - pulled up a few spans of wire 10m of conductor & 9 full tensions | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.22429 | 0.0011006 | 2016 | 2015-09-01 | C | 364 | 0.22429 | 0.0011006
7159181 | 2015-09-16 09:15 | 2015-09-16 12:00 | 165 | 5 | 825 | 165 | 162 | 0.0024946 | 810 | 0.0024492 | 1.5119e-05 | NAPA ID:11902 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses SE6-057 | REPLACE HV POLE # 224884. Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-16 | b | 0.0012246 | 7.559e-06 | 2016 | 2015-09-16 | B | 5 | 0.0024492 | 1.5119e-05
7159217 | 2015-09-16 09:30 | 2015-09-16 14:20 | 290 | 2 | 580 | 290 | 287 | 0.0017538 | 574 | 0.0017356 | 6.0475e-06 | NAPA ID:11903 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-139 | REPLACE HV POLE # 266848. Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-16 | b | 0.00086782 | 3.024e-06 | 2016 | 2015-09-16 | B | 2 | 0.0017356 | 6.0475e-06
7162606 | 2015-09-01 10:24 | 2015-09-01 13:20 | 176 | 1 | 176 | 176 | 173 | 0.00053218 | 173 | 0.00052311 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 6769 | Replace 2 x 6A Fuse | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.00052311 | 3.024e-06 | 2016 | 2015-09-01 | C | 1 | 0.00052311 | 3.0238e-06
7162760 | 2015-09-28 09:15 | 2015-09-28 14:38 | 323.05 | 190 | 61379.5 | 323.05 | 320.05 | 0.1856 | 60809.5 | 0.18387 | 0.00057451 | NAPA ID:12405 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | Replace/ Relocate poles between pole 204945 & 204981 | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-09-28 | b | 0.091937 | 0.00028726 | 2016 | 2015-09-28 | B | 190 | 0.18387 | 0.00057451
7163623 | 2015-09-01 10:17 | 2015-09-01 15:06 | 288.9667 | 3 | 199.8333 | 66.6111 | 63.6111 | 0.00060425 | 190.8333 | 0.00057703 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC4254 | Replace 2 x 6A Fuses. Suspect brid strike | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.00057703 | 9.071e-06 | 2016 | 2015-09-01 | C | 3 | 0.00057703 | 9.0713e-06
7164571 | 2015-09-01 06:30 | 2015-09-01 07:19 | 49 | 1 | 49 | 49 | 46 | 0.00014816 | 46 | 0.00013909 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2722 | Outage on child job was for this customer but they have had their supply moved to Transformer TP2722. This job is to record SAIDI for the customer outage. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.00013909 | 3.024e-06 | 2016 | 2015-09-01 | C | 1 | 0.00013909 | 3.0238e-06
7164833 | 2015-09-01 17:22 | 2015-09-01 17:31 | 9.2 | 8 | 73.6 | 9.2 | 6.2 | 0.00022255 | 49.6 | 0.00014998 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 230081 | ADVISED HUB. ADVISED CONTROL. Isolate line at fuses SF6 008 to remove branch with live line stick from pole 230081. Branch removed all service restored high wind & rain. Materials nil. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-01 | c | 0.00014998 | 2.419e-05 | 2016 | 2015-09-01 | C | 8 | 0.00014998 | 2.419e-05
7165359 | 2015-09-01 17:25 | 2015-09-01 18:03 | 38 | 2 | 76 | 38 | 35 | 0.00022981 | 70 | 0.00021166 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 685 | Faultman found the string insulators at Fuses 685 all rusted and about to break off at the fuses when faultman went to closed them after restoring the supply after a planned shut down. Line was isolated at Fuses 685 to replace all 3 string insulators. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-09-01 | c | 0.00021166 | 6.048e-06 | 2016 | 2015-09-01 | C | 2 | 0.00021166 | 6.0475e-06
7165366 | 2015-09-01 17:30 | 2015-09-01 18:50 | 80.0333 | 5 | 400.1667 | 80.0333 | 77.0333 | 0.00121 | 385.1667 | 0.0011647 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 725015 | Tree Branch removed from HV Lines at Pole 725015. Replaced 2x 6Amp Fuse Links. NDR# N100055. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-09-01 | c | 0.0011647 | 1.5119e-05 | 2016 | 2015-09-01 | C | 5 | 0.0011647 | 1.5119e-05
7166914 | 2015-09-02 11:00 | 2015-09-02 12:04 | 64.1833 | 11 | 706.0167 | 64.1833 | 61.1833 | 0.0021348 | 673.0167 | 0.002035 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220154 | Xarm which is vertical with the pole, only thing holding it there is a bolt in paddock - plz go to customers house as he has stock in the paddock. 6.52pm advised Tans at svs hub. To be left overnight and sorted out first thing Wed Morning. Isolation at fu | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 0.002035 | 3.3261e-05 | 2016 | 2015-09-02 | C | 11 | 0.002035 | 3.3261e-05
7169395 | 2015-09-25 09:50 | 2015-09-25 11:15 | 85 | 4 | 340 | 85 | 82 | 0.0010281 | 328 | 0.00099179 | 1.2095e-05 | NAPA ID:12590 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC676 | To replace the 11kV Transformer Fuses & install a 400V Fuse Unit. Bell Road, Piako. W/O 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-25 | b | 0.0004959 | 6.048e-06 | 2016 | 2015-09-25 | B | 4 | 0.00099179 | 1.2095e-05
7173842 | 2015-09-25 13:00 | 2015-09-25 13:56 | 56 | 6 | 336 | 56 | 53 | 0.001016 | 318 | 0.00096156 | 1.8143e-05 | NAPA ID:12582 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2075 | To replace the 11kV Fuses TC2075 & Install a 400V Fuse unit. Bell Road, Piako. W/O 10147849. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-25 | b | 0.00048078 | 9.071e-06 | 2016 | 2015-09-25 | B | 6 | 0.00096156 | 1.8143e-05
7173867 | 2015-09-02 10:00 | 2015-09-02 12:00 | 120.15 | 5 | 600.75 | 120.15 | 117.15 | 0.0018165 | 585.75 | 0.0017712 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7317 | Replace 2 x 10A fuses due to line clash. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-09-02 | c | 0.0017712 | 1.5119e-05 | 2016 | 2015-09-02 | C | 5 | 0.0017712 | 1.5119e-05
7174982 | 2015-09-02 11:43 | 2015-09-02 12:40 | 57.2167 | 679 | 24523.0333 | 36.1164 | 33.1164 | 0.074152 | 22486.0333 | 0.067992 | 0.0020531 |  | 33 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | WHUPKO008 | Customer reported of lighting strike on Transformer TC2927. Report from NGOC Diff 5.5%.Lines around area of reported strike were patrolled with no fault found. CB 42 went to an invalid state upon loss of supply requiring an onsite reset before it could be | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 0.067992 | 0.0020531 | 2016 | 2015-09-02 | C | 679 | 0.067992 | 0.0020531
7175673 | 2015-09-02 08:39 | 2015-09-02 11:51 | 191.75 | 116 | 94.9 | 0.8181 | -2.1819 | 0.00028695 | 0 | 0 | 0.00035076 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | LI712 | Replace 2 x 8A Fuse LI712 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-02 | c | 0 | 0.00035076 | 2016 | 2015-09-02 | C | 116 | 0 | 0.00035076
7176000 | 2015-09-09 09:00 | 2015-09-09 12:30 | 209.9833 | 21 | 4409.65 | 209.9833 | 206.9833 | 0.013334 | 4346.65 | 0.013143 | 6.3499e-05 | NAPA ID:11654 TP_BUNNYTHORPE GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | Change 7 x 33kv xarms and 7 x 11kV crossarms and hardware. Work Location: Raymond Street. Work Order 30006772 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-09 | b | 0.0065716 | 3.1749e-05 | 2016 | 2015-09-09 | B | 21 | 0.013143 | 6.3499e-05
7177095 | 2015-09-02 16:05 | 2015-09-02 18:27 | 141.8167 | 409 | 140.7833 | 0.34421 | -2.6558 | 0.0004257 | 0 | 0 | 0.0012367 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FP284 | CB 3 A/R, E/F 2 x 10A HV Fuses at Fuses FP284. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 0 | 0.0012367 | 2016 | 2015-09-02 | C | 409 | 0 | 0.0012367
7177608 | 2015-09-07 11:51 | 2015-09-07 12:38 | 46.5667 | 53 | 2468.0333 | 46.5667 | 43.5667 | 0.0074627 | 2309.0333 | 0.006982 | 0.00016026 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E12576 | ### Red Defect ### Requires urgent replacement of 11kV cross arm. To be completed 3rd September during the day. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-09-07 | c | 0.006982 | 0.00016026 | 2016 | 2015-09-07 | C | 53 | 0.006982 | 0.00016026
7177786 | 2015-09-02 22:00 | 2015-09-03 00:53 | 173 | 6 | 1038 | 173 | 170 | 0.0031387 | 1020 | 0.0030842 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF7-039 | Transformer TF7-039 Faulty. Lightning Strike. Replaced | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 0.0030842 | 1.8143e-05 | 2016 | 2015-09-02 | C | 6 | 0.0030842 | 1.8143e-05
7178033 | 2015-09-02 18:33 | 2015-09-02 18:36 | 3.0167 | 625 | 1823.5333 | 2.9177 | -0.082347 | 0.0055139 | 0 | 0 | 0.0018899 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 1332 | T/Power CB 1332 tripped on E/F & C/C flags, CB XT30 was opened and CB XT50 closed to restore supply, line was sectionalised and patrolled were possible and no fault was found. | F1,F2,F3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2015-09-02 | c | 0 | 0.0018898 | 2016 | 2015-09-02 | C | 625 | 0 | 0.0018899
7178809 | 2015-09-02 19:18 | 2015-09-02 19:23 | 4.9167 | 1 | 4.9167 | 4.9167 | 1.9167 | 1.4867e-05 | 1.9167 | 5.7955e-06 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF7-112 | Been out since 4pm. there was a lightning and a loud bang and unsure if that was the lightening or something else. 7.21pm advised Sammy at SVS hub. 2 x 3A HV Fuses replaced. Lightning. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 5.796e-06 | 3.024e-06 | 2016 | 2015-09-02 | C | 1 | 5.7955e-06 | 3.0238e-06
7178817 | 2015-09-02 19:18 | 2015-09-03 03:04 | 465.8667 | 2 | 931.7333 | 465.8667 | 462.8667 | 0.0028173 | 925.7333 | 0.0027992 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE7-137 | Transformer TE7-137 hit by Lightning. Replaced. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-02 | c | 0.0027992 | 6.048e-06 | 2016 | 2015-09-02 | C | 2 | 0.0027992 | 6.0475e-06
7182041 | 2015-09-28 08:45 | 2015-09-28 14:54 | 368.4 | 57 | 20993 | 368.2982 | 365.2982 | 0.063478 | 20822 | 0.062961 | 0.00017235 | NAPA ID:11586 TP_MATAROA GXP > TAIHAPE SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 789042, 789423 | Isolation of 11kV for tree work between pole 789042 pole 789423. Doucle Circuit CB5/CB7. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.03148 | 8.6177e-05 | 2016 | 2015-09-28 | B | 57 | 0.062961 | 0.00017235
7183213 | 2015-09-06 09:32 | 2015-09-06 12:03 | 150.6 | 4 | 602.4 | 150.6 | 147.6 | 0.0018215 | 590.4 | 0.0017852 | 1.2095e-05 | NAPA ID:11691 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 207068 | Install live line break to re-sag 11kV conductors which are clashing causing outages and trim trees. Work is to remedy fault OMS # 3131288426. Re-instate break on completion. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-09-06 | b | 0.00089261 | 6.048e-06 | 2016 | 2015-09-06 | B | 4 | 0.0017852 | 1.2095e-05
7183404 | 2015-09-03 14:23 | 2015-09-03 14:55 | 32 | 35 | 1120 | 32 | 29 | 0.0033866 | 1015 | 0.0030691 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13045 | Replace 1 x jumper at Transformer TC187 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.0030691 | 0.00010583 | 2016 | 2015-09-03 | C | 35 | 0.0030691 | 0.00010583
7184386 | 2015-09-17 08:48 | 2015-09-17 14:53 | 365.6167 | 42 | 15355.9 | 365.6167 | 362.6167 | 0.046433 | 15229.9 | 0.046052 | 0.000127 | NAPA ID:11616 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212269, 212233 | Replace poles hardware and conductor between poles 212269 - 212233 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-17 | b | 0.023026 | 6.3499e-05 | 2016 | 2015-09-17 | B | 42 | 0.046052 | 0.000127
7185253 | 2015-09-08 09:15 | 2015-09-08 14:50 | 335 | 3 | 1005 | 335 | 332 | 0.0030389 | 996 | 0.0030117 | 9.0713e-06 | NAPA ID:12656 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/82 | Replace transformer cross arm on pole P49955 (T5/82). Existing Tranformer to be reused. Replace LV cross arm on pole P07033. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-08 | b | 0.0015058 | 4.536e-06 | 2016 | 2015-09-08 | B | 3 | 0.0030117 | 9.0713e-06
7185965 | 2015-09-15 11:02 | 2015-09-15 15:00 | 237.1833 | 1 | 237.1833 | 237.1833 | 234.1833 | 0.00071719 | 234.1833 | 0.00070811 | 3.0238e-06 | NAPA ID:12655 TP_MARTON GXP > PUKEPAPA SUB > LEEDSTOWN 22KV | 22 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 805390 | Replace rotten 22kv pole 805390, Red tagged. SH 1, Marton. W/O 30014061. | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.00035406 | 1.512e-06 | 2016 | 2015-09-15 | B | 1 | 0.00070811 | 3.0238e-06
7186043 | 2015-09-03 16:20 | 2015-09-03 16:54 | 34 | 2 | 68 | 34 | 31 | 0.00020562 | 62 | 0.00018747 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP103 | Tail at fuses FP103 fallen out. Isolated fuses FP 103 tail reterminated, fuses restored. Have linked two jobs because fuses not on eMap. They both count towards to SAIDI and have same outage and restore times. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.00018747 | 6.048e-06 | 2016 | 2015-09-03 | C | 2 | 0.00018747 | 6.0475e-06
7186371 | 2015-09-04 13:27 | 2015-09-04 14:14 | 47 | 2 | 94 | 47 | 44 | 0.00028423 | 88 | 0.00026609 | 6.0475e-06 | NAPA ID:12693 TP_CARRINGTON GXP > OAKURA SUB > INLAND COAST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX1389 | We are replacing transformer as it has come in as a defect and oil is leaking all over the ground. Work Location: Lower Timaru Road, Okato. Work Order 30013875 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-09-04 | b | 0.00013305 | 3.024e-06 | 2016 | 2015-09-04 | B | 2 | 0.00026609 | 6.0475e-06
7186541 | 2015-09-03 13:52 | 2015-09-03 14:55 | 63 | 4 | 252 | 63 | 60 | 0.00076199 | 240 | 0.0007257 | 1.2095e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TE3-199 | Isolation for works on the LV. Geoff Warner was called to site as part of PQI 1259 and found the LV tails feeding the customers plant was burnt up. No LV fusing so isolated HV fuses to make repairs. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.0007257 | 1.2095e-05 | 2016 | 2015-09-03 | C | 4 | 0.0007257 | 1.2095e-05
7186703 | 2015-09-03 17:15 | 2015-09-03 18:13 | 57.9667 | 4 | 231.8667 | 57.9667 | 54.9667 | 0.00070111 | 219.8667 | 0.00066482 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7462 | Tripping on 2 Fuses at 7462. Reloaded OK. (Rating | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-09-03 | c | 0.00066482 | 1.2095e-05 | 2016 | 2015-09-03 | C | 4 | 0.00066482 | 1.2095e-05
7186796 | 2015-09-03 17:48 | 2015-09-03 18:29 | 41.3 | 121 | 4997.3 | 41.3 | 38.3 | 0.015111 | 4634.3 | 0.014013 | 0.00036588 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | ( LAK 3 ) Sectionaliser SP15 tripped ( no flags ) fault indicators checked. Patrolled no fault found RP15 closed & returned to service. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.014013 | 0.00036587 | 2016 | 2015-09-03 | C | 121 | 0.014013 | 0.00036588
7188406 | 2015-09-03 18:58 | 2015-09-03 23:10 | 252.1667 | 1163 | 162215.65 | 139.4804 | 136.4804 | 0.4905 | 158726.65 | 0.47995 | 0.0035166 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 248439 | ADVISED HUB ADVISED CONTROL 7.10pm advised fire Service that faultman is onsite. Emergency switching to replace pole 248439 damaged by car. Isolations between Sw/Gear 9747/3 & ABS IP529. (No back feeds all of feeder off). Pole replaced all service restore | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.47995 | 0.0035166 | 2016 | 2015-09-03 | C | 1163 | 0.47995 | 0.0035166
7188492 | 2015-09-03 22:15 | 2015-09-03 23:25 | 70 | 9 | 630 | 70 | 67 | 0.001905 | 603 | 0.0018233 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E0861 | OMS 7188590 poss related. Fuses FC2313 opened to replace faulty insulator at Pole E0861. Insulator replaced all service restored. Material 1 x H/V insulator & 1 x 10A H/V, O/H fuse. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-09-03 | c | 0.0018233 | 2.7214e-05 | 2016 | 2015-09-03 | C | 9 | 0.0018233 | 2.7214e-05
7190556 | 2015-09-04 07:52 | 2015-09-04 14:41 | 408.9667 | 4 | 1635.8667 | 408.9667 | 405.9667 | 0.0049465 | 1623.8667 | 0.0049102 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7462 | Initially Part power jobs. Trees removed from Lines and Lines Resagged under AP. Reload reliven 2 x 10 Amp Fuses | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-09-04 | c | 0.0049102 | 1.2095e-05 | 2016 | 2015-09-04 | C | 4 | 0.0049102 | 1.2095e-05
7190635 | 2015-09-04 07:10 | 2015-09-04 10:15 | 185.35 | 1 | 185.35 | 185.35 | 182.35 | 0.00056045 | 182.35 | 0.00055138 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K72 , K80 | Fuses Reload reliven at K72 and K80 all under 7190635 and Includes 7190635 and 7191218 K72 2 x 6A. K80 2 x 3A*** please check if oms 7191376 - 99 WAITUNA - TAPAUE ROAD - tx T5/281 and OMS 191218 - 584 Beaconsfield Valley Road - tx T5/132 are related ***. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-04 | c | 0.00055138 | 3.024e-06 | 2016 | 2015-09-04 | C | 1 | 0.00055138 | 3.0238e-06
7191159 | 2015-09-10 08:31 | 2015-09-10 13:42 | 310.8 | 42 | 13053.6 | 310.8 | 307.8 | 0.039471 | 12927.6 | 0.03909 | 0.000127 | NAPA ID:12586 TP_WAIHOU GXP | 11 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WAIHOU GXP | To complete defect repairs in the 33kV lines during a Transpower outage | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.019545 | 6.3499e-05 | 2016 | 2015-09-10 | B | 42 | 0.03909 | 0.000127
7192917 | 2015-09-04 07:57 | 2015-09-04 10:40 | 163.4167 | 10 | 1634.1667 | 163.4167 | 160.4167 | 0.0049413 | 1604.1667 | 0.0048506 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K72 , K80 | 7192917 includes 2190635 and 7191218 and was ceated when trying to Parent the original jobs. Reload reliven at K72 2 x 6A at K80 2 x 3A | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-04 | c | 0.0048506 | 3.0238e-05 | 2016 | 2015-09-04 | C | 10 | 0.0048506 | 3.0238e-05
7193734 | 2015-09-04 13:15 | 2015-09-04 14:08 | 52.6 | 3 | 157.8 | 52.6 | 49.6 | 0.00047715 | 148.8 | 0.00044994 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SB1-070 | 2 HV fuses blown at Fuses SB1-070. blown due to fallen tree Fuses reloaded & relivened line. Materials 2x6amp HV fuse links | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-09-04 | c | 0.00044994 | 9.071e-06 | 2016 | 2015-09-04 | C | 3 | 0.00044994 | 9.0713e-06
7194405 | 2015-09-04 13:06 | 2015-09-04 15:02 | 116.75 | 7 | 817.25 | 116.75 | 113.75 | 0.0024712 | 796.25 | 0.0024077 | 2.1166e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TB2-101 | Isolation to allow connection of new cable feeding transformer TB2-101 from transformer TB2-060. Customer had been on generator. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-09-04 | c | 0.0024077 | 2.1166e-05 | 2016 | 2015-09-04 | C | 7 | 0.0024077 | 2.1166e-05
7194440 | 2015-09-04 15:25 | 2015-09-04 17:13 | 107.8167 | 1 | 107.8167 | 107.8167 | 104.8167 | 0.00032601 | 104.8167 | 0.00031694 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4657 | replaced 2x 2a HV fuses | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-09-04 | c | 0.00031694 | 3.024e-06 | 2016 | 2015-09-04 | C | 1 | 0.00031694 | 3.0238e-06
7194461 | 2015-09-10 15:06 | 2015-09-10 19:02 | 235.45 | 1 | 235.45 | 235.45 | 232.45 | 0.00071194 | 232.45 | 0.00070287 | 3.0238e-06 | NAPA ID:12710 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 384006 | Replace 3x Lightning Arrestors | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-10 | b | 0.00035144 | 1.512e-06 | 2016 | 2015-09-10 | B | 1 | 0.00070287 | 3.0238e-06
7194706 | 2015-09-24 08:15 | 2015-09-24 08:50 | 35 | 19 | 665 | 35 | 32 | 0.0020108 | 608 | 0.0018384 | 5.7451e-05 | NAPA ID:12736 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE7-032 | Replace Cross arm. Maketu, Pongakawa. W/O 30002362. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-24 | b | 0.00091922 | 2.8726e-05 | 2016 | 2015-09-24 | B | 19 | 0.0018384 | 5.7451e-05
7202187 | 2015-09-06 02:00 | 2015-09-06 05:20 | 200 | 92 | 18400 | 200 | 197 | 0.055637 | 18124 | 0.054803 | 0.00027819 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | CB N21 (Rangiwahia Recloser) tripped on B Phase O/C. (No Control or aalrm indication to NOC via SCADA). CB reclosed on site after receiving "no power" jobs. Closed OK, Control box found to be faulty (To be defected by DOWNER). Cause unknown. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.054803 | 0.00027819 | 2016 | 2015-09-06 | C | 92 | 0.054803 | 0.00027819
7202202 | 2015-09-06 05:21 | 2015-09-06 06:38 | 76.6333 | 385 | 16644.9333 | 43.2336 | 40.2336 | 0.05033 | 15489.9333 | 0.046838 | 0.0011641 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CC18 | Fire service report fire on Pillar box on Staley road north, this is in fact transformer fire on Bowler Road. Fire called to say that fire at pole C14029, transformer TC4143 O & T recloser closed capacitor CC18 faulted. CB 8 opened due to no comms to recl | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-06 | c | 0.046838 | 0.0011641 | 2016 | 2015-09-06 | C | 385 | 0.046838 | 0.0011641
7203854 | 2015-09-06 10:11 | 2015-09-06 16:15 | 364.4 | 93 | 15412.2 | 165.7226 | 162.7226 | 0.046603 | 15133.2 | 0.045759 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11522 | Patrolled & found blown insulator at Pole P11522. Replaced 1x 11kV Pin & Insulator, & 2mtrs of cu. binder. Also attended by Anjay Prasad under OMS 7203382, but his job rolled up into main job before it was completed. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.045759 | 0.00028121 | 2016 | 2015-09-06 | C | 93 | 0.045759 | 0.00028121
7204432 | 2015-09-06 15:20 | 2015-09-06 17:35 | 134.85 | 23 | 972.9833 | 42.3036 | 39.3036 | 0.0029421 | 903.9833 | 0.0027334 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 495 | Replaced 2x 10Amp HV Links. *** please check if oms 7204448 - 160 Te Houhou Rd is also affected *** | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.0027334 | 6.9546e-05 | 2016 | 2015-09-06 | C | 23 | 0.0027334 | 6.9546e-05
7204672 | 2015-09-06 17:14 | 2015-09-06 20:35 | 201.0167 | 19 | 3819.3167 | 201.0167 | 198.0167 | 0.011549 | 3762.3167 | 0.011376 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228595 | repair line line bought down by trees isolation at fuses SF6-012. 50meters of conductor, 15 sleeves | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-06 | c | 0.011376 | 5.7451e-05 | 2016 | 2015-09-06 | C | 19 | 0.011376 | 5.7451e-05
7204691 | 2015-09-06 19:41 | 2015-09-06 20:52 | 70.8667 | 90 | 6340.05 | 70.445 | 67.445 | 0.019171 | 6070.05 | 0.018354 | 0.00027214 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2832 | Broken DDO found at Transformer T2832 - Isolated at ABS's S598 & S513 with back feed installed via ABS S525 - Replaced all 3 DDO's as all old - used 3 x DDO's 3 x 2 amps fuses | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.018354 | 0.00027214 | 2016 | 2015-09-06 | C | 90 | 0.018354 | 0.00027214
7205011 | 2015-09-06 15:25 | 2015-09-06 20:24 | 299.6333 | 1 | 299.6333 | 299.6333 | 296.6333 | 0.00090602 | 296.6333 | 0.00089695 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 160 TE HOUHOU ROAD | Power on, on arrival. part of earlier fault | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.00089695 | 3.024e-06 | 2016 | 2015-09-06 | C | 1 | 0.00089695 | 3.0238e-06
7205123 | 2015-09-06 18:32 | 2015-09-06 20:19 | 106.45 | 161 | 9653.7 | 59.9609 | 56.9609 | 0.02919 | 9170.7 | 0.02773 | 0.00048683 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P17804 | Possium found on line during Sectionlising at Pole P17804 - cleared using Hot Sticks | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.02773 | 0.00048682 | 2016 | 2015-09-06 | C | 161 | 0.02773 | 0.00048683
7205820 | 2015-09-06 20:07 | 2015-09-06 21:06 | 59.0167 | 2 | 118.0333 | 59.0167 | 56.0167 | 0.0003569 | 112.0333 | 0.00033876 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1234 | 2 Fuses found blown at Fuses 1234 - line patrolled with no fault found - used 2 X 6 amp Fuses | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-09-06 | c | 0.00033876 | 6.048e-06 | 2016 | 2015-09-06 | C | 2 | 0.00033876 | 6.0475e-06
7206142 | 2015-09-07 01:25 | 2015-09-07 03:20 | 115.15 | 266 | 21158.3167 | 79.5425 | 76.5425 | 0.063978 | 20360.3167 | 0.061565 | 0.00080432 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726177 | Line Broken at Pole 726177 and hanging in Trees - Isolated at ABS's LI 677, LI672, & LI227 - used two sleeve and 1 mtr of conductor | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-07 | c | 0.061565 | 0.00080432 | 2016 | 2015-09-07 | C | 266 | 0.061565 | 0.00080432
7208263 | 2015-09-25 09:25 | 2015-09-25 10:30 | 65 | 12 | 780 | 65 | 62 | 0.0023585 | 744 | 0.0022497 | 3.6285e-05 | NAPA ID:12526 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses K72 | Replace 11kV X-arms only on poles P12189 and P12190. Beaconsfield Valley Road, Kimbolton. W/O 10160678. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-25 | b | 0.0011248 | 1.8143e-05 | 2016 | 2015-09-25 | B | 12 | 0.0022497 | 3.6285e-05
7208304 | 2015-09-25 13:00 | 2015-09-25 14:16 | 76.2833 | 15 | 1144.25 | 76.2833 | 73.2833 | 0.0034599 | 1099.25 | 0.0033239 | 4.5356e-05 | NAPA ID:12671 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS P4 | Replace 11kV X-arms only on poles P37538, P36894 and P36877. Forest Road, Kimbolton. W/O 10160678. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-25 | b | 0.0016619 | 2.2678e-05 | 2016 | 2015-09-25 | B | 15 | 0.0033239 | 4.5356e-05
7213012 | 2015-09-21 12:48 | 2015-09-21 13:58 | 69.65 | 30 | 2089.5 | 69.65 | 66.65 | 0.0063181 | 1999.5 | 0.006046 | 9.0713e-05 | NAPA ID:12706 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > PALM BEACH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP431 | TO CLEAN H.V TERMINATIONS ON TX TD-310 AFTER FAILED TEST. 20 Hartford Avenue, Papmoa. W/O 30000449. | F3 | PALM BEACH | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-09-21 | b | 0.003023 | 4.5356e-05 | 2016 | 2015-09-21 | B | 30 | 0.006046 | 9.0713e-05
7213168 | 2015-09-21 09:33 | 2015-09-21 11:51 | 138.1333 | 104 | 14365.8667 | 138.1333 | 135.1333 | 0.043439 | 14053.8667 | 0.042496 | 0.00031447 | NAPA ID:12707 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > PALM BEACH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP418 | TO INSTALL TRANSFORMER HOLD DOWN BOLTS ON TX TD5-311. 44 Hartford Avenue, Papamoa. W/O 30000449. | F3 | PALM BEACH | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-09-21 | b | 0.021248 | 0.00015724 | 2016 | 2015-09-21 | B | 104 | 0.042496 | 0.00031447
7215260 | 2015-09-07 16:18 | 2015-09-07 17:45 | 86.75 | 23 | 1995.25 | 86.75 | 83.75 | 0.0060332 | 1926.25 | 0.0058245 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | S8 | Replaced 2x10 Amp HV Links | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-09-07 | c | 0.0058245 | 6.9546e-05 | 2016 | 2015-09-07 | C | 23 | 0.0058245 | 6.9546e-05
7219348 | 2015-09-22 09:37 | 2015-09-22 13:54 | 256.9 | 45 | 11560.5 | 256.9 | 253.9 | 0.034956 | 11425.5 | 0.034548 | 0.00013607 | NAPA ID:11906 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-135 | REPLACE ARMS AND POLES AND ARMS MARK RD AND BROWNS RD. Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-22 | b | 0.017274 | 6.8035e-05 | 2016 | 2015-09-22 | B | 45 | 0.034548 | 0.00013607
7219529 | 2015-09-24 05:41 | 2015-09-24 07:15 | 94.45 | 52 | 3374.7333 | 64.8987 | 61.8987 | 0.010204 | 3218.7333 | 0.0097327 | 0.00015724 | NAPA ID:11476 TP_TE MATAI GXP > TE PUKE SUB > CENTRAL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE5-172 | 1. Live line cable break at pole 222417 to HV link-box SE5-275 (LLP).2. Disc & remove cable from HV link-box SE5-275 (L2) and connect generators to transformers TE5-172 & TE5-213 (AP) 3. Live line cable re-make at pole 222417 (LLP). 4. Joint cable fro | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-24 | b | 0.0048663 | 7.8618e-05 | 2016 | 2015-09-24 | B | 52 | 0.0097327 | 0.00015724
7219531 | 2015-09-23 09:15 | 2015-09-23 13:04 | 229 | 15 | 3435 | 229 | 226 | 0.010387 | 3390 | 0.010251 | 4.5356e-05 | NAPA ID:11909 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-158 | Replace poles and cross arms. Work Location: Te Matai Road, Te Puke. W/O 30002443. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-23 | b | 0.0051253 | 2.2678e-05 | 2016 | 2015-09-23 | B | 15 | 0.010251 | 4.5356e-05
7220448 | 2015-09-22 09:24 | 2015-09-22 15:15 | 351 | 42 | 14742 | 351 | 348 | 0.044576 | 14616 | 0.044195 | 0.000127 | NAPA ID:11572 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole T1448 | Reconductoring between poles T1448 + T13114. Tapu/Coroglen Road, Thames. W/O 30002382. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-22 | b | 0.022098 | 6.3499e-05 | 2016 | 2015-09-22 | B | 42 | 0.044195 | 0.000127
7220582 | 2015-09-29 06:01 | 2015-09-29 16:46 | 645 | 60 | 38700 | 645 | 642 | 0.11702 | 38520 | 0.11648 | 0.00018143 | NAPA ID:11608 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-209 | 1. Connect generator to LV at transfomer TE5-050 (AP1).2. Remove cable from pole 222417 to HV link-box SE5-257 - LV at TE5-264 backfed. Remove jumpers to fuses SE5-209 pole 262426 (LLP1). 3. Remove existing cable from transformer TE5-050 and terminate | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 0.058238 | 9.0713e-05 | 2016 | 2015-09-29 | B | 60 | 0.11648 | 0.00018143
7221650 | 2015-09-08 14:47 | 2015-09-08 15:45 | 58 | 64 | 3712 | 58 | 55 | 0.011224 | 3520 | 0.010644 | 0.00019352 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G175 | Replace 3 x 16A magnefix fuses due to age. This outage is to count SAIDI all other outage jobs can be discounted as there was only a single outage | F3 | PASCAL ST 7 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2015-09-08 | c | 0.010644 | 0.00019352 | 2016 | 2015-09-08 | C | 64 | 0.010644 | 0.00019352
7223704 | 2015-09-09 08:07 | 2015-09-09 12:36 | 268.8667 | 346 | 65250.2 | 188.5844 | 185.5844 | 0.1973 | 64212.2 | 0.19416 | 0.0010462 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | A0029 | CB 3 Trip. Caused By line down at Pole A0029. Line repaired 2 x sleeves 1 mtr 70mm copper. 8.09am advised hub of 999 and taken to control. 2970 OLD TAUPO ROAD, Tokoroa. Lines down F1914358 fire comms require an ETA please | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-09-09 | c | 0.19416 | 0.0010462 | 2016 | 2015-09-09 | C | 346 | 0.19416 | 0.0010462
7224343 | 2015-09-09 09:03 | 2015-09-09 14:15 | 311.6833 | 2 | 623.3667 | 311.6833 | 308.6833 | 0.0018849 | 617.3667 | 0.0018668 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2477 | 2 x 10 A Fuses replaced | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-09-09 | c | 0.0018668 | 6.048e-06 | 2016 | 2015-09-09 | C | 2 | 0.0018668 | 6.0475e-06
7224629 | 2015-09-28 09:40 | 2015-09-28 13:18 | 217.85 | 2 | 435.7 | 217.85 | 214.85 | 0.0013175 | 429.7 | 0.0012993 | 6.0475e-06 | NAPA ID:12697 TP_MASTERTON GXP > AWATOITOI SUB > ROROKOKO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 441253 | Installing a 11kV fixed load transformer and DDOs fit comms and control box to existing pole 441253. Works location: Masterton Castlepoint Rd. WO 10159769 | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.00064965 | 3.024e-06 | 2016 | 2015-09-28 | B | 2 | 0.0012993 | 6.0475e-06
7229842 | 2015-09-25 10:02 | 2015-09-25 12:27 | 144.6833 | 14 | 2025.5667 | 144.6833 | 141.6833 | 0.0061248 | 1983.5667 | 0.0059978 | 4.2333e-05 | NAPA ID:12522 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FC4217 | Replace DDO's FC4217 and upgrade fuses to 30amp. Works locaitoN: Harbour Lights Terrace, Whitianga. WO 30007220 | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-09-25 | b | 0.0029989 | 2.1166e-05 | 2016 | 2015-09-25 | B | 14 | 0.0059978 | 4.2333e-05
7232328 | 2015-09-09 15:55 | 2015-09-09 17:36 | 100.9833 | 3 | 302.95 | 100.9833 | 97.9833 | 0.00091605 | 293.95 | 0.00088883 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716035 | SVS hub advised. Conductor down at Pole 716035. Re-joined | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-09-09 | c | 0.00088883 | 9.071e-06 | 2016 | 2015-09-09 | C | 3 | 0.00088883 | 9.0713e-06
7234091 | 2015-09-10 06:17 | 2015-09-10 12:51 | 394.5667 | 169 | 41483.1167 | 245.4622 | 242.4622 | 0.12544 | 40976.1167 | 0.1239 | 0.00051102 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 822611 | CB C946 fround tripped at Gladstone Sub after receiving "no power" calls. Feeder patrolled / sectionalised with a floating conductor found. Isolation from Fuses 7637. Replaced a Pin and 11kV Insulator at Pole 822611. Relivened OK. NOTE: OMS issue - Frank | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.1239 | 0.00051102 | 2016 | 2015-09-10 | C | 169 | 0.1239 | 0.00051102
7234412 | 2015-09-25 08:45 | 2015-09-25 12:30 | 224.7833 | 12 | 2697.4 | 224.7833 | 221.7833 | 0.0081563 | 2661.4 | 0.0080474 | 3.6285e-05 | NAPA ID:12636 TP_GREYTOWN GXP > HAU NUI SUB > TUTURUMURI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7165 | REPLACE DEFECTED 11KV TX POLE 2856 AND 11KV PINS AND INSULATORS AT POLE SITES 810514 AND 810516. Works location: Lagoon Hill. WO 30011593 | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-09-25 | b | 0.0040237 | 1.8143e-05 | 2016 | 2015-09-25 | B | 12 | 0.0080474 | 3.6285e-05
7234532 | 2015-09-30 09:17 | 2015-09-30 13:20 | 243.1 | 299 | 72686.9 | 243.1 | 240.1 | 0.21979 | 71789.9 | 0.21708 | 0.0009041 | NAPA ID:11911 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF5-002 | REPLACE POLES AND ARMS ON TE MATAI RD. Works location: Te Matai Rd. WO 30002443 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-30 | b | 0.10854 | 0.00045205 | 2016 | 2015-09-30 | B | 299 | 0.21708 | 0.0009041
7235278 | 2015-09-22 12:49 | 2015-09-22 15:08 | 139 | 68 | 9452 | 139 | 136 | 0.028581 | 9248 | 0.027964 | 0.00020562 | NAPA ID:11270 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 111 | This shutdown is to overlay a new 11kv XPLE cable approximately 200 mtrs from T6/175 to a joint pit in Havelock Ave. Robinson Crescent, Kairanga. W/O 30010934. | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-09-22 | b | 0.013982 | 0.00010281 | 2016 | 2015-09-22 | B | 68 | 0.027964 | 0.00020562
7236541 | 2015-09-15 13:01 | 2015-09-15 18:25 | 323.6833 | 297 | 96133.95 | 323.6833 | 320.6833 | 0.29069 | 95242.95 | 0.28799 | 0.00089806 | NAPA ID:12846 TP_BUNNYTHORPE GXP > MILSON SUB > MILSON | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/531 | This shutdown will have two work sites, Site # 1 Terry Cres, run new 11kv XPLE cable approximately 140 mtrs from T6/531 to a joint pit in McGregor St. Site # 2 Terry Cres, run new 11kv XPLE cable approximately 140 mtrs from T6/533 to a joint pit in McGreg | F1 | RUAHINE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.144 | 0.00044903 | 2016 | 2015-09-15 | B | 297 | 0.28799 | 0.00089806
7237217 | 2015-09-10 10:30 | 2015-09-10 12:08 | 98 | 2 | 196 | 98 | 95 | 0.00059266 | 190 | 0.00057451 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 4146 | 10:30 James Prime was driving past and found Fuses 4146 open. Replaced 2 x 10A Fuses. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.00057452 | 6.048e-06 | 2016 | 2015-09-10 | C | 2 | 0.00057451 | 6.0475e-06
7237273 | 2015-09-10 09:30 | 2015-09-10 12:10 | 160 | 2 | 320 | 160 | 157 | 0.0009676 | 314 | 0.00094946 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Replace transformer T7/321. This is the outage job for follow up job 7222403. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.00094946 | 6.048e-06 | 2016 | 2015-09-10 | C | 2 | 0.00094946 | 6.0475e-06
7239476 | 2015-09-10 16:09 | 2015-09-10 16:13 | 4.05 | 1 | 4.05 | 4.05 | 1.05 | 1.2246e-05 | 1.05 | 3.1749e-06 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1659 | This is the outage job for the child job which was on the wrong transformer. Safety isolation required on 11kV Fuses 7820 to enable replacement of a 200A LV fuse at Transformer T1659. (Old type double isolating Fuses). Relivened OK. | F3 | ESSEX ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-09-10 | c | 3.175e-06 | 3.024e-06 | 2016 | 2015-09-10 | C | 1 | 3.1749e-06 | 3.0238e-06
7239480 | 2015-09-10 16:15 | 2015-09-10 22:44 | 389 | 145 | 21997 | 151.7034 | 148.7034 | 0.066514 | 21562 | 0.065198 | 0.00043845 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227727 | ( PKW 2 ) Recloser S6029 tripped A, B & C Ph O/C, E/F, L/O. Feeder sectionalised. Found line down on spur line to transformer TF8-048 Removed jumpers at main line to isolate fault. Relivened. Needs fuses installed on main line so line can be isolated due | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-10 | c | 0.065198 | 0.00043844 | 2016 | 2015-09-10 | C | 145 | 0.065198 | 0.00043845
7241555 | 2015-09-10 20:50 | 2015-09-10 23:17 | 147.3 | 297 | 24142.5833 | 81.2882 | 78.2882 | 0.073001 | 23251.5833 | 0.070307 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB C917 | CB C917 tripped on E/F flags,line was patrolled and sectionalised and no fault was found, faultman reported at about time of tripping that a small storm passed over the area. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.070307 | 0.00089806 | 2016 | 2015-09-10 | C | 297 | 0.070307 | 0.00089806
7244669 | 2015-09-11 00:57 | 2015-09-11 01:32 | 35.3667 | 473 | 16728.4333 | 35.3667 | 32.3667 | 0.050583 | 15309.4333 | 0.046292 | 0.0014302 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13011 | Found jumper broken on top of DDO at transformer TC4505. Isolated at ABS 332 Repaired jumper & relivened | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-09-11 | c | 0.046292 | 0.0014302 | 2016 | 2015-09-11 | C | 473 | 0.046292 | 0.0014302
7244731 | 2015-09-10 20:53 | 2015-09-11 17:45 | 1252.2833 | 177 | 30948.0833 | 174.8479 | 171.8479 | 0.09358 | 30417.0833 | 0.091974 | 0.00053521 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811768 | Initial tripping on sectionaliser CB C633/2. Patrol carried out during the night but only able to liven to ABS S1203. Patrolling continued during the day but fault proved difficult to locate. Also Staff contending with many outages due to weather and 2 Ca | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.091974 | 0.00053521 | 2016 | 2015-09-10 | C | 177 | 0.091974 | 0.00053521
7244942 | 2015-09-11 00:03 | 2015-09-11 14:02 | 839.2 | 73 | 13471.6 | 184.5425 | 181.5425 | 0.040735 | 13252.6 | 0.040073 | 0.00022073 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 812404 | Recloser C613/2 tripped on A & B phase O/C & E/F flags, received a call from the fire service of car vs pole at pole 812404 transformer T1021 structure, line was isolated at ABS S566 and a TLB was make at pole 812406, fault crew will return in morning to | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.040073 | 0.00022074 | 2016 | 2015-09-11 | C | 73 | 0.040073 | 0.00022073
7245949 | 2015-09-11 06:30 | 2015-09-11 08:24 | 114.2333 | 108 | 5873.95 | 54.3884 | 51.3884 | 0.017761 | 5549.95 | 0.016782 | 0.00032657 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7655 | Brad advised he needs a bucket truck to check the DDo's, believes he may need to replace 3 x DDO's. Requesting 2R. Initial Isolation from Fuses 7655 but unable to repair. Area islated back to ABS S306 to enable full set of fuses / holders to be replaced. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.016782 | 0.00032657 | 2016 | 2015-09-11 | C | 108 | 0.016782 | 0.00032657
7246024 | 2015-09-10 10:40 | 2015-09-11 14:10 | 1649.95 | 22 | 36298.9 | 1649.95 | 1646.95 | 0.10976 | 36232.9 | 0.10956 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837774 | burnt off 11kv cross arms . Isolation carried out from Fuses 7893 to replace a burnt out double crossarm. Also replaced on 10A HT fuse. Relivened OK. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-09-10 | c | 0.10956 | 6.6523e-05 | 2016 | 2015-09-10 | C | 22 | 0.10956 | 6.6523e-05
7246321 | 2015-09-11 07:49 | 2015-09-11 13:40 | 351.4 | 75 | 26355 | 351.4 | 348.4 | 0.079691 | 26130 | 0.079011 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 820030 | Car vs pole police require ETA. (1R) check for safety - car vs pole - person in car trapped as wires all over car P022479981. SH 2 Carterton Bridge, Carterton. police - 04 381 2000. 7.46am advised hub of 999 and taken to control. Jason called to request 2 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.079011 | 0.00022678 | 2016 | 2015-09-11 | C | 75 | 0.079011 | 0.00022678
7246604 | 2015-09-29 09:13 | 2015-09-29 10:55 | 102 | 80 | 7763 | 97.0375 | 94.0375 | 0.023473 | 7523 | 0.022748 | 0.0002419 | NAPA ID:12723 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 383808 | Replace two HV crossarms (off road). Works location: Sutherland Rd. WO 30002442 | F2 | WAIHI RD | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 0.011374 | 0.00012095 | 2016 | 2015-09-29 | B | 80 | 0.022748 | 0.0002419
7246911 | 2015-09-11 11:00 | 2015-09-11 14:30 | 210 | 1 | 210 | 210 | 207 | 0.00063499 | 207 | 0.00062592 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2916 | 13:00 Advised that Transformer blown and replacement is being organised. Replaced Transformer X2916 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.00062592 | 3.024e-06 | 2016 | 2015-09-11 | C | 1 | 0.00062592 | 3.0238e-06
7247091 | 2015-09-29 09:05 | 2015-09-29 15:01 | 355.95 | 19 | 6763.05 | 355.95 | 352.95 | 0.02045 | 6706.05 | 0.020277 | 5.7451e-05 | NAPA ID:11573 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2139 | Replace poles and crossarms at Various sites. Works location: Tapu Coroglen Rd, Thames. WO 30002382 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 0.010139 | 2.8726e-05 | 2016 | 2015-09-29 | B | 19 | 0.020277 | 5.7451e-05
7247373 | 2015-09-11 10:36 | 2015-09-11 12:02 | 86.0667 | 2 | 172.1333 | 86.0667 | 83.0667 | 0.00052049 | 166.1333 | 0.00050235 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 771383 | Outage required beyond fuses 685 to repair 2 broken conductors. Damage had been caused by 3rd party vehicle. Tree contractors ("TREE TAMERS LTD - LEVIN") had cut 2 conductors accidently while trimming trees nearby. (Waverley Racecourse). 1 HT fuse blew a | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-09-11 | c | 0.00050235 | 6.048e-06 | 2016 | 2015-09-11 | C | 2 | 0.00050235 | 6.0475e-06
7247401 | 2015-09-11 10:10 | 2015-09-11 11:20 | 69.9 | 33 | 2306.7 | 69.9 | 66.9 | 0.0069749 | 2207.7 | 0.0066756 | 9.9784e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E28 | Isolated at E27 to repair blown jumper at ABS E28. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.0066756 | 9.9784e-05 | 2016 | 2015-09-11 | C | 33 | 0.0066756 | 9.9784e-05
7247643 | 2015-09-27 21:00 | 2015-09-27 22:42 | 102 | 207 | 19512 | 94.2609 | 91.2609 | 0.059 | 18891 | 0.057122 | 0.00062592 | NAPA ID:12691 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Switch 8973/3 | 11kV Magnefix servicing required full switch gear outage. Works location: South Rd. WO 30004367 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-27 | b | 0.028561 | 0.00031296 | 2016 | 2015-09-27 | B | 207 | 0.057122 | 0.00062592
7247701 | 2015-09-27 12:29 | 2015-09-28 00:30 | 721.3667 | 207 | 1882.5 | 9.0942 | 6.0942 | 0.0056922 | 1261.5 | 0.0038145 | 0.00062592 | NAPA ID:12694 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Switch 389/1 | 11kV Magnefix servicing required full switch gear outage. Works location: South Rd. WO 30004367 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-27 | b | 0.0019072 | 0.00031296 | 2016 | 2015-09-27 | B | 207 | 0.0038145 | 0.00062592
7247721 | 2015-09-28 01:30 | 2015-09-28 02:35 | 64.75 | 28 | 1813 | 64.75 | 61.75 | 0.0054821 | 1729 | 0.0052281 | 8.4665e-05 | NAPA ID:12695 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV ABS 307 | 11kV Magnefix servicing required full switch gear outage. Works location: Popular Gr. WO 30004367 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.002614 | 4.2333e-05 | 2016 | 2015-09-28 | B | 28 | 0.0052281 | 8.4665e-05
7247744 | 2015-09-28 04:00 | 2015-09-28 04:44 | 43.6667 | 111 | 4847 | 43.6667 | 40.6667 | 0.014656 | 4514 | 0.013649 | 0.00033564 | NAPA ID:12696 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Switch 8778/1 | 11kV Magnefix servicing required full switch gear outage. Works location: Popular Gr. WO 30004367 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.0068246 | 0.00016782 | 2016 | 2015-09-28 | B | 111 | 0.013649 | 0.00033564
7247817 | 2015-09-28 21:15 | 2015-09-28 22:35 | 80.1 | 161 | 6781.2667 | 42.1197 | 39.1197 | 0.020505 | 6298.2667 | 0.019044 | 0.00048683 | NAPA ID:12698 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 93 | 11kV Magnefix servicing required full switch gear outage. Works location: Morley St. WO 30004442 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.0095222 | 0.00024341 | 2016 | 2015-09-28 | B | 161 | 0.019044 | 0.00048683
7247823 | 2015-09-28 23:01 | 2015-09-29 00:02 | 61.85 | 161 | 5875.75 | 36.4953 | 33.4953 | 0.017767 | 5392.75 | 0.016306 | 0.00048683 | NAPA ID:12700 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch 47/4 | 11kV Magnefix servicing required full switch gear outage. Works location: Morley St. WO 30004442 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-28 | b | 0.0081532 | 0.00024341 | 2016 | 2015-09-28 | B | 161 | 0.016306 | 0.00048683
7248671 | 2015-09-11 15:16 | 2015-09-11 16:41 | 85.0667 | 115 | 8045.0667 | 69.9571 | 66.9571 | 0.024326 | 7700.0667 | 0.023283 | 0.00034773 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2620 | Tripping on recloser CB2620 on O/C C Phase and E/F. Feeder patrolled and sectionalised but nothing found. Restored OK. Many Ducks sighted. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-09-11 | c | 0.023283 | 0.00034773 | 2016 | 2015-09-11 | C | 115 | 0.023283 | 0.00034773
7248847 | 2015-09-11 18:19 | 2015-09-11 19:05 | 46 | 18 | 828 | 46 | 43 | 0.0025037 | 774 | 0.0023404 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714533 | To replace the nut on the kingbolt.Report from contractor (Radar from Pole Tech) that the nut has come off the king bolt on Pole 714533, Line was isolated at Fuses TA989 to replace the nut on the kingbolt. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-09-11 | c | 0.0023404 | 5.4428e-05 | 2016 | 2015-09-11 | C | 18 | 0.0023404 | 5.4428e-05
7250043 | 2015-09-12 03:41 | 2015-09-12 05:10 | 89.0833 | 20 | 1781.6667 | 89.0833 | 86.0833 | 0.0053873 | 1721.6667 | 0.0052059 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7205 | Faultman foundblown fuses at Fuses 7205, line was patrolled by faultmen and no fault was found reloaded fuses. 2 X 20 amp HV fuses used. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-09-12 | c | 0.0052059 | 6.0475e-05 | 2016 | 2015-09-12 | C | 20 | 0.0052059 | 6.0475e-05
7251467 | 2015-09-12 19:21 | 2015-09-12 20:34 | 73.15 | 2 | 80.3667 | 40.1833 | 37.1833 | 0.00024301 | 74.3667 | 0.00022487 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7660 | 2 HT Fuses found tripped at 7660. (Feeds transformer T2938). Fault shown as T1782 (Upstream of fuses, suspect GIS error). Reloaded OK. Rating 10A. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-12 | c | 0.00022487 | 6.048e-06 | 2016 | 2015-09-12 | C | 2 | 0.00022487 | 6.0475e-06
7251476 | 2015-09-12 21:03 | 2015-09-12 21:44 | 40.65 | 2 | 81.3 | 40.65 | 37.65 | 0.00024583 | 75.3 | 0.00022769 | 6.0475e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3179T | 2 HT Fuses found tripped at Transformer 3179T. Reloaded OK. (3A Rating). | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-09-12 | c | 0.00022769 | 6.048e-06 | 2016 | 2015-09-12 | C | 2 | 0.00022769 | 6.0475e-06
7253352 | 2015-09-13 00:04 | 2015-09-13 18:45 | 1121 | 857 | 49681.5667 | 57.9715 | 54.9715 | 0.15023 | 47110.5667 | 0.14245 | 0.0025914 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 790091 | Fault found between Links 705 and Fuses 2890 during sectionlising during the night. fault Isolated at links 705 Faultman continued in morning coms issues so given control past links 705 - lines found down at pole 790091 caused by tree - used 50 mtrs of | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-09-13 | c | 0.14245 | 0.0025914 | 2016 | 2015-09-13 | C | 857 | 0.14245 | 0.0025914
7257237 | 2015-09-13 09:13 | 2015-09-13 11:06 | 112.9667 | 7 | 622.4667 | 88.9238 | 85.9238 | 0.0018822 | 601.4667 | 0.0018187 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826192 | 2 Fuses found blown at Fuses 7659, Faultman aware of fault during night and fuses replaced at Fuses 7660 - line patrolled with duck found at pole 826192 - Faultman check fuse sizes and found both sets were 10 amp fuses - fuses 7660 down graded to 3 amp as | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-13 | c | 0.0018187 | 2.1166e-05 | 2016 | 2015-09-13 | C | 7 | 0.0018187 | 2.1166e-05
7257422 | 2015-09-13 09:42 | 2015-09-13 10:42 | 60.6167 | 1 | 60.6167 | 60.6167 | 57.6167 | 0.00018329 | 57.6167 | 0.00017422 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of HV planned outage, advised customer of restoration time | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-09-13 | c | 0.00017422 | 3.024e-06 | 2016 | 2015-09-13 | C | 1 | 0.00017422 | 3.0238e-06
7257621 | 2015-09-13 11:34 | 2015-09-13 13:17 | 103.85 | 10 | 1038.5 | 103.85 | 100.85 | 0.0031402 | 1008.5 | 0.0030495 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M9 | 2 Fuses found Blown at Fuses M9 - used 2 x 15 amp fuses Suspected bird strike | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-13 | c | 0.0030495 | 3.0238e-05 | 2016 | 2015-09-13 | C | 10 | 0.0030495 | 3.0238e-05
7259061 | 2015-09-13 19:49 | 2015-09-14 16:48 | 1259 | 804 | 3681.3833 | 4.5788 | 1.5788 | 0.011132 | 1269.3833 | 0.0038383 | 0.0024311 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TX 1649 | 2 HT Fuses found tripped at 8472. (Supplies TX1649 (Not TX741 as this job states - suspect error). Area patrolled - looked Ok but CB 8761 tripped on reclosing fuses. Fuses Checked open and CB reclosed. Suspect 11kV Cable fault supplying Transformer 1649 | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-13 | c | 0.0038383 | 0.0024311 | 2016 | 2015-09-13 | C | 804 | 0.0038383 | 0.0024311
7261127 | 2015-09-14 04:08 | 2015-09-14 05:59 | 110.85 | 2 | 221.7 | 110.85 | 107.85 | 0.00067037 | 215.7 | 0.00065223 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1535 | At Fuses FP1535 2x6amp HV Fuses blown. Possible cause a bird through the line as it crosses a canal. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-09-14 | c | 0.00065222 | 6.048e-06 | 2016 | 2015-09-14 | C | 2 | 0.00065223 | 6.0475e-06
7261453 | 2015-09-30 08:46 | 2015-09-30 14:54 | 368.3667 | 7 | 2578.5667 | 368.3667 | 365.3667 | 0.007797 | 2557.5667 | 0.0077335 | 2.1166e-05 | NAPA ID:11622 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212268 | Replace poles hardware and conductor between poles 212268 - 212283. Works location: McLaren Falls Rd. WO 30002540 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-30 | b | 0.0038667 | 1.0583e-05 | 2016 | 2015-09-30 | B | 7 | 0.0077335 | 2.1166e-05
7261524 | 2015-09-20 09:55 | 2015-09-20 10:42 | 47.35 | 1 | 47.35 | 47.35 | 44.35 | 0.00014318 | 44.35 | 0.0001341 | 3.0238e-06 | NAPA ID:12918 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ARMSTRONG ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/678 | Test permit to test cable. Then liven and check phasing at T6/678. Shut cables down and close the line break at T6/678. Transformer T6/678 only feeds one customer and they have agreed to this shutdown on sunday to reconnect the cables. | F2 | ARMSTRONG ST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-20 | b | 6.7052e-05 | 1.512e-06 | 2016 | 2015-09-20 | B | 1 | 0.0001341 | 3.0238e-06
7262281 | 2015-09-14 09:32 | 2015-09-14 11:56 | 144.5333 | 10 | 1445.3333 | 144.5333 | 141.5333 | 0.0043703 | 1415.3333 | 0.0042796 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M9 | Reload Reliven at Fuses M9. 3 x 15 Amp fuses. (worked through and notes entered in by control). Also restrained guy wire at HV pole P18601 using a dead end to restrain the Stay wire | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-14 | c | 0.0042796 | 3.0238e-05 | 2016 | 2015-09-14 | C | 10 | 0.0042796 | 3.0238e-05
7262904 | 2015-09-22 08:35 | 2015-09-22 16:47 | 491.8833 | 180 | 48279.4167 | 268.219 | 265.219 | 0.14599 | 47739.4167 | 0.14435 | 0.00054428 | NAPA ID:12937 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 735012 | Tasman Parade replace poles 753012 ,753913,753915 753916, 753917,753918 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-09-22 | b | 0.072176 | 0.00027214 | 2016 | 2015-09-22 | B | 180 | 0.14435 | 0.00054428
7263291 | 2015-09-24 08:31 | 2015-09-24 15:38 | 427.2 | 180 | 19116 | 106.2 | 103.2 | 0.057802 | 18576 | 0.056169 | 0.00054428 | NAPA ID:12945 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12101/1 | Reconductor between poles 753918 & 440215.APPLICANT HAS REQUESTED HV OFF AT 0830. RESTORATION 1530HRS. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-09-24 | b | 0.028085 | 0.00027214 | 2016 | 2015-09-24 | B | 180 | 0.056169 | 0.00054428
7263646 | 2015-10-01 09:00 | 2015-10-01 12:09 | 189 | 5 | 945 | 189 | 186 | 0.0028575 | 930 | 0.0028121 | 1.5119e-05 | NAPA ID:12547 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5935 | Replace Crossarm at TC5935. Works location: Station Rd, Te Aroha. WO 30002440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.001406 | 7.559e-06 | 2016 | 2015-10-01 | B | 5 | 0.0028121 | 1.5119e-05
7263737 | 2015-10-01 11:08 | 2015-10-01 12:53 | 105.15 | 2 | 210.3 | 105.15 | 102.15 | 0.0006359 | 204.3 | 0.00061775 | 6.0475e-06 | NAPA ID:12294 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1382 | Replace cross arm at pole D12761. Works location: Maungatautari Rd. WO 30002692 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.00030888 | 3.024e-06 | 2016 | 2015-10-01 | B | 2 | 0.00061775 | 6.0475e-06
7263770 | 2015-10-01 13:54 | 2015-10-01 14:40 | 45.8167 | 31 | 1420.3167 | 45.8167 | 42.8167 | 0.0042947 | 1327.3167 | 0.0040135 | 9.3737e-05 | NAPA ID:12295 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1313 | Replace X arm at pole D1388. Works location: Hicks Rd, Maungatautari. WO 30002692 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.0020067 | 4.6868e-05 | 2016 | 2015-10-01 | B | 31 | 0.0040135 | 9.3737e-05
7263970 | 2015-10-02 10:15 | 2015-10-02 11:10 | 55 | 1 | 55 | 55 | 52 | 0.00016631 | 52 | 0.00015724 | 3.0238e-06 | NAPA ID:12334 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP592 | Pole 269292 - replace LV arm. Works location: Wilsdown Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 7.8618e-05 | 1.512e-06 | 2016 | 2015-10-02 | B | 1 | 0.00015724 | 3.0238e-06
7264011 | 2015-09-14 13:49 | 2015-09-14 14:53 | 63.9667 | 34 | 2174.8667 | 63.9667 | 60.9667 | 0.0065763 | 2072.8667 | 0.0062679 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS IC289 | Repair broken hardware at ABS IC289. Live line work that could not be completed on the day without a shutdown as closer inspection revealed 2 glass strains had obvious defects (cracks and tracking). 3 x disc strains replaced with polymer strains. Part of | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-09-14 | c | 0.0062679 | 0.00010281 | 2016 | 2015-09-14 | C | 34 | 0.0062679 | 0.00010281
7264068 | 2015-09-14 13:53 | 2015-09-14 14:59 | 65.8833 | 2 | 131.7667 | 65.8833 | 62.8833 | 0.00039843 | 125.7667 | 0.00038029 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6064 | 2 x 20 Amp Fuses. Suspect Bird Strike | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-09-14 | c | 0.00038029 | 6.048e-06 | 2016 | 2015-09-14 | C | 2 | 0.00038029 | 6.0475e-06
7264088 | 2015-10-02 13:03 | 2015-10-02 14:15 | 72 | 5 | 360 | 72 | 69 | 0.0010886 | 345 | 0.0010432 | 1.5119e-05 | NAPA ID:12331 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC301 | Pole M12846 - replace LV arm. Works location: Old Taupo Rd, Putaruru. WO 30011798 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.0005216 | 7.559e-06 | 2016 | 2015-10-02 | B | 5 | 0.0010432 | 1.5119e-05
7264358 | 2015-10-02 09:08 | 2015-10-02 15:17 | 369.2667 | 78 | 8351.2 | 107.0667 | 104.0667 | 0.025252 | 8117.2 | 0.024544 | 0.00023585 | NAPA ID:11973 TP_KINLEITH GXP > BAIRD ROAD SUB > RATA ST BAIRD ROAD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC5028 | To Remove the 11kV cable from the side box of FC5028 to LC1546 & Reliven FC5028 & TC3053. To Remove the cable from LC1546 and relocate to 9983/1. To Test the cable. To reconect the cable to FC5028. Works location: Tasman Dr, TOkoroa. WO 30002539 | F3 | RATA ST BAIRD ROAD | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.012272 | 0.00011793 | 2016 | 2015-10-02 | B | 78 | 0.024544 | 0.00023585
7264748 | 2015-10-01 14:00 | 2015-10-01 14:30 | 30 | 8 | 240 | 30 | 27 | 0.0007257 | 216 | 0.00065313 | 2.419e-05 | NAPA ID:11829 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1944 | To install a 400V Fuse Disconector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.00032657 | 1.2095e-05 | 2016 | 2015-10-01 | B | 8 | 0.00065313 | 2.419e-05
7264776 | 2015-10-05 10:40 | 2015-10-05 13:30 | 170 | 5 | 850 | 170 | 167 | 0.0025702 | 835 | 0.0025248 | 1.5119e-05 | NAPA ID:11576 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2082 | Install a 400V Fuse/Disconector. Works location: Hwy 26, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.0012624 | 7.559e-06 | 2016 | 2015-10-05 | B | 5 | 0.0025248 | 1.5119e-05
7264792 | 2015-09-15 09:45 | 2015-09-15 10:28 | 43 | 52 | 2236 | 43 | 40 | 0.0067611 | 2080 | 0.0062894 | 0.00015724 | NAPA ID:12948 TP_MATAROA GXP > WAIOURU SUB > IRIRANGI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 2635 | Replace 11 kv polymer strain and make temp fix on burnt termination xarm at pole 779930 ( pole to be defected and change at later date ) | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-09-15 | b | 0.0031447 | 7.8618e-05 | 2016 | 2015-09-15 | B | 52 | 0.0062894 | 0.00015724
7264822 | 2015-10-06 12:00 | 2015-10-06 12:30 | 30 | 10 | 300 | 30 | 27 | 0.00090713 | 270 | 0.00081642 | 3.0238e-05 | NAPA ID:11831 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC268 | To install a 400V Fuse/Disconnector. Works location: Maungatapu Rd, Morrinsville. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-06 | b | 0.00040821 | 1.5119e-05 | 2016 | 2015-10-06 | B | 10 | 0.00081642 | 3.0238e-05
7264829 | 2015-10-06 13:00 | 2015-10-06 13:45 | 45 | 1 | 45 | 45 | 42 | 0.00013607 | 42 | 0.000127 | 3.0238e-06 | NAPA ID:11832 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP997 | To install a 400V Fuse/Disconnector. Works location: Roach Rd, Morrinsville. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-06 | b | 6.3499e-05 | 1.512e-06 | 2016 | 2015-10-06 | B | 1 | 0.000127 | 3.0238e-06
7264876 | 2015-10-01 09:00 | 2015-10-01 14:47 | 347 | 8 | 2776 | 347 | 344 | 0.008394 | 2752 | 0.0083214 | 2.419e-05 | NAPA ID:11898 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T44 | Replace pole and install new conductor. Works location: Kaitawa Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0041607 | 1.2095e-05 | 2016 | 2015-10-01 | B | 8 | 0.0083214 | 2.419e-05
7270846 | 2015-10-02 09:15 | 2015-10-02 10:51 | 95.4333 | 4 | 381.7333 | 95.4333 | 92.4333 | 0.0011543 | 369.7333 | 0.001118 | 1.2095e-05 | NAPA ID:12419 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2168 | Install riser on pole M2258 to prevent line clash. Works location: Ngatira Rd, Lichfield. WO 30000090 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.00055899 | 6.048e-06 | 2016 | 2015-10-02 | B | 4 | 0.001118 | 1.2095e-05
7270959 | 2015-10-05 09:44 | 2015-10-05 13:40 | 236 | 3 | 708 | 236 | 233 | 0.0021408 | 699 | 0.0021136 | 9.0713e-06 | NAPA ID:12279 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4556 | Pole M12840 & TC4556 - replace all crossarms + install LV disconnectors. Works location: Old Taupo Rd, Putaruru. WO 30011798 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.0010568 | 4.536e-06 | 2016 | 2015-10-05 | B | 3 | 0.0021136 | 9.0713e-06
7271022 | 2015-10-01 08:46 | 2015-10-01 10:32 | 106 | 61 | 6466 | 106 | 103 | 0.019552 | 6283 | 0.018998 | 0.00018445 | NAPA ID:12180 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | J41 | Repair 11kV PILC pot head. Works location: North St. WO 10162295 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0094991 | 9.2225e-05 | 2016 | 2015-10-01 | B | 61 | 0.018998 | 0.00018445
7271032 | 2015-10-05 09:12 | 2015-10-05 14:35 | 323 | 5 | 1615 | 323 | 320 | 0.0048834 | 1600 | 0.004838 | 1.5119e-05 | NAPA ID:12247 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I1618 | To Break the jumpers on Pole I1618 suppling Haynes Rd TC3019. To replace arms & Hardware on Haynes Road. To replace the jumpers on Pole I1618 supplying Haynes Rd TC3019. Works location: Haynes Rd, Morrinsville. WO 30013575. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.002419 | 7.559e-06 | 2016 | 2015-10-05 | B | 5 | 0.004838 | 1.5119e-05
7271049 | 2015-10-01 09:15 | 2015-10-01 11:20 | 125 | 4 | 500 | 125 | 122 | 0.0015119 | 488 | 0.0014756 | 1.2095e-05 | NAPA ID:12265 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/76 | Replace Transformer and LV crossarms at T1/76. work Location: Rongotea Road, Palmerston North. W/O 30012048 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0007378 | 6.048e-06 | 2016 | 2015-10-01 | B | 4 | 0.0014756 | 1.2095e-05
7271191 | 2015-10-01 09:30 | 2015-10-01 13:39 | 249 | 86 | 21036 | 244.6047 | 241.6047 | 0.063608 | 20778 | 0.062828 | 0.00026004 | NAPA ID:12483 TP_MANGAMAIRE GXP > MANGAMUTU SUB > KONINI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5 | Change ABS T8 and Hard Wood pole DNO #150720. Works location: Hwy 2. WO 30013004 | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.031414 | 0.00013002 | 2016 | 2015-10-01 | B | 86 | 0.062828 | 0.00026004
7271198 | 2015-10-06 10:23 | 2015-10-06 14:34 | 251.0667 | 60 | 15064 | 251.0667 | 248.0667 | 0.04555 | 14884 | 0.045006 | 0.00018143 | NAPA ID:11761 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2564 | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title ?IR7453 Cambridge Rd Pole Renewal. Works location: Hwy 1. WO 30003711 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-06 | b | 0.022503 | 9.0713e-05 | 2016 | 2015-10-06 | B | 60 | 0.045006 | 0.00018143
7271229 | 2015-10-01 10:00 | 2015-10-01 14:20 | 260 | 6 | 1560 | 260 | 257 | 0.0047171 | 1542 | 0.0046626 | 1.8143e-05 | NAPA ID:12242 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/35 | Replace 11KV arms & Trani T1/35 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0023313 | 9.071e-06 | 2016 | 2015-10-01 | B | 6 | 0.0046626 | 1.8143e-05
7271275 | 2015-10-08 11:06 | 2015-10-08 14:18 | 191.8167 | 8 | 1534.5333 | 191.8167 | 188.8167 | 0.0046401 | 1510.5333 | 0.0045675 | 2.419e-05 | NAPA ID:11767 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 865 | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title ?IR7453 Cambridge Rd Pole Renewal. Works location: Hwy 1. WO 30003711 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.0022837 | 1.2095e-05 | 2016 | 2015-10-08 | B | 8 | 0.0045675 | 2.419e-05
7271286 | 2015-09-15 10:32 | 2015-09-15 11:42 | 70.15 | 1 | 70.15 | 70.15 | 67.15 | 0.00021212 | 67.15 | 0.00020305 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC5989 | this customer is part of a shut down - suspect customer is fed from wrong tx and wont have been carded. North power have an LV shut down. Power due to go on around 13:00. Only LV fuses. Customer not home to advised. Thinks they are fed from TC5989 17- | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-15 | c | 0.00020305 | 3.024e-06 | 2016 | 2015-09-15 | C | 1 | 0.00020305 | 3.0238e-06
7273145 | 2015-10-01 10:00 | 2015-10-01 12:29 | 149 | 3 | 447 | 149 | 146 | 0.0013516 | 438 | 0.0013244 | 9.0713e-06 | NAPA ID:12051 TP_GREYTOWN GXP > FEATHERSTON SUB > DAIRY FACTORY | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 799516 | Replace 11kV pole. Works location: Kahutara Rd, Featherston. WO 10153828 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0006622 | 4.536e-06 | 2016 | 2015-10-01 | B | 3 | 0.0013244 | 9.0713e-06
7274869 | 2015-10-05 11:07 | 2015-10-05 14:13 | 186.0167 | 32 | 5952.5333 | 186.0167 | 183.0167 | 0.017999 | 5856.5333 | 0.017709 | 9.676e-05 | NAPA ID:12069 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links T2 | Replace Rotten Hv/Lv xarms on poles 730990/2. Works location: Victoria St, Kaponga. WO 30007510 | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 0.0088544 | 4.838e-05 | 2016 | 2015-10-05 | B | 32 | 0.017709 | 9.676e-05
7274956 | 2015-10-07 12:00 | 2015-10-07 12:30 | 30 | 1 | 30 | 30 | 27 | 9.0713e-05 | 27 | 8.1642e-05 | 3.0238e-06 | NAPA ID:11840 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1771 | To install a 400V Fuse/Disconector. Works location: Kiwitahi Railway Rd, Morrinsville. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 4.0821e-05 | 1.512e-06 | 2016 | 2015-10-07 | B | 1 | 8.1642e-05 | 3.0238e-06
7274977 | 2015-10-07 10:00 | 2015-10-07 10:55 | 55 | 4 | 220 | 55 | 52 | 0.00066523 | 208 | 0.00062894 | 1.2095e-05 | NAPA ID:11836 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC239 | To install a 400V Fuse Disconector. Works location: Kiwitahi Railway Rd, Morrinsville. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 0.00031447 | 6.048e-06 | 2016 | 2015-10-07 | B | 4 | 0.00062894 | 1.2095e-05
7277768 | 2015-10-08 13:00 | 2015-10-08 13:35 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 | NAPA ID:11848 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5588 | To replace the 400V Pin arm & install a 400V Fuse/Disconector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.00019352 | 6.048e-06 | 2016 | 2015-10-08 | B | 4 | 0.00038704 | 1.2095e-05
7281645 | 2015-10-01 10:15 | 2015-10-01 13:49 | 214 | 21 | 4494 | 214 | 211 | 0.013589 | 4431 | 0.013398 | 6.3499e-05 | NAPA ID:12221 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 824181 | Isolate both sides of S316 so that the strain arms and the ABS can be replaced. Works location: Carters Line, Carterton. WO 10159903 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-01 | b | 0.0066991 | 3.1749e-05 | 2016 | 2015-10-01 | B | 21 | 0.013398 | 6.3499e-05
7282235 | 2015-10-09 13:00 | 2015-10-09 13:50 | 50 | 6 | 300 | 50 | 47 | 0.00090713 | 282 | 0.0008527 | 1.8143e-05 | NAPA ID:11945 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5776 | To install a 400V Fuse/Disconnector. Works location: Brunskill Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-09 | b | 0.00042635 | 9.071e-06 | 2016 | 2015-10-09 | B | 6 | 0.0008527 | 1.8143e-05
7283621 | 2015-10-05 09:20 | 2015-10-05 10:00 | 40 | 1 | 40 | 40 | 37 | 0.00012095 | 37 | 0.00011188 | 3.0238e-06 | NAPA ID:12420 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | X2767 | Lower taps on transformer X2767 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 5.594e-05 | 1.512e-06 | 2016 | 2015-10-05 | B | 1 | 0.00011188 | 3.0238e-06
7283668 | 2015-10-05 10:30 | 2015-10-05 11:00 | 30 | 2 | 60 | 30 | 27 | 0.00018143 | 54 | 0.00016328 | 6.0475e-06 | NAPA ID:12451 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | x2857 | lower tap on Transformer X2857 voltage to high | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 8.1642e-05 | 3.024e-06 | 2016 | 2015-10-05 | B | 2 | 0.00016328 | 6.0475e-06
7283680 | 2015-09-22 10:57 | 2015-09-22 12:11 | 74.1 | 140 | 10374 | 74.1 | 71.1 | 0.031368 | 9954 | 0.030099 | 0.00042333 | NAPA ID:11882 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > MOUNT | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5-011 | AP1 - Disconnect cable to Link box TC5-012 at TC5-011. Open Fuses SC5-029 - L1 & TC5-012 - L1. AP2 - Remove Link box SC5-029 & TC5-012 and replace with CFCF 9985 and CFC 9986. Transfer transformer TC5-013 to Fuse/Sw 9985/2 and TC5-012 to Fuse/Sw 9985/4 | F2 | MOUNT | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-09-22 | b | 0.015049 | 0.00021166 | 2016 | 2015-09-22 | B | 140 | 0.030099 | 0.00042333
7283689 | 2015-10-05 11:05 | 2015-10-05 11:15 | 10 | 2 | 20 | 10 | 7 | 6.0475e-05 | 14 | 4.2333e-05 | 6.0475e-06 | NAPA ID:12456 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | x1514 | Lower tap on Transformer X1514 voltage to high | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 2.1166e-05 | 3.024e-06 | 2016 | 2015-10-05 | B | 2 | 4.2333e-05 | 6.0475e-06
7283718 | 2015-10-05 13:00 | 2015-10-05 13:25 | 25 | 4 | 100 | 25 | 22 | 0.00030238 | 88 | 0.00026609 | 1.2095e-05 | NAPA ID:12458 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | X507 | Lower tap on Transformer X507 voltage to high | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 0.00013305 | 6.048e-06 | 2016 | 2015-10-05 | B | 4 | 0.00026609 | 1.2095e-05
7283816 | 2015-10-05 14:00 | 2015-10-05 14:25 | 25 | 1 | 25 | 25 | 22 | 7.5594e-05 | 22 | 6.6523e-05 | 3.0238e-06 | NAPA ID:12465 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X3198 | Lower tap on Transformer X3198 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 3.3261e-05 | 1.512e-06 | 2016 | 2015-10-05 | B | 1 | 6.6523e-05 | 3.0238e-06
7283848 | 2015-10-05 11:55 | 2015-10-05 13:28 | 93 | 7 | 651 | 93 | 90 | 0.0019685 | 630 | 0.001905 | 2.1166e-05 | NAPA ID:12875 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 22 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Z50 | Replace transformer Z50. Work Location: Main Street, Hunterville. WO 10162459 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-10-05 | b | 0.00095248 | 1.0583e-05 | 2016 | 2015-10-05 | B | 7 | 0.001905 | 2.1166e-05
7284022 | 2015-10-01 09:52 | 2015-10-01 14:10 | 258 | 55 | 14190 | 258 | 255 | 0.042907 | 14025 | 0.042408 | 0.00016631 | NAPA ID:12623 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1314 | Upgrade TC1314 to a 300kVA. Works location: Main Rd, Tairua. WO 30013442 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.021204 | 8.3153e-05 | 2016 | 2015-10-01 | B | 55 | 0.042408 | 0.00016631
7287857 | 2015-09-16 01:09 | 2015-09-16 01:15 | 5.5167 | 491 | 2643.2167 | 5.3833 | 2.3833 | 0.0079925 | 1170.2167 | 0.0035385 | 0.0014847 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB5 Tripped B Phase O/C E/ F Lock Out - VS 10002 didn't open when Auto Back feed system via Switch F481 operated so no power lost. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-16 | c | 0.0035385 | 0.0014847 | 2016 | 2015-09-16 | C | 491 | 0.0035385 | 0.0014847
7290384 | 2015-10-13 09:04 | 2015-10-13 15:14 | 370.5 | 24 | 8892 | 370.5 | 367.5 | 0.026887 | 8820 | 0.02667 | 7.257e-05 | NAPA ID:12580 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T16 | Replace poles P37443, P37444, P37445, P37467, P37468. Works location: Tiraumea Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.013335 | 3.6285e-05 | 2016 | 2015-10-13 | B | 24 | 0.02667 | 7.257e-05
7290391 | 2015-09-29 01:30 | 2015-09-29 02:31 | 60.6667 | 237 | 14378 | 60.6667 | 57.6667 | 0.043476 | 13667 | 0.041326 | 0.00071663 | NAPA ID:12703 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 263 | 11kV Magnefix servicing required full switch gear outage. This follows NAPA 12700. Works location: Cutfield Rd. WO 30004442 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-29 | b | 0.020663 | 0.00035832 | 2016 | 2015-09-29 | B | 237 | 0.041326 | 0.00071663
7290405 | 2015-10-15 09:05 | 2015-10-15 15:11 | 366.05 | 24 | 8785.2 | 366.05 | 363.05 | 0.026564 | 8713.2 | 0.026347 | 7.257e-05 | NAPA ID:12581 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS T16 | Replace poles P37469, P37470, P37471, P37472, P37473. Works location: TIraumea Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-15 | b | 0.013173 | 3.6285e-05 | 2016 | 2015-10-15 | B | 24 | 0.026347 | 7.257e-05
7290427 | 2015-10-06 09:03 | 2015-10-06 10:35 | 92.3167 | 162 | 14955.3 | 92.3167 | 89.3167 | 0.045221 | 14469.3 | 0.043752 | 0.00048985 | NAPA ID:12946 TP_MARTON GXP > BULLS SUB > RACECOURSE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 446 | Fit new 11kV shackle point to pole 803712. Works location: Hwy 1 and Criterion St, Bulls. WO 30007762 | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-10-06 | b | 0.021876 | 0.00024493 | 2016 | 2015-10-06 | B | 162 | 0.043752 | 0.00048985
7290448 | 2015-09-29 09:12 | 2015-09-29 15:51 | 398.9167 | 37 | 14759.9167 | 398.9167 | 395.9167 | 0.04463 | 14648.9167 | 0.044295 | 0.00011188 | NAPA ID:11668 TP_KINLEITH GXP > MARAETAI ROAD SUB > BALMORAL DR | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1508 | Replace NMagnifix (re-use existing labels) & Upgrade Transformer. Works location: Balmoral Dr, Tokoroa. WO 30002433 | F3 | BALMORAL DR | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-09-29 | b | 0.022147 | 5.594e-05 | 2016 | 2015-09-29 | B | 37 | 0.044295 | 0.00011188
7290463 | 2015-10-06 08:57 | 2015-10-06 11:37 | 160.4833 | 6 | 962.9 | 160.4833 | 157.4833 | 0.0029116 | 944.9 | 0.0028572 | 1.8143e-05 | NAPA ID:12363 TP_MASTERTON GXP > GLADSTONE SUB > PUKETIRO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7635 | Replace 11kV crossarms. Works location: Buchanan Rd, Carterton. WO 30012233 | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-06 | b | 0.0014286 | 9.071e-06 | 2016 | 2015-10-06 | B | 6 | 0.0028572 | 1.8143e-05
7290564 | 2015-10-01 08:45 | 2015-10-01 14:50 | 365 | 4 | 1460 | 365 | 362 | 0.0044147 | 1448 | 0.0043784 | 1.2095e-05 | NAPA ID:12359 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4018 | Replace pole at TC5023. Works location: Manaia Rd, Coromandel. WO 30010651 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-01 | b | 0.0021892 | 6.048e-06 | 2016 | 2015-10-01 | B | 4 | 0.0043784 | 1.2095e-05
7291015 | 2015-10-02 10:14 | 2015-10-02 12:57 | 163 | 6 | 978 | 163 | 160 | 0.0029572 | 960 | 0.0029028 | 1.8143e-05 | NAPA ID:12724 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2931 | Upgrade TC2931 to 50kVA | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.0014514 | 9.071e-06 | 2016 | 2015-10-02 | B | 6 | 0.0029028 | 1.8143e-05
7292494 | 2015-10-09 10:00 | 2015-10-09 11:00 | 60 | 6 | 360 | 60 | 57 | 0.0010886 | 342 | 0.0010341 | 1.8143e-05 | NAPA ID:11942 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC708 | To replace the 400V pin arm & install a 400v Fuse/Disconnector. Works location; Te Miro Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-09 | b | 0.00051706 | 9.071e-06 | 2016 | 2015-10-09 | B | 6 | 0.0010341 | 1.8143e-05
7292563 | 2015-10-12 09:30 | 2015-10-12 15:11 | 341.3333 | 18 | 6143.6667 | 341.3148 | 338.3148 | 0.018577 | 6089.6667 | 0.018414 | 5.4428e-05 | NAPA ID:12414 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI771 | Replace poles along Ball rd Beyond ABS LI771. Works location: Ball Rd, Hurleyville. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-12 | b | 0.0092068 | 2.7214e-05 | 2016 | 2015-10-12 | B | 18 | 0.018414 | 5.4428e-05
7296409 | 2015-10-15 09:25 | 2015-10-15 15:07 | 341.75 | 6 | 2050.5 | 341.75 | 338.75 | 0.0062002 | 2032.5 | 0.0061458 | 1.8143e-05 | NAPA ID:12455 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV LI730 | Replace poles and Xarms on Ball rd Alton. Works location: Ball Rd, Alton. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-15 | b | 0.0030729 | 9.071e-06 | 2016 | 2015-10-15 | B | 6 | 0.0061458 | 1.8143e-05
7296509 | 2015-10-02 09:32 | 2015-10-02 14:47 | 314.8 | 2 | 629.6 | 314.8 | 311.8 | 0.0019038 | 623.6 | 0.0018856 | 6.0475e-06 | NAPA ID:12165 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 752707 | Replace pole 752707 with new TX termination pole existing TX 1545 to be relocated to new site cut away existing 11kv line beyond new TX site & install new low cable up pole into LV disconnects | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-02 | b | 0.00094281 | 3.024e-06 | 2016 | 2015-10-02 | B | 2 | 0.0018856 | 6.0475e-06
7301195 | 2015-10-12 10:26 | 2015-10-12 14:54 | 268.1333 | 3 | 804.4 | 268.1333 | 265.1333 | 0.0024323 | 795.4 | 0.0024051 | 9.0713e-06 | NAPA ID:12348 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M12522 | Pole M12522 - Replace Pole and all hardware. Works location: Waotu Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-12 | b | 0.0012025 | 4.536e-06 | 2016 | 2015-10-12 | B | 3 | 0.0024051 | 9.0713e-06
7301308 | 2015-10-22 09:03 | 2015-10-22 13:21 | 258.1833 | 5 | 1290.9167 | 258.1833 | 255.1833 | 0.0039034 | 1275.9167 | 0.0038581 | 1.5119e-05 | NAPA ID:12448 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3192 | Pole: M1557 requires blocking. Poles: M1559, M1558, M1557, M1556, M1555, M1554 & M1553- Replace all 11kV arms. Works location: Old Taupo Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-22 | b | 0.001929 | 7.559e-06 | 2016 | 2015-10-22 | B | 5 | 0.0038581 | 1.5119e-05
7301360 | 2015-10-19 10:04 | 2015-10-19 14:58 | 294.2667 | 1 | 294.2667 | 294.2667 | 291.2667 | 0.00088979 | 291.2667 | 0.00088072 | 3.0238e-06 | NAPA ID:12432 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M12397 | Pole M12397: Replace 11kV arm, TC1902 DDO arm, TC1902, install LV disconnectors, replace LV x-arm. Pole M1041: Replace LV arm. Works location: Lichfield Rd, Putaruru. WO 30011798 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-19 | b | 0.00044036 | 1.512e-06 | 2016 | 2015-10-19 | B | 1 | 0.00088072 | 3.0238e-06
7301375 | 2015-10-06 08:31 | 2015-10-06 15:41 | 430 | 51 | 21930 | 430 | 427 | 0.066311 | 21777 | 0.065848 | 0.00015421 | NAPA ID:12166 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 831551 | Replace 33,11KV pole 831554. Works location: Oak St, Masterton. WO 30008180 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-10-06 | b | 0.032924 | 7.7106e-05 | 2016 | 2015-10-06 | B | 51 | 0.065848 | 0.00015421
7301752 | 2015-09-16 17:12 | 2015-09-16 19:16 | 124.35 | 624 | 14744.85 | 23.6296 | 20.6296 | 0.044585 | 12872.85 | 0.038924 | 0.0018868 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | poss related to oms 7301425 Recloser V5 A/R. CB 1332 A/R, L/O, O/C, E/F Power lost to Pongoroa Sub. PON CB 1 Opened by NOC Pongoroa Sub backfed by closing PON CB XT50 Partial Patrol completed on CB 1332. No fault found. Relivened ok CB 1 Relivened ok up | F1,F2,F3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2015-09-16 | c | 0.038924 | 0.0018868 | 2016 | 2015-09-16 | C | 624 | 0.038924 | 0.0018868
7302566 | 2015-09-16 19:13 | 2015-09-16 19:35 | 22.0333 | 2 | 44.0667 | 22.0333 | 19.0333 | 0.00013325 | 38.0667 | 0.0001151 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 1228 LAKE FERRY ROAD | Isolate due to tree sitting on line. 5.54pm - advise smc. 2R. tree affecting HV line, has spoken to control and this will be done tomorrow as is unsafe to do now, farmer happy to be without power for the night. will work through control tomorrow. tree rem | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-09-16 | c | 0.0001151 | 6.048e-06 | 2016 | 2015-09-16 | C | 2 | 0.0001151 | 6.0475e-06
7302680 | 2015-09-16 18:28 | 2015-09-16 19:40 | 72.4167 | 4 | 289.6667 | 72.4167 | 69.4167 | 0.00087588 | 277.6667 | 0.0008396 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1091 | Reloaded, Relivened 2x DDO's at Fuses FP1091 caused by a pukeko flying into the lines. Paul Cooper Attended. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-09-16 | c | 0.0008396 | 1.2095e-05 | 2016 | 2015-09-16 | C | 4 | 0.0008396 | 1.2095e-05
7302907 | 2015-09-16 20:06 | 2015-09-17 13:42 | 1056.4833 | 2 | 2112.9667 | 1056.4833 | 1053.4833 | 0.0063891 | 2106.9667 | 0.006371 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V7 | Blown jumper at Links V6 causing part power past that point. Temporarily remedied for night by closing ABS V7. To be repaired tomorrow 17/09/15.jumper replaced and repaired abs | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-09-16 | c | 0.006371 | 6.048e-06 | 2016 | 2015-09-16 | C | 2 | 0.006371 | 6.0475e-06
7303535 | 2015-10-15 09:16 | 2015-10-15 14:12 | 296 | 3 | 888 | 296 | 293 | 0.0026851 | 879 | 0.0026579 | 9.0713e-06 | NAPA ID:12425 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2646 | Replace 11kV arms on the following poles M1672, M1671, M1669, M1666 and M1664. Works location: Old Taupo Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-15 | b | 0.0013289 | 4.536e-06 | 2016 | 2015-10-15 | B | 3 | 0.0026579 | 9.0713e-06
7303549 | 2015-10-12 14:00 | 2015-10-12 14:45 | 45 | 5 | 225 | 45 | 42 | 0.00068035 | 210 | 0.00063499 | 1.5119e-05 | NAPA ID:11951 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC672 | To install a 400V Fuse Disconnector. Works location: Brunskill Rd, TE Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-12 | b | 0.00031749 | 7.559e-06 | 2016 | 2015-10-12 | B | 5 | 0.00063499 | 1.5119e-05
7303563 | 2015-10-12 10:00 | 2015-10-12 10:40 | 40 | 2 | 80 | 40 | 37 | 0.0002419 | 74 | 0.00022376 | 6.0475e-06 | NAPA ID:11947 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5533 | Tom install a 400V Fuse/Disconnector. Works location: Maungakawa Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-12 | b | 0.00011188 | 3.024e-06 | 2016 | 2015-10-12 | B | 2 | 0.00022376 | 6.0475e-06
7303572 | 2015-10-12 12:00 | 2015-10-12 12:35 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 | NAPA ID:11948 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5187 | To install a 400V Fuse/Disconnector. Works location: Brunskill Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-12 | b | 0.00019352 | 6.048e-06 | 2016 | 2015-10-12 | B | 4 | 0.00038704 | 1.2095e-05
7303648 | 2015-10-13 09:46 | 2015-10-13 12:34 | 167.8333 | 3 | 503.5 | 167.8333 | 164.8333 | 0.0015225 | 494.5 | 0.0014952 | 9.0713e-06 | NAPA ID:12760 TP_STRATFORD GXP > ELTHAM SUB > NGAERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6259 | Increase height of HV spur line between poles 738563 &738562. Works location: Wingrove Rd, Stratford. WO 30002186 | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.00074763 | 4.536e-06 | 2016 | 2015-10-13 | B | 3 | 0.0014952 | 9.0713e-06
7303674 | 2015-10-13 12:00 | 2015-10-13 13:30 | 90 | 7 | 630 | 90 | 87 | 0.001905 | 609 | 0.0018415 | 2.1166e-05 | NAPA ID:11956 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2499 | To install a 400V Fuse Disconnector. Works location: Brunskill Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.00092073 | 1.0583e-05 | 2016 | 2015-10-13 | B | 7 | 0.0018415 | 2.1166e-05
7303881 | 2015-10-07 10:02 | 2015-10-07 14:35 | 273 | 5 | 1365 | 273 | 270 | 0.0041274 | 1350 | 0.0040821 | 1.5119e-05 | NAPA ID:12598 TP_MANGAMAIRE GXP > ALFREDTON SUB > BROOKLANDS | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/385 | To replace transformer T9/385 and up grade earthing. Work Location: Route 52. Work Order 30011313 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-10-07 | b | 0.002041 | 7.559e-06 | 2016 | 2015-10-07 | B | 5 | 0.0040821 | 1.5119e-05
7303886 | 2015-10-21 09:21 | 2015-10-21 12:26 | 185.2167 | 10 | 1852.1667 | 185.2167 | 182.2167 | 0.0056005 | 1822.1667 | 0.0055098 | 3.0238e-05 | NAPA ID:12445 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2467 | Pole: M124444 - Block leaning pole. Poles: M12450, M12449, M12448 & M12451- Replace all 11kV arms . Works location: Old Taupo Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-21 | b | 0.0027549 | 1.5119e-05 | 2016 | 2015-10-21 | B | 10 | 0.0055098 | 3.0238e-05
7304113 | 2015-10-07 14:07 | 2015-10-07 15:52 | 105.2333 | 1 | 105.2333 | 105.2333 | 102.2333 | 0.0003182 | 102.2333 | 0.00030913 | 3.0238e-06 | NAPA ID:12950 TP_MARTON GXP > BULLS SUB > RACECOURSE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4233 | Isolate metering unit at ANZCO foods Rangitikei for testing and calibration. Works location: Marton/Bulls. WO 10160471 | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-10-07 | b | 0.00015457 | 1.512e-06 | 2016 | 2015-10-07 | B | 1 | 0.00030913 | 3.0238e-06
7304139 | 2015-09-17 18:03 | 2015-09-17 19:42 | 99.05 | 5 | 495.15 | 99.03 | 96.03 | 0.0014972 | 480.15 | 0.0014519 | 1.5119e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/235 | 2:18pm Andrew taken offsite and will return - as waiting for the truck to arrive from Palmerston North with the transformer - this will be approx 2hrs. Replaced 1x 15kVA 3 Phase Transformer. Property still has part power. Andrew Tahura to return tom | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-09-17 | c | 0.0014519 | 1.5119e-05 | 2016 | 2015-09-17 | C | 5 | 0.0014519 | 1.5119e-05
7304173 | 2015-09-17 10:15 | 2015-09-17 12:00 | 105.0167 | 75 | 7875.2167 | 105.0029 | 102.0029 | 0.023813 | 7650.2167 | 0.023132 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V7 | Lines down. HV fault in this area, no request, Control has made fault man aware of this lines down and will advise to attend. Lines down were private lines, section from pole to fuses still live, made safe and cut wires away for now and advised customer. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-09-17 | c | 0.023132 | 0.00022678 | 2016 | 2015-09-17 | C | 75 | 0.023132 | 0.00022678
7304180 | 2015-10-08 09:30 | 2015-10-08 14:39 | 308.3 | 75 | 23122.5 | 308.3 | 305.3 | 0.069917 | 22897.5 | 0.069237 | 0.00022678 | NAPA ID:11962 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5538 | Pole & cross arm replacement as part of the PowerCo IR750 Mountain Road pole renewal w/o 523369 . Shutdown 4 ]Will be starting work from pole 761572 to pole 761518. Works location: Mountain Rd, Inglewood. WO 30010055. | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-08 | b | 0.034618 | 0.00011339 | 2016 | 2015-10-08 | B | 75 | 0.069237 | 0.00022678
7304253 | 2015-10-05 09:15 | 2015-10-05 12:10 | 175 | 1 | 175 | 175 | 172 | 0.00052916 | 172 | 0.00052009 | 3.0238e-06 | NAPA ID:12642 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 229189 | Replace HV Term Arms. Works location: Pongakawa Station Rd. WO 30002468 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.00026004 | 1.512e-06 | 2016 | 2015-10-05 | B | 1 | 0.00052009 | 3.0238e-06
7304264 | 2015-10-07 08:50 | 2015-10-07 15:15 | 384.85 | 16 | 6157.6 | 384.85 | 381.85 | 0.018619 | 6109.6 | 0.018474 | 4.838e-05 | NAPA ID:11875 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P21916 | Replace poles, cross arms and conductor between poles P21916 and P21768. Works location: Mt Stewart Rd, Halcomb Rd. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-07 | b | 0.009237 | 2.419e-05 | 2016 | 2015-10-07 | B | 16 | 0.018474 | 4.838e-05
7304528 | 2015-10-13 09:23 | 2015-10-13 14:10 | 287.45 | 16 | 4599.2 | 287.45 | 284.45 | 0.013907 | 4551.2 | 0.013762 | 4.838e-05 | NAPA ID:11965 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/154 | replace 11kv poles, X arms and conductor between poles P21916 and pole P21768. Works location: Mt Stewart Halcomb Rd. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.0068809 | 2.419e-05 | 2016 | 2015-10-13 | B | 16 | 0.013762 | 4.838e-05
7304566 | 2015-10-13 10:00 | 2015-10-13 11:00 | 60 | 3 | 180 | 60 | 57 | 0.00054428 | 171 | 0.00051706 | 9.0713e-06 | NAPA ID:11953 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC962 | Install a 400V Fuse/Disconnector. Works location: Brunskill Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.00025853 | 4.536e-06 | 2016 | 2015-10-13 | B | 3 | 0.00051706 | 9.0713e-06
7304588 | 2015-10-05 11:20 | 2015-10-05 12:20 | 60 | 2 | 120 | 60 | 57 | 0.00036285 | 114 | 0.00034471 | 6.0475e-06 | NAPA ID:12140 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1342 | Replace pole mount transformer TC1342. Works location: Te Rerenga Kuaotunu Rd, Coromandel. WO 30002490 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.00017235 | 3.024e-06 | 2016 | 2015-10-05 | B | 2 | 0.00034471 | 6.0475e-06
7304603 | 2015-10-05 08:48 | 2015-10-05 10:14 | 86 | 3 | 258 | 86 | 83 | 0.00078013 | 249 | 0.00075292 | 9.0713e-06 | NAPA ID:12393 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1733 | Install L.V fusing. Works location: Manaia Rd, Coromandel. WO 30010651 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-05 | b | 0.00037646 | 4.536e-06 | 2016 | 2015-10-05 | B | 3 | 0.00075292 | 9.0713e-06
7304913 | 2015-10-13 13:05 | 2015-10-13 15:10 | 125 | 2 | 250 | 125 | 122 | 0.00075594 | 244 | 0.0007378 | 6.0475e-06 | NAPA ID:12256 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1841 | To install a 400V Fuse/Disconnector. Works location: Old Te Aroha Rd. WO 10147849 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.0003689 | 3.024e-06 | 2016 | 2015-10-13 | B | 2 | 0.0007378 | 6.0475e-06
7304950 | 2015-09-17 09:42 | 2015-09-17 13:07 | 205.1667 | 29 | 5949.8333 | 205.1667 | 202.1667 | 0.017991 | 5862.8333 | 0.017728 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 1228 LAKE FERRY ROAD | ( KPE CB 5 ) Emergency switching to replace pole 04252 ( hit by car ). Isolation at Fuses FP770 ( no back feeds ). Pole replaced all service restored. Materials 1 x pole , 1 x H/V arm complete, 1 x breast block. NDR No 31184 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-09-17 | c | 0.017728 | 8.7689e-05 | 2016 | 2015-09-17 | C | 29 | 0.017728 | 8.7689e-05
7305113 | 2015-10-09 11:11 | 2015-10-09 13:58 | 167.05 | 37 | 6180.85 | 167.05 | 164.05 | 0.018689 | 6069.85 | 0.018354 | 0.00011188 | NAPA ID:12397 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6389 | LLP install LLB @ pole 840280 - AP replace cracked 11kV ABS WH890 pole - LLP close LLB @ pole 840280. Works location: South Rd, Hawera. WO 30011358 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-09 | b | 0.0091769 | 5.594e-05 | 2016 | 2015-10-09 | B | 37 | 0.018354 | 0.00011188
7305901 | 2015-10-06 09:10 | 2015-10-06 16:01 | 410.4333 | 33 | 13544.3 | 410.4333 | 407.4333 | 0.040955 | 13445.3 | 0.040655 | 9.9784e-05 | NAPA ID:12869 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC2-126 | Replace Crossarms at Various Sites. Works location: Prestidge Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-06 | b | 0.020328 | 4.9892e-05 | 2016 | 2015-10-06 | B | 33 | 0.040655 | 9.9784e-05
7305946 | 2015-10-06 08:45 | 2015-10-06 12:43 | 237.55 | 34 | 8076.7 | 237.55 | 234.55 | 0.024422 | 7974.7 | 0.024114 | 0.00010281 | NAPA ID:12635 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF7-041 | REPLACE HV POLES AND ARMS. Works location: Pongakawa Station Rd. WO 30002468 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-06 | b | 0.012057 | 5.1404e-05 | 2016 | 2015-10-06 | B | 34 | 0.024114 | 0.00010281
7306324 | 2015-10-14 10:04 | 2015-10-14 11:58 | 114.0833 | 41 | 4677.4167 | 114.0833 | 111.0833 | 0.014143 | 4554.4167 | 0.013771 | 0.00012397 | NAPA ID:12101 TP_HUIRANGI GXP > INGLEWOOD SUB | 6.6 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5533 | Install new 11kV under ground cable from transformer 4170T to new fused switch gear 12105/2. Works location: Puketea St. WO 30001909 | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-14 | b | 0.0068857 | 6.1987e-05 | 2016 | 2015-10-14 | B | 41 | 0.013771 | 0.00012397
7306390 | 2015-10-09 08:30 | 2015-10-09 10:23 | 113 | 5 | 565 | 113 | 110 | 0.0017084 | 550 | 0.0016631 | 1.5119e-05 | NAPA ID:12551 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 823657 | to replace 11kv pole. Works location: Longbush Rd, Carterton. WO 30011314 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-09 | b | 0.00083153 | 7.559e-06 | 2016 | 2015-10-09 | B | 5 | 0.0016631 | 1.5119e-05
7306950 | 2015-09-17 16:42 | 2015-09-17 22:26 | 344 | 360 | 51219 | 142.275 | 139.275 | 0.15487 | 50139 | 0.15161 | 0.0010886 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 264669 | CB 3 Lock out Flags B & C O/C. Reported car verses pole Isolated between ABS 812, 556 & 1057. ABS 583 would not open so area extended to ABS 1057. Replaced pole & relivened. NDR 48061. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-09-17 | c | 0.15161 | 0.0010886 | 2016 | 2015-09-17 | C | 360 | 0.15161 | 0.0010886
7309122 | 2015-09-17 21:56 | 2015-09-18 00:10 | 134.5833 | 1033 | 56926.7333 | 55.1082 | 52.1082 | 0.17213 | 53827.7333 | 0.16276 | 0.0031235 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | N/A - NOT APPLICABLE | CB1 & 2 tripped on O/C CB 1 reclosed. Sectionalised and found branch on line at pole 387692. Removed branch and relivened. Fault beyound recloser RP11 | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-17 | c | 0.16276 | 0.0031235 | 2016 | 2015-09-17 | C | 1033 | 0.16276 | 0.0031235
7310000 | 2015-09-17 21:56 | 2015-09-17 22:13 | 16.8167 | 20 | 336.3333 | 16.8167 | 13.8167 | 0.001017 | 276.3333 | 0.00083557 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB1 | CB 1 & CB 2 tripped on O/C CB 1 reclosed | F1 | RANGIURU | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-17 | c | 0.00083557 | 6.0475e-05 | 2016 | 2015-09-17 | C | 20 | 0.00083557 | 6.0475e-05
7312195 | 2015-09-17 23:54 | 2015-09-18 05:38 | 343.5167 | 2 | 687.0333 | 343.5167 | 340.5167 | 0.0020774 | 681.0333 | 0.0020593 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757428 | Faultman found 1x 11kV fuse blown at Fuses 1114 (Not on Scada or OMS Map). Patrol involving climbing poles to find broken 11kV Insulator. Replaced all 3x 11kV Pins & Insulators due to age. Replaced 3x Ali Binders & 3x 3Amp Fuse Links | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-09-17 | c | 0.0020593 | 6.048e-06 | 2016 | 2015-09-17 | C | 2 | 0.0020593 | 6.0475e-06
7314180 | 2015-09-18 07:07 | 2015-09-18 10:08 | 180.8 | 8 | 1446.4 | 180.8 | 177.8 | 0.0043736 | 1422.4 | 0.004301 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC969 | Reload Reliven at Tranformer TC969. 2 x 3 Amp fuses. Possible bird strike, broken jumper found and repaired. | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-18 | c | 0.004301 | 2.419e-05 | 2016 | 2015-09-18 | C | 8 | 0.004301 | 2.419e-05
7317088 | 2015-09-18 15:26 | 2015-09-18 18:28 | 182.3833 | 2 | 231.3833 | 115.6917 | 112.6917 | 0.00069965 | 225.3833 | 0.00068151 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/541 | Fault was downstream of Fuses L81. . Isolation from Fuses L81. A broken HV jumper was replaced at T1/541. (Fault at Al/Cu Joint). Relivened OK. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-18 | c | 0.00068151 | 6.048e-06 | 2016 | 2015-09-18 | C | 2 | 0.00068151 | 6.0475e-06
7317568 | 2015-09-23 11:15 | 2015-09-23 11:20 | 5 | 2 | 10 | 5 | 2 | 3.0238e-05 | 4 | 1.2095e-05 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TP2593 | Can't find issue on network. Need to carry out voltage checks but need to isolate services during the day. Will need to return Monday to investigate further. Advised customer. Tap Up Transformer TP2593 but voltage too high so restored to original settings | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-23 | c | 1.2095e-05 | 6.048e-06 | 2016 | 2015-09-23 | C | 2 | 1.2095e-05 | 6.0475e-06
7317720 | 2015-09-18 21:03 | 2015-09-19 00:31 | 207.9667 | 62 | 12893.9333 | 207.9667 | 204.9667 | 0.038988 | 12707.9333 | 0.038426 | 0.00018747 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 830063 | Kate from Police Comms on 0800 115 019. Cnr Columbo and Worksop Road, Masterton. car vs pole. Event # P 022567233. ETA required. 6.50pm - advise smc. 6.59pm - advise Adam at Police Comms of 10 min eta. Replaced 11m pole 830063 2m HV Crossarm 2.7m LV Cross | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-18 | c | 0.038426 | 0.00018747 | 2016 | 2015-09-18 | C | 62 | 0.038426 | 0.00018747
7318148 | 2015-09-19 08:26 | 2015-09-19 09:30 | 63.7167 | 93 | 5924.9333 | 63.709 | 60.709 | 0.017916 | 5645.9333 | 0.017072 | 0.00028121 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5432 | Initially received a number of part power & no power calls in Inglewood. Patrol found blown jumper at ABS 5432. This had caused damage to the ABS (Poor condition). Isolation from ABS 5384, 5428 and CB5120/3. ABS Removed and jumpered through. Relivened OK. | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.017072 | 0.00028121 | 2016 | 2015-09-19 | C | 93 | 0.017072 | 0.00028121
7318460 | 2015-09-19 11:20 | 2015-09-19 11:51 | 31.1667 | 14 | 436.3333 | 31.1667 | 28.1667 | 0.0013194 | 394.3333 | 0.0011924 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/497 | Outage required from Fuses Q62 to repair a broken HT jumper at transformer T7/497. Relivened OK. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.0011924 | 4.2333e-05 | 2016 | 2015-09-19 | C | 14 | 0.0011924 | 4.2333e-05
7318600 | 2015-09-19 10:28 | 2015-09-19 17:20 | 412.4667 | 53 | 1950.6167 | 36.8041 | 33.8041 | 0.0058982 | 1791.6167 | 0.0054174 | 0.00016026 |  | 11 | Unplanned | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | FS158 | Tripping at Fuses FS158 (Bennett St) due to digger hitting 11kV Cable. Isolation from Fuse Switch FS158 to carryout repairs. (NOTE: Short outages required between Sw/Gear 195 and 235 to enable the Fuse/Sw to be operated dead - backfeed at Sw/Gear 271). C | F2 | RANGITIKEI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.0054174 | 0.00016026 | 2016 | 2015-09-19 | C | 53 | 0.0054174 | 0.00016026
7319421 | 2015-09-19 11:50 | 2015-09-19 13:13 | 82.4833 | 255 | 16562.85 | 64.9524 | 61.9524 | 0.050082 | 15797.85 | 0.047769 | 0.00077106 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03472 | Initial tripping on Recloser CBH131 on Reverse E/F. Area patrolled with a broken binder found and conductor sitting on cross arm. Isolation required from ABS HI27 and HI29 with backfeed at CB 10041. One binder replaced, relivened OK. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.047769 | 0.00077106 | 2016 | 2015-09-19 | C | 255 | 0.047769 | 0.00077106
7320331 | 2015-09-19 15:21 | 2015-09-19 17:05 | 104.2833 | 93 | 9698.35 | 104.2833 | 101.2833 | 0.029325 | 9419.35 | 0.028482 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | Tripping on Recloser N21 on Phase C. (NOTE: No indication or control at NOC due to Control box fault on the Recloser). CB found open on site, reclosed OK. Partial patrol carried out around Peka Rd area. Nothing found. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.028482 | 0.00028121 | 2016 | 2015-09-19 | C | 93 | 0.028482 | 0.00028121
7320840 | 2015-09-19 19:16 | 2015-09-20 02:11 | 415 | 238 | 52630.9167 | 221.1383 | 218.1383 | 0.15914 | 51916.9167 | 0.15698 | 0.00071966 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 824008 | Replaced Pole 824008 after car vs pole. Police ref:- No P022579279. NDR number to follow | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-09-19 | c | 0.15698 | 0.00071966 | 2016 | 2015-09-19 | C | 238 | 0.15698 | 0.00071966
7321802 | 2015-09-20 02:48 | 2015-09-20 09:43 | 414.6667 | 249 | 73984.65 | 297.1271 | 294.1271 | 0.22371 | 73237.65 | 0.22145 | 0.00075292 |  | 11 | Unplanned | UNDERGROUND CABLE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 201142 | AON CB4 tripped ( O/C R & Y Ph ) L/O. Feeder sectionalised Cable between poles 201139 & 201142 faulty. Cable disconnected from poles 201142 & 201139, to be repaired when weather improves. Crosses a golf course. DNO created 150911. Isolation at ABS's IP537 | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.22145 | 0.00075292 | 2016 | 2015-09-20 | C | 249 | 0.22145 | 0.00075292
7322629 | 2015-09-20 04:19 | 2015-09-20 12:30 | 491.4667 | 2 | 982.9333 | 491.4667 | 488.4667 | 0.0029722 | 976.9333 | 0.002954 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE7-130 | Blown Transformer Needs replacing. 30x11x3 Pole 218958. transformer Replaced | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.002954 | 6.048e-06 | 2016 | 2015-09-20 | C | 2 | 0.002954 | 6.0475e-06
7322941 | 2015-09-20 05:57 | 2015-09-20 12:16 | 378.7 | 1 | 378.7 | 378.7 | 375.7 | 0.0011451 | 375.7 | 0.001136 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE6-129 | 2x 2amp HV Fuse blown due to lightning | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.001136 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 0.001136 | 3.0238e-06
7323007 | 2015-09-20 06:45 | 2015-09-20 14:44 | 478.9667 | 15 | 7184.5 | 478.9667 | 475.9667 | 0.021724 | 7139.5 | 0.021588 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1556 | 2 10amp hv fuses blown at fuses fp1556 due to lightning | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.021588 | 4.5356e-05 | 2016 | 2015-09-20 | C | 15 | 0.021588 | 4.5356e-05
7323020 | 2015-09-20 08:37 | 2015-09-20 13:57 | 320.35 | 19 | 4331.05 | 227.95 | 224.95 | 0.013096 | 4274.05 | 0.012924 | 5.7451e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE8-028 | Line down at Pole . Line repaired, transformer TE8-022 blown by lightning, isolated at transformer fuses. Transformer TE8-022 replaced. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.012924 | 5.7451e-05 | 2016 | 2015-09-20 | C | 19 | 0.012924 | 5.7451e-05
7323254 | 2015-09-20 08:21 | 2015-09-20 10:50 | 149.1833 | 2 | 298.3667 | 149.1833 | 146.1833 | 0.00090219 | 292.3667 | 0.00088405 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7-069 | 2x2amp HV fuses blown due to lightning | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.00088405 | 6.048e-06 | 2016 | 2015-09-20 | C | 2 | 0.00088405 | 6.0475e-06
7323355 | 2015-09-20 08:45 | 2015-09-20 10:15 | 90.3667 | 1 | 90.3667 | 90.3667 | 87.3667 | 0.00027325 | 87.3667 | 0.00026418 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7033 | Bird at Bottom of Transformer T3704. 2 x 10amp fuses replaced | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.00026418 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 0.00026418 | 3.0238e-06
7323493 | 2015-09-20 07:31 | 2015-09-21 12:16 | 1724.15 | 21 | 36207.15 | 1724.15 | 1721.15 | 0.10948 | 36144.15 | 0.10929 | 6.3499e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7-125 | Replace faulty transformer. 1 x 3ph 200kVA and 3 x fuses. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.10929 | 6.3499e-05 | 2016 | 2015-09-20 | C | 21 | 0.10929 | 6.3499e-05
7323635 | 2015-09-20 09:38 | 2015-09-20 15:40 | 361.8833 | 3 | 1085.65 | 361.8833 | 358.8833 | 0.0032827 | 1076.65 | 0.0032555 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE5-277 | 2x 3amp HV fuses blown at Transformer TE5-277 due to Lightning. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0032555 | 9.071e-06 | 2016 | 2015-09-20 | C | 3 | 0.0032555 | 9.0713e-06
7323774 | 2015-09-20 10:11 | 2015-09-20 17:20 | 428.2833 | 1 | 428.2833 | 428.2833 | 425.2833 | 0.001295 | 425.2833 | 0.001286 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | TF8-031 | 2x2amp HV fuses blown at Transformer TF8-031 Pole 227938 due to lightning | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.001286 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 0.001286 | 3.0238e-06
7324313 | 2015-09-20 11:48 | 2015-09-20 20:13 | 505.4833 | 1 | 505.4833 | 505.4833 | 502.4833 | 0.0015285 | 502.4833 | 0.0015194 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 325783 | Temporary repairs made to restore power. Lines will need replacing for permanent repair. Submitted Residual Follow Up Fault form. Poles 325783 and 784264. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0015194 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 0.0015194 | 3.0238e-06
7324732 | 2015-09-20 12:23 | 2015-09-20 14:27 | 123.8 | 162 | 9701.4333 | 59.8854 | 56.8854 | 0.029335 | 9215.4333 | 0.027865 | 0.00048985 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 784264 | Close Fuses 838 at 1530 not 17 43 as in scada /OMS | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.027865 | 0.00048985 | 2016 | 2015-09-20 | C | 162 | 0.027865 | 0.00048985
7325689 | 2015-09-20 13:39 | 2015-09-23 08:26 | 4007.0333 | 274 | 29126 | 106.2993 | 103.2993 | 0.08807 | 28304 | 0.085585 | 0.00082851 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3683 | Recloser 9121 tripped. flags at CB 6 a,b,c OC EF. line patrolled & sectionalized. isolated faulted area to between abs's 2604 & IP531. all transformer fuses pulled main line relivened, transformers gradually relivened Transformer TC3683 Faulty. Back feed | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.085585 | 0.00082851 | 2016 | 2015-09-20 | C | 274 | 0.085585 | 0.00082851
7326158 | 2015-09-20 13:46 | 2015-09-20 15:21 | 94.95 | 2 | 189.9 | 94.95 | 91.95 | 0.00057421 | 183.9 | 0.00055607 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE7-069 | transformer TE7-069 blown due to lightning fuses replaced earlier in the day but have since blown . Transformer is a 30-11-3. Transformer Replaced | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.00055607 | 6.048e-06 | 2016 | 2015-09-20 | C | 2 | 0.00055607 | 6.0475e-06
7326167 | 2015-09-20 10:58 | 2015-09-20 20:58 | 599.8 | 113 | 9685.4667 | 85.7121 | 82.7121 | 0.029287 | 9346.4667 | 0.028261 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 839404 | Initial tripping at Sectionaliser C218 (Found open - no flags). Patrol carried out with a conductor found down at Pole 839404). Isolation required from ABS S150 with 20M of conductor replaced and sleeved. Suspect tree branch as conductor was burnt. Reliv | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.028261 | 0.00034168 | 2016 | 2015-09-20 | C | 113 | 0.028261 | 0.00034168
7327822 | 2015-09-20 14:53 | 2015-09-21 | 546.6333 | 7 | 3826.4333 | 546.6333 | 543.6333 | 0.01157 | 3805.4333 | 0.011507 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF3 042 | Replace 3 x 3a H/V, O/H fuses | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.011507 | 2.1166e-05 | 2016 | 2015-09-20 | C | 7 | 0.011507 | 2.1166e-05
7328058 | 2015-09-20 15:27 | 2015-09-21 01:10 | 582.9667 | 5 | 2914.8333 | 582.9667 | 579.9667 | 0.0088138 | 2899.8333 | 0.0087684 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF3 043 | Replace 2 x 2A H/V, O/H fuses | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0087684 | 1.5119e-05 | 2016 | 2015-09-20 | C | 5 | 0.0087684 | 1.5119e-05
7328420 | 2015-09-20 17:11 | 2015-09-22 06:32 | 2241.2333 | 11 | 4453.45 | 404.8591 | 401.8591 | 0.013466 | 4420.45 | 0.013366 | 3.3261e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sf5-025 | Line patrolled found blown tx at TF5-025 suspect wind. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.013366 | 3.3261e-05 | 2016 | 2015-09-20 | C | 11 | 0.013366 | 3.3261e-05
7328438 | 2015-09-20 15:47 | 2015-09-20 23:50 | 483.4 | 2 | 966.8 | 483.4 | 480.4 | 0.0029234 | 960.8 | 0.0029052 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF4 048 | Replace 2 x 2A H/V, O/H fuses lightning | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0029052 | 6.048e-06 | 2016 | 2015-09-20 | C | 2 | 0.0029052 | 6.0475e-06
7328539 | 2015-09-20 16:08 | 2015-09-20 16:24 | 15.95 | 1 | 15.95 | 15.95 | 12.95 | 4.8229e-05 | 12.95 | 3.9158e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TD6-035 | 2x6amp hv fuses blown at transformer TD6-035. Due to lightning | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 3.9158e-05 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 3.9158e-05 | 3.0238e-06
7329225 | 2015-09-20 22:10 | 2015-09-21 14:55 | 1005.2833 | 31 | 31163.7833 | 1005.2833 | 1002.2833 | 0.094232 | 31070.7833 | 0.093951 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758081 | Fuse tripped at 8494. Severe winds in the area. 245 Dover Road (7333263). 1 binder 2 spans of conductor 1 crossarm 10 sleaves | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.093951 | 9.3737e-05 | 2016 | 2015-09-20 | C | 31 | 0.093951 | 9.3737e-05
7329480 | 2015-09-20 17:36 | 2015-09-21 22:44 | 1747.6167 | 6 | 10485.7 | 1747.6167 | 1744.6167 | 0.031706 | 10467.7 | 0.031652 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF7-027 | Transformer TF7 027 blown, feeds pump & cow shed to be replaced in morning customer informed Transformer Transfomer TF7-027 Replaced 15-11-1 Own access permit | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.031652 | 1.8143e-05 | 2016 | 2015-09-20 | C | 6 | 0.031652 | 1.8143e-05
7329523 | 2015-09-20 17:28 | 2015-09-21 11:25 | 1077.2333 | 178 | 35560.05 | 199.7756 | 196.7756 | 0.10753 | 35026.05 | 0.10591 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | Reports of no power found Alfredton CB I23 had tripped. (This feeder was also backfeeding all of Pongaroa CB4 due to voltage issues from Pongaroa end - Ongoing fault).Area parolled and sectionalised with both feeders livened to spur line on Rimu Rd (Fuses | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.10591 | 0.00053823 | 2016 | 2015-09-20 | C | 178 | 0.10591 | 0.00053823
7329618 | 2015-09-20 17:54 | 2015-09-21 11:06 | 1031.8 | 17 | 17540.6 | 1031.8 | 1028.8 | 0.053039 | 17489.6 | 0.052884 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6465 | 1 HT fuse found tripped at Fuses 6465. Patrol found a tree branch hitting the line. Will come back tomorrow and cut away branch. (Fuse left open overnight, only one customer effected). | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.052884 | 5.1404e-05 | 2016 | 2015-09-20 | C | 17 | 0.052884 | 5.1404e-05
7329825 | 2015-09-20 18:20 | 2015-09-21 17:02 | 1362.2167 | 143 | 89133.2 | 623.3091 | 620.3091 | 0.26952 | 88704.2 | 0.26822 | 0.0004324 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 784711 | Tripping on Recloser CB2032 on E/F, A Phase O/C. Area patrolled and sectionalised with trees found through lines on Kauarapaoa Rd. Impracticle to repair during the night so a Temp Line break put in place (Pole 784257) to liven up more Customers. However, | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.26822 | 0.0004324 | 2016 | 2015-09-20 | C | 143 | 0.26822 | 0.0004324
7330402 | 2015-09-20 18:36 | 2015-09-21 10:05 | 928.65 | 3 | 2785.95 | 928.65 | 925.65 | 0.008424 | 2776.95 | 0.0083968 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD6-026 | Blown transformer TD6 026 to be replaced on Monday | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0083968 | 9.071e-06 | 2016 | 2015-09-20 | C | 3 | 0.0083968 | 9.0713e-06
7330521 | 2015-09-20 18:53 | 2015-09-20 23:07 | 254.2833 | 8 | 2034.2667 | 254.2833 | 251.2833 | 0.0061511 | 2010.2667 | 0.0060786 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8178 | 2 HT fuses found tripped at 8178. Suspect Line calsh, high winds. Reliivened OK. Rating 8A. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.0060786 | 2.419e-05 | 2016 | 2015-09-20 | C | 8 | 0.0060786 | 2.419e-05
7330565 | 2015-09-20 22:18 | 2015-09-20 23:46 | 87.5833 | 10 | 875.8333 | 87.5833 | 84.5833 | 0.0026483 | 845.8333 | 0.0025576 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704908 | 1 HV Conductor down on Stent Rd due to high winds. Isolation from Fuses 6803 to carryout repairs. Conductor had broken at Insulator, 1 binder needed with 2 sleeves a conductor. Relivened OK. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.0025576 | 3.0238e-05 | 2016 | 2015-09-20 | C | 10 | 0.0025576 | 3.0238e-05
7331275 | 2015-09-20 19:33 | 2015-09-20 22:25 | 171.4833 | 423 | 29417.9333 | 69.5459 | 66.5459 | 0.088953 | 28148.9333 | 0.085116 | 0.0012791 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tf3-007 | TGA 17 sectionaliser 9208 tripped E/F, L/O. Fault traced to faulty transformer TF3 007. Transformer TF3 007 isolated & needs to be replaced Monday all service restored. 5.38pm clint called to advise relivened TX and all power is restored. | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.085116 | 0.0012791 | 2016 | 2015-09-20 | C | 423 | 0.085116 | 0.0012791
7331832 | 2015-09-20 19:48 | 2015-09-20 23:20 | 211.7667 | 5 | 1058.8333 | 211.7667 | 208.7667 | 0.0032017 | 1043.8333 | 0.0031563 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1451 | Replace 2 x 6A H/V, O/H fuses lightning | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-09-20 | c | 0.0031563 | 1.5119e-05 | 2016 | 2015-09-20 | C | 5 | 0.0031563 | 1.5119e-05
7334117 | 2015-09-20 21:01 | 2015-09-22 18:48 | 2746.7833 | 10 | 5758.1 | 575.81 | 572.81 | 0.017411 | 5728.1 | 0.01732 | 3.0238e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3773T | Transformer 3773T defective, requires changing during daylight hours. 10.01am 22/9 customer calling for update, they have had no power for 3 days. Kaine advised they are still working on organising a vehicle to take the tx into the property as a truck wil | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.01732 | 3.0238e-05 | 2016 | 2015-09-20 | C | 10 | 0.01732 | 3.0238e-05
7334169 | 2015-09-20 21:24 | 2015-09-21 16:49 | 1164.3167 | 4 | 4657.2667 | 1164.3167 | 1161.3167 | 0.014082 | 4645.2667 | 0.014046 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6463 | One Phase down, too windy to do job safely. Will continue during daylight hours. 2 x DDO's Replaced | F3 | MOTUROA 9 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.014046 | 1.2095e-05 | 2016 | 2015-09-20 | C | 4 | 0.014046 | 1.2095e-05
7334269 | 2015-09-20 22:03 | 2015-09-21 00:52 | 169.2667 | 15 | 2539 | 169.2667 | 166.2667 | 0.0076773 | 2494 | 0.0075413 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | 2 HT fuses found tripped at 2829. Reloaded OK. Rating 15A | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.0075413 | 4.5356e-05 | 2016 | 2015-09-20 | C | 15 | 0.0075413 | 4.5356e-05
7334485 | 2015-09-20 22:22 | 2015-09-21 00:25 | 123.45 | 1 | 123.45 | 123.45 | 120.45 | 0.00037328 | 120.45 | 0.00036421 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Y46 | 2 HT Fuses found tripped at Transformer Y46. Reloaded OK. Rating 5A | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.00036421 | 3.024e-06 | 2016 | 2015-09-20 | C | 1 | 0.00036421 | 3.0238e-06
7334788 | 2015-09-20 23:18 | 2015-09-21 14:45 | 927.6833 | 8 | 7421.4667 | 927.6833 | 924.6833 | 0.022441 | 7397.4667 | 0.022368 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8178 | 2 Fuses found tripped, continued to trip on reclosing due to line clashes in the high winds. Left Open, to be investigated in morning. Reload reliven at Fuses 8178. 2 x HV Fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.022368 | 2.419e-05 | 2016 | 2015-09-20 | C | 8 | 0.022368 | 2.419e-05
7335064 | 2015-09-21 00:26 | 2015-09-21 02:18 | 111.95 | 156 | 13176.8 | 84.4667 | 81.4667 | 0.039843 | 12708.8 | 0.038428 | 0.00047171 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | I12747 | PKO 6 Recloser RC35 tripped A, B & C Ph O/C L/O . Feeder sectionalised & branch found across all phases at pole I12747 branch removed all service restored. NOTE conductor at this pole suffered some damage Marty has photos. No 93317 damage report | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.038428 | 0.00047171 | 2016 | 2015-09-21 | C | 156 | 0.038428 | 0.00047171
7335607 | 2015-09-21 00:58 | 2015-09-21 08:07 | 429.1 | 32 | 13731.2 | 429.1 | 426.1 | 0.04152 | 13635.2 | 0.04123 | 9.676e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8423 | 2 HT fuses tripped at 8423, to dangerous to reload in high winds. Reloaded ok 40A | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.04123 | 9.676e-05 | 2016 | 2015-09-21 | C | 32 | 0.04123 | 9.676e-05
7335678 | 2015-09-21 02:30 | 2015-09-21 15:11 | 761 | 9 | 6849 | 761 | 758 | 0.02071 | 6822 | 0.020628 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 8464 | An implement shed has blown into the LV. Isolation at Transformer Fuses 1737N until repairs daylight hours. Will come back in morning to carryout repairs. 21/9 11.32am - Mike from Fire Comms advise the pole # is 372907 and it is for #22. Advised Mike that | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.020628 | 2.7214e-05 | 2016 | 2015-09-21 | C | 9 | 0.020628 | 2.7214e-05
7336888 | 2015-09-21 05:43 | 2015-09-21 11:26 | 342.9833 | 9 | 3086.85 | 342.9833 | 339.9833 | 0.0093339 | 3059.85 | 0.0092523 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 190 Goodwin Rd, New Plymouth | 1R Arcing / sparking Pole. Transformer P4362 fuse tripped. PU 474 one fuse tripped. P4360. All fuses open on PU474 open. Burnt crossarm to be replaced. 3 fuses and holders 2 crossarms and insulators 3 binders | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.0092523 | 2.7214e-05 | 2016 | 2015-09-21 | C | 9 | 0.0092523 | 2.7214e-05
7336991 | 2015-09-21 02:46 | 2015-09-21 18:18 | 931.45 | 4 | 3725.8 | 931.45 | 928.45 | 0.011266 | 3713.8 | 0.01123 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF6-024 | Transformer TF6 024 blown needs replacement ASAP. 16:10 - 712 Allports Road say faultmen have left site but they still have no power. The tx has been replaced. cause: lightning. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.01123 | 1.2095e-05 | 2016 | 2015-09-21 | C | 4 | 0.01123 | 1.2095e-05
7337063 | 2015-09-21 03:30 | 2015-09-21 11:29 | 478.6667 | 418 | 43203.75 | 103.3583 | 100.3583 | 0.13064 | 41949.75 | 0.12685 | 0.0012639 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13355 | MIK CB5 tripped A, B & C Ph O/C, L/O . Feeder sectionalised & found branch has brought down 2 x 11kV lines at pole C13355. Isolation at ABS 664 ( no back feeds ) all other service restored. 3 sleeve 3 lv bases 3 x 100a fuses 25m of conductor | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.12685 | 0.0012639 | 2016 | 2015-09-21 | C | 418 | 0.12685 | 0.0012639
7338894 | 2015-09-21 06:12 | 2015-09-21 08:46 | 153.6833 | 156 | 6926.6667 | 44.4017 | 41.4017 | 0.020945 | 6458.6667 | 0.019529 | 0.00047171 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T31 | Jade Williams did repairs on this job this morning (21/09/15) Kaponga T31 Riverlea Feeder. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.019529 | 0.00047171 | 2016 | 2015-09-21 | C | 156 | 0.019529 | 0.00047171
7339171 | 2015-09-21 06:18 | 2015-09-21 09:00 | 162.2 | 4 | 648.8 | 162.2 | 159.2 | 0.0019618 | 636.8 | 0.0019255 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC888 | 2 x 6 amp fuses due to wind | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.0019255 | 1.2095e-05 | 2016 | 2015-09-21 | C | 4 | 0.0019255 | 1.2095e-05
7339533 | 2015-09-21 06:43 | 2015-09-21 10:27 | 224.1833 | 5 | 1120.9167 | 224.1833 | 221.1833 | 0.0033894 | 1105.9167 | 0.003344 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2657T | 2x 3 anmp fuses | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.003344 | 1.5119e-05 | 2016 | 2015-09-21 | C | 5 | 0.003344 | 1.5119e-05
7339786 | 2015-09-21 06:57 | 2015-09-21 10:01 | 183.4667 | 1 | 183.4667 | 183.4667 | 180.4667 | 0.00055476 | 180.4667 | 0.00054569 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF4-051 | 2 x fuses and holders 3amp | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.00054569 | 3.024e-06 | 2016 | 2015-09-21 | C | 1 | 0.00054569 | 3.0238e-06
7340102 | 2015-09-21 07:09 | 2015-09-21 16:34 | 564.5167 | 235 | 50397.85 | 214.4589 | 211.4589 | 0.15239 | 49692.85 | 0.15026 | 0.00071058 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711300 | Repair twisted crossarm isolated at ABS NG 250 & NG201 & NG479. Backfeed from NG251 1 x jumper 1x Sleeve. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.15026 | 0.00071058 | 2016 | 2015-09-21 | C | 235 | 0.15026 | 0.00071058
7340588 | 2015-09-21 08:06 | 2015-09-21 18:31 | 624.95 | 357 | 34147.8167 | 95.6521 | 92.6521 | 0.10325 | 33076.8167 | 0.10002 | 0.0010795 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730180 | lines down at pole 730180 materials to follow | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.10002 | 0.0010795 | 2016 | 2015-09-21 | C | 357 | 0.10002 | 0.0010795
7340947 | 2015-09-21 07:12 | 2015-09-21 20:32 | 800.4 | 1325 | 139126.8167 | 105.0014 | 102.0014 | 0.42069 | 135151.8167 | 0.40867 | 0.0040065 |  | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 730866 | Truck vs pole and lines down at INT Manaia road and Opunake road control advised, ETA required svs hub advised. 04 801 0812. Blown jumper at ABS 449. truck v pole at 730866. Materials list not supplied | F1,F2,F3 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2015-09-21 | c | 0.40867 | 0.0040065 | 2016 | 2015-09-21 | C | 1325 | 0.40867 | 0.0040065
7342027 | 2015-10-14 10:00 | 2015-10-14 10:15 | 15 | 5 | 75 | 15 | 12 | 0.00022678 | 60 | 0.00018143 | 1.5119e-05 | NAPA ID:12260 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2603 | To install a 400V Fuse/Disconnector. Works location: Te Tuni Rd, Matamata. WO 10147849 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-14 | b | 9.0713e-05 | 7.559e-06 | 2016 | 2015-10-14 | B | 5 | 0.00018143 | 1.5119e-05
7342082 | 2015-10-14 12:00 | 2015-10-14 12:57 | 57.1833 | 1 | 57.1833 | 57.1833 | 54.1833 | 0.00017291 | 54.1833 | 0.00016384 | 3.0238e-06 | NAPA ID:12263 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1100 | To install a 400V Fuse/Disconnector. Works location: Old Te Aroha Rd. Work Order: 10147849 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-14 | b | 8.1919e-05 | 1.512e-06 | 2016 | 2015-10-14 | B | 1 | 0.00016384 | 3.0238e-06
7342124 | 2015-10-14 14:00 | 2015-10-14 15:02 | 62 | 2 | 124 | 62 | 59 | 0.00037495 | 118 | 0.0003568 | 6.0475e-06 | NAPA ID:12264 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP170 | To install a 400V Fuse/Disconnector. Works location: Old Te Aroha Rd. WO 10147849 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-14 | b | 0.0001784 | 3.024e-06 | 2016 | 2015-10-14 | B | 2 | 0.0003568 | 6.0475e-06
7342989 | 2015-09-21 08:52 | 2015-09-21 11:56 | 184.0333 | 640 | 39260.1 | 61.3439 | 58.3439 | 0.11871 | 37340.1 | 0.11291 | 0.0019352 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745777 | C 6775/5 Trip E/F O/C. Materials 1 insulator and less 1 span conductor | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.11291 | 0.0019352 | 2016 | 2015-09-21 | C | 640 | 0.11291 | 0.0019352
7343723 | 2015-10-15 14:00 | 2015-10-15 15:15 | 75 | 9 | 675 | 75 | 72 | 0.002041 | 648 | 0.0019594 | 2.7214e-05 | NAPA ID:12266 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2077 | To install a 400V Fuse Disconnector. Works location: Tower Rd, Matamata. WO 10147849 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-15 | b | 0.0009797 | 1.3607e-05 | 2016 | 2015-10-15 | B | 9 | 0.0019594 | 2.7214e-05
7343760 | 2015-09-21 09:47 | 2015-09-21 10:27 | 40 | 116 | 4430 | 38.1897 | 35.1897 | 0.013395 | 4082 | 0.012343 | 0.00035076 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 743348 | CB 6 trip Tree over lines, repair lines & jumper. Planned works 12369 stopped at Operation 6 and Repair/Restore switching done on the fly. NDR#22863 | F1 | BELL BLOCK 6 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.012343 | 0.00035076 | 2016 | 2015-09-21 | C | 116 | 0.012343 | 0.00035076
7350450 | 2015-09-21 13:05 | 2015-09-22 13:25 | 1460 | 13 | 5130 | 394.6154 | 391.6154 | 0.015512 | 5091 | 0.015394 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8454 | need tx and crossarm to be replaced install generator to be installed tonight as discussed with NCTL. Tx leaking oil needs clean up Please also check OMS 7350439 - 664 KELLY ROAD. Replaced 1 tx and Hardware. 21/9 10.13pm - clicked FM offsite as Control al | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.015394 | 3.9309e-05 | 2016 | 2015-09-21 | C | 13 | 0.015394 | 3.9309e-05
7350588 | 2015-09-21 10:19 | 2015-09-21 11:12 | 53.1833 | 1 | 53.1833 | 53.1833 | 50.1833 | 0.00016081 | 50.1833 | 0.00015174 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD6-039 | replaced 2x DDO fuses, TD6-039 OH due to weather. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.00015174 | 3.024e-06 | 2016 | 2015-09-21 | C | 1 | 0.00015174 | 3.0238e-06
7350627 | 2015-09-21 14:15 | 2015-09-21 20:48 | 392.9333 | 5 | 1964.6667 | 392.9333 | 389.9333 | 0.0059407 | 1949.6667 | 0.0058953 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713144 | Power line down at Witiora Road, Oaonui. Down after Urupa hedge and in between the fox horn hedge. Repairs carried out with conductor requiring 2 sleeves and rebinding in OK. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.0058953 | 1.5119e-05 | 2016 | 2015-09-21 | C | 5 | 0.0058953 | 1.5119e-05
7350644 | 2015-10-07 09:03 | 2015-10-07 12:23 | 199.8 | 161 | 32167.8 | 199.8 | 196.8 | 0.097268 | 31684.8 | 0.095807 | 0.00048683 | NAPA ID:12887 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12970 | Close Line break s at pole P12970 & P0940. Re-liven line following recent new pole install. Red Defect# 101-46089 Powerco Wo 30014097 Refer to Peter Manning. Works location: Moresby Ave, Waihi. WO 30014097 | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 0.047904 | 0.00024341 | 2016 | 2015-10-07 | B | 161 | 0.095807 | 0.00048683
7350871 | 2015-09-21 12:50 | 2015-09-21 13:45 | 55 | 1 | 55 | 55 | 52 | 0.00016631 | 52 | 0.00015724 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc339 | Pole H1441- broken cross arm. HV fuses on transformer TC339 opened to replace broken LV crossarm. No LV isolation fuses on transformer | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.00015724 | 3.024e-06 | 2016 | 2015-09-21 | C | 1 | 0.00015724 | 3.0238e-06
7351039 | 2015-09-21 10:38 | 2015-09-21 11:51 | 72.5667 | 6 | 435.4 | 72.5667 | 69.5667 | 0.0013165 | 417.4 | 0.0012621 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781364 | Blown jumper at pole 781364. 3 connectors and 2 meters conductor | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-09-21 | c | 0.0012621 | 1.8143e-05 | 2016 | 2015-09-21 | C | 6 | 0.0012621 | 1.8143e-05
7351539 | 2015-10-16 12:40 | 2015-10-16 13:05 | 25 | 5 | 125 | 25 | 22 | 0.00037797 | 110 | 0.00033261 | 1.5119e-05 | NAPA ID:12268 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3633 | To install a 400V Fuse/Disconector. Works location: Hwy 27, Waharoa. WO 10147849 | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-10-16 | b | 0.00016631 | 7.559e-06 | 2016 | 2015-10-16 | B | 5 | 0.00033261 | 1.5119e-05
7351581 | 2015-10-16 14:30 | 2015-10-16 15:00 | 30 | 1 | 30 | 30 | 27 | 9.0713e-05 | 27 | 8.1642e-05 | 3.0238e-06 | NAPA ID:12269 TP_HINUERA GXP > TOWER ROAD SUB > BANKS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC352 | To install a 400V Fuse Disconnector. Works location: Hwy 24, Matamata. WO 10147849 | F4 | BANKS ST | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-16 | b | 4.0821e-05 | 1.512e-06 | 2016 | 2015-10-16 | B | 1 | 8.1642e-05 | 3.0238e-06
7351606 | 2015-10-16 09:54 | 2015-10-16 14:15 | 260.5667 | 12 | 3126.8 | 260.5667 | 257.5667 | 0.0094547 | 3090.8 | 0.0093458 | 3.6285e-05 | NAPA ID:12026 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TA805 | Replace Tx structure's T5095 & T5100. Works location: Puketapu Rd, Pihama. WO 10151700 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-16 | b | 0.0046729 | 1.8143e-05 | 2016 | 2015-10-16 | B | 12 | 0.0093458 | 3.6285e-05
7351647 | 2015-10-09 09:50 | 2015-10-09 16:28 | 398 | 3 | 1194 | 398 | 395 | 0.0036104 | 1185 | 0.0035832 | 9.0713e-06 | NAPA ID:12773 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 7430 | ISOLATION FOR TREE TRIMMING AROUND 11KV LINES FROM FUSES 7430 TO POLE 810953. Works location: Lake Ferry Rd, Featherston. WO 10152356 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-10-09 | b | 0.0017916 | 4.536e-06 | 2016 | 2015-10-09 | B | 3 | 0.0035832 | 9.0713e-06
7351945 | 2015-10-16 10:10 | 2015-10-16 11:20 | 69.9333 | 2 | 139.8667 | 69.9333 | 66.9333 | 0.00042292 | 133.8667 | 0.00040478 | 6.0475e-06 | NAPA ID:12267 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP960 | To install a 400V Fuse/Disconnector. Works location: Hwy 27, Waharoa. WO 10147849 | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-10-16 | b | 0.00020239 | 3.024e-06 | 2016 | 2015-10-16 | B | 2 | 0.00040478 | 6.0475e-06
7351980 | 2015-10-20 09:36 | 2015-10-20 14:38 | 302.3667 | 12 | 3628.4 | 302.3667 | 299.3667 | 0.010971 | 3592.4 | 0.010863 | 3.6285e-05 | NAPA ID:12048 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6420 | We are replacing P1255 transformer structure because pole is badly Spalding. Works location: Porikapa Rd, Okato. WO 30011861 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-10-20 | b | 0.0054313 | 1.8143e-05 | 2016 | 2015-10-20 | B | 12 | 0.010863 | 3.6285e-05
7352073 | 2015-10-21 08:47 | 2015-10-21 12:11 | 204.2 | 181 | 11272.7333 | 62.2803 | 59.2803 | 0.034086 | 10729.7333 | 0.032444 | 0.0005473 | NAPA ID:12881 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | Replace Chipped pole. Works location: Totman Rd. WO 30003457. Note: Unplanned Outage occurred during this outage and has been captured under the child OMS number. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-10-21 | b | 0.016222 | 0.00027365 | 2016 | 2015-10-21 | B | 181 | 0.032444 | 0.0005473
7352864 | 2015-09-21 12:24 | 2015-09-22 13:19 | 1495.1667 | 19 | 27688.1667 | 1457.2719 | 1454.2719 | 0.083722 | 27631.1667 | 0.08355 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5008 | 3 x fuses 2 2amp 1 8 amp weather caused | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.08355 | 5.7451e-05 | 2016 | 2015-09-21 | C | 19 | 0.08355 | 5.7451e-05
7352998 | 2015-09-29 08:48 | 2015-09-29 15:17 | 388.95 | 29 | 11279.55 | 388.95 | 385.95 | 0.034107 | 11192.55 | 0.033844 | 8.7689e-05 | NAPA ID:13119 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726859 | Replacing pole's from 726859 to 726910 and 726933 and installing Temp Links 34 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-29 | b | 0.016922 | 4.3845e-05 | 2016 | 2015-09-29 | B | 29 | 0.033844 | 8.7689e-05
7353286 | 2015-10-15 08:41 | 2015-10-15 14:56 | 375.15 | 8 | 3001.2 | 375.15 | 372.15 | 0.0090749 | 2977.2 | 0.0090023 | 2.419e-05 | NAPA ID:11555 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 726876 | Replacing poles from 726876 to 726882. Works location: Wood St. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-15 | b | 0.0045012 | 1.2095e-05 | 2016 | 2015-10-15 | B | 8 | 0.0090023 | 2.419e-05
7353390 | 2015-10-16 08:46 | 2015-10-16 12:28 | 222.0667 | 8 | 1776.5333 | 222.0667 | 219.0667 | 0.0053718 | 1752.5333 | 0.0052992 | 2.419e-05 | NAPA ID:11556 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726883 | Replacing pole's from 726883 to 726889. Works location: Wood St. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-16 | b | 0.0026496 | 1.2095e-05 | 2016 | 2015-10-16 | B | 8 | 0.0052992 | 2.419e-05
7358510 | 2015-10-07 09:16 | 2015-10-07 15:12 | 356.7167 | 10 | 3564.2333 | 356.4233 | 353.4233 | 0.010777 | 3534.2333 | 0.010687 | 3.0238e-05 | NAPA ID:12374 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole U12847 | Break jumpers live line at U12847 to enable crossarm and pole replacement at various sites. Works location: Kitahi Rd, Hikuai. WO 30003727 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 0.0053433 | 1.5119e-05 | 2016 | 2015-10-07 | B | 10 | 0.010687 | 3.0238e-05
7362461 | 2015-09-21 14:12 | 2015-09-21 17:56 | 224.3333 | 283 | 19494.5 | 68.8852 | 65.8852 | 0.058947 | 18645.5 | 0.05638 | 0.00085572 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715887 | CB9 Tripped e/f Isolated at ABS TA995 & TA896. Materials used 1 x crossarm and binders | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.05638 | 0.00085572 | 2016 | 2015-09-21 | C | 283 | 0.05638 | 0.00085572
7362748 | 2015-10-08 08:36 | 2015-10-08 16:01 | 445.1167 | 8 | 3560.9333 | 445.1167 | 442.1167 | 0.010767 | 3536.9333 | 0.010695 | 2.419e-05 | NAPA ID:12803 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V32 | Tree work by Treescape and in the same shut down downer to fly in new 11kV pole to replace red tagged pole P00460. Treescape WO#10152356. Works location: Manuhara Rd. WO 10162794. Pole not replaced due to no helicopter available. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-08 | b | 0.0053474 | 1.2095e-05 | 2016 | 2015-10-08 | B | 8 | 0.010695 | 2.419e-05
7362780 | 2015-10-09 08:57 | 2015-10-09 13:13 | 256 | 8 | 2048 | 256 | 253 | 0.0061927 | 2024 | 0.0061201 | 2.419e-05 | NAPA ID:12806 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses V32 | Tree work by tree scape and in the same shut down downer to fly in new 11kv pole to replace red tagged pole p00460 Treescape WO#10152356. Works location: Manuhara Rd. WO 10162794 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-09 | b | 0.00306 | 1.2095e-05 | 2016 | 2015-10-09 | B | 8 | 0.0061201 | 2.419e-05
7365093 | 2015-10-23 08:56 | 2015-10-23 14:23 | 327.35 | 61 | 19968.35 | 327.35 | 324.35 | 0.06038 | 19785.35 | 0.059826 | 0.00018445 | NAPA ID:12459 TP_HUIRANGI GXP > INGLEWOOD SUB > RATA ST | 6.6 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4851 | Install new poles in work area. upgrade 6.6kv cable to existing tx 2962T. Works location: Hinau St. WO 30001909 | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-23 | b | 0.029913 | 9.2225e-05 | 2016 | 2015-10-23 | B | 61 | 0.059826 | 0.00018445
7365224 | 2015-10-12 09:00 | 2015-10-12 13:11 | 251.1333 | 14 | 3515.8667 | 251.1333 | 248.1333 | 0.010631 | 3473.8667 | 0.010504 | 4.2333e-05 | NAPA ID:12895 TP_MASTERTON GXP > CLAREVILLE SUB > BELVEDERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 7556 | Replace existing pole 817232 with new 11.0m Busck concrete pole and new 15kVA 3 phase transformer and connect. CIW 122517 | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-12 | b | 0.0052521 | 2.1166e-05 | 2016 | 2015-10-12 | B | 14 | 0.010504 | 4.2333e-05
7365275 | 2015-09-21 15:16 | 2015-09-21 17:45 | 148.85 | 10 | 1488.5 | 148.85 | 145.85 | 0.0045009 | 1458.5 | 0.0044102 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M9 | check if OMS 7365332 and 7365408 are related 2 x Fuses found blown at fuses M9 - line patrolled with no fault found - used 2 x 6 amp fuses | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.0044102 | 3.0238e-05 | 2016 | 2015-09-21 | C | 10 | 0.0044102 | 3.0238e-05
7365361 | 2015-10-08 09:30 | 2015-10-08 12:44 | 194 | 9 | 1746 | 194 | 191 | 0.0052795 | 1719 | 0.0051978 | 2.7214e-05 | NAPA ID:12888 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC519 | Replace Crossarm at TC519. Works location: Old Netherton Rd, Netherton. WO 30001145 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.0025989 | 1.3607e-05 | 2016 | 2015-10-08 | B | 9 | 0.0051978 | 2.7214e-05
7365802 | 2015-09-21 16:14 | 2015-09-21 20:43 | 269.2833 | 1 | 269.2833 | 269.2833 | 266.2833 | 0.00081425 | 266.2833 | 0.00080518 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TE8-028 | Faulty transformer to be replaced. Transfomrer replaced 15-11-1, 25mm conductor | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.00080518 | 3.024e-06 | 2016 | 2015-09-21 | C | 1 | 0.00080518 | 3.0238e-06
7365843 | 2015-09-22 12:30 | 2015-09-22 14:15 | 105 | 3 | 315 | 105 | 102 | 0.00095248 | 306 | 0.00092527 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1-370 | Karl is reporting the transformer has fallen off the pole. Contractor reporting the 11kV lines are still live and blowing around in the wind. 4:19pm called through to hub - Dianne. Made safe and will replace the transformer tomorrow - cause was due to | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-09-22 | c | 0.00092527 | 9.071e-06 | 2016 | 2015-09-22 | C | 3 | 0.00092527 | 9.0713e-06
7366075 | 2015-09-21 16:37 | 2015-09-21 17:44 | 66.7667 | 67 | 4447.3 | 66.3776 | 63.3776 | 0.013448 | 4246.3 | 0.01284 | 0.00020259 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231312 | repaired broken lines. used little bit wire and 2 full tension sleeves. hv/oh. worked through control. cause: old age/rusty. FM advise this 500m span of wire over a gully will needs to be replaced as soon as possble otherwise it will happen again soon. Ad | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.01284 | 0.00020259 | 2016 | 2015-09-21 | C | 67 | 0.01284 | 0.00020259
7366999 | 2015-09-21 16:42 | 2015-09-22 00:23 | 461 | 1124 | 183408.8 | 163.1751 | 160.1751 | 0.55458 | 180036.8 | 0.54439 | 0.0033987 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | U20 | The tripping of this feeder was initiated via the Waitara East GFN. Initially had a tripping on CB U40 on E/F GFN (Refer OMS 7366176). When a backfeed was put in at VS8801, CB U20 tripped. Feeder restored OK after patrol. No fault found. GFN bypassed afte | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.54439 | 0.0033987 | 2016 | 2015-09-21 | C | 1124 | 0.54439 | 0.0033987
7368244 | 2015-09-21 15:38 | 2015-09-21 17:41 | 122.7667 | 3 | 368.3 | 122.7667 | 119.7667 | 0.0011137 | 359.3 | 0.0010864 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3173 | 2 x 3amp fuses replaced. due to high wind | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-09-21 | c | 0.0010864 | 9.071e-06 | 2016 | 2015-09-21 | C | 3 | 0.0010864 | 9.0713e-06
7368870 | 2015-09-21 18:29 | 2015-09-21 21:44 | 194.9833 | 107 | 7208.8333 | 67.3723 | 64.3723 | 0.021798 | 6887.8333 | 0.020827 | 0.00032354 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789900 | Tripping on sectionaliser 2592 on Phase A O/C, E/F. Patrol found a Pine tree which had come down breaking an 11kV Conductor. Isolation from Sectionaliser with conductor resleeved, rebound OK. Relivened. NDR 047056 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.020827 | 0.00032354 | 2016 | 2015-09-21 | C | 107 | 0.020827 | 0.00032354
7369130 | 2015-09-21 18:56 | 2015-09-21 20:32 | 96 | 774 | 21097.7 | 27.258 | 24.258 | 0.063794 | 18775.7 | 0.056773 | 0.0023404 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756678 | CB 3 trip E/F. Line patrolled & sectionalized. fault is line down at pole 756678. Isolated at Sw/Gear 12055/1 & ABS 561. Muktiple back feeds used from MRA CB 6 MRA CB 9 BKL CB 7 & OAK CB 2. Materials usrd 2 full tension sleeves & 1 m conductor. Not sure i | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.056773 | 0.0023404 | 2016 | 2015-09-21 | C | 774 | 0.056773 | 0.0023404
7372401 | 2015-09-21 20:21 | 2015-09-22 09:35 | 793.35 | 8 | 6346.8 | 793.35 | 790.35 | 0.019191 | 6322.8 | 0.019119 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8178 | 2 x 8amp fuses caused by weather | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.019119 | 2.419e-05 | 2016 | 2015-09-21 | C | 8 | 0.019119 | 2.419e-05
7373995 | 2015-09-21 18:31 | 2015-09-21 22:05 | 213.8667 | 5 | 1069.3333 | 213.8667 | 210.8667 | 0.0032334 | 1054.3333 | 0.0031881 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4316T | 2 HT fuses replaced at 4316T. (M.Patterson on site).7368920 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.0031881 | 1.5119e-05 | 2016 | 2015-09-21 | C | 5 | 0.0031881 | 1.5119e-05
7374011 | 2015-09-21 23:06 | 2015-09-22 00:34 | 87.8 | 809 | 58947.6333 | 72.8648 | 69.8648 | 0.17824 | 56520.6333 | 0.1709 | 0.0024462 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | S51 | Tripping on CB S51 on E/F. feeder patrolled / sectionalised but nothing found. Restored OK. | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.1709 | 0.0024462 | 2016 | 2015-09-21 | C | 809 | 0.1709 | 0.0024462
7374827 | 2015-09-20 23:09 | 2015-09-22 02:13 | 1624.1167 | 238 | 21917.05 | 92.0884 | 89.0884 | 0.066272 | 21203.05 | 0.064113 | 0.00071966 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737727 | Tripping on Cardiff CB Q11 on E/F, Phase C. Fedder patrolled / sectionalised with a faulty insulator found at Pole 737727. (Isolation at Fuses 4994). Insulator replasced, relivened OK. Windy / heavy rain in area. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-09-20 | c | 0.064113 | 0.00071966 | 2016 | 2015-09-20 | C | 238 | 0.064113 | 0.00071966
7376234 | 2015-09-22 02:00 | 2015-09-22 11:39 | 578.5 | 19 | 10991.5 | 578.5 | 575.5 | 0.033236 | 10934.5 | 0.033063 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6293 | Reload Reliven at 6293. 3 x 8 Amp Fuses. Crossarm and 3 Insulators Replaced at Pole 710124. Check down the road for further DDO's out, other no power jobs logged past these fuses.Relates to Original Job OMS 7376211. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-22 | c | 0.033063 | 5.7451e-05 | 2016 | 2015-09-22 | C | 19 | 0.033063 | 5.7451e-05
7376256 | 2015-09-21 16:58 | 2015-09-22 10:35 | 1056.95 | 29 | 30651.55 | 1056.95 | 1053.95 | 0.092683 | 30564.55 | 0.09242 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8292 | 2 x 15 AMP fuses weather | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.09242 | 8.7689e-05 | 2016 | 2015-09-21 | C | 29 | 0.09242 | 8.7689e-05
7377232 | 2015-09-24 09:45 | 2015-09-24 11:27 | 102 | 12 | 1224 | 102 | 99 | 0.0037011 | 1188 | 0.0035922 | 3.6285e-05 | NAPA ID:13117 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/536 | Replace 11KV Transformer T2/536. Work Location: Stoney Creek Road, Palmerston North. Work Order 30006881 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-24 | b | 0.0017961 | 1.8143e-05 | 2016 | 2015-09-24 | B | 12 | 0.0035922 | 3.6285e-05
7380547 | 2015-09-21 12:12 | 2015-09-21 12:26 | 14 | 640 | 8960 | 14 | 11 | 0.027093 | 7040 | 0.021287 | 0.0019352 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Recreation of OMS 7342989. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.021287 | 0.0019352 | 2016 | 2015-09-21 | C | 640 | 0.021287 | 0.0019352
7380553 | 2015-09-22 13:50 | 2015-09-22 14:10 | 20 | 4 | 80 | 20 | 17 | 0.0002419 | 68 | 0.00020562 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P1205 | Isolated on hv to repair lv lines. 1 63amp fuse carrier | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-22 | c | 0.00020562 | 1.2095e-05 | 2016 | 2015-09-22 | C | 4 | 0.00020562 | 1.2095e-05
7380607 | 2015-10-08 09:31 | 2015-10-08 12:44 | 193.2333 | 18 | 3374.7833 | 187.488 | 184.488 | 0.010205 | 3320.7833 | 0.010041 | 5.4428e-05 | NAPA ID:12641 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 229189 | REPLACE HV POLES AND ARMS. Works location: Pongakawa Station Rd. WO 30002468 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.0050206 | 2.7214e-05 | 2016 | 2015-10-08 | B | 18 | 0.010041 | 5.4428e-05
7381587 | 2015-09-22 13:32 | 2015-09-22 14:07 | 35.25 | 1 | 35.25 | 35.25 | 32.25 | 0.00010659 | 32.25 | 9.7516e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of planned outage 11270, advised customer. transformer T6/167 is not on spreadsheet as an affected trransformer | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-09-22 | c | 9.7516e-05 | 3.024e-06 | 2016 | 2015-09-22 | C | 1 | 9.7516e-05 | 3.0238e-06
7381958 | 2015-09-22 14:06 | 2015-09-22 18:50 | 283.6167 | 2 | 567.2333 | 283.6167 | 280.6167 | 0.0017152 | 561.2333 | 0.001697 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD6-046 | FM thought lightning may have hit this transformer but once he was up the pole he noticed it was just all corroded and has had it. Cross arms may have to be replaced as well. Transformer replaced 15-11-1 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-09-22 | c | 0.001697 | 6.048e-06 | 2016 | 2015-09-22 | C | 2 | 0.001697 | 6.0475e-06
7382640 | 2015-09-22 16:26 | 2015-09-22 16:46 | 19.4333 | 8 | 155.4667 | 19.4333 | 16.4333 | 0.00047009 | 131.4667 | 0.00039752 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 213 COULTERS LINE | Isolated transformer for tap change. Self permit. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-09-22 | c | 0.00039752 | 2.419e-05 | 2016 | 2015-09-22 | C | 8 | 0.00039752 | 2.419e-05
7385390 | 2015-09-23 06:08 | 2015-09-23 07:20 | 72.1833 | 3 | 216.55 | 72.1833 | 69.1833 | 0.0006548 | 207.55 | 0.00062758 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 762527 | 2 X 8AMP FUSE BRD STRIKE | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-23 | c | 0.00062758 | 9.071e-06 | 2016 | 2015-09-23 | C | 3 | 0.00062758 | 9.0713e-06
7387719 | 2015-10-13 08:04 | 2015-10-13 13:50 | 346.4333 | 129 | 44689.7333 | 346.432 | 343.432 | 0.13513 | 44302.7333 | 0.13396 | 0.00039007 | NAPA ID:11725 TP_MASTERTON GXP > CLAREVILLE SUB > SOMERSET RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 824090 | Close S364, open C437/2 to decrease load, open S343, Make live line cut at pole 824090, open S363, check open S328. So that ABS S343 can be changed. Works location: Carters Line, Carterton. WO 10159903 | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.06698 | 0.00019503 | 2016 | 2015-10-13 | B | 129 | 0.13396 | 0.00039007
7388719 | 2015-09-23 07:48 | 2015-09-23 11:07 | 198.6 | 2 | 397.2 | 198.6 | 195.6 | 0.001201 | 391.2 | 0.0011829 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 1433 | Replaced 3x 10Amp Links & 1x Candle | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-09-23 | c | 0.0011829 | 6.048e-06 | 2016 | 2015-09-23 | C | 2 | 0.0011829 | 6.0475e-06
7389256 | 2015-10-08 10:01 | 2015-10-08 15:13 | 312.1333 | 2 | 624.2667 | 312.1333 | 309.1333 | 0.0018876 | 618.2667 | 0.0018695 | 6.0475e-06 | NAPA ID:12422 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE NORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1498 | Replace termination pole and pole mount transformer. Works location: Collins Rd. WO 30000818 | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.00093474 | 3.024e-06 | 2016 | 2015-10-08 | B | 2 | 0.0018695 | 6.0475e-06
7389301 | 2015-10-13 09:33 | 2015-10-13 14:51 | 317.4833 | 5 | 1587.4167 | 317.4833 | 314.4833 | 0.0048 | 1572.4167 | 0.0047546 | 1.5119e-05 | NAPA ID:12254 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/32 | Remove 1pole of 2pole structure replace trani. Works location: Hwy 1, Sanson. WO 10159772 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.0023773 | 7.559e-06 | 2016 | 2015-10-13 | B | 5 | 0.0047546 | 1.5119e-05
7389337 | 2015-10-08 08:45 | 2015-10-08 14:07 | 321.8 | 6 | 1930.8 | 321.8 | 318.8 | 0.0058383 | 1912.8 | 0.0057838 | 1.8143e-05 | NAPA ID:11626 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212268 | Replace poles hardware and conductor between poles 212268 - 212283. Works location: McLaren Falls Rd. WO 30002530 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-08 | b | 0.0028919 | 9.071e-06 | 2016 | 2015-10-08 | B | 6 | 0.0057838 | 1.8143e-05
7389577 | 2015-10-02 09:15 | 2015-10-02 12:15 | 180 | 2 | 360 | 180 | 177 | 0.0010886 | 354 | 0.0010704 | 6.0475e-06 | NAPA ID:12727 TP_GREYTOWN GXP > KEMPTON SUB > PONATAHI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3677 | Upgrade T3677 to a 30-11-3 to accommodate future lots | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2015-10-02 | b | 0.00053521 | 3.024e-06 | 2016 | 2015-10-02 | B | 2 | 0.0010704 | 6.0475e-06
7389581 | 2015-10-13 08:30 | 2015-10-13 14:57 | 386.9333 | 9 | 3482.4 | 386.9333 | 383.9333 | 0.01053 | 3455.4 | 0.010448 | 2.7214e-05 | NAPA ID:11528 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726900 | Replacing pole's from 726901 to 726934. Works location: Wilson Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-13 | b | 0.0052242 | 1.3607e-05 | 2016 | 2015-10-13 | B | 9 | 0.010448 | 2.7214e-05
7389641 | 2015-10-14 09:32 | 2015-10-14 15:29 | 357.0833 | 9 | 3213.75 | 357.0833 | 354.0833 | 0.0097176 | 3186.75 | 0.009636 | 2.7214e-05 | NAPA ID:11530 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726900 | Replacing poles from 726901 to 726934. Works location: Wilson Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-14 | b | 0.004818 | 1.3607e-05 | 2016 | 2015-10-14 | B | 9 | 0.009636 | 2.7214e-05
7389681 | 2015-10-17 08:55 | 2015-10-17 11:30 | 155 | 1 | 155 | 155 | 152 | 0.00046868 | 152 | 0.00045961 | 3.0238e-06 | NAPA ID:11559 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI721 | Replacing pole's from 726934 to 726941. Works location: Marsh Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-17 | b | 0.00022981 | 1.512e-06 | 2016 | 2015-10-17 | B | 1 | 0.00045961 | 3.0238e-06
7389709 | 2015-10-19 10:24 | 2015-10-19 12:39 | 134.9 | 8 | 116.5333 | 14.5667 | 11.5667 | 0.00035237 | 92.5333 | 0.0002798 | 2.419e-05 | NAPA ID:11562 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI754 | Replacing pole's from 726932 to 726919. Works location: Pariroa Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-19 | b | 0.0001399 | 1.2095e-05 | 2016 | 2015-10-19 | B | 8 | 0.0002798 | 2.419e-05
7390724 | 2015-09-23 13:50 | 2015-09-23 14:28 | 37.6667 | 854 | 16128 | 18.8852 | 15.8852 | 0.048767 | 13566 | 0.04102 | 0.0025823 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | V0247 | Car vs Pole. Emergency switching carried out by faultman. ABS 2644 opened & tagged. Then carried out rest of switching normanly. Isolated at ABS 2643 then backfeed via ABS 9235/1. Repaired damage & relivened. NDR 047801. 1 pole 1 ht arm 1lt arm 3 63a fus | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-09-23 | c | 0.04102 | 0.0025823 | 2016 | 2015-09-23 | C | 854 | 0.04102 | 0.0025823
7390730 | 2015-10-21 09:30 | 2015-10-21 13:28 | 238.0667 | 8 | 1904.5333 | 238.0667 | 235.0667 | 0.0057589 | 1880.5333 | 0.0056863 | 2.419e-05 | NAPA ID:11567 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV LI701 | Replacing Condutor from 726876 to 726889. Works location: Woods St. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-21 | b | 0.0028431 | 1.2095e-05 | 2016 | 2015-10-21 | B | 8 | 0.0056863 | 2.419e-05
7390758 | 2015-10-22 09:55 | 2015-10-22 12:37 | 161.9333 | 29 | 4696.0667 | 161.9333 | 158.9333 | 0.0142 | 4609.0667 | 0.013937 | 8.7689e-05 | NAPA ID:11568 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV LI797 | Removing TEMP links from pole 726900 and work mist in shut downs between 24/9/15 and 21/10/15. Works location: Wilson Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-22 | b | 0.0069684 | 4.3845e-05 | 2016 | 2015-10-22 | B | 29 | 0.013937 | 8.7689e-05
7391733 | 2015-09-23 14:26 | 2015-09-23 15:19 | 52.7333 | 1 | 52.7333 | 52.7333 | 49.7333 | 0.00015945 | 49.7333 | 0.00015038 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | confirmed related to planned outage 12524 , shay confirms the customer is actually feed from TD4-010. Email sent to BI team for corrections. | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-09-23 | c | 0.00015038 | 3.024e-06 | 2016 | 2015-09-23 | C | 1 | 0.00015038 | 3.0238e-06
7392486 | 2015-09-21 22:26 | 2015-09-22 00:23 | 116.9833 | 117 | 5392.05 | 46.0859 | 43.0859 | 0.016304 | 5041.05 | 0.015243 | 0.00035378 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Received initial tripping on CB U40 on GFN E/F. A backfeed at VS8801 to recloser 6224 was put in service but this tripped CB U20 via GFN (Refer OMS 7366999). CBU40 was then sectionalised / patrolled but nothing found and all restored OK. However, A.Joyce | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-09-21 | c | 0.015243 | 0.00035378 | 2016 | 2015-09-21 | C | 117 | 0.015243 | 0.00035378
7392597 | 2015-10-14 09:00 | 2015-10-14 15:25 | 385.2667 | 5 | 1926.3333 | 385.2667 | 382.2667 | 0.0058248 | 1911.3333 | 0.0057794 | 1.5119e-05 | NAPA ID:12304 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/431 | Replace poles and cross arms between poles P21768 and pole P21781. Works location: Sandon Rd, Halcom. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-14 | b | 0.0028897 | 7.559e-06 | 2016 | 2015-10-14 | B | 5 | 0.0057794 | 1.5119e-05
7393747 | 2015-09-23 18:46 | 2015-09-23 20:04 | 78.3833 | 1 | 78.3833 | 78.3833 | 75.3833 | 0.00023701 | 75.3833 | 0.00022794 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP214 | 2 x 6 amp HV fuses replaced at FP214. Cause unknown | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-23 | c | 0.00022794 | 3.024e-06 | 2016 | 2015-09-23 | C | 1 | 0.00022794 | 3.0238e-06
7393958 | 2015-09-23 20:25 | 2015-09-23 22:34 | 128.4 | 14 | 1797.6 | 128.4 | 125.4 | 0.0054355 | 1755.6 | 0.0053085 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V52 | 2 Fuses found Blown at Fuses V52 - Line Patrolled with no Fault Found | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-09-23 | c | 0.0053085 | 4.2333e-05 | 2016 | 2015-09-23 | C | 14 | 0.0053085 | 4.2333e-05
7394980 | 2015-09-24 07:15 | 2015-09-24 09:01 | 105.5833 | 3 | 316.75 | 105.5833 | 102.5833 | 0.00095778 | 307.75 | 0.00093056 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 705083 | HV line down - Requesting help due to wind and also requires more gear - Have advised FM to contact the SMC and let them know what he needs. Can discuss whether this needs to be a 2R once we know scope of work at completion. Line Isolated at Fuses 6299 to | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.00093056 | 9.071e-06 | 2016 | 2015-09-24 | C | 3 | 0.00093056 | 9.0713e-06
7395336 | 2015-10-09 09:23 | 2015-10-09 14:30 | 307 | 4 | 1228 | 307 | 304 | 0.0037132 | 1216 | 0.0036769 | 1.2095e-05 | NAPA ID:12882 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-039 | Replace crossarms at various sites. Works location: Knyvett Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-09 | b | 0.0018384 | 6.048e-06 | 2016 | 2015-10-09 | B | 4 | 0.0036769 | 1.2095e-05
7395346 | 2015-09-24 07:53 | 2015-09-24 13:00 | 306.7 | 40 | 12268 | 306.7 | 303.7 | 0.037095 | 12148 | 0.036733 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P00904 | Please also check 7395599 - 562 Turitea Road. Tree through the lines. Replace 2m conductor & rehang at pole 300102. NDR 300102 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.036733 | 0.00012095 | 2016 | 2015-09-24 | C | 40 | 0.036733 | 0.00012095
7395367 | 2015-09-24 06:30 | 2015-09-25 17:18 | 2088.0167 | 86 | 14019.8333 | 163.0213 | 160.0213 | 0.042393 | 13761.8333 | 0.041612 | 0.00026004 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 796000 | Slip beyond Fuses 622 on Makopu Rd. There are 4 woolsheds and only on house effected. The resident of the house and has a generator he is happy to use for the duration of the outage. Fulton Hogan are trying to gain access to slip which may take 2 - 3 days | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.041612 | 0.00026004 | 2016 | 2015-09-24 | C | 86 | 0.041612 | 0.00026004
7395586 | 2015-09-27 09:30 | 2015-09-27 10:41 | 71.5 | 1 | 71.5 | 71.5 | 68.5 | 0.0002162 | 68.5 | 0.00020713 | 3.0238e-06 | NAPA ID:13176 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ARMSTRONG ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/678 | Shut cables down and close the line break at T6/678. Transformer T6/678 only feeds one customer and they have agreed to this shutdown on Sunday to reconnect the cables. Phasing as already been checked and is correct. Works location: Kelvin Grove Rd. WO 30 | F2 | ARMSTRONG ST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-09-27 | b | 0.00010356 | 1.512e-06 | 2016 | 2015-09-27 | B | 1 | 0.00020713 | 3.0238e-06
7396271 | 2015-10-12 09:01 | 2015-10-12 16:31 | 449.5833 | 7 | 3147.0833 | 449.5833 | 446.5833 | 0.009516 | 3126.0833 | 0.0094525 | 2.1166e-05 | NAPA ID:12798 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-059 | Replace poles, hardware and conductor between poles 220183 & 220205. Works location: Te Puke Quarry Rd. WO 30003844 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-10-12 | b | 0.0047263 | 1.0583e-05 | 2016 | 2015-10-12 | B | 7 | 0.0094525 | 2.1166e-05
7396438 | 2015-09-24 12:45 | 2015-09-24 15:25 | 160 | 41 | 6560 | 160 | 157 | 0.019836 | 6437 | 0.019464 | 0.00012397 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 8062/2 | ABS 8061 Opended to replace 1 x 6A fuse | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.019464 | 0.00012397 | 2016 | 2015-09-24 | C | 41 | 0.019464 | 0.00012397
7397303 | 2015-09-24 10:08 | 2015-09-24 11:09 | 61.4667 | 20 | 1229.3333 | 61.4667 | 58.4667 | 0.0037172 | 1169.3333 | 0.0035358 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E12970 | Lightning Arresters Replaced at Pole E12970. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-09-24 | c | 0.0035358 | 6.0475e-05 | 2016 | 2015-09-24 | C | 20 | 0.0035358 | 6.0475e-05
7397888 | 2015-09-24 12:15 | 2015-09-24 13:30 | 74.75 | 50 | 3737.5 | 74.75 | 71.75 | 0.011301 | 3587.5 | 0.010848 | 0.00015119 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Sectionaliser C218 found tripped. No flags | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.010848 | 0.00015119 | 2016 | 2015-09-24 | C | 50 | 0.010848 | 0.00015119
7397908 | 2015-09-24 12:21 | 2015-09-24 15:01 | 160 | 495 | 23403 | 47.2788 | 44.2788 | 0.070765 | 21918 | 0.066275 | 0.0014968 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P37160 | CB 9 Te Arakura Tripped on E/F at 12:21:22. Also check OMS 7398594 - 1011 RANGITIKEI LINE. Farmer hit pole and broke cross arm. NDR30894. Replace crossarm and insulators. | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.066275 | 0.0014968 | 2016 | 2015-09-24 | C | 495 | 0.066275 | 0.0014968
7398426 | 2015-10-02 09:00 | 2015-10-02 13:05 | 245 | 2 | 490 | 245 | 242 | 0.0014816 | 484 | 0.0014635 | 6.0475e-06 | NAPA ID:12713 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 222998, 222991 | Replace poles, crossarms and conductors. Install TEMP62 on pole 344726. Connect new 11kV line to existing 11kV at pole site 226106. Wokr Location: Te Puke Quarry Road. W/O 30003844. | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.00073175 | 3.024e-06 | 2016 | 2015-10-02 | B | 2 | 0.0014635 | 6.0475e-06
7398691 | 2015-10-15 08:45 | 2015-10-15 12:30 | 224.35 | 14 | 3140.9 | 224.35 | 221.35 | 0.0094973 | 3098.9 | 0.0093703 | 4.2333e-05 | NAPA ID:12571 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7028 | Replace defective transformer and pole T621. Works location: Kiriwhakapapa Rd, Masterton. WO 30013018 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-10-15 | b | 0.0046852 | 2.1166e-05 | 2016 | 2015-10-15 | B | 14 | 0.0093703 | 4.2333e-05
7398816 | 2015-10-20 09:15 | 2015-10-20 13:45 | 270 | 8 | 2160 | 270 | 267 | 0.0065313 | 2136 | 0.0064588 | 2.419e-05 | NAPA ID:11564 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726915 | Replacing pole726915. Works location: Pairoa Rd. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-20 | b | 0.0032294 | 1.2095e-05 | 2016 | 2015-10-20 | B | 8 | 0.0064588 | 2.419e-05
7399412 | 2015-10-16 10:30 | 2015-10-16 12:17 | 107 | 5 | 535 | 107 | 104 | 0.0016177 | 520 | 0.0015724 | 1.5119e-05 | NAPA ID:13132 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/382 | Upgrade 11kV Transformer T1/382 to 50kVA. Work Location: Cemetry Road, Sanson. W/O 30012863. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-16 | b | 0.00078618 | 7.559e-06 | 2016 | 2015-10-16 | B | 5 | 0.0015724 | 1.5119e-05
7403053 | 2015-09-24 16:42 | 2015-09-24 17:59 | 77.0333 | 17 | 1309.5667 | 77.0333 | 74.0333 | 0.0039598 | 1258.5667 | 0.0038056 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 837389 | Turned power off so trees could be removed from around wire to stop outage later on Jason Hall attended | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.0038056 | 5.1404e-05 | 2016 | 2015-09-24 | C | 17 | 0.0038056 | 5.1404e-05
7403210 | 2015-09-24 17:30 | 2015-09-24 19:51 | 140.9167 | 2 | 281.8333 | 140.9167 | 137.9167 | 0.0008522 | 275.8333 | 0.00083405 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC967 | 3 x 3 amp fuses replaced at transformer TC967 & 2 x 10 amp fuses replaced at fuses 2310. Lightning in area. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-09-24 | c | 0.00083405 | 6.048e-06 | 2016 | 2015-09-24 | C | 2 | 0.00083405 | 6.0475e-06
7403419 | 2015-09-24 17:44 | 2015-09-24 18:24 | 40 | 2 | 61.8333 | 30.9167 | 27.9167 | 0.00018697 | 55.8333 | 0.00016883 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R67 | Part of Job 7403301 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-09-24 | c | 0.00016883 | 6.048e-06 | 2016 | 2015-09-24 | C | 2 | 0.00016883 | 6.0475e-06
7404788 | 2015-09-25 05:12 | 2015-09-25 09:00 | 227.8333 | 1 | 227.8333 | 227.8333 | 224.8333 | 0.00068891 | 224.8333 | 0.00067984 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF8-012 | 11.35am - FM advise he signed this job off with Control at about 9:00am. replaced 2 x 2 amp hv. cause: unknown. The tx is noted as but it is TF8-012. No ICPs attached to TF8-012 in system. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-25 | c | 0.00067984 | 3.024e-06 | 2016 | 2015-09-25 | C | 1 | 0.00067984 | 3.0238e-06
7405322 | 2015-10-16 08:30 | 2015-10-16 14:23 | 353 | 10 | 3530 | 353 | 350 | 0.010674 | 3500 | 0.010583 | 3.0238e-05 | NAPA ID:12575 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7742 | Replace defective transformer and pole T618. Works location: Kiriwhakapapa Rd, Masterton. WO 30013021 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-10-16 | b | 0.0052916 | 1.5119e-05 | 2016 | 2015-10-16 | B | 10 | 0.010583 | 3.0238e-05
7405763 | 2015-10-19 10:00 | 2015-10-19 12:59 | 179 | 9 | 1611 | 179 | 176 | 0.0048713 | 1584 | 0.0047896 | 2.7214e-05 | NAPA ID:12686 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7277 | Replace Hv conductor. Works location: Western Lake Rd, Featherston. WO 30013127 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-19 | b | 0.0023948 | 1.3607e-05 | 2016 | 2015-10-19 | B | 9 | 0.0047896 | 2.7214e-05
7405838 | 2015-10-21 09:05 | 2015-10-21 12:22 | 197 | 2 | 394 | 197 | 194 | 0.0011914 | 388 | 0.0011732 | 6.0475e-06 | NAPA ID:12687 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7278 | Replace x2 poles and Hv conductors. Works location: Western Lake Rd, Featherston. WO 30013127 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-21 | b | 0.00058661 | 3.024e-06 | 2016 | 2015-10-21 | B | 2 | 0.0011732 | 6.0475e-06
7406174 | 2015-10-18 12:30 | 2015-10-18 15:54 | 203.7333 | 157 | 31986.1333 | 203.7333 | 200.7333 | 0.096718 | 31515.1333 | 0.095294 | 0.00047473 | NAPA ID:12593 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS T16 | Replace poles P18140 and P37441. Pole P18140 also includes the replacement and installation of a new ABS switch (T18). Works location: Tiraumea Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-18 | b | 0.047647 | 0.00023736 | 2016 | 2015-10-18 | B | 157 | 0.095294 | 0.00047473
7406392 | 2015-09-26 12:01 | 2015-09-28 16:25 | 3144.2167 | 10 | 4289.4833 | 428.9483 | 425.9483 | 0.01297 | 4259.4833 | 0.01288 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | Te Ore Ore Sub CB C822 | Patrol Line from Recloser C217 To The End. Jason Hall Will Do. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-26 | c | 0.01288 | 3.0238e-05 | 2016 | 2015-09-26 | C | 10 | 0.01288 | 3.0238e-05
7406874 | 2015-10-13 09:17 | 2015-10-13 12:20 | 183.2667 | 106 | 19426.2667 | 183.2667 | 180.2667 | 0.05874 | 19108.2667 | 0.057779 | 0.00032052 | NAPA ID:12889 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-012 | Replace H/V Crossarms at Various Sites. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.028889 | 0.00016026 | 2016 | 2015-10-13 | B | 106 | 0.057779 | 0.00032052
7406956 | 2015-10-13 09:33 | 2015-10-13 15:01 | 327.7167 | 44 | 14419.5333 | 327.7167 | 324.7167 | 0.043601 | 14287.5333 | 0.043202 | 0.00013305 | NAPA ID:12668 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF7-026 | Replace HV Poles & Crossarms. Works location: Old Coach Rd, Benner Rd. WO 30002468 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.021601 | 6.6523e-05 | 2016 | 2015-10-13 | B | 44 | 0.043202 | 0.00013305
7407277 | 2015-10-13 09:01 | 2015-10-13 14:15 | 314.4 | 19 | 5973.6 | 314.4 | 311.4 | 0.018063 | 5916.6 | 0.01789 | 5.7451e-05 | NAPA ID:12828 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2139 | Reconductoring from IC2139 to pole 269585. Works location: Tapu Coroglen Rd, Thames. WO 30002382 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.0089452 | 2.8726e-05 | 2016 | 2015-10-13 | B | 19 | 0.01789 | 5.7451e-05
7407333 | 2015-10-13 09:47 | 2015-10-13 12:15 | 148.4833 | 11 | 1633.3167 | 148.4833 | 145.4833 | 0.0049388 | 1600.3167 | 0.004839 | 3.3261e-05 | NAPA ID:12418 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-018 | Replace pole and raise conductors. Works location: Waitoa Rd. WO 30000817 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.0024195 | 1.6631e-05 | 2016 | 2015-10-13 | B | 11 | 0.004839 | 3.3261e-05
7412686 | 2015-10-21 09:16 | 2015-10-21 14:36 | 320.0833 | 2 | 640.1667 | 320.0833 | 317.0833 | 0.0019357 | 634.1667 | 0.0019176 | 6.0475e-06 | NAPA ID:12365 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP103 | Replace poles and crossarms at various sites. Works location: Manaia Rd, Coromandel. WO 30002265 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-21 | b | 0.00095878 | 3.024e-06 | 2016 | 2015-10-21 | B | 2 | 0.0019176 | 6.0475e-06
7412891 | 2015-10-22 08:31 | 2015-10-22 15:10 | 399.2167 | 185 | 73855.0833 | 399.2167 | 396.2167 | 0.22332 | 73300.0833 | 0.22164 | 0.0005594 | NAPA ID:10894 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 753852 | Change poles 753848,753852 ,753853,753857. Works location: Dixon ave, Oakura. WO 10136166 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-10-22 | b | 0.11082 | 0.0002797 | 2016 | 2015-10-22 | B | 185 | 0.22164 | 0.0005594
7414033 | 2015-09-26 09:12 | 2015-09-26 11:28 | 136 | 18 | 2448 | 136 | 133 | 0.0074022 | 2394 | 0.0072389 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 710016 | Brian Roache on 027445788 advised pole on very bad lean in danger of falling. Replace pole in morning. Craig has spoken to control and discussed - this pole is safe until tomorrow and they will reattend and replace pole tomorrow 26/9- Todd advised ok to c | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-09-26 | c | 0.0072389 | 5.4428e-05 | 2016 | 2015-09-26 | C | 18 | 0.0072389 | 5.4428e-05
7414059 | 2015-10-27 08:30 | 2015-10-27 15:26 | 416.1667 | 185 | 19560.6667 | 105.7333 | 102.7333 | 0.059147 | 19005.6667 | 0.057469 | 0.0005594 | NAPA ID:10896 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 753840 | Reconductor between poles 849476 & 753840. Works location: Dixon Ave, Oakura. WO 10136166 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-10-27 | b | 0.028734 | 0.0002797 | 2016 | 2015-10-27 | B | 185 | 0.057469 | 0.0005594
7414061 | 2015-10-14 09:46 | 2015-10-14 13:28 | 222.5 | 4 | 890 | 222.5 | 219.5 | 0.0026911 | 878 | 0.0026549 | 1.2095e-05 | NAPA ID:13203 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 216801 | Replace both sets of Term HV arms. Works location: Taumata Rd, Tauranga. WO 30001482 | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-14 | b | 0.0013274 | 6.048e-06 | 2016 | 2015-10-14 | B | 4 | 0.0026549 | 1.2095e-05
7414261 | 2015-09-25 17:04 | 2015-09-25 18:12 | 67.85 | 20 | 1261.9333 | 63.0967 | 60.0967 | 0.0038158 | 1201.9333 | 0.0036344 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI771 | Near the intersection Ball Rd and Wilford Rd. Contractors have been working in the area today at pole 393908 with tag L1771 on it - the pole is arching (sounds like a some one is welding on the pole). Called in by Brian Scone on 0274 983 204. 4:29pm | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-09-25 | c | 0.0036344 | 6.0475e-05 | 2016 | 2015-09-25 | C | 20 | 0.0036344 | 6.0475e-05
7416774 | 2015-09-25 22:33 | 2015-09-26 00:01 | 87.8167 | 113 | 9353.3167 | 82.7727 | 79.7727 | 0.028282 | 9014.3167 | 0.027257 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | RS C217/2, A/R, L/O, O/C B & C Phase. Sectionalised & Partially patrolled. No fault found. Trees were subsequently found. See OMS 7425397 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-25 | c | 0.027257 | 0.00034168 | 2016 | 2015-09-25 | C | 113 | 0.027257 | 0.00034168
7417367 | 2015-09-26 05:40 | 2015-09-26 07:17 | 97.3 | 1 | 97.3 | 97.3 | 94.3 | 0.00029421 | 94.3 | 0.00028514 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C23 | Replaced 2X 6aHV Fuses | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-09-26 | c | 0.00028514 | 3.024e-06 | 2016 | 2015-09-26 | C | 1 | 0.00028514 | 3.0238e-06
7417373 | 2015-09-26 08:25 | 2015-09-26 10:03 | 97.5167 | 3 | 292.55 | 97.5167 | 94.5167 | 0.0008846 | 283.55 | 0.00085739 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1607 | Tree branch in spur line at pole. Isolation at Fuses FC2387 to trim branches ( no back feeds ). Tree branch removed from poleE1607, all service restored. Materials 2 x 3A H/V O/H fuses. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-09-26 | c | 0.00085739 | 9.071e-06 | 2016 | 2015-09-26 | C | 3 | 0.00085739 | 9.0713e-06
7421683 | 2015-09-26 07:07 | 2015-09-26 08:27 | 80.3333 | 1 | 80.3333 | 80.3333 | 77.3333 | 0.00024291 | 77.3333 | 0.00023384 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 586 | Replaced 2 X 20a HV Fuses and carriers | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-09-26 | c | 0.00023384 | 3.024e-06 | 2016 | 2015-09-26 | C | 1 | 0.00023384 | 3.0238e-06
7426181 | 2015-09-27 00:22 | 2015-09-27 01:52 | 89.7667 | 833 | 74775.6333 | 89.7667 | 86.7667 | 0.2261 | 72276.6333 | 0.21855 | 0.0025188 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | CB C823 tripped E/F C Phase. Patrolled Feeder nothing found. Had trouble closing breaker. | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-27 | c | 0.21855 | 0.0025188 | 2016 | 2015-09-27 | C | 833 | 0.21855 | 0.0025188
7427319 | 2015-09-27 08:26 | 2015-09-27 09:56 | 90.4167 | 1 | 90.4167 | 90.4167 | 87.4167 | 0.0002734 | 87.4167 | 0.00026433 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7268 | Replaced 2X 10a HV Fuses | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2015-09-27 | c | 0.00026433 | 3.024e-06 | 2016 | 2015-09-27 | C | 1 | 0.00026433 | 3.0238e-06
7429497 | 2015-09-27 19:04 | 2015-09-27 20:44 | 100.45 | 1 | 100.45 | 100.45 | 97.45 | 0.00030374 | 97.45 | 0.00029467 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1754 | 3 X 2 Amp Fuses | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-09-27 | c | 0.00029466 | 3.024e-06 | 2016 | 2015-09-27 | C | 1 | 0.00029467 | 3.0238e-06
7430943 | 2015-09-28 07:30 | 2015-09-28 13:00 | 329.9333 | 2 | 659.8667 | 329.9333 | 326.9333 | 0.0019953 | 653.8667 | 0.0019771 | 6.0475e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | TESTING CABLES to check for tracking | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-09-28 | c | 0.0019771 | 6.048e-06 | 2016 | 2015-09-28 | C | 2 | 0.0019771 | 6.0475e-06
7431137 | 2015-09-28 08:08 | 2015-09-28 10:15 | 126.5833 | 2 | 253.1667 | 126.5833 | 123.5833 | 0.00076552 | 247.1667 | 0.00074737 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4184 | 3x fuses 2 amp fuses. Due to lightning strike. Internal board had problems too. Sparky to attend. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-09-28 | c | 0.00074737 | 6.048e-06 | 2016 | 2015-09-28 | C | 2 | 0.00074737 | 6.0475e-06
7431383 | 2015-10-02 13:00 | 2015-10-02 13:45 | 45 | 5 | 225 | 45 | 42 | 0.00068035 | 210 | 0.00063499 | 1.5119e-05 | NAPA ID:13274 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4293 | Replace unsafe staywire. Works location: Pioneer Rd, Morrinsville. OW 30009302 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-02 | b | 0.00031749 | 7.559e-06 | 2016 | 2015-10-02 | B | 5 | 0.00063499 | 1.5119e-05
7432633 | 2015-10-07 08:15 | 2015-10-07 15:40 | 444.7167 | 6 | 1856.3 | 309.3833 | 306.3833 | 0.005613 | 1838.3 | 0.0055586 | 1.8143e-05 | NAPA ID:11939 TP_MT MAUNGANUI 33 GXP > TRITON SUB > WHARF | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace existing Series 1 SD units SC4-490, SC4-136, SC4-138 & SC4-137 with a Safelink CFCF unit. NOTE ; Works continue until 09/10/15. Generator in Place. No Outage | F1 | WHARF | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 0.0027793 | 9.071e-06 | 2016 | 2015-10-07 | B | 6 | 0.0055586 | 1.8143e-05
7432977 | 2015-10-22 08:40 | 2015-10-22 12:21 | 221.25 | 6 | 1327.5 | 221.25 | 218.25 | 0.004014 | 1309.5 | 0.0039596 | 1.8143e-05 | NAPA ID:13313 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 726949 | Request from Daniel Woollaston to replace old faulty pole 726949 / L1265. Works location: Wilson Rd, Kakaramea. WO 30010596 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-10-22 | b | 0.0019798 | 9.071e-06 | 2016 | 2015-10-22 | B | 6 | 0.0039596 | 1.8143e-05
7452447 | 2015-10-07 06:31 | 2015-10-07 16:55 | 624.55 | 1 | 624.55 | 624.55 | 621.55 | 0.0018885 | 621.55 | 0.0018794 | 3.0238e-06 | NAPA ID:12772 TP_MT MAUNGANUI 33 GXP | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-256 | Isolate Rmu S5907-S5911 and TC4-256 via LLB (LL Permit) and install Generator to liven ICP's at TX.(Access Permit) Remove RMU to new site, joint 11kv cables to new section of cable and terminate to Rmu at new site(Access Permit) Test (Test Permit) and Rel | F2 | HEWLETTS RD | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-10-07 | b | 0.00093971 | 1.512e-06 | 2016 | 2015-10-07 | B | 1 | 0.0018794 | 3.0238e-06
7453080 | 2015-10-09 09:03 | 2015-10-09 15:33 | 390.45 | 17 | 6637.65 | 390.45 | 387.45 | 0.020071 | 6586.65 | 0.019916 | 5.1404e-05 | NAPA ID:11976 TP_PIAKO GXP > PIAKO SUB | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | - | Change 11kV ABS IC2529 on CB5, IC1074 on CB 8 and arm on Both CB 8 and CB 5 feeder from Piako. Work Location: Walton Road, Morrinsville. W/O 10148253 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-09 | b | 0.0099582 | 2.5702e-05 | 2016 | 2015-10-09 | B | 17 | 0.019916 | 5.1404e-05
7453144 | 2015-09-28 10:43 | 2015-09-28 13:45 | 182.2833 | 2 | 364.5667 | 182.2833 | 179.2833 | 0.0011024 | 358.5667 | 0.0010842 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TC4743 | Replace 2 x 3A Fuses | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-09-28 | c | 0.0010842 | 6.048e-06 | 2016 | 2015-09-28 | C | 2 | 0.0010842 | 6.0475e-06
7453163 | 2015-10-17 06:19 | 2015-10-23 07:14 | 8695 | 257 | 15888.7833 | 61.8241 | 58.8241 | 0.048044 | 15117.7833 | 0.045713 | 0.00077711 | NAPA ID:13288 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P16738 | 1)make cable break at transformer T6/538 (break to be going back towards 142, disconnect LV from bushings at transformer T6/587 due to LV not paralleling in.) 2)connect and test new cable on either side of T6/587 3)liven to phase at T6/587 4)close cable b | F1 | RUAHINE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-10-17 | b | 0.022856 | 0.00038855 | 2016 | 2015-10-17 | B | 257 | 0.045713 | 0.00077711
7454061 | 2015-09-28 18:57 | 2015-09-29 05:44 | 646.8 | 1 | 646.8 | 646.8 | 643.8 | 0.0019558 | 643.8 | 0.0019467 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF7 092 | Replace transformer TF& 092 & 1 x fuse H/V, O/H at Fuses SF7 012 (lightning). B Sperling own isolation & AP transformer replaced all service restored. Material 1 x transformer , 3 x 8 A fuses 1 x 8 A fuse at fuses SF7 012 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-28 | c | 0.0019467 | 3.024e-06 | 2016 | 2015-09-28 | C | 1 | 0.0019467 | 3.0238e-06
7454185 | 2015-09-28 19:33 | 2015-09-28 20:55 | 81.5167 | 1 | 81.5167 | 81.5167 | 78.5167 | 0.00024649 | 78.5167 | 0.00023742 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228650 | Replace 2 x 2A O/H, H/V fuses ( lightning ) | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-28 | c | 0.00023742 | 3.024e-06 | 2016 | 2015-09-28 | C | 1 | 0.00023742 | 3.0238e-06
7454302 | 2015-09-28 20:33 | 2015-09-29 05:49 | 555.2 | 8 | 423.85 | 52.9813 | 49.9813 | 0.0012816 | 399.85 | 0.0012091 | 2.419e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | TE8 022 | Replace transformer TE8 022 (lightning). H Hiha own isolation & AP. Transformer replaced all service restored. Materials 1 x transformer 3 x 3 A H/V O/H fuses. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-28 | c | 0.0012091 | 2.419e-05 | 2016 | 2015-09-28 | C | 8 | 0.0012091 | 2.419e-05
7454817 | 2015-09-28 21:24 | 2015-09-28 22:45 | 81.2833 | 6 | 487.7 | 81.2833 | 78.2833 | 0.0014747 | 469.7 | 0.0014203 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 852922 | Replace 2 x 2A H/V, O/H fuses lightning | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-09-28 | c | 0.0014203 | 1.8143e-05 | 2016 | 2015-09-28 | C | 6 | 0.0014203 | 1.8143e-05
7455505 | 2015-09-29 06:22 | 2015-09-29 09:00 | 158.45 | 12 | 1901.4 | 158.45 | 155.45 | 0.0057494 | 1865.4 | 0.0056405 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7774 | Replace 2 x 10A fuse | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-09-29 | c | 0.0056405 | 3.6285e-05 | 2016 | 2015-09-29 | C | 12 | 0.0056405 | 3.6285e-05
7456201 | 2015-10-22 09:36 | 2015-10-22 16:47 | 431.5667 | 24 | 10357.6 | 431.5667 | 428.5667 | 0.031319 | 10285.6 | 0.031101 | 7.257e-05 | NAPA ID:13196 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS T16 | Replace and install new poles. Works location: Riccarton Rd & Chatham St, Pahiatua. WO 10151698. Job had a over run due to poles that needed to be removed were concerted in which slowed the work down and job was late going back due to faultman been on fee | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-22 | b | 0.015551 | 3.6285e-05 | 2016 | 2015-10-22 | B | 24 | 0.031101 | 7.257e-05
7456236 | 2015-10-20 09:31 | 2015-10-20 15:40 | 369.1333 | 24 | 8859.2 | 369.1333 | 366.1333 | 0.026788 | 8787.2 | 0.02657 | 7.257e-05 | NAPA ID:13194 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS T16 | Replace and install new poles. Install new conductor. Works location: Tiraumea Rd & Riccarton Rd, Pahiatua. WO 10151698. NOTE: Delay in restoration - Contractors unable to complete work in allocated time. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-20 | b | 0.013285 | 3.6285e-05 | 2016 | 2015-10-20 | B | 24 | 0.02657 | 7.257e-05
7457164 | 2015-09-29 12:01 | 2015-09-29 12:52 | 51.2833 | 52 | 2666.7333 | 51.2833 | 48.2833 | 0.0080636 | 2510.7333 | 0.0075919 | 0.00015724 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2230 | Replaced 3x HV Fuse Holders complete with 3 Amp Links. 1 fuse holder broken at Transformer M2230 so due to their age the full set were replaced. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-09-29 | c | 0.0075919 | 0.00015724 | 2016 | 2015-09-29 | C | 52 | 0.0075919 | 0.00015724
7457733 | 2015-09-29 16:40 | 2015-09-29 16:42 | 2 | 7 | 14 | 2 | -1 | 4.2333e-05 | 0 | 0 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2645T | Report of lines making loud buzzing sound. Line patrolled and 3 3 amp links replaced. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-09-29 | c | 0 | 2.1166e-05 | 2016 | 2015-09-29 | C | 7 | 0 | 2.1166e-05
7458323 | 2015-10-15 09:16 | 2015-10-15 15:05 | 349.35 | 8 | 2775.8 | 346.975 | 343.975 | 0.0083934 | 2751.8 | 0.0083208 | 2.419e-05 | NAPA ID:12670 TP_TE MATAI GXP > PONGAKAWA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 322792 | REPLACE HV POLES AND ARMS. Works location: Old Coach Rd. WO 30002468 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-15 | b | 0.0041604 | 1.2095e-05 | 2016 | 2015-10-15 | B | 8 | 0.0083208 | 2.419e-05
7458379 | 2015-10-21 09:00 | 2015-10-21 15:01 | 360.8333 | 76 | 27423.3333 | 360.8333 | 357.8333 | 0.082922 | 27195.3333 | 0.082232 | 0.00022981 | NAPA ID:12680 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS M76 | Replace poles, X arms and install temporary ABS 4100 on pole P21959. Works location: Te Rakehou Rd, Halcombe. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-21 | b | 0.041116 | 0.0001149 | 2016 | 2015-10-21 | B | 76 | 0.082232 | 0.00022981
7458615 | 2015-10-04 08:25 | 2015-10-04 10:41 | 136.1167 | 5 | 680.5833 | 136.1167 | 133.1167 | 0.0020579 | 665.5833 | 0.0020126 | 1.5119e-05 | NAPA ID:13235 TP_TAURANGA 33 GXP > HAMILTON STREET SUB > CHAPEL ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | TL2 017 | Disconnect HV cable at Transformer TL2-001 which feeds Tl2-017, then remove Transformer TL2-017. | F1 | CHAPEL ST | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 2015-10-04 | b | 0.0010063 | 7.559e-06 | 2016 | 2015-10-04 | B | 5 | 0.0020126 | 1.5119e-05
7459222 | 2015-09-29 21:05 | 2015-09-29 23:42 | 156.6833 | 22 | 3447.0333 | 156.6833 | 153.6833 | 0.010423 | 3381.0333 | 0.010223 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 837780 | 824 WAITAWHITI ROAD - Tractor has brought lines down. Advised hub and control.Large span 11kV Conductor on ground (250M). Rejointed OK. Also 2 guy wires temp repaired. Relivened OK. NDR 37763. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-09-29 | c | 0.010223 | 6.6523e-05 | 2016 | 2015-09-29 | C | 22 | 0.010223 | 6.6523e-05
7459739 | 2015-09-29 17:58 | 2015-09-30 06:28 | 749.5 | 1161 | 70573.8 | 60.7871 | 57.7871 | 0.2134 | 67090.8 | 0.20287 | 0.0035106 |  | 33 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | PON-ALF 33kV | Received Initial tripping on MGM GXP CB1332 on E/F, O/C. This caused a loss of supply at both Pongaroa and Alfredton as the Parkville-Alfredton 33kV section was out of service. ( Work on Parkville CB XT40). Supply restored OK up to Pongaroa and Sub restor | F1,F2,F3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2015-09-29 | c | 0.20287 | 0.0035106 | 2016 | 2015-09-29 | C | 1161 | 0.20287 | 0.0035106
7460706 | 2015-09-29 18:16 | 2015-09-29 21:21 | 185.4 | 1 | 185.4 | 185.4 | 182.4 | 0.00056061 | 182.4 | 0.00055153 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5643 | replacing 2x3amp HV fuses blown at TX TC 5643 (sent email to NI to change TX on data base for the above address and ICP) Replace 2 fuses & 1 Fuse barrell. Line patrolled Unknown cause | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-09-29 | c | 0.00055153 | 3.024e-06 | 2016 | 2015-09-29 | C | 1 | 0.00055153 | 3.0238e-06
7460762 | 2015-09-29 20:21 | 2015-09-29 22:50 | 149 | 2 | 298 | 149 | 146 | 0.00090108 | 292 | 0.00088294 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/224 | pole # P15391 TX 3 T8/224. check to see if oms 7460726 (4994 MANGATAINOKA VALLEY ROAD)is the same fault. 2R to replace TX. Transformer replaced and relivened. (Rusty / poor condition). | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-09-29 | c | 0.00088294 | 6.048e-06 | 2016 | 2015-09-29 | C | 2 | 0.00088294 | 6.0475e-06
7461653 | 2015-09-30 17:42 | 2015-09-30 17:48 | 5.7167 | 180 | 1029 | 5.7167 | 2.7167 | 0.0031114 | 489 | 0.0014786 | 0.00054428 | Referral | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | ALF-PON 33kV line | 2R Carryout line patrol on ALF-PON 33kV Daylight hours Wednesday 30th. May require helicopter. Line patrol carrier out with Oppossum found on crossarm, access to pole very difficult. Decide as possum clear of lines to leave. Discussion with Nigel Timms of | F1,F2,F3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-09-30 | c | 0.0014786 | 0.00054428 | 2016 | 2015-09-30 | C | 180 | 0.0014786 | 0.00054428
7463705 | 2015-09-30 08:00 | 2015-09-30 09:30 | 90.5167 | 14 | 1267.2333 | 90.5167 | 87.5167 | 0.0038318 | 1225.2333 | 0.0037048 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 707 | Replace 15Amp fuses at 707 | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-09-30 | c | 0.0037048 | 4.2333e-05 | 2016 | 2015-09-30 | C | 14 | 0.0037048 | 4.2333e-05
7465093 | 2015-10-02 09:30 | 2015-10-02 13:40 | 249.5 | 6 | 1497 | 249.5 | 246.5 | 0.0045266 | 1479 | 0.0044721 | 1.8143e-05 | NAPA ID:13374 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7776 | 11kv pole leaning over coming out of ground due to track being installed by logging contractor for tree removal unsure of when little remaining ground which was surporting pole has giving way due to heavy rain. Works location: Mangapurupuru Rd, Bideford. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-02 | b | 0.0022361 | 9.071e-06 | 2016 | 2015-10-02 | B | 6 | 0.0044721 | 1.8143e-05
7465214 | 2015-10-07 08:00 | 2015-10-07 11:32 | 211.1333 | 3 | 633.4 | 211.1333 | 208.1333 | 0.0019153 | 624.4 | 0.001888 | 9.0713e-06 | NAPA ID:13382 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 8287 | Isolations to cut burnt trees causing fluctuations on line. Works location: Awai Rd. WO 30007226 | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-10-07 | b | 0.00094402 | 4.536e-06 | 2016 | 2015-10-07 | B | 3 | 0.001888 | 9.0713e-06
7465251 | 2015-10-16 09:23 | 2015-10-16 14:40 | 316.55 | 64 | 20259.2 | 316.55 | 313.55 | 0.061259 | 20067.2 | 0.060678 | 0.00019352 | NAPA ID:12600 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV IC247 | Tree trimming Standover for Asplundh. Works location: Waitawheta. WO 10152354 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-16 | b | 0.030339 | 9.676e-05 | 2016 | 2015-10-16 | B | 64 | 0.060678 | 0.00019352
7466122 | 2015-10-20 08:46 | 2015-10-20 16:30 | 464.15 | 20 | 9283 | 464.15 | 461.15 | 0.02807 | 9223 | 0.027888 | 6.0475e-05 | NAPA ID:12583 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS L52 | Cut a line break at the two pole structure P26820, P26826, run new conductor from ABS L52 to the two pole structure, reinstate the line break. NOTE: Delay in restoration, Contractor unable to complete all work in allocated time. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-20 | b | 0.013944 | 3.0238e-05 | 2016 | 2015-10-20 | B | 20 | 0.027888 | 6.0475e-05
7467157 | 2015-09-30 19:34 | 2015-09-30 20:56 | 81.3333 | 2 | 162.6667 | 81.3333 | 78.3333 | 0.00049187 | 156.6667 | 0.00047372 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2273 | 2x30amp fuses blown at FC2273. line patrolled no fault found. | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-09-30 | c | 0.00047372 | 6.048e-06 | 2016 | 2015-09-30 | C | 2 | 0.00047372 | 6.0475e-06
7467716 | 2015-10-01 04:41 | 2015-10-01 09:01 | 259.55 | 67 | 9247.85 | 138.0276 | 135.0276 | 0.027963 | 9046.85 | 0.027356 | 0.00020259 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | H0015 | Police reported Car V Pole lines down. Pole H0015 Isolation at ABS IC757 & IC622. 11m Busk Thru Pole and All associated Hardware Replaced. | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-10-01 | c | 0.027356 | 0.00020259 | 2016 | 2015-10-01 | C | 67 | 0.027356 | 0.00020259
7467728 | 2015-10-01 03:34 | 2015-10-01 07:53 | 259.3333 | 4 | 755.75 | 188.9375 | 185.9375 | 0.0022852 | 743.75 | 0.0022489 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1293 | 2X fuses at FP1293 10 Amp Emap shows wrong place | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-01 | c | 0.0022489 | 1.2095e-05 | 2016 | 2015-10-01 | C | 4 | 0.0022489 | 1.2095e-05
7471028 | 2015-10-27 09:44 | 2015-10-27 14:40 | 295.8333 | 7 | 2070.8333 | 295.8333 | 292.8333 | 0.0062617 | 2049.8333 | 0.0061982 | 2.1166e-05 | NAPA ID:12515 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses V8 | To replace rotten larch poles. Works location: Korora Rd. WO 30000750 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-27 | b | 0.0030991 | 1.0583e-05 | 2016 | 2015-10-27 | B | 7 | 0.0061982 | 2.1166e-05
7471171 | 2015-10-28 09:55 | 2015-10-28 16:02 | 367 | 7 | 2569 | 367 | 364 | 0.007768 | 2548 | 0.0077045 | 2.1166e-05 | NAPA ID:12517 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V8 | To replace rotten larch poles. Works location: Korora Rd. WO 30000750 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-28 | b | 0.0038523 | 1.0583e-05 | 2016 | 2015-10-28 | B | 7 | 0.0077045 | 2.1166e-05
7471315 | 2015-10-31 09:28 | 2015-10-31 11:55 | 146.6333 | 7 | 1026.4333 | 146.6333 | 143.6333 | 0.0031037 | 1005.4333 | 0.0030402 | 2.1166e-05 | NAPA ID:12519 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses V8 | To replace rotten larch poles. Works location: Korora Rd. WO 30000750 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-31 | b | 0.0015201 | 1.0583e-05 | 2016 | 2015-10-31 | B | 7 | 0.0030402 | 2.1166e-05
7471795 | 2015-10-02 08:45 | 2015-10-02 10:10 | 85 | 40 | 3400 | 85 | 82 | 0.010281 | 3280 | 0.0099179 | 0.00012095 | NAPA ID:13407 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 379238 | Close 11Kv line break @ pole 379207 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-10-02 | b | 0.004959 | 6.0475e-05 | 2016 | 2015-10-02 | B | 40 | 0.0099179 | 0.00012095
7472079 | 2015-10-01 11:55 | 2015-10-01 15:55 | 240.05 | 15 | 3600.75 | 240.05 | 237.05 | 0.010888 | 3555.75 | 0.010752 | 4.5356e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 763155 | Faultman required to isolate & earth for emergency tree cutting work. Faultman please call NOC control when assigned to job. Trees cut by Asplundh, | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-01 | c | 0.010752 | 4.5356e-05 | 2016 | 2015-10-01 | C | 15 | 0.010752 | 4.5356e-05
7472086 | 2015-10-01 11:19 | 2015-10-01 16:55 | 336.1 | 82 | 148.75 | 1.814 | -1.186 | 0.00044978 | 0 | 0 | 0.00024795 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 739280 | CB 7121 A/R, O/C, E/F. Line was patrolled & trees found to be contacting HV at Pole 739280. Lines Isolated at Fuses 5650 & Asplundh attended to cut trees. NDR #N100065 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-10-01 | c | 0 | 0.00024795 | 2016 | 2015-10-01 | C | 82 | 0 | 0.00024795
7473926 | 2015-10-17 09:01 | 2015-10-17 14:26 | 325 | 14 | 4550 | 325 | 322 | 0.013758 | 4508 | 0.013631 | 4.2333e-05 | NAPA ID:13262 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC487 | To replace a pole, install a new transformer & Repair damaged lines. Works location: Kaihere Rd, Ngatea. WO 30015055 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-10-17 | b | 0.0068156 | 2.1166e-05 | 2016 | 2015-10-17 | B | 14 | 0.013631 | 4.2333e-05
7474137 | 2015-10-19 09:30 | 2015-10-19 15:30 | 359.7333 | 34 | 12230.9333 | 359.7333 | 356.7333 | 0.036983 | 12128.9333 | 0.036675 | 0.00010281 | NAPA ID:11631 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 382234 | Replace poles, hardware and conductor between poles 382234 - 383038. LL Connect new conductor to SF3-010 once AP cancelled. Works location: McLaren Falls Rd. WO 30002530 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-19 | b | 0.018337 | 5.1404e-05 | 2016 | 2015-10-19 | B | 34 | 0.036675 | 0.00010281
7474279 | 2015-10-01 12:51 | 2015-10-01 15:16 | 144.9667 | 2 | 138.5167 | 69.2583 | 66.2583 | 0.00041884 | 132.5167 | 0.0004007 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x4181 | 3X2 amp fuses at tx x4181 SAIDI on child job | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-10-01 | c | 0.0004007 | 6.048e-06 | 2016 | 2015-10-01 | C | 2 | 0.0004007 | 6.0475e-06
7474524 | 2015-10-28 09:18 | 2015-10-28 15:01 | 342.8667 | 49 | 16800.4667 | 342.8667 | 339.8667 | 0.050801 | 16653.4667 | 0.050356 | 0.00014816 | NAPA ID:12835 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M76 | Replace poles, cross arms and conductor between poles P21782 and P21959. Works location: Te Rakehou Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-28 | b | 0.025178 | 7.4082e-05 | 2016 | 2015-10-28 | B | 49 | 0.050356 | 0.00014816
7474808 | 2015-10-28 09:11 | 2015-10-28 15:07 | 356.6333 | 19 | 6776.0333 | 356.6333 | 353.6333 | 0.020489 | 6719.0333 | 0.020317 | 5.7451e-05 | NAPA ID:13199 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T24 | Replace and install new poles. Works location: Mangaramarama Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-28 | b | 0.010158 | 2.8726e-05 | 2016 | 2015-10-28 | B | 19 | 0.020317 | 5.7451e-05
7475335 | 2015-10-01 15:38 | 2015-10-01 20:00 | 262 | 60 | 15720 | 262 | 259 | 0.047534 | 15540 | 0.046989 | 0.00018143 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | R1525 | car v pole. SVS hub advised. ETA required, svs hub advise 15 min ETA police comms advised. P022709806. Requesting 2R - will need to replace LV pole, insulators etc. Wayne is leaving site. | F4 | WHIRITOA | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-10-01 | c | 0.046989 | 0.00018143 | 2016 | 2015-10-01 | C | 60 | 0.046989 | 0.00018143
7477507 | 2015-10-01 18:22 | 2015-10-01 19:33 | 70.5333 | 649 | 22827.6667 | 35.1736 | 32.1736 | 0.069025 | 20880.6667 | 0.063138 | 0.0019624 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 747721 | Outside 1283 Junction road - trees on lines, arching and sparking. 6.26pm - advised hub of 999 Fire require an ETA 04 801 0812. F1928259. Branch on lines at Pole 747721 - Isolated at ABS's 402 & 161 with a backfeed installed via ABS 115. Branch Cleared v | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-01 | c | 0.063138 | 0.0019624 | 2016 | 2015-10-01 | C | 649 | 0.063138 | 0.0019624
7480076 | 2015-10-02 03:54 | 2015-10-02 14:36 | 642.05 | 58 | 18324.9 | 315.9466 | 312.9466 | 0.05541 | 18150.9 | 0.054884 | 0.00017538 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 708732 | Trees contacted lines & bought lines down. Asplundh called to cut trees. Lines repaired using 4 sleeves, 10 m squirrel conductor, & 1x 6Amps HV Link. NDR100068 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-10-02 | c | 0.054884 | 0.00017538 | 2016 | 2015-10-02 | C | 58 | 0.054884 | 0.00017538
7480799 | 2015-10-02 11:56 | 2015-10-02 13:32 | 96 | 596 | 57216 | 96 | 93 | 0.17301 | 55428 | 0.1676 | 0.0018022 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P32424 | Blown jumper at P32424 Isolated at ABS L39. 5 x 25mm Sleeves used. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-02 | c | 0.1676 | 0.0018022 | 2016 | 2015-10-02 | C | 596 | 0.1676 | 0.0018022
7482805 | 2015-10-20 09:00 | 2015-10-20 14:00 | 300 | 6 | 1800 | 300 | 297 | 0.0054428 | 1782 | 0.0053883 | 1.8143e-05 | NAPA ID:12625 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4505 | Replace H.V crossarm and DDO,s controlling TC4505 liveline and then replace L.V arms under an AP. Works location: Te Rerenga Kuaotunu Rd, Coromandel. WO 30002490 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-10-20 | b | 0.0026942 | 9.071e-06 | 2016 | 2015-10-20 | B | 6 | 0.0053883 | 1.8143e-05
7483702 | 2015-10-02 12:08 | 2015-10-02 15:50 | 222.1667 | 331 | 60954.4167 | 184.1523 | 181.1523 | 0.18431 | 59961.4167 | 0.18131 | 0.0010009 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 325103 | car v pole isolated at abs SD4-670 And recloser 9182 se4-023 Backfed via Recloser 9507 Materials 1 pole 2x crossarms. NDR 44778 | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-10-02 | c | 0.18131 | 0.0010009 | 2016 | 2015-10-02 | C | 331 | 0.18131 | 0.0010009
7485347 | 2015-10-30 09:16 | 2015-10-30 12:56 | 219.8333 | 8 | 1758.6667 | 219.8333 | 216.8333 | 0.0053178 | 1734.6667 | 0.0052452 | 2.419e-05 | NAPA ID:13200 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse T44 | Replace and install new 11kV O/H conductor. Works location: Kaitawa Rd, Pahiatua. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-30 | b | 0.0026226 | 1.2095e-05 | 2016 | 2015-10-30 | B | 8 | 0.0052452 | 2.419e-05
7485380 | 2015-10-17 14:05 | 2015-10-17 19:54 | 349.2167 | 5 | 1430.0333 | 286.0067 | 283.0067 | 0.0043241 | 1415.0333 | 0.0042787 | 1.5119e-05 | NAPA ID:12819 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-630 | Replace the existing 11kV overhead lines in Clarke Street to underground. Replace pole 203419 and install a new 11kV cable onto the O/H line at the new pole. Both Safelink switch units will be installed and ready for livening. Transfer the existing Transf | F2 | WAIHI RD | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-10-17 | b | 0.0021394 | 7.559e-06 | 2016 | 2015-10-17 | B | 5 | 0.0042787 | 1.5119e-05
7486940 | 2015-10-02 23:32 | 2015-10-03 13:00 | 807.5333 | 421 | 48460.9833 | 115.1092 | 112.1092 | 0.14653 | 47197.9833 | 0.14272 | 0.001273 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 228416 | CB 3 Trip. E/F L/O. Backfed up to Recloser 9556 via RS9679. Fault isolated beyond ABS SF7-011 and rest of feeder restored. Car V Pole. Pole 228416. Also brought lines down at Poles 266881 & 228358. Pole replaced and lines restrung. 1 x 11 metre pole and | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-02 | c | 0.14272 | 0.001273 | 2016 | 2015-10-02 | C | 421 | 0.14272 | 0.001273
7488670 | 2015-10-03 06:43 | 2015-10-03 11:42 | 299.1333 | 355 | 48287.9 | 136.0223 | 133.0223 | 0.14601 | 47222.9 | 0.14279 | 0.0010734 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K12955 | TAH 1 tripped A & B Ph O/C, E/F, L/O. Feeder sectionalised with lines down found at pole K12955. Isolation at ABS 573 ( no back feeds ) Lines x 3 repaired all service restored.Materials 12 x 16 mm sleeves, 20 meters conductor. NDR No 55004. Cause possabl | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-03 | c | 0.14279 | 0.0010734 | 2016 | 2015-10-03 | C | 355 | 0.14279 | 0.0010734
7506096 | 2015-10-03 13:19 | 2015-10-03 18:34 | 315.3833 | 74 | 23338.3667 | 315.3833 | 312.3833 | 0.07057 | 23116.3667 | 0.069898 | 0.00022376 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T6/408 | Gyro hit by vehicle check for safety. 2.38pm woody advised it is a hit transformer - oil leaking out of the transformer - T6/408 - this transformer will probably need to be replaced, Woody has spoken to control about this. Person driving a white vehicle | F3 | PASCAL ST 5 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2015-10-03 | c | 0.069898 | 0.00022376 | 2016 | 2015-10-03 | C | 74 | 0.069898 | 0.00022376
7506554 | 2015-10-03 16:34 | 2015-10-03 18:59 | 144.3 | 1 | 144.3 | 144.3 | 141.3 | 0.00043633 | 141.3 | 0.00042726 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2178 | 2 x 6amp fuses replace HT | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-10-03 | c | 0.00042726 | 3.024e-06 | 2016 | 2015-10-03 | C | 1 | 0.00042726 | 3.0238e-06
7507017 | 2015-10-03 23:50 | 2015-10-04 06:48 | 417.4667 | 715 | 16547.4833 | 23.1433 | 20.1433 | 0.050036 | 14402.4833 | 0.04355 | 0.002162 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D1392 | Found line down at pole D1392. Isolated at fuses FP1313. repaired line & relivened | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-03 | c | 0.04355 | 0.002162 | 2016 | 2015-10-03 | C | 715 | 0.04355 | 0.002162
7508908 | 2015-10-04 04:28 | 2015-10-04 07:58 | 210 | 1458 | 225782.6 | 154.8578 | 151.8578 | 0.68271 | 221408.6 | 0.66949 | 0.0044086 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | na | Waihou 312, TAH3 tripped O/C, E/F, L/O (loss of TAH sub ). Partial backfeeds of TAH2 Sectionaliser 9778 closed, Recloser 9320 open. TAH4 Sectionaliser 9668 closed, Recloser RC27 open. 33kV line patrolled with no obvious fault found but suspect bird strik | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-04 | c | 0.66949 | 0.0044086 | 2016 | 2015-10-04 | C | 1458 | 0.66949 | 0.0044086
7511986 | 2015-10-04 06:24 | 2015-10-04 10:45 | 261.15 | 2 | 522.3 | 261.15 | 258.15 | 0.0015793 | 516.3 | 0.0015612 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1243 | Replace 2 x 15A H/V, O/H fuses FP1243 ( birds ) | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-04 | c | 0.0015612 | 6.048e-06 | 2016 | 2015-10-04 | C | 2 | 0.0015612 | 6.0475e-06
7528491 | 2015-10-04 10:00 | 2015-10-04 11:50 | 110 | 2 | 220 | 110 | 107 | 0.00066523 | 214 | 0.00064708 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5540E | Faultman found blown fuses on transformer 5540E, Faultman reloaded fuses and the blown transformer was isolated and found to be faulty, transformer was replaced. 1 X Transformer. 3 x 6 amp HV fuses. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.00064709 | 6.048e-06 | 2016 | 2015-10-04 | C | 2 | 0.00064708 | 6.0475e-06
7529720 | 2015-10-04 14:28 | 2015-10-04 14:42 | 14 | 1 | 14 | 14 | 11 | 4.2333e-05 | 11 | 3.3261e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K12766 | Repair jumper @ TX TC2632. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-04 | c | 3.3261e-05 | 3.024e-06 | 2016 | 2015-10-04 | C | 1 | 3.3261e-05 | 3.0238e-06
7529725 | 2015-10-04 13:10 | 2015-10-04 16:26 | 196 | 768 | 62128.6333 | 80.8967 | 77.8967 | 0.18786 | 59824.6333 | 0.1809 | 0.0023222 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3999T | CB U20 tripped on GFN E/F flags, line was sectionalised and patrolled,and transformer 3999T was found to be faulty, transformer was isolated and replaced. 1 X transformer | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.1809 | 0.0023222 | 2016 | 2015-10-04 | C | 768 | 0.1809 | 0.0023222
7530909 | 2015-10-04 13:15 | 2015-10-04 14:27 | 72.0167 | 1024 | 73138.2333 | 71.4241 | 68.4241 | 0.22115 | 70066.2333 | 0.21186 | 0.0030963 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB U30 | CB U30 tripped on GFN E/F flags, line was patrolled and sectionalised and no fault was found, faultman reported that there was a burning smell coming from the GFN, GFN was by-passed, Ken Pattie will need to investigate. 5 before CB U30 tripped CB U20 at t | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.21186 | 0.0030963 | 2016 | 2015-10-04 | C | 1024 | 0.21186 | 0.0030963
7535221 | 2015-10-04 18:04 | 2015-10-04 22:16 | 252.3833 | 143 | 15646.9333 | 109.4191 | 106.4191 | 0.047313 | 15217.9333 | 0.046015 | 0.0004324 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845512 | Recloser C613/2 tripped on A phase E/F & O/C flags, | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.046015 | 0.0004324 | 2016 | 2015-10-04 | C | 143 | 0.046015 | 0.0004324
7535828 | 2015-10-04 19:04 | 2015-10-04 20:25 | 81 | 65 | 5265 | 81 | 78 | 0.01592 | 5070 | 0.01533 | 0.00019654 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V8 | 2 X AL Conectors | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.01533 | 0.00019654 | 2016 | 2015-10-04 | C | 65 | 0.01533 | 0.00019654
7536149 | 2015-10-04 21:28 | 2015-10-05 11:36 | 848 | 233 | 39173.3667 | 168.126 | 165.126 | 0.11845 | 38474.3667 | 0.11634 | 0.00070454 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851727 | Andrew Said its to windy to climb poles to fix tonight so off over night 14 Transformers off.0808 ADVISED BY RETAILER, LINES DOWN OUTSIDE 356 SOUTH ROAD ADVISED CONTROL, 10m conductor 2 x sleeves 3 x insulators | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.11634 | 0.00070454 | 2016 | 2015-10-04 | C | 233 | 0.11634 | 0.00070454
7540135 | 2015-10-05 05:16 | 2015-10-05 06:29 | 73.05 | 1 | 73.05 | 73.05 | 70.05 | 0.00022089 | 70.05 | 0.00021181 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 799023 | Top lead up to Line needs fixing Live line crew Please. 6/10 email sent to hub to get jo to sign off. 8/10 email sent to hub to get sign off. 3.25 16/10 Joe called to advise they have completed at link 7315 replaced set of 3x 6amp ddo fuses & cartridge ho | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-10-05 | c | 0.00021181 | 3.024e-06 | 2016 | 2015-10-05 | C | 1 | 0.00021181 | 3.0238e-06
7540142 | 2015-10-03 09:15 | 2015-10-03 10:07 | 52 | 7 | 364 | 52 | 49 | 0.0011006 | 343 | 0.0010371 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7445 | Replace 1x10amp HV fuse at 7445. tree branch over line. F/M going to come back & trim up tree branches still hanging over line | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-10-03 | c | 0.0010371 | 2.1166e-05 | 2016 | 2015-10-03 | C | 7 | 0.0010371 | 2.1166e-05
7540211 | 2015-10-05 08:22 | 2015-10-05 11:31 | 188.9167 | 64 | 4645.4667 | 72.5854 | 69.5854 | 0.014047 | 4453.4667 | 0.013466 | 0.00019352 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C890 | Line patrolled sectionalised nothing found Sect C637 found tripped. High winds in the area at the time. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-10-05 | c | 0.013466 | 0.00019352 | 2016 | 2015-10-05 | C | 64 | 0.013466 | 0.00019352
7540998 | 2015-10-05 08:02 | 2015-10-06 10:23 | 1580.9167 | 178 | 138359.1167 | 777.2984 | 774.2984 | 0.41836 | 137825.1167 | 0.41675 | 0.00053823 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P08206 | Possible feeder fault phoned hub at 0819 I 23 Faulty, Trying to arrange a spare, also trying to arrange for the cable to be tested between V72 & V73 to acertain if it is faulty. Recloser I23 DNO'd . Repairs being carried out to CB 4 ABS V72 at Pongaroa. C | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-10-05 | c | 0.41675 | 0.00053823 | 2016 | 2015-10-05 | C | 178 | 0.41675 | 0.00053823
7541630 | 2015-10-21 09:00 | 2015-10-21 14:12 | 312 | 3 | 936 | 312 | 309 | 0.0028302 | 927 | 0.002803 | 9.0713e-06 | NAPA ID:11634 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212283 | Replace poles hardware and conductor between poles 212283 - 382234. Works location: McLaren Falls Rd. WO 30002530 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-21 | b | 0.0014015 | 4.536e-06 | 2016 | 2015-10-21 | B | 3 | 0.002803 | 9.0713e-06
7541949 | 2015-10-27 08:21 | 2015-10-27 14:45 | 384.25 | 2 | 78.5 | 39.25 | 36.25 | 0.00023737 | 72.5 | 0.00021922 | 6.0475e-06 | NAPA ID:12460 TP_HUIRANGI GXP > INGLEWOOD SUB > BROOKES ST | 6.6 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5488 | Install new poles in work area. replace abs 5509 and 5532 also upgrade 6.6kv cable from abs 5532 to tx 2963T. Works location: Hinau St. WO 30001909 | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-27 | b | 0.00010961 | 3.024e-06 | 2016 | 2015-10-27 | B | 2 | 0.00021922 | 6.0475e-06
7542281 | 2015-10-22 09:15 | 2015-10-22 11:25 | 130 | 2 | 260 | 130 | 127 | 0.00078618 | 254 | 0.00076804 | 6.0475e-06 | NAPA ID:12638 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3254 | Replace DDO's controlling TC3254 under LLP, then Replace single phase Transformer TC3254 under AP. Works location: Boat Harbour Rd, Whitianga. WO 30002490 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-10-22 | b | 0.00038402 | 3.024e-06 | 2016 | 2015-10-22 | B | 2 | 0.00076804 | 6.0475e-06
7542476 | 2015-10-29 09:25 | 2015-10-29 11:15 | 110 | 1 | 110 | 110 | 107 | 0.00033261 | 107 | 0.00032354 | 3.0238e-06 | NAPA ID:12640 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4674 | Replace DDO's controlling TC4674 under LLP, replace single phase Transformer TC4674 under AP. Works location: Port Charles Rd, Coromandel. WO 30002490 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-29 | b | 0.00016177 | 1.512e-06 | 2016 | 2015-10-29 | B | 1 | 0.00032354 | 3.0238e-06
7542560 | 2015-10-05 10:31 | 2015-10-05 13:23 | 171.6667 | 4 | 686.6667 | 171.6667 | 168.6667 | 0.0020763 | 674.6667 | 0.00204 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 839476 | 10.33am - advise smc. Transformer 482 Isolated so that LV work can be carried out safely. Wire spragged mid span needs about 13 metres on new conductor. Materials Used 12m conductor 1 x 60a fuse 2 x sleeves | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-05 | c | 0.00204 | 1.2095e-05 | 2016 | 2015-10-05 | C | 4 | 0.00204 | 1.2095e-05
7542899 | 2015-10-05 11:21 | 2015-10-05 23:10 | 709 | 160 | 44883.75 | 280.5234 | 277.5234 | 0.13572 | 44403.75 | 0.13427 | 0.0004838 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 227036 | FM has spoken to the SMC to organize a bucket truck to cut some trees before the lift the back up PKW3 recloser 9556 tripped L/O ( no flags ). Feeder sectionalised with fault found to be beyond sectionaliser 9833/2. Isolation at sectionaliser links 9833/ | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-05 | c | 0.13427 | 0.0004838 | 2016 | 2015-10-05 | C | 160 | 0.13427 | 0.0004838
7543079 | 2015-11-03 08:30 | 2015-11-03 15:22 | 411.4333 | 72 | 29623.2 | 411.4333 | 408.4333 | 0.089573 | 29407.2 | 0.08892 | 0.00021771 | NAPA ID:13003 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | replacing remander of 11kv poles on kaka amu job bluff rangataumu road all pole numbers xarms etc are mark on plan attached | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.04446 | 0.00010886 | 2016 | 2015-11-03 | B | 72 | 0.08892 | 0.00021771
7543768 | 2015-10-27 09:00 | 2015-10-27 15:21 | 381 | 97 | 36957 | 381 | 378 | 0.11175 | 36666 | 0.11087 | 0.0002933 | NAPA ID:11637 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV poles 212283 | Replace poles hardware and conductor between poles 212283 - 382234. Works location: McLaren Falls Rd. WO 30002530 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-27 | b | 0.055435 | 0.00014665 | 2016 | 2015-10-27 | B | 97 | 0.11087 | 0.0002933
7545316 | 2015-10-05 13:35 | 2015-10-05 14:10 | 35 | 1 | 35 | 35 | 32 | 0.00010583 | 32 | 9.676e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1276 | Repaired 11kV Connector at Transformer 1276. Repaired under Own AP. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-05 | c | 9.676e-05 | 3.024e-06 | 2016 | 2015-10-05 | C | 1 | 9.676e-05 | 3.0238e-06
7550688 | 2015-10-04 22:32 | 2015-10-04 23:51 | 78.5833 | 524 | 41177.6667 | 78.5833 | 75.5833 | 0.12451 | 39605.6667 | 0.11976 | 0.0015845 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 828110 | Circuit Breaker C856 tripped E/F O/C A phase. Line patrolled. Possum located at Pole 828110. | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-10-04 | c | 0.11976 | 0.0015845 | 2016 | 2015-10-04 | C | 524 | 0.11976 | 0.0015845
7552073 | 2015-10-06 04:03 | 2015-10-06 07:08 | 184.6333 | 112 | 17240.9667 | 153.9372 | 150.9372 | 0.052133 | 16904.9667 | 0.051117 | 0.00033866 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7552073 | CB C634 tripped Found broken binder at pole 798204 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-06 | c | 0.051117 | 0.00033866 | 2016 | 2015-10-06 | C | 112 | 0.051117 | 0.00033866
7552618 | 2015-10-06 06:53 | 2015-10-06 09:50 | 177 | 341 | 4078 | 11.9589 | 8.9589 | 0.012331 | 3055 | 0.0092376 | 0.0010311 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 170 SKEET ROAD | need to change tx 2218t at pole 731248 160 and 170 skeet road ar affected due to age Brett leaving site and another crew will come to do the replacement later on tx replaced off 0703 on 0950 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-10-06 | c | 0.0092376 | 0.0010311 | 2016 | 2015-10-06 | C | 341 | 0.0092376 | 0.0010311
7554929 | 2015-10-06 08:51 | 2015-10-06 08:56 | 4.4167 | 282 | 1245.5 | 4.4167 | 1.4167 | 0.0037661 | 399.5 | 0.001208 | 0.0008527 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | tripped when backfeeding no power off | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-10-06 | c | 0.001208 | 0.0008527 | 2016 | 2015-10-06 | C | 282 | 0.001208 | 0.0008527
7556091 | 2015-10-06 10:17 | 2015-10-06 12:22 | 124.7167 | 1 | 124.7167 | 124.7167 | 121.7167 | 0.00037711 | 121.7167 | 0.00036804 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844594 | 0273552572 No power at water pump, please call Neville for access if needed. Please attend ASAP as drinking water pump for the village 10.21am advised Shannon at svs hub. Repaired broken HV jumper using 1x pg Clamp | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-10-06 | c | 0.00036804 | 3.024e-06 | 2016 | 2015-10-06 | C | 1 | 0.00036804 | 3.0238e-06
7556614 | 2015-10-31 09:09 | 2015-10-31 18:03 | 533.85 | 1 | 533.85 | 533.85 | 530.85 | 0.0016142 | 530.85 | 0.0016052 | 3.0238e-06 | NAPA ID:13506 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links SE5-174 | Replace poles, crossarms and conductors. Connect new 11kV line to existing 11kV at pole site 226106 and liven through to TEMP62 on pole 344726. Works location: Te Puek Quarry Rd. WO 30003844. 2 r issued to have generator installed at Papamoa radio repeate | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-31 | b | 0.00080258 | 1.512e-06 | 2016 | 2015-10-31 | B | 1 | 0.0016052 | 3.0238e-06
7573351 | 2015-10-21 09:45 | 2015-10-21 14:12 | 267.1167 | 412 | 7563.75 | 18.3586 | 15.3586 | 0.022871 | 6327.75 | 0.019134 | 0.0012458 | NAPA ID:13517 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 336 | To Replace Links 336 [DNO 150916 ]. Works location: Roto St, New Plymouth. WO 30015185 | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-10-21 | b | 0.0095668 | 0.0006229 | 2016 | 2015-10-21 | B | 412 | 0.019134 | 0.0012458
7574612 | 2015-10-06 19:50 | 2015-10-06 20:03 | 13 | 33 | 429 | 13 | 10 | 0.0012972 | 330 | 0.00099784 | 9.9784e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 5231E | Transformer 5231E has been hit by unknown vehicle and wires exposed. 6.55pm advised Dianne at svs hub. Bevon advised - tx has been clipped and pushed off slab. will need to isolate tx and make repairs - will work through control when having to isolate thi | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-10-06 | c | 0.00099784 | 9.9784e-05 | 2016 | 2015-10-06 | C | 33 | 0.00099784 | 9.9784e-05
7575723 | 2015-10-13 10:15 | 2015-10-13 15:10 | 295.3167 | 67 | 19786.2167 | 295.3167 | 292.3167 | 0.059829 | 19585.2167 | 0.059221 | 0.00020259 | NAPA ID:11771 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | na | Poles, crossarms & associated equipment replacement program including general Maintenance; under the title ?IR7453 Cambridge Rd Pole Renewal? | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-10-13 | b | 0.029611 | 0.0001013 | 2016 | 2015-10-13 | B | 67 | 0.059221 | 0.00020259
7577086 | 2015-10-28 08:46 | 2015-10-28 15:01 | 375.35 | 68 | 25523.8 | 375.35 | 372.35 | 0.077178 | 25319.8 | 0.076561 | 0.00020562 | NAPA ID:13069 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-279 | REPLACE POLES & HV ARM'S, CLEAR TREES AWAY FROM HV LINES, RECONDUCTOR HV NETWORK ALONG NO4 ROAD, INSTALL NEW ABS IP629 AT POLE 223288. Works location: No 4 Rd, Te Puke. WO 30002430 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-28 | b | 0.038281 | 0.00010281 | 2016 | 2015-10-28 | B | 68 | 0.076561 | 0.00020562
7577137 | 2015-10-07 11:46 | 2015-10-07 15:20 | 214 | 35 | 7490 | 214 | 211 | 0.022648 | 7385 | 0.02233 | 0.00010583 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G105T | Gyro box is smoking and melting. No power to all bussiness in the area. 11.03am advised hub of 999. Replaced tx (Refurbished 300kVA tx) restored power tested and all ok. 1x 25amp hv fuse & 1x 400amp j type fuse. Replaced termination joint in ground outsid | F2 | MAIN ST 15 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-10-07 | c | 0.02233 | 0.00010583 | 2016 | 2015-10-07 | C | 35 | 0.02233 | 0.00010583
7577213 | 2015-10-28 09:00 | 2015-10-28 15:54 | 414 | 111 | 41965.6833 | 378.0692 | 375.0692 | 0.12689 | 41632.6833 | 0.12589 | 0.00033564 | NAPA ID:12654 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11k VABS 2702 | Replace pole V13386 and install new Tx TP2847,liven + commission. Upgrade TC4763 to a 30-11-1 and replace all H/ware. Create L.V open point at pole V13388. Works location: Tuateawa Rd, Coromandel. WO 30011685 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-28 | b | 0.062944 | 0.00016782 | 2016 | 2015-10-28 | B | 111 | 0.12589 | 0.00033564
7577300 | 2015-10-07 09:03 | 2015-10-07 11:47 | 163.8 | 6 | 272.3833 | 45.3972 | 42.3972 | 0.00082362 | 254.3833 | 0.00076919 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9612/2 | Mike Strange Fault man. Replace 1 x 20 A Fuse at Fuse Switch 9612/2. | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-07 | c | 0.00076919 | 1.8143e-05 | 2016 | 2015-10-07 | C | 6 | 0.00076919 | 1.8143e-05
7577541 | 2015-11-06 10:13 | 2015-11-06 14:13 | 240 | 40 | 9581 | 239.525 | 236.525 | 0.028971 | 9461 | 0.028608 | 0.00012095 | NAPA ID:12532 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5738 | Install new Fluorine 33Kv conductor over 11Kv road crossing conductors. Works location: Ahuroa Rd, Toko. WO 30010304 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-06 | b | 0.014304 | 6.0475e-05 | 2016 | 2015-11-06 | B | 40 | 0.028608 | 0.00012095
7577618 | 2015-10-09 10:06 | 2015-10-09 13:07 | 181.6667 | 264 | 8669.0667 | 32.8374 | 29.8374 | 0.026213 | 7877.0667 | 0.023818 | 0.00079827 | NAPA ID:13587 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B0803 | To replace faulty 11kV joints between undergroung cable and overhead 11kV at pole B0803. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-09 | b | 0.011909 | 0.00039914 | 2016 | 2015-10-09 | B | 264 | 0.023818 | 0.00079827
7577621 | 2015-10-07 13:09 | 2015-10-07 14:40 | 91.0333 | 24 | 2184.8 | 91.0333 | 88.0333 | 0.0066063 | 2112.8 | 0.0063886 | 7.257e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 9359/2 | Isolation of Transformer TC3174 for repair/replacement of LV fuse rack. Fuse rack had burnt up connection to it. no Back feeds available. Materials:- 1x andelect fuse base, 1x 200amp andelect fuse | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-10-07 | c | 0.0063886 | 7.257e-05 | 2016 | 2015-10-07 | C | 24 | 0.0063886 | 7.257e-05
7578700 | 2015-10-07 17:25 | 2015-10-07 19:38 | 132.55 | 1 | 132.55 | 132.55 | 129.55 | 0.0004008 | 129.55 | 0.00039173 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/209 | 2R blown tx 28/204. Initially found 2 Ht fuses found blown at S40. Fault traced to defective transformer T8/209. Transformer replaced and relivened OK with isolation at Fuses S40. Full set DDOs also replaced at 6A Rating. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-07 | c | 0.00039173 | 3.024e-06 | 2016 | 2015-10-07 | C | 1 | 0.00039173 | 3.0238e-06
7578707 | 2015-10-07 15:44 | 2015-10-07 17:39 | 115.0167 | 1325 | 141773.6833 | 106.999 | 103.999 | 0.42869 | 137798.6833 | 0.41667 | 0.0040065 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737611 | Stratford TP CB 2862 , OCB 2862 E/F Trip. (Loss of Supply to Kaponga and Cardiff Subs). Feeder sectionalised with cardiff Supplied via ABS S360 and Kaponga restored. (Fault found on 33kV Section between ABS 366 abd 365 with a broken insulator). Insulator | F1,F2,F3 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2015-10-07 | c | 0.41667 | 0.0040065 | 2016 | 2015-10-07 | C | 1325 | 0.41667 | 0.0040065
7580466 | 2015-10-07 16:10 | 2015-10-07 16:42 | 32.5167 | 869 | 19002.0333 | 21.8666 | 18.8666 | 0.057458 | 16395.0333 | 0.049575 | 0.0026276 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 789335 | CB 4 Trip, O/C. Blown HV Cable Termination at Pole 789335. Cable isolated and backfeed installed via ABS 523. DNO 151004 created to repair cable. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-10-07 | c | 0.049575 | 0.0026276 | 2016 | 2015-10-07 | C | 869 | 0.049575 | 0.0026276
7586429 | 2015-10-07 22:31 | 2015-10-08 00:20 | 109.4833 | 21 | 2158.9333 | 102.8063 | 99.8063 | 0.0065281 | 2095.9333 | 0.0063376 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 358640 | Reports of no power found 2 HV fuses tripped at V16. Further patrol found badly damaged pole (Top burnt off) on Range Rd. Isolation made between ABS V19 and V16 to make 2 temp line breaks (Poles P358640 and P06802). All customers were then relivened OK - | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-07 | c | 0.0063376 | 6.3499e-05 | 2016 | 2015-10-07 | C | 21 | 0.0063376 | 6.3499e-05
7586478 | 2015-10-07 18:42 | 2015-10-07 21:44 | 181.6667 | 90 | 16350 | 181.6667 | 178.6667 | 0.049438 | 16080 | 0.048622 | 0.00027214 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 781753 | Initial auto-reclose on CB 693 on O/C A Phase and E/F. Reports of part power found an 11kV conductor on the ground not far from the recloser. Isolation from CB 693 required to repair the conductor with 4 extra metres and 2 jointers required. Fault caused | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-10-07 | c | 0.048622 | 0.00027214 | 2016 | 2015-10-07 | C | 90 | 0.048622 | 0.00027214
7586706 | 2015-10-07 20:25 | 2015-10-07 20:55 | 30.4667 | 517 | 15751.2667 | 30.4667 | 27.4667 | 0.047628 | 14200.2667 | 0.042938 | 0.0015633 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-042 | Emergency isolation to replace a burnt up HV fuse Holder at Fuses SD5-042. Isolation between ABS SD5-024, ABS IP158 and Fuse/Sw 9022/4. Backfeed via RS 9697. 1 x HV DDO Base Replaced. | F2 | GRAVATT RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-10-07 | c | 0.042938 | 0.0015633 | 2016 | 2015-10-07 | C | 517 | 0.042938 | 0.0015633
7599292 | 2015-10-07 21:42 | 2015-10-07 23:18 | 96 | 20 | 1920 | 96 | 93 | 0.0058056 | 1860 | 0.0056242 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815095 | Fault caused by blown jumper at pole 815095. Isolation required from Fuses 7205 to repair. Relivened OK. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-10-07 | c | 0.0056242 | 6.0475e-05 | 2016 | 2015-10-07 | C | 20 | 0.0056242 | 6.0475e-05
7637588 | 2015-10-08 03:11 | 2015-10-08 12:54 | 583.7167 | 54 | 31520.7 | 583.7167 | 580.7167 | 0.095311 | 31358.7 | 0.094821 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805867, 806950, 806949 | Alan Cox and Gary Fisher went home at 7.30am. Paul Osborne Pa Koru and Paul Webster have been onsite all morning. This is a 2r and an NDR. Replaced 2 x Pin crossarms and 1 x Fuse crossarm and 50m 25mm Copper conductor. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.094821 | 0.00016328 | 2016 | 2015-10-08 | C | 54 | 0.094821 | 0.00016328
7642523 | 2015-10-08 05:28 | 2015-10-08 09:48 | 259.7167 | 494 | 48737.5833 | 98.6591 | 95.6591 | 0.14737 | 47255.5833 | 0.14289 | 0.0014937 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704169 | Tony Julian abd Paul Sullivan Attended. Replaced burnt crossarm due to old age. Used 1 x Crossarm 3 x HV Pins and Insulators 2 x 16mm sleeves 3 x 10A Fuses 1 x DDO Sleeve | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.14289 | 0.0014937 | 2016 | 2015-10-08 | C | 494 | 0.14289 | 0.0014937
7643464 | 2015-10-08 10:34 | 2015-10-08 13:18 | 164 | 1 | 164 | 164 | 161 | 0.0004959 | 161 | 0.00048683 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P590035 | Pole P590035 needs to be replaced due to damage by high load. The load was roller on the back of a truck. Les is unsure why is caught the line as it looked under 5 meter and it did not catch any other lines. Advised hub and control. High load will wait | F1 | DAIRYFACT | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.00048682 | 3.024e-06 | 2016 | 2015-10-08 | C | 1 | 0.00048683 | 3.0238e-06
7643574 | 2015-10-08 07:30 | 2015-10-08 08:45 | 74.7333 | 440 | 32253.35 | 73.3031 | 70.3031 | 0.097526 | 30933.35 | 0.093535 | 0.0013305 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835490 | Line fault indicators beyond ABS S68 checked and line sectionalised to restore supply . Further patrol carried out and found floating conductor at pole 835490 and repaired 'Live Line' . | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.093535 | 0.0013305 | 2016 | 2015-10-08 | C | 440 | 0.093535 | 0.0013305
7648205 | 2015-10-08 08:34 | 2015-10-08 10:20 | 105.7333 | 4 | 422.9333 | 105.7333 | 102.7333 | 0.0012788 | 410.9333 | 0.0012426 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 827018 | replaced cossarm NDR No7937980 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.0012426 | 1.2095e-05 | 2016 | 2015-10-08 | C | 4 | 0.0012426 | 1.2095e-05
7648720 | 2015-10-08 10:03 | 2015-10-08 13:35 | 211.55 | 118 | 3449.8 | 29.2356 | 26.2356 | 0.010431 | 3095.8 | 0.009361 | 0.0003568 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FC2720 | SS 9941 Trip, E/F, O/C A-B-C Phase. Faultman found tree down through lines between Poles M2441 & M2442. Repaired using 6x squirrel full tension sleeves. NDR 38531. 7648720 = Momentary Loss of Supply followed by outage reflected under OMS 7648859. | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-08 | c | 0.009361 | 0.0003568 | 2016 | 2015-10-08 | C | 118 | 0.009361 | 0.0003568
7649514 | 2015-10-08 11:18 | 2015-10-08 19:02 | 464 | 795 | 87506.6833 | 110.0713 | 107.0713 | 0.2646 | 85121.6833 | 0.25739 | 0.0024039 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FC2720 | Customer heard 2 loud bangs from across the road, and can smell burning from transformer or pillar boxes across the road - Wanda 07 8866421 or 022 5141 917 - advised Peter. Fuse/Sw FC2720 has burnt up bushings Bushings cleaned up and restored to service. | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-10-08 | c | 0.25739 | 0.0024039 | 2016 | 2015-10-08 | C | 795 | 0.25739 | 0.0024039
7650560 | 2015-10-27 10:49 | 2015-10-27 14:10 | 200.8833 | 22 | 4419.4333 | 200.8833 | 197.8833 | 0.013363 | 4353.4333 | 0.013164 | 6.6523e-05 | NAPA ID:12860 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 12080/1 | Replace DNO 150507 Abs WH252 & install xarms. Works location: Meremere Rd, Hawera. WO 30010046 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-27 | b | 0.0065819 | 3.3261e-05 | 2016 | 2015-10-27 | B | 22 | 0.013164 | 6.6523e-05
7650809 | 2015-10-08 15:02 | 2015-10-08 16:01 | 59 | 36 | 2124 | 59 | 56 | 0.0064225 | 2016 | 0.0060959 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | N1874 | Check branch on line at pole N1874. Large branch found cross all 3 phases. 2 r requested to have removed. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-10-08 | c | 0.0060959 | 0.00010886 | 2016 | 2015-10-08 | C | 36 | 0.0060959 | 0.00010886
7654213 | 2015-10-08 14:39 | 2015-10-08 20:26 | 347.3833 | 816 | 61892.7333 | 75.8489 | 72.8489 | 0.18715 | 59444.7333 | 0.17975 | 0.0024674 |  | 11 | Unplanned | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | S6169 | CB 6 tripped to L/O. No flags. Report of Northpower staff striking 11kV cable in Palm Springs subdivision. Downer faultman advised. Dave Evans advised NOC agreement has been made between Northpower & Downer for Northpower to carry out cable repairs. Furt | F3 | SIMPSON RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-10-08 | c | 0.17975 | 0.0024674 | 2016 | 2015-10-08 | C | 816 | 0.17975 | 0.0024674
7656704 | 2015-10-09 10:50 | 2015-10-09 12:30 | 100 | 27 | 2700 | 100 | 97 | 0.0081642 | 2619 | 0.0079192 | 8.1642e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708297 | Report of loose 11kV crossarm on pole #708297, will require a new 11kV pin arm to fix. Reported by Jerry Almano, Powerco SD 6322. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-10-09 | c | 0.0079192 | 8.1642e-05 | 2016 | 2015-10-09 | C | 27 | 0.0079192 | 8.1642e-05
7657385 | 2015-10-08 23:51 | 2015-10-09 05:35 | 343.8833 | 52 | 17881.9333 | 343.8833 | 340.8833 | 0.054071 | 17725.9333 | 0.053599 | 0.00015724 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 843612 | Truck / Pole on SH3 Kaitoki, Wanganui. Isolation required from Fuses 075. Required pole change with all associated hardware with 3 broken conductors also rejointed / rehung. Livened OK. NDR 22679 | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-10-08 | c | 0.053599 | 0.00015724 | 2016 | 2015-10-08 | C | 52 | 0.053599 | 0.00015724
7659861 | 2015-10-09 09:19 | 2015-10-09 09:39 | 19.6667 | 1716 | 26697.6667 | 15.5581 | 12.5581 | 0.080727 | 21549.6667 | 0.065161 | 0.0051888 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 3162 Trip causing loss of supply to Walton Sub & CB 1 & 3 at Waharoa Sub. Backfeed installed via CB 3246. 33kv line was patrolled with no fault found. Line sectionalised and relivened ok. Suspect bird strike | F1,F2,F3 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 2015-10-09 | c | 0.065161 | 0.0051888 | 2016 | 2015-10-09 | C | 1716 | 0.065161 | 0.0051888
7661634 | 2015-10-30 09:03 | 2015-10-30 13:34 | 271.1167 | 5 | 1355.5833 | 271.1167 | 268.1167 | 0.004099 | 1340.5833 | 0.0040536 | 1.5119e-05 | NAPA ID:12804 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2368 | Replace single phase Transformer TC4192 and repair other Defects at various sites. Works location: Waikanae Valley Rd, Coromandel. WO 30002490 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-30 | b | 0.0020268 | 7.559e-06 | 2016 | 2015-10-30 | B | 5 | 0.0040536 | 1.5119e-05
7662560 | 2015-10-22 10:24 | 2015-10-22 14:40 | 256.5 | 15 | 3847.5 | 256.5 | 253.5 | 0.011634 | 3802.5 | 0.011498 | 4.5356e-05 | NAPA ID:13670 TP_STRATFORD GXP > KAPONGA SUB | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 444 | Kaponga sub Isolate Both 33Kv circuits Replace DNO 33kv Abs's 444 & 446 - Manaia Rd remove DNO U/g cable replace with 1 span of O/h Iodine conductor | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-10-22 | b | 0.0057489 | 2.2678e-05 | 2016 | 2015-10-22 | B | 15 | 0.011498 | 4.5356e-05
7663226 | 2015-10-31 08:03 | 2015-10-31 16:17 | 494.0833 | 1 | 494.0833 | 494.0833 | 491.0833 | 0.001494 | 491.0833 | 0.0014849 | 3.0238e-06 | NAPA ID:10085 TP_TE MATAI GXP > TE PUKE SUB > MOEHAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-186 | 1. Replace 11kv Switchgear SE5-184 /189 /190 /191 (Long & Crawford) with CFCF Safelink2 9971-1-2-3-4, joint and terminate existing cables 2.Replace 11kv Switchgear SE5-259/261/263 (Series1) with CFC Safelink2 9972-1-2-3 re-connect existing cables. Works l | F3 | MOEHAU ST | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-10-31 | b | 0.00074246 | 1.512e-06 | 2016 | 2015-10-31 | B | 1 | 0.0014849 | 3.0238e-06
7663313 | 2015-10-13 10:00 | 2015-10-13 10:40 | 40 | 1 | 40 | 40 | 37 | 0.00012095 | 37 | 0.00011188 | 3.0238e-06 | NAPA ID:13651 TP_GREYTOWN GXP > MARTINBOROUGH SUB > COLOGNE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | tc962 | Fit LV fusing. Need access to LV bushing and leads. Electrician has safety concerns about main switch in building. Own isolation & AP . | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-10-13 | b | 5.594e-05 | 1.512e-06 | 2016 | 2015-10-13 | B | 1 | 0.00011188 | 3.0238e-06
7664649 | 2015-10-10 03:56 | 2015-10-10 12:03 | 487.4167 | 3 | 1461.8333 | 487.2778 | 484.2778 | 0.0044202 | 1452.8333 | 0.004393 | 9.0713e-06 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p23612 | CB 10060 Trip. E/F. O/C. Zone 3 Trip. Line down at Pole P23612. Affects Tararua wind farm. | F1,F2,F3 | BUNNYTHORPE-KELVIN GV 33KV | BUNNYTHORPE | Manawatu | TP_BUNNYTHORPE | Western Electricity | POWERCO | 2015-10-10 | c | 0.004393 | 9.071e-06 | 2016 | 2015-10-10 | C | 3 | 0.004393 | 9.0713e-06
7664974 | 2015-10-10 10:00 | 2015-10-10 12:28 | 148 | 2 | 296 | 148 | 145 | 0.00089503 | 290 | 0.00087689 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 854575 | 50 kva tx t3250. pole 854575. Tx is going to be changed. House and cowshed affected. Advise customer who currently running off a generator. Replaced transformer Off at 10:00 On at 12:28. No paperwork. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-10 | c | 0.00087689 | 6.048e-06 | 2016 | 2015-10-10 | C | 2 | 0.00087689 | 6.0475e-06
7665283 | 2015-10-10 14:30 | 2015-10-10 16:30 | 120 | 1 | 120 | 120 | 117 | 0.00036285 | 117 | 0.00035378 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Te Puke Quary Road | Tree dropped on 33kV line. Matthew Cook advise line down at 482 Te Puke Quarry Road, in the vicinity of the Looking Glass Garden. CB 2182 @ Kaitimako sub & CB 62 @ Welcome Bay sub tripped to L/O. O/C flags. Tree dopped through line. Atuaroa sub off loade | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-10 | c | 0.00035378 | 3.024e-06 | 2016 | 2015-10-10 | C | 1 | 0.00035378 | 3.0238e-06
7665440 | 2015-10-10 11:54 | 2015-10-10 15:17 | 202.7167 | 66 | 13379.3 | 202.7167 | 199.7167 | 0.040456 | 13181.3 | 0.039857 | 0.00019957 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 632215 | Replace pole 632215 hit by car. Used 1 X Pole complete for transformer 50 kVA transformer. NDR Number 43431 | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-10-10 | c | 0.039857 | 0.00019957 | 2016 | 2015-10-10 | C | 66 | 0.039857 | 0.00019957
7665580 | 2015-10-10 12:48 | 2015-10-10 14:12 | 83.9167 | 1 | 83.9167 | 83.9167 | 80.9167 | 0.00025374 | 80.9167 | 0.00024467 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 062 | 2 X 2Amp Fuses | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-10-10 | c | 0.00024467 | 3.024e-06 | 2016 | 2015-10-10 | C | 1 | 0.00024467 | 3.0238e-06
7666312 | 2015-10-10 22:36 | 2015-10-11 01:11 | 154.1667 | 6 | 160.5 | 26.75 | 23.75 | 0.00048531 | 142.5 | 0.00043089 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD3-119 | 2 x HV fuses replaced. 2 x 3 amp HV fuses replaced | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-10-10 | c | 0.00043089 | 1.8143e-05 | 2016 | 2015-10-10 | C | 6 | 0.00043089 | 1.8143e-05
7666464 | 2015-10-11 06:47 | 2015-10-11 07:35 | 47.6833 | 1 | 47.6833 | 47.6833 | 44.6833 | 0.00014418 | 44.6833 | 0.00013511 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2984 | 2 X 10 Amp Fuses Birds | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-10-11 | c | 0.00013511 | 3.024e-06 | 2016 | 2015-10-11 | C | 1 | 0.00013511 | 3.0238e-06
7666517 | 2015-10-11 06:47 | 2015-10-11 07:35 | 47.6833 | 1 | 47.6833 | 47.6833 | 44.6833 | 0.00014418 | 44.6833 | 0.00013511 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2984 | Was Part of Job 7666464 Came in after i closed job off | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-10-11 | c | 0.00013511 | 3.024e-06 | 2016 | 2015-10-11 | C | 1 | 0.00013511 | 3.0238e-06
7666608 | 2015-10-11 08:27 | 2015-10-11 09:45 | 77.95 | 7 | 545.65 | 77.95 | 74.95 | 0.0016499 | 524.65 | 0.0015864 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH267 | 2 X 10 Amp Birds | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-11 | c | 0.0015864 | 2.1166e-05 | 2016 | 2015-10-11 | C | 7 | 0.0015864 | 2.1166e-05
7667177 | 2015-10-11 14:13 | 2015-10-11 17:15 | 182.2667 | 43 | 2818.9667 | 65.5574 | 62.5574 | 0.0085239 | 2689.9667 | 0.0081338 | 0.00013002 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S12713 | MAT 3 Em switching to replace burnt fuse holders at Transformer TC2409. Isolations between normal open point ABS IC461 & ABS IC395 ( no back feeds ). Fuse holders replaced all service restored. Materials 3 x H/V fuses holders, 3 x 3A Fuse Links. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-10-11 | c | 0.0081338 | 0.00013002 | 2016 | 2015-10-11 | C | 43 | 0.0081338 | 0.00013002
7667186 | 2015-10-11 14:16 | 2015-10-11 18:28 | 252.3 | 250 | 20085.3 | 80.3412 | 77.3412 | 0.060733 | 19335.3 | 0.058465 | 0.00075594 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720426 | Kapuni CB KA7 tripped on O/C and E/F. Replaced 1xHv Crossarm , 10m 35mm , 10m 25mm , 4m 16mm , 16 sleeves and 1x Lv Fuse box | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-10-11 | c | 0.058465 | 0.00075594 | 2016 | 2015-10-11 | C | 250 | 0.058465 | 0.00075594
7668399 | 2015-10-12 01:56 | 2015-10-12 07:11 | 314.5333 | 329 | 77878.2667 | 236.7121 | 233.7121 | 0.23549 | 76891.2667 | 0.2325 | 0.00099482 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 214444 | Car verses pole lines down. Isolated between 9258/3, SC4-045, SC4-776, 9978/1, 9978/6 & 9289/3. Replaced pole 214444. NDR 048444. Pole replaced all service restored. Materials 1 x pole, 4 x H/V arms, 3 x H/V insulators, 6 x polymers, 2 x L/V arms, 3 x H/V | F3 | TUI ST | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-10-12 | c | 0.2325 | 0.00099482 | 2016 | 2015-10-12 | C | 329 | 0.2325 | 0.00099482
7669420 | 2015-10-12 09:20 | 2015-10-12 10:01 | 40.5833 | 17 | 689.9167 | 40.5833 | 37.5833 | 0.0020861 | 638.9167 | 0.0019319 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | ABS IC1044 | Emergency switching to repair burnt jumper at ABS IC1044. Possible bird strike. Isolation at ABS IC1044 (no back feed). All repairs completed all service restored. Materials 1 x H/V lug | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-10-12 | c | 0.0019319 | 5.1404e-05 | 2016 | 2015-10-12 | C | 17 | 0.0019319 | 5.1404e-05
7673529 | 2015-10-12 15:29 | 2015-10-12 18:30 | 181.0667 | 306 | 45703.7833 | 149.3588 | 146.3588 | 0.1382 | 44785.7833 | 0.13542 | 0.00092527 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C627 | Tripped Ph A OC, EF Trip. Feeder patrolled and sectionaliser CB2924 also found tripped. All restored OK. Cause of original fault unknown | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-10-12 | c | 0.13542 | 0.00092527 | 2016 | 2015-10-12 | C | 306 | 0.13542 | 0.00092527
7674467 | 2015-10-12 16:54 | 2015-10-12 19:36 | 162.2667 | 776 | 22031.6833 | 28.3913 | 25.3913 | 0.066619 | 19703.6833 | 0.059579 | 0.0023464 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K1515 | Line Down between Pole K1515 & K13342. ABS IC484 Open no back feeds available. Line Repaired. 3 x 6amp fuses. 1.5m wire. 6 sleeves | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-10-12 | c | 0.059579 | 0.0023464 | 2016 | 2015-10-12 | C | 776 | 0.059579 | 0.0023464
7677350 | 2015-10-12 18:06 | 2015-10-12 22:45 | 278.25 | 177 | 32129.2 | 181.5209 | 178.5209 | 0.097151 | 31598.2 | 0.095545 | 0.00053521 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844712 | RS 4659/2 A/R, L/O, E/F, O/C B Phase. Sectionalised & Patrolled with two different faults found & repaired. 1./ Pole 809612. Line down. Materials used: 14mtrs squirrel conductor & 2 sleeves 2./ Pole 844712. Floating conductor. Materials used: 1mtr 16mm ba | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-10-12 | c | 0.095545 | 0.00053521 | 2016 | 2015-10-12 | C | 177 | 0.095545 | 0.00053521
7678235 | 2015-10-12 22:28 | 2015-10-13 01:05 | 156.7 | 37 | 5797.9 | 156.7 | 153.7 | 0.017531 | 5686.9 | 0.017196 | 0.00011188 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - EARTHQUAKE | T2/536 | Broken HV Fuse holder due to earthquake. Isolated for repair at ABS D45. Replaced fuse holder complete with 6 Amp Link | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-10-12 | c | 0.017196 | 0.00011188 | 2016 | 2015-10-12 | C | 37 | 0.017196 | 0.00011188
7682268 | 2015-10-13 10:17 | 2015-10-13 11:56 | 98.8333 | 419 | 24850.25 | 59.3085 | 56.3085 | 0.075141 | 23593.25 | 0.07134 | 0.001267 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB Q61 | Tripping on Recloser Q61 on Phase B O/C, E/F. Extended outage as this recloser was backfeeding through ABS Q77 to Recloser T21 (Coonoor Feeder) for a planned outage. Feeders patrolled / sectionalised but nothing found. Restored OK. | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-13 | c | 0.07134 | 0.001267 | 2016 | 2015-10-13 | C | 419 | 0.07134 | 0.001267
7683812 | 2015-10-14 09:15 | 2015-10-14 14:15 | 299.5167 | 119 | 35642.4833 | 299.5167 | 296.5167 | 0.10777 | 35285.4833 | 0.10669 | 0.00035983 | NAPA ID:13834 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12061 | Relocate fused ABS pole 12061 towards transformer 1374. Work Location: McLean Street. Work Order 30002062 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-10-14 | b | 0.053347 | 0.00017991 | 2016 | 2015-10-14 | B | 119 | 0.10669 | 0.00035983
7683865 | 2015-10-13 12:59 | 2015-10-13 14:53 | 113.4167 | 15 | 1701.25 | 113.4167 | 110.4167 | 0.0051442 | 1656.25 | 0.0050081 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2066 | Requesting a 2r broken 11kV Fuses, will need to isolate and change cross arm also. Will go through to control now to discuss. Isolation required from Fuses 708 to repair hardware at Transformer X2066. 1 broken HV Fuse crossarm replaced, a full set of fuse | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-10-13 | c | 0.0050081 | 4.5356e-05 | 2016 | 2015-10-13 | C | 15 | 0.0050081 | 4.5356e-05
7684747 | 2015-10-13 13:33 | 2015-10-13 18:25 | 291.6667 | 314 | 32702 | 104.1465 | 101.1465 | 0.098883 | 31760 | 0.096035 | 0.00094946 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714855 | CB TA8 A/R to Trip. Def E/F Line Sectionalized & Patrolled. insulator at pole 714855 blown. Isolation at ABS's 6751, TA876, TA837 & TA824. Back feed from TAS CB TA9 via ABS TA971. Materials used: 1x 11kV pin & insulator. 2mtrs of ali binder. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-13 | c | 0.096035 | 0.00094946 | 2016 | 2015-10-13 | C | 314 | 0.096035 | 0.00094946
7685495 | 2015-11-02 10:25 | 2015-11-02 14:08 | 223 | 40 | 8920 | 223 | 220 | 0.026972 | 8800 | 0.026609 | 0.00012095 | NAPA ID:12523 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5738 | Replace 33Kv poles with 11Kv crossings. Works location: Ahuroa & Wawiri Rds, Toko. WO 30010304 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.013305 | 6.0475e-05 | 2016 | 2015-11-02 | B | 40 | 0.026609 | 0.00012095
7685500 | 2015-11-02 10:12 | 2015-11-02 12:53 | 161.6333 | 8 | 1293.0667 | 161.6333 | 158.6333 | 0.0039099 | 1269.0667 | 0.0038374 | 2.419e-05 | NAPA ID:13114 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS E3 | Replace 11KV Trani fuses T2/195. Works location: Nannestads Lane, Palmerston North. WO 10161138 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.0019187 | 1.2095e-05 | 2016 | 2015-11-02 | B | 8 | 0.0038374 | 2.419e-05
7685626 | 2015-11-02 08:16 | 2015-11-02 14:36 | 379.75 | 4 | 1519 | 379.75 | 376.75 | 0.0045931 | 1507 | 0.0045568 | 1.2095e-05 | NAPA ID:13510 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 7771 | Tree work near 11kV lines. Works location: Tanglewood Rd. WO 10152356 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.0022784 | 6.048e-06 | 2016 | 2015-11-02 | B | 4 | 0.0045568 | 1.2095e-05
7685849 | 2015-11-02 09:43 | 2015-11-02 15:33 | 350.2167 | 28 | 9806.0667 | 350.2167 | 347.2167 | 0.029651 | 9722.0667 | 0.029397 | 8.4665e-05 | NAPA ID:13566 TP_WANGANUI GXP > HATRICKS WHARF SUB > MARANGAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2660 | Remove pole 767487 to a safe position away from the edge of slippage, move to the other side of the road. Works location: Shakespeare Rd, Wanganui. WO 30013284 | F3 | MARANGAI | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.014699 | 4.2333e-05 | 2016 | 2015-11-02 | B | 28 | 0.029397 | 8.4665e-05
7685921 | 2015-10-13 15:45 | 2015-10-13 19:00 | 194.9333 | 163 | 31774.1333 | 194.9333 | 191.9333 | 0.096077 | 31285.1333 | 0.094599 | 0.00049287 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708448 | Isolation at recloser 4897 due to cows dying from wire down. F/M Dispatched to carry out repairs.Transformer 3192T Isolated to allow for LV Conductor repairs. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-10-13 | c | 0.094599 | 0.00049287 | 2016 | 2015-10-13 | C | 163 | 0.094599 | 0.00049287
7686308 | 2015-10-13 13:39 | 2015-10-13 16:06 | 147.0667 | 93 | 13677.2 | 147.0667 | 144.0667 | 0.041357 | 13398.2 | 0.040513 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | line patrol done onsite and no fault found, has been live for 45mins, advised to let control know also. Area patrolled and CB N21 found tripped. (Presently no control or indication to NOC due to control box fault). Reclosed OK. Cause unknown. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-10-13 | c | 0.040513 | 0.00028121 | 2016 | 2015-10-13 | C | 93 | 0.040513 | 0.00028121
7686530 | 2015-10-13 16:07 | 2015-10-13 21:00 | 293.0667 | 22 | 6447.4667 | 293.0667 | 290.0667 | 0.019496 | 6381.4667 | 0.019296 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P46448 | HV fuses blown due to trees on lines. Work area isolated at Fuses T39 & Treescape called to cut trees. Floating conductor also fixed at Pole P46882 by replacing nut on insulator. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-13 | c | 0.019296 | 6.6523e-05 | 2016 | 2015-10-13 | C | 22 | 0.019296 | 6.6523e-05
7687000 | 2015-10-13 21:55 | 2015-10-13 22:58 | 63.1167 | 10 | 631.1667 | 63.1167 | 60.1167 | 0.0019085 | 601.1667 | 0.0018178 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L12492 | FRM 6 Faulty H/V fuseholders at transformer TC4916. Isolation at fuses FC2278 ( no back feeds ) H/V fuse holders replaced all service restored. Materials 2 x H/V fuse holders, 2 x 2A fuses | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-13 | c | 0.0018178 | 3.0238e-05 | 2016 | 2015-10-13 | C | 10 | 0.0018178 | 3.0238e-05
7687303 | 2015-10-14 00:12 | 2015-10-14 00:53 | 40.6333 | 363 | 14749.9 | 40.6333 | 37.6333 | 0.0446 | 13660.9 | 0.041307 | 0.0010976 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 768787 | Pole/Lines arcing. Tree branch contacting lines at Pole 768787. Fault isolated via ABS 1092 & tree branch removed using hot stick techniques. Faultman to contact tree contractors regarding further work required. | F2/F3 | WANGANUI EAST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2015-10-14 | c | 0.041307 | 0.0010976 | 2016 | 2015-10-14 | C | 363 | 0.041307 | 0.0010976
7687907 | 2015-11-02 09:33 | 2015-11-02 14:00 | 267 | 4 | 1068 | 267 | 264 | 0.0032294 | 1056 | 0.0031931 | 1.2095e-05 | NAPA ID:13095 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/320 | Replace transformer T7/320. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.0015965 | 6.048e-06 | 2016 | 2015-11-02 | B | 4 | 0.0031931 | 1.2095e-05
7687921 | 2015-11-02 09:00 | 2015-11-02 15:21 | 381 | 31 | 11811 | 381 | 378 | 0.035714 | 11718 | 0.035432 | 9.3737e-05 | NAPA ID:13023 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | To install TEMP 86 and 87, replace poles and hardware in preparation for 11kV conductor upgrade. Note: New 11kV cable is to be livened between Poles E12492 and E12493, the existing 11kV overhead will be removed. Works location: Totmans Rd. WO 30002570 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-02 | b | 0.017716 | 4.6868e-05 | 2016 | 2015-11-02 | B | 31 | 0.035432 | 9.3737e-05
7687929 | 2015-11-03 09:00 | 2015-11-03 12:05 | 185 | 2 | 370 | 185 | 182 | 0.0011188 | 364 | 0.0011006 | 6.0475e-06 | NAPA ID:13097 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | Replace and install new transformer crossarms. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.00055032 | 3.024e-06 | 2016 | 2015-11-03 | B | 2 | 0.0011006 | 6.0475e-06
7687952 | 2015-11-05 09:15 | 2015-11-05 15:30 | 375 | 1 | 375 | 375 | 372 | 0.0011339 | 372 | 0.0011248 | 3.0238e-06 | NAPA ID:13100 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/295 | Reposition existing O/H transformer on pole. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.00056242 | 1.512e-06 | 2016 | 2015-11-05 | B | 1 | 0.0011248 | 3.0238e-06
7687974 | 2015-11-02 08:41 | 2015-11-02 14:43 | 362 | 33 | 11946 | 362 | 359 | 0.036122 | 11847 | 0.035822 | 9.9784e-05 | NAPA ID:13014 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P1896 | TO CREATE TEMP BREAK AT POLE P1896 TO ENABLE ABS IC220 & STRAIN XARMS TO BE REPLACED UNDER AN ACCESS PERMIT. Works location: Franklin Rd, Waitawheta. WO 10148222 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-11-02 | b | 0.017911 | 4.9892e-05 | 2016 | 2015-11-02 | B | 33 | 0.035822 | 9.9784e-05
7688017 | 2015-11-03 10:05 | 2015-11-03 15:58 | 352.9667 | 4 | 1153.5333 | 288.3833 | 285.3833 | 0.003488 | 1141.5333 | 0.0034517 | 1.2095e-05 | NAPA ID:13025 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole E12468 | To replace 11kV conductors between Pole #'s E12468 and E12477. Works location: Totmans Rd, Hinuera. WO 30002570 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-03 | b | 0.0017259 | 6.048e-06 | 2016 | 2015-11-03 | B | 4 | 0.0034517 | 1.2095e-05
7688036 | 2015-11-03 10:01 | 2015-11-03 15:17 | 316.4167 | 21 | 6644.75 | 316.4167 | 313.4167 | 0.020092 | 6581.75 | 0.019902 | 6.3499e-05 | NAPA ID:13068 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV F63 | Cutting trees around the 11 Kv. Works location: Pohangina Rd, Ashhurst. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.0099508 | 3.1749e-05 | 2016 | 2015-11-03 | B | 21 | 0.019902 | 6.3499e-05
7690435 | 2015-11-03 09:45 | 2015-11-03 13:46 | 240.1333 | 46 | 11046.1333 | 240.1333 | 237.1333 | 0.033401 | 10908.1333 | 0.032984 | 0.00013909 | NAPA ID:13258 TP_BRUNSWICK GXP > CASTLECLIFF SUB > HEADS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4497 | Replace 400v switchgear for transformer 2305W. Works location: Lee St, Wanganui. WO 30013304 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.016492 | 6.9546e-05 | 2016 | 2015-11-03 | B | 46 | 0.032984 | 0.00013909
7690441 | 2015-11-03 09:30 | 2015-11-03 11:30 | 120 | 3 | 360 | 120 | 117 | 0.0010886 | 351 | 0.0010613 | 9.0713e-06 | NAPA ID:13507 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4046 | REPLACE DDO XARM UNDER ACCESS PERMIT ON TC4046. Works location; Hwy 29, Te Poi. WO 30003315 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-11-03 | b | 0.00053067 | 4.536e-06 | 2016 | 2015-11-03 | B | 3 | 0.0010613 | 9.0713e-06
7690498 | 2015-11-03 08:46 | 2015-11-03 14:53 | 367.55 | 27 | 9923.85 | 367.55 | 364.55 | 0.030007 | 9842.85 | 0.029762 | 8.1642e-05 | NAPA ID:13029 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10256 | Replacing poles, cross arms and conductor between poles P215959 and ABS 1025 pole P21797. Works location; Te Rakehou Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.014881 | 4.0821e-05 | 2016 | 2015-11-03 | B | 27 | 0.029762 | 8.1642e-05
7690544 | 2015-11-11 08:40 | 2015-11-11 14:06 | 326 | 27 | 8802 | 326 | 323 | 0.026615 | 8721 | 0.02637 | 8.1642e-05 | NAPA ID:13434 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 10256 | Replacing poles, X arms and conductor between poles P21959 and ABS 10256, pole P21797. Works location: Te Rakehou Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-11 | b | 0.013185 | 4.0821e-05 | 2016 | 2015-11-11 | B | 27 | 0.02637 | 8.1642e-05
7690561 | 2015-11-18 08:50 | 2015-11-18 14:20 | 330 | 27 | 8910 | 330 | 327 | 0.026942 | 8829 | 0.026697 | 8.1642e-05 | NAPA ID:13449 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 10256 | Replacing poles, X arms and conductor between poles P21959 and pole P21797. Works location: Te Rakehou Rd, Sanson. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-18 | b | 0.013348 | 4.0821e-05 | 2016 | 2015-11-18 | B | 27 | 0.026697 | 8.1642e-05
7690688 | 2015-11-02 00:01 | 2015-11-02 04:34 | 273 | 165 | 45045 | 273 | 270 | 0.13621 | 44550 | 0.13471 | 0.00049892 | NAPA ID:13415 TP_TAURANGA 33 GXP > OTUMOETAI SUB > CHERRYWOOD DRIVE | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G SC4-423 | Replace Cable Term at Sw/gear SC4-430 and joint to existing 11kv cable. Works location: Otumoetai Rd, Tauranga. WO 30011999 | F3 | CHERRYWOOD DRIVE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-11-02 | b | 0.067354 | 0.00024946 | 2016 | 2015-11-02 | B | 165 | 0.13471 | 0.00049892
7690738 | 2015-11-02 09:38 | 2015-11-02 11:40 | 122 | 3 | 366 | 122 | 119 | 0.0011067 | 357 | 0.0010795 | 9.0713e-06 | NAPA ID:13123 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2865 | Replace Transformer and Crossarm at TC2865. Works location: Hwy 26, Puriri. WO 10147831 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-11-02 | b | 0.00053974 | 4.536e-06 | 2016 | 2015-11-02 | B | 3 | 0.0010795 | 9.0713e-06
7690747 | 2015-11-05 09:23 | 2015-11-05 13:39 | 256 | 38 | 9728 | 256 | 253 | 0.029415 | 9614 | 0.02907 | 0.0001149 | NAPA ID:13446 TP_WANGANUI GXP > HATRICKS WHARF SUB > BELL ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X2365 | Replace 400V switchgear for transformer X2365, all 400V lines will be backfeed Advertising required for for 63Dublin st,Burwood motel. Works location: Campbell St, Wanganui. WO 30008167 | F3 | BELL ST | WANGANUI | Wanganui | HATRICKS WHARF SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.014535 | 5.7451e-05 | 2016 | 2015-11-05 | B | 38 | 0.02907 | 0.0001149
7690831 | 2015-11-02 13:00 | 2015-11-02 15:40 | 160 | 1 | 160 | 160 | 157 | 0.0004838 | 157 | 0.00047473 | 3.0238e-06 | NAPA ID:13130 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC272 | Replace Crossarm at TC272. Works location: Awaiti West Rd, Awaiti. WO 30010640 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-02 | b | 0.00023736 | 1.512e-06 | 2016 | 2015-11-02 | B | 1 | 0.00047473 | 3.0238e-06
7690840 | 2015-11-03 10:10 | 2015-11-03 14:50 | 280 | 33 | 9240 | 280 | 277 | 0.02794 | 9141 | 0.02764 | 9.9784e-05 | NAPA ID:13219 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI707 | Replace poles and Xarms on Ball rd Hurleyville. Works location: Ball Rd, Hurleyville. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.01382 | 4.9892e-05 | 2016 | 2015-11-03 | B | 33 | 0.02764 | 9.9784e-05
7690894 | 2015-11-05 10:00 | 2015-11-05 12:27 | 146.4667 | 200 | 29293.3333 | 146.4667 | 143.4667 | 0.088576 | 28693.3333 | 0.086762 | 0.00060475 | NAPA ID:13065 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 773473 | Trimming trees around poles 773473 and 773474. Works location: SH3 Waitotara. WO 10152359. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-05 | b | 0.043381 | 0.00030238 | 2016 | 2015-11-05 | B | 200 | 0.086762 | 0.00060475
7691030 | 2015-11-03 09:00 | 2015-11-03 15:18 | 377.3667 | 43 | 16226.7667 | 377.3667 | 374.3667 | 0.049066 | 16097.7667 | 0.048676 | 0.00013002 | NAPA ID:13072 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 223288 | REPLACE POLES AND ARMS AND RECONDUTOR FEEDER NO 4 ROAD. Works location: No 4 Rd. WO 30002430 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-11-03 | b | 0.024338 | 6.5011e-05 | 2016 | 2015-11-03 | B | 43 | 0.048676 | 0.00013002
7691044 | 2015-11-05 09:26 | 2015-11-05 14:04 | 277.9333 | 3 | 833.8 | 277.9333 | 274.9333 | 0.0025212 | 824.8 | 0.002494 | 9.0713e-06 | NAPA ID:12801 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links Q48 | To Replace defected larch pole. Works location: Pahiatua Pongaroa Rd. WO 30010305 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.001247 | 4.536e-06 | 2016 | 2015-11-05 | B | 3 | 0.002494 | 9.0713e-06
7691052 | 2015-11-05 08:45 | 2015-11-05 14:19 | 334.2333 | 43 | 14372.0333 | 334.2333 | 331.2333 | 0.043458 | 14243.0333 | 0.043068 | 0.00013002 | NAPA ID:13074 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IP629 | REPLACE POLES AND ARMS AND RECONDUTOR FEEDER NO 4 ROAD. Works location: No 4 Rd. WO 30002430 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-11-05 | b | 0.021534 | 6.5011e-05 | 2016 | 2015-11-05 | B | 43 | 0.043068 | 0.00013002
7691155 | 2015-11-05 09:43 | 2015-11-05 16:00 | 377.15 | 32 | 12068.8 | 377.15 | 374.15 | 0.036493 | 11972.8 | 0.036203 | 9.676e-05 | NAPA ID:13222 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABs LI731 | Replace poles on Ball Rd Alton. Works location: Ball Rd, Alton. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.018101 | 4.838e-05 | 2016 | 2015-11-05 | B | 32 | 0.036203 | 9.676e-05
7691262 | 2015-11-10 09:16 | 2015-11-10 15:01 | 345 | 18 | 6210 | 345 | 342 | 0.018778 | 6156 | 0.018614 | 5.4428e-05 | NAPA ID:13215 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI730 | Replace poles and xarms on Ball rd Hurleyville. Works location: Ball Rd, Hurleyville. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-10 | b | 0.0093071 | 2.7214e-05 | 2016 | 2015-11-10 | B | 18 | 0.018614 | 5.4428e-05
7691296 | 2015-11-12 09:30 | 2015-11-12 15:47 | 377 | 20 | 7427.4 | 371.37 | 368.37 | 0.022459 | 7367.4 | 0.022277 | 6.0475e-05 | NAPA ID:13224 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI716 | Replace conductor. Works location: Ball Rd, Hurleyville. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-12 | b | 0.011139 | 3.0238e-05 | 2016 | 2015-11-12 | B | 20 | 0.022277 | 6.0475e-05
7691332 | 2015-11-05 09:32 | 2015-11-05 12:17 | 165.3667 | 34 | 5622.4667 | 165.3667 | 162.3667 | 0.017001 | 5520.4667 | 0.016693 | 0.00010281 | NAPA ID:13371 TP_GREYTOWN GXP > MARTINBOROUGH SUB > COLOGNE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7383 | Replace 11kV pole and hardware. Works location: Longbush Rd. WO 300094123 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.0083463 | 5.1404e-05 | 2016 | 2015-11-05 | B | 34 | 0.016693 | 0.00010281
7691399 | 2015-11-10 09:01 | 2015-11-10 15:27 | 385.9167 | 43 | 16557.0167 | 385.0469 | 382.0469 | 0.050064 | 16428.0167 | 0.049674 | 0.00013002 | NAPA ID:13076 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 223246 | REPLACE POLES AND ARMS AND RECONDUTOR FEEDER NO 4 ROAD. Works location: No 4 Rd. WO 30002430 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-11-10 | b | 0.024837 | 6.5011e-05 | 2016 | 2015-11-10 | B | 43 | 0.049674 | 0.00013002
7691559 | 2015-11-04 09:13 | 2015-11-04 12:41 | 207.95 | 5 | 1039.75 | 207.95 | 204.95 | 0.003144 | 1024.75 | 0.0030986 | 1.5119e-05 | NAPA ID:13697 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP869 | Re-Level Ground mount Transformer TP1554. Works location: Tapu Coroglen Rd, Thames. WO 30010652 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-04 | b | 0.0015493 | 7.559e-06 | 2016 | 2015-11-04 | B | 5 | 0.0030986 | 1.5119e-05
7691616 | 2015-10-14 12:00 | 2015-10-14 14:05 | 125.05 | 1 | 125.05 | 125.05 | 122.05 | 0.00037812 | 122.05 | 0.00036905 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2684 | 2 x3 amp HV Fuses and 1 holder unknown cause. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-14 | c | 0.00036905 | 3.024e-06 | 2016 | 2015-10-14 | C | 1 | 0.00036905 | 3.0238e-06
7693186 | 2015-11-06 09:31 | 2015-11-06 12:33 | 182.2333 | 16 | 2915.7333 | 182.2333 | 179.2333 | 0.0088165 | 2867.7333 | 0.0086713 | 4.838e-05 | NAPA ID:12886 TP_MARTON GXP > PUKEPAPA SUB > TURAKINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 859 | Replace high voltage X arms on Transformer pole X1512. Works location: Reynolds Rd, Turakina. WO 30003154 | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-11-06 | b | 0.0043357 | 2.419e-05 | 2016 | 2015-11-06 | B | 16 | 0.0086713 | 4.838e-05
7693795 | 2015-11-08 09:31 | 2015-11-08 13:18 | 227.35 | 83 | 18870.05 | 227.35 | 224.35 | 0.057059 | 18621.05 | 0.056306 | 0.00025097 | NAPA ID:13484 TP_HUIRANGI GXP > INGLEWOOD SUB > BROOKES ST | 6.6 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5506 | Inglewood part CBD upgrade. emove HV O/H and U/G cable from pole 707786 (incl. Fuse 4864).Replace pole 707785 with new and install Fused ABS 4864 with new HV U/G cable to supply new transformer 4154T. Remove old (existing) Transformer 4154T, relocate and | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-11-08 | b | 0.028153 | 0.00012549 | 2016 | 2015-11-08 | B | 83 | 0.056306 | 0.00025097
7693798 | 2015-11-09 10:38 | 2015-11-09 13:54 | 196.3833 | 136 | 26708.1333 | 196.3833 | 193.3833 | 0.080759 | 26300.1333 | 0.079525 | 0.00041123 | NAPA ID:13654 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4210 | Move pole 784436 away from the river bank that is slipping away and also clearance from ground to 11kv getting close. Works location: Papaiti Rd, Wanganui. WO 30015332 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-11-09 | b | 0.039763 | 0.00020562 | 2016 | 2015-11-09 | B | 136 | 0.079525 | 0.00041123
7693829 | 2015-11-09 08:50 | 2015-11-09 13:50 | 300.0333 | 2 | 600.0667 | 300.0333 | 297.0333 | 0.0018145 | 594.0667 | 0.0017963 | 6.0475e-06 | NAPA ID:13606 TP_MASTERTON GXP > TE ORE ORE SUB > TAUWERU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7070 | Replace T/X pole. Works location: Te Parae Rd, Masterton. WO 30014038 | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-09 | b | 0.00089816 | 3.024e-06 | 2016 | 2015-11-09 | B | 2 | 0.0017963 | 6.0475e-06
7695000 | 2015-11-05 10:20 | 2015-11-05 13:00 | 160 | 24 | 3840 | 160 | 157 | 0.011611 | 3768 | 0.011394 | 7.257e-05 | NAPA ID:13543 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD7-004 | Isolate HV for work to be done on the LV bus isolater of Transformer TD7-004. Works location: Williams Crescent, Maketu, Te Puke. WO 30012285 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-05 | b | 0.0056968 | 3.6285e-05 | 2016 | 2015-11-05 | B | 24 | 0.011394 | 7.257e-05
7695720 | 2015-11-09 08:30 | 2015-11-09 09:23 | 53.3833 | 8 | 427.0667 | 53.3833 | 50.3833 | 0.0012913 | 403.0667 | 0.0012188 | 2.419e-05 | NAPA ID:13182 TP_WAVERLEY GXP > TP_WAVERLEY | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4490/3 | Clean HV cables due to failed acoustic test. Works location: Rosmount Rd, Waipipi. WO 30013723 | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-09 | b | 0.00060939 | 1.2095e-05 | 2016 | 2015-11-09 | B | 8 | 0.0012188 | 2.419e-05
7695790 | 2015-11-14 09:02 | 2015-11-14 11:19 | 137 | 190 | 18715.75 | 98.5039 | 95.5039 | 0.056592 | 18145.75 | 0.054868 | 0.00057451 | NAPA ID:13494 TP_BUNNYTHORPE GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 414 | Change 1 x 33kV cross arms and 1 x 11kV cross arms and hardware. Works location: Roberts Line. WO 30006772 | F3 | KARAMEA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-14 | b | 0.027434 | 0.00028726 | 2016 | 2015-11-14 | B | 190 | 0.054868 | 0.00057451
7695844 | 2015-11-09 09:51 | 2015-11-09 12:20 | 149.5333 | 10 | 1495.3333 | 149.5333 | 146.5333 | 0.0045215 | 1465.3333 | 0.0044308 | 3.0238e-05 | NAPA ID:13001 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV E54 | Isolate and earth lines so Treescape can carry out tree works. Works location: Hazelhurst Rd. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-09 | b | 0.0022154 | 1.5119e-05 | 2016 | 2015-11-09 | B | 10 | 0.0044308 | 3.0238e-05
7696530 | 2015-10-14 21:35 | 2015-10-14 23:43 | 127.85 | 170 | 14578.4 | 85.7553 | 82.7553 | 0.044082 | 14068.4 | 0.042539 | 0.00051404 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T4250 | Reports of no power; found CB C946 tripped at Gladstone Sub. Feeder patrolled / sectionalised with a dead Magpie found at transformer T4250. Removed with fuse stick and all relivened OK. | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-14 | c | 0.042539 | 0.00051404 | 2016 | 2015-10-14 | C | 170 | 0.042539 | 0.00051404
7696977 | 2015-10-15 06:15 | 2015-10-15 08:02 | 107 | 319 | 33386 | 104.6583 | 101.6583 | 0.10095 | 32429 | 0.098058 | 0.00096458 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 282 | CB 282 tripped no flags, line was patrolled and sectionalised and no fault was found. Suspect bird strike. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-10-15 | c | 0.098058 | 0.00096458 | 2016 | 2015-10-15 | C | 319 | 0.098058 | 0.00096458
7699003 | 2015-10-16 10:19 | 2015-10-16 11:20 | 60.6333 | 31 | 1879.6333 | 60.6333 | 57.6333 | 0.0056836 | 1786.6333 | 0.0054024 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K03434 | Red defect - HV Crossarm arm is rotten needs to be replaced tomorrow 15/10. Crossarm replaced complete | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-16 | c | 0.0054024 | 9.3737e-05 | 2016 | 2015-10-16 | C | 31 | 0.0054024 | 9.3737e-05
7699435 | 2015-11-10 09:39 | 2015-11-10 10:25 | 46 | 13 | 598 | 46 | 43 | 0.0018082 | 559 | 0.0016903 | 3.9309e-05 | NAPA ID:13565 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P26113 | Replace 11kV arrestors P26113. Works location: Stoney Creek Rd, Palmerston North. WO 10162065 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-10 | b | 0.00084514 | 1.9654e-05 | 2016 | 2015-11-10 | B | 13 | 0.0016903 | 3.9309e-05
7699482 | 2015-11-10 10:05 | 2015-11-10 13:15 | 190 | 6 | 1140 | 190 | 187 | 0.0034471 | 1122 | 0.0033927 | 1.8143e-05 | NAPA ID:13365 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 511 | replace t/f pole x2225 to opposite side of rd upgarde with new t/f and liven new ug pillar. Works location: Abittior Rd, Taihape. WO 30011329 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-10 | b | 0.0016963 | 9.071e-06 | 2016 | 2015-11-10 | B | 6 | 0.0033927 | 1.8143e-05
7699515 | 2015-10-15 10:23 | 2015-10-15 12:35 | 132.2333 | 777 | 26469.1 | 34.0658 | 31.0658 | 0.080036 | 24138.1 | 0.072988 | 0.0023495 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 832704 | Resag Lines at Pole 832704 due to Tractor hitting Pole. 3 x Binders Used | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-10-15 | c | 0.072988 | 0.0023495 | 2016 | 2015-10-15 | C | 777 | 0.072988 | 0.0023495
7701873 | 2015-11-11 09:00 | 2015-11-11 11:00 | 120 | 40 | 4800 | 120 | 117 | 0.014514 | 4680 | 0.014151 | 0.00012095 | NAPA ID:13002 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV H34 | Isolate and earth lines so Treescape can carry out tree works. Works location: Tiritea Rd. WO 10152357. Fault man had problems locating Fuses H34 and only had 1 set of operator earths job cancelled due to this factors | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-11-11 | b | 0.0070756 | 6.0475e-05 | 2016 | 2015-11-11 | B | 40 | 0.014151 | 0.00012095
7702763 | 2015-11-11 10:00 | 2015-11-11 13:25 | 205 | 6 | 1230 | 205 | 202 | 0.0037192 | 1212 | 0.0036648 | 1.8143e-05 | NAPA ID:13655 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7101 | Replace 11kv pole. Works location: Admiral Rd, Carterton. WO 30013869 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-11-11 | b | 0.0018324 | 9.071e-06 | 2016 | 2015-11-11 | B | 6 | 0.0036648 | 1.8143e-05
7702813 | 2015-11-05 09:30 | 2015-11-05 15:22 | 351.9167 | 27 | 9501.75 | 351.9167 | 348.9167 | 0.028731 | 9420.75 | 0.028486 | 8.1642e-05 | NAPA ID:12812 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 220115 | Replace poles, crossarms and conductors between poles 220115 & 220170. Works location: Te Puke Quarry Rd. WO 30003844 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-05 | b | 0.014243 | 4.0821e-05 | 2016 | 2015-11-05 | B | 27 | 0.028486 | 8.1642e-05
7702922 | 2015-11-02 09:50 | 2015-11-02 13:25 | 215 | 2 | 430 | 215 | 212 | 0.0013002 | 424 | 0.0012821 | 6.0475e-06 | NAPA ID:13788 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 1518 | We Have to replace the transformer and upgrade the earths as it is leaking oil onto the ground. Works location: Tate Rd. WO 30015276 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.00064104 | 3.024e-06 | 2016 | 2015-11-02 | B | 2 | 0.0012821 | 6.0475e-06
7703283 | 2015-11-05 09:09 | 2015-11-05 15:16 | 367.1833 | 1 | 367.1833 | 367.1833 | 364.1833 | 0.0011103 | 364.1833 | 0.0011012 | 3.0238e-06 | NAPA ID:13334 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 228 | isolation of 11 kv line for Treescape Temoehau Rd Taihape. Works location: Temoehau Rd. WO 10152359 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.0005506 | 1.512e-06 | 2016 | 2015-11-05 | B | 1 | 0.0011012 | 3.0238e-06
7704315 | 2015-11-12 09:33 | 2015-11-12 14:19 | 286 | 1 | 286 | 286 | 283 | 0.0008648 | 283 | 0.00085572 | 3.0238e-06 | NAPA ID:13602 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P08979 | To replace transformer pole T9/471 and replace 11kV conductor. Works location: Mangaone Valley Rd. WO 10162458 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-11-12 | b | 0.00042786 | 1.512e-06 | 2016 | 2015-11-12 | B | 1 | 0.00085572 | 3.0238e-06
7704321 | 2015-10-15 17:17 | 2015-10-15 19:55 | 157.9833 | 17 | 2685.7167 | 157.9833 | 154.9833 | 0.008121 | 2634.7167 | 0.0079668 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810017 | Faultman found a broken cross arm at pole 810017, liner was isolated at Fuses O57 to replace cross arm. Relivened OK. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-10-15 | c | 0.0079668 | 5.1404e-05 | 2016 | 2015-10-15 | C | 17 | 0.0079668 | 5.1404e-05
7704431 | 2015-10-15 16:45 | 2015-10-15 18:05 | 79.9833 | 19 | 1519.6833 | 79.9833 | 76.9833 | 0.0045952 | 1462.6833 | 0.0044228 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 815263 | 2R Jason Hall On Site. Tree acroos Live Lines. Truck to arrive. Isolate for safety to remove tree from lines. Line was isolated at Fuses 8040 to cut branch away from line at pole 815263.Tree not in zone.NDR will follow at later date. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-10-15 | c | 0.0044228 | 5.7451e-05 | 2016 | 2015-10-15 | C | 19 | 0.0044228 | 5.7451e-05
7706666 | 2015-11-13 08:38 | 2015-11-13 16:59 | 500.3833 | 4 | 2001.5333 | 500.3833 | 497.3833 | 0.0060522 | 1989.5333 | 0.0060159 | 1.2095e-05 | NAPA ID:13631 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | V36 | To remove trees near over head lines between poles numbers p04915 and p04745. Works location: River Rd. WO 10152357 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-13 | b | 0.0030079 | 6.048e-06 | 2016 | 2015-11-13 | B | 4 | 0.0060159 | 1.2095e-05
7707681 | 2015-11-13 09:35 | 2015-11-13 14:06 | 271 | 8 | 2168 | 271 | 268 | 0.0065555 | 2144 | 0.0064829 | 2.419e-05 | NAPA ID:13750 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 838689 | To replace crossarms and ddo's. Works location: Matikona Rd, Masterton. WO 30014039 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-11-13 | b | 0.0032415 | 1.2095e-05 | 2016 | 2015-11-13 | B | 8 | 0.0064829 | 2.419e-05
7707719 | 2015-10-16 10:19 | 2015-10-16 11:30 | 71.05 | 21 | 1492.05 | 71.05 | 68.05 | 0.0045116 | 1429.05 | 0.0043211 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ma298 | Replace 2 x 10A fuses at MA298 | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.0043211 | 6.3499e-05 | 2016 | 2015-10-16 | C | 21 | 0.0043211 | 6.3499e-05
7707863 | 2015-11-04 09:20 | 2015-11-04 14:36 | 316 | 27 | 8532 | 316 | 313 | 0.025799 | 8451 | 0.025554 | 8.1642e-05 | NAPA ID:13289 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F0136 | To install temporary ABS TEMP60 and TEMP78 in conjunction with pole replacements in preparation for conductor upgrade. Works location: Puketutu Rd. WO 30002534 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-04 | b | 0.012777 | 4.0821e-05 | 2016 | 2015-11-04 | B | 27 | 0.025554 | 8.1642e-05
7708487 | 2015-10-28 08:50 | 2015-10-28 16:04 | 434 | 113 | 19848 | 175.646 | 172.646 | 0.060016 | 19509 | 0.058991 | 0.00034168 | NAPA ID:13924 TP_WAIKINO GXP > WAIHI BEACH SUB > WILSON RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP627 | Replace 11kV poles and hardware at various sites. Works location: Wilson Rd, Waihi Beach. WO 30002441 | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-10-28 | b | 0.029495 | 0.00017084 | 2016 | 2015-10-28 | B | 113 | 0.058991 | 0.00034168
7708711 | 2015-10-16 14:59 | 2015-10-16 16:04 | 65.45 | 291 | 19045.95 | 65.45 | 62.45 | 0.05759 | 18172.95 | 0.054951 | 0.00087991 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NA | CB 3 Tripped OC. DELAY DUE TO TREEWORKS IN AREA OF NO COMMS NOTHING FOUND | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.054951 | 0.00087991 | 2016 | 2015-10-16 | C | 291 | 0.054951 | 0.00087991
7709052 | 2015-10-16 18:17 | 2015-10-16 21:40 | 202.4833 | 2112 | 209099.95 | 99.0057 | 96.0057 | 0.63227 | 202763.95 | 0.61311 | 0.0063862 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P19803 | 1R- 33kV Crossarm inspection. Crossarm at Pole P19803 : 245 Kimbolton Rd ; Broken Crossarm. FM Advise Crossarm requires immediate Replacement.Line was isolated at 33KV ABS's X22, X23, X72, X73 and on 11KV, ABS's K2, K3, K12, J69 Sw/Gear's 265 & 379 to rep | F1,F2,F3 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.61311 | 0.0063862 | 2016 | 2015-10-16 | C | 2112 | 0.61311 | 0.0063862
7709123 | 2015-10-16 14:58 | 2015-10-16 15:12 | 14 | 249 | 3486 | 14 | 11 | 0.010541 | 2739 | 0.0082821 | 0.00075292 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V0864 | 3 x 11kV binders Replaced at Poles V0864. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-16 | c | 0.0082821 | 0.00075292 | 2016 | 2015-10-16 | C | 249 | 0.0082821 | 0.00075292
7709742 | 2015-11-06 09:36 | 2015-11-06 13:45 | 249 | 14 | 3486 | 249 | 246 | 0.010541 | 3444 | 0.010414 | 4.2333e-05 | NAPA ID:13708 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 205214 | TO REPLACE POLE 205214 LIVE L;INE. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-11-06 | b | 0.0052069 | 2.1166e-05 | 2016 | 2015-11-06 | B | 14 | 0.010414 | 4.2333e-05
7709768 | 2015-11-05 10:00 | 2015-11-05 12:05 | 125 | 3 | 375 | 125 | 122 | 0.0011339 | 366 | 0.0011067 | 9.0713e-06 | NAPA ID:13375 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3692 | To replace/upgrade TC3692 from a 15kVA to a 50kVA transformer. Works location SH 26 Tatuanui, Morrinsville. WO 30014785 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-11-05 | b | 0.00055335 | 4.536e-06 | 2016 | 2015-11-05 | B | 3 | 0.0011067 | 9.0713e-06
7710394 | 2015-11-05 09:25 | 2015-11-05 14:30 | 305 | 1 | 305 | 305 | 302 | 0.00092225 | 302 | 0.00091318 | 3.0238e-06 | NAPA ID:13556 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 12113 | Replace rusted leaking tc K4015 with new citypad type tx of same size at STOS site. Works location: Skeet Rd. WO 30011413 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.00045659 | 1.512e-06 | 2016 | 2015-11-05 | B | 1 | 0.00091318 | 3.0238e-06
7710486 | 2015-10-16 16:45 | 2015-10-16 17:15 | 30 | 1 | 30 | 30 | 27 | 9.0713e-05 | 27 | 8.1642e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC1110 | 3.40pm - no pole down. one line is off the insulator and hanging down but not broken. the other line is knocked off the insulator as well and resting on cross arm. 3.45pm - advise smc. Isolated by Opening Fuses FC1110 - Replaced Binder, Poles not numbered | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-10-16 | c | 8.1642e-05 | 3.024e-06 | 2016 | 2015-10-16 | C | 1 | 8.1642e-05 | 3.0238e-06
7710729 | 2015-10-16 16:42 | 2015-10-20 16:58 | 5776.1833 | 6 | 18718.1 | 3119.6833 | 3116.6833 | 0.056599 | 18700.1 | 0.056545 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P06293 | V19 11KV wire come off insulators and crossed over the other lines and landed in the trees due to very strong winds - No way to repair tonight in the weather so going to organize generators for the customer. Line was isolated at Fuses V18 .Generator has | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.056545 | 1.8143e-05 | 2016 | 2015-10-16 | C | 6 | 0.056545 | 1.8143e-05
7711858 | 2015-10-16 17:30 | 2015-10-16 21:08 | 218 | 232 | 29225.8333 | 125.9734 | 122.9734 | 0.088372 | 28529.8333 | 0.086267 | 0.00070151 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10335 | Repaired floating conductor @ pole P10335 and restored line break @ pole P28873. Outage reflected under OMS 7713428 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.086267 | 0.00070151 | 2016 | 2015-10-16 | C | 232 | 0.086267 | 0.00070151
7713197 | 2015-10-16 06:52 | 2015-10-17 18:09 | 2117.25 | 99 | 87973.2333 | 888.6185 | 885.6185 | 0.26601 | 87676.2333 | 0.26511 | 0.00029935 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | as per notes | Recloser V5 autoreclosed on B & C phase O/C & E/F flags, CB 1 was opened as NOC could not get Recloser V5 to open via Scada due to comms kept failing, later Recloser V5 was opened and faultman confirmed lines down on a spur line going down to transformer | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.26511 | 0.00029935 | 2016 | 2015-10-16 | C | 99 | 0.26511 | 0.00029935
7717619 | 2015-10-16 21:11 | 2015-10-16 22:50 | 98.7167 | 212 | 20729.4 | 97.7802 | 94.7802 | 0.062681 | 20093.4 | 0.060758 | 0.00064104 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | CB 2 | CB 2 tripped on B phase O/C & E/F flags, line was patrolled and faultman remove debris from line at verse spots along the line blown onto them by the high winds in the area. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-16 | c | 0.060758 | 0.00064104 | 2016 | 2015-10-16 | C | 212 | 0.060758 | 0.00064104
7719644 | 2015-10-16 22:09 | 2015-10-17 00:07 | 117.5 | 108 | 12690 | 117.5 | 114.5 | 0.038372 | 12366 | 0.037392 | 0.00032657 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD2-009 | Check oms 7719685, 7719697 and 7721905. 2 X HV Fuses replaced. Suspect Opossum or Line Clash | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-10-16 | c | 0.037392 | 0.00032657 | 2016 | 2015-10-16 | C | 108 | 0.037392 | 0.00032657
7724341 | 2015-10-17 00:14 | 2015-10-17 05:52 | 337.9833 | 299 | 36197.0333 | 121.0603 | 118.0603 | 0.10945 | 35300.0333 | 0.10674 | 0.0009041 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | RS 9560 Trip. A/R. E/F. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-10-17 | c | 0.10674 | 0.0009041 | 2016 | 2015-10-17 | C | 299 | 0.10674 | 0.0009041
7725901 | 2015-10-17 08:07 | 2015-10-17 15:20 | 433.0333 | 1 | 433.0333 | 433.0333 | 430.0333 | 0.0013094 | 430.0333 | 0.0013003 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838338 | Temporary repaired crossarm and floater on pole 838338 . Check 1582 and 1472 OTAHOME ROAD - 7725972 and 7726049 | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.0013003 | 3.024e-06 | 2016 | 2015-10-17 | C | 1 | 0.0013003 | 3.0238e-06
7726251 | 2015-10-17 09:50 | 2015-10-17 17:10 | 439.9 | 2 | 623.2667 | 311.6333 | 308.6333 | 0.0018846 | 617.2667 | 0.0018665 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 10148 | *** please check if oms 7727511 is part of this outage - 631 KAITUNA ROAD off tx T9/107 *** Removed branch from lines @ pole 1095 and replaced 2X HV fuses @ 10148 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.0018665 | 6.048e-06 | 2016 | 2015-10-17 | C | 2 | 0.0018665 | 6.0475e-06
7726272 | 2015-10-17 09:58 | 2015-10-17 19:09 | 550.55 | 8 | 4404.4 | 550.55 | 547.55 | 0.013318 | 4380.4 | 0.013245 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837915 | Replaced 4 crossarms at pole 837915 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.013245 | 2.419e-05 | 2016 | 2015-10-17 | C | 8 | 0.013245 | 2.419e-05
7726530 | 2015-10-17 10:33 | 2015-10-17 16:54 | 381.4833 | 424 | 161308.9667 | 380.4457 | 377.4457 | 0.48776 | 160036.9667 | 0.48391 | 0.0012821 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 838557 | Circuit Braker C937 tripped Tree on line at pole 838557. Isolated at ABS S165 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.48391 | 0.0012821 | 2016 | 2015-10-17 | C | 424 | 0.48391 | 0.0012821
7727348 | 2015-10-17 13:14 | 2015-10-17 16:15 | 181.0333 | 1 | 181.0333 | 181.0333 | 178.0333 | 0.0005474 | 178.0333 | 0.00053833 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tf8049 | replace 2 x 8 amp hv fuses. tx tf8049. cause: unknown. FM had no reception out there and he could not phone control to advise he is replacing the fuses. Transferred him through to control. FM met customer onsite this time and they could show where the iss | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-17 | c | 0.00053833 | 3.024e-06 | 2016 | 2015-10-17 | C | 1 | 0.00053833 | 3.0238e-06
7727917 | 2015-10-17 16:25 | 2015-10-17 18:44 | 139 | 2 | 278 | 139 | 136 | 0.00084061 | 272 | 0.00082246 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | J30 | Replaced 2 X fuses @ J30 | F3 | WEST TOWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.00082246 | 6.048e-06 | 2016 | 2015-10-17 | C | 2 | 0.00082246 | 6.0475e-06
7728114 | 2015-10-17 17:10 | 2015-10-17 21:15 | 244.6 | 1 | 244.6 | 244.6 | 241.6 | 0.00073961 | 241.6 | 0.00073054 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T8/324 | Faultman found transformer T8/324 to be deffective, transformer is been replaced. 1 x transformer replaced. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.00073054 | 3.024e-06 | 2016 | 2015-10-17 | C | 1 | 0.00073054 | 3.0238e-06
7729641 | 2015-10-17 21:46 | 2015-10-18 01:20 | 214.3167 | 7 | 1500.2167 | 214.3167 | 211.3167 | 0.0045363 | 1479.2167 | 0.0044728 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 850014 | Car v pole 850014 Junction Rd New Plymouth. Near cnr Hydro & Waiwakaiho Rd. Reported by Fire Service. Ref F1939551. Line was isolated at Fuses 8252 to replace pole. NDR: N100071 | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.0044728 | 2.1166e-05 | 2016 | 2015-10-17 | C | 7 | 0.0044728 | 2.1166e-05
7729920 | 2015-10-17 23:33 | 2015-10-18 02:34 | 181 | 774 | 68441.5333 | 88.4258 | 85.4258 | 0.20695 | 66119.5333 | 0.19993 | 0.0023404 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Moturoa Sub, CB3 | CB 3 tripped on E/F flags, line was patrolled and sectionalised and a broken insulator was found at pole, line was isolated at ABS's 363 & 374 to replace the insulator on pole 756535. Traffic management was needed & a bucket truck to carry out the repairs | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-10-17 | c | 0.19993 | 0.0023404 | 2016 | 2015-10-17 | C | 774 | 0.19993 | 0.0023404
7730972 | 2015-10-18 06:49 | 2015-10-18 12:29 | 339.8833 | 38 | 12915.5667 | 339.8833 | 336.8833 | 0.039054 | 12801.5667 | 0.038709 | 0.0001149 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P06220 | Temp Job until can get truck in as to wet | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.038709 | 0.0001149 | 2016 | 2015-10-18 | C | 38 | 0.038709 | 0.0001149
7731563 | 2015-10-18 10:47 | 2015-10-18 13:37 | 170.2167 | 7 | 465.0667 | 66.4381 | 63.4381 | 0.0014063 | 444.0667 | 0.0013428 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | S25 | Advised Hub and Control. Removed Tree off Line. | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0013428 | 2.1166e-05 | 2016 | 2015-10-18 | C | 7 | 0.0013428 | 2.1166e-05
7731756 | 2015-10-18 12:12 | 2015-10-18 14:51 | 158.4 | 1 | 158.4 | 158.4 | 155.4 | 0.00047896 | 155.4 | 0.00046989 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | T961 | Removed Bit of Tree off line at Transformer T961 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.00046989 | 3.024e-06 | 2016 | 2015-10-18 | C | 1 | 0.00046989 | 3.0238e-06
7732144 | 2015-10-18 12:57 | 2015-10-18 17:57 | 300.1667 | 302 | 83848.15 | 277.6429 | 274.6429 | 0.25354 | 82942.15 | 0.2508 | 0.00091318 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C225 | Tree across Lines at Pole 838651. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.2508 | 0.00091318 | 2016 | 2015-10-18 | C | 302 | 0.2508 | 0.00091318
7732851 | 2015-10-18 13:06 | 2015-10-18 14:02 | 55.8167 | 197 | 10365.3833 | 52.6162 | 49.6162 | 0.031342 | 9774.3833 | 0.029555 | 0.00059568 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | P06672 | Chopper Patrol of 33kV Lines Found 11kV floater on Pongaroa CB 1. | F1,F2,F3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.029555 | 0.00059568 | 2016 | 2015-10-18 | C | 197 | 0.029555 | 0.00059568
7733345 | 2015-10-18 13:56 | 2015-10-18 15:39 | 103 | 1472 | 127894 | 86.8845 | 83.8845 | 0.38672 | 123478 | 0.37337 | 0.004451 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | Patrolled Nothing found Lots of Wind and some Big Trees Back Feeds Still in Place | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.37337 | 0.004451 | 2016 | 2015-10-18 | C | 1472 | 0.37337 | 0.004451
7734819 | 2015-10-18 13:56 | 2015-10-18 14:35 | 39 | 36 | 1404 | 39 | 36 | 0.0042454 | 1296 | 0.0039188 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | Patrolled nothing found Lots of wind | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0039188 | 0.00010886 | 2016 | 2015-10-18 | C | 36 | 0.0039188 | 0.00010886
7734863 | 2015-10-18 13:57 | 2015-10-18 15:26 | 89.0667 | 833 | 74192.5333 | 89.0667 | 86.0667 | 0.22434 | 71693.5333 | 0.21678 | 0.0025188 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C823 | CB C823 Tripped A & C Phase O/C. Line Patrolled - Nothing Found. Lots Of Wind. | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.21678 | 0.0025188 | 2016 | 2015-10-18 | C | 833 | 0.21678 | 0.0025188
7737600 | 2015-10-18 14:49 | 2015-10-18 17:42 | 173.1167 | 178 | 14677.8 | 82.4596 | 79.4596 | 0.044382 | 14143.8 | 0.042767 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P27930 | Floating Conductor at Pole P27930. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.042767 | 0.00053823 | 2016 | 2015-10-18 | C | 178 | 0.042767 | 0.00053823
7740302 | 2015-10-18 15:55 | 2015-10-18 17:53 | 117.9 | 1 | 117.9 | 117.9 | 114.9 | 0.0003565 | 114.9 | 0.00034743 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7645 | Removed Tree Off Lines Using Hot Sticks Fuses 7645 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.00034743 | 3.024e-06 | 2016 | 2015-10-18 | C | 1 | 0.00034743 | 3.0238e-06
7740556 | 2015-10-18 18:19 | 2015-10-18 19:30 | 71.05 | 48 | 3410.4 | 71.05 | 68.05 | 0.010312 | 3266.4 | 0.0098768 | 0.00014514 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7778 | DDO out as per Neville Pope Replaced set of drop out fuses | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0098768 | 0.00014514 | 2016 | 2015-10-18 | C | 48 | 0.0098768 | 0.00014514
7740865 | 2015-10-18 16:52 | 2015-10-18 20:18 | 206.35 | 1 | 206.35 | 206.35 | 203.35 | 0.00062395 | 203.35 | 0.00061488 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 818746 | Also check 7741500. Replaced 2x 3A HV fuse. Due to lines tangled in the trees. Nothing else repaired or replaced. All other assets up to Powerco standard | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.00061488 | 3.024e-06 | 2016 | 2015-10-18 | C | 1 | 0.00061488 | 3.0238e-06
7740920 | 2015-10-18 16:59 | 2015-10-19 01:00 | 480.3833 | 83 | 3897.9667 | 46.9635 | 43.9635 | 0.011787 | 3648.9667 | 0.011034 | 0.00025097 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7088 | Repaired jumper on HV fuses 7088 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.011034 | 0.00025097 | 2016 | 2015-10-18 | C | 83 | 0.011034 | 0.00025097
7740952 | 2015-10-18 17:09 | 2015-10-18 18:40 | 90.1833 | 5 | 450.9167 | 90.1833 | 87.1833 | 0.0013635 | 435.9167 | 0.0013181 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 7655 | NDR 37928. Isolated beyond Fuses 7655. Removed tree at pole 826508 and pulled up lines. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0013181 | 1.5119e-05 | 2016 | 2015-10-18 | C | 5 | 0.0013181 | 1.5119e-05
7741068 | 2015-10-18 17:30 | 2015-10-19 11:55 | 1105.1833 | 17 | 18788.1167 | 1105.1833 | 1102.1833 | 0.056811 | 18737.1167 | 0.056657 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R48 | Please also check 7741076 and 7745057 Reload Reliven at Fuses R48 2 x 10 Amp fuses Wind | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.056657 | 5.1404e-05 | 2016 | 2015-10-18 | C | 17 | 0.056657 | 5.1404e-05
7741543 | 2015-10-18 18:41 | 2015-10-19 00:06 | 324.45 | 1 | 324.45 | 324.45 | 321.45 | 0.00098106 | 321.45 | 0.00097199 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T11 | Replaced 2X hV fuses | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.00097199 | 3.024e-06 | 2016 | 2015-10-18 | C | 1 | 0.00097199 | 3.0238e-06
7743538 | 2015-10-18 19:55 | 2015-10-18 22:03 | 128.65 | 3 | 385.95 | 128.65 | 125.65 | 0.001167 | 376.95 | 0.0011398 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2236 | Replaced 2X hV Fuses | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0011398 | 9.071e-06 | 2016 | 2015-10-18 | C | 3 | 0.0011398 | 9.0713e-06
7745057 | 2015-10-18 17:31 | 2015-10-19 12:14 | 1122.8167 | 2 | 2245.6333 | 1122.8167 | 1119.8167 | 0.0067903 | 2239.6333 | 0.0067721 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R48 | Reload Reliven at Fuses R48. 2 x 10 Amp fuses.Wind | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.0067721 | 6.048e-06 | 2016 | 2015-10-18 | C | 2 | 0.0067721 | 6.0475e-06
7745197 | 2015-10-18 18:45 | 2015-10-19 13:40 | 1135.1333 | 842 | 179270.05 | 212.9098 | 209.9098 | 0.54207 | 176744.05 | 0.53443 | 0.002546 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-18 | c | 0.53443 | 0.002546 | 2016 | 2015-10-18 | C | 842 | 0.53443 | 0.002546
7746008 | 2015-10-19 04:41 | 2015-10-19 06:12 | 90.55 | 75 | 6791.25 | 90.55 | 87.55 | 0.020535 | 6566.25 | 0.019855 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 820085 | Report from Fire Comms of Car vs Pole. Pole 820085 replaced. NDR 23270 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.019855 | 0.00022678 | 2016 | 2015-10-19 | C | 75 | 0.019855 | 0.00022678
7746319 | 2015-10-19 06:02 | 2015-10-19 08:02 | 120 | 1049 | 25761.7 | 24.5583 | 21.5583 | 0.077897 | 22614.7 | 0.068381 | 0.0031719 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762492 | WAE CB U20 tripped L/O. CB 4989 opened & back feed VS 8801 closed tripping donor CB 6224 (WAE U40). VS 8801 opened WAE U40 returned to service. Feeder sectionalised with fault isolated to between isolation points Recloser links 4838 & ABS 5300 (back feed | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.068381 | 0.0031719 | 2016 | 2015-10-19 | C | 1049 | 0.068381 | 0.0031719
7748262 | 2015-10-19 11:17 | 2015-10-19 15:29 | 251.7333 | 17 | 4279.4667 | 251.7333 | 248.7333 | 0.01294 | 4228.4667 | 0.012786 | 5.1404e-05 | NAPA ID:13927 TP_MANGAMAIRE GXP > ALFREDTON SUB > IHURAUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P31341 | To replace burnt off softwood pole P31341. Work Location: Bartons Line, Ihuraua. Work Order 30007224 | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-10-19 | b | 0.0063929 | 2.5702e-05 | 2016 | 2015-10-19 | B | 17 | 0.012786 | 5.1404e-05
7749052 | 2015-11-16 11:51 | 2015-11-16 13:41 | 110 | 12 | 44 | 3.6667 | 0.66667 | 0.00013305 | 0 | 0 | 3.6285e-05 | NAPA ID:13743 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X2167 | commission Regulator 4462/2, and check voltages on transformers from the regulator to the end of the line, tap down as required. Works location: Parewanui Rd, Bulls. WO 30010487. Only Transformers X2170, X2455 need tapping. X2263 outage due to opening FAB | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-11-16 | b | 0 | 1.8143e-05 | 2016 | 2015-11-16 | B | 12 | 0 | 3.6285e-05
7750176 | 2015-10-19 11:00 | 2015-10-19 12:15 | 74.85 | 1 | 74.85 | 74.85 | 71.85 | 0.00022633 | 71.85 | 0.00021726 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4709 | Reload Reliven at Fuses 4709 DDO's that feed Transformer X2500 not shown on SCADA. 2 x 3A Fuses Unknown Cause | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.00021726 | 3.024e-06 | 2016 | 2015-10-19 | C | 1 | 0.00021726 | 3.0238e-06
7750235 | 2015-10-19 11:12 | 2015-10-19 12:07 | 54.9667 | 15 | 824.5 | 54.9667 | 51.9667 | 0.0024931 | 779.5 | 0.002357 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838338 | 1 X 3m Crossarm 3 X H/T Insulators | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.002357 | 4.5356e-05 | 2016 | 2015-10-19 | C | 15 | 0.002357 | 4.5356e-05
7750630 | 2015-10-28 09:05 | 2015-10-28 15:39 | 393.6333 | 35 | 7485.7167 | 213.8776 | 210.8776 | 0.022635 | 7380.7167 | 0.022318 | 0.00010583 | NAPA ID:13956 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2326 | AP1: To replace the 11kV Pin arm & the 11kV Fuse Arm. AP2: To replace the 400V arms & install a 400V Fuse disconnector. Works location: Scherer Rd, Matamata. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-10-28 | b | 0.011159 | 5.2916e-05 | 2016 | 2015-10-28 | B | 35 | 0.022318 | 0.00010583
7750738 | 2015-10-19 12:18 | 2015-10-19 13:23 | 64.6667 | 118 | 2505.1 | 21.2297 | 18.2297 | 0.0075748 | 2151.1 | 0.0065044 | 0.0003568 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 9941 | Recloser 1 trip, Reclosed.Sectionaliser Trip OC Ph B and C. Line patrolled and branch located on line at pole M13432. NDR 55555 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-19 | c | 0.0065044 | 0.0003568 | 2016 | 2015-10-19 | C | 118 | 0.0065044 | 0.0003568
7750939 | 2015-11-17 08:45 | 2015-11-17 14:40 | 355 | 47 | 16685 | 355 | 352 | 0.050451 | 16544 | 0.050025 | 0.00014212 | NAPA ID:13364 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 239 | Erect pole and change wire over. Works location: Otuarei Rd, Taihape. WO 30006838 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-17 | b | 0.025013 | 7.1058e-05 | 2016 | 2015-11-17 | B | 47 | 0.050025 | 0.00014212
7750992 | 2015-11-24 08:56 | 2015-11-24 16:01 | 424.6333 | 47 | 19957.7667 | 424.6333 | 421.6333 | 0.060348 | 19816.7667 | 0.059921 | 0.00014212 | NAPA ID:13370 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 238, X1207 | Erect pole and change wire over. Work Location: Otuarei Road, Taihape. Work Order 30006838. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-24 | b | 0.029961 | 7.1058e-05 | 2016 | 2015-11-24 | B | 47 | 0.059921 | 0.00014212
7751772 | 2015-10-19 12:29 | 2015-10-19 13:33 | 63.3333 | 229 | 14485.75 | 63.2566 | 60.2566 | 0.043801 | 13798.75 | 0.041724 | 0.00069244 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 766242 | CB7 tripped O/C. Line patrolled and tree on line ,ocated at pole 766242. Removed with Hot sticks. | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.041724 | 0.00069244 | 2016 | 2015-10-19 | C | 229 | 0.041724 | 0.00069244
7752700 | 2015-11-17 08:34 | 2015-11-17 12:16 | 221.9833 | 56 | 12421.6167 | 221.8146 | 218.8146 | 0.03756 | 12253.6167 | 0.037052 | 0.00016933 | NAPA ID:13390 TP_MASTERTON GXP > AWATOITOI SUB | 33 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S103 | ABS maintenance. Works location: Awatoitoi. WO 10154324 | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-11-17 | b | 0.018526 | 8.4665e-05 | 2016 | 2015-11-17 | B | 56 | 0.037052 | 0.00016933
7752895 | 2015-10-19 14:19 | 2015-10-19 15:36 | 76.5167 | 3 | 75.3167 | 25.1056 | 22.1056 | 0.00022774 | 66.3167 | 0.00020053 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2132 | Outage was on the child transformer, farm is fed from both. Replace 2 x 2 A Fuses | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.00020053 | 9.071e-06 | 2016 | 2015-10-19 | C | 3 | 0.00020053 | 9.0713e-06
7752953 | 2015-10-19 14:29 | 2015-10-19 16:25 | 115.9167 | 6 | 695.5 | 115.9167 | 112.9167 | 0.002103 | 677.5 | 0.0020486 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T357 | 2.32pm - advise smc. Replacer 2 x 3A fuse | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.0020486 | 1.8143e-05 | 2016 | 2015-10-19 | C | 6 | 0.0020486 | 1.8143e-05
7753168 | 2015-10-19 15:00 | 2015-10-19 19:46 | 286 | 149 | 17861.8 | 119.8779 | 116.8779 | 0.05401 | 17414.8 | 0.052658 | 0.00045054 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783715 | Found LV tangled with 11kv and 11kv lines down Repaired 11kv lines LV lines cut away and made safe until traffic management can be arranged . Faultman discussed with property owner and the supply is to an implement shed which he is happy for the supply to | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-10-19 | c | 0.052658 | 0.00045054 | 2016 | 2015-10-19 | C | 149 | 0.052658 | 0.00045054
7753928 | 2015-10-19 15:36 | 2015-10-19 18:47 | 191.3667 | 121 | 8914.95 | 73.6773 | 70.6773 | 0.026957 | 8551.95 | 0.025859 | 0.00036588 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | POO316 | Floating Conductor at Pole P00316. Replaced insulator and rebound. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.025859 | 0.00036587 | 2016 | 2015-10-19 | C | 121 | 0.025859 | 0.00036588
7755002 | 2015-10-19 16:19 | 2015-10-19 20:00 | 220.55 | 2 | 441.1 | 220.55 | 217.55 | 0.0013338 | 435.1 | 0.0013156 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | tc5129 | Reports of no power. Found 2 x blown fuses at TC5129. Isolated at TC5129 to remove tree. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-10-19 | c | 0.0013156 | 6.048e-06 | 2016 | 2015-10-19 | C | 2 | 0.0013156 | 6.0475e-06
7755638 | 2015-10-19 18:23 | 2015-10-19 18:59 | 35.9167 | 30 | 1077.5 | 35.9167 | 32.9167 | 0.0032581 | 987.5 | 0.002986 | 9.0713e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD3-035 | 2 x 15amp ht fuses O/H Wind | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-10-19 | c | 0.002986 | 9.0713e-05 | 2016 | 2015-10-19 | C | 30 | 0.002986 | 9.0713e-05
7755706 | 2015-10-19 18:46 | 2015-10-19 22:21 | 215.4833 | 1 | 215.4833 | 215.4833 | 212.4833 | 0.00065157 | 212.4833 | 0.0006425 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V8 | Replaced 2X 10a HV fuses @ V8 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.0006425 | 3.024e-06 | 2016 | 2015-10-19 | C | 1 | 0.0006425 | 3.0238e-06
7756832 | 2015-10-19 19:58 | 2015-10-19 21:41 | 103 | 1228 | 59289 | 48.2809 | 45.2809 | 0.17928 | 55605 | 0.16814 | 0.0037132 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | AON CB 42 Tripped OCB. Lines Sectionalised and Patrolled. No Fault found. High winds in area at time. | F1,F2,F3 | AONGATETE42-KAURI POINT 33KV | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-19 | c | 0.16814 | 0.0037132 | 2016 | 2015-10-19 | C | 1228 | 0.16814 | 0.0037132
7759510 | 2015-10-19 23:33 | 2015-10-19 23:37 | 4.8 | 366 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0011067 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | B&C phase O/C | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0 | 0.0011067 | 2016 | 2015-10-19 | C | 366 | 0 | 0.0011067
7762130 | 2015-10-20 04:09 | 2015-10-20 13:38 | 569 | 99 | 44072 | 445.1717 | 442.1717 | 0.13326 | 43775 | 0.13237 | 0.00029935 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | I12509 | PKO CB6 Car verse pole. I12509. Isolated between 658, 661 & IC2137. All damaged equipment replaced, all service restored. Materials 1 x pole, 1 x Transformer, 1 x H/V arm Complete, 3 x fuseholders H/V, 3 x H/V fuses 6A, 2 x L/V arms complete. NDR 48182 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-20 | c | 0.13237 | 0.00029935 | 2016 | 2015-10-20 | C | 99 | 0.13237 | 0.00029935
7763472 | 2015-10-19 23:13 | 2015-10-20 12:11 | 778.3333 | 368 | 24497.3333 | 66.5688 | 63.5688 | 0.074074 | 23393.3333 | 0.070736 | 0.0011127 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747464 | 12.52pm Wes called to advise that he has completed this job. Spoken to control line down and found broken insulator. replaced 1 x HV insulator and rehung line 2 KV Sleeves. 1m HV conductor Outage recorded in OMS 7763472 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-10-19 | c | 0.070736 | 0.0011127 | 2016 | 2015-10-19 | C | 368 | 0.070736 | 0.0011127
7763721 | 2015-10-20 08:26 | 2015-10-20 11:45 | 198.9333 | 1 | 198.9333 | 198.9333 | 195.9333 | 0.00060153 | 195.9333 | 0.00059246 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7 | Reload Reliven 2 x 2A Fuses. Wind Clash | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-10-20 | c | 0.00059246 | 3.024e-06 | 2016 | 2015-10-20 | C | 1 | 0.00059246 | 3.0238e-06
7763746 | 2015-11-08 09:38 | 2015-11-08 14:57 | 319.2167 | 10 | 3192.1667 | 319.2167 | 316.2167 | 0.0096523 | 3162.1667 | 0.0095616 | 3.0238e-05 | NAPA ID:13152 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD5-035 | To replace TD5-035 tank transformer with a new pad mount (existing has a leak). Works location: Welcome Bay Rd, Te Puke. WO 30000449 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-08 | b | 0.0047808 | 1.5119e-05 | 2016 | 2015-11-08 | B | 10 | 0.0095616 | 3.0238e-05
7764001 | 2015-10-20 09:02 | 2015-10-20 16:55 | 473 | 525 | 27703.5333 | 52.7686 | 49.7686 | 0.083769 | 26128.5333 | 0.079006 | 0.0015875 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M13020 | Event #F1940935. PUT CB8 tripped O/C, L/O. Report of digger at Pacific Pine hitting pole M13020. Isolation at Sw/Gear 9072 ( spur line ) CB 8 returned to service, all repairs completed, all service restored. NDR No 048063. Materials 1 x pole, 3 x H/V arms | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-20 | c | 0.079006 | 0.0015875 | 2016 | 2015-10-20 | C | 525 | 0.079006 | 0.0015875
7765655 | 2015-10-20 14:57 | 2015-10-20 16:31 | 93.6333 | 7 | 655.4333 | 93.6333 | 90.6333 | 0.0019819 | 634.4333 | 0.0019184 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06672 | 2R - Chopper Patrol Found 11kV floater Pongaroa CB 1 Beyond .Fuses V8. Isolation required from Fuses V8 to repair va floating conductor. 2 Insulators required, rebound / relivened OK. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-20 | c | 0.0019184 | 2.1166e-05 | 2016 | 2015-10-20 | C | 7 | 0.0019184 | 2.1166e-05
7765691 | 2015-11-10 09:41 | 2015-11-10 14:51 | 310 | 2 | 620 | 310 | 307 | 0.0018747 | 614 | 0.0018566 | 6.0475e-06 | NAPA ID:13693 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5510 | Replace Ground mount Transformer TC5510 (30-11-1) | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-10 | b | 0.00092829 | 3.024e-06 | 2016 | 2015-11-10 | B | 2 | 0.0018566 | 6.0475e-06
7765755 | 2015-11-12 09:16 | 2015-11-12 11:17 | 121.0667 | 106 | 12805.4667 | 120.8063 | 117.8063 | 0.038721 | 12487.4667 | 0.037759 | 0.00032052 | NAPA ID:13965 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 786436 | Outage to replace pole 786436 in large span as existing pole has damage to top of pole , exposed steel , no concrete holding at arm level. Works location: Napier Taihape Rd, Moawhango. WO 30015873 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-12 | b | 0.01888 | 0.00016026 | 2016 | 2015-11-12 | B | 106 | 0.037759 | 0.00032052
7766792 | 2015-11-11 09:10 | 2015-11-11 15:01 | 351 | 23 | 8073 | 351 | 348 | 0.024411 | 8004 | 0.024202 | 6.9546e-05 | NAPA ID:13523 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227722 | Reconductor HV Feeder wires. Replace poles and arms. Works location: Otamarakau Valley Rd. WO 10146562 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-11 | b | 0.012101 | 3.4773e-05 | 2016 | 2015-11-11 | B | 23 | 0.024202 | 6.9546e-05
7767200 | 2015-10-20 17:13 | 2015-10-21 12:40 | 1167.15 | 3 | 3501.45 | 1167.15 | 1164.15 | 0.010588 | 3492.45 | 0.01056 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 858329 | Ditch - North Power - 021 497 372. Check for safety - Lines down across the road holding up traffic. Advised hub and control. Also received call from NZ Fire , re this required eta 09 486 7948. Advised by HUB eta 45 minutes to one hour, NZ Fire Advised. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-10-20 | c | 0.01056 | 9.071e-06 | 2016 | 2015-10-20 | C | 3 | 0.01056 | 9.0713e-06
7769253 | 2015-10-20 18:05 | 2015-10-20 20:00 | 114.7833 | 11 | 1262.6167 | 114.7833 | 111.7833 | 0.0038179 | 1229.6167 | 0.0037181 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H47 | Replaced 2x 10Amp Links | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-10-20 | c | 0.0037181 | 3.3261e-05 | 2016 | 2015-10-20 | C | 11 | 0.0037181 | 3.3261e-05
7769813 | 2015-10-21 01:00 | 2015-10-21 03:00 | 119.9167 | 10 | 1199.1667 | 119.9167 | 116.9167 | 0.003626 | 1169.1667 | 0.0035353 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sd5-036 | replaced 2 x 8amp fuses at SD5-036 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-10-21 | c | 0.0035353 | 3.0238e-05 | 2016 | 2015-10-21 | C | 10 | 0.0035353 | 3.0238e-05
7774458 | 2015-10-21 06:16 | 2015-10-21 12:19 | 363.1167 | 5120 | 214647.75 | 41.9234 | 38.9234 | 0.64904 | 199287.75 | 0.6026 | 0.015482 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7778036 | Piako CB 3162 and CB6 tripped. LOS Walton, Waharoa and Browne Street Substations. Cause was found to be a blown lightning arrestor at Pole 7778036 on Kereone feeder. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-21 | c | 0.6026 | 0.015482 | 2016 | 2015-10-21 | C | 5120 | 0.6026 | 0.015482
7776278 | 2015-11-08 07:22 | 2015-11-08 14:43 | 441 | 2 | 882 | 441 | 438 | 0.002667 | 876 | 0.0026488 | 6.0475e-06 | NAPA ID:13787 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S195 | Replace defective 2 pole structure 831458/831459, which is leaning into the road badly and needs replacing A.S.A.P and also 33kv pole 832554. Works location: Ngaumutawwa Rd, Masterton. WO 30003449 | F2 | NGAUMUTAWA RD | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-08 | b | 0.0013244 | 3.024e-06 | 2016 | 2015-11-08 | B | 2 | 0.0026488 | 6.0475e-06
7776379 | 2015-10-21 08:24 | 2015-10-21 09:46 | 82.0833 | 2 | 164.1667 | 82.0833 | 79.0833 | 0.0004964 | 158.1667 | 0.00047826 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1597 | Replace 2 x 3 A fuse | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.00047826 | 6.048e-06 | 2016 | 2015-10-21 | C | 2 | 0.00047826 | 6.0475e-06
7776873 | 2015-10-30 09:32 | 2015-10-30 15:04 | 332.0667 | 37 | 12286.4667 | 332.0667 | 329.0667 | 0.037151 | 12175.4667 | 0.036816 | 0.00011188 | NAPA ID:13909 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 840280 | AP replace cracked 11Kv Abs WH890 pole - LLP close LLB @ pole 840280. Works location: South Rd, Hawera. WO 30011358 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-30 | b | 0.018408 | 5.594e-05 | 2016 | 2015-10-30 | B | 37 | 0.036816 | 0.00011188
7777084 | 2015-10-21 06:30 | 2015-10-21 15:15 | 525 | 7 | 3675 | 525 | 522 | 0.011112 | 3654 | 0.011049 | 2.1166e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4772 | 11kV Transformer TC4772 Replaced under Own Isolation. off 06:30 on 15:159.31am | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-10-21 | c | 0.011049 | 2.1166e-05 | 2016 | 2015-10-21 | C | 7 | 0.011049 | 2.1166e-05
7777147 | 2015-11-09 09:00 | 2015-11-09 13:21 | 261 | 13 | 3393 | 261 | 258 | 0.01026 | 3354 | 0.010142 | 3.9309e-05 | NAPA ID:13303 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F0123 | To reconductor 11kV lines between Pole # F0123 and ABS IC823. Works location: Puketutu Rd, Matamata. WO 30002534 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-09 | b | 0.0050708 | 1.9654e-05 | 2016 | 2015-11-09 | B | 13 | 0.010142 | 3.9309e-05
7777875 | 2015-10-21 13:50 | 2015-10-21 19:25 | 335 | 34 | 3518 | 103.4706 | 100.4706 | 0.010638 | 3416 | 0.010329 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P18603 | ndr # n300115. treescape on site now clearing the tree. FM worked through Control, the job is still open. After-hours FM to attend to re-connect the power. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.010329 | 0.00010281 | 2016 | 2015-10-21 | C | 34 | 0.010329 | 0.00010281
7777955 | 2015-10-21 11:28 | 2015-10-21 13:30 | 122.0667 | 19 | 2319.2667 | 122.0667 | 119.0667 | 0.0070129 | 2262.2667 | 0.0068406 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R48 | Reload Reliven at Fuses R48. 2 x 10 A Fuses. No cause found | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.0068406 | 5.7451e-05 | 2016 | 2015-10-21 | C | 19 | 0.0068406 | 5.7451e-05
7778040 | 2015-11-12 09:09 | 2015-11-12 15:23 | 373.8167 | 5 | 1785.6333 | 357.1267 | 354.1267 | 0.0053993 | 1770.6333 | 0.005354 | 1.5119e-05 | NAPA ID:13541 TP_TE MATAI GXP > PONGAKAWA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227843 | Reconductor HV Feeder wires. Replace poles and arms. Works location: Otamarakau Valley Rd. WO 10146562 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-12 | b | 0.002677 | 7.559e-06 | 2016 | 2015-11-12 | B | 5 | 0.005354 | 1.5119e-05
7780625 | 2015-10-21 17:09 | 2015-10-22 13:15 | 1205.9333 | 178 | 84197.65 | 473.0205 | 470.0205 | 0.25459 | 83663.65 | 0.25298 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P04175 | This fault affected Pongoroa CB4 & Alfredton I23. Fault Isolated between ABS V73 & V75. Too dangerous to continue due to wind & terrain. To be patrolled tomorrow. Faulty recloser I23 temporarily bypassed & HV fuse links installed at I24 so as to liven I23 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.25298 | 0.00053823 | 2016 | 2015-10-21 | C | 178 | 0.25298 | 0.00053823
7781530 | 2015-10-21 17:52 | 2015-10-22 12:10 | 1098.4667 | 231 | 109112.8667 | 472.3501 | 469.3501 | 0.32993 | 108419.8667 | 0.32784 | 0.00069849 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P29104 | Andrew Tahura repaired floating conductor at Pole P29778. Used 1x Binder. Chris Naylor repaired floating conductor at Pole P10315. Used 1x Ali binder & 2x 10Amp HV Links. Four Faults Within this Job. 1 - 1 x Binder. 2 - 1 x Binder, 2 x 10 A fuse. 3 - 1 x | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.32784 | 0.00069849 | 2016 | 2015-10-21 | C | 231 | 0.32784 | 0.00069849
7782156 | 2015-10-22 09:13 | 2015-10-22 10:00 | 47 | 35 | 1645 | 47 | 44 | 0.0049741 | 1540 | 0.0046566 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44372 | Fuses R54 opened and tagged. Repair Floating HV. 1 x Binder. 2 x 10 Amp Fuse. 1 x Candle. 12.42am svshub advise that this job will be done first thing tomorrow as tararua FM on stand down and feeder faults | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.0046566 | 0.00010583 | 2016 | 2015-10-22 | C | 35 | 0.0046566 | 0.00010583
7782657 | 2015-10-21 18:11 | 2015-10-21 19:31 | 79.8 | 60 | 4788 | 79.8 | 76.8 | 0.014478 | 4608 | 0.013933 | 0.00018143 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | RS C641 A/R | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.013933 | 0.00018143 | 2016 | 2015-10-21 | C | 60 | 0.013933 | 0.00018143
7783247 | 2015-10-21 19:40 | 2015-10-22 00:20 | 280.0667 | 176 | 44537.45 | 253.0537 | 250.0537 | 0.13467 | 44009.45 | 0.13307 | 0.00053218 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 811083 | CB C642 tripped and L/O. Floating conductor repaired at pole 811083. 3 x Ali binders | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.13307 | 0.00053218 | 2016 | 2015-10-21 | C | 176 | 0.13307 | 0.00053218
7787090 | 2015-10-21 20:43 | 2015-10-21 22:19 | 95.9333 | 590 | 48426.2 | 82.0783 | 79.0783 | 0.14643 | 46656.2 | 0.14108 | 0.001784 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB C928 A/R, L/O. Sectionalised & patrolled with no fault found | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.14108 | 0.001784 | 2016 | 2015-10-21 | C | 590 | 0.14108 | 0.001784
7789421 | 2015-10-21 21:05 | 2015-10-22 14:25 | 1040.45 | 4 | 4161.8 | 1040.45 | 1037.45 | 0.012584 | 4149.8 | 0.012548 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V53 | Reload Reliven at Fuses V53. 2 x 6A. Wind | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.012548 | 1.2095e-05 | 2016 | 2015-10-21 | C | 4 | 0.012548 | 1.2095e-05
7789864 | 2015-10-21 21:37 | 2015-10-21 22:26 | 48.9667 | 2 | 48.9667 | 24.4833 | 21.4833 | 0.00014806 | 42.9667 | 0.00012992 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1077 | 2x10Amp HV Fuses Blown at FC1077 Unknown cause, line Patrolled | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-10-21 | c | 0.00012992 | 6.048e-06 | 2016 | 2015-10-21 | C | 2 | 0.00012992 | 6.0475e-06
7790033 | 2015-10-21 23:02 | 2015-10-21 23:08 | 6 | 61 | 366 | 6 | 3 | 0.0011067 | 183 | 0.00055335 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Faultmen found non scadarised Sectionaliser C641/2 tripped on arrival. Closed C641/2. No fault found | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-21 | c | 0.00055335 | 0.00018445 | 2016 | 2015-10-21 | C | 61 | 0.00055335 | 0.00018445
7791412 | 2015-10-22 01:00 | 2015-10-22 05:37 | 276.8 | 1721 | 128624.1 | 74.738 | 71.738 | 0.38893 | 123461.1 | 0.37332 | 0.0052039 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 700791 | Car vs Pole at Pole 700791. 11m Pole, 2 x 2m Crossarms, 4 x Arm Braces, 3 x HV Insulators, 5 x LV Insulators, 2 Spans of conductor. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.37332 | 0.0052039 | 2016 | 2015-10-22 | C | 1721 | 0.37332 | 0.0052039
7799342 | 2015-10-22 03:02 | 2015-10-22 06:31 | 209.2 | 1142 | 17753.0667 | 15.5456 | 12.5456 | 0.053681 | 14327.0667 | 0.043322 | 0.0034531 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755087 | Lines arcing. Fire brigade attending. Repaired floating HV conductor using 1x Ali binder. LV line still needs to be repaired. pole # 855087. re-strained 1 x conductor. used 1 x full tension hony sleeve, single phase dead end and shrink. cause: 11 kv jumpe | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.043322 | 0.0034531 | 2016 | 2015-10-22 | C | 1142 | 0.043322 | 0.0034531
7799595 | 2015-10-22 06:27 | 2015-10-22 09:11 | 163.5833 | 100 | 16357.75 | 163.5775 | 160.5775 | 0.049462 | 16057.75 | 0.048555 | 0.00030238 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P37271 | plz check if oms 7789877 - 783 State Highway 1 part power related? Lines down at Pole P37271. Nick Brown attended. USED: 1 x Squirrel Clamp & 1 x G-clamp on HV pole | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.048555 | 0.00030238 | 2016 | 2015-10-22 | C | 100 | 0.048555 | 0.00030238
7800769 | 2015-10-22 05:27 | 2015-10-22 07:44 | 136.85 | 97 | 13274.45 | 136.85 | 133.85 | 0.040139 | 12983.45 | 0.039259 | 0.0002933 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 785970 | RS 4692 tripped and L/O. Patrol found floating conductor at Pole 785970. 3 x binder used. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.039259 | 0.0002933 | 2016 | 2015-10-22 | C | 97 | 0.039259 | 0.0002933
7800964 | 2015-10-22 05:49 | 2015-10-22 10:15 | 266.1167 | 11 | 1503.45 | 136.6773 | 133.6773 | 0.0045461 | 1470.45 | 0.0044463 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7257 | Reload Reliven at Fuses 7257. Suspect ICP error at T714 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.0044463 | 3.3261e-05 | 2016 | 2015-10-22 | C | 11 | 0.0044463 | 3.3261e-05
7801919 | 2015-10-22 07:08 | 2015-10-22 13:16 | 367.5833 | 1 | 367.5833 | 367.5833 | 364.5833 | 0.0011115 | 364.5833 | 0.0011024 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7780016 | 2x 6amp ddo fuses at B12 cause wind - worked through control - spoke to Markus and he will complete job | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.0011024 | 3.024e-06 | 2016 | 2015-10-22 | C | 1 | 0.0011024 | 3.0238e-06
7802667 | 2015-10-22 08:17 | 2015-10-22 08:46 | 29 | 286 | 8294 | 29 | 26 | 0.025079 | 7436 | 0.022485 | 0.0008648 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13020 | Emergency isolation to repair jumper at Pole P13020. Single phase from 0704 till 0846. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-22 | c | 0.022485 | 0.0008648 | 2016 | 2015-10-22 | C | 286 | 0.022485 | 0.0008648
7803965 | 2015-11-10 09:42 | 2015-11-10 15:45 | 362.9167 | 6 | 2177.5 | 362.9167 | 359.9167 | 0.0065842 | 2159.5 | 0.0065298 | 1.8143e-05 | NAPA ID:13041 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole E12493 | To replace 11kV conductor between Pole # E12477 and E12492. Works location: Totmans Rd, Hinuera. WO 30002570 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-10 | b | 0.0032649 | 9.071e-06 | 2016 | 2015-11-10 | B | 6 | 0.0065298 | 1.8143e-05
7804011 | 2015-11-12 09:15 | 2015-11-12 15:41 | 386 | 23 | 8878 | 386 | 383 | 0.026845 | 8809 | 0.026636 | 6.9546e-05 | NAPA ID:12808 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-030 | Replace poles, hardware and conductor. Remove SD5-059. Works location: Kaiate Falls Rd. WO 30003844 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-12 | b | 0.013318 | 3.4773e-05 | 2016 | 2015-11-12 | B | 23 | 0.026636 | 6.9546e-05
7805370 | 2015-10-22 10:23 | 2015-10-22 15:01 | 278.4 | 201 | 10619.7 | 52.8343 | 49.8343 | 0.032111 | 10016.7 | 0.030288 | 0.00060778 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 223342 | Recloser RP10 Trip. E/F. L/O. Fuses SE5-143 found blown. Fuses opened and recloser restored.. Tree found through the lines at Pole 223342. Lines repaired. 20mtrs Name, 8 sleeves and 3 HV DDO fuses used. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-10-22 | c | 0.030288 | 0.00060778 | 2016 | 2015-10-22 | C | 201 | 0.030288 | 0.00060778
7807189 | 2015-10-22 11:19 | 2015-10-22 15:21 | 242.4 | 76 | 11445.5 | 150.5987 | 147.5987 | 0.034608 | 11217.5 | 0.033919 | 0.00022981 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7417 | 7417 Tripped Ph A O/C and E/F. Not Patrolled | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.033919 | 0.00022981 | 2016 | 2015-10-22 | C | 76 | 0.033919 | 0.00022981
7807888 | 2015-10-22 11:56 | 2015-10-22 20:43 | 526.6833 | 34 | 17907.2333 | 526.6833 | 523.6833 | 0.054147 | 17805.2333 | 0.053839 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 4001 | 4001 Tripped PH A B & C OC and EF. Van hit train, bounced off train at hit 11kv pole # 807605. ndr # n200019. 2 other poles may need to be repaired but it depends on what work is being done on pole # 807605. it is safe for now. Pole replaced. Isolation a | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.053839 | 0.00010281 | 2016 | 2015-10-22 | C | 34 | 0.053839 | 0.00010281
7808181 | 2015-11-20 09:30 | 2015-11-20 11:30 | 120 | 37 | 4440 | 120 | 117 | 0.013425 | 4329 | 0.01309 | 0.00011188 | NAPA ID:13608 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I39 | To replace two larch poles and hardware. Works location: Mangaone Valley Rd. WO 10162458 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-11-20 | b | 0.0065449 | 5.594e-05 | 2016 | 2015-11-20 | B | 37 | 0.01309 | 0.00011188
7813090 | 2015-11-11 10:24 | 2015-11-11 13:13 | 168.9333 | 25 | 4223.3333 | 168.9333 | 165.9333 | 0.01277 | 4148.3333 | 0.012544 | 7.5594e-05 | NAPA ID:13419 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 4957 | Replace 33kv pole 737437 + Run 1 span 33Kv Fluorine conductor over 11Kv circuit. Works location: Gorden Rd. WO 30010304 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-11 | b | 0.0062718 | 3.7797e-05 | 2016 | 2015-11-11 | B | 25 | 0.012544 | 7.5594e-05
7813098 | 2015-11-20 08:10 | 2015-11-20 14:00 | 350 | 4 | 1384 | 346 | 343 | 0.0041849 | 1372 | 0.0041486 | 1.2095e-05 | NAPA ID:13745 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 95 | Replace C206 with new recloser and pole. Works location: Hwy 2. WO 10159904 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-20 | b | 0.0020743 | 6.048e-06 | 2016 | 2015-11-20 | B | 4 | 0.0041486 | 1.2095e-05
7813414 | 2015-10-22 14:49 | 2015-10-22 22:37 | 468 | 142 | 17715.75 | 124.7588 | 121.7588 | 0.053568 | 17289.75 | 0.05228 | 0.00042937 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 2032 | 2032 tripped on EF. Line Patrolled & sectionalised. Fault isolated to between ABS 085 & 1026. all transformer fuses removed line relivened. Fuses replaced. no fault found. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.05228 | 0.00042937 | 2016 | 2015-10-22 | C | 142 | 0.05228 | 0.00042937
7814398 | 2015-10-22 16:52 | 2015-10-22 19:25 | 153.5833 | 2 | 307.1667 | 153.5833 | 150.5833 | 0.0009288 | 301.1667 | 0.00091066 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7110 | 2x8amp HV Fuses blown at 7110. line patrolled no cause found sucessfully reloaded & livened | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-22 | c | 0.00091066 | 6.048e-06 | 2016 | 2015-10-22 | C | 2 | 0.00091066 | 6.0475e-06
7815559 | 2015-10-23 00:47 | 2015-10-23 02:00 | 73.65 | 818 | 56837.05 | 69.4829 | 66.4829 | 0.17186 | 54383.05 | 0.16444 | 0.0024734 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Unknown | at 00:46 Waihi Beach Sub, CB 1 Beach Rd Feeder, Tripped, Ph A & B O/C, L/O. Faultmen dispatched and investigation began. Feeder Sectionalised & Patrolled. No Fault Found. Unknown Cause. Dion Sanders Attended. | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-10-23 | c | 0.16444 | 0.0024734 | 2016 | 2015-10-23 | C | 818 | 0.16444 | 0.0024734
7817031 | 2015-10-23 01:51 | 2015-10-23 06:06 | 255 | 141 | 13629.2333 | 96.6612 | 93.6612 | 0.041212 | 13206.2333 | 0.039932 | 0.00042635 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1669 | 1 x faulty pin & insulator replaced at pole E1669 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-10-23 | c | 0.039932 | 0.00042635 | 2016 | 2015-10-23 | C | 141 | 0.039932 | 0.00042635
7818039 | 2015-10-23 04:20 | 2015-10-23 07:41 | 201.35 | 142 | 15472.1667 | 108.9589 | 105.9589 | 0.046784 | 15046.1667 | 0.045496 | 0.00042937 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784059 | At pole 784059 Replaced. 1 x HV Insulator. 1 x Binder. 2 X Sleeves. 2m Squirrel Conductor | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-10-23 | c | 0.045496 | 0.00042937 | 2016 | 2015-10-23 | C | 142 | 0.045496 | 0.00042937
7819337 | 2015-11-11 09:45 | 2015-11-11 13:21 | 216.4667 | 85 | 18399.6667 | 216.4667 | 213.4667 | 0.055636 | 18144.6667 | 0.054865 | 0.00025702 | NAPA ID:13754 TP_KINLEITH GXP > MARAETAI ROAD SUB > ARAWA ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1495 | Replacement Side box Bushing on interconnecting Bus section on SDAF unit with switches IC1463, FC2720, IC1450 and FC2743. Works location: Arawa St, Tokoroa. WO 30015600 | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-11-11 | b | 0.027433 | 0.00012851 | 2016 | 2015-11-11 | B | 85 | 0.054865 | 0.00025702
7820292 | 2015-10-23 13:00 | 2015-10-23 14:42 | 102 | 1 | 102 | 102 | 99 | 0.00030842 | 99 | 0.00029935 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TP520 | Faulty transformer requires replacing. 2 r requested. Replace 15kVA transformer | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-10-23 | c | 0.00029935 | 3.024e-06 | 2016 | 2015-10-23 | C | 1 | 0.00029935 | 3.0238e-06
7820409 | 2015-10-23 11:03 | 2015-10-23 14:24 | 201.3833 | 255 | 23183.15 | 90.9143 | 87.9143 | 0.0701 | 22418.15 | 0.067787 | 0.00077106 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | H131 | Recloser H131 Tripped on PH B OC & Reverse EF. Inspector to check LV Instations after 11kV to 400V Line Contact. Replace 10m Squirel, 3 x sleeves, 2 x binders, Line guard & 2 x LV joints | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-10-23 | c | 0.067787 | 0.00077106 | 2016 | 2015-10-23 | C | 255 | 0.067787 | 0.00077106
7821223 | 2015-11-11 14:30 | 2015-11-11 14:45 | 15 | 8 | 120 | 15 | 12 | 0.00036285 | 96 | 0.00029028 | 2.419e-05 | NAPA ID:14112 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1593 | To install a 400V Fuse Disconnector. Works location: Kereone Rd, Morrinsville. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-11 | b | 0.00014514 | 1.2095e-05 | 2016 | 2015-11-11 | B | 8 | 0.00029028 | 2.419e-05
7829265 | 2015-10-23 14:11 | 2015-10-24 10:25 | 1214 | 53 | 5741.4 | 108.3283 | 105.3283 | 0.017361 | 5582.4 | 0.01688 | 0.00016026 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | VEGETATION | VEGETATION - INSIDE ZONE | T3289 | CB C844 tripped no flags, line was isolated at ABS S158 when received a call of tree on the lines, line was isolated at Fuses 7077 to cut tree away, transformer T3289 was isolated and needs to be replaced as has broken bushing on it. Faultman will return | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-10-23 | c | 0.01688 | 0.00016026 | 2016 | 2015-10-23 | C | 53 | 0.01688 | 0.00016026
7833120 | 2015-11-11 10:30 | 2015-11-11 12:45 | 135 | 3 | 405 | 135 | 132 | 0.0012246 | 396 | 0.0011974 | 9.0713e-06 | NAPA ID:13335 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kVa Fuses TC2086 | LLP: To replace the 11kV D.O.Fuse arm & Fuses. AP: To install a 400V Fuse/Disconnector. Manugatapu Road, Morrinsville, Piako. W/O 10147849. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-11-11 | b | 0.00059871 | 4.536e-06 | 2016 | 2015-11-11 | B | 3 | 0.0011974 | 9.0713e-06
7834173 | 2015-10-23 00:33 | 2015-10-23 00:37 | 4 | 93 | 372 | 4 | 1 | 0.0011248 | 93 | 0.00028121 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N21 | 7834180 & 7834207 MAY BE LINKED. Recloser N21 Open. can not open on OMS & Recloser not shown on SCADA so can not do anything with job. Recloser Locally closed & Line patrolled | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-10-23 | c | 0.00028121 | 0.00028121 | 2016 | 2015-10-23 | C | 93 | 0.00028121 | 0.00028121
7834908 | 2015-10-23 23:35 | 2015-10-24 02:23 | 167.75 | 337 | 54054.9167 | 160.4003 | 157.4003 | 0.16345 | 53043.9167 | 0.16039 | 0.001019 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P34076 | Line on crosarm at pole P34076. Recloser L10 not working from SCADA had to be closed Manually on site. Line Patrolled & sectionalized on liven no other fault s found. Isolation at ABS L17 for repair fault. No Back feeds available. Recloser will be looked | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-23 | c | 0.16039 | 0.001019 | 2016 | 2015-10-23 | C | 337 | 0.16039 | 0.001019
7835682 | 2015-10-24 02:57 | 2015-10-24 03:46 | 49.1167 | 809 | 36870.05 | 45.5748 | 42.5748 | 0.11149 | 34443.05 | 0.10415 | 0.0024462 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | S51 | CB S51 Trip E/F Line patrolled & sectionalized no Fault Found. | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-10-24 | c | 0.10415 | 0.0024462 | 2016 | 2015-10-24 | C | 809 | 0.10415 | 0.0024462
7837175 | 2015-10-24 04:06 | 2015-10-24 04:23 | 16.3833 | 154 | 2230.4333 | 14.4833 | 11.4833 | 0.0067443 | 1768.4333 | 0.0053473 | 0.00046566 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | H41 | CB H41 Trip to Lock out E/F Successfully Reclosed after 15 Minutes. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-10-24 | c | 0.0053473 | 0.00046566 | 2016 | 2015-10-24 | C | 154 | 0.0053473 | 0.00046566
7837479 | 2015-10-24 08:09 | 2015-10-24 12:32 | 263.0833 | 1 | 263.0833 | 263.0833 | 260.0833 | 0.0007955 | 260.0833 | 0.00078643 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4184 | Transformer X4184 found to be Faulty, replaced under own AP - Used 1 X 15 kVA 3 Phase Transformer | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-10-24 | c | 0.00078643 | 3.024e-06 | 2016 | 2015-10-24 | C | 1 | 0.00078643 | 3.0238e-06
7839434 | 2015-10-24 21:03 | 2015-10-24 23:04 | 120.65 | 1 | 120.65 | 120.65 | 117.65 | 0.00036482 | 117.65 | 0.00035575 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4612 | Faultman found blown fuses at Fuses 4612. 2 x 3 amp HV fuses replaced | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-24 | c | 0.00035574 | 3.024e-06 | 2016 | 2015-10-24 | C | 1 | 0.00035575 | 3.0238e-06
7839996 | 2015-10-25 05:41 | 2015-10-25 07:43 | 122.4333 | 886 | 72327.65 | 81.6339 | 78.6339 | 0.2187 | 69669.65 | 0.21066 | 0.0026791 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208957 | OMO CB3 RP08 Trip O/C. A/R. OMO CB3 Trip. O/C L/O. GRE CB202 Trip E/F. A/R AON CB82 Trip. BLM CB82 Trip. Isolated between ABS SC2-028, 9695/1, 9695/6. Repaired broken jumper at pole 208957 & relivened | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-10-25 | c | 0.21066 | 0.0026791 | 2016 | 2015-10-25 | C | 886 | 0.21066 | 0.0026791
7840898 | 2015-10-25 06:14 | 2015-10-25 08:03 | 109.45 | 250 | 17647.4 | 70.5896 | 67.5896 | 0.053362 | 16897.4 | 0.051094 | 0.00075594 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 371316 | Feeder Fault Recloser 12080/2. Lines Down at Pole 371316. Used 2x Sleeves. 1m of Conductor. 1 x Binder | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-25 | c | 0.051094 | 0.00075594 | 2016 | 2015-10-25 | C | 250 | 0.051094 | 0.00075594
7842197 | 2015-10-25 03:52 | 2015-10-25 06:45 | 172.9333 | 3 | 518.8 | 172.9333 | 169.9333 | 0.0015687 | 509.8 | 0.0015415 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5344E | Replaced 11kV Transformer 5344E. 1 x 30kVA | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-10-25 | c | 0.0015415 | 9.071e-06 | 2016 | 2015-10-25 | C | 3 | 0.0015415 | 9.0713e-06
7845329 | 2015-10-25 11:42 | 2015-10-25 14:52 | 189.95 | 6 | 1139.7 | 189.95 | 186.95 | 0.0034462 | 1121.7 | 0.0033918 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T33 | 2 Fuses found Blown at Fuses T33 - used 2 x 6amp fuses | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-10-25 | c | 0.0033918 | 1.8143e-05 | 2016 | 2015-10-25 | C | 6 | 0.0033918 | 1.8143e-05
7846452 | 2015-10-25 14:10 | 2015-10-25 15:05 | 55.1167 | 70 | 3858.1667 | 55.1167 | 52.1167 | 0.011666 | 3648.1667 | 0.011031 | 0.00021166 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | l12381 | Burnt out DDO at TC5104. Isolated between ABS IC644 & CB 6 Replace DDO unit relivened. 1 DDO unit. 1 20amp fuse | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-25 | c | 0.011031 | 0.00021166 | 2016 | 2015-10-25 | C | 70 | 0.011031 | 0.00021166
7847501 | 2015-10-25 12:15 | 2015-10-25 12:56 | 41 | 20 | 820 | 41 | 38 | 0.0024795 | 760 | 0.0022981 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Unknown | Sparking and smoking pole Isolated at ABS IP613 Removed tree from line | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-10-25 | c | 0.0022981 | 6.0475e-05 | 2016 | 2015-10-25 | C | 20 | 0.0022981 | 6.0475e-05
7848790 | 2015-10-26 05:58 | 2015-10-26 07:36 | 97.7 | 1 | 97.7 | 97.7 | 94.7 | 0.00029542 | 94.7 | 0.00028635 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP852 | Replaced 2 x 6 amp fuse | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-10-26 | c | 0.00028635 | 3.024e-06 | 2016 | 2015-10-26 | C | 1 | 0.00028635 | 3.0238e-06
7849990 | 2015-10-26 14:54 | 2015-10-26 17:00 | 125.8833 | 171 | 15421.55 | 90.1845 | 87.1845 | 0.046631 | 14908.55 | 0.04508 | 0.00051706 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | No Fault Found maybe Birds | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-26 | c | 0.04508 | 0.00051706 | 2016 | 2015-10-26 | C | 171 | 0.04508 | 0.00051706
7850325 | 2015-10-26 15:40 | 2015-10-26 17:23 | 103 | 809 | 37853 | 46.7899 | 43.7899 | 0.11446 | 35426 | 0.10712 | 0.0024462 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734037 | Line outside house and on cnr of Pembroke saw big flash of light and exploded, lines still up. ..now no power. Advised Glen in control. Termination Insulator replaced at Pole 734037 | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-10-26 | c | 0.10712 | 0.0024462 | 2016 | 2015-10-26 | C | 809 | 0.10712 | 0.0024462
7851931 | 2015-10-26 20:04 | 2015-10-26 23:06 | 182.1333 | 1 | 182.1333 | 182.1333 | 179.1333 | 0.00055073 | 179.1333 | 0.00054166 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | X4007 | Found 3 fuses blown at Transformer X4007 - Used 3 x 2amp fuses | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-10-26 | c | 0.00054166 | 3.024e-06 | 2016 | 2015-10-26 | C | 1 | 0.00054166 | 3.0238e-06
7852199 | 2015-10-26 19:50 | 2015-10-26 21:28 | 97.5333 | 2 | 97.5333 | 48.7667 | 45.7667 | 0.00029492 | 91.5333 | 0.00027677 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2147 | 2 x 6amp HV fuses replaced at fuses FC2147. Suspected bird strike | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-26 | c | 0.00027677 | 6.048e-06 | 2016 | 2015-10-26 | C | 2 | 0.00027677 | 6.0475e-06
7852282 | 2015-10-27 06:00 | 2015-10-27 08:16 | 135.7333 | 740 | 79971.9333 | 108.0702 | 105.0702 | 0.24182 | 77751.9333 | 0.2351 | 0.0022376 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | S51 Tripped on OC. Feeder sectionalised and Patrolled. No fault Found. | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-10-27 | c | 0.2351 | 0.0022376 | 2016 | 2015-10-27 | C | 740 | 0.2351 | 0.0022376
7853107 | 2015-10-27 06:22 | 2015-10-27 07:26 | 63.5 | 1 | 63.5 | 63.5 | 60.5 | 0.00019201 | 60.5 | 0.00018294 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7026 | Reload Reliven at Fuses 7026. 2x 10 A Fuses. Possible Bird Strike | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-10-27 | c | 0.00018294 | 3.024e-06 | 2016 | 2015-10-27 | C | 1 | 0.00018294 | 3.0238e-06
7853126 | 2015-10-27 06:40 | 2015-10-27 09:00 | 139.9167 | 3 | 419.75 | 139.9167 | 136.9167 | 0.0012692 | 410.75 | 0.001242 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/57 | Replace 2 x 10 hv fuses at fuse # m60. called control. back on: 9:00am. already off when arrived on site. cause: unknown. Customer at #462 advise power back on. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-27 | c | 0.001242 | 9.071e-06 | 2016 | 2015-10-27 | C | 3 | 0.001242 | 9.0713e-06
7854871 | 2015-11-04 09:30 | 2015-11-04 13:15 | 224.6 | 27 | 6064.2 | 224.6 | 221.6 | 0.018337 | 5983.2 | 0.018092 | 8.1642e-05 | NAPA ID:13186 TP_GREYTOWN GXP > TUHITARATA SUB > KUMENGA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | T4328 | Between pole 798810 and 798812 new 200KVA pole mount transformer on new 2 pole structure | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-11-04 | b | 0.0090459 | 4.0821e-05 | 2016 | 2015-11-04 | B | 27 | 0.018092 | 8.1642e-05
7859441 | 2015-10-27 09:23 | 2015-10-27 11:48 | 144.65 | 1228 | 67352.95 | 54.8477 | 51.8477 | 0.20366 | 63668.95 | 0.19252 | 0.0037132 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 33kV Kauri Point Lines | at 09:23, Aongatete Sub, CB 42 Kauri Point Feeder, Tripped, Ph A O/C, E/F, L/O. Loss of Supply to Kauri Point Sub. Faultmen dispatched & investigation began. 11kV Backfed from Waihi Beach CB 5 and Katikati CB 6. KPT CB 1 Opened, Sectionaliser 9223 Closed. | F1,F2,F3 | AONGATETE42-KAURI POINT 33KV | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-10-27 | c | 0.19252 | 0.0037132 | 2016 | 2015-10-27 | C | 1228 | 0.19252 | 0.0037132
7862913 | 2015-11-17 09:00 | 2015-11-17 14:25 | 325 | 23 | 7475 | 325 | 322 | 0.022603 | 7406 | 0.022394 | 6.9546e-05 | NAPA ID:13546 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp ABS 25 | RECON HV FEEDER WIRES. REPLACE POLES AND ARMS. Otamarakau Valley Road, Pongakawa. W/O 10146562. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-17 | b | 0.011197 | 3.4773e-05 | 2016 | 2015-11-17 | B | 23 | 0.022394 | 6.9546e-05
7863005 | 2015-10-27 10:01 | 2015-10-27 10:25 | 24.0333 | 3074 | 62450.45 | 20.3157 | 17.3157 | 0.18884 | 53228.45 | 0.16095 | 0.009295 |  | 11 | Unplanned | ZONE SUB EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | CB 3212 | Bell Block CB 3212 Tripped open during SIS 12508. The part power job shown was in the system when CB3212 tripped and was integrated in to the sub outage. | F1,F2,F3 | CITY NO 1 33KV | CARRINGTON ST 33 | Taranaki | TP_CARRINGTON | Western Electricity | POWERCO | 2015-10-27 | c | 0.16095 | 0.009295 | 2016 | 2015-10-27 | C | 3074 | 0.16095 | 0.009295
7863022 | 2015-11-16 09:27 | 2015-11-16 15:28 | 361 | 21 | 7497 | 357 | 354 | 0.022669 | 7434 | 0.022479 | 6.3499e-05 | NAPA ID:13596 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS E61 | Change 15 x 33kv Xarms and 9 x 11kv xarms. Between Raymond Street and Parrs Road. Kelvin Grove. W/O 30006772. | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-16 | b | 0.011239 | 3.1749e-05 | 2016 | 2015-11-16 | B | 21 | 0.022479 | 6.3499e-05
7867204 | 2015-10-27 10:36 | 2015-10-27 12:21 | 105.05 | 1 | 105.05 | 105.05 | 102.05 | 0.00031765 | 102.05 | 0.00030857 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2517 | replace 2 x 10 amp drop out fuse. cause: lightning last night. tx X2517. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-10-27 | c | 0.00030858 | 3.024e-06 | 2016 | 2015-10-27 | C | 1 | 0.00030857 | 3.0238e-06
7868520 | 2015-11-18 09:45 | 2015-11-18 14:52 | 307 | 5 | 1535 | 307 | 304 | 0.0046415 | 1520 | 0.0045961 | 1.5119e-05 | NAPA ID:13547 TP_TE MATAI GXP > PONGAKAWA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF7-035 | RECON HV FEEDER WIRES. REPLACE POLES AND ARMS. Otamarakau Valley Road, Pongakawa. W/O 10146562. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-18 | b | 0.0022981 | 7.559e-06 | 2016 | 2015-11-18 | B | 5 | 0.0045961 | 1.5119e-05
7868773 | 2015-11-03 08:33 | 2015-11-03 16:24 | 471 | 15 | 7065 | 471 | 468 | 0.021363 | 7020 | 0.021227 | 4.5356e-05 | NAPA ID:14163 TP_CARRINGTON GXP > BELL BLOCK SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754873 | Structure/Crossarm/Insulator replacement on 754873 , 754872 , 754871 , 743606 , 743608 , 743609 , 743610 , 743612. | F2 | BELL BLOCK 5 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.010613 | 2.2678e-05 | 2016 | 2015-11-03 | B | 15 | 0.021227 | 4.5356e-05
7868879 | 2015-11-18 09:30 | 2015-11-18 13:10 | 220 | 23 | 5060 | 220 | 217 | 0.0153 | 4991 | 0.015092 | 6.9546e-05 | NAPA ID:12809 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-030 | Replace poles, hardware and conductor. Replace existing links at SD5-030 with solid links on completion of works. Kaiate Falls Road between poles 220170, 220183. W/O 30003844. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-18 | b | 0.0075458 | 3.4773e-05 | 2016 | 2015-11-18 | B | 23 | 0.015092 | 6.9546e-05
7871804 | 2015-11-17 10:00 | 2015-11-17 12:30 | 150 | 5 | 750 | 150 | 147 | 0.0022678 | 735 | 0.0022225 | 1.5119e-05 | NAPA ID:14113 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | T8/132 | Upgrade T8/132 to a 30-11- | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-11-17 | b | 0.0011112 | 7.559e-06 | 2016 | 2015-11-17 | B | 5 | 0.0022225 | 1.5119e-05
7872374 | 2015-10-28 09:22 | 2015-10-28 10:46 | 84.2333 | 1 | 84.2333 | 84.2333 | 81.2333 | 0.0002547 | 81.2333 | 0.00024563 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 1273 | Replaced 4x 3A fuses at 8175 and 1273. Due to possum. Nothing else repaired or replaced. All other assets up to Powerco standard. FM has worked through control | F3 | BELL BLOCK 7 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-10-28 | c | 0.00024563 | 3.024e-06 | 2016 | 2015-10-28 | C | 1 | 0.00024563 | 3.0238e-06
7873075 | 2015-11-03 09:00 | 2015-11-03 14:55 | 355 | 64 | 22720 | 355 | 352 | 0.0687 | 22528 | 0.068119 | 0.00019352 | NAPA ID:14188 TP_HUIRANGI GXP > INGLEWOOD SUB | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 707811 | Ap1 install generator at tx 2963T. Ap2 replace pole 707811 and remove abs 5488 from network. replace all hv conductor in work area. Ap3 dissconnect generator at tx 2963T | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-11-03 | b | 0.03406 | 9.676e-05 | 2016 | 2015-11-03 | B | 64 | 0.068119 | 0.00019352
7873484 | 2015-10-28 13:11 | 2015-10-28 14:38 | 87 | 240 | 5655 | 23.5625 | 20.5625 | 0.017099 | 4935 | 0.014922 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | K1537 | Recloser RC27 tripped on PH A, B, C OC and EF. Don Watson was doing a stand over for Tree Contractors (Hedge Co. Phone 021 853 878) when a branch fell the wrong way into lines breaking one Conductor. 11kV conductor came down onto 400V at Transformer TC172 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-10-28 | c | 0.014922 | 0.0007257 | 2016 | 2015-10-28 | C | 240 | 0.014922 | 0.0007257
7874664 | 2015-10-28 09:04 | 2015-10-28 15:50 | 405.8833 | 29 | 3108.6 | 107.1931 | 104.1931 | 0.0093997 | 3021.6 | 0.0091366 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P04385 | Unplanned to Restore HV Supply. Residual Fault ID 100,013. Line breaks being closed and Poles replaced. Materials Used: 30mtrs ferret, 12x sleeves, 6x deadends, 2x stays complete, 3x 11m poles, 2x pin arms, 4x Termination arms | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-10-28 | c | 0.0091366 | 8.7689e-05 | 2016 | 2015-10-28 | C | 29 | 0.0091366 | 8.7689e-05
7874751 | 2015-10-29 11:30 | 2015-10-30 15:15 | 1665 | 2 | 3330 | 1665 | 1662 | 0.010069 | 3324 | 0.010051 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3762 | Fuses 7144 found blown & removed from holders. Transformer T3762 has bad oil leak & appears to have had blow up on LV side of it. Jason Hall investigating. CR. Sam Smith and Bryan Butler returning to site tomorrow to asses transformer and decide on repair | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-10-29 | c | 0.010051 | 6.048e-06 | 2016 | 2015-10-29 | C | 2 | 0.010051 | 6.0475e-06
7875051 | 2015-11-04 09:32 | 2015-11-04 14:31 | 299 | 65 | 19435 | 299 | 296 | 0.058767 | 19240 | 0.058177 | 0.00019654 | NAPA ID:14199 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P06220 | To run new 11kv conductor to t9/30 and to replace burnt off softwood pole p06220 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-04 | b | 0.029089 | 9.8272e-05 | 2016 | 2015-11-04 | B | 65 | 0.058177 | 0.00019654
7880244 | 2015-10-28 14:00 | 2015-10-29 17:40 | 1660 | 5 | 1100 | 220 | 217 | 0.0033261 | 1085 | 0.0032808 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | T5140 | Lines down in paddock brought down by Truck. Truck belonged to Campbell Contracting. Brian Campbell 06 761 8884. NDR 22905. Crew has been organised to attend via Kaine Mackay, looks like hv has gone into 3 houses 219,235,239 Patiki Road so contractor will | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-28 | c | 0.0032808 | 1.5119e-05 | 2016 | 2015-10-28 | C | 5 | 0.0032808 | 1.5119e-05
7880353 | 2015-10-29 08:10 | 2015-10-29 08:14 | 3.7 | 322 | 737.3 | 2.2898 | -0.71025 | 0.0022294 | 0 | 0 | 0.00097365 |  | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 9779 | Safety Manager 513752. During planned switching under NAPA 13024 Recloser 9779/2 tripped on EF OC causing loss of supply past that point. After power was restored it was found that lines had been bought down and it is suspected that this event may have ca | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-10-29 | c | 0 | 0.00097365 | 2016 | 2015-10-29 | C | 322 | 0 | 0.00097365
7880687 | 2015-11-20 09:30 | 2015-11-20 14:31 | 300.8667 | 13 | 3911.2667 | 300.8667 | 297.8667 | 0.011827 | 3872.2667 | 0.011709 | 3.9309e-05 | NAPA ID:13677 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV pole 737393 | Install new 33Kv ple 737393 & run new 1 span 33Kv conductor over 11Kv + new stall new 11Kv 9.5 pole under 33Kv conductor. Works location: Standish Rd, Stratford. WO 30010304 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-20 | b | 0.0058544 | 1.9654e-05 | 2016 | 2015-11-20 | B | 13 | 0.011709 | 3.9309e-05
7881505 | 2015-11-17 10:40 | 2015-11-17 13:40 | 180 | 2 | 360 | 180 | 177 | 0.0010886 | 354 | 0.0010704 | 6.0475e-06 | NAPA ID:13612 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/302 | To replace hardware and earthing on Transformer T8/302 and move to correct height. Works location: Mangamarie Rd. WO 10161214 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-17 | b | 0.00053521 | 3.024e-06 | 2016 | 2015-11-17 | B | 2 | 0.0010704 | 6.0475e-06
7882989 | 2015-10-29 10:01 | 2015-10-29 10:15 | 14.2667 | 8644 | 79574.4 | 9.2057 | 6.2057 | 0.24061 | 53642.4 | 0.1622 | 0.026137 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | CB 202 | 33kV CB 202 at Greerton Tripped when ABS 54 at Aongatete was opened as part of the switching to repair CB 42 at Aongatete. This normally would not have been a problem but one of the 33kV Feed lines to Omokoroa and Aongatete was out for Maintenance. When c | F1,F2,F3 | GREERTON202-AONGATETE82 33KV | TAURANGA 31 | Tauranga | GREERTON | Eastern Electricity | POWERCO | 2015-10-29 | c | 0.1622 | 0.026137 | 2016 | 2015-10-29 | C | 8644 | 0.1622 | 0.026137
7891652 | 2015-10-29 10:07 | 2015-10-29 17:01 | 414.35 | 23 | 4079.9 | 177.387 | 174.387 | 0.012337 | 4010.9 | 0.012128 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 832488 | Retailer called to advise customer can see 11kv lines down near property. 10.22am called hub to advise 999, printed and taken to control.Pole & Lines Down. Materials used: 10mtr Busck pole, 2x 2.7m Crossarms complete with hardware, 1x breast block | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-29 | c | 0.012128 | 6.9546e-05 | 2016 | 2015-10-29 | C | 23 | 0.012128 | 6.9546e-05
7891688 | 2015-10-29 10:15 | 2015-10-29 13:34 | 199.1667 | 1 | 199.1667 | 199.1667 | 196.1667 | 0.00060223 | 196.1667 | 0.00059316 | 3.0238e-06 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P45800 | 33kv Broken Binders, Lines in danger of Falling. Reported by Darryl Rothery. Urgent job to replace Binders, Crossamrs and Insulators. Materials Used: 2x 4mtr crossarms, 3x Clamp top insulators & Pins, 3x Pin & Insulators, & all Associated Hardware. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-10-29 | c | 0.00059316 | 3.024e-06 | 2016 | 2015-10-29 | C | 1 | 0.00059316 | 3.0238e-06
7891748 | 2015-11-17 09:31 | 2015-11-17 10:55 | 84 | 27 | 2268 | 84 | 81 | 0.0068579 | 2187 | 0.006613 | 8.1642e-05 | NAPA ID:13455 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6575 | Remove 11KV Fuses 6575 And Jumper Through at Pole 741801. Works location: Tate Rd, Brixton. WO 10159896 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-17 | b | 0.0033065 | 4.0821e-05 | 2016 | 2015-11-17 | B | 27 | 0.006613 | 8.1642e-05
7891976 | 2015-11-01 08:33 | 2015-11-01 12:26 | 232.5 | 74 | 17205 | 232.5 | 229.5 | 0.052024 | 16983 | 0.051353 | 0.00022376 | NAPA ID:14231 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME EXPRESS | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9248 | AP-1 Isolate Switch unit 9250 and investigate and repair Faulty indication on Switch 9250-4. Confirm and correct Switch Label. Also Connect new cable to Switch 9250-2 and liven new cable feeding switch unit 9994 and new TX's TP2849 and TP2850. AP-2 Isola | F2 | MALEME EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-11-01 | b | 0.025676 | 0.00011188 | 2016 | 2015-11-01 | B | 74 | 0.051353 | 0.00022376
7892029 | 2015-10-29 11:38 | 2015-10-29 18:36 | 418.3 | 72 | 18195.7167 | 252.7183 | 249.7183 | 0.055019 | 17979.7167 | 0.054366 | 0.00021771 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 832315 | CB 7417 tripped e/f o/c. 1 X H/T Insulator at Pole 832315 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-10-29 | c | 0.054366 | 0.00021771 | 2016 | 2015-10-29 | C | 72 | 0.054366 | 0.00021771
7892101 | 2015-11-04 09:25 | 2015-11-04 11:00 | 95 | 51 | 4845 | 95 | 92 | 0.01465 | 4692 | 0.014187 | 0.00015421 | NAPA ID:14227 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD INDUSTRIAL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5880 | Urgent 11Kv 200Kva O/h leaking Tx 2975T replacement. Works location: Warwick Rd, Stratford. WO 30014854 | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-04 | b | 0.0070937 | 7.7106e-05 | 2016 | 2015-11-04 | B | 51 | 0.014187 | 0.00015421
7894129 | 2015-10-29 19:18 | 2015-10-30 03:13 | 474.6333 | 5 | 2373.1667 | 474.6333 | 471.6333 | 0.0071759 | 2358.1667 | 0.0071305 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 804618 | James from Targa Rally head quarters called to advise a rally car has hit a pole and some lines are down on the road side. Used 1 X Pole 2 X Crossarms 3 X Insulators 6 X Polymas Insulators. NDR Number 30450 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-10-29 | c | 0.0071305 | 1.5119e-05 | 2016 | 2015-10-29 | C | 5 | 0.0071305 | 1.5119e-05
7894471 | 2015-10-30 00:10 | 2015-10-30 01:35 | 84.5667 | 23 | 1945.0333 | 84.5667 | 81.5667 | 0.0058813 | 1876.0333 | 0.0056727 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 748846 | Big Bang & Flash from pole outside house Please Check For Saftey . Replaced 1 X H/T Insulator At Pole 748846 | F2 | MOTUROA 7 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-10-30 | c | 0.0056727 | 6.9546e-05 | 2016 | 2015-10-30 | C | 23 | 0.0056727 | 6.9546e-05
7895218 | 2015-10-30 02:11 | 2015-10-30 14:00 | 709.1333 | 680 | 231479 | 340.4103 | 337.4103 | 0.69994 | 229439 | 0.69377 | 0.0020562 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 707734 | Car v pole caused an outage on CB I31. Replace 11 meter pole and hardware and full set of fuses. NDR 045503 | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-10-30 | c | 0.69377 | 0.0020562 | 2016 | 2015-10-30 | C | 680 | 0.69377 | 0.0020562
7898561 | 2015-10-30 05:44 | 2015-10-30 05:57 | 13 | 904 | 11187.7167 | 12.3758 | 9.3758 | 0.033829 | 8475.7167 | 0.025629 | 0.0027335 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Rata Sub 11kV Bus | CB 3035 tripped on OC. Suspect Bird Strike on 11kV Bus at Rata Sub. NOTE ; Also includes 11kV Recloser 4246 tripping. | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-10-30 | c | 0.025629 | 0.0027335 | 2016 | 2015-10-30 | C | 904 | 0.025629 | 0.0027335
7900073 | 2015-10-30 06:44 | 2015-10-30 09:04 | 140.3 | 577 | 46348.55 | 80.3268 | 77.3268 | 0.14015 | 44617.55 | 0.13491 | 0.0017447 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P2169 | CB 6 Trip. E/F. L/O. Feeder Sectionalised. Broken insulator found at Pole P2169. Isolated between ABS 292 and ABS 290. Small backfeed via ABS IC1223. Insulator replaced. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-10-30 | c | 0.13491 | 0.0017447 | 2016 | 2015-10-30 | C | 577 | 0.13491 | 0.0017447
7901632 | 2015-10-30 08:40 | 2015-10-30 09:00 | 20 | 1 | 20 | 20 | 17 | 6.0475e-05 | 17 | 5.1404e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L76 | Jumper Repaired at Fuses L76. No materials used. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-10-30 | c | 5.1404e-05 | 3.024e-06 | 2016 | 2015-10-30 | C | 1 | 5.1404e-05 | 3.0238e-06
7902037 | 2015-10-30 09:04 | 2015-10-30 14:10 | 306 | 1 | 306 | 306 | 303 | 0.00092527 | 303 | 0.0009162 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | M4365 | SMC advise: FM responding to an emergency job, clicked off site by Dispatch. 2R crew request was already made earlier. re-do 11kv cable terminate. used 11kv 3/4 termination kit. 4m x 25mm bear copper. 3 x 25x25mm bi-metal sleeves. 6x HD 12 connectors caus | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-10-30 | c | 0.0009162 | 3.024e-06 | 2016 | 2015-10-30 | C | 1 | 0.0009162 | 3.0238e-06
7902931 | 2015-10-30 11:33 | 2015-10-30 11:39 | 6 | 4 | 24 | 6 | 3 | 7.257e-05 | 12 | 3.6285e-05 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC233 | Northpower is doing pole changing and reconductoring down the road, since yesterday, when turn things on, things blow up. tested voltage at TX - 4 or 5 spans away, tested main switch at cowshed. TX 225-229volts and 390-399volts on cross phases main switc | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-10-30 | c | 3.6285e-05 | 1.2095e-05 | 2016 | 2015-10-30 | C | 4 | 3.6285e-05 | 1.2095e-05
7902988 | 2015-11-18 08:30 | 2015-11-18 13:10 | 280 | 38 | 10640 | 280 | 277 | 0.032173 | 10526 | 0.031828 | 0.0001149 | NAPA ID:13466 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 741894 | Install a new ABS12114 and 11Metre BusckTo replace Pole741894 Remove Fuses 8905 and jumper Thru at pole388977 Remove Fuses 8173 and jumper Thru at pole741934. Works location: Mahoetahi Rd, Brixton. WO 10159896 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-18 | b | 0.015914 | 5.7451e-05 | 2016 | 2015-11-18 | B | 38 | 0.031828 | 0.0001149
7904022 | 2015-10-30 09:45 | 2015-10-30 12:10 | 145 | 9 | 1305 | 145 | 142 | 0.003946 | 1278 | 0.0038644 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 717156 | 8.47am - advised hub of 999 and taken into control. 153 Little Oeo Road. Tree has taken down 11kv lines. 1 x 15 A fuse. Crimps. 20 M Conductor | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-30 | c | 0.0038644 | 2.7214e-05 | 2016 | 2015-10-30 | C | 9 | 0.0038644 | 2.7214e-05
7904072 | 2015-11-18 08:50 | 2015-11-18 16:56 | 486.4167 | 39 | 7545.8833 | 193.4842 | 190.4842 | 0.022817 | 7428.8833 | 0.022463 | 0.00011793 | NAPA ID:13616 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/702 | Change 15 x 33kV cross arms and 17 x 11kV cross arms. Works location: Parrs Rd. WO 30006772 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-18 | b | 0.011232 | 5.8963e-05 | 2016 | 2015-11-18 | B | 39 | 0.022463 | 0.00011793
7904245 | 2015-11-09 09:00 | 2015-11-09 12:00 | 180 | 1 | 180 | 180 | 177 | 0.00054428 | 177 | 0.00053521 | 3.0238e-06 | NAPA ID:14246 TP_TE MATAI GXP > TE PUKE SUB > MOEHAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer TE5-123 | REPLACE ROTTEN ARMS HOLDING TX UP. Works location: Washers Rd. WO 30002455 | F3 | MOEHAU ST | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-11-09 | b | 0.0002676 | 1.512e-06 | 2016 | 2015-11-09 | B | 1 | 0.00053521 | 3.0238e-06
7904382 | 2015-11-09 13:00 | 2015-11-09 14:32 | 92 | 1 | 92 | 92 | 89 | 0.00027819 | 89 | 0.00026911 | 3.0238e-06 | NAPA ID:14244 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer TE5-255 | REPLACE ROTTEN ARMS HOLDING TX UP. Works location: Te Puke Quarry Rd. WO 30002455 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-11-09 | b | 0.00013456 | 1.512e-06 | 2016 | 2015-11-09 | B | 1 | 0.00026911 | 3.0238e-06
7904446 | 2015-11-13 09:30 | 2015-11-13 11:15 | 105 | 3 | 315 | 105 | 102 | 0.00095248 | 306 | 0.00092527 | 9.0713e-06 | NAPA ID:14247 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC1-007 | Replace transformer. Works location: Lockington Rd. WO 30002455 | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-11-13 | b | 0.00046263 | 4.536e-06 | 2016 | 2015-11-13 | B | 3 | 0.00092527 | 9.0713e-06
7922782 | 2015-11-18 10:00 | 2015-11-18 10:40 | 40 | 2 | 80 | 40 | 37 | 0.0002419 | 74 | 0.00022376 | 6.0475e-06 | NAPA ID:13624 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2832 | To install a 400V Fuse/disconnector at TC2832. Works location: Brunskill Rd, Te Miro. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-11-18 | b | 0.00011188 | 3.024e-06 | 2016 | 2015-11-18 | B | 2 | 0.00022376 | 6.0475e-06
7922976 | 2015-11-18 13:30 | 2015-11-18 14:15 | 45 | 1 | 45 | 45 | 42 | 0.00013607 | 42 | 0.000127 | 3.0238e-06 | NAPA ID:13626 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1624 | To install a 400V Fuse disconnector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-11-18 | b | 6.3499e-05 | 1.512e-06 | 2016 | 2015-11-18 | B | 1 | 0.000127 | 3.0238e-06
7923004 | 2015-11-19 10:00 | 2015-11-19 12:15 | 135 | 8 | 1080 | 135 | 132 | 0.0032657 | 1056 | 0.0031931 | 2.419e-05 | NAPA ID:13269 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1797 | To replace the 400V pin arm & Service arm. To install a 400V Fuse disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.0015965 | 1.2095e-05 | 2016 | 2015-11-19 | B | 8 | 0.0031931 | 2.419e-05
7923023 | 2015-11-19 14:00 | 2015-11-19 14:40 | 40 | 4 | 160 | 40 | 37 | 0.0004838 | 148 | 0.00044752 | 1.2095e-05 | NAPA ID:13273 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1083 | To install a 3n phase 400V Fuse disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.00022376 | 6.048e-06 | 2016 | 2015-11-19 | B | 4 | 0.00044752 | 1.2095e-05
7923074 | 2015-11-19 13:31 | 2015-11-19 14:15 | 44 | 8 | 352 | 44 | 41 | 0.0010644 | 328 | 0.00099179 | 2.419e-05 | NAPA ID:13243 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC670 | To install a 3 phase fuse disconnector on TC3670. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.0004959 | 1.2095e-05 | 2016 | 2015-11-19 | B | 8 | 0.00099179 | 2.419e-05
7923098 | 2015-11-27 10:00 | 2015-11-27 11:15 | 75 | 4 | 300 | 75 | 72 | 0.00090713 | 288 | 0.00087084 | 1.2095e-05 | NAPA ID:13276 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5761 | To replace the 400V Pin arm & install a 3 phase 400V Fuse Disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-27 | b | 0.00043542 | 6.048e-06 | 2016 | 2015-11-27 | B | 4 | 0.00087084 | 1.2095e-05
7923106 | 2015-11-27 14:00 | 2015-11-27 14:40 | 40 | 3 | 120 | 40 | 37 | 0.00036285 | 111 | 0.00033564 | 9.0713e-06 | NAPA ID:13277 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2321 | To install a 400V Fuse disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-27 | b | 0.00016782 | 4.536e-06 | 2016 | 2015-11-27 | B | 3 | 0.00033564 | 9.0713e-06
7923147 | 2015-11-18 09:45 | 2015-11-18 14:23 | 278 | 5 | 1390 | 278 | 275 | 0.004203 | 1375 | 0.0041577 | 1.5119e-05 | NAPA ID:13250 TP_WAIHOU GXP > FARMER ROAD SUB > TATUANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2650 | LLP1: To break the 11kV line to TC2650 at pole L0244. AP: To replace all the arms on pole TC2650. LLP2: To reconnect the 11kV line to TC2650 at pole L0244. Works location: Hwy 27, Tatuanui. WO 30014669 | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-11-18 | b | 0.0020788 | 7.559e-06 | 2016 | 2015-11-18 | B | 5 | 0.0041577 | 1.5119e-05
7923490 | 2015-11-12 09:45 | 2015-11-12 16:30 | 405 | 21 | 8505 | 405 | 402 | 0.025717 | 8442 | 0.025527 | 6.3499e-05 | NAPA ID:13042 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | To replace pole and hardware including ABS 2588 in preparation for conductor upgrade between poles E12537 and E12492. Works location: Totman Rd, Hinuera. WO 30002570 Late getting power back on Northpower had trouble with Trucks | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-12 | b | 0.012763 | 3.1749e-05 | 2016 | 2015-11-12 | B | 21 | 0.025527 | 6.3499e-05
7923507 | 2015-11-17 09:30 | 2015-11-17 15:05 | 335 | 21 | 7035 | 335 | 332 | 0.021272 | 6972 | 0.021082 | 6.3499e-05 | NAPA ID:13044 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole E12537 | To replace 11kV conductor between poles E12537 and E12492. Works location: Totman Rd, Hinuera. WO 30002570. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-17 | b | 0.010541 | 3.1749e-05 | 2016 | 2015-11-17 | B | 21 | 0.021082 | 6.3499e-05
7923625 | 2015-11-19 08:45 | 2015-11-19 17:54 | 549 | 52 | 8086 | 155.5 | 152.5 | 0.02445 | 7930 | 0.023978 | 0.00015724 | NAPA ID:13628 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS E85 | Change 26 x 33kv Xarms and 23 x 11kv xarms. Works location: Tutaki Rd. WO 30006772 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-19 | b | 0.011989 | 7.8618e-05 | 2016 | 2015-11-19 | B | 52 | 0.023978 | 0.00015724
7924971 | 2015-10-30 19:54 | 2015-10-31 01:50 | 356 | 2 | 712 | 356 | 353 | 0.0021529 | 706 | 0.0021348 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF8-011 | at 19:54, Pongakawa Sub, CB 2 Otamarakau Feeder. Found transformer TF8-011 had blown. Own Isolation & AP Issued & Transformer Replaced. Also found 1x Fuse Blown at Fuses SF7-007. Reloaded, relivened. All Power Restored on completion. Mike James Attended. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-10-30 | c | 0.0021348 | 6.048e-06 | 2016 | 2015-10-30 | C | 2 | 0.0021348 | 6.0475e-06
7925800 | 2015-10-31 04:23 | 2015-10-31 10:23 | 359.65 | 175 | 7469.4333 | 42.6825 | 39.6825 | 0.022586 | 6944.4333 | 0.020998 | 0.00052916 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 363690 | Recloser 687 auto reclosed on A, B & C phase O/C flags, received a call from police of car vs pole, line was isolated at ABS 1467, 4729 , 4690/1 and Links 4690/6 to replace pole 363690 and to reblock pole 363699. NDR: NS00021. 1 X pole & all hardware repl | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-10-31 | c | 0.020998 | 0.00052916 | 2016 | 2015-10-31 | C | 175 | 0.020998 | 0.00052916
7925993 | 2015-10-31 06:47 | 2015-10-31 06:57 | 10 | 1 | 10 | 10 | 7 | 3.0238e-05 | 7 | 2.1166e-05 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP768 | Transformer TP768 isolated to alter taps. Problems at installation caused by low voltage. Voltage following alteration 237v line to earth. Customer advised a voltage complaint will be instigated if further problem occur. May then need to seek advise from | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2015-10-31 | c | 2.1166e-05 | 3.024e-06 | 2016 | 2015-10-31 | C | 1 | 2.1166e-05 | 3.0238e-06
7926187 | 2015-10-31 08:21 | 2015-10-31 10:03 | 102 | 181 | 18462 | 102 | 99 | 0.055825 | 17919 | 0.054183 | 0.0005473 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB C885 | CB C885 tripped on C phase O/C & E/F flags, Recloser 3141/2 also tripped on B & C phase O/C & E/F flags, line was patrolled and sectionalised and no fault was found, suspect bird strike.When closing Recloser 3141/2, CB 1332 at T/power auto reclosed on O/C | F1,F2,F3 | PAHAUTEA 33KV TIE | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2015-10-31 | c | 0.054183 | 0.0005473 | 2016 | 2015-10-31 | C | 181 | 0.054183 | 0.0005473
7929256 | 2015-10-31 16:16 | 2015-10-31 20:19 | 243 | 137 | 14150.6167 | 103.2892 | 100.2892 | 0.042788 | 13739.6167 | 0.041545 | 0.00041426 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P05185 | Recloser P61 tripped on C phase O/C & E/F flags, line was patrolled and sectionalised and line were found down and broken x-arm on pole P05185 due to a tree that had fallen. Materials used: 1x crossarm & hardware, 4mtrs of 25mm cu. & 6 sleeves. NDR #N3001 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-10-31 | c | 0.041545 | 0.00041425 | 2016 | 2015-10-31 | C | 137 | 0.041545 | 0.00041426
7929885 | 2015-10-31 18:45 | 2015-10-31 20:53 | 127.8333 | 32 | 1840.8667 | 57.5271 | 54.5271 | 0.0055663 | 1744.8667 | 0.0052761 | 9.676e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715526 | Line Down, Repaired using 5mtrs of 16mm cu. wire, 3x sleeves, & 1x 10Amp HV Link | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-10-31 | c | 0.0052761 | 9.676e-05 | 2016 | 2015-10-31 | C | 32 | 0.0052761 | 9.676e-05
7936427 | 2015-11-01 14:43 | 2015-11-01 18:49 | 246.5333 | 361 | 32877.6333 | 91.0738 | 88.0738 | 0.099414 | 31794.6333 | 0.096139 | 0.0010916 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 718286 | CB5 tripped on O/C. Police comms advising car vs pole on Manaia road 200m North of intersection of Normanby Road. ETA required, P023059625. 0800115 019 Line was isolated at ABS MA 121 & MA164 to replace pole 718286. 1 X pole & all 11KV & 400V hardware rep | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-11-01 | c | 0.096139 | 0.0010916 | 2016 | 2015-11-01 | C | 361 | 0.096139 | 0.0010916
7937421 | 2015-11-01 15:03 | 2015-11-01 16:00 | 57.0333 | 95 | 5418.1667 | 57.0333 | 54.0333 | 0.016383 | 5133.1667 | 0.015521 | 0.00028726 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7368 | 1x10amp HV fuse at fuses 7368, 2x10amp HV fuses blown at 7607. line patrolled & no fault found. Fuses reloaded & livened | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-11-01 | c | 0.015521 | 0.00028726 | 2016 | 2015-11-01 | C | 95 | 0.015521 | 0.00028726
7937428 | 2015-11-01 15:05 | 2015-11-01 15:45 | 39.8167 | 1 | 39.8167 | 39.8167 | 36.8167 | 0.0001204 | 36.8167 | 0.00011132 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 821714 | fire comms reporting smoking transformer, check for safety required F194868 ETA required 3.10pm - fire advised of 10 min eta bird nest at back of transformer causing smoke, removed and all ok now. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-11-01 | c | 0.00011132 | 3.024e-06 | 2016 | 2015-11-01 | C | 1 | 0.00011132 | 3.0238e-06
7937724 | 2015-11-01 16:40 | 2015-11-01 18:00 | 80.3 | 4 | 321.2 | 80.3 | 77.3 | 0.00097123 | 309.2 | 0.00093495 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7171 | 2x10amp HV fuses blown at fuses 7171 Line patrolled fuses reloaded & livened. Unknown Cause | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-11-01 | c | 0.00093495 | 1.2095e-05 | 2016 | 2015-11-01 | C | 4 | 0.00093495 | 1.2095e-05
7943158 | 2015-11-02 10:02 | 2015-11-02 11:11 | 68.85 | 5 | 344.25 | 68.85 | 65.85 | 0.0010409 | 329.25 | 0.00099557 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X9/280 | Blown Jumper Found at Transformer X9/280 - Isolated at Fuses V82 Used 1 x Fuse base and Holder and a 3 amp fuses pluse connector | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-02 | c | 0.00099557 | 1.5119e-05 | 2016 | 2015-11-02 | C | 5 | 0.00099557 | 1.5119e-05
7943268 | 2015-11-02 07:42 | 2015-11-02 07:51 | 9.0167 | 2 | 18.0333 | 9.0167 | 6.0167 | 5.4528e-05 | 12.0333 | 3.6386e-05 | 6.0475e-06 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Wind farm during planned outage. Unknown failure reason. | F2 | FAIRS RD | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-02 | c | 3.6386e-05 | 6.048e-06 | 2016 | 2015-11-02 | C | 2 | 3.6386e-05 | 6.0475e-06
7943633 | 2015-11-19 09:15 | 2015-11-19 13:35 | 260 | 33 | 8580 | 260 | 257 | 0.025944 | 8481 | 0.025645 | 9.9784e-05 | NAPA ID:13300 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1129 | To Remove the existing cable from switch 9558/2, Connect the new cable to new transformer TC1129, Join the new cable from TC1129 to the existing cables supplying TC1191, disconnect the old transformer. Works location: Purangi Rd, Cooks Beach. WO 30002527 | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.012822 | 4.9892e-05 | 2016 | 2015-11-19 | B | 33 | 0.025645 | 9.9784e-05
7943715 | 2015-11-19 08:30 | 2015-11-19 15:08 | 398 | 23 | 4539 | 197.3478 | 194.3478 | 0.013725 | 4470 | 0.013516 | 6.9546e-05 | NAPA ID:13712 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2525 | Replace Transformer + structure TC2525 and other poles and arms at various sites. Works location: Kitahi Rd, Hikuai. WO 30003727 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.0067581 | 3.4773e-05 | 2016 | 2015-11-19 | B | 23 | 0.013516 | 6.9546e-05
7943889 | 2015-11-02 22:10 | 2015-11-03 02:50 | 279.6333 | 126 | 35233.8 | 279.6333 | 276.6333 | 0.10654 | 34855.8 | 0.1054 | 0.00038099 | NAPA ID:14297 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/Gear 778 | Urgent outage to repair covers on 11kV SW/Gear CA778. Work Location: Disraeli Street, Hawera. W/O 30007226. | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-11-02 | b | 0.052698 | 0.0001905 | 2016 | 2015-11-02 | B | 126 | 0.1054 | 0.00038099
7947013 | 2015-11-26 08:55 | 2015-11-26 15:00 | 365 | 11 | 3853 | 350.2727 | 347.2727 | 0.011651 | 3820 | 0.011551 | 3.3261e-05 | NAPA ID:12561 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 806267 | Cut line break at pole 806267 for isolation, replace pole 806246 reinstate line break at pole 806267. Works location: SH 3, Marton. WO 10154048 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-11-26 | b | 0.0057754 | 1.6631e-05 | 2016 | 2015-11-26 | B | 11 | 0.011551 | 3.3261e-05
7947048 | 2015-11-02 11:45 | 2015-11-02 15:01 | 195.6833 | 638 | 26617.9333 | 41.7209 | 38.7209 | 0.080486 | 24703.9333 | 0.074699 | 0.0019292 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P00995 | Turitea CB 8 Tripped on EF. Car V Pole 166 Old West Rd, Linton. Crossarm Broken. Car still up against Pole behind Massey Unit. Isolated at ABS's H101, H31 and H103. with a backfeed via ABS 10107. Pole replaced complete with Crossarm and insulators NDR #N3 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-11-02 | c | 0.074699 | 0.0019292 | 2016 | 2015-11-02 | C | 638 | 0.074699 | 0.0019292
7947726 | 2015-11-02 14:22 | 2015-11-02 15:25 | 63.4167 | 15 | 951.25 | 63.4167 | 60.4167 | 0.0028764 | 906.25 | 0.0027403 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210318 | Needs to replace set of ddo fuses, Full set of Fuses replaced at TD3-269. Isolation at fuses SD3-001 No Back Feeds available. | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-11-02 | c | 0.0027403 | 4.5356e-05 | 2016 | 2015-11-02 | C | 15 | 0.0027403 | 4.5356e-05
7948302 | 2015-11-05 08:37 | 2015-11-05 16:52 | 495 | 493 | 114527 | 232.3063 | 229.3063 | 0.3463 | 113048 | 0.34183 | 0.0014907 | NAPA ID:14300 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC201 | Replace Crossarms at Various Sites. LV outage for 30 min at start and 30 min at finish of job on TXs with generator. This job ran over time due to the cable being too short to reach up to lines. All Power Restored at 16:52. s. | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-05 | b | 0.17092 | 0.00074536 | 2016 | 2015-11-05 | B | 493 | 0.34183 | 0.0014907
7949465 | 2015-11-19 08:30 | 2015-11-19 15:59 | 449.1833 | 10 | 4491.8333 | 449.1833 | 446.1833 | 0.013582 | 4461.8333 | 0.013492 | 3.0238e-05 | NAPA ID:13552 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 248738 | Install live line break at pole 248738 to isolate section of line to replace ABS 1331 and H/V crossarms at various sites. Reinstate live line break on completion of work. Works location: No 5 Rd, Springdale. WO 30015154 | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.0067458 | 1.5119e-05 | 2016 | 2015-11-19 | B | 10 | 0.013492 | 3.0238e-05
7949527 | 2015-11-23 09:15 | 2015-11-23 14:55 | 340 | 5 | 1700 | 340 | 337 | 0.0051404 | 1685 | 0.005095 | 1.5119e-05 | NAPA ID:14088 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole W2018 | liveline break jumpers at pole W2018 , replace Transformer TC1198 and all crossarms and hardware etc. Works location: Camp Rd, Whitianga. WO 30002490 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-23 | b | 0.0025475 | 7.559e-06 | 2016 | 2015-11-23 | B | 5 | 0.005095 | 1.5119e-05
7950235 | 2015-11-02 03:19 | 2015-11-02 15:19 | 720.1833 | 690 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0020864 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P31690 | RS L34 Tripped A Ph O/C E/F. Appears a high load made contact with lines broken LV line found at Pole P31690. Pole also cracked and will need replacing. Used 3 x sleeves and 3x 60 amp HRC fuses. NDR # 045376 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-02 | c | 0 | 0.0020864 | 2016 | 2015-11-02 | C | 690 | 0 | 0.0020864
7951475 | 2015-11-02 16:46 | 2015-11-02 22:14 | 327.55 | 286 | 68498.5333 | 239.5054 | 236.5054 | 0.20712 | 67640.5333 | 0.20453 | 0.0008648 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 791536 | Recloser 4200 tripped and Recloser 1087 tripped on B & C phase O/C & E/F flags, line was sectionalised and patrolled and found lines down at transformer X2691. Line was isolated at ABS's 811 & 267 to repair lines at pole 791536. 5 meters rabbit conductor | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-11-02 | c | 0.20453 | 0.0008648 | 2016 | 2015-11-02 | C | 286 | 0.20453 | 0.0008648
7955363 | 2015-11-03 06:30 | 2015-11-03 08:54 | 143.5667 | 21 | 3014.9 | 143.5667 | 140.5667 | 0.0091163 | 2951.9 | 0.0089258 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V16 | Reload Reliven. 2 x 10 A Fuses. Cause by Wind | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-03 | c | 0.0089258 | 6.3499e-05 | 2016 | 2015-11-03 | C | 21 | 0.0089258 | 6.3499e-05
7955511 | 2015-11-03 06:22 | 2015-11-03 07:18 | 55.7333 | 5 | 278.6667 | 55.7333 | 52.7333 | 0.00084262 | 263.6667 | 0.00079726 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/301 | Reload Reliven, 1 x 6A Fuse., Cause Unknown | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-11-03 | c | 0.00079727 | 1.5119e-05 | 2016 | 2015-11-03 | C | 5 | 0.00079726 | 1.5119e-05
7956781 | 2015-11-23 09:07 | 2015-11-23 13:09 | 241.5333 | 1 | 241.5333 | 241.5333 | 238.5333 | 0.00073034 | 238.5333 | 0.00072127 | 3.0238e-06 | NAPA ID:13306 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP2232 | To replace poles and hardware in preparation for 11kV conductor upgrade. Works location: Puketutu Rd, Matamata. WO 30002534 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-23 | b | 0.00036063 | 1.512e-06 | 2016 | 2015-11-23 | B | 1 | 0.00072127 | 3.0238e-06
7956809 | 2015-11-25 09:00 | 2015-11-25 13:15 | 255 | 19 | 4845 | 255 | 252 | 0.01465 | 4788 | 0.014478 | 5.7451e-05 | NAPA ID:13307 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1819 | To replace 11kV poles and hardware in preparation for 11kV upgrade. Works location: Puketutu Rd, Matamata. WO 30002534 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-25 | b | 0.0072389 | 2.8726e-05 | 2016 | 2015-11-25 | B | 19 | 0.014478 | 5.7451e-05
7956864 | 2015-11-25 09:16 | 2015-11-25 17:50 | 514 | 46 | 23644 | 514 | 511 | 0.071494 | 23506 | 0.071077 | 0.00013909 | NAPA ID:13751 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 722334 | 1st LLP Install LLB @ pole 722321 - 2nd AP Install new 11Kv 12099 xarm/pole 722334 connect new Hv u/g cable remove Hv o/h line & o/h & Tx C6175 install new u/g cable/Tx C6175 - 3rd LLP close LLB @ pole 722321 4th - then commission/test new u/g Tx C6175. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-11-25 | b | 0.035538 | 6.9546e-05 | 2016 | 2015-11-25 | B | 46 | 0.071077 | 0.00013909
7957682 | 2015-11-03 13:00 | 2015-11-03 14:49 | 108.9167 | 1 | 108.9167 | 108.9167 | 105.9167 | 0.00032934 | 105.9167 | 0.00032027 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | defect # 244-10374 | amber 1 defected the spur line on trimble, needs work asap. defect # 244-10374. 8 x 11kv poles with cross arms in poor state as well as 4 x lv cross arms. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-11-03 | c | 0.00032027 | 3.024e-06 | 2016 | 2015-11-03 | C | 1 | 0.00032027 | 3.0238e-06
7961231 | 2015-11-25 10:05 | 2015-11-25 13:20 | 195 | 82 | 15990 | 195 | 192 | 0.04835 | 15744 | 0.047606 | 0.00024795 | NAPA ID:13305 TP_WAIKINO GXP > WHANGAMATA SUB > OTAHU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5117 | To replace transformer TC5117. Works location: Otahu Rd, Whangamata. WO 30002527 | F3 | OTAHU RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-11-25 | b | 0.023803 | 0.00012397 | 2016 | 2015-11-25 | B | 82 | 0.047606 | 0.00024795
7961644 | 2015-11-23 09:30 | 2015-11-23 15:02 | 332 | 10 | 3320 | 332 | 329 | 0.010039 | 3290 | 0.0099482 | 3.0238e-05 | NAPA ID:12739 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 749201 | Replace ABS163 on Pole 749201 &Xarms. Works location: Smart Rd, New Plymouth. WO 30013272 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-23 | b | 0.0049741 | 1.5119e-05 | 2016 | 2015-11-23 | B | 10 | 0.0099482 | 3.0238e-05
7961685 | 2015-11-03 15:49 | 2015-11-03 20:07 | 257.75 | 88 | 16723.4 | 190.0386 | 187.0386 | 0.050568 | 16459.4 | 0.049769 | 0.00026609 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798070 | CB C926 Tripped C Phase O/C L/O Lines found down due to age at Pole 798070 - Isolated at ABS S571 plus isolations for embedded generation - lines repaired Used 6 mtrs of conductor 4 sleeves and 1x padlock | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-11-03 | c | 0.049769 | 0.00026609 | 2016 | 2015-11-03 | C | 88 | 0.049769 | 0.00026609
7962172 | 2015-11-03 17:40 | 2015-11-03 17:56 | 16 | 15 | 240 | 16 | 13 | 0.0007257 | 195 | 0.00058963 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC3-069 | 1 hv fuse blown at SC3-069 due to possible overload due to new works taken place past the fuses sc3-069. The fuses probably had not been up graded to meet the new demand. Reloaded all 3 fuses with 50amp fuses. 860KVA capacity of transformers past SC3-069. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-11-03 | c | 0.00058963 | 4.5356e-05 | 2016 | 2015-11-03 | C | 15 | 0.00058963 | 4.5356e-05
7962254 | 2015-11-03 16:40 | 2015-11-04 12:13 | 1172.5667 | 76 | 11976.1667 | 157.5811 | 154.5811 | 0.036213 | 11748.1667 | 0.035524 | 0.00022981 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 834010 | Recloser 7417 Tripped B Ph O/C E/F L/O - Lines down reported by Public - Isolated at Fuses 7904. Temp Line break made at Pole 824010 - line to be repaired in day light Power restored to Transformer T279 at 21:20. 04/11/15 Lines Repaired and Line Break Cl | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-11-03 | c | 0.035524 | 0.00022981 | 2016 | 2015-11-03 | C | 76 | 0.035524 | 0.00022981
7966512 | 2015-11-03 16:46 | 2015-11-03 18:02 | 76.7 | 18 | 1380.6 | 76.7 | 73.7 | 0.0041746 | 1326.6 | 0.0040113 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sc3-0069 | 1 hv fuse blown at SC3-069 due to possible overload due to new works taken place past the fuses sc3-069. The fuses probably had not been up graded to meet the new demand. Reloaded all 3 fuses with 50amp fuses. 860KVA capacity of transformers past SC3-069. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-11-03 | c | 0.0040113 | 5.4428e-05 | 2016 | 2015-11-03 | C | 18 | 0.0040113 | 5.4428e-05
7966549 | 2015-11-03 17:38 | 2015-11-03 18:03 | 25 | 80 | 2000 | 25 | 22 | 0.0060475 | 1760 | 0.0053218 | 0.0002419 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sc3-069 | 1 hv fuse blown at SC3-069 due to possible overload due to new works taken place past the fuses sc3-069. The fuses probably had not been up graded to meet the new demand. Reloaded all 3 fuses with 50amp fuses. 860KVA capacity of transformers past SC3-069. | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-11-03 | c | 0.0053218 | 0.0002419 | 2016 | 2015-11-03 | C | 80 | 0.0053218 | 0.0002419
7966923 | 2015-11-03 20:31 | 2015-11-03 21:20 | 49.2833 | 1 | 49.2833 | 49.2833 | 46.2833 | 0.00014902 | 46.2833 | 0.00013995 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2611 | Used 2 x 8 amp fuses | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-03 | c | 0.00013995 | 3.024e-06 | 2016 | 2015-11-03 | C | 1 | 0.00013995 | 3.0238e-06
7967474 | 2015-11-04 05:47 | 2015-11-04 07:18 | 90.3167 | 4937 | 151755.5 | 30.7384 | 27.7384 | 0.45887 | 136944.5 | 0.41409 | 0.014928 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 266910 | at 05:47, Matapihi Sub, CB 3042 Tripped, Ph A B C O/C, L/O. Triton Sub, CB 36, CB 37, CB 62 & CB 72 All Tripped, E/F O/C, L/O. Omanu Sub, CB 5 Tripped, Ph C O/C,L/O, CB 8 Tripped, Ph A O/C, L/O. Loss of Supply to Triton Sub and to Omanu CB 5 & Omanu CB 8. | F1,F2,F3 | TRITON 1 33KV | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.41409 | 0.014928 | 2016 | 2015-11-04 | C | 4937 | 0.41409 | 0.014928
7972435 | 2015-11-04 05:45 | 2015-11-04 08:06 | 141.4 | 924 | 52716 | 57.0519 | 54.0519 | 0.1594 | 49944 | 0.15102 | 0.002794 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 305 south rd | C 8 Tripped Found tree in lines at 305 south rd no pole number .Backfeed applied at Rec 8820 to rec 6427 Fault isolated at ABS 4857 And 6712. Delay due to recloser 6427 no NOC close had to be closed on site hence 2 jobs. NDr to follow | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.15102 | 0.002794 | 2016 | 2015-11-04 | C | 924 | 0.15102 | 0.002794
7974288 | 2015-11-07 09:40 | 2015-11-07 10:38 | 58 | 28 | 1531.95 | 54.7125 | 51.7125 | 0.0046323 | 1447.95 | 0.0043783 | 8.4665e-05 | NAPA ID:14359 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 359738, P06802 | To Close temp line breaks at poles P06802 and 358640. Work Location: Range Road. Work Order: 30007285. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-07 | b | 0.0021891 | 4.2333e-05 | 2016 | 2015-11-07 | B | 28 | 0.0043783 | 8.4665e-05
7974405 | 2015-11-04 07:48 | 2015-11-04 08:43 | 54.6 | 1 | 54.6 | 54.6 | 51.6 | 0.0001651 | 51.6 | 0.00015603 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9657/1 | Cb 9657/1 found tripped. Possible cause 33kv tripping earlier in day | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.00015603 | 3.024e-06 | 2016 | 2015-11-04 | C | 1 | 0.00015603 | 3.0238e-06
7974500 | 2015-11-04 08:18 | 2015-11-04 10:29 | 130.9 | 310 | 39500.2 | 127.42 | 124.42 | 0.11944 | 38570.2 | 0.11663 | 0.00093737 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | v1393 | Recloser 9736 Trip NO flags Found line down at pole V1393 unknown cause isolated at ABS IC 355 no backfeed | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.11663 | 0.00093737 | 2016 | 2015-11-04 | C | 310 | 0.11663 | 0.00093737
7974853 | 2015-11-05 08:50 | 2015-11-05 16:17 | 446.2167 | 253 | 51227.7167 | 202.4811 | 199.4811 | 0.1549 | 50468.7167 | 0.15261 | 0.00076501 | NAPA ID:10622 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 751085 | Ap 1 Replace poles 751085 751097. Ap2 Remove temp fuses 39. Works location: Hamblyn St, McLean St. WO 30002062 | F2 | KATERE 10 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2015-11-05 | b | 0.076303 | 0.00038251 | 2016 | 2015-11-05 | B | 253 | 0.15261 | 0.00076501
7981957 | 2015-11-04 10:05 | 2015-11-04 13:40 | 214.8833 | 651 | 66940.85 | 102.8277 | 99.8277 | 0.20241 | 64987.85 | 0.19651 | 0.0019685 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9228 | at 10:05, Thames Sub, CB 4 Thames Coast Feeder, Recloser 9228 Tripped, O/C, L/O. Faultmen dispatched & investigation began. Line Patrolled & Sectionalised. No Fault Found, Unknown Cause. Was windy at the time of tripping. Stu Simpson Attended. | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.19651 | 0.0019685 | 2016 | 2015-11-04 | C | 651 | 0.19651 | 0.0019685
7982633 | 2015-11-04 10:11 | 2015-11-04 11:56 | 105.4833 | 1 | 105.4833 | 105.4833 | 102.4833 | 0.00031896 | 102.4833 | 0.00030989 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc3546 | 3x 2amp fuses birds strike | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.00030988 | 3.024e-06 | 2016 | 2015-11-04 | C | 1 | 0.00030989 | 3.0238e-06
7983924 | 2015-11-04 11:25 | 2015-11-04 12:22 | 57.3167 | 5 | 286.5833 | 57.3167 | 54.3167 | 0.00086656 | 271.5833 | 0.0008212 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20904 | Blown Jumper at Pole P20904. 2R Request for transformer Replacement Cancelled. Used 1m Squirrel Conductor and 2 x P/G Clamp | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.0008212 | 1.5119e-05 | 2016 | 2015-11-04 | C | 5 | 0.0008212 | 1.5119e-05
7984160 | 2015-11-04 11:52 | 2015-11-04 12:35 | 43.4 | 3 | 130.2 | 43.4 | 40.4 | 0.00039369 | 121.2 | 0.00036648 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1634 | Reload Reliven. 2 x 3A Fuses. Caused by Duck Strike | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.00036648 | 9.071e-06 | 2016 | 2015-11-04 | C | 3 | 0.00036648 | 9.0713e-06
7984360 | 2015-11-04 12:29 | 2015-11-04 13:49 | 80.1833 | 366 | 21271.1 | 58.1178 | 55.1178 | 0.064319 | 20173.1 | 0.060999 | 0.0011067 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | OAK 8 | OAK CB 8 Tripped on E/F. Patrolled Sectionalised. No Fault Found | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.060999 | 0.0011067 | 2016 | 2015-11-04 | C | 366 | 0.060999 | 0.0011067
7985180 | 2015-11-04 12:34 | 2015-11-04 16:30 | 235.5833 | 315 | 34452.9833 | 109.3746 | 106.3746 | 0.10418 | 33507.9833 | 0.10132 | 0.00095248 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713947 | CB TA8 L/O on E/F Sectionalised and found DDO hanging at transformer T5245. Isolated between TA824, 6388 & TA828. Repaired an relivened | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.10132 | 0.00095248 | 2016 | 2015-11-04 | C | 315 | 0.10132 | 0.00095248
7986672 | 2015-11-04 12:39 | 2015-11-04 17:58 | 318.75 | 209 | 32514.1667 | 155.5702 | 152.5702 | 0.098315 | 31887.1667 | 0.096419 | 0.00063197 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 721611 | CB NG3 L/O Sectionalised and found DDO hanging at trany N3308 on pole 721611. Isolated between ABS NG310 & NG326. Repaired & Relivened | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.096419 | 0.00063197 | 2016 | 2015-11-04 | C | 209 | 0.096419 | 0.00063197
7987428 | 2015-11-04 13:30 | 2015-11-04 16:16 | 165.9 | 232 | 30789.4667 | 132.7132 | 129.7132 | 0.0931 | 30093.4667 | 0.090995 | 0.00070151 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 840464 | Recloser 6497 Tripped on E/F. Burnt Cross arm found at Pole 840464 - Isolated at ABS 6092. Cross arm shortened at Conductor repaired - used 1 mtr of conductor and 1 sleeve | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.090995 | 0.00070151 | 2016 | 2015-11-04 | C | 232 | 0.090995 | 0.00070151
7988112 | 2015-11-04 13:45 | 2015-11-04 14:50 | 65.1667 | 14 | 912.3333 | 65.1667 | 62.1667 | 0.0027587 | 870.3333 | 0.0026317 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH841 | plz check if oms 7988187 is related? part power 53 Beach Road. Reload Reliven at Fuses WH841. 2 x 6A. Windy | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.0026317 | 4.2333e-05 | 2016 | 2015-11-04 | C | 14 | 0.0026317 | 4.2333e-05
7988157 | 2015-11-27 09:45 | 2015-11-27 12:44 | 179 | 3 | 537 | 179 | 176 | 0.0016238 | 528 | 0.0015965 | 9.0713e-06 | NAPA ID:14299 TP_MARTON GXP > RATA SUB > PUTORINO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1008 | Disconnect spur line at pole 805881 by glove and barrier method feeding transformer X1008, change hardware and transformer X1008, reconnect and test voltage. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-11-27 | b | 0.00079827 | 4.536e-06 | 2016 | 2015-11-27 | B | 3 | 0.0015965 | 9.0713e-06
7988269 | 2015-11-04 14:12 | 2015-11-04 17:01 | 169 | 212 | 15816.1 | 74.6042 | 71.6042 | 0.047824 | 15180.1 | 0.045901 | 0.00064104 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CB PU3 | Pungarehu CB PU 3 Tripped on EF, PH A Fault, Ground Fault. 287 Tipoka Road. Lines down touch the ground at this address. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.045901 | 0.00064104 | 2016 | 2015-11-04 | C | 212 | 0.045901 | 0.00064104
7989101 | 2015-11-04 15:17 | 2015-11-04 17:59 | 161.9333 | 1 | 161.9333 | 161.9333 | 158.9333 | 0.00048965 | 158.9333 | 0.00048058 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SB1-042 | at 17:38, Katikati Sub, CB 4 Wharawhara Rd Feeder. Faultman found 1x broken jumper at bottom of fuses SB1-042. Isolated at Fuses SB1-042. Permit issued & repairs carried out. All Power Restored on completion. Clint Johnstone Attended. No Materials Used (R | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.00048058 | 3.024e-06 | 2016 | 2015-11-04 | C | 1 | 0.00048058 | 3.0238e-06
7989230 | 2015-11-04 15:25 | 2015-11-04 15:32 | 6.6667 | 154 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00046566 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | H41 | H41 Trip flags. Ph B OC. PH C OC | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0 | 0.00046566 | 2016 | 2015-11-04 | C | 154 | 0 | 0.00046566
7989671 | 2015-11-04 16:59 | 2015-11-04 17:15 | 16 | 1 | 16 | 16 | 13 | 4.838e-05 | 13 | 3.9309e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | tree on line fell of before faultman arrived | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-11-04 | c | 3.9309e-05 | 3.024e-06 | 2016 | 2015-11-04 | C | 1 | 3.9309e-05 | 3.0238e-06
7995784 | 2015-11-04 16:59 | 2015-11-04 17:15 | 16 | 107 | 1712 | 16 | 13 | 0.0051767 | 1391 | 0.0042061 | 0.00032354 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Waiouru CB7. Tree on line which fell off before faultman got to site. 107 opened and Temp 02 closed. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.0042061 | 0.00032354 | 2016 | 2015-11-04 | C | 107 | 0.0042061 | 0.00032354
7995834 | 2015-11-04 16:59 | 2015-11-04 17:15 | 16.2 | 44 | 711.4 | 16.1682 | 13.1682 | 0.0021511 | 579.4 | 0.001752 | 0.00013305 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | N/A - NOT APPLICABLE | Waiouru CB7. Tree on line which fell off before faultman got to site. 107 opened and Temp 02 closed. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.001752 | 0.00013305 | 2016 | 2015-11-04 | C | 44 | 0.001752 | 0.00013305
7997723 | 2015-11-04 17:15 | 2015-11-04 18:46 | 90.5333 | 8 | 724.2667 | 90.5333 | 87.5333 | 0.00219 | 700.2667 | 0.0021174 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8178 | fuses reloaded & re livened possible line clash 2x8amp fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.0021174 | 2.419e-05 | 2016 | 2015-11-04 | C | 8 | 0.0021174 | 2.419e-05
7998727 | 2015-11-04 18:03 | 2015-11-04 21:30 | 207.0833 | 4 | 578.1333 | 144.5333 | 141.5333 | 0.0017481 | 566.1333 | 0.0017119 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD4-047 | 2xHV fuses blown at SD4-047 due to tree growing up through the lines at pole 203613. Isolation at fuses SD4-047 for tree cutters to remove tree. no back feeds available. No Asplundh staff available to respond to the tree fault. | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-11-04 | c | 0.0017119 | 1.2095e-05 | 2016 | 2015-11-04 | C | 4 | 0.0017119 | 1.2095e-05
7998882 | 2015-11-04 19:48 | 2015-11-04 20:46 | 57.9 | 4 | 231.6 | 57.9 | 54.9 | 0.0007003 | 219.6 | 0.00066402 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1215 | Lines down found at Transformer T1215. Isolated at Fuses TA113. Used 3 mtrs of conductor, 1 x sleeve, 2x fuse carriers, 2 x 3amp fuses. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.00066402 | 1.2095e-05 | 2016 | 2015-11-04 | C | 4 | 0.00066402 | 1.2095e-05
7998984 | 2015-11-04 20:29 | 2015-11-04 23:48 | 199.2833 | 8 | 1594.2667 | 199.2833 | 196.2833 | 0.0048207 | 1570.2667 | 0.0047481 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704567 | Lines down found at Pole 704567 - Isolated at Fuses 6297. Used 60 mtrs of Conductor, 5 x sleeves, 1 binder | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-11-04 | c | 0.0047481 | 2.419e-05 | 2016 | 2015-11-04 | C | 8 | 0.0047481 | 2.419e-05
7999614 | 2015-11-05 04:07 | 2015-11-05 05:22 | 75.2333 | 1 | 75.2333 | 75.2333 | 72.2333 | 0.00022749 | 72.2333 | 0.00021842 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | X1115 | Fuse found blown at Transformer X1115 - due to possum. Used 2 x 3amp fuses | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-05 | c | 0.00021842 | 3.024e-06 | 2016 | 2015-11-05 | C | 1 | 0.00021842 | 3.0238e-06
7999628 | 2015-11-05 04:55 | 2015-11-05 06:32 | 96.9 | 3 | 290.7 | 96.9 | 93.9 | 0.00087901 | 281.7 | 0.00085179 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1305 | Fuses found blown at Transformer T1305. Used 2 x 3amp fuses | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-11-05 | c | 0.00085179 | 9.071e-06 | 2016 | 2015-11-05 | C | 3 | 0.00085179 | 9.0713e-06
7999652 | 2015-11-05 05:34 | 2015-11-05 07:00 | 85.7333 | 1 | 85.7333 | 85.7333 | 82.7333 | 0.00025924 | 82.7333 | 0.00025017 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 6488 | Replace 2 x 6A fuses. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-11-05 | c | 0.00025017 | 3.024e-06 | 2016 | 2015-11-05 | C | 1 | 0.00025017 | 3.0238e-06
7999694 | 2015-11-05 06:08 | 2015-11-05 08:15 | 126.95 | 19 | 2412.05 | 126.95 | 123.95 | 0.0072935 | 2355.05 | 0.0071211 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 2336 | 1 x 8 amp fuse unknown | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-05 | c | 0.0071211 | 5.7451e-05 | 2016 | 2015-11-05 | C | 19 | 0.0071211 | 5.7451e-05
7999736 | 2015-11-05 06:42 | 2015-11-05 09:01 | 138.35 | 1 | 138.35 | 138.35 | 135.35 | 0.00041834 | 135.35 | 0.00040927 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2926 | isolated tx for lv work repair line down | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-11-05 | c | 0.00040927 | 3.024e-06 | 2016 | 2015-11-05 | C | 1 | 0.00040927 | 3.0238e-06
8001612 | 2015-11-05 08:01 | 2015-11-05 08:28 | 27.0167 | 4722 | 50990.1 | 10.7984 | 7.7984 | 0.15418 | 36824.1 | 0.11135 | 0.014278 |  | 11 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | CB INC 1 | * 11kV CB INC 1 tripped E/F O/C L/O. Loss of supply to all feeders. * Background info: T2 Transformer removed from service at time via planned works SIS 13961, commenced on the 4th. * Due to an overly cold morning (Previous week load checks approx 50Amps | F2 | ARMSTRONG ST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-05 | c | 0.11135 | 0.014278 | 2016 | 2015-11-05 | C | 4722 | 0.11135 | 0.014278
8011345 | 2015-11-05 08:08 | 2015-11-05 14:12 | 364.4167 | 302 | 25990.3 | 86.0606 | 83.0606 | 0.078588 | 25084.3 | 0.075849 | 0.00091318 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M2309 | CB 3 Tripped on B & C OC due to a truck V pole. Backfeeds from TIR9 via Sectionaliser 9777. Isolated at ABS 915, ABS IP62 & ABS 877. Nearest side rd - state Highway 5. **lines down on truck (person tapped in truck). Fire Comms Event # F1951043. NDR 5 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-11-05 | c | 0.075849 | 0.00091318 | 2016 | 2015-11-05 | C | 302 | 0.075849 | 0.00091318
8013179 | 2015-11-05 09:24 | 2015-11-05 09:29 | 5 | 4 | 20 | 5 | 2 | 6.0475e-05 | 8 | 2.419e-05 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | 153 DIAGONAL ROAD | Isolated at fuses FC2307 tap transformer up customer wanted someone after milking time. Job actually at TC 4311 low voltage at cow shed. Referral of 7999033 | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-11-05 | c | 2.419e-05 | 1.2095e-05 | 2016 | 2015-11-05 | C | 4 | 2.419e-05 | 1.2095e-05
8014400 | 2015-11-25 09:20 | 2015-11-25 14:43 | 323 | 3 | 969 | 323 | 320 | 0.00293 | 960 | 0.0029028 | 9.0713e-06 | NAPA ID:13672 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4556 | Pole M12840 & TC4556 - replace all crossarms + install LV disconnectors. Works location: Old taupo Rd, Arapuni. WO 30011798 | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-11-25 | b | 0.0014514 | 4.536e-06 | 2016 | 2015-11-25 | B | 3 | 0.0029028 | 9.0713e-06
8014817 | 2015-11-22 08:30 | 2015-11-22 15:55 | 445 | 19 | 7806 | 410.8421 | 407.8421 | 0.023603 | 7749 | 0.023431 | 5.7451e-05 | NAPA ID:12974 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4-074 | Install new CFCF Safelink Sw/gear 9984 between pole 213319 and existing Sw/gear 9672/1. Live Line Permit will be required to disconnect HV cable feeding 9672/1. Remove from the network redundant Fuses SC4-088, SC4-090, SC4-089 and associated cabling. Re | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-11-22 | b | 0.011716 | 2.8726e-05 | 2016 | 2015-11-22 | B | 19 | 0.023431 | 5.7451e-05
8040086 | 2015-11-26 09:43 | 2015-11-26 14:34 | 290.9 | 7 | 2036.3 | 290.9 | 287.9 | 0.0061573 | 2015.3 | 0.0060938 | 2.1166e-05 | NAPA ID:13252 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1316 | To replace arms & Hardware Beyond FP1316. Works location: Given Rd, Walton. WO 30014505 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-26 | b | 0.0030469 | 1.0583e-05 | 2016 | 2015-11-26 | B | 7 | 0.0060938 | 2.1166e-05
8040950 | 2015-11-05 19:07 | 2015-11-07 17:43 | 2796 | 508 | 105130.1 | 206.949 | 203.949 | 0.31789 | 103606.1 | 0.31328 | 0.0015361 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 219989 | 7.14pm - advise Carlo at Fire Comms of 10 min eta. NDR 34414. Serious crash unit on site, not letting lines crews begin to work until scene all mapped out & they are clear. Crews waiting on site. Multiple poles down Line breaks going to be cut to allow so | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-05 | c | 0.31328 | 0.0015361 | 2016 | 2015-11-05 | C | 508 | 0.31328 | 0.0015361
8042973 | 2015-11-06 07:42 | 2015-11-06 12:59 | 316.8 | 317 | 18072.55 | 57.0112 | 54.0112 | 0.054647 | 17121.55 | 0.051771 | 0.00095853 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772282 | Part of 8042945. HV Line down at Pole 772282. Isolated at ABS O61 Repairs made &.ABS O61 closed, CB 282 tripped. ABS O61 Opened & CB 282 relivened. Materials used: 2mtrs of Ali conductor & 2x Ali sleeves. Fuses 4289 Opened - Transformer 4597W blown & requ | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-06 | c | 0.051771 | 0.00095853 | 2016 | 2015-11-06 | C | 317 | 0.051771 | 0.00095853
8044033 | 2015-11-06 07:14 | 2015-11-06 08:36 | 81.7 | 1 | 81.7 | 81.7 | 78.7 | 0.00024704 | 78.7 | 0.00023797 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | FC917 | Unplanned outage for aerial spraying. TJ Tanoa has confirmed that the outage only affects the farmer who is doing the spraying. The job was planned but it was incorrectly identified as an LV service line. When crew arrived on site the line was found to be | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-06 | c | 0.00023797 | 3.024e-06 | 2016 | 2015-11-06 | C | 1 | 0.00023797 | 3.0238e-06
8050036 | 2015-11-06 08:55 | 2015-11-06 11:42 | 167.05 | 1 | 167.05 | 167.05 | 164.05 | 0.00050512 | 164.05 | 0.00049605 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7 | Replaced 2x 2Amp HV Fuse Links | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-11-06 | c | 0.00049605 | 3.024e-06 | 2016 | 2015-11-06 | C | 1 | 0.00049605 | 3.0238e-06
8052991 | 2015-11-06 15:39 | 2015-11-06 19:59 | 260.4167 | 90 | 12978.4333 | 144.2048 | 141.2048 | 0.039244 | 12708.4333 | 0.038427 | 0.00027214 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 693 | TP Waverley - CB242 Waitotara. Recloser 693 trip flags Ph C OC, EF. Line patrolled. Found Transformer X672 Faulty Replaced ( 1 x 15kVA). | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-06 | c | 0.038427 | 0.00027214 | 2016 | 2015-11-06 | C | 90 | 0.038427 | 0.00027214
8053422 | 2015-11-06 16:20 | 2015-11-06 20:25 | 244.6667 | 8 | 1957.3333 | 244.6667 | 241.6667 | 0.0059185 | 1933.3333 | 0.0058459 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1779 | 4.24pm map not jumping to map, have checked active jobs no other jobs for this substation or feeder Replace 3 x lightning arrestors,11kV. Replaced 5 amp fuse. Transformer 1779N. Cause: fuse was blown, when new fuse fitted, lightning arrestors blew. The | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-11-06 | c | 0.0058459 | 2.419e-05 | 2016 | 2015-11-06 | C | 8 | 0.0058459 | 2.419e-05
8053786 | 2015-11-06 18:02 | 2015-11-07 01:58 | 475.55 | 4 | 1902.2 | 475.55 | 472.55 | 0.0057518 | 1890.2 | 0.0057155 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2213 | at 20:49, Mikkelsen Rd Sub, CB 8 Springdale Feeder. Found transformer TC2213 had faulted. Own Isolation & AP carried out. Transformer Replaced, All Power Restored on Completion. Pieter Diedericks Attended. 1x Transformer & 4x HV Fuses Replaced. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-06 | c | 0.0057155 | 1.2095e-05 | 2016 | 2015-11-06 | C | 4 | 0.0057155 | 1.2095e-05
8056593 | 2015-11-07 14:40 | 2015-11-07 15:30 | 50 | 329 | 16450 | 50 | 47 | 0.049741 | 15463 | 0.046756 | 0.00099482 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783 | Check for safety - Crossarm broken and lines arcing. Stephanie 06 3455 599.Faultman found that the jumpers were burnt on ABS 783, line was isolated at ABS's 1031 & 1158 to replace 11kV jumpers, Faultman has also defected the ABS 783 needs contacts to be c | F3 | DURIE HILL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-11-07 | c | 0.046756 | 0.00099482 | 2016 | 2015-11-07 | C | 329 | 0.046756 | 0.00099482
8056621 | 2015-11-07 14:35 | 2015-11-07 17:50 | 194.8833 | 1 | 194.8833 | 194.8833 | 191.8833 | 0.00058928 | 191.8833 | 0.00058021 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2274 | Hub gave Faultman incorrect address, faultman found blown fuses on transformer X2274. 2 X 2 amp HV fuses replaced. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-07 | c | 0.00058021 | 3.024e-06 | 2016 | 2015-11-07 | C | 1 | 0.00058021 | 3.0238e-06
8075224 | 2015-11-07 17:35 | 2015-11-09 13:32 | 2637.6167 | 14 | 28569.2333 | 2040.6595 | 2037.6595 | 0.086387 | 28527.2333 | 0.08626 | 4.2333e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4781 | Blown Fuse And Lightning Arrestor found ay Fuses FC2434. Isolated at Fuses TC4789 Lightening Arrestor cut away and Fuse replaced- Fuse blow on livening - line patrolled up to Fuses FC4204 which hadn't blown with no fault found. Fuses FC4204 opened and Fus | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-07 | c | 0.08626 | 4.2333e-05 | 2016 | 2015-11-07 | C | 14 | 0.08626 | 4.2333e-05
8078535 | 2015-11-08 04:50 | 2015-11-08 07:05 | 135.45 | 1 | 135.45 | 135.45 | 132.45 | 0.00040957 | 132.45 | 0.0004005 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU250 | Faultman found blown fuses at Fuses PU250, suspect cause was a bird strike. 2 X 6 amp HV fuses replaced. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-11-08 | c | 0.0004005 | 3.024e-06 | 2016 | 2015-11-08 | C | 1 | 0.0004005 | 3.0238e-06
8081473 | 2015-11-08 10:01 | 2015-11-08 10:52 | 51.1 | 1 | 51.1 | 51.1 | 48.1 | 0.00015451 | 48.1 | 0.00014544 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of planned outage taking place today, customer advises they did not get notice, advised customer of outage end time of 4pm. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-08 | c | 0.00014544 | 3.024e-06 | 2016 | 2015-11-08 | C | 1 | 0.00014544 | 3.0238e-06
8081696 | 2015-11-08 10:30 | 2015-11-08 12:15 | 105.2833 | 2 | 210.5667 | 105.2833 | 102.2833 | 0.0006367 | 204.5667 | 0.00061856 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H3135 | 2 x 3 amp fuses replaced at FC2125. Line had been patrolled and nothing found. Fuses on site are labelled with FP595. Label issue requires addressing | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-08 | c | 0.00061856 | 6.048e-06 | 2016 | 2015-11-08 | C | 2 | 0.00061856 | 6.0475e-06
8085738 | 2015-11-08 17:56 | 2015-11-08 19:57 | 121.3333 | 17 | 2062.6667 | 121.3333 | 118.3333 | 0.006237 | 2011.6667 | 0.0060828 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 113 | Replaced 2x 6Amp HV Links | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-11-08 | c | 0.0060828 | 5.1404e-05 | 2016 | 2015-11-08 | C | 17 | 0.0060828 | 5.1404e-05
8093590 | 2015-11-09 07:00 | 2015-11-09 08:16 | 75.5667 | 4 | 289.4 | 72.35 | 69.35 | 0.00087508 | 277.4 | 0.00083879 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7312 | 1 fuse at 7310 and 2 fuses at 7312. 3 x 10 amp fuses at 7312. Suspect bird strike. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-11-09 | c | 0.00083879 | 1.2095e-05 | 2016 | 2015-11-09 | C | 4 | 0.00083879 | 1.2095e-05
8100809 | 2015-11-10 07:39 | 2015-11-10 11:40 | 240.9167 | 154 | 18522.9667 | 120.279 | 117.279 | 0.056009 | 18060.9667 | 0.054612 | 0.00046566 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711743 | Feeder fault. Line down at pole 711743 isolated at ABS NG425 326 455 Backfed via NG408. Materials: 2 sleeves, 3m conductor, 1 insulator. Unknown reason for failure. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-11-10 | c | 0.054612 | 0.00046566 | 2016 | 2015-11-10 | C | 154 | 0.054612 | 0.00046566
8100830 | 2015-11-25 11:05 | 2015-11-25 13:18 | 133 | 1 | 133 | 133 | 130 | 0.00040216 | 130 | 0.00039309 | 3.0238e-06 | NAPA ID:14575 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV FC2335 | Pole straightens and Anchors. Works location: Gordon Te Aroha Rd, Te Aroha. WO 30015346 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-25 | b | 0.00019654 | 1.512e-06 | 2016 | 2015-11-25 | B | 1 | 0.00039309 | 3.0238e-06
8101024 | 2015-11-10 07:39 | 2015-11-10 07:41 | 2 | 254 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00076804 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | A/R C927 | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-11-10 | c | 0 | 0.00076804 | 2016 | 2015-11-10 | C | 254 | 0 | 0.00076804
8102161 | 2015-11-10 09:07 | 2015-11-10 11:25 | 138 | 1160 | 43388.35 | 37.4038 | 34.4038 | 0.1312 | 39908.35 | 0.12067 | 0.0035076 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CA161 | 8.39 advised Joanne at Hub 8.43 advised fire eta is 15-20 mins 0901 car v pole hunter st hub advised link CA161 found burnt out Materials used 1 link ddo unit | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-11-10 | c | 0.12067 | 0.0035076 | 2016 | 2015-11-10 | C | 1160 | 0.12067 | 0.0035076
8102251 | 2015-11-10 08:51 | 2015-11-10 09:06 | 14.8667 | 1090 | 13625.4667 | 12.5004 | 9.5004 | 0.0412 | 10355.4667 | 0.031312 | 0.0032959 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Arahina - Rata 33kV | Tripping on Arahina-Rata 33kV line on E/F, Phase A O/C. Rata Sub Backfeed via Pukepapa CB1133 and full line patrol carried out. Nothing was found and All restored OK. Suspect Bird Strike. | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-11-10 | c | 0.031312 | 0.0032959 | 2016 | 2015-11-10 | C | 1090 | 0.031312 | 0.0032959
8107247 | 2015-11-10 10:52 | 2015-11-10 12:45 | 113 | 3 | 338.1 | 112.7 | 109.7 | 0.0010223 | 329.1 | 0.00099512 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6211 | Reload Reliven at Transformer TC6211. ICP my be related to wrong transformer. 3x20A Fuses. Incorrect fuse rating(3A) | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-11-10 | c | 0.00099512 | 9.071e-06 | 2016 | 2015-11-10 | C | 3 | 0.00099512 | 9.0713e-06
8111581 | 2015-11-10 17:50 | 2015-11-10 20:30 | 160.3167 | 3 | 480.95 | 160.3167 | 157.3167 | 0.0014543 | 471.95 | 0.0014271 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | W2470 | Blown transformer W2470. FM requested 2R to replace transformer. Faultman replaced faulty transformer W2470. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-11-10 | c | 0.0014271 | 9.071e-06 | 2016 | 2015-11-10 | C | 3 | 0.0014271 | 9.0713e-06
8111873 | 2015-11-10 20:35 | 2015-11-11 01:42 | 306.2333 | 4 | 1224.9333 | 306.2333 | 303.2333 | 0.0037039 | 1212.9333 | 0.0036676 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12997 | transformer TC2159 requires replacement Mike James own isolation's & AP to replace. Transformer replaced, all service restored. Materials 1 x 30 kva transformer | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-11-10 | c | 0.0036676 | 1.2095e-05 | 2016 | 2015-11-10 | C | 4 | 0.0036676 | 1.2095e-05
8111954 | 2015-11-10 22:41 | 2015-11-10 23:10 | 29.4 | 1 | 29.4 | 29.4 | 26.4 | 8.8899e-05 | 26.4 | 7.9827e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | T2231 | Faultman found 2 blown fuses at transformer T2231 due to a Opossum on the transformer. 2 X 15 amp HV fuses replaced. | F3 | ESSEX ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-11-10 | c | 7.9827e-05 | 3.024e-06 | 2016 | 2015-11-10 | C | 1 | 7.9827e-05 | 3.0238e-06
8112318 | 2015-11-10 23:49 | 2015-11-11 00:58 | 69.85 | 107 | 6233.6167 | 58.2581 | 55.2581 | 0.018849 | 5912.6167 | 0.017878 | 0.00032354 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P13891 | Recloser E33 tripped on A & B phase O/C & E/F flags, line was patrolled and isolated and a Opossum was found on th elines at pole P13891, faultman removed the Opossum with a hot stick. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-10 | c | 0.017878 | 0.00032354 | 2016 | 2015-11-10 | C | 107 | 0.017878 | 0.00032354
8117827 | 2015-11-26 08:45 | 2015-11-26 09:53 | 68 | 122 | 8296 | 68 | 65 | 0.025085 | 7930 | 0.023978 | 0.0003689 | NAPA ID:12911 TP_TAURANGA 33 GXP > KAURI POINT > LINDERMANN RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SB2-010 | Replace SD1 with CFCC Safelink 13021. Works location: Hwy 2 Tahawai, Katikati. WO 10147833. This outage was cancelled after an hour due to late traffic management. The outage will be reapplied for. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-11-26 | b | 0.011989 | 0.00018445 | 2016 | 2015-11-26 | B | 122 | 0.023978 | 0.0003689
8118696 | 2015-11-12 09:59 | 2015-11-12 13:30 | 211 | 1 | 211 | 211 | 208 | 0.00063801 | 208 | 0.00062894 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2253 | Advised hub of pole down. TX structure on ground, isolated through Control. Seems like it may have been like this for some time. Just feeding a water pump. Replaced Pole including Hardware and Transformer T2253. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.00062894 | 3.024e-06 | 2016 | 2015-11-12 | C | 1 | 0.00062894 | 3.0238e-06
8118914 | 2015-12-02 10:05 | 2015-12-02 16:50 | 405 | 11 | 4455 | 405 | 402 | 0.013471 | 4422 | 0.013371 | 3.3261e-05 | NAPA ID:14062 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F59 | Tree removal close to 11kV. Works location: Pohangina Rd, Ashhurst. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0066855 | 1.6631e-05 | 2016 | 2015-12-02 | B | 11 | 0.013371 | 3.3261e-05
8118917 | 2015-12-03 10:01 | 2015-12-03 14:25 | 263.7667 | 28 | 7385.4667 | 263.7667 | 260.7667 | 0.022332 | 7301.4667 | 0.022078 | 8.4665e-05 | NAPA ID:14486 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Links 2996 | Tree trimming near poles 783017, and 783018. Works location: Koatanui Rd, Wanganui. WO 10152359 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.011039 | 4.2333e-05 | 2016 | 2015-12-03 | B | 28 | 0.022078 | 8.4665e-05
8118936 | 2015-11-11 12:38 | 2015-11-12 13:30 | 1491.8833 | 1 | 1491.8833 | 1491.8833 | 1488.8833 | 0.0045111 | 1488.8833 | 0.004502 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 7191 | TX has blown HV fuses and is is so hot its about to explode - FM has isolated and spoken to control Power has not been restored but this is only feeding one home stay dwelling that is vacant 2R for pillar to be replaced Spoke to control and unable to sig | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-11-11 | c | 0.004502 | 3.024e-06 | 2016 | 2015-11-11 | C | 1 | 0.004502 | 3.0238e-06
8119359 | 2015-11-11 13:02 | 2015-11-11 16:30 | 208.2167 | 882 | 137411.2333 | 155.795 | 152.795 | 0.4155 | 134765.2333 | 0.4075 | 0.002667 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 9864 | The crew requested on the child job attached was in error. Forwarded to the hub. Lines down. Tree contractors dropped branch on to the line past recloser 9864/2, recloser A/R, fault current bought line down up stream of recloser 9864 & tripped CB 7. Isola | F3 | VALE ST | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-11-11 | c | 0.4075 | 0.002667 | 2016 | 2015-11-11 | C | 882 | 0.4075 | 0.002667
8123694 | 2015-11-23 08:50 | 2015-11-23 16:03 | 433.2 | 112 | 48518.4 | 433.2 | 430.2 | 0.14671 | 48182.4 | 0.14569 | 0.00033866 | NAPA ID:13111 TP_BUNNYTHORPE GXP > MILSON SUB > GEMINI | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/452 | replace to legs of 11KV U/G cable feeding transfomer T6/452. Works location: JFK Drive. WO 30013577 | F3 | GEMINI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-23 | b | 0.072846 | 0.00016933 | 2016 | 2015-11-23 | B | 112 | 0.14569 | 0.00033866
8123707 | 2015-11-11 15:38 | 2015-11-11 15:52 | 13.85 | 26 | 360.1 | 13.85 | 10.85 | 0.0010889 | 282.1 | 0.000853 | 7.8618e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4015 | Shane noticed a large oil leak coming from Transformer TC4015. With NOC an emergency shutdown was started to replace the transformer under own AP. Transformer replaced, relivened OK. Shane commented on the transformer being very small, 50kVA for 26 ICP's | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-11 | c | 0.000853 | 7.8618e-05 | 2016 | 2015-11-11 | C | 26 | 0.000853 | 7.8618e-05
8142575 | 2015-11-12 01:19 | 2015-11-12 04:18 | 179 | 26 | 3900 | 150 | 147 | 0.011793 | 3822 | 0.011557 | 7.8618e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC1477 | Suspected blown H/V fuse in G/M transformer TC1477. Isolation at Sw/Gear 9280/1. Fuse replaced all service restored. Isolated a second time to check & tighten loose connections to fusing on L/V bus bar ( sparking ) caused H/V fuse to blow. All repairs car | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-12 | c | 0.011557 | 7.8618e-05 | 2016 | 2015-11-12 | C | 26 | 0.011557 | 7.8618e-05
8142884 | 2015-11-12 05:38 | 2015-11-12 06:40 | 62.3333 | 8 | 498.6667 | 62.3333 | 59.3333 | 0.0015078 | 474.6667 | 0.0014353 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7236 | Fuses 7236 2 x 10 amp fuses birdstrike | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.0014353 | 2.419e-05 | 2016 | 2015-11-12 | C | 8 | 0.0014353 | 2.419e-05
8142928 | 2015-11-12 05:37 | 2015-11-12 06:40 | 63 | 1 | 63 | 63 | 60 | 0.0001905 | 60 | 0.00018143 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t1093 | this was related to 8142884 icp is wron should be fed off T1093 jason hall confirmed | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.00018143 | 3.024e-06 | 2016 | 2015-11-12 | C | 1 | 0.00018143 | 3.0238e-06
8144946 | 2015-12-01 09:45 | 2015-12-01 12:12 | 147 | 6 | 882 | 147 | 144 | 0.002667 | 864 | 0.0026125 | 1.8143e-05 | NAPA ID:13245 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC298 | To replace the 11kV Pin arm, D.O.Fuse arm, 400V Pin Arm & install a 3 phase 400V fuse disconnector. Works location: McLaren Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.0013063 | 9.071e-06 | 2016 | 2015-12-01 | B | 6 | 0.0026125 | 1.8143e-05
8145023 | 2015-11-13 08:25 | 2015-11-13 16:50 | 505 | 251 | 24484 | 97.5458 | 94.5458 | 0.074034 | 23731 | 0.071757 | 0.00075896 | NAPA ID:14665 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-134 | Replace HV terminations in Transformer TD4-134 Step 1 09:15 to 10:00 open 9970/4. AP to remove H.V cable going to TD4-134 at SD4-566, then reliven. Step 2 10:00 to 14:30. AP to reterminate HV cable at transformer TD4-134. Step 3 14:30 to 15:30 open 9 | F3 | MAUNGATAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-11-13 | b | 0.035878 | 0.00037948 | 2016 | 2015-11-13 | B | 251 | 0.071757 | 0.00075896
8145054 | 2015-12-01 10:00 | 2015-12-01 10:45 | 45 | 5 | 225 | 45 | 42 | 0.00068035 | 210 | 0.00063499 | 1.5119e-05 | NAPA ID:13282 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3002 | Install a 400V Fuse disconnector on TC3002. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.00031749 | 7.559e-06 | 2016 | 2015-12-01 | B | 5 | 0.00063499 | 1.5119e-05
8145090 | 2015-12-01 12:00 | 2015-12-01 12:50 | 50 | 3 | 150 | 50 | 47 | 0.00045356 | 141 | 0.00042635 | 9.0713e-06 | NAPA ID:13283 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3026 | To install a 3 phase 400V Fuse Disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.00021317 | 4.536e-06 | 2016 | 2015-12-01 | B | 3 | 0.00042635 | 9.0713e-06
8145415 | 2015-12-08 10:01 | 2015-12-08 10:59 | 57.8167 | 3 | 173.45 | 57.8167 | 54.8167 | 0.00052447 | 164.45 | 0.00049726 | 9.0713e-06 | NAPA ID:14531 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | F42 | Tree cutting around 11kV. Works location: Pohangina Rd, Ashhurst. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-12-08 | b | 0.00024863 | 4.536e-06 | 2016 | 2015-12-08 | B | 3 | 0.00049726 | 9.0713e-06
8146217 | 2015-12-01 10:30 | 2015-12-01 13:42 | 192 | 2 | 384 | 192 | 189 | 0.0011611 | 378 | 0.001143 | 6.0475e-06 | NAPA ID:14503 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P00495 | To replace cross arms and re sag 11kV conductor. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-01 | b | 0.00057149 | 3.024e-06 | 2016 | 2015-12-01 | B | 2 | 0.001143 | 6.0475e-06
8146245 | 2015-12-02 09:30 | 2015-12-02 14:04 | 274 | 5 | 1370 | 274 | 271 | 0.0041426 | 1355 | 0.0040972 | 1.5119e-05 | NAPA ID:13939 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P21768 | Resag conductor between poles P21768 and pole P21781. Works location: Sandon Rd, Halcom. WO 30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0020486 | 7.559e-06 | 2016 | 2015-12-02 | B | 5 | 0.0040972 | 1.5119e-05
8146387 | 2015-12-01 10:20 | 2015-12-01 15:28 | 308 | 10 | 3080 | 308 | 305 | 0.0093132 | 3050 | 0.0092225 | 3.0238e-05 | NAPA ID:13951 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M12421,M1298, M1300, M1305, M1310, M1311, M1313, M12427, M1246 | Poles: M12421, M1298, M1300, M1305, M1310, M1311, M1313, M12427, M1246 - Replace all 11kV arms and LV arms. Works location: Waotu Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.0046112 | 1.5119e-05 | 2016 | 2015-12-01 | B | 10 | 0.0092225 | 3.0238e-05
8147062 | 2015-11-12 14:00 | 2015-11-12 14:33 | 33.2833 | 22 | 732.2333 | 33.2833 | 30.2833 | 0.0022141 | 666.2333 | 0.0020145 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1256 | Replaced 1 Dead End Insulator at Transformer TC1256. FM was Grant Jorden | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-12 | c | 0.0020145 | 6.6523e-05 | 2016 | 2015-11-12 | C | 22 | 0.0020145 | 6.6523e-05
8147159 | 2015-12-01 14:08 | 2015-12-01 14:23 | 15 | 5 | 75 | 15 | 12 | 0.00022678 | 60 | 0.00018143 | 1.5119e-05 | NAPA ID:13246 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2952 | To install a 400V Fuse disconnector on TC2952. Works location: McLaren Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 9.0713e-05 | 7.559e-06 | 2016 | 2015-12-01 | B | 5 | 0.00018143 | 1.5119e-05
8147311 | 2015-11-12 13:55 | 2015-11-12 19:29 | 333.8167 | 332 | 84560.1333 | 254.6992 | 251.6992 | 0.25569 | 83564.1333 | 0.25268 | 0.0010039 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 802030 | Possible feeder fault at 4217 informed hub. Faultman found Recloser 4217/2 open on arrival, line was patrolled and sectionalised and a broken cross arm was found at pole 802030, line was isolated at ABS' 030, 4217/6 & Links 4217/6 to replace the cross arm | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.25268 | 0.0010039 | 2016 | 2015-11-12 | C | 332 | 0.25268 | 0.0010039
8147442 | 2015-12-01 08:30 | 2015-12-01 15:13 | 403 | 49 | 19747 | 403 | 400 | 0.05971 | 19600 | 0.059266 | 0.00014816 | NAPA ID:14211 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-017 | REPLACE 33KV FEEDER POLES AND ARMS. Works location: Wairoa Rd. WO 30002512 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.029633 | 7.4082e-05 | 2016 | 2015-12-01 | B | 49 | 0.059266 | 0.00014816
8149324 | 2015-11-12 17:18 | 2015-11-12 19:00 | 101.5667 | 1 | 101.5667 | 101.5667 | 98.5667 | 0.00030711 | 98.5667 | 0.00029804 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2576T | 2 x2amp HV Fuse blown due to LV termination fault. Fault went through the LV transformer fusing. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.00029804 | 3.024e-06 | 2016 | 2015-11-12 | C | 1 | 0.00029804 | 3.0238e-06
8149337 | 2015-11-12 17:21 | 2015-11-12 20:35 | 194.5 | 232 | 14571.25 | 62.8071 | 59.8071 | 0.04406 | 13875.25 | 0.041955 | 0.00070151 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11458 | CB 1 tripped on E/F flags, line was patrolled and sectionalised. Broken Conductor found beyond fuses S16. 3m No.8 Conductor sleeved in and 3 binders replaced. Conductors in this area now in poor condition. Relivened OK. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-11-12 | c | 0.041955 | 0.00070151 | 2016 | 2015-11-12 | C | 232 | 0.041955 | 0.00070151
8150435 | 2015-11-12 18:06 | 2015-11-12 18:24 | 18 | 2318 | 34521.5667 | 14.8928 | 11.8928 | 0.10438 | 27567.5667 | 0.083358 | 0.0070091 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 342 | Tripping on Taupo Quay 33kV CB342 causing loss of supply to Sub. (Phase B-C O/C) Sub initially backfed via CB1 Tie Cable and Hatricks CBs 6 and 9. Full inspection carried out on Sub, Sw/Gear and Transformer by Technician. No cause found, relivened OK and | F1,F2,F3 | TAUPO QUAY 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 2015-11-12 | c | 0.083358 | 0.0070091 | 2016 | 2015-11-12 | C | 2318 | 0.083358 | 0.0070091
8154404 | 2015-11-12 18:32 | 2015-11-13 01:04 | 391.5333 | 81 | 5382.1333 | 66.4461 | 63.4461 | 0.016274 | 5139.1333 | 0.01554 | 0.00024492 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12359 | 1 HV fuse top broken at transformer TC2407. Replaced all Three fuse holders & fuse crossarm. Isolated at ABS IC454, IP620, IC501 & IC465. 3 HV fuse holders, 3x 3amp HV fuse links 1xcrossarm | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-12 | c | 0.01554 | 0.00024493 | 2016 | 2015-11-12 | C | 81 | 0.01554 | 0.00024492
8155212 | 2015-11-13 06:41 | 2015-11-13 08:11 | 89.85 | 2 | 179.7 | 89.85 | 86.85 | 0.00054337 | 173.7 | 0.00052523 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8440 | 2 X 25 Amp Fuses | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-11-13 | c | 0.00052523 | 6.048e-06 | 2016 | 2015-11-13 | C | 2 | 0.00052523 | 6.0475e-06
8155253 | 2015-11-13 07:03 | 2015-11-13 08:58 | 114.7833 | 3516 | 152996.15 | 43.5143 | 40.5143 | 0.46262 | 142448.15 | 0.43073 | 0.010632 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | CB242 tripped. LOS experienced at Lake Rd, Tower Rd and Tirau Substations. Isolated each substation and backfeeds put in place. Faultmen dispatched to investigate Bus work - no cause of fault located. Cable testers dispatched to site and undertook cable | F1,F2,F3 | HINUERA242-BROWNE ST 33KV | HINUERA | Valley | TP_HINUERA | Eastern Electricity | POWERCO | 2015-11-13 | c | 0.43073 | 0.010632 | 2016 | 2015-11-13 | C | 3516 | 0.43073 | 0.010632
8158818 | 2015-11-13 07:03 | 2015-11-13 08:39 | 96 | 1434 | 83055 | 57.9184 | 54.9184 | 0.25114 | 78753 | 0.23813 | 0.0043361 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 3232 Tripped O/C on zone 1 line fault suspect seeing fault on CB 242 Hin(8155253) Protection review needed. | F1 | ARAPUNI ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-11-13 | c | 0.23813 | 0.0043361 | 2016 | 2015-11-13 | C | 1434 | 0.23813 | 0.0043361
8165661 | 2015-12-04 09:45 | 2015-12-04 15:45 | 360 | 12 | 4320 | 360 | 357 | 0.013063 | 4284 | 0.012954 | 3.6285e-05 | NAPA ID:14372 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV B10 | Change 7 x poles and 6 x xarms. Works location: Maindrain Rd. WO 30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-04 | b | 0.0064769 | 1.8143e-05 | 2016 | 2015-12-04 | B | 12 | 0.012954 | 3.6285e-05
8165862 | 2015-12-01 08:45 | 2015-12-01 12:43 | 238 | 1 | 238 | 238 | 235 | 0.00071966 | 235 | 0.00071058 | 3.0238e-06 | NAPA ID:13840 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7879 | Replace 11kV transformer pole. Works location: Tanawa Rd, Masterton. WO 30013477 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-01 | b | 0.00035529 | 1.512e-06 | 2016 | 2015-12-01 | B | 1 | 0.00071058 | 3.0238e-06
8166111 | 2015-12-01 09:29 | 2015-12-01 11:45 | 136 | 13 | 1768 | 136 | 133 | 0.005346 | 1729 | 0.0052281 | 3.9309e-05 | NAPA ID:14108 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 795278 | Replace poles 795278 /795265 poles in poor condition. Works location: Wairepu East Rd, Taihape. WO 10161734 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-01 | b | 0.002614 | 1.9654e-05 | 2016 | 2015-12-01 | B | 13 | 0.0052281 | 3.9309e-05
8166218 | 2015-12-02 09:15 | 2015-12-02 14:31 | 316 | 3 | 948 | 316 | 313 | 0.0028665 | 939 | 0.0028393 | 9.0713e-06 | NAPA ID:13253 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP776 | To replace arms & hardware on the lines Beyond FP776. Works location: Hwy 27, Walton. WO 30014502 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-02 | b | 0.0014197 | 4.536e-06 | 2016 | 2015-12-02 | B | 3 | 0.0028393 | 9.0713e-06
8166368 | 2015-12-01 13:45 | 2015-12-01 14:40 | 55 | 4 | 220 | 55 | 52 | 0.00066523 | 208 | 0.00062894 | 1.2095e-05 | NAPA ID:13286 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3647 | install a 3 phase 400V Fuse Disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.00031447 | 6.048e-06 | 2016 | 2015-12-01 | B | 4 | 0.00062894 | 1.2095e-05
8166401 | 2015-12-01 10:15 | 2015-12-01 13:58 | 223 | 9 | 2007 | 223 | 220 | 0.0060687 | 1980 | 0.005987 | 2.7214e-05 | NAPA ID:14106 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-030 | Replace 2 xarms. Works location: Omanawa Rd, Tauranga. WO 30008235 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.0029935 | 1.3607e-05 | 2016 | 2015-12-01 | B | 9 | 0.005987 | 2.7214e-05
8166802 | 2015-12-07 08:52 | 2015-12-07 12:07 | 194.7667 | 12 | 2337.2 | 194.7667 | 191.7667 | 0.0070671 | 2301.2 | 0.0069583 | 3.6285e-05 | NAPA ID:14375 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | Change 5 x poles and 7 x cross arms. Work Location: Maindrain Road. Work Order: 30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-07 | b | 0.0034791 | 1.8143e-05 | 2016 | 2015-12-07 | B | 12 | 0.0069583 | 3.6285e-05
8166860 | 2015-12-03 08:45 | 2015-12-03 14:20 | 335 | 11 | 3685 | 335 | 332 | 0.011143 | 3652 | 0.011043 | 3.3261e-05 | NAPA ID:13841 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7907 | Replace transformer and all hardware on existing pole. Works location: Te Mai Rd, Tinui Valley. WO 30013477 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.0055214 | 1.6631e-05 | 2016 | 2015-12-03 | B | 11 | 0.011043 | 3.3261e-05
8166886 | 2015-12-03 08:30 | 2015-12-03 15:10 | 400 | 8 | 3200 | 400 | 397 | 0.009676 | 3176 | 0.0096035 | 2.419e-05 | NAPA ID:14121 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 933 | replace poles 795234 /795236 , poles in poor condition. Works location: Pukemaou Rd, Taihape. WO 10161734 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.0048017 | 1.2095e-05 | 2016 | 2015-12-03 | B | 8 | 0.0096035 | 2.419e-05
8166922 | 2015-11-21 08:01 | 2015-11-21 12:22 | 260.75 | 110 | 28532.4 | 259.3855 | 256.3855 | 0.086275 | 28202.4 | 0.085277 | 0.00033261 | NAPA ID:14119 TP_MASTERTON GXP > TE ORE ORE SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV C823 | To replace x2 11kv poles and hardware. Works location: Colombo Rd, Masterton. WO 30016020 | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-21 | b | 0.042639 | 0.00016631 | 2016 | 2015-11-21 | B | 110 | 0.085277 | 0.00033261
8166935 | 2015-11-13 11:39 | 2015-11-13 13:54 | 135.5333 | 1 | 135.5333 | 135.5333 | 132.5333 | 0.00040982 | 132.5333 | 0.00040075 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t3273 | Replaced fuse on spur line 1. 2 x 2 amp fuse at transformer also 1x 3 amp fuse at 7781. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-13 | c | 0.00040075 | 3.024e-06 | 2016 | 2015-11-13 | C | 1 | 0.00040075 | 3.0238e-06
8166998 | 2015-12-01 09:10 | 2015-12-01 14:10 | 300 | 2 | 600 | 300 | 297 | 0.0018143 | 594 | 0.0017961 | 6.0475e-06 | NAPA ID:13444 TP_HAWERA GXP > LIVINGSTONE SUB > OTAUTU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L4132 | Replace L4132 pad mount transformer with new 100kVA mini sub. Works location: Patea. WO 30013203 | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-01 | b | 0.00089806 | 3.024e-06 | 2016 | 2015-12-01 | B | 2 | 0.0017961 | 6.0475e-06
8167001 | 2015-11-27 08:59 | 2015-11-27 17:44 | 525 | 81 | 42525 | 525 | 522 | 0.12859 | 42282 | 0.12785 | 0.00024492 | NAPA ID:13739 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 834195 | Replace C219 and pole, C1024 and pole and cut trees. Works location: Matahiwi Rd, Masterton. WO 10159904 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-27 | b | 0.063925 | 0.00012246 | 2016 | 2015-11-27 | B | 81 | 0.12785 | 0.00024492
8167045 | 2015-12-02 11:55 | 2015-12-02 15:34 | 219 | 19 | 4161 | 219 | 216 | 0.012582 | 4104 | 0.01241 | 5.7451e-05 | NAPA ID:13359 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 728630 | LLP Install LLBreak @ pole 728630 - AP Replace cracked AbS LI729 pole - LLP Close LLB @ pole 728630. Works location: Kakaramea Wilson Rd. WO 10159896 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0062048 | 2.8726e-05 | 2016 | 2015-12-02 | B | 19 | 0.01241 | 5.7451e-05
8167074 | 2015-12-03 09:45 | 2015-12-03 12:27 | 162 | 20 | 3240 | 162 | 159 | 0.009797 | 3180 | 0.0096156 | 6.0475e-05 | NAPA ID:14505 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Q51 | To change rotten larch pole. Works location: Middle Rd. WO 30010305 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.0048078 | 3.0238e-05 | 2016 | 2015-12-03 | B | 20 | 0.0096156 | 6.0475e-05
8167327 | 2015-12-02 10:30 | 2015-12-02 11:25 | 55 | 28 | 1540 | 55 | 52 | 0.0046566 | 1456 | 0.0044026 | 8.4665e-05 | NAPA ID:13845 TP_MASTERTON GXP > GLADSTONE SUB > PUKETIRO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7637 | Replace 11kV pole. Works location: Te Kopi Rd, Carterton. WO 30012265 | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0022013 | 4.2333e-05 | 2016 | 2015-12-02 | B | 28 | 0.0044026 | 8.4665e-05
8167433 | 2015-12-02 10:15 | 2015-12-02 14:45 | 270 | 18 | 4860 | 270 | 267 | 0.014695 | 4806 | 0.014532 | 5.4428e-05 | NAPA ID:14587 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8882 | Replace Transformer W5105 with same size unit due to corrosion. Works location: Ramanui Ave. WO 30000717 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0072661 | 2.7214e-05 | 2016 | 2015-12-02 | B | 18 | 0.014532 | 5.4428e-05
8167455 | 2015-11-29 08:45 | 2015-11-29 13:53 | 308 | 51 | 15708 | 308 | 305 | 0.047497 | 15555 | 0.047035 | 0.00015421 | NAPA ID:14739 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC835 | Replace 11kV & 400V X arms. Works location: Smith St, Matamata. WO 30002466 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-29 | b | 0.023517 | 7.7106e-05 | 2016 | 2015-11-29 | B | 51 | 0.047035 | 0.00015421
8167539 | 2015-12-04 13:00 | 2015-12-04 15:08 | 128 | 6 | 768 | 128 | 125 | 0.0023222 | 750 | 0.0022678 | 1.8143e-05 | NAPA ID:13847 TP_MASTERTON GXP > GLADSTONE SUB > PUKETIRO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7635 | Replace 11kV pole. Works location: Buchannon Rd, Carterton. WO 30012265 | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-12-04 | b | 0.0011339 | 9.071e-06 | 2016 | 2015-12-04 | B | 6 | 0.0022678 | 1.8143e-05
8168044 | 2015-12-01 09:15 | 2015-12-01 15:09 | 354 | 196 | 69384 | 354 | 351 | 0.2098 | 68796 | 0.20802 | 0.00059266 | NAPA ID:12626 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC523 | Replace Cross arms at Various Sites. Works location: Leo St, Waihi Beach. WO 30002513 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-12-01 | b | 0.10401 | 0.00029633 | 2016 | 2015-12-01 | B | 196 | 0.20802 | 0.00059266
8169565 | 2015-12-02 12:45 | 2015-12-02 15:16 | 151 | 4 | 604 | 151 | 148 | 0.0018264 | 592 | 0.0017901 | 1.2095e-05 | NAPA ID:14539 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC346 | Straighten Pole, check TX for oil level. Works location: Wani Rd, Awaiti. WO 30010116 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-02 | b | 0.00089503 | 6.048e-06 | 2016 | 2015-12-02 | B | 4 | 0.0017901 | 1.2095e-05
8171373 | 2015-11-13 17:43 | 2015-11-13 19:02 | 79 | 239 | 13845.1833 | 57.9296 | 54.9296 | 0.041865 | 13128.1833 | 0.039696 | 0.00072268 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 823192 | CB C831 tripped on O/C flags, line was isolated and patrolled. Received a call from customer that a branch from the tree they were cutting has landed on the line at pole 823192, line was isolated at ABS S363 and faultman knocked the branch off with hot li | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-11-13 | c | 0.039696 | 0.00072268 | 2016 | 2015-11-13 | C | 239 | 0.039696 | 0.00072268
8172693 | 2015-11-13 23:25 | 2015-11-14 00:42 | 77.4333 | 676 | 43688.7167 | 64.6283 | 61.6283 | 0.1321 | 41660.7167 | 0.12597 | 0.0020441 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | S61 | CB S61 tripped on E/F flags, line was patrolled and sectionalised and no fault was found. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-13 | c | 0.12597 | 0.0020441 | 2016 | 2015-11-13 | C | 676 | 0.12597 | 0.0020441
8176529 | 2015-11-14 05:45 | 2015-11-14 09:03 | 198.2 | 340 | 25771.6833 | 75.7991 | 72.7991 | 0.077927 | 24751.6833 | 0.074843 | 0.0010281 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782726 | Repaired Line Down using 3x sleeves, 10mtrs squirrel conductor, 1x binder. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.074843 | 0.0010281 | 2016 | 2015-11-14 | C | 340 | 0.074843 | 0.0010281
8177712 | 2015-11-14 08:03 | 2015-11-14 09:58 | 115.1167 | 13 | 1496.5167 | 115.1167 | 112.1167 | 0.0045251 | 1457.5167 | 0.0044072 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5708 | Replaced 2x 10Amp Links | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.0044072 | 3.9309e-05 | 2016 | 2015-11-14 | C | 13 | 0.0044072 | 3.9309e-05
8178154 | 2015-11-14 11:02 | 2015-11-14 15:30 | 267.8 | 726 | 46690.2333 | 64.3116 | 61.3116 | 0.14118 | 44512.2333 | 0.13459 | 0.0021953 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P17977 | CB 5 Trip, E/F, O/C A-B-C Phase. Started sectionalising when call came in of tree down through lines. Fault Area Isolated at ABS M66 & Fuses M78. Repairs made & relivened ok. Note: Tree was a large poplar situated about 30mtrs from lines, which split and | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.13459 | 0.0021953 | 2016 | 2015-11-14 | C | 726 | 0.13459 | 0.0021953
8180832 | 2015-11-14 19:37 | 2015-11-15 00:46 | 308.95 | 626 | 54675.4333 | 87.3409 | 84.3409 | 0.16533 | 52797.4333 | 0.15965 | 0.0018929 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 813128 | CB C890 L/O on Deft E/F. Reported transformer on fire in New York West St. Found line down due to a piece of scaffold hitting line. Isolated beween ABS S523, S510, S521 & S517. Backed feed rest of area. repaired line down & re-livened. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.15965 | 0.0018929 | 2016 | 2015-11-14 | C | 626 | 0.15965 | 0.0018929
8181490 | 2015-11-14 23:07 | 2015-11-14 23:15 | 8 | 3 | 23.5667 | 7.8556 | 4.8556 | 7.126e-05 | 14.5667 | 4.4046e-05 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | SE6-178/L2 | at Te Puke Sub, CB 2 Mangorewa Feeder. Found 1x Blown Fuse Link Box SE6-178/L2. To reload new fuse, had to isolate at Fuses SE6-030. Reloaded & Relivened fuse - All Power Restored on Completion. Fault was caused by rodent shorting out live conductors, fou | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-11-14 | c | 4.4046e-05 | 9.071e-06 | 2016 | 2015-11-14 | C | 3 | 4.4046e-05 | 9.0713e-06
8181559 | 2015-11-14 20:54 | 2015-11-14 23:19 | 144.95 | 1 | 144.95 | 144.95 | 141.95 | 0.00043829 | 141.95 | 0.00042922 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/144 | Found 2 x 6amp HT fuses blowen replaced OK | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.00042922 | 3.024e-06 | 2016 | 2015-11-14 | C | 1 | 0.00042922 | 3.0238e-06
8181650 | 2015-11-14 23:19 | 2015-11-15 02:40 | 200.8167 | 832 | 51483.6 | 61.8793 | 58.8793 | 0.15567 | 48987.6 | 0.14813 | 0.0025158 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 745489 | CB 2 L/O on O/C. Car hit pole 745489 Mountain Rd. Isolated between ABS 279 & 159. Backfed rest of area via CB 9. CB 2 would not close NDR N100075. Materials Used: 1 pole, 1 crossarm & 3 HT insulators. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-14 | c | 0.14813 | 0.0025158 | 2016 | 2015-11-14 | C | 832 | 0.14813 | 0.0025158
8185463 | 2015-11-15 02:13 | 2015-11-15 03:45 | 91.9833 | 1015 | 13219.5667 | 13.0242 | 10.0242 | 0.039973 | 10174.5667 | 0.030765 | 0.0030691 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745783 | CB 5 L/O on O/C & E/F, opened at Sw/Gear 12026/2 & closed 12026/3. CB 6 auto reclosed. Reclosed CB 5 then returned switching to normal. Found faulty insulator at pole 745783, isolated between ABS 315 & 331. Replaced insulator & re-livened | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.030765 | 0.0030691 | 2016 | 2015-11-15 | C | 1015 | 0.030765 | 0.0030691
8188333 | 2015-11-15 06:18 | 2015-11-15 09:26 | 188.1167 | 236 | 21529.9 | 91.2284 | 88.2284 | 0.065101 | 20821.9 | 0.06296 | 0.00071361 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747021 | Recloser 499 tripped on O/C & E/F flags, line was patrolled and sectionalised and a broken 11kV insulator was found on pole 747021, line was isolated at ABS's 229 & 548 to replace the insulator. 1 X 11kV insulator and binder replaced. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.06296 | 0.00071361 | 2016 | 2015-11-15 | C | 236 | 0.06296 | 0.00071361
8190943 | 2015-11-15 08:21 | 2015-11-15 11:30 | 189.0833 | 365 | 23331 | 63.9205 | 60.9205 | 0.070547 | 22236 | 0.067236 | 0.0011037 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757107 | CB 8 tripped on E/F flags, line was patrolled and sectionalised andblown insulator was found at pole 757107, line was isolated at ABS's 514 & 6565 to replace the insulator. 1 X 11KV Insulator & binder replaced. 1 meter Namu conductor & 2 Sleeves | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.067236 | 0.0011037 | 2016 | 2015-11-15 | C | 365 | 0.067236 | 0.0011037
8194774 | 2015-11-15 12:55 | 2015-11-15 15:39 | 164 | 67 | 10988 | 164 | 161 | 0.033225 | 10787 | 0.032617 | 0.00020259 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745786 | Faultman found a line down at pole 745786, line was isolated at ABS's 315 & 331 to repair the line. 1 X 11kV insulator & binder replaced. 1 meter 16 mm copper conductor & 1 X spindle & 2 X line taps used. 2 x 40 amp HV fuses replaced. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.032617 | 0.00020259 | 2016 | 2015-11-15 | C | 67 | 0.032617 | 0.00020259
8195057 | 2015-11-15 14:17 | 2015-11-15 17:03 | 165.95 | 92 | 13973.7833 | 151.8889 | 148.8889 | 0.042253 | 13697.7833 | 0.041419 | 0.00027819 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | please check if oms 8195072 & 8195089 & 8195099,8195110 related Faultman found Recloser N21 open NOC have no Scada contol or indication on this Recloser, line was patrolled and sectionalised and no fault was found. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.041419 | 0.00027819 | 2016 | 2015-11-15 | C | 92 | 0.041419 | 0.00027819
8198817 | 2015-11-15 14:23 | 2015-11-15 17:02 | 158.7333 | 1 | 158.7333 | 158.7333 | 155.7333 | 0.00047997 | 155.7333 | 0.0004709 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | This is part of OMS 8195057 pushed throughg | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-11-15 | c | 0.0004709 | 3.024e-06 | 2016 | 2015-11-15 | C | 1 | 0.0004709 | 3.0238e-06
8200673 | 2015-11-15 22:38 | 2015-11-15 22:55 | 16.6833 | 1 | 16.6833 | 16.6833 | 13.6833 | 5.0446e-05 | 13.6833 | 4.1375e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/69 | Shutdown Transformer to remove faulty insulator at T3/69. Insulator no longer required so not replaced. Used 1x 3Amp HV fuse link. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-11-15 | c | 4.1375e-05 | 3.024e-06 | 2016 | 2015-11-15 | C | 1 | 4.1375e-05 | 3.0238e-06
8205179 | 2015-11-19 09:02 | 2015-11-19 11:04 | 122.5 | 16 | 1844.2667 | 115.2667 | 112.2667 | 0.0055766 | 1796.2667 | 0.0054315 | 4.838e-05 | NAPA ID:14752 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2737 | replace rotten crossarm. Works location: Hwy 26, Motumaoho. WO 30007220 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-11-19 | b | 0.0027157 | 2.419e-05 | 2016 | 2015-11-19 | B | 16 | 0.0054315 | 4.838e-05
8205210 | 2015-12-02 09:32 | 2015-12-02 16:51 | 438.75 | 9 | 3948.75 | 438.75 | 435.75 | 0.01194 | 3921.75 | 0.011858 | 2.7214e-05 | NAPA ID:13181 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 917 | Replace pole M1917 with new 2 pole structure ready for new regulator site. Works location: Whites Rd, Putaruru. WO 30002469 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-02 | b | 0.0059292 | 1.3607e-05 | 2016 | 2015-12-02 | B | 9 | 0.011858 | 2.7214e-05
8205387 | 2015-12-02 10:38 | 2015-12-02 11:49 | 71 | 72 | 5112 | 71 | 68 | 0.015457 | 4896 | 0.014804 | 0.00021771 | NAPA ID:14562 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5216 | 11kV wire strands broken but can't get access with vehicles so we have to lower wire across the river and fix the broken wire then pull it back up. Works location: Okoki Rd, Urenui. WO 30016093 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0074022 | 0.00010886 | 2016 | 2015-12-02 | B | 72 | 0.014804 | 0.00021771
8205434 | 2015-12-07 09:33 | 2015-12-07 14:06 | 273.1333 | 42 | 11471.6 | 273.1333 | 270.1333 | 0.034687 | 11345.6 | 0.034306 | 0.000127 | NAPA ID:14556 TP_MANGAMAIRE GXP > MANGAMUTU SUB > KONINI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8 | To replace Hardwood 11kV pole. Works location: Hwy 2. WO 30014014 | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-12-07 | b | 0.017153 | 6.3499e-05 | 2016 | 2015-12-07 | B | 42 | 0.034306 | 0.000127
8205544 | 2015-12-07 09:48 | 2015-12-07 13:00 | 192 | 13 | 2496 | 192 | 189 | 0.0075473 | 2457 | 0.0074294 | 3.9309e-05 | NAPA ID:13846 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7849 | Replace 2x 11kV poles. Works location: Craigie Lea Rd, Carterton. WO 30012265 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-12-07 | b | 0.0037147 | 1.9654e-05 | 2016 | 2015-12-07 | B | 13 | 0.0074294 | 3.9309e-05
8205611 | 2015-12-05 09:00 | 2015-12-05 13:16 | 256 | 6 | 1536 | 256 | 253 | 0.0046445 | 1518 | 0.0045901 | 1.8143e-05 | NAPA ID:13940 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1612 | Replacing defected transformer structure T1612 making live line cut at pole 839976 to save SAIDI only two transformers off. Works location: Black Hill Rd, Tinui. WO 30013477 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-05 | b | 0.002295 | 9.071e-06 | 2016 | 2015-12-05 | B | 6 | 0.0045901 | 1.8143e-05
8207072 | 2015-12-03 09:46 | 2015-12-03 10:55 | 69 | 2 | 138 | 69 | 66 | 0.00041728 | 132 | 0.00039914 | 6.0475e-06 | NAPA ID:14469 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1427 | Pole M13392 (TC1427): Upgrade earthing on transformer and pole structure. Works location: Hwy 1, Putaruru. WO 30015661 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00019957 | 3.024e-06 | 2016 | 2015-12-03 | B | 2 | 0.00039914 | 6.0475e-06
8207229 | 2015-12-03 09:15 | 2015-12-03 14:54 | 339 | 5 | 1695 | 339 | 336 | 0.0051253 | 1680 | 0.0050799 | 1.5119e-05 | NAPA ID:13992 TP_HUIRANGI GXP > INGLEWOOD SUB > KAIMATA | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5368 | We are replacing transformer structure 3810T as it is poor condition. Works location: Suffolk Rd, Inglewood. WO 30000313 | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.00254 | 7.559e-06 | 2016 | 2015-12-03 | B | 5 | 0.0050799 | 1.5119e-05
8208068 | 2015-12-07 09:14 | 2015-12-07 14:33 | 318.7333 | 133 | 10330.3 | 77.6714 | 74.6714 | 0.031236 | 9931.3 | 0.03003 | 0.00040216 | NAPA ID:14117 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 6403 | Remove Tx C6770 & 3 spans low Lv lines, Install new 15Kva Tx 5649E on pole 725223. Works location: Ararata Rd, Hawera. WO 30010864 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-12-07 | b | 0.015015 | 0.00020108 | 2016 | 2015-12-07 | B | 133 | 0.03003 | 0.00040216
8208134 | 2015-12-08 09:46 | 2015-12-08 14:42 | 295.9667 | 38 | 11246.7333 | 295.9667 | 292.9667 | 0.034007 | 11132.7333 | 0.033663 | 0.0001149 | NAPA ID:14579 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 662 | Replace two 11kv poles 774985 and 773075. Works location: Ridge Rd, Waitotara. WO 30011372 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-12-08 | b | 0.016831 | 5.7451e-05 | 2016 | 2015-12-08 | B | 38 | 0.033663 | 0.0001149
8208156 | 2015-11-16 12:23 | 2015-11-16 15:23 | 180 | 720 | 32224.6667 | 44.7565 | 41.7565 | 0.09744 | 30064.6667 | 0.090908 | 0.0021771 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole D12760 | The CB 5 Did A/R as Recloser 9773 is by passed at present Due to fault Sectionaliser SS9396 Stayed Open. E/F O/C Blue Phase. Cut Arrestors away at Pole D12760 as Faulty | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-11-16 | c | 0.090908 | 0.0021771 | 2016 | 2015-11-16 | C | 720 | 0.090908 | 0.0021771
8208891 | 2015-12-08 08:33 | 2015-12-08 14:51 | 377.9833 | 53 | 20033.1167 | 377.9833 | 374.9833 | 0.060575 | 19874.1167 | 0.060095 | 0.00016026 | NAPA ID:13753 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7747 | Replace T1763 with new 300kva citypad. Works location: Atkinson St. WO 30002203 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-12-08 | b | 0.030047 | 8.013e-05 | 2016 | 2015-12-08 | B | 53 | 0.060095 | 0.00016026
8210466 | 2015-12-03 10:10 | 2015-12-03 10:23 | 13 | 5 | 65 | 13 | 10 | 0.00019654 | 50 | 0.00015119 | 1.5119e-05 | NAPA ID:13293 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC549 | To install a 400V 3 phase fuse Disconnector. Works location: Waghorn Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 7.5594e-05 | 7.559e-06 | 2016 | 2015-12-03 | B | 5 | 0.00015119 | 1.5119e-05
8210542 | 2015-12-03 10:00 | 2015-12-03 10:30 | 30 | 10 | 300 | 30 | 27 | 0.00090713 | 270 | 0.00081642 | 3.0238e-05 | NAPA ID:13287 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2345 | To install a 400V 3 Phase disconnector. Works location: Wairere Rd. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00040821 | 1.5119e-05 | 2016 | 2015-12-03 | B | 10 | 0.00081642 | 3.0238e-05
8212528 | 2015-12-03 11:45 | 2015-12-03 12:00 | 15 | 8 | 120 | 15 | 12 | 0.00036285 | 96 | 0.00029028 | 2.419e-05 | NAPA ID:13294 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3000 | To install a 400V Fuse Disconnector. Works location: Alexandra Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00014514 | 1.2095e-05 | 2016 | 2015-12-03 | B | 8 | 0.00029028 | 2.419e-05
8212610 | 2015-12-03 12:15 | 2015-12-03 12:55 | 40 | 3 | 120 | 40 | 37 | 0.00036285 | 111 | 0.00033564 | 9.0713e-06 | NAPA ID:13290 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3654 | Install a 3 phase fuse disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00016782 | 4.536e-06 | 2016 | 2015-12-03 | B | 3 | 0.00033564 | 9.0713e-06
8212670 | 2015-12-03 14:00 | 2015-12-03 14:20 | 20 | 4 | 80 | 20 | 17 | 0.0002419 | 68 | 0.00020562 | 1.2095e-05 | NAPA ID:13292 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC627 | Install a 3 phase 400V Fuse Disconnector. Works location: Hwy 27, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00010281 | 6.048e-06 | 2016 | 2015-12-03 | B | 4 | 0.00020562 | 1.2095e-05
8212703 | 2015-12-03 13:45 | 2015-12-13 14:00 | 14415 | 1 | 14415 | 14415 | 14412 | 0.043588 | 14412 | 0.043578 | 3.0238e-06 | NAPA ID:13295 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC774 | To install a 400V Fuse Disconnector. Work slocation: Wairere Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.021789 | 1.512e-06 | 2016 | 2015-12-03 | B | 1 | 0.043578 | 3.0238e-06
8215088 | 2015-12-04 10:00 | 2015-12-04 10:30 | 30 | 5 | 150 | 30 | 27 | 0.00045356 | 135 | 0.00040821 | 1.5119e-05 | NAPA ID:13296 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC695 | To install a 3 phase Fuse disconnector. Works location: Alexandra Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.0002041 | 7.559e-06 | 2016 | 2015-12-04 | B | 5 | 0.00040821 | 1.5119e-05
8215130 | 2015-12-03 10:05 | 2015-12-03 11:30 | 85 | 1 | 85 | 85 | 82 | 0.00025702 | 82 | 0.00024795 | 3.0238e-06 | NAPA ID:14527 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W2174 | Replace pole W2174. Works location: Tapu Coroglen Rd, Whitianga. WO 30016976 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00012397 | 1.512e-06 | 2016 | 2015-12-03 | B | 1 | 0.00024795 | 3.0238e-06
8215156 | 2015-12-02 09:02 | 2015-12-02 15:35 | 393.0333 | 14 | 5502.2333 | 393.0167 | 390.0167 | 0.016637 | 5460.2333 | 0.01651 | 4.2333e-05 | NAPA ID:13768 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G SE6-169 | Replace Series I Sw/gear (SE6-169,171 & 173) with CFCF (SE6-169, -171, -173 & -152). Remove Fuses SE6-152 and replace termination arms at pole 221199. Reconnect Transformers TE6-202 to Fuse/Sw SE6-152 and TE6-205 to Fuse/Sw SE6-169. Works location: Casu | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-12-02 | b | 0.0082552 | 2.1166e-05 | 2016 | 2015-12-02 | B | 14 | 0.01651 | 4.2333e-05
8215608 | 2015-11-16 16:30 | 2015-11-16 22:00 | 330 | 680 | 62680.2 | 92.1768 | 89.1768 | 0.18953 | 60640.2 | 0.18336 | 0.0020562 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 708 | 027 339 7325. Fuse box blown up opp 159 Coronation ave - Rob Parsons. Big bang and saw flames, no flames at the moment. 4.37pm advised Glenn in control. Fire service called wanting eta - svs hub to call re eta 4.44pm Cindy called advising eta 20mins - 4.4 | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2015-11-16 | c | 0.18336 | 0.0020562 | 2016 | 2015-11-16 | C | 680 | 0.18336 | 0.0020562
8219043 | 2015-12-04 10:45 | 2015-12-04 11:42 | 57 | 37 | 2109 | 57 | 54 | 0.0063771 | 1998 | 0.0060415 | 0.00011188 | NAPA ID:13975 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 336 | 11kV Magnefix servicing required full switch gear outage. This can now be done after Links 336 (DNO 150916) replaced. Works location: Popular Gr. WO 30004442 | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-12-04 | b | 0.0030207 | 5.594e-05 | 2016 | 2015-12-04 | B | 37 | 0.0060415 | 0.00011188
8219094 | 2015-12-04 12:00 | 2015-12-04 12:20 | 20 | 1 | 20 | 20 | 17 | 6.0475e-05 | 17 | 5.1404e-05 | 3.0238e-06 | NAPA ID:13297 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6043 | Install a 3 phase 400V Fuse Unit. Works location: Alexandra Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 2.5702e-05 | 1.512e-06 | 2016 | 2015-12-04 | B | 1 | 5.1404e-05 | 3.0238e-06
8219256 | 2015-12-03 09:46 | 2015-12-03 16:13 | 387 | 5 | 1935 | 387 | 384 | 0.005851 | 1920 | 0.0058056 | 1.5119e-05 | NAPA ID:13977 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 205478 | Replace pole 205478. Works location: Hwy 2, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.0029028 | 7.559e-06 | 2016 | 2015-12-03 | B | 5 | 0.0058056 | 1.5119e-05
8219325 | 2015-12-03 12:30 | 2015-12-03 13:30 | 60 | 3 | 180 | 60 | 57 | 0.00054428 | 171 | 0.00051706 | 9.0713e-06 | NAPA ID:14573 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-176 | Upgrade Earthbank at TC2-176. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00025853 | 4.536e-06 | 2016 | 2015-12-03 | B | 3 | 0.00051706 | 9.0713e-06
8219375 | 2015-12-10 09:15 | 2015-12-10 14:31 | 316 | 120 | 37920 | 316 | 313 | 0.11466 | 37560 | 0.11357 | 0.00036285 | NAPA ID:14214 TP_BRUNSWICK GXP > PEAT ST SUB > SPRINGVALE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 766116 | Run new conductor between poles 766116 and pole 766026. Works location: Peat St, Wanganui. WO 10147893 | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.056786 | 0.00018143 | 2016 | 2015-12-10 | B | 120 | 0.11357 | 0.00036285
8219444 | 2015-12-09 09:10 | 2015-12-09 14:34 | 324 | 18 | 5832 | 324 | 321 | 0.017635 | 5778 | 0.017471 | 5.4428e-05 | NAPA ID:14379 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P29599 | Change 5 x poles and 18 x xarms. Works location: Maindrain Rd. WO 30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-09 | b | 0.0087356 | 2.7214e-05 | 2016 | 2015-12-09 | B | 18 | 0.017471 | 5.4428e-05
8219492 | 2015-12-09 08:30 | 2015-12-09 15:52 | 442 | 15 | 6630 | 442 | 439 | 0.020048 | 6585 | 0.019911 | 4.5356e-05 | NAPA ID:14422 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7114 | removing trees from 11kv lines burning badly. Works location: Ngahapi Rd. WO 10152356 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-09 | b | 0.0099557 | 2.2678e-05 | 2016 | 2015-12-09 | B | 15 | 0.019911 | 4.5356e-05
8219857 | 2015-11-17 11:45 | 2015-11-17 14:05 | 140 | 26 | 3640 | 140 | 137 | 0.011006 | 3562 | 0.010771 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | N2147 | Fire service reporting large tree caught in power lines. Eta required F1960094 Fire comms 094867948. Isolated at fuses FP905, removed tree, Relivened. NDR 31186 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-11-17 | c | 0.010771 | 7.8618e-05 | 2016 | 2015-11-17 | C | 26 | 0.010771 | 7.8618e-05
8220474 | 2015-12-04 12:25 | 2015-12-04 12:50 | 25 | 5 | 125 | 25 | 22 | 0.00037797 | 110 | 0.00033261 | 1.5119e-05 | NAPA ID:13298 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1650 | Install a 3 phase 400v fuse disconnector. Works location: Alexandra Rd, Walton. WO 10147849 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.00016631 | 7.559e-06 | 2016 | 2015-12-04 | B | 5 | 0.00033261 | 1.5119e-05
8220506 | 2015-11-17 13:50 | 2015-11-17 16:35 | 165 | 3 | 495 | 165 | 162 | 0.0014968 | 486 | 0.0014695 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 759357 | Insulator pulled out of double cross arm. Check for safety. In the paddock with animals. Alt number 0272474696. Replaced 2 crossarms 1 complete with insulators. Isolated at fuses 5648 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-17 | c | 0.0014695 | 9.071e-06 | 2016 | 2015-11-17 | C | 3 | 0.0014695 | 9.0713e-06
8220510 | 2015-12-11 11:46 | 2015-12-11 15:46 | 240 | 23 | 5520 | 240 | 237 | 0.016691 | 5451 | 0.016483 | 6.9546e-05 | NAPA ID:14212 TP_WAIKINO GXP > PAEROA SUB > RAILWAY ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4830 | Isolate and earth transformer TC4830 to install new LV Switchgear to remeady defect of burning out switchgear | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.0082413 | 3.4773e-05 | 2016 | 2015-12-11 | B | 23 | 0.016483 | 6.9546e-05
8220532 | 2015-12-06 09:40 | 2015-12-06 12:03 | 143.35 | 6 | 860.1 | 143.35 | 140.35 | 0.0026007 | 842.1 | 0.0025463 | 1.8143e-05 | NAPA ID:14057 TP_HUIRANGI GXP > INGLEWOOD SUB > RATA ST | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 5456 | We have to replace LV bare wire going over the top off a building as it does not have the legal clearance. We have to isolate the HV for safety as it will be inside the MADs. We have to do it on a sunday as the LV feeds a business of inta steak. Works loc | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2015-12-06 | b | 0.0012732 | 9.071e-06 | 2016 | 2015-12-06 | B | 6 | 0.0025463 | 1.8143e-05
8220793 | 2015-12-07 10:00 | 2015-12-07 10:16 | 16 | 5 | 80 | 16 | 13 | 0.0002419 | 65 | 0.00019654 | 1.5119e-05 | NAPA ID:13638 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1481 | To install a 400V Fuse disconnector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-07 | b | 9.8272e-05 | 7.559e-06 | 2016 | 2015-12-07 | B | 5 | 0.00019654 | 1.5119e-05
8220800 | 2015-12-04 10:00 | 2015-12-04 11:37 | 97 | 1 | 97 | 97 | 94 | 0.0002933 | 94 | 0.00028423 | 3.0238e-06 | NAPA ID:13431 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2994 | Replace 15-11-1 pole mount transformer. Works location: Whitianga Tairua Rd. WO 30002490 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.00014212 | 1.512e-06 | 2016 | 2015-12-04 | B | 1 | 0.00028423 | 3.0238e-06
8220833 | 2015-12-04 10:05 | 2015-12-04 13:35 | 210 | 1 | 210 | 210 | 207 | 0.00063499 | 207 | 0.00062592 | 3.0238e-06 | NAPA ID:14526 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole N1590 | Install pole to separate 11 kv over LV. Works location: Rotokohu Rd, Paeroa. WO 30008252 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.00031296 | 1.512e-06 | 2016 | 2015-12-04 | B | 1 | 0.00062592 | 3.0238e-06
8220936 | 2015-12-07 13:00 | 2015-12-07 14:05 | 65 | 4 | 260 | 65 | 62 | 0.00078618 | 248 | 0.00074989 | 1.2095e-05 | NAPA ID:13640 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1622 | To replace the 400V pin arm and install a 400V Fuse/Disconnector. Works location: Dodd Rd, Morrinsville. WO 10147849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-07 | b | 0.00037495 | 6.048e-06 | 2016 | 2015-12-07 | B | 4 | 0.00074989 | 1.2095e-05
8220969 | 2015-12-04 13:15 | 2015-12-04 15:28 | 133 | 1 | 133 | 133 | 130 | 0.00040216 | 130 | 0.00039309 | 3.0238e-06 | NAPA ID:13430 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6284 | Replace 15-11-1 pole mount transformer. Works location: Mill Creek Rd, Whitianga. WO 30002490 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.00019654 | 1.512e-06 | 2016 | 2015-12-04 | B | 1 | 0.00039309 | 3.0238e-06
8221055 | 2015-12-02 11:05 | 2015-12-02 11:48 | 43 | 41 | 1763 | 43 | 40 | 0.0053309 | 1640 | 0.004959 | 0.00012397 | NAPA ID:14459 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC805 | Replace transformer earths. Works location: Herbert Drive, Whangamata. WO 30002457 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-12-02 | b | 0.0024795 | 6.1987e-05 | 2016 | 2015-12-02 | B | 41 | 0.004959 | 0.00012397
8221084 | 2015-12-08 10:13 | 2015-12-08 13:00 | 167 | 4 | 668 | 167 | 164 | 0.0020199 | 656 | 0.0019836 | 1.2095e-05 | NAPA ID:14594 TP_HAWERA GXP > MANAIA SUB > OKAIAWA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer M3215 | Replace Tx M3215 with same size unit. Works location: Burgon Rd. WO 30002200 | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-12-08 | b | 0.00099179 | 6.048e-06 | 2016 | 2015-12-08 | B | 4 | 0.0019836 | 1.2095e-05
8221270 | 2015-11-17 16:20 | 2015-11-17 16:35 | 15 | 2 | 30 | 15 | 12 | 9.0713e-05 | 24 | 7.257e-05 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | C5403 | Replace lug to make repair on jumper. | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-11-17 | c | 7.257e-05 | 6.048e-06 | 2016 | 2015-11-17 | C | 2 | 7.257e-05 | 6.0475e-06
8221278 | 2015-12-08 08:43 | 2015-12-08 17:16 | 513 | 22 | 11286 | 513 | 510 | 0.034126 | 11220 | 0.033927 | 6.6523e-05 | NAPA ID:14319 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI782 | Replace Poles and conductor on Ball rd and remove tewp links 72 from pole 729105. Works location: Ball Rd, Hurleyville. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-08 | b | 0.016963 | 3.3261e-05 | 2016 | 2015-12-08 | B | 22 | 0.033927 | 6.6523e-05
8222531 | 2015-11-18 08:18 | 2015-11-18 09:40 | 82.0833 | 3 | 246.25 | 82.0833 | 79.0833 | 0.0007446 | 237.25 | 0.00071739 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7753 | check to see if OMS 822617 is related the same address (MASTER BLASTER WAIRARAPA 2005) but fed from different TX (T2448_).T2446 8:51am advised Frank of this job poss related 2 x 15 amp poss bird strike. 7751 | F3 | OXFORD ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-18 | c | 0.00071739 | 9.071e-06 | 2016 | 2015-11-18 | C | 3 | 0.00071739 | 9.0713e-06
8223106 | 2015-12-10 09:45 | 2015-12-10 16:48 | 423 | 128 | 51092 | 399.1562 | 396.1562 | 0.15449 | 50708 | 0.15333 | 0.00038704 | NAPA ID:13399 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S95 | Change Poles at 829421 and install Temp ABS 41, Pole 829398 with double discs, and poles 829452, 829453. Change 11Kv arm tap off DDO 7646 & 7645. Works location: Church Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.076664 | 0.00019352 | 2016 | 2015-12-10 | B | 128 | 0.15333 | 0.00038704
8223189 | 2015-11-18 09:26 | 2015-11-18 15:00 | 334.3833 | 2 | 668.7667 | 334.3833 | 331.3833 | 0.0020222 | 662.7667 | 0.002004 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2/171 | advised Jeff of OMS 8223365 (25 Keohlers Road, Palmerston North) - Jeff confirmed that 25 Keohlers Road is fed from same TX T2/171 Replace transformer, relivened OK | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-11-18 | c | 0.002004 | 6.048e-06 | 2016 | 2015-11-18 | C | 2 | 0.002004 | 6.0475e-06
8223335 | 2015-11-18 09:23 | 2015-11-18 12:58 | 215 | 9 | 1935 | 215 | 212 | 0.005851 | 1908 | 0.0057693 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | U35 | 7:51am called through to hub - Joanne. Lines down caused by Trees. Replace 2 x sleeves. NDR 19115. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-11-18 | c | 0.0057693 | 2.7214e-05 | 2016 | 2015-11-18 | C | 9 | 0.0057693 | 2.7214e-05
8223743 | 2015-11-18 17:10 | 2015-11-19 15:25 | 1334.9167 | 1 | 1334.9167 | 1334.9167 | 1331.9167 | 0.0040365 | 1331.9167 | 0.0040274 | 3.0238e-06 | NAPA ID:14803 TP_CARRINGTON GXP > CITY SUB > CITY 4 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 708 | DNO switchgear 708. Currently AP 151543 from 1228/2 to 375/2 with generators connected(one to LV tx 708 and another to both LV's tx 526 & 986) TP from 14:00 to 15:30 to test cables towards 1228/2 and 375/2. Switching 15:30 to 16:00 is to do phasing across | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2015-11-18 | b | 0.0020137 | 1.512e-06 | 2016 | 2015-11-18 | B | 1 | 0.0040274 | 3.0238e-06
8224110 | 2015-12-10 09:00 | 2015-12-10 15:50 | 410 | 15 | 6150 | 410 | 407 | 0.018596 | 6105 | 0.01846 | 4.5356e-05 | NAPA ID:14426 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 7114 | removing trees from 11kv lines burning badly. Works location: Ngahapi Rd. WO 10152356 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.00923 | 2.2678e-05 | 2016 | 2015-12-10 | B | 15 | 0.01846 | 4.5356e-05
8224152 | 2015-12-04 12:20 | 2015-12-04 13:05 | 45 | 5 | 225 | 45 | 42 | 0.00068035 | 210 | 0.00063499 | 1.5119e-05 | NAPA ID:14574 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-013 | Upgrade Earthbank at TC2-013 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.00031749 | 7.559e-06 | 2016 | 2015-12-04 | B | 5 | 0.00063499 | 1.5119e-05
8224206 | 2015-11-18 12:43 | 2015-11-18 18:10 | 327 | 34 | 11118 | 327 | 324 | 0.033618 | 11016 | 0.03331 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P20742 | Lines down at pole P20742. Fuses 427 opened and tagged. Materials 1 pole 1 crossarm 1 span conductor | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-18 | c | 0.03331 | 0.00010281 | 2016 | 2015-11-18 | C | 34 | 0.03331 | 0.00010281
8224217 | 2015-12-04 12:32 | 2015-12-04 14:49 | 137 | 14 | 1918 | 137 | 134 | 0.0057996 | 1876 | 0.0056726 | 4.2333e-05 | NAPA ID:13980 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC2-009 | Replace Crossarm at TC2-009 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-04 | b | 0.0028363 | 2.1166e-05 | 2016 | 2015-12-04 | B | 14 | 0.0056726 | 4.2333e-05
8224531 | 2015-12-09 14:00 | 2015-12-09 14:52 | 52 | 3 | 156 | 52 | 49 | 0.00047171 | 147 | 0.00044449 | 9.0713e-06 | NAPA ID:14016 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP950 | To install a 400V Fuse Disconnector. Works location: Settlement Rd. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-09 | b | 0.00022225 | 4.536e-06 | 2016 | 2015-12-09 | B | 3 | 0.00044449 | 9.0713e-06
8224533 | 2015-12-16 10:00 | 2015-12-16 10:47 | 47 | 5 | 235 | 47 | 44 | 0.00071058 | 220 | 0.00066523 | 1.5119e-05 | NAPA ID:14018 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2236 | To replace the 400V arm & install a 400V Fuse disconnector. Works location: Maungakawa Rd. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.00033261 | 7.559e-06 | 2016 | 2015-12-16 | B | 5 | 0.00066523 | 1.5119e-05
8224603 | 2015-12-16 13:00 | 2015-12-16 15:13 | 133 | 4 | 532 | 133 | 130 | 0.0016086 | 520 | 0.0015724 | 1.2095e-05 | NAPA ID:14019 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1452 | To replace the 400V arm & install a 400V Fuse disconnector at TC2530. Works location: Hwy 27, Tatuanui. WO 10147849. NOTE: Additional Work was carried out under this NAPA Job. See OMS 8697249 for details on extra work carried out (child job) | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.00078618 | 6.048e-06 | 2016 | 2015-12-16 | B | 4 | 0.0015724 | 1.2095e-05
8225272 | 2015-12-11 09:00 | 2015-12-11 13:52 | 292 | 4 | 1168 | 292 | 289 | 0.0035318 | 1156 | 0.0034955 | 1.2095e-05 | NAPA ID:13490 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7646 | Replace poles 829462 and 829463 and arms between 829464-829470. Works location: Te Whiti Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-11 | b | 0.0017477 | 6.048e-06 | 2016 | 2015-12-11 | B | 4 | 0.0034955 | 1.2095e-05
8225285 | 2015-12-07 11:15 | 2015-12-07 11:22 | 7 | 1 | 7 | 7 | 4 | 2.1166e-05 | 4 | 1.2095e-05 | 3.0238e-06 | NAPA ID:13982 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-192 | Replace Crossarm at TC2-192. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-07 | b | 6.048e-06 | 1.512e-06 | 2016 | 2015-12-07 | B | 1 | 1.2095e-05 | 3.0238e-06
8225370 | 2015-11-18 16:34 | 2015-11-18 17:52 | 78.3 | 1 | 78.3 | 78.3 | 75.3 | 0.00023676 | 75.3 | 0.00022769 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5390 | Advised Sammy at HUB Advised Marcus in Control Used 1 X Dead end at transformer TC5390 on Dead End | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-18 | c | 0.00022769 | 3.024e-06 | 2016 | 2015-11-18 | C | 1 | 0.00022769 | 3.0238e-06
8225923 | 2015-11-18 17:44 | 2015-11-18 19:05 | 80.75 | 398 | 11632.8167 | 29.2282 | 26.2282 | 0.035175 | 10438.8167 | 0.031564 | 0.0012035 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 10 | CB 10 tripped on B & C phase O/C, line was patrolled and sectionalised and no fault was found. Customer in the contact at 44 Owen St told faultman when he arrived that their supply was back on it went off for about 20 minutes and then came back on and it | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-18 | c | 0.031564 | 0.0012035 | 2016 | 2015-11-18 | C | 398 | 0.031564 | 0.0012035
8226880 | 2015-11-19 03:27 | 2015-11-19 04:53 | 86.75 | 1804 | 112507.6667 | 62.3657 | 59.3657 | 0.3402 | 107095.6667 | 0.32383 | 0.0054549 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/Gear's G266/B & G292/C | CB 12 tripped on A phase O/C & E/F flags, cable network was sectionalised and a cable fault was found between Sw/Gear's G266/B & G292/C. 2 R job has been made to locate the cable fault under OMS 8228889 | F2 | MAIN ST 12 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-11-19 | c | 0.32383 | 0.0054549 | 2016 | 2015-11-19 | C | 1804 | 0.32383 | 0.0054549
8229342 | 2015-11-19 06:44 | 2015-11-19 08:49 | 125.4333 | 12 | 1505.2 | 125.4333 | 122.4333 | 0.0045514 | 1469.2 | 0.0044425 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 981 | Replace 2 x HV Fuses | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-19 | c | 0.0044425 | 3.6285e-05 | 2016 | 2015-11-19 | C | 12 | 0.0044425 | 3.6285e-05
8229351 | 2015-12-10 09:45 | 2015-12-10 13:30 | 225 | 2 | 450 | 225 | 222 | 0.0013607 | 444 | 0.0013425 | 6.0475e-06 | NAPA ID:14597 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 12112 | Replace Tx K4014 with same size unit. This is a STOS site and I'm in communication with the person controlling works for STOS in that area. Works location: Skeet Rd. WO 30002200 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.00067128 | 3.024e-06 | 2016 | 2015-12-10 | B | 2 | 0.0013425 | 6.0475e-06
8230877 | 2015-11-19 08:20 | 2015-11-19 10:47 | 147.3167 | 10 | 1473.1667 | 147.3167 | 144.3167 | 0.0044545 | 1443.1667 | 0.0043638 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2464 | Replace 2x6amp HV fuse. Line patrolled No fault found. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-19 | c | 0.0043638 | 3.0238e-05 | 2016 | 2015-11-19 | C | 10 | 0.0043638 | 3.0238e-05
8233866 | 2015-12-07 12:00 | 2015-12-07 13:00 | 60 | 2 | 120 | 60 | 57 | 0.00036285 | 114 | 0.00034471 | 6.0475e-06 | NAPA ID:13984 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-079 | Replace Crossarm at TC2-079. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-07 | b | 0.00017235 | 3.024e-06 | 2016 | 2015-12-07 | B | 2 | 0.00034471 | 6.0475e-06
8233950 | 2015-12-02 10:05 | 2015-12-02 16:11 | 366.1333 | 15 | 5492 | 366.1333 | 363.1333 | 0.016606 | 5447 | 0.01647 | 4.5356e-05 | NAPA ID:14821 TP_CARRINGTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754873, 754872, 754871, 743606, 743608, 743609, 743610, 743612 | Replacement of insulator clamps on 33kV poles: 754873, 754872, 754871, 743606, 743608, 743609, 743610, 743612. Works location: Arthur Rd. WO 30002054 | F2 | BELL BLOCK 5 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0082352 | 2.2678e-05 | 2016 | 2015-12-02 | B | 15 | 0.01647 | 4.5356e-05
8234159 | 2015-11-19 10:20 | 2015-11-19 11:52 | 91.9333 | 21 | 1930.6 | 91.9333 | 88.9333 | 0.0058377 | 1867.6 | 0.0056472 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P16588 | Found floating wire at pole 16588 isolated at fuses U15 1 Binder | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-11-19 | c | 0.0056472 | 6.3499e-05 | 2016 | 2015-11-19 | C | 21 | 0.0056472 | 6.3499e-05
8235134 | 2015-12-12 09:00 | 2015-12-12 16:04 | 424 | 21 | 8894 | 423.5238 | 420.5238 | 0.026893 | 8831 | 0.026703 | 6.3499e-05 | NAPA ID:13459 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 829398 | Open live line jumpers at pole 829398, change poles during shutdown between 829396 to 829387. Works location: Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-12 | b | 0.013351 | 3.1749e-05 | 2016 | 2015-12-12 | B | 21 | 0.026703 | 6.3499e-05
8235197 | 2015-11-19 12:45 | 2015-11-19 15:24 | 159.25 | 1 | 159.25 | 159.25 | 156.25 | 0.00048153 | 156.25 | 0.00047246 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2131 | Reload Reliven. 2 x 11A Fuses. Bird Strike | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-11-19 | c | 0.00047246 | 3.024e-06 | 2016 | 2015-11-19 | C | 1 | 0.00047246 | 3.0238e-06
8237083 | 2015-11-24 13:11 | 2015-11-24 14:00 | 49.6 | 31 | 1537.6 | 49.6 | 46.6 | 0.0046493 | 1444.6 | 0.0043681 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 712398, Manihi Rd, | ### RED DEFECT### not KPI Applicable, AW-NCTL. Urgent defects that need attention Pole 712398, faulty surge arrestors, imminent failure. Requires urgent planned 11kV shut to replace. Fed from Ngariki Sub, on NG3- South Rd. Isolation point Fuses NG375. no | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-11-24 | c | 0.0043681 | 9.3737e-05 | 2016 | 2015-11-24 | C | 31 | 0.0043681 | 9.3737e-05
8237137 | 2015-12-14 08:50 | 2015-12-14 15:22 | 392 | 25 | 9800 | 392 | 389 | 0.029633 | 9725 | 0.029406 | 7.5594e-05 | NAPA ID:13792 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P15137 | replace pole p12710 and replace conductor between P15137 and P12710. Works location: Hwy 2, Mt Bruce. WO 10162575 | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-12-14 | b | 0.014703 | 3.7797e-05 | 2016 | 2015-12-14 | B | 25 | 0.029406 | 7.5594e-05
8237702 | 2015-11-19 18:55 | 2015-11-19 20:18 | 82.9333 | 93 | 7712.8 | 82.9333 | 79.9333 | 0.023322 | 7433.8 | 0.022478 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | Reports of "No Power" found recloser N21 Tripped (Rangiwahia). CB Reclosed OK and patrolled to Peka and Orangipongo Rd. Nothing found. Suspect cracked insulator, feeder sectionalised to ABS N29 to narrow fault area. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-11-19 | c | 0.022478 | 0.00028121 | 2016 | 2015-11-19 | C | 93 | 0.022478 | 0.00028121
8238190 | 2015-11-20 04:08 | 2015-11-20 07:03 | 175.1833 | 676 | 69952.75 | 103.4804 | 100.4804 | 0.21152 | 67924.75 | 0.20539 | 0.0020441 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740510 | Tripping on CB S61 on E/F. Feeder patrolled / sectionalised with a broken conductor found cross country to Beaconsfield RD. Isolation between ABS 5760 and CB4812. (Backfeed at ABS 5643). | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.20539 | 0.0020441 | 2016 | 2015-11-20 | C | 676 | 0.20539 | 0.0020441
8242148 | 2015-12-08 09:30 | 2015-12-08 16:45 | 435 | 35 | 15225 | 435 | 432 | 0.046037 | 15120 | 0.045719 | 0.00010583 | NAPA ID:14537 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC2-042 | Replace H/V Crossarms at Various Sites. Works location: Work Rd, Aongatete. WO 30003302 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-12-08 | b | 0.02286 | 5.2916e-05 | 2016 | 2015-12-08 | B | 35 | 0.045719 | 0.00010583
8242336 | 2015-11-20 13:30 | 2015-11-20 15:38 | 128 | 30 | 3840 | 128 | 125 | 0.011611 | 3750 | 0.011339 | 9.0713e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IC2583 | REPLACE 1X BROKEN X ARM ON POLE SO281 LV OH. REPLACE 1X TERMINATION ARM ON POLE S12866. 2R REQUESTED. MAY HAVE TO TAKE POWER OFF THIS WILL AFFECT PURIRI FIRE STATION THAMES STU WILL ADVISE IF WE NEED TO PHONE FIRE COMMS WHEN HE IS SURE THE POWER WILL BE O | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-11-20 | c | 0.011339 | 9.0713e-05 | 2016 | 2015-11-20 | C | 30 | 0.011339 | 9.0713e-05
8242550 | 2015-12-09 09:05 | 2015-12-09 17:14 | 489 | 39 | 19071 | 489 | 486 | 0.057666 | 18954 | 0.057312 | 0.00011793 | NAPA ID:14419 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC380 | Replacing ABS pole IC380 and replacing crossarms + reconductoring between IC368 + T1577. Works location: Thames Coast Rd, Thames. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-12-09 | b | 0.028656 | 5.8963e-05 | 2016 | 2015-12-09 | B | 39 | 0.057312 | 0.00011793
8243602 | 2015-12-15 08:05 | 2015-12-18 15:13 | 4748 | 4 | 96 | 24 | 21 | 0.00029028 | 84 | 0.000254 | 1.2095e-05 | NAPA ID:13793 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/405 | Replace all poles on spur line past S39 to upgrade line for new Powerco repeater site at T8/405. Works location: Hwy 2, Mt Bruce. WO 10162575 | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.000127 | 6.048e-06 | 2016 | 2015-12-15 | B | 4 | 0.000254 | 1.2095e-05
8243653 | 2015-12-15 09:00 | 2015-12-15 16:07 | 427 | 47 | 20069 | 427 | 424 | 0.060684 | 19928 | 0.060258 | 0.00014212 | NAPA ID:13499 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11062 | Replace poles and cross arms between poles 834905 & 834914. Treescape will be work under the same shutdown to clean & remove tree from the 11kv line. Works location: Kaka Amu Rd. WO 30014082 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.030129 | 7.1058e-05 | 2016 | 2015-12-15 | B | 47 | 0.060258 | 0.00014212
8243655 | 2015-11-24 07:05 | 2015-11-24 15:46 | 521 | 93 | 4511.8333 | 48.5143 | 45.5143 | 0.013643 | 4232.8333 | 0.012799 | 0.00028121 | NAPA ID:14863 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3252, TC6213 | AP1. Connect Generator to Transformer TC3252. AP2. Connect Generator to Transformer TC6213. AP3. Replace cross arms & hardware between isolation points. (08:30 - 09:30) Connect Generation to Transformers TP1339, TP1113 and TC3624. - all LV Isolation. (15: | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-24 | b | 0.0063995 | 0.0001406 | 2016 | 2015-11-24 | B | 93 | 0.012799 | 0.00028121
8243657 | 2015-12-15 09:47 | 2015-12-15 15:10 | 323.1833 | 3 | 969.55 | 323.1833 | 320.1833 | 0.0029317 | 960.55 | 0.0029045 | 9.0713e-06 | NAPA ID:13416 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7644 | Change 11kV pole and arm from DDO 7644. Works location: Te Whiti Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.0014522 | 4.536e-06 | 2016 | 2015-12-15 | B | 3 | 0.0029045 | 9.0713e-06
8243674 | 2015-12-15 09:31 | 2015-12-15 13:37 | 246.2333 | 30 | 7387 | 246.2333 | 243.2333 | 0.022337 | 7297 | 0.022064 | 9.0713e-05 | NAPA ID:14507 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V5 | To Change larch pole. Works location: Route 52. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.011032 | 4.5356e-05 | 2016 | 2015-12-15 | B | 30 | 0.022064 | 9.0713e-05
8245292 | 2015-12-15 09:35 | 2015-12-15 15:06 | 331.15 | 47 | 15564.05 | 331.15 | 328.15 | 0.047062 | 15423.05 | 0.046636 | 0.00014212 | NAPA ID:13438 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 787310 | Change cross arms and erect poles from pole 787310 to pole 787407. Works location: Otuarie Rd, Taihape. WO 30006838 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.023318 | 7.1058e-05 | 2016 | 2015-12-15 | B | 47 | 0.046636 | 0.00014212
8245628 | 2015-12-15 09:24 | 2015-12-15 15:35 | 371 | 24 | 8904 | 371 | 368 | 0.026924 | 8832 | 0.026706 | 7.257e-05 | NAPA ID:14391 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | T1/104 | Dismantle two pole structure T1/104. Change 4 x poles and 7 x xarms commission new transformers 7333P and 7332P | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.013353 | 3.6285e-05 | 2016 | 2015-12-15 | B | 24 | 0.026706 | 7.257e-05
8245686 | 2015-12-08 09:38 | 2015-12-08 11:21 | 102.3333 | 71 | 1467.3333 | 20.6667 | 17.6667 | 0.0044369 | 1254.3333 | 0.0037928 | 0.00021469 | NAPA ID:14408 TP_WAIHOU GXP > FARMER ROAD SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13019 | Farmer Rd Stage 4. Upgrading FMR CB6 including new panel fronts, protection relay, CT's, and arc flash. Connect new relay to 3530 and disconnect CB6 from old RTU Carry out an outage to break CB6 cable from line at L12349 and another to reconnect and compl | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-12-08 | b | 0.0018964 | 0.00010734 | 2016 | 2015-12-08 | B | 71 | 0.0037928 | 0.00021469
8245724 | 2015-11-26 09:00 | 2015-11-26 12:29 | 209 | 2 | 418 | 209 | 206 | 0.0012639 | 412 | 0.0012458 | 6.0475e-06 | NAPA ID:14880 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 222997 | AP. Install new 11kV Sectionaliser 9954/2 and Links 9954/4 on pole 222997. Liven new Sectionaliser 9954/2 from TEMP62 (CLOSE Links). LLP. Liven between links 9954/4 and Fuses SE5-174 by jumpering out the Fuses SE5-174 (CLOSED) and connecting the third ph | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2015-11-26 | b | 0.0006229 | 3.024e-06 | 2016 | 2015-11-26 | B | 2 | 0.0012458 | 6.0475e-06
8245757 | 2015-11-20 14:30 | 2015-11-20 16:27 | 117.1333 | 7 | 819.9333 | 117.1333 | 114.1333 | 0.0024793 | 798.9333 | 0.0024158 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 914 | 2 X 8A HV Fuses replaced | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.0024158 | 2.1166e-05 | 2016 | 2015-11-20 | C | 7 | 0.0024158 | 2.1166e-05
8246378 | 2015-12-07 10:06 | 2015-12-07 12:40 | 153.65 | 39 | 5992.35 | 153.65 | 150.65 | 0.018119 | 5875.35 | 0.017766 | 0.00011793 | NAPA ID:14811 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC209 | Replace ABS IC209 to remedy DNO 151110. Works location: Mathers Rd, Waihi. WO 30017330 | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-12-07 | b | 0.0088828 | 5.8963e-05 | 2016 | 2015-12-07 | B | 39 | 0.017766 | 0.00011793
8246832 | 2015-11-24 11:07 | 2015-11-24 11:42 | 34.6333 | 34 | 1177.5333 | 34.6333 | 31.6333 | 0.0035606 | 1075.5333 | 0.0032522 | 0.00010281 | NAPA ID:14885 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 711207 | replace 11kv xarm | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-11-24 | b | 0.0016261 | 5.1404e-05 | 2016 | 2015-11-24 | B | 34 | 0.0032522 | 0.00010281
8246861 | 2015-11-24 09:03 | 2015-11-24 10:45 | 101.75 | 48 | 4884 | 101.75 | 98.75 | 0.014768 | 4740 | 0.014333 | 0.00014514 | NAPA ID:14883 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 712038 | replace 11kv xarm | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-11-24 | b | 0.0071663 | 7.257e-05 | 2016 | 2015-11-24 | B | 48 | 0.014333 | 0.00014514
8247881 | 2015-11-20 16:06 | 2015-11-21 10:58 | 1132.4833 | 279 | 23644.45 | 84.7471 | 81.7471 | 0.071495 | 22807.45 | 0.068964 | 0.00084363 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763639 | Reports of Part power / No power found fuses tripped at 5308. Area patrolled / sectionalised with a large span found down at Pole 763639. (300 metres, No.8). Impractical to repair at night, Temp line break installed at Pole 763649 to liven most customers. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.068964 | 0.00084363 | 2016 | 2015-11-20 | C | 279 | 0.068964 | 0.00084363
8248042 | 2015-11-20 20:00 | 2015-11-20 21:30 | 90 | 74 | 6660 | 90 | 87 | 0.020138 | 6438 | 0.019467 | 0.00022376 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727437 | Floating Conductor at Pole 727437 After Milking Please do job about 7 PM. Isolation required between ABS LI185 and LI146 to repair a floating conductor. (Backfeed at ABS LI170). One HV Pin Insulator replaced, rebound and livened OK. | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.019467 | 0.00022376 | 2016 | 2015-11-20 | C | 74 | 0.019467 | 0.00022376
8248342 | 2015-11-20 21:50 | 2015-11-20 22:34 | 44.4667 | 6 | 266.8 | 44.4667 | 41.4667 | 0.00080674 | 248.8 | 0.00075231 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10069 | Isolation required at Fuses N31 to replace one cracked insulator. Rebound / relivened OK. This may have been the cause of ongoing problems with N21 trippings. (Feeder configuration restored to normal - ABS N29 reclosed, was open to narrow down faulted are | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.00075231 | 1.8143e-05 | 2016 | 2015-11-20 | C | 6 | 0.00075231 | 1.8143e-05
8248386 | 2015-11-20 19:49 | 2015-11-20 22:08 | 139.4667 | 649 | 27501.2167 | 42.3748 | 39.3748 | 0.083157 | 25554.2167 | 0.07727 | 0.0019624 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 5 | Tripping on Mangorei CB5 on E/F, Phase B O/C. Feeder initially backfed to unfaulted areas via CB 12094/2 and Sw/Gear 12026/3. Feeder patrolled and sectionalised but nothing found. Cause unknown. (raining in area). | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.07727 | 0.0019624 | 2016 | 2015-11-20 | C | 649 | 0.07727 | 0.0019624
8248803 | 2015-11-20 19:52 | 2015-11-20 21:40 | 108.6667 | 1 | 108.6667 | 108.6667 | 105.6667 | 0.00032858 | 105.6667 | 0.00031951 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | Faultman suspects HV fault here; will require quad bike to investigate. Only one customer affected, and customer is happy for this to be attended to tomorrow. Customer has a generator running overnight. Follow Up job entered for reattendance tomorrow to l | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-20 | c | 0.00031951 | 3.024e-06 | 2016 | 2015-11-20 | C | 1 | 0.00031951 | 3.0238e-06
8248869 | 2015-11-20 20:36 | 2015-11-20 20:43 | 6.1667 | 904 | 4985.5333 | 5.515 | 2.515 | 0.015075 | 2273.5333 | 0.0068746 | 0.0027335 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2762 | CB 2762 Trip OC Time Line Patrolled & sectionalised. No Fault found. | F1,F2,F3 | DOUGLAS 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2015-11-20 | c | 0.0068746 | 0.0027335 | 2016 | 2015-11-20 | C | 904 | 0.0068746 | 0.0027335
8251553 | 2015-11-21 10:42 | 2015-11-21 11:56 | 74.0333 | 5 | 370.1667 | 74.0333 | 71.0333 | 0.0011193 | 355.1667 | 0.0010739 | 1.5119e-05 | Referral | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20906 | Locate suspected HV fault affecting 12231 Masterton Road, Woodville. Phil Barnes previously attended on job 8248803 Repaired broken 11kV jumper at Pole P20906. Materials used: 3x Conductor joints, 1mtr of Galv wire conductor. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-11-21 | c | 0.0010739 | 1.5119e-05 | 2016 | 2015-11-21 | C | 5 | 0.0010739 | 1.5119e-05
8253529 | 2015-11-21 10:58 | 2015-11-21 12:10 | 72 | 22 | 1584 | 72 | 69 | 0.0047896 | 1518 | 0.0045901 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SA2-011 | at 10:58, Kauri Point Sub, CB 2 Bowentown Feeder. Found 2x Blown DDOs at Fuses SA2-011 caused by trees in 400V Lines at Poles 207055 & 207056. Fuses SA2-011 Open & Tagged for isolation only. 400V Isolation also carried out to remove trees from lines. All | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-11-21 | c | 0.0045901 | 6.6523e-05 | 2016 | 2015-11-21 | C | 22 | 0.0045901 | 6.6523e-05
8253698 | 2015-11-21 09:28 | 2015-11-21 11:16 | 108.4 | 2 | 216.8 | 108.4 | 105.4 | 0.00065555 | 210.8 | 0.00063741 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC2-132 | Reloaded, Relivened 2x DDOs at Fuses SC2-132. Dennis Ngatai Attended. High winds in the area at the time. ADVISED DIANE AT HUB ADVISED CONTROL | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-11-21 | c | 0.00063741 | 6.048e-06 | 2016 | 2015-11-21 | C | 2 | 0.00063741 | 6.0475e-06
8254537 | 2015-11-21 12:06 | 2015-11-21 12:30 | 24.3333 | 6 | 146 | 24.3333 | 21.3333 | 0.00044147 | 128 | 0.00038704 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD3-111 | Reloaded, Relivened 2x DDO's at Transformer TD3-111. Ciaan Van Der Vyver Attended. Bad weather in the area at the time. This job was reported directly from the customer to the faultman. The customer had contacted their retailer but the retailer told them | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-11-21 | c | 0.00038704 | 1.8143e-05 | 2016 | 2015-11-21 | C | 6 | 0.00038704 | 1.8143e-05
8254978 | 2015-11-21 12:07 | 2015-11-21 19:06 | 418.6333 | 403 | 14531.7333 | 36.0589 | 33.0589 | 0.04394 | 13322.7333 | 0.040285 | 0.0012186 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 322 Landsdowne Rd, Waharoa | Fire called in to report Car Vs Pole. Fire event number: F1962608. Isolated at ABS 768 & 1206. Back feed from WAH CB 3 via ABS IC1275. Materials 1xpole 5xcrossarms complete, polymers. NDR48186 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-11-21 | c | 0.040285 | 0.0012186 | 2016 | 2015-11-21 | C | 403 | 0.040285 | 0.0012186
8256593 | 2015-11-22 02:30 | 2015-11-22 02:31 | 1.1667 | 758 | 884.3333 | 1.1667 | -1.8333 | 0.002674 | 0 | 0 | 0.002292 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB 3 | CB 3 A/R due to Lightning | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0 | 0.002292 | 2016 | 2015-11-22 | C | 758 | 0 | 0.002292
8259534 | 2015-11-22 03:16 | 2015-11-22 06:58 | 222.0333 | 4 | 888.1333 | 222.0333 | 219.0333 | 0.0026855 | 876.1333 | 0.0026492 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC424 | No Power Gabriel Black 0274863052. 3x3amp fuses blown at transformer TC424 blown due to lightning. Reload Reliven 0658. Outage reflected under OMS 8285475 | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0026492 | 1.2095e-05 | 2016 | 2015-11-22 | C | 4 | 0.0026492 | 1.2095e-05
8259686 | 2015-11-22 05:10 | 2015-11-22 05:26 | 15.8 | 279 | 4408.2 | 15.8 | 12.8 | 0.013329 | 3571.2 | 0.010798 | 0.00084363 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 9147 | recloser 9147 tripped due to lightning. NOC closed after 15minutes | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.010798 | 0.00084363 | 2016 | 2015-11-22 | C | 279 | 0.010798 | 0.00084363
8260162 | 2015-11-22 05:20 | 2015-11-22 09:44 | 264.3 | 1 | 264.3 | 264.3 | 261.3 | 0.00079918 | 261.3 | 0.00079011 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TP1788 | 2 x 6A Fuses and Carriers | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00079011 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00079011 | 3.0238e-06
8260171 | 2015-11-22 05:20 | 2015-11-22 08:20 | 180 | 3 | 469.65 | 156.55 | 153.55 | 0.0014201 | 460.65 | 0.0013929 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2783 | TC2783 2 X 3A Fuses Replaced TP2369 1 X 2A Fuses Replaced (refer outage OMS 8286759) TC2295 3 X 3A Fuses Replaced | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0013929 | 9.071e-06 | 2016 | 2015-11-22 | C | 3 | 0.0013929 | 9.0713e-06
8260371 | 2015-11-22 05:34 | 2015-11-22 09:50 | 256.0167 | 2 | 512.0333 | 256.0167 | 253.0167 | 0.0015483 | 506.0333 | 0.0015301 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4484 | 3 x 2A HV Fuses. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0015301 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.0015301 | 6.0475e-06
8260377 | 2015-11-22 05:34 | 2015-11-22 15:06 | 572.2 | 8 | 4577.6 | 572.2 | 569.2 | 0.013842 | 4553.6 | 0.013769 | 2.419e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC219 | Transformer blown by lightning. Replaced | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.013769 | 2.419e-05 | 2016 | 2015-11-22 | C | 8 | 0.013769 | 2.419e-05
8261538 | 2015-11-22 06:00 | 2015-11-22 10:09 | 249.0167 | 1 | 249.0167 | 249.0167 | 246.0167 | 0.00075297 | 246.0167 | 0.0007439 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2230 | *** please check if 114 MCCABE ROAD - tx tc5277 is part of this outage *** 3 x 3A Fuses. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0007439 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0007439 | 3.0238e-06
8262393 | 2015-11-22 06:10 | 2015-11-22 06:26 | 16.1833 | 841 | 5399.5833 | 6.4204 | 3.4204 | 0.016327 | 2876.5833 | 0.0086981 | 0.002543 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 9512 | Trip Flag E/F. Suspect Lightning. These steps are recorded in 8260677. This switching sheet was copied and then renamed to reflect these steps. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0086981 | 0.002543 | 2016 | 2015-11-22 | C | 841 | 0.0086981 | 0.002543
8263249 | 2015-11-22 06:14 | 2015-11-22 10:35 | 261.3833 | 6 | 1568.3 | 261.3833 | 258.3833 | 0.0047422 | 1550.3 | 0.0046877 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC701 | 2x 2A Fuse Replaced | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0046877 | 1.8143e-05 | 2016 | 2015-11-22 | C | 6 | 0.0046877 | 1.8143e-05
8263282 | 2015-11-22 06:21 | 2015-11-22 07:44 | 82.9667 | 1 | 82.9667 | 82.9667 | 79.9667 | 0.00025087 | 79.9667 | 0.0002418 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1687 | 2 x 3A Fuses Replaced | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0002418 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0002418 | 3.0238e-06
8263514 | 2015-11-22 06:35 | 2015-11-23 14:56 | 1940.7833 | 2 | 3881.5667 | 1940.7833 | 1937.7833 | 0.011737 | 3875.5667 | 0.011719 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC5176 | Transformer TC5175 found blown. To be replaced. svs hub advised transformer to be replaced tomorrow, Pieter called control to advise of this earlier today, 1 house without power. Transformer Changed | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.011719 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.011719 | 6.0475e-06
8263551 | 2015-11-22 06:41 | 2015-11-22 11:00 | 258.9667 | 1 | 258.9667 | 258.9667 | 255.9667 | 0.00078305 | 255.9667 | 0.00077398 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2896 | 2 x 2A HV Fuses | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00077398 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00077398 | 3.0238e-06
8263576 | 2015-11-22 06:50 | 2015-11-22 11:43 | 293.3167 | 1 | 293.3167 | 293.3167 | 290.3167 | 0.00088692 | 290.3167 | 0.00087785 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4044 | 2 x 20A HV Fuses | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00087785 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00087785 | 3.0238e-06
8263596 | 2015-11-22 07:03 | 2015-11-22 08:58 | 114.85 | 1 | 114.85 | 114.85 | 111.85 | 0.00034728 | 111.85 | 0.00033821 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD3018 | 2 X 3A Fuses Replaced | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00033821 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00033821 | 3.0238e-06
8263606 | 2015-11-22 07:07 | 2015-11-22 09:03 | 115.85 | 1 | 115.85 | 115.85 | 112.85 | 0.0003503 | 112.85 | 0.00034123 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1011 | 2 x 3A Fuses | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00034123 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00034123 | 3.0238e-06
8264753 | 2015-11-22 07:42 | 2015-11-22 19:33 | 710.6 | 8 | 2828.2667 | 353.5333 | 350.5333 | 0.008552 | 2804.2667 | 0.0084794 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1089 | Reloaded, Relivened 3x DDO's at Transformer TC1089. Also replaced 1x LV Pin & Insulator. Lightning is the probable cause of this fault. OMS Outage for TC1089 was child job: 8275365. TC2694 never went off. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0084794 | 2.419e-05 | 2016 | 2015-11-22 | C | 8 | 0.0084794 | 2.419e-05
8264812 | 2015-11-22 07:52 | 2015-11-22 10:52 | 180.4167 | 1 | 180.4167 | 180.4167 | 177.4167 | 0.00054554 | 177.4167 | 0.00053647 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC3374 | TC 3374. 2 x 3A HV Fuses Replaced. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00053647 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00053647 | 3.0238e-06
8264822 | 2015-11-22 07:53 | 2015-11-22 13:20 | 327.6667 | 2 | 655.3333 | 327.6667 | 324.6667 | 0.0019816 | 649.3333 | 0.0019634 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC5313 | Letitia from Mercury advise the customer at #162 only heard this explosion at 5am. No smoking or fire, ect so removed the hazard. 2 X 3 AMP DDO LINKS DUE TO LIGHTNING. DISPATCH SIGNED OFF MURRAY TO BUSY | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0019634 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.0019634 | 6.0475e-06
8264844 | 2015-11-22 07:54 | 2015-11-22 16:20 | 505.6167 | 1 | 505.6167 | 505.6167 | 502.6167 | 0.0015289 | 502.6167 | 0.0015198 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP65 | Fuses FP65 2 x 8A HV Fuses. TC1588 3 x 3A HV Fuses | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0015198 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0015198 | 3.0238e-06
8264873 | 2015-11-22 07:57 | 2015-11-22 11:52 | 234.6333 | 1 | 234.6333 | 234.6333 | 231.6333 | 0.00070948 | 231.6333 | 0.0007004 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4424 | 3 x 6A Fuses | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0007004 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0007004 | 3.0238e-06
8264896 | 2015-11-22 08:01 | 2015-11-22 09:31 | 89.6833 | 1 | 89.6833 | 89.6833 | 86.6833 | 0.00027118 | 86.6833 | 0.00026211 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1039 | *** check if oms 8265863 - 5836A SH2 - Transformer TC3046 relates *** 2 x 6A HV Fuses Replaced | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00026211 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00026211 | 3.0238e-06
8265497 | 2015-11-22 08:13 | 2015-11-22 08:34 | 20.9833 | 163 | 3420.2833 | 20.9833 | 17.9833 | 0.010342 | 2931.2833 | 0.0088635 | 0.00049287 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RC04 | Recloser Tripped. E/F. L/O. Not Patrolled. Closed back in OK | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0088635 | 0.00049287 | 2016 | 2015-11-22 | C | 163 | 0.0088635 | 0.00049287
8265708 | 2015-11-22 08:27 | 2015-11-22 21:20 | 772.6667 | 4 | 3090.6667 | 772.6667 | 769.6667 | 0.0093454 | 3078.6667 | 0.0093092 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA2-035 | Reloaded, Relivened 2x DDO's at Transformer TA2-035. Caused by lightning | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0093092 | 1.2095e-05 | 2016 | 2015-11-22 | C | 4 | 0.0093092 | 1.2095e-05
8265753 | 2015-11-22 08:33 | 2015-11-22 20:10 | 696.6167 | 4 | 2786.4667 | 696.6167 | 693.6167 | 0.0084256 | 2774.4667 | 0.0083893 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TB1-162 | Reloaded, Relivened 2x DDO's at Transformer TB1-162. Cause was lightning. Mike James Attended. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0083893 | 1.2095e-05 | 2016 | 2015-11-22 | C | 4 | 0.0083893 | 1.2095e-05
8265849 | 2015-11-22 08:41 | 2015-11-22 16:58 | 496.65 | 1 | 496.65 | 496.65 | 493.65 | 0.0015018 | 493.65 | 0.0014927 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC650 | oms 8259642 possibly relates 12.03pm called customer to confirm if power restored? Job 8259642 has been completed 1x 8amp fuse replaced... Called customer no ans on celphone 12.07pm still no ans 12.17pm called customer still no answer 12.45pm called custo | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0014927 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0014927 | 3.0238e-06
8265883 | 2015-11-22 08:47 | 2015-11-22 20:06 | 679.05 | 4 | 2377.3167 | 594.3292 | 591.3292 | 0.0071884 | 2365.3167 | 0.0071522 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC442 | At 08:46, Kerepehi Sub, CB 6 Ngatea Feeder. Found Transformer TC442 had blown due to lightning. Own Isolation & AP. Transformer Replaced. All Power Restored on Completion. 1x Transformer Used. plz check if oms 8269193 related 310 Pipiroa Road. Transformer | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0071522 | 1.2095e-05 | 2016 | 2015-11-22 | C | 4 | 0.0071522 | 1.2095e-05
8266029 | 2015-11-22 09:07 | 2015-11-22 15:17 | 370.4667 | 1 | 370.4667 | 370.4667 | 367.4667 | 0.0011202 | 367.4667 | 0.0011111 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1888 | 3 x 3A fuses | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0011111 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.0011111 | 3.0238e-06
8266471 | 2015-11-22 09:10 | 2015-11-22 11:30 | 140.1667 | 3 | 420.5 | 140.1667 | 137.1667 | 0.0012715 | 411.5 | 0.0012443 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4682 | Replaced 3x 8Amp HV Fuse Links | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0012443 | 9.071e-06 | 2016 | 2015-11-22 | C | 3 | 0.0012443 | 9.0713e-06
8266482 | 2015-11-22 09:02 | 2015-11-22 10:42 | 100 | 649 | 21038 | 32.416 | 29.416 | 0.063614 | 19091 | 0.057727 | 0.0019624 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | Feeder fault CB 6777/5 A/R, L/O, E/F, O/C B Phase. Sectionalised & Patrolled with no fault found | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-22 | c | 0.057727 | 0.0019624 | 2016 | 2015-11-22 | C | 649 | 0.057727 | 0.0019624
8266495 | 2015-11-22 09:15 | 2015-11-22 17:54 | 518.9 | 7 | 3632.3 | 518.9 | 515.9 | 0.010983 | 3611.3 | 0.01092 | 2.1166e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA2-014 | Transformer TA2-014 blown by lightning. Transformer Replaced. | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.01092 | 2.1166e-05 | 2016 | 2015-11-22 | C | 7 | 0.01092 | 2.1166e-05
8266527 | 2015-11-22 09:21 | 2015-11-22 17:28 | 486.6167 | 2 | 973.2333 | 486.6167 | 483.6167 | 0.0029428 | 967.2333 | 0.0029247 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1998 | 2 x 6A Fuse Replaced | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0029247 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.0029247 | 6.0475e-06
8266592 | 2015-11-22 09:28 | 2015-11-22 10:43 | 74.85 | 1 | 74.85 | 74.85 | 71.85 | 0.00022633 | 71.85 | 0.00021726 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2230 | 3 x 3A Fuses TC2230 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00021726 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00021726 | 3.0238e-06
8266847 | 2015-11-22 09:58 | 2015-11-22 10:20 | 22.3333 | 1 | 22.3333 | 22.3333 | 19.3333 | 6.7531e-05 | 19.3333 | 5.8459e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP231 | Replace Fuse after Lightning Strike. Taui Ganley on Site 2 x 6A Fuses | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 5.8459e-05 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 5.8459e-05 | 3.0238e-06
8267121 | 2015-11-22 10:41 | 2015-11-22 13:11 | 149.8833 | 1 | 149.8833 | 149.8833 | 146.8833 | 0.00045321 | 146.8833 | 0.00044414 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 8261538 | 2 x 3amp DDO FUSES AT TX DUE TO LIGHTNING, SIGNED OFF VIA HUB MURRAY TOO BUSY. No other assets repaired or replaced. Adjacent assets ok | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00044414 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00044414 | 3.0238e-06
8267491 | 2015-11-22 10:57 | 2015-11-22 13:13 | 136.7167 | 1 | 136.7167 | 136.7167 | 133.7167 | 0.0004134 | 133.7167 | 0.00040433 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5/277 | 3 X 6AMP DDO DUE TO LIGHTNING. DISPATCH SIGNED OFF MURRAY BUSY | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00040433 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00040433 | 3.0238e-06
8267595 | 2015-11-22 11:15 | 2015-11-22 13:05 | 109.85 | 1 | 109.85 | 109.85 | 106.85 | 0.00033216 | 106.85 | 0.00032309 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE8-007 | 2 x 10A HV fuses | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00032309 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00032309 | 3.0238e-06
8269147 | 2015-11-22 12:23 | 2015-11-22 17:06 | 282.9333 | 2 | 565.8667 | 282.9333 | 279.9333 | 0.001711 | 559.8667 | 0.0016929 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1573 | ADVISES 3X HT FUSES DOWN. 1 x 6A HV Fuse replaced in Fuses FP1-076. Replaced 2x 3a HV fuses on TC1533 and 1x 6a fuse at fuse 1076 and also cut away LV causing fault, due to lightning | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0016929 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.0016929 | 6.0475e-06
8269526 | 2015-11-22 13:30 | 2015-11-22 16:12 | 161.7333 | 1 | 161.7333 | 161.7333 | 158.7333 | 0.00048904 | 158.7333 | 0.00047997 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA2-128 | 1.48pm called customer to confirm they still have part power as faultman has just replaced and hv fuse down the road, confirmed with Lewis that pump still has part power advised Lianne at svs hub svshub advised that FM replaced 2a HV fuse TP212, svs hub a | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00047997 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00047997 | 3.0238e-06
8269979 | 2015-11-22 14:42 | 2015-11-22 16:04 | 82.1833 | 17 | 1397.1167 | 82.1833 | 79.1833 | 0.0042245 | 1346.1167 | 0.0040703 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 802379 | Repaired 11kV Line Down. Isolated at Fuses 1424. Materials used: 6mtrs of 16mm cu. conductor, 2 sleeves, 1x 8Amp HV Link | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-11-22 | c | 0.0040703 | 5.1404e-05 | 2016 | 2015-11-22 | C | 17 | 0.0040703 | 5.1404e-05
8270876 | 2015-11-22 16:10 | 2015-11-22 17:03 | 52.85 | 1 | 52.85 | 52.85 | 49.85 | 0.00015981 | 49.85 | 0.00015073 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5430 | 2 x 2A HV Fuses Replaced | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00015073 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00015073 | 3.0238e-06
8270967 | 2015-11-22 16:32 | 2015-11-22 20:51 | 258.8 | 90 | 17198.4833 | 191.0943 | 188.0943 | 0.052004 | 16928.4833 | 0.051188 | 0.00027214 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | RS693 | O/C A B Phase | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-22 | c | 0.051188 | 0.00027214 | 2016 | 2015-11-22 | C | 90 | 0.051188 | 0.00027214
8271078 | 2015-11-22 16:36 | 2015-11-22 19:07 | 151.0667 | 30 | 4532 | 151.0667 | 148.0667 | 0.013704 | 4442 | 0.013432 | 9.0713e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5562 | customer advising duck strike at 44 Kent terrace, advised control and svs hub. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-22 | c | 0.013432 | 9.0713e-05 | 2016 | 2015-11-22 | C | 30 | 0.013432 | 9.0713e-05
8271314 | 2015-11-22 16:43 | 2015-11-22 18:03 | 80.5 | 904 | 30747.7333 | 34.013 | 31.013 | 0.092974 | 28035.7333 | 0.084773 | 0.0027335 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | CB 3086 A/R, L/O, E/F, O/C A-B-C Phase causing total outage of Rata Sub. Backfed Rata CB1350(Hunterville 22kV feeder) but CB control problems meant rest of Sub could not be backfed. Patrolled 33kV with no fault found. Relivened ok. | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-11-22 | c | 0.084773 | 0.0027335 | 2016 | 2015-11-22 | C | 904 | 0.084773 | 0.0027335
8272390 | 2015-11-22 17:10 | 2015-11-22 20:46 | 216 | 5 | 1079.7667 | 215.9533 | 212.9533 | 0.003265 | 1064.7667 | 0.0032196 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC6116 | Reloaded Relivened 3x DDO's at Transformer TC6116. Caused by lightning. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0032196 | 1.5119e-05 | 2016 | 2015-11-22 | C | 5 | 0.0032196 | 1.5119e-05
8273914 | 2015-11-22 17:29 | 2015-11-22 20:30 | 180.8333 | 317 | 37207.5 | 117.3738 | 114.3738 | 0.11251 | 36256.5 | 0.10963 | 0.00095853 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772308 | Floating Conductor at Pole 772308 Car has hit this pole at some time fence Broken Paint on Pole | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-22 | c | 0.10963 | 0.00095853 | 2016 | 2015-11-22 | C | 317 | 0.10963 | 0.00095853
8275417 | 2015-11-22 19:46 | 2015-11-22 22:00 | 134.35 | 2 | 268.7 | 134.35 | 131.35 | 0.00081248 | 262.7 | 0.00079434 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA2-055 | Reloaded Relivened 2x DDOs at Transformer TA2-055. Also had to replace both DDO barrels as they were old and deteriorated. Mike James Attended. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00079434 | 6.048e-06 | 2016 | 2015-11-22 | C | 2 | 0.00079434 | 6.0475e-06
8276259 | 2015-11-23 08:34 | 2015-11-23 09:20 | 46 | 36 | 1656 | 46 | 43 | 0.0050073 | 1548 | 0.0046808 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2378 | Isolated to replace fuse at FC2378 | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-23 | c | 0.0046808 | 0.00010886 | 2016 | 2015-11-23 | C | 36 | 0.0046808 | 0.00010886
8278527 | 2015-11-23 09:09 | 2015-11-23 11:40 | 150.6333 | 2 | 301.2667 | 150.6333 | 147.6333 | 0.00091096 | 295.2667 | 0.00089282 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC4009 | Fuses FC4009 3 x 6A Fuses Replaced. Transformer TC1362 3 X 6A Fuses Replaced | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-23 | c | 0.00089282 | 6.048e-06 | 2016 | 2015-11-23 | C | 2 | 0.00089282 | 6.0475e-06
8278542 | 2015-11-23 09:10 | 2015-11-23 09:57 | 46.8667 | 1 | 46.8667 | 46.8667 | 43.8667 | 0.00014171 | 43.8667 | 0.00013264 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of planned outage 13111. fault man confirms customer is feed from Transformer T6/452 which is part of outage. email sent to GIS team to correct. | F3 | GEMINI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-23 | c | 0.00013264 | 3.024e-06 | 2016 | 2015-11-23 | C | 1 | 0.00013264 | 3.0238e-06
8278653 | 2015-11-23 09:26 | 2015-11-23 14:19 | 293.3 | 78 | 22877.4 | 293.3 | 290.3 | 0.069176 | 22643.4 | 0.068468 | 0.00023585 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219118 | 10341 OMS 8280059 related 1044A Papmoa Beach Road, Low voltage. 1 x 11kv Crossarm 3 x 11kv DDO units. 3 x 15A HV Fuses | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-23 | c | 0.068468 | 0.00023585 | 2016 | 2015-11-23 | C | 78 | 0.068468 | 0.00023585
8279987 | 2015-12-16 08:45 | 2015-12-16 15:35 | 409.4833 | 3 | 1228.45 | 409.4833 | 406.4833 | 0.0037145 | 1219.45 | 0.0036873 | 9.0713e-06 | NAPA ID:13486 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 829449 | Replace pole 829448 and arms between 829449 to 829451 deenergised. Works location: Te Whiti Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-16 | b | 0.0018437 | 4.536e-06 | 2016 | 2015-12-16 | B | 3 | 0.0036873 | 9.0713e-06
8280376 | 2015-12-08 10:30 | 2015-12-08 14:15 | 225 | 8 | 1800 | 225 | 222 | 0.0054428 | 1776 | 0.0053702 | 2.419e-05 | NAPA ID:13823 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TF5-007 | Upgrade TF5-007 from 30kVA to 50kVA. LLP- Tap -up third phase for new transformer. Works location: No. 1 Rd, Te Puke. WO 30015624 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-12-08 | b | 0.0026851 | 1.2095e-05 | 2016 | 2015-12-08 | B | 8 | 0.0053702 | 2.419e-05
8280717 | 2015-11-23 12:36 | 2015-11-23 16:30 | 234 | 10 | 2340 | 234 | 231 | 0.0070756 | 2310 | 0.0069849 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 791859 | tree branches on network power lines and now lines are down. customer has no power. thinks network line. 12.15pm advised Tallia at svs hub & adv control. Faultman found tree had falling over the lines at pole 791859, line was isolated at Fuses 765 to rep | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-11-23 | c | 0.0069849 | 3.0238e-05 | 2016 | 2015-11-23 | C | 10 | 0.0069849 | 3.0238e-05
8280777 | 2015-11-23 12:21 | 2015-11-23 14:45 | 143.1333 | 1 | 143.1333 | 143.1333 | 140.1333 | 0.0004328 | 140.1333 | 0.00042373 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219118 | Relates to 8280777. OMS 8280059 related 1044A Papmoa Beach Road, Low voltage. 1 x 11kv Crossarm. 3 x 11kv DDO units. 3 x 15A HV Fuses | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-23 | c | 0.00042373 | 3.024e-06 | 2016 | 2015-11-23 | C | 1 | 0.00042373 | 3.0238e-06
8281743 | 2015-11-23 15:46 | 2015-11-23 16:29 | 43 | 9 | 387 | 43 | 40 | 0.0011702 | 360 | 0.0010886 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 836288 | Faultman found broken guy wire on pole 836288 at transformer T3672, suspect hit by hedge cutter, line was isolated at Fuses 7013 to re-terminate the guy wire. NDR : 34819 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-11-23 | c | 0.0010886 | 2.7214e-05 | 2016 | 2015-11-23 | C | 9 | 0.0010886 | 2.7214e-05
8281899 | 2015-11-23 15:33 | 2015-11-23 16:46 | 73.3667 | 4 | 293.4667 | 73.3667 | 70.3667 | 0.00088737 | 281.4667 | 0.00085109 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2472 | 2 x 2A HV Fuses Replaced | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-11-23 | c | 0.00085109 | 1.2095e-05 | 2016 | 2015-11-23 | C | 4 | 0.00085109 | 1.2095e-05
8282480 | 2015-11-23 17:09 | 2015-11-23 18:40 | 90.5833 | 2 | 181.1667 | 90.5833 | 87.5833 | 0.0005478 | 175.1667 | 0.00052966 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | M68 | Faultman found blown fuses at Fuses M68, faultman found that trees are in the lines, faultman has advised the customer to get them cut by Powerco tree contractor. 2 x 6A Amp HV fuses replaced. NDR #N300127 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-23 | c | 0.00052966 | 6.048e-06 | 2016 | 2015-11-23 | C | 2 | 0.00052966 | 6.0475e-06
8284755 | 2015-11-24 01:06 | 2015-11-24 11:35 | 629.15 | 113 | 57523.7833 | 509.06 | 506.06 | 0.17394 | 57184.7833 | 0.17291 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780187 | RS 513 A/R, L/O, E/F, O/C B & C Phase. 0855 Call from retailer to advise lines down 1244 Waitotara Valley Road, advised Todd in Control. Faultman found LV line rapped around 11KV line between poles 780187 & 780188, LV line was unwound with hot line sticks | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-11-24 | c | 0.17291 | 0.00034168 | 2016 | 2015-11-24 | C | 113 | 0.17291 | 0.00034168
8286709 | 2015-11-22 05:49 | 2015-11-22 07:27 | 98.4833 | 21 | 2068.15 | 98.4833 | 95.4833 | 0.0062536 | 2005.15 | 0.0060631 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC4044 | Replaced 2x 20A fuses at FC4044 due to lightning. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.0060631 | 6.3499e-05 | 2016 | 2015-11-22 | C | 21 | 0.0060631 | 6.3499e-05
8286744 | 2015-12-11 10:00 | 2015-12-11 10:30 | 30 | 7 | 210 | 30 | 27 | 0.00063499 | 189 | 0.00057149 | 2.1166e-05 | NAPA ID:14020 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3923 | To install a 400V Fuse disconnector. Works location: Hwy 17, Tatuanui. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.00028575 | 1.0583e-05 | 2016 | 2015-12-11 | B | 7 | 0.00057149 | 2.1166e-05
8286865 | 2015-12-11 11:30 | 2015-12-11 12:40 | 70 | 4 | 280 | 70 | 67 | 0.00084665 | 268 | 0.00081037 | 1.2095e-05 | NAPA ID:14021 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4099 | To install a 400V Fuse disconnector. Works location: Hwy 27, Tatuanui. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.00040518 | 6.048e-06 | 2016 | 2015-12-11 | B | 4 | 0.00081037 | 1.2095e-05
8286885 | 2015-12-11 14:00 | 2015-12-11 14:25 | 25 | 4 | 100 | 25 | 22 | 0.00030238 | 88 | 0.00026609 | 1.2095e-05 | NAPA ID:14022 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4602 | To install a 400V Fuse disconnector. Works location: Hwy 27, Tatuanui. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.00013305 | 6.048e-06 | 2016 | 2015-12-11 | B | 4 | 0.00026609 | 1.2095e-05
8287433 | 2015-12-09 09:00 | 2015-12-09 09:19 | 19 | 17 | 323 | 19 | 16 | 0.00097667 | 272 | 0.00082246 | 5.1404e-05 | NAPA ID:13925 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-021 | Replace 11kV fuse enclosure SD3-072 with a CFCF RMU. Works location: Gargan Rd, Tauranga. WO 30015152. Shutdown cancelled as major customer had not been notified. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-09 | b | 0.00041123 | 2.5702e-05 | 2016 | 2015-12-09 | B | 17 | 0.00082246 | 5.1404e-05
8287495 | 2015-12-14 10:00 | 2015-12-14 10:40 | 40 | 3 | 120 | 40 | 37 | 0.00036285 | 111 | 0.00033564 | 9.0713e-06 | NAPA ID:14023 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC718 | To install a 400V Fuse Disconnector. Works location: Settlement Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-14 | b | 0.00016782 | 4.536e-06 | 2016 | 2015-12-14 | B | 3 | 0.00033564 | 9.0713e-06
8287528 | 2015-12-14 12:00 | 2015-12-14 12:30 | 30 | 9 | 270 | 30 | 27 | 0.00081642 | 243 | 0.00073477 | 2.7214e-05 | NAPA ID:14024 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2208 | To install a 400V fuse disconnector. Works location: Settlement Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-14 | b | 0.00036739 | 1.3607e-05 | 2016 | 2015-12-14 | B | 9 | 0.00073477 | 2.7214e-05
8287550 | 2015-12-14 14:00 | 2015-12-14 15:15 | 75 | 4 | 300 | 75 | 72 | 0.00090713 | 288 | 0.00087084 | 1.2095e-05 | NAPA ID:14025 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3577 | To install a 400V Fuse Disconnector. Works location: Hwy 27, Tatuanui. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-14 | b | 0.00043542 | 6.048e-06 | 2016 | 2015-12-14 | B | 4 | 0.00087084 | 1.2095e-05
8287601 | 2015-12-15 09:54 | 2015-12-15 15:54 | 360 | 33 | 11880 | 360 | 357 | 0.035922 | 11781 | 0.035623 | 9.9784e-05 | NAPA ID:14555 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI707 | Replace poles and lines ball rd alton. Works location: Ball Rd. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.017811 | 4.9892e-05 | 2016 | 2015-12-15 | B | 33 | 0.035623 | 9.9784e-05
8287756 | 2015-12-09 09:04 | 2015-12-09 15:51 | 407 | 204 | 83028 | 407 | 404 | 0.25106 | 82416 | 0.24921 | 0.00061685 | NAPA ID:14572 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC4-616 | Replace poles, crossarms and conductors. Works location: Matua Rd. WO 30015219 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2015-12-09 | b | 0.1246 | 0.00030842 | 2016 | 2015-12-09 | B | 204 | 0.24921 | 0.00061685
8287805 | 2015-12-09 09:12 | 2015-12-09 13:27 | 254.7667 | 4 | 1019.0667 | 254.7667 | 251.7667 | 0.0030814 | 1007.0667 | 0.0030451 | 1.2095e-05 | NAPA ID:14875 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV N20 | Replace faulty recloser N21 with a NOVA and form 6 controller. Works location: Pembertons Corner. WO 30014813 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-12-09 | b | 0.0015226 | 6.048e-06 | 2016 | 2015-12-09 | B | 4 | 0.0030451 | 1.2095e-05
8287847 | 2015-12-11 09:00 | 2015-12-11 14:15 | 315 | 204 | 64260 | 315 | 312 | 0.19431 | 63648 | 0.19246 | 0.00061685 | NAPA ID:14576 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC4-616 | Replace poles, crossarms and conductors. Works location: Matua Rd. WO 30015219 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.096228 | 0.00030842 | 2016 | 2015-12-11 | B | 204 | 0.19246 | 0.00061685
8288816 | 2015-12-03 09:01 | 2015-12-03 16:42 | 461 | 34 | 15674 | 461 | 458 | 0.047394 | 15572 | 0.047086 | 0.00010281 | NAPA ID:14781 TP_CARRINGTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse 8202 | Pi pole replacement 754885/754886. Works location: Paraite Rd. WO 30002054 | F1 | BELL BLOCK 3 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.023543 | 5.1404e-05 | 2016 | 2015-12-03 | B | 34 | 0.047086 | 0.00010281
8288830 | 2015-11-24 19:00 | 2015-11-24 20:58 | 118 | 4 | 472 | 118 | 115 | 0.0014272 | 460 | 0.0013909 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E13046 | Report of rotten crossarm hanging down at Pole E13046 beyond Fuses FP1384. Rapid no. 771 TaoTaoroa Rd. At transformer TC1058. 11kV Crossarm complete replaced | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-24 | c | 0.0013909 | 1.2095e-05 | 2016 | 2015-11-24 | C | 4 | 0.0013909 | 1.2095e-05
8288940 | 2015-12-15 09:38 | 2015-12-15 12:46 | 188 | 4 | 752 | 188 | 185 | 0.0022739 | 740 | 0.0022376 | 1.2095e-05 | NAPA ID:13653 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3349 | LLP to replace the 11kV Fuses TC3349. AP to replace the 400V Cross-arm and install a 400V Fuse Disconnector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.0011188 | 6.048e-06 | 2016 | 2015-12-15 | B | 4 | 0.0022376 | 1.2095e-05
8289171 | 2015-12-15 12:00 | 2015-12-15 12:25 | 25 | 12 | 300 | 25 | 22 | 0.00090713 | 264 | 0.00079827 | 3.6285e-05 | NAPA ID:14029 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3606 | To install a 400V Fuse Disconnector. Works location: Hutchinson Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.00039914 | 1.8143e-05 | 2016 | 2015-12-15 | B | 12 | 0.00079827 | 3.6285e-05
8289195 | 2015-12-15 13:59 | 2015-12-15 15:04 | 65.3167 | 3 | 195.95 | 65.3167 | 62.3167 | 0.00059251 | 186.95 | 0.00056529 | 9.0713e-06 | NAPA ID:13752 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2364 | To install a 400V Fuse disconnector. Works location: Morrinsville Walton Rd. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.00028265 | 4.536e-06 | 2016 | 2015-12-15 | B | 3 | 0.00056529 | 9.0713e-06
8289287 | 2015-11-22 10:05 | 2015-11-22 13:26 | 200.5833 | 1 | 200.5833 | 200.5833 | 197.5833 | 0.00060652 | 197.5833 | 0.00059744 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tp505 | Blown transformer due to lightning. Replaced. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-22 | c | 0.00059745 | 3.024e-06 | 2016 | 2015-11-22 | C | 1 | 0.00059744 | 3.0238e-06
8289309 | 2015-12-15 14:00 | 2015-12-15 14:20 | 20 | 4 | 80 | 20 | 17 | 0.0002419 | 68 | 0.00020562 | 1.2095e-05 | NAPA ID:14031 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1958 | To install a 400V fuse Disconnector. Works location: Hwy 27, Tatuanui. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.00010281 | 6.048e-06 | 2016 | 2015-12-15 | B | 4 | 0.00020562 | 1.2095e-05
8289351 | 2015-12-16 09:05 | 2015-12-16 16:18 | 433 | 51 | 22083 | 433 | 430 | 0.066774 | 21930 | 0.066311 | 0.00015421 | NAPA ID:14561 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV LI707 | Replace poles and lines on ball rd patea. NOTE TEMP 71 & TEMP 70 WILL BE REMOVED DURING THIS SHUTDOWN. Works location: Ball Rd. WO 30010887. Ran Over Time : Problems with Wire Run. 41 Spans not in a straight Line. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-16 | b | 0.033156 | 7.7106e-05 | 2016 | 2015-12-16 | B | 51 | 0.066311 | 0.00015421
8289436 | 2015-12-16 09:40 | 2015-12-16 13:15 | 215 | 3 | 645 | 215 | 212 | 0.0019503 | 636 | 0.0019231 | 9.0713e-06 | NAPA ID:14040 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1496 | To install 11kV fuses on TC766, straighten pole, Replace 400V Pin arm & install 400V disconnector on TP1848 & TC766. Works location: Duncan Rd, Matamata. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.00096156 | 4.536e-06 | 2016 | 2015-12-16 | B | 3 | 0.0019231 | 9.0713e-06
8289462 | 2015-12-16 14:00 | 2015-12-16 15:00 | 60 | 4 | 240 | 60 | 57 | 0.0007257 | 228 | 0.00068942 | 1.2095e-05 | NAPA ID:14042 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC295 | To install a 400V fuse Disconnector. Works location: Scherer Rd. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.00034471 | 6.048e-06 | 2016 | 2015-12-16 | B | 4 | 0.00068942 | 1.2095e-05
8291492 | 2015-11-24 19:39 | 2015-11-24 20:20 | 41.1833 | 9 | 370.65 | 41.1833 | 38.1833 | 0.0011208 | 343.65 | 0.0010391 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 361893 | Straighten Twisted crossarm. 2x 10Amp HV Fuse Links, 2x 16mm Nuts & Washer | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-11-24 | c | 0.0010391 | 2.7214e-05 | 2016 | 2015-11-24 | C | 9 | 0.0010391 | 2.7214e-05
8291787 | 2015-11-24 21:49 | 2015-11-25 03:22 | 333.4 | 857 | 95055.2 | 110.9162 | 107.9162 | 0.28742 | 92484.2 | 0.27965 | 0.0025914 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 222246 | Car V Pole. 1 x 11mtr Busk Pole. 2 x 11kV Crossarm assemblies. 1 x opossum Gaurd | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-11-24 | c | 0.27965 | 0.0025914 | 2016 | 2015-11-24 | C | 857 | 0.27965 | 0.0025914
8293226 | 2015-11-25 05:55 | 2015-11-25 07:00 | 64.8333 | 10 | 648.3333 | 64.8333 | 61.8333 | 0.0019604 | 618.3333 | 0.0018697 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 045 | 2 x 11kV Fuses replaced, due to bird strike. no damage to network. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-11-25 | c | 0.0018697 | 3.0238e-05 | 2016 | 2015-11-25 | C | 10 | 0.0018697 | 3.0238e-05
8293329 | 2015-12-16 10:10 | 2015-12-16 13:31 | 201 | 17 | 3417 | 201 | 198 | 0.010332 | 3366 | 0.010178 | 5.1404e-05 | NAPA ID:14599 TP_OPUNAKE GXP > TASMAN SUB > OPUNAKE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12121 | Relocate and replace transformer T2255 with same size unit. Works location: Ihaia Rd. WO 30002200 | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-12-16 | b | 0.005089 | 2.5702e-05 | 2016 | 2015-12-16 | B | 17 | 0.010178 | 5.1404e-05
8293582 | 2015-11-25 08:26 | 2015-11-25 09:59 | 92.5167 | 6 | 91.8333 | 15.3056 | 12.3056 | 0.00027768 | 73.8333 | 0.00022325 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7789 | Replaced 2 x 10amp fuses. 7789. Cause: Birds. Outage steps on child job attached | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-25 | c | 0.00022325 | 1.8143e-05 | 2016 | 2015-11-25 | C | 6 | 0.00022325 | 1.8143e-05
8293632 | 2015-11-25 06:09 | 2015-11-25 08:39 | 149.55 | 6 | 897.3 | 149.55 | 146.55 | 0.0027132 | 879.3 | 0.0026588 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD6-006 | Replaced 2 x 15Amp Fuses, due to bird strike | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-11-25 | c | 0.0026588 | 1.8143e-05 | 2016 | 2015-11-25 | C | 6 | 0.0026588 | 1.8143e-05
8293723 | 2015-12-15 08:30 | 2015-12-15 15:28 | 418.8667 | 39 | 16335.8 | 418.8667 | 415.8667 | 0.049396 | 16218.8 | 0.049042 | 0.00011793 | NAPA ID:13717 TP_WAIKINO GXP > PAEROA SUB > RAILWAY ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 382515 | Create L/L break at Pole 382515. Replace H/V crossarms at vaious locations and replace TC2679. Reinstate L/L break. Works location: Cullen St, Paeroa. WO 30010961 | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.024521 | 5.8963e-05 | 2016 | 2015-12-15 | B | 39 | 0.049042 | 0.00011793
8293780 | 2015-12-14 10:58 | 2015-12-15 14:29 | 1651 | 1 | 1651 | 1651 | 1648 | 0.0049922 | 1648 | 0.0049832 | 3.0238e-06 | NAPA ID:14884 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | Cut away the 11kV at pole 784396, and remove the line from pole 784396 to transformer X1419. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-12-14 | b | 0.0024916 | 1.512e-06 | 2016 | 2015-12-14 | B | 1 | 0.0049832 | 3.0238e-06
8294260 | 2015-11-25 09:39 | 2015-11-25 10:44 | 65.4333 | 1 | 65.4333 | 65.4333 | 62.4333 | 0.00019785 | 62.4333 | 0.00018878 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | fault was related to power works shut down, murrary advises that power has just been restored to people affected, this customer was not notified. not sure of planned outage number, could not find anything HV or LV related to this address | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-11-25 | c | 0.00018878 | 3.024e-06 | 2016 | 2015-11-25 | C | 1 | 0.00018878 | 3.0238e-06
8294448 | 2015-11-25 10:01 | 2015-11-25 13:50 | 228.8333 | 1 | 228.8333 | 228.8333 | 225.8333 | 0.00069194 | 225.8333 | 0.00068287 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1712 | 2R required to replace cross arm and 3x HV fuse Mounts TC3389 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-25 | c | 0.00068287 | 3.024e-06 | 2016 | 2015-11-25 | C | 1 | 0.00068287 | 3.0238e-06
8294845 | 2015-12-13 08:31 | 2015-12-13 17:04 | 512.5667 | 1 | 512.5667 | 512.5667 | 509.5667 | 0.0015499 | 509.5667 | 0.0015408 | 3.0238e-06 | NAPA ID:14894 TP_MT MAUNGANUI 33 GXP > TRITON SUB > HEWLETTS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | N/A - NOT APPLICABLE | Relocate Switchgear 9042 and TX TP580 and associated cables to allow room for open cut culvert installation. | F2 | HEWLETTS RD | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-12-13 | b | 0.0007704 | 1.512e-06 | 2016 | 2015-12-13 | B | 1 | 0.0015408 | 3.0238e-06
8294958 | 2015-12-14 09:30 | 2015-12-14 16:06 | 396 | 1 | 396 | 396 | 393 | 0.0011974 | 393 | 0.0011883 | 3.0238e-06 | NAPA ID:14859 TP_WAIKINO GXP > PAEROA SUB > SHAW AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP2894 | Replace pole N0697 and install new transformer TP2894 | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2015-12-14 | b | 0.00059417 | 1.512e-06 | 2016 | 2015-12-14 | B | 1 | 0.0011883 | 3.0238e-06
8323213 | 2015-12-17 09:15 | 2015-12-17 15:25 | 370.2333 | 28 | 10366.5333 | 370.2333 | 367.2333 | 0.031346 | 10282.5333 | 0.031092 | 8.4665e-05 | NAPA ID:14591 TP_BRUNSWICK GXP > PEAT ST SUB > WESTMERE PEAT ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4110 | Replace pole 769179 damaged by truck NDR 41839. Works location: Rapanui Rd, Wanganui. WO 30007436 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-12-17 | b | 0.015546 | 4.2333e-05 | 2016 | 2015-12-17 | B | 28 | 0.031092 | 8.4665e-05
8331748 | 2015-11-25 18:57 | 2015-11-25 19:30 | 33 | 1 | 33 | 33 | 30 | 9.9784e-05 | 30 | 9.0713e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L58 | Faultman found burnt jumper at bottom of Fuses L58, line was isolated at Fuses L58 to repair the jumper. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-25 | c | 9.0713e-05 | 3.024e-06 | 2016 | 2015-11-25 | C | 1 | 9.0713e-05 | 3.0238e-06
8332176 | 2015-11-25 20:29 | 2015-11-25 23:10 | 160.55 | 1 | 160.55 | 160.55 | 157.55 | 0.00048546 | 157.55 | 0.00047639 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4145T | Faultman found blown HV fuse on transformer 4145T. 1 X 2 amp HV fuse replaced. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-11-25 | c | 0.00047639 | 3.024e-06 | 2016 | 2015-11-25 | C | 1 | 0.00047639 | 3.0238e-06
8333694 | 2015-11-26 03:27 | 2015-11-26 06:10 | 162.9833 | 649 | 22259.4 | 34.298 | 31.298 | 0.067307 | 20312.4 | 0.06142 | 0.0019624 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 369 | CB 5 tripped on Bphase O/C & E/F flags line was patrolled and sectionalised and a broken insulator was found on ABS 369, line was isolated at ABS's 397 & 538 to replace the insulator. 1 X 11KV Insulator replaced. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-26 | c | 0.06142 | 0.0019624 | 2016 | 2015-11-26 | C | 649 | 0.06142 | 0.0019624
8335915 | 2015-11-26 05:19 | 2015-11-26 12:17 | 418.1833 | 689 | 69327.6167 | 100.6206 | 97.6206 | 0.20963 | 67260.6167 | 0.20338 | 0.0020834 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 380795 | Car V Pole 198 Wilson Rd North Maketu. Fire Comms Event # F1965958. Pole # 380795 Hilton left site at 9, Josh Read staying on site. Replace Pole, 8 x arms, 3 x Fuses | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-11-26 | c | 0.20338 | 0.0020834 | 2016 | 2015-11-26 | C | 689 | 0.20338 | 0.0020834
8337352 | 2015-11-26 06:46 | 2015-11-26 10:12 | 205.85 | 649 | 37972.65 | 58.5095 | 55.5095 | 0.11482 | 36025.65 | 0.10893 | 0.0019624 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752098 | Trip on E/F Ph A B & C OC. 1 x 11kV Insulator and Spindle. 1 x Binder | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-26 | c | 0.10893 | 0.0019624 | 2016 | 2015-11-26 | C | 649 | 0.10893 | 0.0019624
8338412 | 2015-11-26 07:07 | 2015-11-26 08:30 | 83.45 | 6 | 500.7 | 83.45 | 80.45 | 0.001514 | 482.7 | 0.0014596 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD4-034 | Reload Reliven at Transformer TD4-034. 2 x 20 A Fuses. Poss Bird Strike | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2015-11-26 | c | 0.0014596 | 1.8143e-05 | 2016 | 2015-11-26 | C | 6 | 0.0014596 | 1.8143e-05
8338628 | 2015-11-26 10:19 | 2015-11-26 14:42 | 263.4667 | 25 | 6586.6667 | 263.4667 | 260.4667 | 0.019917 | 6511.6667 | 0.01969 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | E1213 | Fire comms reporting car v pole. ETA required. F1965995. 094867948. Service hub advised eta 15mins. Notified fire comms. Car V Pole at Pole E1213. All persons Clear of lines. Lines 3m above Ground. Line isolated between ABS 2526 & 803 to replace broken po | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-11-26 | c | 0.01969 | 7.5594e-05 | 2016 | 2015-11-26 | C | 25 | 0.01969 | 7.5594e-05
8338713 | 2015-11-26 07:59 | 2015-11-26 09:04 | 64.9667 | 2 | 129.9333 | 64.9667 | 61.9667 | 0.00039289 | 123.9333 | 0.00037474 | 6.0475e-06 |  | 33 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | CB10060 | Tripping on 33kV CB10060 on OC protection. (Loss of supply to TWP North Wind Farm). CB had a HLT applied at the time for tree cutters. Advised by M.Allpress, trip on O/C due to high load at TWP while HLT applied (Approx 550A). Restriction of 500A to be ap | F2 | FAIRS RD | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-11-26 | c | 0.00037475 | 6.048e-06 | 2016 | 2015-11-26 | C | 2 | 0.00037474 | 6.0475e-06
8339183 | 2015-12-17 09:15 | 2015-12-17 11:40 | 145 | 24 | 3480 | 145 | 142 | 0.010523 | 3408 | 0.010305 | 7.257e-05 | NAPA ID:14860 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 819 | Replace very rotten termination X arms at poles E1990 & E1086. Works location: Pond Rd, Hinuera. WO 30017381 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-12-17 | b | 0.0051525 | 3.6285e-05 | 2016 | 2015-12-17 | B | 24 | 0.010305 | 7.257e-05
8339595 | 2015-12-17 10:00 | 2015-12-17 11:10 | 70 | 2 | 140 | 70 | 67 | 0.00042333 | 134 | 0.00040518 | 6.0475e-06 | NAPA ID:14047 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2342 | To replace the 400V arm & install a 400V fuse Disconnector. Works location: Landsdown Rd, Matamata. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-17 | b | 0.00020259 | 3.024e-06 | 2016 | 2015-12-17 | B | 2 | 0.00040518 | 6.0475e-06
8339698 | 2015-12-17 14:00 | 2015-12-17 14:35 | 35 | 7 | 245 | 35 | 32 | 0.00074082 | 224 | 0.00067732 | 2.1166e-05 | NAPA ID:14048 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC339 | To Replace the 400V Pin arm & install a 400V Disconnector. Works location: Kerk Rd, Matamata. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-17 | b | 0.00033866 | 1.0583e-05 | 2016 | 2015-12-17 | B | 7 | 0.00067732 | 2.1166e-05
8390271 | 2015-12-10 08:34 | 2015-12-10 08:46 | 12 | 122 | 1464 | 12 | 9 | 0.0044268 | 1098 | 0.0033201 | 0.0003689 | NAPA ID:14993 TP_TAURANGA 33 GXP > KAURI POINT > LINDERMANN RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Safelink 13021 | Replace SD1 with CFCC Safelink 13021. Works location: Hwy 2, Katikati. WO 10147833 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-12-10 | b | 0.00166 | 0.00018445 | 2016 | 2015-12-10 | B | 122 | 0.0033201 | 0.0003689
8391165 | 2015-11-26 12:14 | 2015-11-26 20:07 | 473.15 | 857 | 61462.05 | 71.7177 | 68.7177 | 0.18585 | 58891.05 | 0.17807 | 0.0025914 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 215457 | No Trip Flags. Pole down at 215457. Feeder sectionalizer & patrolled fault past Sw/Gear 9311/4. Isolation at Sw/Gear 9311/4 ( no back feeds ) pole 215457 replaced, all service restored Materials 1 x pole, 1 x double x arm complete, 2 x H/V sleeves | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-11-26 | c | 0.17807 | 0.0025914 | 2016 | 2015-11-26 | C | 857 | 0.17807 | 0.0025914
8426170 | 2015-11-26 20:48 | 2015-11-27 00:35 | 226.7833 | 833 | 40757.1 | 48.9281 | 45.9281 | 0.12324 | 38258.1 | 0.11568 | 0.0025188 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741869 | CB 2 tripped on O/C & E/F flags, received a call from fire services of lines down in Brown St, line was isolated at ABS"s 445 & 12114 to repair the lines that were in the river between poles 741869 & 741871. NDR: N100077. 50 meters of Namu conductor.15 Na | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-11-26 | c | 0.11568 | 0.0025188 | 2016 | 2015-11-26 | C | 833 | 0.11568 | 0.0025188
8427893 | 2015-11-26 21:16 | 2015-11-26 22:25 | 69.4167 | 1 | 69.4167 | 69.4167 | 66.4167 | 0.0002099 | 66.4167 | 0.00020083 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1316 | Faultman found a blown fuse on transformer 1316 and also found the customers meter box was damaged, did a safety disconnect - Number:15422. 1 X 2 amp HV fuse was replaced. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-11-26 | c | 0.00020083 | 3.024e-06 | 2016 | 2015-11-26 | C | 1 | 0.00020083 | 3.0238e-06
8428498 | 2015-11-27 06:15 | 2015-11-27 10:05 | 230 | 2 | 460 | 230 | 227 | 0.0013909 | 454 | 0.0013728 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC744 | Job started as Reload reliven at TC744.under 8428414 @ 05:00. This didn't fix the problem. Mundhir then did Reload reliven at fuses FP1487 at 06:15. Mundhir has found that transformer TC744 needs Replacement. All 1R component of job is covered under 84284 | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-11-27 | c | 0.0013728 | 6.048e-06 | 2016 | 2015-11-27 | C | 2 | 0.0013728 | 6.0475e-06
8428951 | 2015-11-27 07:42 | 2015-11-27 12:48 | 305.8667 | 307 | 33896.8333 | 110.4131 | 107.4131 | 0.1025 | 32975.8333 | 0.099711 | 0.00092829 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797194 | Recloser C627 Trip flags, Ph B O/C, E/F. Brunt cross arm and Pole were only repaired, NOT Replaced as Crew requests would indicate. Used 6 x Connectors and 3 Bolts. Defect to be lodged to Replace burnt pole and cross arm. | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.099711 | 0.00092829 | 2016 | 2015-11-27 | C | 307 | 0.099711 | 0.00092829
8429680 | 2015-11-27 09:47 | 2015-11-27 10:40 | 53 | 4 | 212 | 53 | 50 | 0.00064104 | 200 | 0.00060475 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 375713 | Crossarm at Pole 375713 Re-secured using 1 new Bolt. Fuses 7159 Opened, Tagged and Earths applied at pole 375753. | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.00060475 | 1.2095e-05 | 2016 | 2015-11-27 | C | 4 | 0.00060475 | 1.2095e-05
8445820 | 2015-11-27 08:35 | 2015-11-27 13:50 | 315 | 1 | 315 | 315 | 312 | 0.00095248 | 312 | 0.00094341 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 738832 | Hanging lines on farm, aprox 1-2m from ground, possible broken insulator. Replace 2 x cross arms, 3 x dead ends | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.00094341 | 3.024e-06 | 2016 | 2015-11-27 | C | 1 | 0.00094341 | 3.0238e-06
8446303 | 2015-11-27 09:19 | 2015-11-27 11:36 | 137.0833 | 1 | 137.0833 | 137.0833 | 134.0833 | 0.00041451 | 134.0833 | 0.00040544 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7 | Blown Fuses found at Transformer T7 - Used 2 x 2 amp fuses | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.00040544 | 3.024e-06 | 2016 | 2015-11-27 | C | 1 | 0.00040544 | 3.0238e-06
8447064 | 2015-11-27 10:52 | 2015-11-27 14:00 | 188.15 | 35 | 6585.25 | 188.15 | 185.15 | 0.019912 | 6480.25 | 0.019595 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7255 | 1 X 10A Fuse and Candle at 7255. 2 x 6A Fuse at 7257. NDR 23391 due to trees down stream of links 11057 at pole 848597. NOTE : There are 2 x 1R Request under this OMS Job. This covers both reload relivens at seperate Fuses. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.019595 | 0.00010583 | 2016 | 2015-11-27 | C | 35 | 0.019595 | 0.00010583
8447119 | 2015-12-11 02:47 | 2015-12-11 05:06 | 139.2167 | 173 | 23164.25 | 133.8974 | 130.8974 | 0.070043 | 22645.25 | 0.068474 | 0.00052311 | NAPA ID:14654 TP_KOPU GXP > TAIRUA SUB > PEPE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2635 | Replace L.V fuse base and leads. Works location: Main Rd, Tairua. WO 30013442 | F3 | PEPE RD | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-12-11 | b | 0.034237 | 0.00026156 | 2016 | 2015-12-11 | B | 173 | 0.068474 | 0.00052311
8447159 | 2015-12-03 08:40 | 2015-12-03 16:13 | 453 | 61 | 16149 | 264.7377 | 261.7377 | 0.048831 | 15966 | 0.048277 | 0.00018445 | NAPA ID:13864 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1927 | Replace 11kV Transformer T1927 and LV switchboard and reterminate 11kV cables at Transformer T1927. | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-12-03 | b | 0.024139 | 9.2225e-05 | 2016 | 2015-12-03 | B | 61 | 0.048277 | 0.00018445
8448023 | 2015-12-18 09:30 | 2015-12-18 10:57 | 87 | 48 | 4176 | 87 | 84 | 0.012627 | 4032 | 0.012192 | 0.00014514 | NAPA ID:14551 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V81 | To Remove temp fuses 47, not able to remove under LLP due to access issues. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-18 | b | 0.0060959 | 7.257e-05 | 2016 | 2015-12-18 | B | 48 | 0.012192 | 0.00014514
8449077 | 2015-12-18 09:03 | 2015-12-18 15:24 | 381.2167 | 8 | 3049.7333 | 381.2167 | 378.2167 | 0.0092217 | 3025.7333 | 0.0091491 | 2.419e-05 | NAPA ID:14400 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C19 | Change 2 pole transformer structure, install 13 x poles. Works location: Sanson Rd. WO 30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-18 | b | 0.0045745 | 1.2095e-05 | 2016 | 2015-12-18 | B | 8 | 0.0091491 | 2.419e-05
8449120 | 2015-11-27 13:43 | 2015-11-27 20:10 | 387.15 | 9 | 3484.35 | 387.15 | 384.15 | 0.010536 | 3457.35 | 0.010454 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8452491, P01608 | Trees over line at Pole P01608. Fuses H137 opened and tagged for repairs. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.010454 | 2.7214e-05 | 2016 | 2015-11-27 | C | 9 | 0.010454 | 2.7214e-05
8452446 | 2015-12-14 12:34 | 2015-12-14 14:26 | 112 | 2 | 224 | 112 | 109 | 0.00067732 | 218 | 0.00065918 | 6.0475e-06 | NAPA ID:15056 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 998 | We need to open and tag 11kv fuses 998 so we can replace 11kv fuses live line. Works location: Lepper Rd, Inglewood. WO 30013476 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-14 | b | 0.00032959 | 3.024e-06 | 2016 | 2015-12-14 | B | 2 | 0.00065918 | 6.0475e-06
8452531 | 2015-12-14 09:15 | 2015-12-14 10:50 | 95 | 5 | 475 | 95 | 92 | 0.0014363 | 460 | 0.0013909 | 1.5119e-05 | NAPA ID:15058 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1520 | We are replacing 11kV DDOs live line so we are just opening 11kV fuses 1520 and doing the rest live line. Works location: Upland Rd, New Plymouth. WO 30013476 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-14 | b | 0.00069547 | 7.559e-06 | 2016 | 2015-12-14 | B | 5 | 0.0013909 | 1.5119e-05
8452536 | 2015-11-27 16:43 | 2015-11-27 17:35 | 52 | 3 | 156 | 52 | 49 | 0.00047171 | 147 | 0.00044449 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L4095 | Replace 1m conductor, 1 x sleeve | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-11-27 | c | 0.00044449 | 9.071e-06 | 2016 | 2015-11-27 | C | 3 | 0.00044449 | 9.0713e-06
8452555 | 2015-11-30 10:00 | 2015-11-30 12:25 | 145 | 1 | 145 | 145 | 142 | 0.00043845 | 142 | 0.00042937 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704593 | CR as per Shan. Warren was onsite, needed to leave to do some switching for control ] HV fuse has been replaced on the road by Warren. It is holding fine - Tony is now onsite and believes a line patrol is needed OH/UG. There are also some big trees near | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-11-30 | c | 0.00042937 | 3.024e-06 | 2016 | 2015-11-30 | C | 1 | 0.00042937 | 3.0238e-06
8453957 | 2015-11-27 15:40 | 2015-11-27 15:41 | 1.2333 | 1832 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0055395 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Auto reclose due to loading issues with back feed of pongakawa sub through regulators 9176/2. regulators 9176 on tap 16, selected to manual, closed CB 37 at Pongakawa CB 4 tripped. Sectionalizer was opened CB 4 closed. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-11-27 | c | 0 | 0.0055395 | 2016 | 2015-11-27 | C | 1832 | 0 | 0.0055395
8456038 | 2015-11-27 19:05 | 2015-11-27 19:25 | 20.1333 | 181 | 3637.8167 | 20.0984 | 17.0984 | 0.011 | 3094.8167 | 0.009358 | 0.0005473 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C885 | CB C885 Tripped E/F A/B Phase O/C. Possible Bird Strike. | F1,F2,F3 | PAHAUTEA 33KV TIE | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2015-11-27 | c | 0.009358 | 0.0005473 | 2016 | 2015-11-27 | C | 181 | 0.009358 | 0.0005473
8456444 | 2015-11-27 21:44 | 2015-11-27 23:33 | 108.9 | 273 | 29729.7 | 108.9 | 105.9 | 0.089895 | 28910.7 | 0.087419 | 0.00082549 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 202316 | AON CB1 tripped L/O ( no flags ) . Feeder patrolled ( on foot ) & branch found on line at pole 202316 ( wind blown ) heavy rain at time of outage. Branch removed with hotstick, CB1 close all service restored. Materials Nil | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2015-11-27 | c | 0.087419 | 0.00082549 | 2016 | 2015-11-27 | C | 273 | 0.087419 | 0.00082549
8457598 | 2015-11-28 06:15 | 2015-11-28 07:58 | 102.65 | 59 | 6056.35 | 102.65 | 99.65 | 0.018313 | 5879.35 | 0.017778 | 0.0001784 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5555 | 2 Fuses found Blown at Fuses 5555 - Used 2x 15 amp fuses | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-11-28 | c | 0.017778 | 0.0001784 | 2016 | 2015-11-28 | C | 59 | 0.017778 | 0.0001784
8459218 | 2015-11-28 11:15 | 2015-11-28 12:25 | 70 | 27 | 1890 | 70 | 67 | 0.0057149 | 1809 | 0.00547 | 8.1642e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1588 | Blown Jumper found at Transformer X1588. Isolated at Fuses 595. Used 1 mtr conductor and 2x sleeves | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-11-28 | c | 0.00547 | 8.1642e-05 | 2016 | 2015-11-28 | C | 27 | 0.00547 | 8.1642e-05
8459266 | 2015-12-21 10:04 | 2015-12-21 11:52 | 107.75 | 22 | 2370.5 | 107.75 | 104.75 | 0.0071678 | 2304.5 | 0.0069683 | 6.6523e-05 | NAPA ID:14395 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7893 | Replace defected 2 sets of 11kV strain arms. Works location: Waiawhiti Rd. WO 30015784 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-21 | b | 0.0034841 | 3.3261e-05 | 2016 | 2015-12-21 | B | 22 | 0.0069683 | 6.6523e-05
8459690 | 2015-11-28 17:13 | 2015-11-28 18:18 | 65 | 603 | 39195 | 65 | 62 | 0.11852 | 37386 | 0.11305 | 0.0018233 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/381 | Please check this job as well as possibly related to OMS: 8459720 also 8459776. Broken DDO found at Transformer T1/381. Isolated at ABS L39 - DDO unit replaced - Used 1 x DDO, 1 x 20 amp fuse & 1 x LV carrier | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-28 | c | 0.11305 | 0.0018233 | 2016 | 2015-11-28 | C | 603 | 0.11305 | 0.0018233
8461009 | 2015-11-28 17:15 | 2015-11-28 22:20 | 304.85 | 444 | 15821.9667 | 35.6351 | 32.6351 | 0.047842 | 14489.9667 | 0.043814 | 0.0013425 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9275 | Line patrolled & sectionalized, Line isolated at fuses SD3-084 for testing of cables to transformers. No fault found. feeder successfully restored. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-11-28 | c | 0.043814 | 0.0013426 | 2016 | 2015-11-28 | C | 444 | 0.043814 | 0.0013425
8466128 | 2015-11-29 10:20 | 2015-11-29 10:36 | 16.1167 | 87 | 1402.15 | 16.1167 | 13.1167 | 0.0042398 | 1141.15 | 0.0034506 | 0.00026307 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 838395 | Repaired broken connection where Transformer T46 taps off from main line. Repaired using 1x conductor joint | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-11-29 | c | 0.0034506 | 0.00026307 | 2016 | 2015-11-29 | C | 87 | 0.0034506 | 0.00026307
8466750 | 2015-11-29 14:28 | 2015-11-29 19:22 | 294.5167 | 46 | 12760.3833 | 277.3996 | 274.3996 | 0.038584 | 12622.3833 | 0.038167 | 0.00013909 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P02436 | Lines down after planned burn off got out of hand and burnt lines down. NDR #19222. Materials used: 20mtrs of squirrel conductor & 6x conductor joints. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-29 | c | 0.038167 | 0.00013909 | 2016 | 2015-11-29 | C | 46 | 0.038167 | 0.00013909
8467041 | 2015-11-29 17:11 | 2015-11-29 17:30 | 18.4833 | 65 | 1201.4167 | 18.4833 | 15.4833 | 0.0036328 | 1006.4167 | 0.0030432 | 0.00019654 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Non Scadarised Recloser M79 found tripped at 17:13hrs. This was due to a fire burning lines down in Reu Reu Rd (See OMS 8466750). Relivened ok once Fuses M71 had been opened to isolate fault. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-11-29 | c | 0.0030432 | 0.00019654 | 2016 | 2015-11-29 | C | 65 | 0.0030432 | 0.00019654
8468988 | 2015-11-30 06:31 | 2015-11-30 07:25 | 54.2833 | 69 | 3745.55 | 54.2833 | 51.2833 | 0.011326 | 3538.55 | 0.0107 | 0.00020864 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7752 | Reload Reliven 2 x 10 A Fuses Possibly house moving | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-11-30 | c | 0.0107 | 0.00020864 | 2016 | 2015-11-30 | C | 69 | 0.0107 | 0.00020864
8470510 | 2015-12-02 09:00 | 2015-12-02 13:50 | 290 | 10 | 2900 | 290 | 287 | 0.0087689 | 2870 | 0.0086782 | 3.0238e-05 | NAPA ID:12622 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T692 | Replace Transformer T692 and Pole. Work Location: Homebush Road, Masterton. Work Order 30013778. | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-02 | b | 0.0043391 | 1.5119e-05 | 2016 | 2015-12-02 | B | 10 | 0.0086782 | 3.0238e-05
8470944 | 2015-12-16 09:00 | 2015-12-16 14:26 | 326 | 4 | 1304 | 326 | 323 | 0.003943 | 1292 | 0.0039067 | 1.2095e-05 | NAPA ID:14242 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 210640 | Replace Pole 210640 and Lower 11kV conductors on pole 210641. Works location: Munro Rd. WO 30015899 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.0019533 | 6.048e-06 | 2016 | 2015-12-16 | B | 4 | 0.0039067 | 1.2095e-05
8471771 | 2015-11-30 10:00 | 2015-11-30 13:30 | 210 | 2 | 420 | 210 | 207 | 0.00127 | 414 | 0.0012518 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 212095 | Josh Reid required an isolation for safety to replace LV cross arms. Cross arms replaced, relivend OK | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-11-30 | c | 0.0012518 | 6.048e-06 | 2016 | 2015-11-30 | C | 2 | 0.0012518 | 6.0475e-06
8471975 | 2015-11-30 15:24 | 2015-11-30 15:47 | 22.5167 | 416 | 8867.25 | 21.3155 | 18.3155 | 0.026812 | 7619.25 | 0.023039 | 0.0012579 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Motukawa Sub | 33kV CB2742 Tripped / 6.6kV H21 & H11 Tripped. E/F O/C NTime. L/O. Relivened OK. Alot of magpies around at the moment. Suspect bird strike. | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2015-11-30 | c | 0.023039 | 0.0012579 | 2016 | 2015-11-30 | C | 416 | 0.023039 | 0.0012579
8474804 | 2015-11-30 17:35 | 2015-11-30 21:51 | 256.2667 | 1100 | 67866.9833 | 61.6973 | 58.6973 | 0.20521 | 64566.9833 | 0.19524 | 0.0033261 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13143 | at 17:35, Tairua Sub, CB 5 Tairua North Feeder, Recloser 9170 Tripped, E/F, L/O. at 17:37 Whitianga Sub, CB 4 Coroglen Feeder, Recloser 9512, Tripped, No Flags, L/O. CB 4 Flagged with E/F. Faultmen dispatched & investigation began. Both feeder sectionalis | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-11-30 | c | 0.19524 | 0.0033261 | 2016 | 2015-11-30 | C | 1100 | 0.19524 | 0.0033261
8479092 | 2015-12-01 04:35 | 2015-12-01 07:18 | 163.5 | 396 | 30373.4 | 76.7005 | 73.7005 | 0.091842 | 29185.4 | 0.08825 | 0.0011974 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40280 | Recloser K13 tripped on E/F flags line was patrolled and sectionalised, received a call from a farmer of a flash on the line faultman found a broken insulator on pole P40280, line was isolated at ABS's E22 & E23 to replace the insulator. 1 x 11KV insulato | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-12-01 | c | 0.08825 | 0.0011974 | 2016 | 2015-12-01 | C | 396 | 0.08825 | 0.0011974
8480239 | 2015-12-01 07:33 | 2015-12-01 09:00 | 87.35 | 1 | 87.35 | 87.35 | 84.35 | 0.00026413 | 84.35 | 0.00025505 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1342 | Reload reliven 3 x 2A Fuses Unknown Cause. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-01 | c | 0.00025505 | 3.024e-06 | 2016 | 2015-12-01 | C | 1 | 0.00025505 | 3.0238e-06
8480941 | 2015-12-16 09:21 | 2015-12-16 16:27 | 425.55 | 91 | 33150.7167 | 364.2936 | 361.2936 | 0.10024 | 32877.7167 | 0.099414 | 0.00027516 | NAPA ID:13070 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC419 | Awaiti pole renewal - Stage 1. Works location: Kaikahu Rd, Kerepehi. WO 30002579 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-16 | b | 0.049707 | 0.00013758 | 2016 | 2015-12-16 | B | 91 | 0.099414 | 0.00027516
8481077 | 2015-12-17 09:16 | 2015-12-17 17:03 | 467.55 | 38 | 17688.3 | 465.4816 | 462.4816 | 0.053485 | 17574.3 | 0.05314 | 0.0001149 | NAPA ID:14200 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC422 | Awaiti pole renewal - stage 2. Works location: Wani Rd. WO 30002579 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-17 | b | 0.02657 | 5.7451e-05 | 2016 | 2015-12-17 | B | 38 | 0.05314 | 0.0001149
8481537 | 2015-12-01 10:05 | 2015-12-01 13:30 | 205 | 167 | 16756.0833 | 100.3358 | 97.3358 | 0.050666 | 16255.0833 | 0.049151 | 0.00050497 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6286 | Recloser 6286 Trip. E/F. L/O. Feeder sectionalised but no fault found. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-01 | c | 0.049151 | 0.00050497 | 2016 | 2015-12-01 | C | 167 | 0.049151 | 0.00050497
8482593 | 2015-12-15 10:00 | 2015-12-15 13:19 | 199 | 62 | 12338 | 199 | 196 | 0.037307 | 12152 | 0.036745 | 0.00018747 | NAPA ID:15107 TP_HUIRANGI GXP > TP_HUIRANGI > BELL BLOCK-HUIRANGI 33KV | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV aBS 419 | Destringing of 33kV Bell Block-Huirangi circuit above 11kV. Works location: Corbett Rd. WO 30011788 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-15 | b | 0.018372 | 9.3737e-05 | 2016 | 2015-12-15 | B | 62 | 0.036745 | 0.00018747
8484190 | 2015-12-03 11:30 | 2015-12-03 14:00 | 150 | 3 | 450 | 150 | 147 | 0.0013607 | 441 | 0.0013335 | 9.0713e-06 | NAPA ID:14148 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-229 | Upgrade transformer to a 30/11/1 pole mount | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.00066674 | 4.536e-06 | 2016 | 2015-12-03 | B | 3 | 0.0013335 | 9.0713e-06
8484768 | 2015-12-01 17:05 | 2015-12-01 18:10 | 65 | 1 | 65 | 65 | 62 | 0.00019654 | 62 | 0.00018747 | 3.0238e-06 |  | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805387 | Faultman found a broken insulator on pole 805387, line was isolated at Fuses 2756 to replace the insulator. 1 X 22KV insulator replaced. 2 X binders used. | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-12-01 | c | 0.00018747 | 3.024e-06 | 2016 | 2015-12-01 | C | 1 | 0.00018747 | 3.0238e-06
8484779 | 2015-12-09 09:47 | 2015-12-09 12:18 | 151 | 10 | 1510 | 151 | 148 | 0.0045659 | 1480 | 0.0044752 | 3.0238e-05 | NAPA ID:15148 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CAMPBELL RD | To replace 11kV Arms, 400V Arms & Install 400V Fuse disconnector | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-09 | b | 0.0022376 | 1.5119e-05 | 2016 | 2015-12-09 | B | 10 | 0.0044752 | 3.0238e-05
8485164 | 2015-12-01 18:25 | 2015-12-01 18:41 | 16 | 57 | 912 | 16 | 13 | 0.0027577 | 741 | 0.0022406 | 0.00017235 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Crn Devon Road and Raleigh Street, Waitara - Pole 369656 | Streetlight has been hit by car and if it falls over it will take out 11kV line - Have advised hub and control. 17:57 - Job was manually dispatched to SMC as OMS was down. Emergency isolation between ABS 6505 and ABS 443 for New Plymouth Electrical to saf | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-01 | c | 0.0022406 | 0.00017235 | 2016 | 2015-12-01 | C | 57 | 0.0022406 | 0.00017235
8486448 | 2015-12-02 09:32 | 2015-12-02 10:57 | 84.9 | 19 | 1613.1 | 84.9 | 81.9 | 0.0048776 | 1556.1 | 0.0047053 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1322 | Please check OMS: 8486671 as part power same road possibly related. Replace 2 x 20A fuses | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-12-02 | c | 0.0047053 | 5.7451e-05 | 2016 | 2015-12-02 | C | 19 | 0.0047053 | 5.7451e-05
8486696 | 2015-12-02 09:52 | 2015-12-02 12:16 | 144.3333 | 1 | 144.3333 | 144.3333 | 141.3333 | 0.00043643 | 141.3333 | 0.00042736 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1518 | 2 X 3A Fuses Replaced | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-12-02 | c | 0.00042736 | 3.024e-06 | 2016 | 2015-12-02 | C | 1 | 0.00042736 | 3.0238e-06
8487207 | 2015-12-02 11:10 | 2015-12-02 14:19 | 189.1667 | 76 | 7635.6667 | 100.4693 | 97.4693 | 0.023088 | 7407.6667 | 0.022399 | 0.00022981 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 365120 | Recloser 7417/2 tripped on B & C phase O/C & E/F flags,received a call from Harvard Logging that are working on CAC 30969 that they have dropped a tree through the lines, line was isolated at Fuses 7904.. to repair the line only single phase number 8 wire | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-12-02 | c | 0.022399 | 0.00022981 | 2016 | 2015-12-02 | C | 76 | 0.022399 | 0.00022981
8487695 | 2015-12-21 10:57 | 2015-12-21 16:31 | 333.9333 | 10 | 3339.3333 | 333.9333 | 330.9333 | 0.010097 | 3309.3333 | 0.010007 | 3.0238e-05 | NAPA ID:15039 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 852200 | Move 11KV single phase line to opposite side of Bucks Rd. Line damaged by trees. Works location: Bucks Rd, Featherston. WO 30017721. Job ran over by 1.5 hours only explanation from Poltech was that it took longer that they thought | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-12-21 | b | 0.0050033 | 1.5119e-05 | 2016 | 2015-12-21 | B | 10 | 0.010007 | 3.0238e-05
8487721 | 2015-12-18 09:15 | 2015-12-18 16:06 | 410.75 | 36 | 14787 | 410.75 | 407.75 | 0.044712 | 14679 | 0.044386 | 0.00010886 | NAPA ID:14229 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC346 | Awaiti pole renewal - stage 3. Works location: Wani Rd, Awaiti Canal Rd. WO 30002579 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-18 | b | 0.022193 | 5.4428e-05 | 2016 | 2015-12-18 | B | 36 | 0.044386 | 0.00010886
8487926 | 2015-12-18 09:15 | 2015-12-18 12:18 | 183 | 2 | 366 | 183 | 180 | 0.0011067 | 360 | 0.0010886 | 6.0475e-06 | NAPA ID:13901 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 209821 | Replace 33kV Crossarm H Structure 209821/209822. Works location: I'Anson Rd. WO 30015899 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-18 | b | 0.00054428 | 3.024e-06 | 2016 | 2015-12-18 | B | 2 | 0.0010886 | 6.0475e-06
8488181 | 2015-12-21 12:43 | 2015-12-21 14:01 | 78 | 5 | 390 | 78 | 75 | 0.0011793 | 375 | 0.0011339 | 1.5119e-05 | NAPA ID:14004 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4842 | To replace the 11kV Fuses & install a 3 phase 400V Fuse disconnector. Works location: Campbell Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-21 | b | 0.00056695 | 7.559e-06 | 2016 | 2015-12-21 | B | 5 | 0.0011339 | 1.5119e-05
8488916 | 2015-12-21 09:22 | 2015-12-21 10:57 | 95 | 5 | 475 | 95 | 92 | 0.0014363 | 460 | 0.0013909 | 1.5119e-05 | NAPA ID:14003 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3130 | To replace the 11kV Fuse arm.To install a 400V Fuse Disconector. Works location: Campbell Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-21 | b | 0.00069547 | 7.559e-06 | 2016 | 2015-12-21 | B | 5 | 0.0013909 | 1.5119e-05
8489117 | 2015-12-03 09:30 | 2015-12-03 13:58 | 268 | 9 | 2412 | 268 | 265 | 0.0072933 | 2385 | 0.0072117 | 2.7214e-05 | NAPA ID:15250 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M1917 | Replace pole M1917 with new 2 pole structure ready for new regulator site. Works location: Whites Rd, Putaruru. WO 30002469 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-03 | b | 0.0036058 | 1.3607e-05 | 2016 | 2015-12-03 | B | 9 | 0.0072117 | 2.7214e-05
8512819 | 2015-12-21 09:03 | 2015-12-21 17:04 | 480.65 | 82 | 39413.3 | 480.65 | 477.65 | 0.11918 | 39167.3 | 0.11843 | 0.00024795 | NAPA ID:14230 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 409 | Awaiti pole renewal - stage 4. Works location: Wani Rd. WO 30002579. Shutdown ran 2 hrs over time due to on site & switching issues | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-21 | b | 0.059216 | 0.00012397 | 2016 | 2015-12-21 | B | 82 | 0.11843 | 0.00024795
8515058 | 2015-12-06 14:23 | 2015-12-07 00:30 | 606.5167 | 1 | 606.5167 | 606.5167 | 603.5167 | 0.001834 | 603.5167 | 0.0018249 | 3.0238e-06 | NAPA ID:15264 TP_WAIHOU GXP > FARMER ROAD SUB > WOODS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Farmer Rd Stage 3 - Note This outage has been advertised under NAPA 14405. Upgrading FMR CB2 including new panel fronts, protection relay and arc flash. Connect new relay to 3530 and disconnect CB2 from old RTU. Install Arc Flash Fibre in 11kV Bus Compart | F1 | WOODS RD | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-12-06 | b | 0.00091245 | 1.512e-06 | 2016 | 2015-12-06 | B | 1 | 0.0018249 | 3.0238e-06
8515479 | 2015-12-03 09:03 | 2015-12-03 09:15 | 12.25 | 1643 | 9288.5667 | 5.6534 | 2.6534 | 0.028086 | 4359.5667 | 0.013182 | 0.004968 |  | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | CB8 | Tripping on Sanson CB8 while carrying out Switching on NAPA 14326. (No flaggings). Switching involved backfeeding part of CB6 onto CB8 with ABS L96 being closed and ABS L7 opened. As ABS L7 was being open, Sanson CB8 Tripped also causing partial loss on C | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-03 | c | 0.013182 | 0.004968 | 2016 | 2015-12-03 | C | 1643 | 0.013182 | 0.004968
8518707 | 2015-12-22 08:30 | 2015-12-22 15:38 | 427.4 | 67 | 28635.8 | 427.4 | 424.4 | 0.086588 | 28434.8 | 0.08598 | 0.00020259 | NAPA ID:14543 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 787310 | change xarms and erect poles from pole 787310 to pole 787407. Works location: Otuarie Rd, Taihape. WO 30006838 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-22 | b | 0.04299 | 0.0001013 | 2016 | 2015-12-22 | B | 67 | 0.08598 | 0.00020259
8518879 | 2015-12-10 11:07 | 2015-12-10 13:20 | 133 | 1 | 133 | 133 | 130 | 0.00040216 | 130 | 0.00039309 | 3.0238e-06 | NAPA ID:15085 TP_HAWERA GXP > MANAIA SUB > AUROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8518879 | Remove 1 span to allow for TX removal | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.00019654 | 1.512e-06 | 2016 | 2015-12-10 | B | 1 | 0.00039309 | 3.0238e-06
8518979 | 2015-12-03 11:20 | 2015-12-03 13:50 | 150 | 15 | 2250 | 150 | 147 | 0.0068035 | 2205 | 0.0066674 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 360416 | Outage required from Fuses 7889 due to a broken 11kV conductor. (Had broken off at insulator, high winds). Materials include 2 sleeves, 15m Al Conductor, and a binder. Relivened OK. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-03 | c | 0.0066674 | 4.5356e-05 | 2016 | 2015-12-03 | C | 15 | 0.0066674 | 4.5356e-05
8519573 | 2015-12-22 10:06 | 2015-12-22 13:59 | 233 | 10 | 732 | 73.2 | 70.2 | 0.0022134 | 702 | 0.0021227 | 3.0238e-05 | NAPA ID:14006 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1582 | To replace the 11kV Fuses TC1582, Install a 3 phase 400V Fuse Disconnector. Works location: Campbell Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-22 | b | 0.0010613 | 1.5119e-05 | 2016 | 2015-12-22 | B | 10 | 0.0021227 | 3.0238e-05
8519929 | 2015-12-22 09:51 | 2015-12-22 14:09 | 258 | 91 | 23478 | 258 | 255 | 0.070992 | 23205 | 0.070166 | 0.00027516 | NAPA ID:15253 TP_OPUNAKE GXP > NGARIKI SUB > SOUTH RD NGARIKI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 712689 | to change pole 712689 for new 11kv pole and new 50kva 5645E on new pole. Works location: Kina Rd. WO 30017575 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-12-22 | b | 0.035083 | 0.00013758 | 2016 | 2015-12-22 | B | 91 | 0.070166 | 0.00027516
8520992 | 2015-12-18 08:45 | 2015-12-18 16:00 | 434.9 | 19 | 8263.1 | 434.9 | 431.9 | 0.024986 | 8206.1 | 0.024813 | 5.7451e-05 | NAPA ID:13467 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829362 | Replace poles between 829362 and 829347. Works location: Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-18 | b | 0.012407 | 2.8726e-05 | 2016 | 2015-12-18 | B | 19 | 0.024813 | 5.7451e-05
8521011 | 2015-12-22 08:52 | 2015-12-22 17:07 | 494.5333 | 19 | 9396.1333 | 494.5333 | 491.5333 | 0.028412 | 9339.1333 | 0.028239 | 5.7451e-05 | NAPA ID:13464 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 829362 | Replace poles between 829362 and 829387. Works location: Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-22 | b | 0.01412 | 2.8726e-05 | 2016 | 2015-12-22 | B | 19 | 0.028239 | 5.7451e-05
8521698 | 2015-12-03 18:08 | 2015-12-03 19:20 | 71.9167 | 1 | 71.9167 | 71.9167 | 68.9167 | 0.00021746 | 68.9167 | 0.00020839 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2955T | 100kva pole mount TX, small drip from radiator of TX, all safe for now, will need to replace transformer. have amber defected transformer. Entered into Safety Manager for leaking oil under # 524745 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-03 | c | 0.00020839 | 3.024e-06 | 2016 | 2015-12-03 | C | 1 | 0.00020839 | 3.0238e-06
8522007 | 2015-12-04 02:40 | 2015-12-04 04:17 | 97.1 | 1 | 97.1 | 97.1 | 94.1 | 0.00029361 | 94.1 | 0.00028454 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | Found Sw/Gear 9657/2 tripped. Faultman not familiar with equipment had to get someone out to show how to operate. closed 9657/2 | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-12-04 | c | 0.00028454 | 3.024e-06 | 2016 | 2015-12-04 | C | 1 | 0.00028454 | 3.0238e-06
8524906 | 2015-12-11 10:18 | 2015-12-11 15:28 | 310 | 58 | 17980 | 310 | 307 | 0.054367 | 17806 | 0.053841 | 0.00017538 | NAPA ID:15345 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV LI716 | Reconductor Hv lines Ball rd Between poles 731015 and 731073. Works location: Ball Rd, Alton. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-11 | b | 0.026921 | 8.7689e-05 | 2016 | 2015-12-11 | B | 58 | 0.053841 | 0.00017538
8525474 | 2015-12-17 09:45 | 2015-12-17 14:06 | 261 | 13 | 3393 | 261 | 258 | 0.01026 | 3354 | 0.010142 | 3.9309e-05 | NAPA ID:15340 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS206, Pole 749195 | Replace Abs 206 & Xarms @ Pole 749195. 331 Smart Road, Hillsborough, New Plymouth. W/O 30013271 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-17 | b | 0.0050708 | 1.9654e-05 | 2016 | 2015-12-17 | B | 13 | 0.010142 | 3.9309e-05
8525879 | 2015-12-04 15:44 | 2015-12-04 17:38 | 114.1167 | 167 | 16988.6333 | 101.7283 | 98.7283 | 0.05137 | 16487.6333 | 0.049855 | 0.00050497 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6286 | Recloser 6286 tripped on E/F flags, line was patrolled and sectionalised and faultman found Recloser 6274 had a malfunction alarm up on it and the batteries are also dead, suspect recloser is faulty will need a Tech to inspect. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-04 | c | 0.049855 | 0.00050497 | 2016 | 2015-12-04 | C | 167 | 0.049855 | 0.00050497
8530238 | 2015-12-05 11:55 | 2015-12-05 15:50 | 235.4667 | 422 | 7686 | 18.2133 | 15.2133 | 0.023241 | 6420 | 0.019413 | 0.001276 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793164 | Bob from Fire Comms advise the line is down at 117 Tauri Road and the grass fire has now got bigger and require power shutdown before fire can be put out. 12.33pm - advise Bob of 15min eta. Isolated at ABS 4026 Line Repaired at Pole 793164. Used 1 x 30 am | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.019413 | 0.001276 | 2016 | 2015-12-05 | C | 422 | 0.019413 | 0.001276
8530819 | 2015-12-05 13:09 | 2015-12-05 14:11 | 61.95 | 116 | 5906.8167 | 50.9208 | 47.9208 | 0.017861 | 5558.8167 | 0.016809 | 0.00035076 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB C936 Tripped during NAPA 13940 A, C Ph O/C. Crew contacted Line break had been Closed, LLP 13940 Cancelled. ABS S92 Opened and CB tripped again on closing , Branch found on lines Near T1612 - Cleared using Hot Sticks. CB Tripped again second Brach foun | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.016809 | 0.00035076 | 2016 | 2015-12-05 | C | 116 | 0.016809 | 0.00035076
8530978 | 2015-12-05 13:25 | 2015-12-05 14:00 | 34.9667 | 15 | 524.5 | 34.9667 | 31.9667 | 0.001586 | 479.5 | 0.0014499 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | Fuse found Blown at fuses 2829. Used 2 x 15 amp fuses. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.0014499 | 4.5356e-05 | 2016 | 2015-12-05 | C | 15 | 0.0014499 | 4.5356e-05
8531172 | 2015-12-05 13:58 | 2015-12-05 18:25 | 267.3667 | 465 | 27974.0833 | 60.1593 | 57.1593 | 0.084587 | 26579.0833 | 0.080369 | 0.001406 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/499 | CB 5 Tripped E/F. While Sectionlising found faulty Cable between Sw/Gear 10091/4 and Sw/gear 10122/2. Cable tested and temp line brake made at Transformer T6/499 Cable DNO'd (DNO 151204) | F2 | FAIRS RD | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.080369 | 0.001406 | 2016 | 2015-12-05 | C | 465 | 0.080369 | 0.001406
8531754 | 2015-12-05 16:02 | 2015-12-05 16:56 | 54 | 12 | 648 | 54 | 51 | 0.0019594 | 612 | 0.0018505 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P26313 | big pine branch on 2 phases of the 11kv line. this has blown 2 x links and feeding 3 x transformers. FM requested a 2R but checked with Control and they advise another 1R should be fine, not a 2R. Please sort at invoicing level. FM will work through contr | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.0018505 | 3.6285e-05 | 2016 | 2015-12-05 | C | 12 | 0.0018505 | 3.6285e-05
8533387 | 2015-12-05 19:00 | 2015-12-05 19:47 | 46.9833 | 28 | 1315.5333 | 46.9833 | 43.9833 | 0.0039779 | 1231.5333 | 0.0037239 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | V16 | Tripping on 2 HT fuses V16. Reclosed OK - 10A. High winds. (Line Clash). | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-05 | c | 0.0037239 | 8.4665e-05 | 2016 | 2015-12-05 | C | 28 | 0.0037239 | 8.4665e-05
8534128 | 2015-12-06 08:53 | 2015-12-06 12:27 | 213.6833 | 132 | 22698.6333 | 171.9593 | 168.9593 | 0.068635 | 22302.6333 | 0.067438 | 0.00039914 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | CB 4 Tripped E/F L/O - Feeder Sectionlised with no Fault Found | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-06 | c | 0.067438 | 0.00039914 | 2016 | 2015-12-06 | C | 132 | 0.067438 | 0.00039914
8534771 | 2015-12-06 11:45 | 2015-12-06 16:24 | 279.2333 | 56 | 2892.1667 | 51.6458 | 48.6458 | 0.0087452 | 2724.1667 | 0.0082372 | 0.00016933 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IP18 | at 11:45, Inghams Sub, CB 2, Tripped, E/F, B Ph O/C, L/O. Tripping occured during Planned Switching on NAPA 15264. ABS IP18 insulators failed when opening ABS. Decision was made to cut jumpers away from ABS to allow planned work to go ahead. Lines Isolate | F1 | WAIHEKAU RD | WAIHOU | Valley | INGHAMS SUB | Eastern Electricity | POWERCO | 2015-12-06 | c | 0.0082372 | 0.00016933 | 2016 | 2015-12-06 | C | 56 | 0.0082372 | 0.00016933
8534914 | 2015-12-06 13:15 | 2015-12-06 15:08 | 112.45 | 132 | 8936.4 | 67.7 | 64.7 | 0.027022 | 8540.4 | 0.025824 | 0.00039914 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | CB 4 Tripped E/F - Line Patrolled with no Fault Found - feeder split due to repeated trips | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-06 | c | 0.025824 | 0.00039914 | 2016 | 2015-12-06 | C | 132 | 0.025824 | 0.00039914
8536533 | 2015-12-06 17:56 | 2015-12-06 19:16 | 80.4333 | 25 | 2010.8333 | 80.4333 | 77.4333 | 0.0060803 | 1935.8333 | 0.0058535 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 8194 | Tripping on 2 HT fuses at 8194. Area patrolled along Alfred Rd with nothing found. Fuses Reloaded OK. (25A Rating). - Suspect Bird strike. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-06 | c | 0.0058535 | 7.5594e-05 | 2016 | 2015-12-06 | C | 25 | 0.0058535 | 7.5594e-05
8537302 | 2015-12-06 22:36 | 2015-12-07 01:03 | 147.2167 | 12 | 1766.6 | 147.2167 | 144.2167 | 0.0053418 | 1730.6 | 0.0052329 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-006 | 2 x 10 Amp fuses blown at SD5-006. Suspect line clash. Line patrolled, reloaded Relivened. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-12-06 | c | 0.0052329 | 3.6285e-05 | 2016 | 2015-12-06 | C | 12 | 0.0052329 | 3.6285e-05
8537688 | 2015-12-07 06:32 | 2015-12-07 07:51 | 78.0833 | 1 | 78.0833 | 78.0833 | 75.0833 | 0.00023611 | 75.0833 | 0.00022703 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/506 | Broken Jumper T1/506 Isolated at fuses L80. Materials: 1 line tap. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-07 | c | 0.00022703 | 3.024e-06 | 2016 | 2015-12-07 | C | 1 | 0.00022703 | 3.0238e-06
8538942 | 2015-12-21 10:00 | 2015-12-21 10:35 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 | NAPA ID:15383 TP_HUIRANGI GXP > WAITARA EAST SUB > PRINCESS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 764199 | To repair broken strand of 16mm wire 11kV. 55 Turangi Rd, Waitara. W/O 30017256. | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-21 | b | 0.00019352 | 6.048e-06 | 2016 | 2015-12-21 | B | 4 | 0.00038704 | 1.2095e-05
8539084 | 2015-12-21 08:46 | 2015-12-21 11:14 | 148.1833 | 429 | 63570.65 | 148.1833 | 145.1833 | 0.19222 | 62283.65 | 0.18833 | 0.0012972 | NAPA ID:14294 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 838610, 838617 | Repair broken conductor (down to steel core). Treescape also to cut trees at pole 838615 working earths to be applied at poles 838610 and 838617. Access Permit all parties inclusive Treescape team to work under AP. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-21 | b | 0.094165 | 0.0006486 | 2016 | 2015-12-21 | B | 429 | 0.18833 | 0.0012972
8539354 | 2015-12-07 11:28 | 2015-12-07 15:46 | 258 | 435 | 32554.8167 | 74.8387 | 71.8387 | 0.098438 | 31249.8167 | 0.094492 | 0.0013153 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P12646 | CB 6 Trip, HLT Trip-A Phase. Tree Crew were working on feeder at the time of tripping, so they were contacted and stood down until fault located & feeder restored. Sectionalised & patrolled with fault being found on CB 10 (Konini Feeder) which was fed fro | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-12-07 | c | 0.094492 | 0.0013153 | 2016 | 2015-12-07 | C | 435 | 0.094492 | 0.0013153
8541623 | 2015-12-07 13:09 | 2015-12-07 22:17 | 547.9833 | 759 | 134676.95 | 177.44 | 174.44 | 0.40723 | 132399.95 | 0.40035 | 0.002295 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 202337 | Breaks at poles 262472 & 202334. Back feed from OTE CB 5 via ABS IP597. Materials Pole, Double termination arm, Double LV pin arm & insulators. 3x200amp fuses cable, sleeves, heat shrinks. NDR 51705. Police event # P023455325. Fire event # F1973790. Car | F3 | BELLEVUE RD | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2015-12-07 | c | 0.40035 | 0.002295 | 2016 | 2015-12-07 | C | 759 | 0.40035 | 0.002295
8544018 | 2015-12-07 14:51 | 2015-12-07 16:15 | 84.5 | 15 | 1267.5 | 84.5 | 81.5 | 0.0038326 | 1222.5 | 0.0036965 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | Replaced 2x 15Amp HV Links. Cause unknown | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-07 | c | 0.0036965 | 4.5356e-05 | 2016 | 2015-12-07 | C | 15 | 0.0036965 | 4.5356e-05
8545126 | 2015-12-07 17:02 | 2015-12-07 18:49 | 107.1 | 511 | 26702.5 | 52.2554 | 49.2554 | 0.080742 | 25169.5 | 0.076107 | 0.0015451 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 802670 | RS 4242 Tripped to L/O - Lines reported by public at Pole 802670 - Isolated at ABS 1090 and Links 4242/6 plus ABS 4242/1, back feed installed via VS 4661/2. Line repaired - used 2x sleeves & 7 mtrs of Conductor. NDR # 30359 | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-12-07 | c | 0.076107 | 0.0015451 | 2016 | 2015-12-07 | C | 511 | 0.076107 | 0.0015451
8545657 | 2015-12-07 16:21 | 2015-12-07 17:45 | 83.8333 | 22 | 1844.3333 | 83.8333 | 80.8333 | 0.0055768 | 1778.3333 | 0.0053773 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P41 | Replaced 2x 15Amp HV Links. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-12-07 | c | 0.0053773 | 6.6523e-05 | 2016 | 2015-12-07 | C | 22 | 0.0053773 | 6.6523e-05
8546620 | 2015-12-07 16:09 | 2015-12-07 17:20 | 71.4833 | 28 | 2001.5333 | 71.4833 | 68.4833 | 0.0060522 | 1917.5333 | 0.0057982 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1167 | James Kennerley Attended. Reloaded, Relivened 2x DDO's at Fuses FP1167. Unknown cause - was windy in the area at the time. James was originally assigned to Job 8544083 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-07 | c | 0.0057982 | 8.4665e-05 | 2016 | 2015-12-07 | C | 28 | 0.0057982 | 8.4665e-05
8550530 | 2015-12-08 10:42 | 2015-12-08 11:21 | 39 | 1 | 39 | 39 | 36 | 0.00011793 | 36 | 0.00010886 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TX T4018, Homewood | Frank Martin onsite, reporting 2 x hv fuses out at tx T 4018. Please assign Frank to this job. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-12-08 | c | 0.00010886 | 3.024e-06 | 2016 | 2015-12-08 | C | 1 | 0.00010886 | 3.0238e-06
8551978 | 2015-12-22 08:00 | 2015-12-22 10:00 | 120 | 1 | 120 | 120 | 117 | 0.00036285 | 117 | 0.00035378 | 3.0238e-06 | NAPA ID:15483 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | X3220 | Inatlling CT's on customer switch board no low voltage isolation. Hautapu Pines Taihape. CIW111111 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-22 | b | 0.00017689 | 1.512e-06 | 2016 | 2015-12-22 | B | 1 | 0.00035378 | 3.0238e-06
8552849 | 2015-12-08 21:35 | 2015-12-09 05:35 | 479.9667 | 284 | 29376.1333 | 103.4371 | 100.4371 | 0.088826 | 28524.1333 | 0.08625 | 0.00085875 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 716454 | CB 9 Tripped O/C L/O - Car V Pole at Pole 716454 called in by Public - Isolated at ABS's TA975 & TA991 - Pole replaced and all equipment - faultman to call in list later of equipment used later & NDR number. NDR # 22903 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-12-08 | c | 0.08625 | 0.00085875 | 2016 | 2015-12-08 | C | 284 | 0.08625 | 0.00085875
8554354 | 2015-12-09 05:10 | 2015-12-09 07:12 | 122.2667 | 6 | 733.6 | 122.2667 | 119.2667 | 0.0022182 | 715.6 | 0.0021638 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1067 | 2 x 10amp fuses bird strike | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-09 | c | 0.0021638 | 1.8143e-05 | 2016 | 2015-12-09 | C | 6 | 0.0021638 | 1.8143e-05
8556109 | 2015-12-16 08:31 | 2015-12-16 13:18 | 287.8833 | 40 | 11515.3333 | 287.8833 | 284.8833 | 0.03482 | 11395.3333 | 0.034457 | 0.00012095 | NAPA ID:14828 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Pole P00909 | Isolate and earth lines so Treescape can carry out tree works. Tiritea Road. W/O10152357 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-12-16 | b | 0.017228 | 6.0475e-05 | 2016 | 2015-12-16 | B | 40 | 0.034457 | 0.00012095
8556308 | 2015-12-22 09:21 | 2015-12-22 14:42 | 321.35 | 17 | 5462.95 | 321.35 | 318.35 | 0.016519 | 5411.95 | 0.016364 | 5.1404e-05 | NAPA ID:15524 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD3-021 | Replace 11kV fuse enclosure SD3-072 with a CFCF RMU. Gargan Rd, Tauranga. W/O30015152 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-22 | b | 0.0081822 | 2.5702e-05 | 2016 | 2015-12-22 | B | 17 | 0.016364 | 5.1404e-05
8560059 | 2015-12-09 12:24 | 2015-12-09 15:30 | 186.3667 | 1240 | 107879.5667 | 86.9997 | 83.9997 | 0.3262 | 104159.5667 | 0.31495 | 0.0037495 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Recloser K13 tripped E/F. This was related to planned switching to backfeed to Kimbolton sub. The tripping resulted in LOS to Kimbolton Sub. Patrolled but nothing immediately found. Further investigation found protection fault at K13. Protection setting h | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-12-09 | c | 0.31495 | 0.0037495 | 2016 | 2015-12-09 | C | 1240 | 0.31495 | 0.0037495
8567100 | 2015-12-09 13:54 | 2015-12-09 15:30 | 95.8333 | 1 | 95.8333 | 95.8333 | 92.8333 | 0.00028978 | 92.8333 | 0.00028071 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752780 | On Farm - Truck has wire wrapped around it, poss service line - person still in truck cab, driver can smell burning smell. Advised Jo at svs hub & control. Ross (in Truck). 0272207521. Repaired 2 X hV conductors used 4m conductor 8 sleeves 3 fuses. NDR No | F3 | MOTUROA 9 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-12-09 | c | 0.00028071 | 3.024e-06 | 2016 | 2015-12-09 | C | 1 | 0.00028071 | 3.0238e-06
8569028 | 2015-12-10 05:45 | 2015-12-10 07:10 | 84.6 | 6 | 507.6 | 84.6 | 81.6 | 0.0015349 | 489.6 | 0.0014804 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L21 | First Reload Reliven at Fuses L21 2 x 6A fuses. Found faulty stand-off insulator which was removed. Second reload reliven at transformer T1/302at Pole P08776. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-10 | c | 0.0014804 | 1.8143e-05 | 2016 | 2015-12-10 | C | 6 | 0.0014804 | 1.8143e-05
8569799 | 2015-12-10 09:01 | 2015-12-10 09:07 | 6 | 592 | 3552 | 6 | 3 | 0.01074 | 1776 | 0.0053702 | 0.0017901 |  | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | OAK CB 7 | Under Planned Switching 14652, CB 7 Tripped on PH A and PH B Fault when opening ABS 535, faultman found burnt and damaged insulators on ABS 535, ABS has been DNO'd to be replaced. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2015-12-10 | b | 0.0026851 | 0.00089503 | 2016 | 2015-12-10 | B | 592 | 0.0053702 | 0.0017901
8571673 | 2015-12-17 08:47 | 2015-12-17 14:19 | 332 | 39 | 12948 | 332 | 329 | 0.039152 | 12831 | 0.038798 | 0.00011793 | NAPA ID:14453 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP16 | replace crossarms at various sites and install Temporary DDO's TEMP16 at pole 854054 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2015-12-17 | b | 0.019399 | 5.8963e-05 | 2016 | 2015-12-17 | B | 39 | 0.038798 | 0.00011793
8571792 | 2015-12-10 13:04 | 2015-12-10 15:03 | 119 | 666 | 59909 | 89.9535 | 86.9535 | 0.18115 | 57911 | 0.17511 | 0.0020138 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 210283 | 1r feeder fault omo cb 1 Suspect trees, relivened OK | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-10 | c | 0.17511 | 0.0020138 | 2016 | 2015-12-10 | C | 666 | 0.17511 | 0.0020138
8573113 | 2016-01-22 09:45 | 2016-01-22 12:44 | 179 | 4 | 716 | 179 | 176 | 0.002165 | 704 | 0.0021287 | 1.2095e-05 | NAPA ID:15511 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | TP2147 | We are installing HT fuses on TP2147,Installing new cable termination pole with HT fuses FP1751 in front of TP2147,We will connect HT cable to new transformer TP2909,Upgrade FP1252.Close new fuses on TP2147. Close new fuses FP1252 and test TP2909. 351 Wai | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-22 | b | 0.0010644 | 6.048e-06 | 2016 | 2016-01-22 | B | 4 | 0.0021287 | 1.2095e-05
8607852 | 2016-01-27 08:30 | 2016-01-27 14:30 | 360 | 18 | 6480 | 360 | 357 | 0.019594 | 6426 | 0.019431 | 5.4428e-05 | NAPA ID:15182 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | P40439 | Run new 33kV conductor between poles P40439 & P49431. Work Location: Scarborough Rd, Pahiatua. CIW 115489. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-27 | b | 0.0097153 | 2.7214e-05 | 2016 | 2016-01-27 | B | 18 | 0.019431 | 5.4428e-05
8607879 | 2015-12-10 15:09 | 2015-12-10 17:47 | 158.3833 | 15 | 2375.75 | 158.3833 | 155.3833 | 0.0071837 | 2330.75 | 0.0070476 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | 2 X 15 Amp | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-10 | c | 0.0070476 | 4.5356e-05 | 2016 | 2015-12-10 | C | 15 | 0.0070476 | 4.5356e-05
8608000 | 2016-01-28 08:42 | 2016-01-28 15:37 | 415 | 9 | 3735 | 415 | 412 | 0.011294 | 3708 | 0.011212 | 2.7214e-05 | NAPA ID:15188 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | RUN NEW 33KV CONDUCTOR between poles p40495 & p16799 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-28 | b | 0.0056061 | 1.3607e-05 | 2016 | 2016-01-28 | B | 9 | 0.011212 | 2.7214e-05
8608152 | 2015-12-10 11:04 | 2015-12-10 12:10 | 66 | 5 | 330 | 66 | 63 | 0.00099784 | 315 | 0.00095248 | 1.5119e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TA2-069 | Replace Transformer TA2-069 due to oil leaking on the ground. Transformer replaced, relivened OK | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-12-10 | c | 0.00095248 | 1.5119e-05 | 2016 | 2015-12-10 | C | 5 | 0.00095248 | 1.5119e-05
8608785 | 2015-12-10 14:28 | 2015-12-10 16:37 | 128.9667 | 22 | 2837.2667 | 128.9667 | 125.9667 | 0.0085792 | 2771.2667 | 0.0083796 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t7396 | Jumper off at tx T7396 Isolated at fuses T39. No materials just 2 screws | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-12-10 | c | 0.0083796 | 6.6523e-05 | 2016 | 2015-12-10 | C | 22 | 0.0083796 | 6.6523e-05
8608885 | 2015-12-10 17:02 | 2015-12-10 17:15 | 12.5667 | 5167 | 62262.35 | 12.05 | 9.05 | 0.18827 | 46761.35 | 0.1414 | 0.015624 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB 1132 | Tripping at Transpower during planned switching under NAPA 12122. Feild Switcher onsite no crew required. Restored OK. Only a single outage, second job created to collect up contacts. | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-12-10 | c | 0.1414 | 0.015624 | 2016 | 2015-12-10 | C | 5167 | 0.1414 | 0.015624
8625877 | 2015-12-11 02:03 | 2015-12-11 12:11 | 608 | 34 | 16793 | 493.9118 | 490.9118 | 0.050778 | 16691 | 0.05047 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F0233 | 10.05pm called hub to advise 999 and taken to control. Lines are on the road, massive explosions on power lines, power is off to a few neighbors also, area is not safe as lines are lying on the road for cars to drive over. 400 mts sth of Wainui Rd, (fire | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2015-12-11 | c | 0.05047 | 0.00010281 | 2016 | 2015-12-11 | C | 34 | 0.05047 | 0.00010281
8627074 | 2015-12-11 07:15 | 2015-12-11 12:51 | 335.15 | 2 | 670.3 | 335.15 | 332.15 | 0.0020268 | 664.3 | 0.0020087 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4221 | Replace 2 x 15A fuse. Bird strike. | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-12-11 | c | 0.0020087 | 6.048e-06 | 2016 | 2015-12-11 | C | 2 | 0.0020087 | 6.0475e-06
8627215 | 2016-01-29 08:31 | 2016-01-29 13:30 | 298.5 | 18 | 5373 | 298.5 | 295.5 | 0.016247 | 5319 | 0.016083 | 5.4428e-05 | NAPA ID:15190 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P40439 | Run new 33kV conductor between poles P40439 & P49431. Work Location: Scarborough Road, Pahiatua. CIW 115489. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-29 | b | 0.0080417 | 2.7214e-05 | 2016 | 2016-01-29 | B | 18 | 0.016083 | 5.4428e-05
8627242 | 2016-02-02 09:01 | 2016-02-02 14:25 | 323.7333 | 30 | 9606.65 | 320.2217 | 317.2217 | 0.029048 | 9516.65 | 0.028776 | 9.0713e-05 | NAPA ID:15192 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | RUN NEW 33KV CONDUCTOR between poles p40495 & p16799 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-02 | b | 0.014388 | 4.5356e-05 | 2016 | 2016-02-02 | B | 30 | 0.028776 | 9.0713e-05
8627275 | 2016-02-04 08:31 | 2016-02-04 14:25 | 354.2 | 48 | 17001.6 | 354.2 | 351.2 | 0.051409 | 16857.6 | 0.050973 | 0.00014514 | NAPA ID:15196 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P40439 | Replace poles p405525,p40439,p49431 & p49432. run 33kv conductor for mangamutu 33kv #2 upgrade and temp links temp 52 for use in future shutdowns.Tree work by Treescape during outage time. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-04 | b | 0.025487 | 7.257e-05 | 2016 | 2016-02-04 | B | 48 | 0.050973 | 0.00014514
8629561 | 2015-12-11 12:13 | 2015-12-11 13:20 | 67 | 52 | 3484 | 67 | 64 | 0.010535 | 3328 | 0.010063 | 0.00015724 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5-026 | Replace faulty transformer TC5 026 | F3 | GRENADA ST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-12-11 | c | 0.010063 | 0.00015724 | 2016 | 2015-12-11 | C | 52 | 0.010063 | 0.00015724
8630644 | 2015-12-11 10:15 | 2015-12-11 11:20 | 64.5833 | 4 | 258.3333 | 64.5833 | 61.5833 | 0.00078114 | 246.3333 | 0.00074485 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SB2-020 | Reload Reliven. 2 x 10A Fuses. Cause Unknown. | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-12-11 | c | 0.00074485 | 1.2095e-05 | 2016 | 2015-12-11 | C | 4 | 0.00074485 | 1.2095e-05
8630856 | 2015-12-11 10:44 | 2015-12-11 16:49 | 365 | 93 | 12410 | 133.4409 | 130.4409 | 0.037525 | 12131 | 0.036681 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 17484 | Recloser N21 trip on O/C B Phase, E/F. Area patrolled / sectionalised with a floating conductor found at Pole 17484. Isolation between ABS N53 and the recloser wiyth backfeed at ABS N34.. Conductor rebound OK and relivened. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-12-11 | c | 0.036681 | 0.00028121 | 2016 | 2015-12-11 | C | 93 | 0.036681 | 0.00028121
8631013 | 2015-12-11 11:01 | 2015-12-11 12:07 | 65.6333 | 2 | 131.2667 | 65.6333 | 62.6333 | 0.00039692 | 125.2667 | 0.00037878 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786632 | Outage required from Fuses 4013 to repair a floating conductor. Rebound, relivened OK. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-12-11 | c | 0.00037878 | 6.048e-06 | 2016 | 2015-12-11 | C | 2 | 0.00037878 | 6.0475e-06
8631784 | 2016-01-11 09:30 | 2016-01-11 11:50 | 140 | 3 | 420 | 140 | 137 | 0.00127 | 411 | 0.0012428 | 9.0713e-06 | NAPA ID:15445 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | H0108, TC1853 | To replace pole H0108. 5729 SH27, Walton. W/O30014502 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-11 | b | 0.00062138 | 4.536e-06 | 2016 | 2016-01-11 | B | 3 | 0.0012428 | 9.0713e-06
8631850 | 2016-01-07 08:30 | 2016-01-07 08:38 | 8 | 24 | 192 | 8 | 5 | 0.00058056 | 120 | 0.00036285 | 7.257e-05 | NAPA ID:15617 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC846 | Isolate transformer TC846 to return tap setting to normal. Transformer has been tapped up due to voltage issues. New transformer has been installed TP2877 and customers have been transferred to new transformer. 8099 Paeroa - Kopu Road, Hikutaia. W/O300159 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-01-07 | b | 0.00018143 | 3.6285e-05 | 2016 | 2016-01-07 | B | 24 | 0.00036285 | 7.257e-05
8631855 | 2016-01-11 13:00 | 2016-01-11 14:40 | 100 | 2 | 200 | 100 | 97 | 0.00060475 | 194 | 0.00058661 | 6.0475e-06 | NAPA ID:14008 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2943 | To replace the 11kV Fuses & install a 400V Fuse Disconnector. 285 Maungakawa Rd, Walton. W/O 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-11 | b | 0.0002933 | 3.024e-06 | 2016 | 2016-01-11 | B | 2 | 0.00058661 | 6.0475e-06
8631980 | 2016-01-11 09:30 | 2016-01-11 11:45 | 135 | 6 | 810 | 135 | 132 | 0.0024492 | 792 | 0.0023948 | 1.8143e-05 | NAPA ID:14007 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC359 | Live Line to replace the 11kV Pin Arm & 11kV Fuse Arm. 626 Campbell Rd, Walton, Morrinsville. W/O 10147849. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-11 | b | 0.0011974 | 9.071e-06 | 2016 | 2016-01-11 | B | 6 | 0.0023948 | 1.8143e-05
8632053 | 2016-01-12 09:15 | 2016-01-12 15:25 | 370 | 21 | 7770 | 370 | 367 | 0.023495 | 7707 | 0.023304 | 6.3499e-05 | NAPA ID:14431 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kopane CB22 | Change 3 x poles 13 x xarms refit 3 x TXs. Kaimatarau Rd. W/O30011145 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.011652 | 3.1749e-05 | 2016 | 2016-01-12 | B | 21 | 0.023304 | 6.3499e-05
8632115 | 2016-01-12 09:33 | 2016-01-12 11:44 | 130.8333 | 32 | 4186.6667 | 130.8333 | 127.8333 | 0.012659 | 4090.6667 | 0.012369 | 9.676e-05 | NAPA ID:15158 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P46600 | To replace pole P46600 with new 11m busk pole. Pori Rd. W/O30006914 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.0061846 | 4.838e-05 | 2016 | 2016-01-12 | B | 32 | 0.012369 | 9.676e-05
8632141 | 2016-01-12 08:43 | 2016-01-12 11:58 | 195 | 340 | 66300 | 195 | 192 | 0.20048 | 65280 | 0.19739 | 0.0010281 | NAPA ID:15237 TP_LINTON GXP > KAIRANGA SUB > TREMAINE AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | T6/408 | Annual maintenance on Magnefix 505/506/507/FS144. 57 Herbert Ave. W/O30003942 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.098696 | 0.00051404 | 2016 | 2016-01-12 | B | 340 | 0.19739 | 0.0010281
8632178 | 2016-01-13 12:30 | 2016-01-13 14:50 | 140 | 508 | 71120 | 140 | 137 | 0.21505 | 69596 | 0.21044 | 0.0015361 | NAPA ID:13902 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 6 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Transformer 722 &1233 | 11kV Magnefix 1325 & 387 servicing. Fernleigh Straight and Govett Ave. W/O30004437. Field staff report ABS 320 may require being upgraded to a flicker type ABS or Sw/Gear unit due to load. OMS 9463305 carried out under same outage area during 13902. | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.10522 | 0.00076804 | 2016 | 2016-01-13 | B | 508 | 0.21044 | 0.0015361
8632195 | 2015-12-11 15:14 | 2015-12-13 16:01 | 2927 | 302 | 57592 | 190.702 | 187.702 | 0.17414 | 56686 | 0.1714 | 0.00091318 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 838594 | Pole badly leaning into Bush - possible fire hazard. Isolation required from Recloser CB C225 to ABS S167. Arrangements made by DOWNER to install an 11kV 1MW generator to Supply Castlepoint and area to ABS S167. (Only 2 Transformers off). Difficult locati | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-11 | c | 0.1714 | 0.00091318 | 2016 | 2015-12-11 | C | 302 | 0.1714 | 0.00091318
8632923 | 2016-01-07 09:36 | 2016-01-07 16:12 | 396.4333 | 77 | 30525.3667 | 396.4333 | 393.4333 | 0.092301 | 30294.3667 | 0.091603 | 0.00023283 | NAPA ID:15312 TP_KOPU GXP | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles O1190 & O12614/ O12610 & O12609 | Stage 2 of Turua Cable installation project. Connection of new ABS and cable pole. Conductors to be transferred from Pole O12609 to new ABS and new cable Pole O12609 to existing Pole O12614. 10 Raratuna Rd, Turua. W/O10159812 | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-07 | b | 0.045801 | 0.00011642 | 2016 | 2016-01-07 | B | 77 | 0.091603 | 0.00023283
8636394 | 2015-12-12 04:18 | 2015-12-12 04:33 | 15 | 240 | 3436 | 14.3167 | 11.3167 | 0.01039 | 2716 | 0.0082125 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB6 | E/F O/C B Phase | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.0082125 | 0.0007257 | 2016 | 2015-12-12 | C | 240 | 0.0082125 | 0.0007257
8637446 | 2015-12-12 10:54 | 2015-12-12 13:08 | 133.8667 | 5 | 669.3333 | 133.8667 | 130.8667 | 0.0020239 | 654.3333 | 0.0019785 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8448 | pls check if 8638068 is related. Tripping on all 3 phase at Fuses 8448. Dead bird found. Reloaded OK. 8 A rating. | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.0019785 | 1.5119e-05 | 2016 | 2015-12-12 | C | 5 | 0.0019785 | 1.5119e-05
8637810 | 2015-12-12 12:19 | 2015-12-12 14:00 | 100.6 | 240 | 16598.1333 | 69.1589 | 66.1589 | 0.050189 | 15878.1333 | 0.048012 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB6 | Tripping on CB6 on E/F. Feeder patrolled / sectionalised but nothing found. Restored OK. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.048012 | 0.0007257 | 2016 | 2015-12-12 | C | 240 | 0.048012 | 0.0007257
8639661 | 2015-12-12 17:36 | 2015-12-12 18:39 | 63 | 110 | 6930 | 63 | 60 | 0.020955 | 6600 | 0.019957 | 0.00033261 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE |  | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.019957 | 0.00033261 | 2016 | 2015-12-12 | C | 110 | 0.019957 | 0.00033261
8639887 | 2015-12-12 19:45 | 2015-12-12 20:58 | 73.35 | 110 | 5987.7 | 54.4336 | 51.4336 | 0.018105 | 5657.7 | 0.017108 | 0.00033261 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | Changed open points of feeder to test | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.017108 | 0.00033261 | 2016 | 2015-12-12 | C | 110 | 0.017108 | 0.00033261
8640674 | 2015-12-12 22:18 | 2015-12-13 01:30 | 191.8167 | 240 | 30105.5833 | 125.4399 | 122.4399 | 0.091032 | 29385.5833 | 0.088855 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773598 | 2 X H/T Insulators & Pulled up some Conductor at Pole 773598 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.088855 | 0.0007257 | 2016 | 2015-12-12 | C | 240 | 0.088855 | 0.0007257
8641789 | 2015-12-12 23:13 | 2015-12-13 12:45 | 812.5833 | 116 | 22335.7667 | 192.5497 | 189.5497 | 0.067538 | 21987.7667 | 0.066486 | 0.00035076 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03225 | Damaged insulator found at Pole P03225 - isolated at ABS V81 and Temp Links 47 - Isulator replaced - Used 1 x HV insulator | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-12 | c | 0.066486 | 0.00035076 | 2016 | 2015-12-12 | C | 116 | 0.066486 | 0.00035076
8641917 | 2015-12-13 00:40 | 2015-12-13 02:00 | 80 | 51 | 4080 | 80 | 77 | 0.012337 | 3927 | 0.011874 | 0.00015421 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 216676 | Blown H/V fuse at Fuses SE3 017. Found line down x 1 at pole 216678 possum found at base of pole. Isolation at fuses SE3 017. ( Spur no back feeds ) Line repaired all service restored. Materials 1 x metre conductor, 2 x comp sleeves | F2/F4 | MALEME ST | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-13 | c | 0.011874 | 0.00015421 | 2016 | 2015-12-13 | C | 51 | 0.011874 | 0.00015421
8643037 | 2015-12-13 05:36 | 2015-12-13 08:35 | 178.75 | 236 | 31451.0667 | 133.2672 | 130.2672 | 0.0951 | 30743.0667 | 0.09296 | 0.00071361 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 499 | RS 499 Tripped B, C Phase Over Current L/O - Line patrolled and sectionlised with no fault found | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.09296 | 0.00071361 | 2016 | 2015-12-13 | C | 236 | 0.09296 | 0.00071361
8643477 | 2015-12-13 07:17 | 2015-12-13 08:25 | 67.6167 | 2 | 135.2333 | 67.6167 | 64.6167 | 0.00040891 | 129.2333 | 0.00039077 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2634 | 2 Fuses found blown at Fuses 2634 - line patrolled with no cause found - used 2 x 6amp fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.00039077 | 6.048e-06 | 2016 | 2015-12-13 | C | 2 | 0.00039077 | 6.0475e-06
8643527 | 2015-12-13 10:21 | 2015-12-13 12:58 | 157.3167 | 31 | 1204.6 | 38.8581 | 35.8581 | 0.0036424 | 1111.6 | 0.0033612 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P31459 | Car vs Pole - insulator hanging. F1977935. Fire require an ETA please 04 801 0812 10 mins advised fire comms 8.19am called hub to advise 999. Broken 11 kv cross arm and conductor is hanging - will need to shut down and replace today. P31459. Fm requesting | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.0033612 | 9.3737e-05 | 2016 | 2015-12-13 | C | 31 | 0.0033612 | 9.3737e-05
8643584 | 2015-12-13 08:34 | 2015-12-13 16:49 | 494.95 | 719 | 277756.3333 | 386.3092 | 383.3092 | 0.83987 | 275599.3333 | 0.83335 | 0.0021741 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | D12537 | Report of car v pole at 1892 Tirau Rd was preceded by AC fail alarms on sectionalisers 9892/2, SS9396 & Maungatautari repeater. Significant loss of load also noticed on CB 5 at Tirau sub. CB 5 opened by NOC until contractor arrives on site and access's da | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-12-13 | c | 0.83335 | 0.0021741 | 2016 | 2015-12-13 | C | 719 | 0.83335 | 0.0021741
8644359 | 2015-12-13 09:00 | 2015-12-13 10:00 | 60.3333 | 2 | 96.8 | 48.4 | 45.4 | 0.0002927 | 90.8 | 0.00027456 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2128 | 9.02am called hub to advise of 999. Please check if 8644443 is related. 2 fuses found blown at Transformer T2128 - used 2x 3amp fuses and carriers | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.00027456 | 6.048e-06 | 2016 | 2015-12-13 | C | 2 | 0.00027456 | 6.0475e-06
8645326 | 2015-12-13 14:02 | 2015-12-13 15:27 | 85 | 20 | 1700 | 85 | 82 | 0.0051404 | 1640 | 0.004959 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2650 | 2 fuse found blown at fuses 2650 - used 2 x 20 amp fuses - caused by weather | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.004959 | 6.0475e-05 | 2016 | 2015-12-13 | C | 20 | 0.004959 | 6.0475e-05
8646051 | 2015-12-13 14:02 | 2015-12-13 16:01 | 118.45 | 717 | 63464.2667 | 88.5136 | 85.5136 | 0.1919 | 61313.2667 | 0.1854 | 0.002168 |  | 22 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 806596 | Branch contacting lines at Pole 806596- cleared using hot sticks - faultman to put in defect for tree. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.1854 | 0.002168 | 2016 | 2015-12-13 | C | 717 | 0.1854 | 0.002168
8648126 | 2015-12-13 16:34 | 2015-12-13 21:21 | 286.9667 | 353 | 28123.25 | 79.6693 | 76.6693 | 0.085038 | 27064.25 | 0.081836 | 0.0010674 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21359, P21416 | Recloser CB10050 found tripped (No Comms). Broken Conductor found up Pahiatua Track at Pole P21359. Isolation required from FABS 10105. Repairs made with 1 DDO Unit replaced, 1 sleeve and 1 * 3A HT fuse. However, when FABS 10105 was closed to restore s | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.081836 | 0.0010674 | 2016 | 2015-12-13 | C | 353 | 0.081836 | 0.0010674
8648165 | 2015-12-13 15:39 | 2015-12-13 20:07 | 267.15 | 346 | 17588.9667 | 50.8352 | 47.8352 | 0.053185 | 16550.9667 | 0.050046 | 0.0010462 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T6/524 | Tripping on Recloser 4258 on B-C Phase E/F. Fault traced to defective Transformer T6/524. HT fuses Open and Transformer replaced. Restored to Service OK. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.050046 | 0.0010462 | 2016 | 2015-12-13 | C | 346 | 0.050046 | 0.0010462
8648517 | 2015-12-13 15:41 | 2015-12-13 18:13 | 152.1333 | 15 | 2282 | 152.1333 | 149.1333 | 0.0069002 | 2237 | 0.0067642 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | 2 fuses found blown at Fuses 2829 - used 2 x 15 amp fuses - cause unknown Unable to close | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.0067642 | 4.5356e-05 | 2016 | 2015-12-13 | C | 15 | 0.0067642 | 4.5356e-05
8648610 | 2015-12-13 16:32 | 2015-12-13 17:00 | 28 | 8 | 224 | 28 | 25 | 0.00067732 | 200 | 0.00060475 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7544 | 2 fuses found blown at Fuses 7544 - caused by bird strike - used 2 x 10 amp fuses | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.00060475 | 2.419e-05 | 2016 | 2015-12-13 | C | 8 | 0.00060475 | 2.419e-05
8650244 | 2015-12-13 18:35 | 2015-12-13 20:30 | 114.4 | 229 | 26113.3333 | 114.032 | 111.032 | 0.07896 | 25426.3333 | 0.076883 | 0.00069244 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 766242 | Tripping on CB7 on O/C. Fault traced to large tree branch fallen onto lines on Kelvin Street. (Isolation from ABS 1498). Tree cut away with a damaged conductor also repaired. NDR 047254 | F2 | ARAMOHO INLAND | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.076883 | 0.00069244 | 2016 | 2015-12-13 | C | 229 | 0.076883 | 0.00069244
8651023 | 2015-12-13 19:45 | 2015-12-13 23:52 | 246.4833 | 1 | 246.4833 | 246.4833 | 243.4833 | 0.00074531 | 243.4833 | 0.00073624 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N9 | 2 HT Fuses tripped at N9. (3A Rating). Relosed OK. Suspect line clash. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-12-13 | c | 0.00073624 | 3.024e-06 | 2016 | 2015-12-13 | C | 1 | 0.00073624 | 3.0238e-06
8651212 | 2015-12-14 08:43 | 2015-12-14 10:40 | 117 | 4 | 468 | 117 | 114 | 0.0014151 | 456 | 0.0013788 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t3/249 | The Spur line feeding this Transformer T3/249 has fuses 10268 (nNo number on site). 2 fuses had tripped due to tree branch over the line. Unable to remove. Staying off in the meantime until daylight hours, tree contractors required. tree branch removed | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-14 | c | 0.0013788 | 1.2095e-05 | 2016 | 2015-12-14 | C | 4 | 0.0013788 | 1.2095e-05
8651650 | 2015-12-13 23:32 | 2015-12-14 01:13 | 101.45 | 132 | 13391.4 | 101.45 | 98.45 | 0.040492 | 12995.4 | 0.039295 | 0.00039914 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 207486 | Burnt fuse holders found at Fuses SA2 041. Emergency isolation at ABS SA2 007 ( Spur no back feeds ). Materials 3 x fuse holders replaces, 3 x 20A H/V fuses replaced , all service restored | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-12-13 | c | 0.039295 | 0.00039914 | 2016 | 2015-12-13 | C | 132 | 0.039295 | 0.00039914
8651733 | 2015-12-13 20:30 | 2015-12-13 21:55 | 85 | 54 | 4590 | 85 | 82 | 0.013879 | 4428 | 0.013389 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210221 | Fuse x1 blown at Fuses SD2 023, found line x1 down at pole 210221. Line repaired all service restored. Materials 1 x H/V insulator/polymer | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-13 | c | 0.013389 | 0.00016328 | 2016 | 2015-12-13 | C | 54 | 0.013389 | 0.00016328
8654001 | 2015-12-14 06:55 | 2015-12-14 07:05 | 10 | 32 | 320 | 10 | 7 | 0.0009676 | 224 | 0.00067732 | 9.676e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6038 | at 06:59, Cardiff Sub, CB Q21 Mahoe Feeder. Found ABS 6038 had a damaged contact. ABS 6038 was Opened (faultman advised safe to open) and then closed ABS 6126 shortly after to restore power. ABS 6038 DNO 151209. This was the cause for the other related jo | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2015-12-14 | c | 0.00067732 | 9.676e-05 | 2016 | 2015-12-14 | C | 32 | 0.00067732 | 9.676e-05
8654410 | 2015-12-18 09:16 | 2015-12-18 11:47 | 151.8667 | 185 | 28095.3333 | 151.8667 | 148.8667 | 0.084954 | 27540.3333 | 0.083275 | 0.0005594 | NAPA ID:15019 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 12 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 3787018 | 11kV lines install new 50kVA pole mounted transformer Transformer 2287N to network pole 378018 and LV line break at pole 751514. 14 Junction Street, New Plymouth. CIW115082 | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-18 | b | 0.041638 | 0.0002797 | 2016 | 2015-12-18 | B | 185 | 0.083275 | 0.0005594
8654793 | 2016-01-12 09:15 | 2016-01-12 13:37 | 262 | 118 | 30916 | 262 | 259 | 0.093483 | 30562 | 0.092412 | 0.0003568 | NAPA ID:15006 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 704712 & 704714 | Replace network poles 704712 & 704714. Main South Road, Warea. W/O30010591 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.046206 | 0.0001784 | 2016 | 2016-01-12 | B | 118 | 0.092412 | 0.0003568
8654907 | 2016-01-13 09:35 | 2016-01-13 16:28 | 413 | 3 | 1239 | 413 | 410 | 0.0037464 | 1230 | 0.0037192 | 9.0713e-06 | NAPA ID:13554 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 839107 | Change poles between 829101 and pole 839107. Work Location: Kaka Amu Rd. W/O 30014082. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.0018596 | 4.536e-06 | 2016 | 2016-01-13 | B | 3 | 0.0037192 | 9.0713e-06
8654937 | 2016-01-18 09:10 | 2016-01-18 15:50 | 400 | 19 | 7600 | 400 | 397 | 0.022981 | 7543 | 0.022808 | 5.7451e-05 | NAPA ID:13586 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 839028 | Change cross arms between poles 839028 and 839064. Work Location: Kaka Amu Rd. W/O 30014082. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-18 | b | 0.011404 | 2.8726e-05 | 2016 | 2016-01-18 | B | 19 | 0.022808 | 5.7451e-05
8654967 | 2015-12-15 09:02 | 2015-12-15 09:21 | 18.7333 | 126 | 2222.1333 | 17.636 | 14.636 | 0.0067192 | 1844.1333 | 0.0055762 | 0.00038099 | NAPA ID:15659 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 210357 | Urgent replacement of ABS arms at pole 210357, (SD3-038). Work Location: Armstrong Rd, Te Puna. Work Order: 30018282 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-15 | b | 0.0027881 | 0.0001905 | 2016 | 2015-12-15 | B | 126 | 0.0055762 | 0.00038099
8655533 | 2016-01-19 09:15 | 2016-01-19 16:02 | 407 | 8 | 3256 | 407 | 404 | 0.0098454 | 3232 | 0.0097728 | 2.419e-05 | NAPA ID:13601 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 839065 | Change poles 839065,839066,839067,839068,839073. Replace arms from poles 839069 to 839071. Work Location: Kaka Amu Rd. W/O 30014082. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-19 | b | 0.0048864 | 1.2095e-05 | 2016 | 2016-01-19 | B | 8 | 0.0097728 | 2.419e-05
8655561 | 2016-01-12 09:00 | 2016-01-12 15:57 | 417 | 47 | 19599 | 417 | 414 | 0.059263 | 19458 | 0.058836 | 0.00014212 | NAPA ID:13513 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 834939 & 839012 | Change pole 839012. Replace arms from 834939 to 839015. Install Temp ABS at pole 839017. Kaka Amu Rd. W/O 30014082. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.029418 | 7.1058e-05 | 2016 | 2016-01-12 | B | 47 | 0.058836 | 0.00014212
8655838 | 2015-12-14 10:55 | 2015-12-14 11:38 | 43 | 2 | 86 | 43 | 40 | 0.00026004 | 80 | 0.0002419 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2342 | at 10:55, Walton Sub, CB 3 Piakoiti Feeder. Found LV Lines down at Transformer Pole TC2342. Own Isolation & AP and repairs carried out. All Power restored on completion. 2x Sleeves and 3m of conductor 1 phase replaced. Paul Cooper Attended. 10.10am - advi | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-14 | c | 0.0002419 | 6.048e-06 | 2016 | 2015-12-14 | C | 2 | 0.0002419 | 6.0475e-06
8655866 | 2016-01-13 09:35 | 2016-01-13 16:15 | 400 | 26 | 10400 | 400 | 397 | 0.031447 | 10322 | 0.031211 | 7.8618e-05 | NAPA ID:14448 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rongotea CB8 | Run approximately 1200mtr of new WEKE conductor. Sanson Rd. W/O30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.015606 | 3.9309e-05 | 2016 | 2016-01-13 | B | 26 | 0.031211 | 7.8618e-05
8655915 | 2016-01-12 10:15 | 2016-01-12 11:31 | 76 | 64 | 4864 | 76 | 73 | 0.014708 | 4672 | 0.014127 | 0.00019352 | NAPA ID:13914 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 10 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 362 | 11kV Magnefix 362 servicing. Fernleigh Straight and Govett Ave. W/O30004437 | F3 | BROOKLANDS 10 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.0070635 | 9.676e-05 | 2016 | 2016-01-12 | B | 64 | 0.014127 | 0.00019352
8655917 | 2016-01-13 08:30 | 2016-01-13 14:24 | 353.6167 | 66 | 23338.7 | 353.6167 | 350.6167 | 0.070571 | 23140.7 | 0.069972 | 0.00019957 | NAPA ID:15386 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 787310 | Change cross arms and erect poles from pole 787310 to pole 787407. Otuarei Rd, Taihape. W/O30006838. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.034986 | 9.9784e-05 | 2016 | 2016-01-13 | B | 66 | 0.069972 | 0.00019957
8656359 | 2015-12-14 12:27 | 2015-12-14 12:46 | 18.6667 | 87 | 1624 | 18.6667 | 15.6667 | 0.0049106 | 1363 | 0.0041214 | 0.00026307 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | N/A - NOT APPLICABLE | at 12:27, Waitara East Sub, CB U30 Main Rd Motunui Feeder. Faultman advised that he had been told of trees that were down over the lines and the lines were still alive. Faultman requested Control to Open Recloser 5329 for safety. Faultman inspected once a | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-14 | c | 0.0041214 | 0.00026307 | 2016 | 2015-12-14 | C | 87 | 0.0041214 | 0.00026307
8656460 | 2016-01-20 08:49 | 2016-01-20 15:18 | 388.8333 | 67 | 26051.8333 | 388.8333 | 385.8333 | 0.078775 | 25850.8333 | 0.078167 | 0.00020259 | NAPA ID:15387 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 787309 | Change cross arms and erect poles from pole 787310 to pole 787407. Work location: Otuari Road, Taihape. Work Order: 30006838. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-01-20 | b | 0.039083 | 0.0001013 | 2016 | 2016-01-20 | B | 67 | 0.078167 | 0.00020259
8656488 | 2015-12-14 11:06 | 2015-12-14 15:45 | 278.9333 | 2 | 557.8667 | 278.9333 | 275.9333 | 0.0016869 | 551.8667 | 0.0016687 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1375 | at 14:08 Tasman Sub, CB TA1 Ihaia Rd Feeder. Found blown transformer at T1375. Own Isolation & AP. Transformer Replaced. All Power Restored on Completion and all OK. 1x Transformer & 3x HV Fuses Replaced. Paul Fitzpatrick attended. FM called to request a | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-12-14 | c | 0.0016687 | 6.048e-06 | 2016 | 2015-12-14 | C | 2 | 0.0016687 | 6.0475e-06
8656621 | 2016-01-10 09:00 | 2016-01-10 13:30 | 270 | 2 | 540 | 270 | 267 | 0.0016328 | 534 | 0.0016147 | 6.0475e-06 | NAPA ID:15236 TP_TAURANGA 33 GXP > HAMILTON STREET SUB > SULPHUR PT | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T10-1 & T10-2 | Replace Transformer T10-1 with a 100kVA Ground Mount. Port of Tauranga- Sulphur Point. W/O30002526 | F1 | SULPHUR PT | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 2016-01-10 | b | 0.00080734 | 3.024e-06 | 2016 | 2016-01-10 | B | 2 | 0.0016147 | 6.0475e-06
8656662 | 2016-01-13 10:14 | 2016-01-13 15:05 | 291 | 45 | 13095 | 291 | 288 | 0.039596 | 12960 | 0.039188 | 0.00013607 | NAPA ID:14388 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1370, Pole 825874 | Liveline break to replace 11kv poles. Jordan Terrace, Masterton. W/O30013208 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.019594 | 6.8035e-05 | 2016 | 2016-01-13 | B | 45 | 0.039188 | 0.00013607
8656911 | 2016-01-12 13:00 | 2016-01-12 14:00 | 60 | 232 | 13920 | 60 | 57 | 0.042091 | 13224 | 0.039986 | 0.00070151 | NAPA ID:13923 TP_CARRINGTON GXP > CITY SUB > CITY 4 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Transformers 1228 & 808 | 11kV Magnefix 1228 servicing. Coronation Ave. W/O30004437 | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2016-01-12 | b | 0.019993 | 0.00035076 | 2016 | 2016-01-12 | B | 232 | 0.039986 | 0.00070151
8656920 | 2016-01-13 10:05 | 2016-01-13 10:57 | 52 | 90 | 4680 | 52 | 49 | 0.014151 | 4410 | 0.013335 | 0.00027214 | NAPA ID:13900 TP_CARRINGTON GXP > CITY SUB > CITY 4 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 4 | 11kV Magnefix 380 servicing. Work Location: 34 Leach Street. W/O 30004437. | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.0066674 | 0.00013607 | 2016 | 2016-01-13 | B | 90 | 0.013335 | 0.00027214
8656978 | 2016-01-13 09:45 | 2016-01-13 15:00 | 315 | 32 | 10080 | 315 | 312 | 0.03048 | 9984 | 0.030189 | 9.676e-05 | NAPA ID:14748 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3084T, Pole 760999 | We are replacing the whole transformer structure as it is not in very good condition. Also we are upgrading transformer as it is over loaded. 276 Tikorangi Road, Waitara. W/O30015320 | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.015095 | 4.838e-05 | 2016 | 2016-01-13 | B | 32 | 0.030189 | 9.676e-05
8657072 | 2016-01-13 10:21 | 2016-01-13 12:16 | 115.2333 | 28 | 3226.5333 | 115.2333 | 112.2333 | 0.0097563 | 3142.5333 | 0.0095023 | 8.4665e-05 | NAPA ID:15167 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P06891 | To replace 11kv cross arms and repair conductor. Work Location: Range Road. W/O30015048 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.0047511 | 4.2333e-05 | 2016 | 2016-01-13 | B | 28 | 0.0095023 | 8.4665e-05
8657317 | 2016-01-14 09:15 | 2016-01-14 15:13 | 358 | 27 | 9666 | 358 | 355 | 0.029228 | 9585 | 0.028983 | 8.1642e-05 | NAPA ID:15064 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 704730 | Replace network poles 704715 to 704730. Work Location: Main South Road, Warea. W/O 30010591. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-14 | b | 0.014491 | 4.0821e-05 | 2016 | 2016-01-14 | B | 27 | 0.028983 | 8.1642e-05
8657324 | 2016-01-14 08:48 | 2016-01-14 15:52 | 423.6667 | 19 | 8049.6667 | 423.6667 | 420.6667 | 0.02434 | 7992.6667 | 0.024168 | 5.7451e-05 | NAPA ID:13555 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 839064 | Change stub pole at pole 839016. Change pole at 839027. Change cross arms between 839017 and 839027. Install temporary 11kV ABS "ABS 38" at pole 839064. Work Location: Kaka Amu Rd. W/O 30014082. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-14 | b | 0.012084 | 2.8726e-05 | 2016 | 2016-01-14 | B | 19 | 0.024168 | 5.7451e-05
8657360 | 2016-01-14 08:52 | 2016-01-14 11:45 | 173 | 2 | 346 | 173 | 170 | 0.0010462 | 340 | 0.0010281 | 6.0475e-06 | NAPA ID:14382 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE7-090 | Pole change 218013. Work Location: Kaikokopu Road, Pongakawa. W/O 30012281 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-14 | b | 0.00051404 | 3.024e-06 | 2016 | 2016-01-14 | B | 2 | 0.0010281 | 6.0475e-06
8657378 | 2016-01-15 09:00 | 2016-01-15 15:54 | 414 | 2 | 828 | 414 | 411 | 0.0025037 | 822 | 0.0024855 | 6.0475e-06 | NAPA ID:13591 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Change poles 839030,839031,839032,839033 and 839037. Change arms between poles 839030-839055. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-15 | b | 0.0012428 | 3.024e-06 | 2016 | 2016-01-15 | B | 2 | 0.0024855 | 6.0475e-06
8657514 | 2016-01-27 09:15 | 2016-01-27 16:00 | 405 | 47 | 19035 | 405 | 402 | 0.057557 | 18894 | 0.057131 | 0.00014212 | NAPA ID:13509 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 834924 | Changes poles 834928 and 834932. Change all arms between poles 834924 to 834939. Temp ABS will be removed in the shutdown | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-27 | b | 0.028565 | 7.1058e-05 | 2016 | 2016-01-27 | B | 47 | 0.057131 | 0.00014212
8657668 | 2016-01-14 10:10 | 2016-01-14 15:15 | 305 | 2 | 610 | 305 | 302 | 0.0018445 | 604 | 0.0018264 | 6.0475e-06 | NAPA ID:15254 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 764707 | Replacing pole and transformer 4286T. Work Location: Rowe Rd. W/O 30013844. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-14 | b | 0.00091318 | 3.024e-06 | 2016 | 2016-01-14 | B | 2 | 0.0018264 | 6.0475e-06
8657716 | 2016-01-14 10:50 | 2016-01-14 12:15 | 85 | 2 | 170 | 85 | 82 | 0.00051404 | 164 | 0.0004959 | 6.0475e-06 | NAPA ID:15428 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4442, Pole M13516 | Pole M13516 (TC4442) replace transformer. 590 Harris Rd, Putaruru. W/O30015661 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-14 | b | 0.00024795 | 3.024e-06 | 2016 | 2016-01-14 | B | 2 | 0.0004959 | 6.0475e-06
8660154 | 2016-01-14 08:32 | 2016-01-14 11:20 | 167.6833 | 106 | 17774.4333 | 167.6833 | 164.6833 | 0.053746 | 17456.4333 | 0.052784 | 0.00032052 | NAPA ID:14432 TP_BUNNYTHORPE GXP > FEILDING SUB > COLYTON | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/307 | Replace Transformer LV panel at T3/307. Seddon Street. W/O30015269 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-01-14 | b | 0.026392 | 0.00016026 | 2016 | 2016-01-14 | B | 106 | 0.052784 | 0.00032052
8660227 | 2016-01-14 09:32 | 2016-01-14 15:35 | 362.9333 | 12 | 4355.2 | 362.9333 | 359.9333 | 0.013169 | 4319.2 | 0.01306 | 3.6285e-05 | NAPA ID:14442 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8 | Run 2000mtrs of WEKE conductor. Work Location: Maindrain Rd. W/O 30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-14 | b | 0.0065301 | 1.8143e-05 | 2016 | 2016-01-14 | B | 12 | 0.01306 | 3.6285e-05
8665130 | 2015-12-15 11:31 | 2015-12-15 15:58 | 267 | 36 | 9612 | 267 | 264 | 0.029064 | 9504 | 0.028738 | 0.00010886 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3770 | at 10:47, Morrinsville Sub, CB 1 Lorne St Feeder. Found badly burnt out LV Fuse gear. Isolated LV of transformer at TC3770 T-Blade Switch. Repairs carried out. Also found that the red phase HV Fuse had also burnt out. Repairs were also made to this using | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 2015-12-15 | c | 0.028738 | 0.00010886 | 2016 | 2015-12-15 | C | 36 | 0.028738 | 0.00010886
8665281 | 2016-01-15 10:45 | 2016-01-15 12:08 | 83 | 2 | 166 | 83 | 80 | 0.00050194 | 160 | 0.0004838 | 6.0475e-06 | NAPA ID:15564 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole M12421 | Pole M12421 (TC2643): Replace cross arms. 407 Waotu Road, Putaruru. W/O30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-15 | b | 0.0002419 | 3.024e-06 | 2016 | 2016-01-15 | B | 2 | 0.0004838 | 6.0475e-06
8665637 | 2016-01-17 05:00 | 2016-01-17 07:12 | 132 | 32 | 4224 | 132 | 129 | 0.012772 | 4128 | 0.012482 | 9.676e-05 | NAPA ID:15329 TP_KINLEITH GXP > BAIRD ROAD SUB > ASHWORTH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4047 | Replacement of Local kiosk 400 Volt Red Phase Switch board off TC4047 which is in Warratah Place Kiosk Tokoroa. The Fuse is mounted in the Large 400 Volt Switch board in Kiosk, mounted hard on 400 Volt Busbars. Waratah Place, Tokoroa. W/O30017540 | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-17 | b | 0.006241 | 4.838e-05 | 2016 | 2016-01-17 | B | 32 | 0.012482 | 9.676e-05
8665963 | 2015-12-22 10:15 | 2015-12-22 11:34 | 79 | 6 | 474 | 79 | 76 | 0.0014333 | 456 | 0.0013788 | 1.8143e-05 | NAPA ID:15679 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | T2789 | TX UPGRADE DUE TO OVERLOAD ON EXISTING TX | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-12-22 | b | 0.00068942 | 9.071e-06 | 2016 | 2015-12-22 | B | 6 | 0.0013788 | 1.8143e-05
8666004 | 2015-12-18 09:15 | 2015-12-18 12:00 | 165 | 7 | 1155 | 165 | 162 | 0.0034924 | 1134 | 0.0034289 | 2.1166e-05 | NAPA ID:15677 TP_MASTERTON GXP > CLAREVILLE SUB > BELVEDERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | N/A - NOT APPLICABLE | TRANSFORMER UPGRADE ONLY. Work Location: Connollys Line, Carterton. CIW125065 | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-12-18 | b | 0.0017145 | 1.0583e-05 | 2016 | 2015-12-18 | B | 7 | 0.0034289 | 2.1166e-05
8666496 | 2016-01-18 09:38 | 2016-01-18 12:35 | 177 | 9 | 1593 | 177 | 174 | 0.0048169 | 1566 | 0.0047352 | 2.7214e-05 | NAPA ID:14011 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3181 | LLP: To replace the 11kV Fuses. AP: To replace the transformer & install a 400V Fuse Disconnector. Work Location: Campbell Road, Walton. W/O 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-18 | b | 0.0023676 | 1.3607e-05 | 2016 | 2016-01-18 | B | 9 | 0.0047352 | 2.7214e-05
8666836 | 2016-01-15 08:53 | 2016-01-15 14:27 | 334.05 | 8 | 2672.4 | 334.05 | 331.05 | 0.0080807 | 2648.4 | 0.0080081 | 2.419e-05 | NAPA ID:14751 TP_MASTERTON GXP > AWATOITOI SUB > ROROKOKO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1873 | Replace T1873 and pole. Work Location: 87 Blair Logie Road, Masterton. W/O 30014822. | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-01-15 | b | 0.0040041 | 1.2095e-05 | 2016 | 2016-01-15 | B | 8 | 0.0080081 | 2.419e-05
8667165 | 2016-01-16 10:00 | 2016-01-16 13:18 | 197.7167 | 6 | 1186.3 | 197.7167 | 194.7167 | 0.0035871 | 1168.3 | 0.0035327 | 1.8143e-05 | NAPA ID:15451 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole M13402 | Pole M13402 (TC2666) replace crossarms and transformer. White Road, Putaruru. W/O30015661 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-16 | b | 0.0017663 | 9.071e-06 | 2016 | 2016-01-16 | B | 6 | 0.0035327 | 1.8143e-05
8667222 | 2016-01-16 09:49 | 2016-01-16 15:36 | 347 | 9 | 3123 | 347 | 344 | 0.0094432 | 3096 | 0.0093616 | 2.7214e-05 | NAPA ID:14443 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Rongotea CB8 | Run 1700mtrs of WEKE conductor. Maindrain Road. W/O30011145 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-16 | b | 0.0046808 | 1.3607e-05 | 2016 | 2016-01-16 | B | 9 | 0.0093616 | 2.7214e-05
8667329 | 2015-12-16 09:20 | 2015-12-16 16:30 | 430.5 | 47 | 20233.5 | 430.5 | 427.5 | 0.061181 | 20092.5 | 0.060755 | 0.00014212 | NAPA ID:15694 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 834915 | Change various poles an cross arms between poles 834915 and 834924. Change fuse arm and DDOs at pole 839101 (DDOs 7480) Treescape will be working under the same shutdown. Works location: Kaka Amu Rd. WO 30014082 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-12-16 | b | 0.030377 | 7.1058e-05 | 2016 | 2015-12-16 | B | 47 | 0.060755 | 0.00014212
8667340 | 2016-01-16 11:23 | 2016-01-16 11:50 | 27 | 1 | 27 | 27 | 24 | 8.1642e-05 | 24 | 7.257e-05 | 3.0238e-06 | NAPA ID:15618 TP_CARRINGTON GXP > CITY SUB > CITY 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Transformer 482 | 11kV magnefix 104 maintenance. This magnefix supply a dedicated tx 482 to STOS head office. I've negotiated a date for a outage to do this maintenance. Email will be attached. Corner Dawson and Devon Streets. W/O30004373 | F2 | CITY 5 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 2016-01-16 | b | 3.6285e-05 | 1.512e-06 | 2016 | 2016-01-16 | B | 1 | 7.257e-05 | 3.0238e-06
8667342 | 2016-01-15 12:30 | 2016-01-15 15:06 | 156.45 | 167 | 26127.15 | 156.45 | 153.45 | 0.079002 | 25626.15 | 0.077487 | 0.00050497 | NAPA ID:15269 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 7 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | G100, G175 | Annual maintenance of Magnefix G100 A/B/C/T & G175A/T. Work Location: Seddon Street. W/O 30003942. | F3 | PASCAL ST 7 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-01-15 | b | 0.038744 | 0.00025248 | 2016 | 2016-01-15 | B | 167 | 0.077487 | 0.00050497
8667416 | 2016-01-18 09:45 | 2016-01-18 14:30 | 285 | 18 | 5130 | 285 | 282 | 0.015512 | 5076 | 0.015349 | 5.4428e-05 | NAPA ID:15444 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | U30 | Tree cutting, burnt trees at 42 Putts Rd. W/O10152358. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-18 | b | 0.0076743 | 2.7214e-05 | 2016 | 2016-01-18 | B | 18 | 0.015349 | 5.4428e-05
8667437 | 2016-01-19 10:00 | 2016-01-19 15:34 | 334 | 27 | 9018 | 334 | 331 | 0.027268 | 8937 | 0.027023 | 8.1642e-05 | NAPA ID:15065 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 704754 | Replace network poles 704734 to 704754. Work Location: Main South Road, Warea. W/O 30010591. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-19 | b | 0.013512 | 4.0821e-05 | 2016 | 2016-01-19 | B | 27 | 0.027023 | 8.1642e-05
8667465 | 2016-01-16 06:15 | 2016-01-16 09:10 | 175 | 2 | 350 | 175 | 172 | 0.0010583 | 344 | 0.0010402 | 6.0475e-06 | NAPA ID:15627 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Pascal Street CB5 | 1Yr Maintenance on Magnefix G305a/b/c/d/t, G288a/t and G201a/t. This is a major customer (Goodman Fielder) they have agreed to the shutdown as it will take there whole plant offline for 6hrs. Botanical Road. W/O30003942 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-16 | b | 0.00052009 | 3.024e-06 | 2016 | 2016-01-16 | B | 2 | 0.0010402 | 6.0475e-06
8668332 | 2016-01-13 09:30 | 2016-01-13 12:44 | 194 | 57 | 11058 | 194 | 191 | 0.033437 | 10887 | 0.03292 | 0.00017235 | NAPA ID:15146 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2204 | Replace 33kV ,11kV & 400V cross arms at various sites. Work location: Maungakawa Road. W/O 30008216. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-13 | b | 0.01646 | 8.6177e-05 | 2016 | 2016-01-13 | B | 57 | 0.03292 | 0.00017235
8668341 | 2016-01-14 09:18 | 2016-01-14 15:10 | 352 | 2 | 704 | 352 | 349 | 0.0021287 | 698 | 0.0021106 | 6.0475e-06 | NAPA ID:15352 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF8-026 | To replace the transformer pole and upgrade the transformer to a 100kVA. Work Location: McDougall Quarry Rd- Hereford Park Rd, Pongakawa. W/O 30018235 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-14 | b | 0.0010553 | 3.024e-06 | 2016 | 2016-01-14 | B | 2 | 0.0021106 | 6.0475e-06
8668389 | 2016-01-20 09:48 | 2016-01-20 12:19 | 151 | 71 | 10721 | 151 | 148 | 0.032418 | 10508 | 0.031774 | 0.00021469 | NAPA ID:15319 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C1483 | Replace 11 kV Cross Arms at various locations. Work location: Tui Street, Te Aroha. W/O 30002440. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.015887 | 0.00010734 | 2016 | 2016-01-20 | B | 71 | 0.031774 | 0.00021469
8668472 | 2016-01-20 10:00 | 2016-01-20 14:30 | 270 | 5 | 1350 | 270 | 267 | 0.0040821 | 1335 | 0.0040367 | 1.5119e-05 | NAPA ID:15367 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 741867 | To replace transformer structure with new 11m pole plus new 15kVA transformer at transformer 1607. Work Location: 257 Brown Road, Brixton. W/O 30017366 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-01-20 | b | 0.0020184 | 7.559e-06 | 2016 | 2016-01-20 | B | 5 | 0.0040367 | 1.5119e-05
8668656 | 2016-01-22 10:16 | 2016-01-22 15:44 | 328.1 | 53 | 17389.3 | 328.1 | 325.1 | 0.052581 | 17230.3 | 0.0521 | 0.00016026 | NAPA ID:15469 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 790879 | Replace rotten two pole 11kV structure 790879 & 790878. Work Location: Longacre Valley Road, Wanganui. W/O 10150487 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2016-01-22 | b | 0.02605 | 8.013e-05 | 2016 | 2016-01-22 | B | 53 | 0.0521 | 0.00016026
8668726 | 2016-01-19 09:47 | 2016-01-19 12:45 | 177.95 | 9 | 1601.55 | 177.95 | 174.95 | 0.0048427 | 1574.55 | 0.0047611 | 2.7214e-05 | NAPA ID:15570 TP_MASTERTON GXP > NORFOLK SUB > HOLDSWORTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1127 | Replace transformer and pole. Work Location: Norfolk Road, Carterton. W/O 30008371 | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2016-01-19 | b | 0.0023805 | 1.3607e-05 | 2016 | 2016-01-19 | B | 9 | 0.0047611 | 2.7214e-05
8668728 | 2016-01-15 08:37 | 2016-01-15 11:21 | 164 | 1 | 164 | 164 | 161 | 0.0004959 | 161 | 0.00048683 | 3.0238e-06 | NAPA ID:15083 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 220102 & 220106 | Live Line Permit Make temporary 11kV break pole 226102. Access Permit. O/H Fit vibration dampers to 11kV Line adjacent pole 226106. Live Line Permit Remove temporary 11kV line break pole 226102. Te Puke Quarry Road, Papamoa. W/O30003844 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-01-15 | b | 0.00024341 | 1.512e-06 | 2016 | 2016-01-15 | B | 1 | 0.00048683 | 3.0238e-06
8668835 | 2016-01-20 08:55 | 2016-01-20 15:25 | 390 | 31 | 12090 | 390 | 387 | 0.036557 | 11997 | 0.036276 | 9.3737e-05 | NAPA ID:15113 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 722417 & 722423 | LLP install LLB @ pole 722417- AP replace Hv cable ground Tx & pole 722423 - LLP close LLB @ pole 722417. 7 Grey Street, Normanby. W/O30002200 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-01-20 | b | 0.018138 | 4.6868e-05 | 2016 | 2016-01-20 | B | 31 | 0.036276 | 9.3737e-05
8668881 | 2016-01-20 09:01 | 2016-01-20 15:51 | 410.6333 | 184 | 75556.5333 | 410.6333 | 407.6333 | 0.22846 | 75004.5333 | 0.2268 | 0.00055637 | NAPA ID:14384 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Miro Street Feeder CB C810 | Multilpe 11kv pole replacements. Queen Alexander Street, Miro Street, Opaki Street, King Edward Street, Masterton. W/O30013208 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-20 | b | 0.1134 | 0.00027819 | 2016 | 2016-01-20 | B | 184 | 0.2268 | 0.00055637
8670788 | 2015-12-15 18:42 | 2015-12-15 19:10 | 28 | 21 | 588 | 28 | 25 | 0.001778 | 525 | 0.0015875 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 855158 | Asplundh tree trimmers have spotted some conductor that is freyed while carrying out their work today. Needs inspection - may need to be defected or repaired urgently. Between Poles H2998 & 855158. Frayed Cunductor cut out small lenght of new conductor jo | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2015-12-15 | c | 0.0015875 | 6.3499e-05 | 2016 | 2015-12-15 | C | 21 | 0.0015875 | 6.3499e-05
8670835 | 2016-01-21 08:47 | 2016-01-21 14:34 | 347.2833 | 48 | 16669.6 | 347.2833 | 344.2833 | 0.050405 | 16525.6 | 0.049969 | 0.00014514 | NAPA ID:15628 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/181 | Remove old O/H Transformer T3/181 and replace with a new 200kVA Minipad Transformer. Connect new U/G 400v cables and 11kV cables to the existing O/H lines at T3/181. Work Location: Churcher Street, Feilding. W/O 30013890. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.024985 | 7.257e-05 | 2016 | 2016-01-21 | B | 48 | 0.049969 | 0.00014514
8670928 | 2015-12-15 19:20 | 2015-12-15 20:30 | 70 | 61 | 4270 | 70 | 67 | 0.012911 | 4087 | 0.012358 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835942 | Check for safety - Crossarm is broken and one line is hanging down. Advised hub of 999. Isolated at ABS S166 - Cross arm replaced at Pole 835942 and line rehung | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2015-12-15 | c | 0.012358 | 0.00018445 | 2016 | 2015-12-15 | C | 61 | 0.012358 | 0.00018445
8673148 | 2015-12-15 23:13 | 2015-12-16 03:55 | 282 | 61 | 17202 | 282 | 279 | 0.052015 | 17019 | 0.051461 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 217855 | Car V Pole Pole # 217855. NDR 40948. Pole replaced plus 1 x LV xarm. 1 x HV xarm. 4 x LV Insulators. 3 X HV Insulators. Straps and Bolts. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-12-15 | c | 0.051461 | 0.00018445 | 2016 | 2015-12-15 | C | 61 | 0.051461 | 0.00018445
8673606 | 2015-12-16 07:32 | 2015-12-16 08:20 | 47.8 | 4 | 191.2 | 47.8 | 44.8 | 0.00057814 | 179.2 | 0.00054186 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746675 | 7.33am - advise smc that the customer has been waiting for some time as the fax was not entered earlier this morning. 2 x 3amp fuse | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-16 | c | 0.00054186 | 1.2095e-05 | 2016 | 2015-12-16 | C | 4 | 0.00054186 | 1.2095e-05
8673687 | 2016-01-13 09:36 | 2016-01-13 13:15 | 219 | 168 | 36617.15 | 217.9592 | 214.9592 | 0.11072 | 36113.15 | 0.1092 | 0.00050799 | NAPA ID:14838 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P19146 | Replace 11KV pole P19146 install new ABS 10255. Halcombe Road. W/O30002718 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.054599 | 0.000254 | 2016 | 2016-01-13 | B | 168 | 0.1092 | 0.00050799
8673793 | 2016-01-21 09:50 | 2016-01-21 13:50 | 240 | 4 | 960 | 240 | 237 | 0.0029028 | 948 | 0.0028665 | 1.2095e-05 | NAPA ID:15571 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/12 | Replace the transformer x arms T3/12 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.0014333 | 6.048e-06 | 2016 | 2016-01-21 | B | 4 | 0.0028665 | 1.2095e-05
8673821 | 2016-01-20 08:58 | 2016-01-20 15:06 | 368.4167 | 27 | 9947.25 | 368.4167 | 365.4167 | 0.030078 | 9866.25 | 0.029833 | 8.1642e-05 | NAPA ID:14832 TP_KOPU GXP > KEREPEHI SUB > AWAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1421 | Replace H/V Crossarms, DDO's at TC1421. Work Location: 708 Wani Road, Kerepehi. W/O 30008218. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.014917 | 4.0821e-05 | 2016 | 2016-01-20 | B | 27 | 0.029833 | 8.1642e-05
8673882 | 2016-01-21 09:00 | 2016-01-21 15:40 | 400 | 51 | 20400 | 400 | 397 | 0.061685 | 20247 | 0.061222 | 0.00015421 | NAPA ID:15145 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformers C4085 & C4090, Poles 723383 & 723374 | Replace 2 x ground mount Tx's C4085 & C4090 & 2 x Hv Tx cable/fuse poles 723383 & 723374. Wybourne Road & Mason Road, Hawera. W/O30002200 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.030611 | 7.7106e-05 | 2016 | 2016-01-21 | B | 51 | 0.061222 | 0.00015421
8674249 | 2016-01-21 09:30 | 2016-01-21 14:30 | 300 | 5 | 1500 | 300 | 297 | 0.0045356 | 1485 | 0.0044903 | 1.5119e-05 | NAPA ID:15576 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/480 | Replace transformer cross arms at T3/480. Work location: Te Rakehou Road, Mt Stewart. W/O 30002718. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.0022451 | 7.559e-06 | 2016 | 2016-01-21 | B | 5 | 0.0044903 | 1.5119e-05
8674268 | 2016-01-19 09:16 | 2016-01-19 11:13 | 117 | 2 | 234 | 117 | 114 | 0.00070756 | 228 | 0.00068942 | 6.0475e-06 | NAPA ID:14012 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4841 | LLP: To replace the 11kV Fuses. AP: To replace the transformer & install a 400V Fuse Disconnector. Work Location: Campbell Road, Walton. W/O 10147849. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-19 | b | 0.00034471 | 3.024e-06 | 2016 | 2016-01-19 | B | 2 | 0.00068942 | 6.0475e-06
8674378 | 2016-01-20 09:16 | 2016-01-20 12:50 | 213.5 | 1 | 213.5 | 213.5 | 210.5 | 0.00064557 | 210.5 | 0.0006365 | 3.0238e-06 | NAPA ID:14013 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1887 | LLP: To replace the 11kV Fuses. AP: To replace the transformer & install a 400V Fuse Disconnector. Work Location: Kereone Road, Walton. W/O 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.00031825 | 1.512e-06 | 2016 | 2016-01-20 | B | 1 | 0.0006365 | 3.0238e-06
8674447 | 2016-01-25 08:51 | 2016-01-25 11:45 | 174 | 5 | 870 | 174 | 171 | 0.0026307 | 855 | 0.0025853 | 1.5119e-05 | NAPA ID:14032 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2325 | LLP: to replace the 11kV pin arm & 11kV Fuse arm. AP: To install a 3 phase Fuse disconnector & replace Cutouts. Work Location: Scherer Road, Matamata. W/O 10147849. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.0012927 | 7.559e-06 | 2016 | 2016-01-25 | B | 5 | 0.0025853 | 1.5119e-05
8674486 | 2016-01-20 08:40 | 2016-01-20 12:10 | 210 | 285 | 59850 | 210 | 207 | 0.18097 | 58995 | 0.17839 | 0.00086177 | NAPA ID:14389 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TD4-548 | To inspect HV cables maintain and repair as required. SD156,. Work Location: 2 Dingadee Street. W/O 30010107. | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.089193 | 0.00043089 | 2016 | 2016-01-20 | B | 285 | 0.17839 | 0.00086177
8674508 | 2016-01-25 13:57 | 2016-01-25 14:07 | 10 | 10 | 100 | 10 | 7 | 0.00030238 | 70 | 0.00021166 | 3.0238e-05 | NAPA ID:14033 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC647 | To install a 400V Fuse Disconnector. Landsdown Road, Matamata. W/O10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.00010583 | 1.5119e-05 | 2016 | 2016-01-25 | B | 10 | 0.00021166 | 3.0238e-05
8674512 | 2016-01-19 09:03 | 2016-01-19 14:48 | 345 | 5 | 1725 | 345 | 342 | 0.005216 | 1710 | 0.0051706 | 1.5119e-05 | NAPA ID:15259 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 387445 | Replace poles, hardware & conductor. Between SC2-124 and SC2-074. Work Location: Wainui South Road. W/O 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | b | 0.0025853 | 7.559e-06 | 2016 | 2016-01-19 | B | 5 | 0.0051706 | 1.5119e-05
8674633 | 2016-01-21 08:57 | 2016-01-21 11:38 | 160.7167 | 3 | 482.15 | 160.7167 | 157.7167 | 0.0014579 | 473.15 | 0.0014307 | 9.0713e-06 | NAPA ID:14014 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2204 | LLP: To replace the 11kV Fuses. AP: To replace the transformer & install a 400V Fuse Disconnector. Work Location: Maungakawa Road, Walton. W/O 10147849. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-21 | b | 0.00071535 | 4.536e-06 | 2016 | 2016-01-21 | B | 3 | 0.0014307 | 9.0713e-06
8696629 | 2015-12-16 11:35 | 2015-12-16 16:03 | 267.5833 | 3652 | 267.0167 | 0.073115 | -2.9269 | 0.00080739 | 0 | 0 | 0.011043 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | PAE7 | Paegaroa CB 7 Tripped and locked out. Flags were: Trip Flag AUFLS2. Resulted in the loss of supply to the Local service transformer at the Paengaroa Sub. Cause still being ascertained NOTE: Oddly 11kV CB's 3 & 5 also flagged on AUFL's, all in circuit Ear | F1,F2,F3 | TE MATAI1122-PONGAKAWA2007 33KV | TE MATAI | Tauranga | TP_TE MATAI | Eastern Electricity | POWERCO | 2015-12-16 | c | 0 | 0.011043 | 2016 | 2015-12-16 | C | 3652 | 0 | 0.011043
8696732 | 2016-01-21 10:07 | 2016-01-21 13:37 | 210 | 42 | 8820 | 210 | 207 | 0.02667 | 8694 | 0.026289 | 0.000127 | NAPA ID:15318 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4337 | Replace 11kV Cross Arms at various locations. Work Location: SH26, Te Aroha. W/O 30002440. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-21 | b | 0.013144 | 6.3499e-05 | 2016 | 2016-01-21 | B | 42 | 0.026289 | 0.000127
8697359 | 2016-01-28 13:34 | 2016-01-28 15:48 | 134 | 5 | 670 | 134 | 131 | 0.0020259 | 655 | 0.0019806 | 1.5119e-05 | NAPA ID:14046 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1932 | To install a 400V fuse Disconnector. Scherer Road, Matamata. W/O10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-28 | b | 0.00099028 | 7.559e-06 | 2016 | 2016-01-28 | B | 5 | 0.0019806 | 1.5119e-05
8697662 | 2016-01-28 09:50 | 2016-01-28 14:21 | 271 | 27 | 7317 | 271 | 268 | 0.022125 | 7236 | 0.02188 | 8.1642e-05 | NAPA ID:15069 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 704712 & 704743 | Run new wire. Main South Road, Warea. W/O30010591 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-28 | b | 0.01094 | 4.0821e-05 | 2016 | 2016-01-28 | B | 27 | 0.02188 | 8.1642e-05
8697664 | 2016-01-21 08:32 | 2016-01-21 15:16 | 403.6333 | 34 | 13723.5333 | 403.6333 | 400.6333 | 0.041497 | 13621.5333 | 0.041188 | 0.00010281 | NAPA ID:14798 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformers T1101 & T2572 | Replace 11Kv pole in 11Kv shutdown and transformer T700 & T1100. Lees Pakaraka Road. W/O30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.020594 | 5.1404e-05 | 2016 | 2016-01-21 | B | 34 | 0.041188 | 0.00010281
8697742 | 2016-01-27 14:01 | 2016-01-27 14:13 | 12 | 4 | 48 | 12 | 9 | 0.00014514 | 36 | 0.00010886 | 1.2095e-05 | NAPA ID:14039 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4869 | To install a 400V Fuse Disconnector. Work Location: 370 Landsdown Road, Matamata. W/O 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-27 | b | 5.4428e-05 | 6.048e-06 | 2016 | 2016-01-27 | B | 4 | 0.00010886 | 1.2095e-05
8697777 | 2016-01-27 09:19 | 2016-01-27 15:13 | 354.2667 | 57 | 20193.2 | 354.2667 | 351.2667 | 0.061059 | 20022.2 | 0.060542 | 0.00017235 | NAPA ID:15320 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1449, Pole C3387 | Replace 11 kV x Arms at various locations. Rawhiti Road, Te Aroha. W/O 30002440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-27 | b | 0.030271 | 8.6177e-05 | 2016 | 2016-01-27 | B | 57 | 0.060542 | 0.00017235
8697783 | 2016-01-21 09:51 | 2016-01-21 16:36 | 405 | 151 | 61155 | 405 | 402 | 0.18492 | 60702 | 0.18355 | 0.00045659 | NAPA ID:14387 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C810 | To replace multiple 11kV poles. Work Location: Queen Alexander Street, King Edward Street, Jordan Terrace, Masterton. W/O 30013208. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.091774 | 0.00022829 | 2016 | 2016-01-21 | B | 151 | 0.18355 | 0.00045659
8697792 | 2016-01-26 13:38 | 2016-01-26 14:15 | 37 | 5 | 185 | 37 | 34 | 0.0005594 | 170 | 0.00051404 | 1.5119e-05 | NAPA ID:14037 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4866 | To install a 400V Fuse Disconnector. Work Location: 305 Landsdown Road, Matamata. W/O 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-26 | b | 0.00025702 | 7.559e-06 | 2016 | 2016-01-26 | B | 5 | 0.00051404 | 1.5119e-05
8697859 | 2016-01-20 08:43 | 2016-01-20 15:24 | 401 | 28 | 3605 | 128.75 | 125.75 | 0.010901 | 3521 | 0.010647 | 8.4665e-05 | NAPA ID:14399 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > RIPPLE PLANT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE3-085 | Replacing transformer pole TE3-085 with new pole. Belk Road & Griffin Road, Tauranga. W/O30001481 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.0053233 | 4.2333e-05 | 2016 | 2016-01-20 | B | 28 | 0.010647 | 8.4665e-05
8701267 | 2015-12-17 00:39 | 2015-12-17 02:40 | 121.2667 | 204 | 22377.9167 | 109.6957 | 106.6957 | 0.067665 | 21765.9167 | 0.065815 | 0.00061685 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 9969/2 | Recloser 9969/2 on Kerepehi CB 5 feeder tripped to L/O. E/F flag. 1 x 1r requested. Line sectionalised & patrolled. No apparent fault found. All supply restored 02:40. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-17 | c | 0.065815 | 0.00061685 | 2016 | 2015-12-17 | C | 204 | 0.065815 | 0.00061685
8701482 | 2015-12-17 01:52 | 2015-12-17 04:48 | 176 | 258 | 38924.5667 | 150.8704 | 147.8704 | 0.1177 | 38150.5667 | 0.11536 | 0.00078013 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9643/2 | Recloser 9643/2 tripped to L/O. E/F flag. 2 x 1 r requested. Line sectionalised & patrolled. No apparent fault found. All supply restored 04:48. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-12-17 | c | 0.11536 | 0.00078013 | 2016 | 2015-12-17 | C | 258 | 0.11536 | 0.00078013
8701893 | 2015-12-17 04:25 | 2015-12-17 13:01 | 515.55 | 37 | 19075.35 | 515.55 | 512.55 | 0.057679 | 18964.35 | 0.057344 | 0.00011188 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Car v pole | Car V Pole reported by Fire services Event Number F1980498. People trapped in car eta required. ETA 10 min Two poles replaced but xarms and equipment reused | F3 | OXFORD ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-12-17 | c | 0.057344 | 0.00011188 | 2016 | 2015-12-17 | C | 37 | 0.057344 | 0.00011188
8701961 | 2015-12-17 05:51 | 2015-12-17 10:20 | 268.8333 | 92 | 5365.05 | 58.3158 | 55.3158 | 0.016223 | 5089.05 | 0.015388 | 0.00027819 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | N/A - NOT APPLICABLE | RS 8156 tripped and A/R B&C ph O/C. Branch on lines at Pole 841962. Removed with hot sticks. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-12-17 | c | 0.015388 | 0.00027819 | 2016 | 2015-12-17 | C | 92 | 0.015388 | 0.00027819
8702184 | 2015-12-17 06:12 | 2015-12-17 11:21 | 308.65 | 476 | 99348.0333 | 208.7144 | 205.7144 | 0.3004 | 97920.0333 | 0.29609 | 0.0014393 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 366067 | CB 4 Tripped O/C L/O. Car V Pole Reported by Fire Service Event Number F1980511 Line was isolated at ABS's 372 & 519 to replace pole 366067 hit by car. 1 x pole and all hardware, under ground cable, stay wire, conductor & support anchor. NDR: N100083 | F1 | BELL BLOCK 4 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-17 | c | 0.29609 | 0.0014393 | 2016 | 2015-12-17 | C | 476 | 0.29609 | 0.0014393
8703075 | 2015-12-17 06:50 | 2015-12-17 07:30 | 39.55 | 75 | 2966.25 | 39.55 | 36.55 | 0.0089692 | 2741.25 | 0.0082889 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8376 | Smoking line & a big bang heard. 6.51am advised Joanne at svs hub. Reload Reliven 2 x 25 A. Cause unknown | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-17 | c | 0.0082889 | 0.00022678 | 2016 | 2015-12-17 | C | 75 | 0.0082889 | 0.00022678
8705553 | 2015-12-17 08:36 | 2015-12-18 12:20 | 1663.9 | 1 | 1663.9 | 1663.9 | 1660.9 | 0.0050312 | 1660.9 | 0.0050222 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TE3 129 | 12:20 Generator connected , Disconnected 1622 18/12/15. 6.13pm Dianne from svs hub called and advised that a generator has been installed for customers and they will reattending tomorrow 18/12 morning to make full repairs. have completed Shay from site fo | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-17 | c | 0.0050222 | 3.024e-06 | 2016 | 2015-12-17 | C | 1 | 0.0050222 | 3.0238e-06
8708153 | 2016-01-20 09:08 | 2016-01-20 15:01 | 353 | 7 | 2471 | 353 | 350 | 0.0074717 | 2450 | 0.0074082 | 2.1166e-05 | NAPA ID:15210 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4740 & TC4963 & TC5908 | Replace 11kV X-arms between poles 854050 & T1567. Thames Coast Road, Thames. W/O30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.0037041 | 1.0583e-05 | 2016 | 2016-01-20 | B | 7 | 0.0074082 | 2.1166e-05
8709574 | 2016-01-22 09:00 | 2016-01-22 12:50 | 230 | 3 | 690 | 230 | 227 | 0.0020864 | 681 | 0.0020592 | 9.0713e-06 | NAPA ID:15215 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4740 & TC4963 & TC5908 | Reconductor Between Poles 854054 to T1569. Thames Coast Road, Thames. W/O30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-01-22 | b | 0.0010296 | 4.536e-06 | 2016 | 2016-01-22 | B | 3 | 0.0020592 | 9.0713e-06
8712435 | 2015-12-20 11:07 | 2015-12-20 11:45 | 38 | 1 | 9 | 9 | 6 | 2.7214e-05 | 6 | 1.8143e-05 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE6-158/1 | Job will require a HV electrician please. Affco Rangiuru site electrician Tony Gillgren has requested (via usual processes to Powerco) they require No.2 Engine room (Cool store) transformer TE6-158/1 to be tapped up to improve static voltage for installat | F1 | RANGIURU | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-12-20 | c | 1.8143e-05 | 3.024e-06 | 2016 | 2015-12-20 | C | 1 | 1.8143e-05 | 3.0238e-06
8714588 | 2016-01-29 08:49 | 2016-01-29 15:45 | 416 | 47 | 19552 | 416 | 413 | 0.059121 | 19411 | 0.058694 | 0.00014212 | NAPA ID:14471 TP_HINUERA GXP > PUTARURU SUB > TAUMANGI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles M1778 & M1816 | Pole M13315 (888) - Replace pole, ABS, all crossarms. M1778 - replace LV crossarm. M1816, M1817 & M1818 - replace cross arms. M1838, M1837 & M1836 replace crossarms. M1844 - remove 11kV span and replace crossarms. M13332 - replace pole and crossarms. 199, | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-29 | b | 0.029347 | 7.1058e-05 | 2016 | 2016-01-29 | B | 47 | 0.058694 | 0.00014212
8715184 | 2016-01-21 09:20 | 2016-01-21 15:15 | 355 | 9 | 3195 | 355 | 352 | 0.0096609 | 3168 | 0.0095793 | 2.7214e-05 | NAPA ID:14840 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | O1338 | Replace Poles O1337/O1338. Work Location: Ngataipua Road, Orongo. W/O 30010108. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-21 | b | 0.0047896 | 1.3607e-05 | 2016 | 2016-01-21 | B | 9 | 0.0095793 | 2.7214e-05
8715228 | 2016-01-13 10:56 | 2016-01-13 13:37 | 161 | 40 | 6440 | 161 | 158 | 0.019473 | 6320 | 0.01911 | 0.00012095 | NAPA ID:15473 TP_OPUNAKE GXP > TASMAN SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformers 5585E & T3215 | Replace spalling 11Kv double circuit pole 713536. 4566 South Road, Opunake. W/O30001367 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-01-13 | b | 0.0095551 | 6.0475e-05 | 2016 | 2016-01-13 | B | 40 | 0.01911 | 0.00012095
8715774 | 2016-01-25 09:45 | 2016-01-25 12:15 | 150 | 7 | 1050 | 150 | 147 | 0.0031749 | 1029 | 0.0031114 | 2.1166e-05 | NAPA ID:15284 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC812 | Isolate transformer TC812 and cut away 1 span LV O/H line from poles P0436 and P0435. Install double termination cross arm on pole P0435. Install 50kVA transformer on pole P0436 to solve power quality issue on existing transformer TC812. Work Location: 47 | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.0015557 | 1.0583e-05 | 2016 | 2016-01-25 | B | 7 | 0.0031114 | 2.1166e-05
8717635 | 2015-12-18 03:06 | 2015-12-18 03:23 | 17 | 59 | 1003 | 17 | 14 | 0.0030328 | 826 | 0.0024976 | 0.0001784 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5734 | Replaced 1x 20Amp HV Fuse Link. Fused ABS opened to allow this, hence 3 phase shutdown | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-12-18 | c | 0.0024976 | 0.0001784 | 2016 | 2015-12-18 | C | 59 | 0.0024976 | 0.0001784
8717711 | 2015-12-18 04:14 | 2015-12-18 06:25 | 131.45 | 1 | 131.45 | 131.45 | 128.45 | 0.00039747 | 128.45 | 0.0003884 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | T1347 | Replaced 2x15Amp Fuse Links at Transformer T1347. Dead possum found at base of pole | F3 | ESSEX ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2015-12-18 | c | 0.0003884 | 3.024e-06 | 2016 | 2015-12-18 | C | 1 | 0.0003884 | 3.0238e-06
8718372 | 2015-12-18 06:12 | 2015-12-18 07:15 | 62.6833 | 43 | 2695.3833 | 62.6833 | 59.6833 | 0.0081502 | 2566.3833 | 0.0077601 | 0.00013002 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 586 | 2 x 20 amp fuse unknown reason | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-18 | c | 0.0077601 | 0.00013002 | 2016 | 2015-12-18 | C | 43 | 0.0077601 | 0.00013002
8718876 | 2016-01-22 09:30 | 2016-01-22 13:00 | 210 | 1 | 210 | 210 | 207 | 0.00063499 | 207 | 0.00062592 | 3.0238e-06 | NAPA ID:15252 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/146 | To cut in live line gap at pole p30089 and change two larch poles to 11m busck poles close live line gap. Glen Ora Road. W/O10162794 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-22 | b | 0.00031296 | 1.512e-06 | 2016 | 2016-01-22 | B | 1 | 0.00062592 | 3.0238e-06
8719003 | 2016-01-16 09:15 | 2016-01-16 14:15 | 300 | 56 | 16800 | 300 | 297 | 0.050799 | 16632 | 0.050291 | 0.00016933 | NAPA ID:15110 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/426 | To change red tagged 11kv pole. Sedcole Street, Pahiatua. W/O30001378 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-16 | b | 0.025146 | 8.4665e-05 | 2016 | 2016-01-16 | B | 56 | 0.050291 | 0.00016933
8720588 | 2015-12-18 10:20 | 2015-12-18 13:10 | 170.2667 | 1 | 170.2667 | 170.2667 | 167.2667 | 0.00051485 | 167.2667 | 0.00050577 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 1759 | 2 X 3 Amp Fuses Bird Strike | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-18 | c | 0.00050577 | 3.024e-06 | 2016 | 2015-12-18 | C | 1 | 0.00050577 | 3.0238e-06
8720892 | 2016-01-26 08:15 | 2016-01-26 15:17 | 422.1333 | 19 | 8020.5333 | 422.1333 | 419.1333 | 0.024252 | 7963.5333 | 0.02408 | 5.7451e-05 | NAPA ID:15368 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 778385 | Replace 11kV poles and hardware from poles 778300 to 778385. Work Location: Parapara Road. W/O 30002305. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-01-26 | b | 0.01204 | 2.8726e-05 | 2016 | 2016-01-26 | B | 19 | 0.02408 | 5.7451e-05
8721500 | 2016-01-26 09:30 | 2016-01-26 15:29 | 359 | 82 | 29036 | 354.0976 | 351.0976 | 0.087798 | 28790 | 0.087054 | 0.00024795 | NAPA ID:15530 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 831731 | Replace 11kv pole. Matahiwi Road, Masterton. W/O10159904 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-26 | b | 0.043527 | 0.00012397 | 2016 | 2016-01-26 | B | 82 | 0.087054 | 0.00024795
8724770 | 2015-12-18 18:26 | 2015-12-18 19:40 | 74.7333 | 1916 | 60772.0167 | 31.7182 | 28.7182 | 0.18376 | 55024.0167 | 0.16638 | 0.0057935 |  | 33 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC3-083 | CB 202 Greerton O/C, CB 82 Aomgatete CB62 O/C REV, CB 36 & Cb 38 L/O at Omokaroa. Back feed CB 4 Found trany TC3-083 hit by lightening, Restored 33kv & T6 & bus at Omokaroa & CB 2 & CB 6. Replaced trany TC3-083 & relivened | F1,F2,F3 | GREERTON202-AONGATETE82 33KV | TAURANGA 31 | Tauranga | GREERTON | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.16638 | 0.0057935 | 2016 | 2015-12-18 | C | 1916 | 0.16638 | 0.0057935
8725401 | 2015-12-18 18:54 | 2015-12-18 20:05 | 70.9667 | 3 | 212.9 | 70.9667 | 67.9667 | 0.00064376 | 203.9 | 0.00061654 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc614 | 2 x 3 amp fuse replaced | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.00061655 | 9.071e-06 | 2016 | 2015-12-18 | C | 3 | 0.00061654 | 9.0713e-06
8726283 | 2015-12-18 19:54 | 2015-12-18 21:02 | 68.7833 | 1 | 68.7833 | 68.7833 | 65.7833 | 0.00020798 | 65.7833 | 0.00019891 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1998 | 2 x 6amp fuses replaced | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.00019891 | 3.024e-06 | 2016 | 2015-12-18 | C | 1 | 0.00019891 | 3.0238e-06
8726439 | 2015-12-18 23:45 | 2015-12-19 00:44 | 59 | 15 | 885 | 59 | 56 | 0.002676 | 840 | 0.00254 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | td3-008 | 2 X DDO units replaced on single phase trany TD3-008. 2 x 100amp LV fuses replaced | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.00254 | 4.5356e-05 | 2016 | 2015-12-18 | C | 15 | 0.00254 | 4.5356e-05
8726521 | 2015-12-18 20:40 | 2015-12-18 23:58 | 197.6333 | 1 | 197.6333 | 197.6333 | 194.6333 | 0.0005976 | 194.6333 | 0.00058852 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc2499 | TC2499 2 x3 amp fuses replaced | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.00058853 | 3.024e-06 | 2016 | 2015-12-18 | C | 1 | 0.00058852 | 3.0238e-06
8726554 | 2015-12-18 20:48 | 2015-12-18 22:43 | 114.7667 | 1 | 114.7667 | 114.7667 | 111.7667 | 0.00034703 | 111.7667 | 0.00033796 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | possible related to 872652 | 2 x 3amp fuses replaced | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-18 | c | 0.00033796 | 3.024e-06 | 2016 | 2015-12-18 | C | 1 | 0.00033796 | 3.0238e-06
8727399 | 2015-12-19 16:46 | 2015-12-19 19:05 | 139 | 3 | 417 | 139 | 136 | 0.0012609 | 408 | 0.0012337 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tp1460 | Transformer TP1460 faulty & needs replacement Isolated at fuses FP465 replace trany & relivened. NDR 048064 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-12-19 | c | 0.0012337 | 9.071e-06 | 2016 | 2015-12-19 | C | 3 | 0.0012337 | 9.0713e-06
8727655 | 2015-12-19 03:50 | 2015-12-19 10:18 | 388.0333 | 1114 | 226412.6667 | 203.243 | 200.243 | 0.68462 | 223070.6667 | 0.67451 | 0.0033685 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 214611 | CB 4 L/O on O/C & E/F Reported car verses pole corner of Girven & Grenada. Isolated between 9007/3, SC5-017, SC5-003, SC5-028 & SC5-004. Backfeed rest of area Replaced pole & relivened. Materials 1 x pole, 1 x H/V arm complete, 2 x L/V arms complete all L | F3 | ARATAKI | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 2015-12-19 | c | 0.67451 | 0.0033685 | 2016 | 2015-12-19 | C | 1114 | 0.67451 | 0.0033685
8729007 | 2015-12-19 05:41 | 2015-12-19 07:18 | 96.6333 | 25 | 2415.8333 | 96.6333 | 93.6333 | 0.0073049 | 2340.8333 | 0.0070781 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 4957 | 2 HT fuses tripped, Reloaded OK (10A). Birdstrike | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2015-12-19 | c | 0.0070781 | 7.5594e-05 | 2016 | 2015-12-19 | C | 25 | 0.0070781 | 7.5594e-05
8729049 | 2015-12-19 06:19 | 2015-12-19 07:28 | 68.75 | 9 | 618.75 | 68.75 | 65.75 | 0.001871 | 591.75 | 0.0017893 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8295 | 2 HT fuses tripped. (8A). Reloaded OK. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-19 | c | 0.0017893 | 2.7214e-05 | 2016 | 2015-12-19 | C | 9 | 0.0017893 | 2.7214e-05
8729083 | 2015-12-19 07:11 | 2015-12-19 10:21 | 190.1833 | 464 | 29398.7 | 63.3593 | 60.3593 | 0.088895 | 28006.7 | 0.084686 | 0.001403 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/499 | Tripping on Milson CB5 on O/C phase B E/F. Fault traced to defective 11kV Cable between Sw/Gear 10122/2 and 1009/4. (Backfeed at ABS D13). Isolation made between Sw/gear and Cables tested. Fault between T6/499 and Sw/Gear 10091/4. Cables disconnected and | F2 | FAIRS RD | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-12-19 | c | 0.084686 | 0.001403 | 2016 | 2015-12-19 | C | 464 | 0.084686 | 0.001403
8729679 | 2015-12-19 08:36 | 2015-12-19 09:35 | 58.8 | 2 | 117.6 | 58.8 | 55.8 | 0.00035559 | 111.6 | 0.00033745 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 11001 | Tripping on 2 HT fuses at 11001 - (10A Rating). Birdstrike. | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-12-19 | c | 0.00033745 | 6.048e-06 | 2016 | 2015-12-19 | C | 2 | 0.00033745 | 6.0475e-06
8730882 | 2015-12-19 11:02 | 2015-12-19 12:17 | 74.95 | 1 | 74.95 | 74.95 | 71.95 | 0.00022663 | 71.95 | 0.00021756 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6693 | OMS (GIS) Issue with location. Fault not at 1181 but 2 fuses tripped down the Road at 6693. Reloaded OK (10A). OMS job linked. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-19 | c | 0.00021756 | 3.024e-06 | 2016 | 2015-12-19 | C | 1 | 0.00021756 | 3.0238e-06
8734132 | 2015-12-20 16:45 | 2015-12-20 19:00 | 135 | 1 | 135 | 135 | 132 | 0.00040821 | 132 | 0.00039914 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF8-045 | Faulty transformer TF8-045 isolated under self issue AP to change. Replaced transformer & returned to service. Materials 1 x transformer, 3 x 6A H/V fuses, 1 x 63A Hrc fuse & base | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-12-20 | c | 0.00039914 | 3.024e-06 | 2016 | 2015-12-20 | C | 1 | 0.00039914 | 3.0238e-06
8735512 | 2015-12-21 07:18 | 2015-12-21 08:43 | 84.6 | 16 | 1353.6 | 84.6 | 81.6 | 0.004093 | 1305.6 | 0.0039478 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5265 | *** 15 Carrs Road - tx 4125T possibly relates *** advised SMC to tell FM to go past fuse # 5265. Found 2 x 10 amp fuse. Unknown cause. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-12-21 | c | 0.0039478 | 4.838e-05 | 2016 | 2015-12-21 | C | 16 | 0.0039478 | 4.838e-05
8735554 | 2015-12-21 07:32 | 2015-12-21 07:44 | 12 | 138 | 1656 | 12 | 9 | 0.0050073 | 1242 | 0.0037555 | 0.00041728 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | cb 6 | CB 6 - B and C PH O/C | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2015-12-21 | c | 0.0037555 | 0.00041728 | 2016 | 2015-12-21 | C | 138 | 0.0037555 | 0.00041728
8737168 | 2016-01-27 10:10 | 2016-01-27 15:40 | 330.4167 | 21 | 6938.75 | 330.4167 | 327.4167 | 0.020981 | 6875.75 | 0.020791 | 6.3499e-05 | NAPA ID:14454 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kopane Feeder CB22 | Run approximately 1200mtrs of new conductor. Kaimatarau Road. W/O30011145 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-27 | b | 0.010395 | 3.1749e-05 | 2016 | 2016-01-27 | B | 21 | 0.020791 | 6.3499e-05
8737619 | 2016-01-22 10:40 | 2016-01-22 16:20 | 340 | 1 | 340 | 340 | 337 | 0.0010281 | 337 | 0.001019 | 3.0238e-06 | NAPA ID:14948 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 737383 | Replace 33kV conductor/poles over 11kV lines pole 737383. Work Location: 548 East Road, Stratford. W/O 30010304 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-01-22 | b | 0.0005095 | 1.512e-06 | 2016 | 2016-01-22 | B | 1 | 0.001019 | 3.0238e-06
8738408 | 2015-12-21 14:11 | 2015-12-23 11:25 | 2713.35 | 41 | 13378.0667 | 326.2943 | 323.2943 | 0.040452 | 13255.0667 | 0.04008 | 0.00012397 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | Maewa rd fielding | Line break created at Pole P30174 to isolate on request of the fire service due to fire at Saw Mill. Generator connected to T3/543.nz fire serve request attendance. Phone Jo explained why going Powerco Requested Generator to be installed at Transformer T | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-12-21 | c | 0.04008 | 0.00012397 | 2016 | 2015-12-21 | C | 41 | 0.04008 | 0.00012397
8739699 | 2016-01-28 08:37 | 2016-01-28 11:02 | 145.0167 | 19 | 2755.3167 | 145.0167 | 142.0167 | 0.0083314 | 2698.3167 | 0.0081591 | 5.7451e-05 | NAPA ID:15267 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 7 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Transformer G127 | 1Yr maintenance on Magnefix G127 A/B/C/T. Work Location: Waldergrave Street. W/O 30003942. | F3 | PASCAL ST 7 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-01-28 | b | 0.0040795 | 2.8726e-05 | 2016 | 2016-01-28 | B | 19 | 0.0081591 | 5.7451e-05
8739711 | 2016-01-28 08:51 | 2016-01-28 14:47 | 356.2167 | 19 | 6768.1167 | 356.2167 | 353.2167 | 0.020465 | 6711.1167 | 0.020293 | 5.7451e-05 | NAPA ID:15494 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 778300 & 778385 | Replace 11kv poles and Hardware From poles 778300 to 778385. Parapara Road. W/O30002305 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-01-28 | b | 0.010146 | 2.8726e-05 | 2016 | 2016-01-28 | B | 19 | 0.020293 | 5.7451e-05
8741378 | 2016-01-28 09:30 | 2016-01-28 13:44 | 253.6 | 7 | 1775.2 | 253.6 | 250.6 | 0.0053678 | 1754.2 | 0.0053043 | 2.1166e-05 | NAPA ID:15313 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P06649 | Replace burnt off S/W poles. Korora Road. W/O30017084 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-28 | b | 0.0026521 | 1.0583e-05 | 2016 | 2016-01-28 | B | 7 | 0.0053043 | 2.1166e-05
8741394 | 2016-01-29 10:13 | 2016-01-29 13:06 | 172.7 | 7 | 1208.9 | 172.7 | 169.7 | 0.0036554 | 1187.9 | 0.0035919 | 2.1166e-05 | NAPA ID:15316 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P06670 | replace burnt off S/W poles. Kororoa Road. W/O30017084 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-29 | b | 0.001796 | 1.0583e-05 | 2016 | 2016-01-29 | B | 7 | 0.0035919 | 2.1166e-05
8741405 | 2015-12-21 17:15 | 2015-12-21 17:42 | 27.4833 | 108 | 2968.2 | 27.4833 | 24.4833 | 0.0089751 | 2644.2 | 0.0079954 | 0.00032657 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W1642 | Allen Miles from north power reporting bolt out of cross arm and cross arm is loose between poles w1639 and w1643. David is the property owner, may need to contact him for access to pole on his property. 07 866 3152. 3.38pm Pole is 11kv pole, on H structu | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2015-12-21 | c | 0.0079954 | 0.00032657 | 2016 | 2015-12-21 | C | 108 | 0.0079954 | 0.00032657
8743026 | 2015-12-21 21:33 | 2015-12-21 23:00 | 86.5667 | 16 | 1385.0667 | 86.5667 | 83.5667 | 0.0041881 | 1337.0667 | 0.004043 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4174 | Replaced 2 x 10A H/V, O/H fuses (unknown cause happens frequently) Needs investigation for permanent fix. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-21 | c | 0.004043 | 4.838e-05 | 2016 | 2015-12-21 | C | 16 | 0.004043 | 4.838e-05
8743033 | 2015-12-21 20:40 | 2015-12-21 20:44 | 4 | 1 | 4 | 4 | 1 | 1.2095e-05 | 1 | 3.0238e-06 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | 1755N | Reports of Low voltage in area. This transformer 1755N has extra load added (Chicken sheds, Voltage at 216 P-N). Transformer isolated and raised one tap (Position 4). Voltage now 235V P-N. Dispatch advised of quality issue, to be investigated. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-21 | c | 3.024e-06 | 3.024e-06 | 2016 | 2015-12-21 | C | 1 | 3.0238e-06 | 3.0238e-06
8743043 | 2015-12-21 21:15 | 2015-12-21 21:21 | 6 | 1 | 6 | 6 | 3 | 1.8143e-05 | 3 | 9.0713e-06 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | 1756N | Reports of Low voltage in area. This transformer 1756N has extra load added (Chicken sheds, Voltage at 2120 P-N). Transformer isolated and raised one tap (Position 4). Voltage now 235V P-N. Dispatch advised of quality issue, to be investigated. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-21 | c | 9.071e-06 | 3.024e-06 | 2016 | 2015-12-21 | C | 1 | 9.0713e-06 | 3.0238e-06
8743124 | 2015-12-21 22:42 | 2015-12-22 00:17 | 94.4667 | 1089 | 23337.9333 | 21.4306 | 18.4306 | 0.070568 | 20070.9333 | 0.06069 | 0.0032929 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | Rata Sub | Tripping on Arahina 33kV CB3086 causing loss of supply to Rata Sub. (Flags Phase A-B-C O/C).Hunterville feeder backfed via Pukepapa CB1133. Feeder patrolled and Rata Sub checked. Remnants of Birds nests found in Sub. All relivened OK. | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-12-21 | c | 0.06069 | 0.0032929 | 2016 | 2015-12-21 | C | 1089 | 0.06069 | 0.0032929
8744812 | 2015-12-22 09:10 | 2015-12-22 09:47 | 37 | 5 | 185 | 37 | 34 | 0.0005594 | 170 | 0.00051404 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 837588 | 7.51am - advise smc. Advised fire comms 048010812 ETA is 1 hr. Isolated at Fuses 7870 and branch cleared using hot sticks. Branch on lines near Pole 837588. NDR #37930. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-12-22 | c | 0.00051404 | 1.5119e-05 | 2016 | 2015-12-22 | C | 5 | 0.00051404 | 1.5119e-05
8746130 | 2016-01-25 05:08 | 2016-01-25 15:58 | 650 | 100 | 3600 | 36 | 33 | 0.010886 | 3300 | 0.0099784 | 0.00030238 | NAPA ID:15361 TP_HINUERA GXP > TOWER ROAD SUB > RAWHITI AVE | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3793 & TC1713 | To remove an 11kV cable from TC3793 to IC2026, Relocate the cable to New transformer TP2902, Liven TP2902. Refer to Day 1 of the attached Methodology. Rawhiti Avenue, Matamata. W/O30002528 | F3 | RAWHITI AVE | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.0049892 | 0.00015119 | 2016 | 2016-01-25 | B | 100 | 0.0099784 | 0.00030238
8746417 | 2016-01-27 09:15 | 2016-01-27 13:40 | 265 | 98 | 25970 | 265 | 262 | 0.078527 | 25676 | 0.077638 | 0.00029633 | NAPA ID:15573 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1888N | Moturoa 5 backfeed tie installation as part Project IR 7908. Shut 1 will be to cut existing HV cable at transformer 1888N (feeding from transformer 1920N) and joint this cable to new cable and to install and connect new HV cable to transformer 1888N. Nex | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-27 | b | 0.038819 | 0.00014816 | 2016 | 2016-01-27 | B | 98 | 0.077638 | 0.00029633
8746490 | 2015-12-22 10:16 | 2015-12-22 14:25 | 248.7833 | 7 | 1741.4833 | 248.7833 | 245.7833 | 0.0052658 | 1720.4833 | 0.0052023 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | temp 30 | Please also check 8746729 - 1550 Coast Road, Pongaroa. 2 x 20amp fuse poss under rated | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-12-22 | c | 0.0052023 | 2.1166e-05 | 2016 | 2015-12-22 | C | 7 | 0.0052023 | 2.1166e-05
8746574 | 2016-01-28 09:30 | 2016-01-28 14:47 | 317 | 44 | 13948 | 317 | 314 | 0.042175 | 13816 | 0.041776 | 0.00013305 | NAPA ID:15593 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Moturoa 5 backfeed tie isstallation as part Project IR 7908. Shut 2 is the next step after Shut 1 on NAPA 15573 Shut 2 consist of 3 steps. Step 1 is to cut live line break at pole 750460. Step 2 will be to change pole 750452 with a double pole with a new | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-28 | b | 0.020888 | 6.6523e-05 | 2016 | 2016-01-28 | B | 44 | 0.041776 | 0.00013305
8746685 | 2016-01-26 08:49 | 2016-01-26 10:59 | 130 | 3 | 390 | 130 | 127 | 0.0011793 | 381 | 0.0011521 | 9.0713e-06 | NAPA ID:14036 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4824 | LLP: To replace the 11kV Fuse arm & Fuses. AP: To install a 400V Fuse Disconnector. Work Location: 109 Scherer Road, Matamata. W/O 10147849. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-26 | b | 0.00057603 | 4.536e-06 | 2016 | 2016-01-26 | B | 3 | 0.0011521 | 9.0713e-06
8746712 | 2016-01-27 08:47 | 2016-01-27 10:45 | 118 | 3 | 354 | 118 | 115 | 0.0010704 | 345 | 0.0010432 | 9.0713e-06 | NAPA ID:14038 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1008 | LLP: to replace the 11kV Fuse Arm. AP: to replace the 400V Arm & install a 400V Fuse Disconnector. Work Location: 16 Duncan Road, Matamata. W/O 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-27 | b | 0.0005216 | 4.536e-06 | 2016 | 2016-01-27 | B | 3 | 0.0010432 | 9.0713e-06
8746746 | 2016-01-28 08:55 | 2016-01-28 11:45 | 170 | 5 | 850 | 170 | 167 | 0.0025702 | 835 | 0.0025248 | 1.5119e-05 | NAPA ID:14044 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4827 | LLP: To replace the 11kV Pin arm & 11kV Fuse Arm. AP: to replace the 400V pin arm & install a 400V Fuse Disconnector. Work Location: Scherer Road, Matamata. W/O 10147849. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-28 | b | 0.0012624 | 7.559e-06 | 2016 | 2016-01-28 | B | 5 | 0.0025248 | 1.5119e-05
8747047 | 2015-12-22 13:52 | 2015-12-22 14:10 | 18 | 10 | 180 | 18 | 15 | 0.00054428 | 150 | 0.00045356 | 3.0238e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G181/T | This was part of OMS 8746849 that was closed off by control before related jobs were linked up. These were partial supply so did not roll up to the main job (Single Fuse found blown at Fuses G181/T - used 1 x 25 amp HV fuse - no cause found) | F3 | KEITH ST 21 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 2015-12-22 | c | 0.00045356 | 3.0238e-05 | 2016 | 2015-12-22 | C | 10 | 0.00045356 | 3.0238e-05
8748454 | 2015-12-22 14:43 | 2015-12-22 17:50 | 186.9167 | 609 | 37253.3333 | 61.1713 | 58.1713 | 0.11265 | 35426.3333 | 0.10712 | 0.0018415 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | RS 687 | CB 5 Tripped No Flags - Comms Tech on site at RS 687 and reported burnt off jumper - Reported jumper burnt off on feed side - Back feed installed via VS912, resulted in trip on RS912 - Back feed removed - Faultman arrived on site and Isolation's put in pl | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2015-12-22 | c | 0.10712 | 0.0018415 | 2016 | 2015-12-22 | C | 609 | 0.10712 | 0.0018415
8758605 | 2015-12-22 19:29 | 2015-12-23 02:04 | 395.1667 | 574 | 41262.8333 | 71.8865 | 68.8865 | 0.12477 | 39540.8333 | 0.11956 | 0.0017356 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222535 | CB 3 Trip. E/F L/O. Feeder Sectionalised and line found down between Poles 222535 and 222536. Whilst sectionalising and to save further outages, once it was known that there was no fault beyond Recloser 9147 that part of the feeder was offloaded to Pongak | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-12-22 | c | 0.11956 | 0.0017356 | 2016 | 2015-12-22 | C | 574 | 0.11956 | 0.0017356
8783749 | 2015-12-23 09:33 | 2015-12-23 09:35 | 2.6 | 327 | 850.2 | 2.6 | -0.4 | 0.0025708 | 0 | 0 | 0.00098877 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | 01381 | fax received. SR# tmre0001104. At the beginning of Orongo Road there are 2 chains that is hanging on the network lines. Trucks may drive under the lines and pull it down. Power was affected last night but not at the moment. Customer advised a cherry picke | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-23 | c | 0 | 0.00098877 | 2016 | 2015-12-23 | C | 327 | 0 | 0.00098877
8784314 | 2016-01-22 07:30 | 2016-01-22 14:58 | 448 | 42 | 6507 | 154.9286 | 151.9286 | 0.019676 | 6381 | 0.019295 | 0.000127 | NAPA ID:14992 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10214 | Start of stage 2c after stage 2b complete on NAPA 14990. Terminate 11kv line at pole 341159. Remove ABS 10214/1 and 11kv line between pole 341159 and 341105 from network. Remove ABS K21 from the network. Terminate cable from 10275/2 to pole 341105. Test a | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-22 | b | 0.0096473 | 6.3499e-05 | 2016 | 2016-01-22 | B | 42 | 0.019295 | 0.000127
8794821 | 2015-12-23 15:39 | 2015-12-23 16:16 | 36.85 | 33 | 1216.05 | 36.85 | 33.85 | 0.003677 | 1117.05 | 0.0033777 | 9.9784e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 227727 | The spur line feeding Transformer TF8-048 was cut away from the main line at Pole 227727 after a feeder tripping in the winter and was cut away from the main line (OMS 7239480). The lines are being repaired now and we require a crew to isolate the main li | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-12-23 | c | 0.0033777 | 9.9784e-05 | 2016 | 2015-12-23 | C | 33 | 0.0033777 | 9.9784e-05
8795085 | 2015-12-23 15:04 | 2015-12-23 17:04 | 120.1667 | 4 | 216.3 | 54.075 | 51.075 | 0.00065404 | 204.3 | 0.00061775 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 704890 | Replaced 2x 6Amp HV Links due to Seagull contacting lines. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2015-12-23 | c | 0.00061775 | 1.2095e-05 | 2016 | 2015-12-23 | C | 4 | 0.00061775 | 1.2095e-05
8797898 | 2015-12-23 21:27 | 2015-12-23 22:52 | 84.2333 | 1431 | 33664.1 | 23.5249 | 20.5249 | 0.10179 | 29371.1 | 0.088811 | 0.004327 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G254D | CR to dig up and rejoin the cable ( this may take a couple of days to complete) Chris has located the cable fault, to be done on Tues 29/12. Red pin 151215. Scheduled for 13.01.16 NAPA 15938. | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-12-23 | c | 0.088811 | 0.004327 | 2016 | 2015-12-23 | C | 1431 | 0.088811 | 0.004327
8801138 | 2015-12-23 23:59 | 2015-12-24 02:00 | 121.3667 | 54 | 6553.8 | 121.3667 | 118.3667 | 0.019817 | 6391.8 | 0.019327 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C269 | OYT RS C269/2 found tripped closed in on operation, faultman requested to check Sectionliser C213 as well. This was found to be closed. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-12-23 | c | 0.019327 | 0.00016328 | 2016 | 2015-12-23 | C | 54 | 0.019327 | 0.00016328
8802202 | 2015-12-24 08:12 | 2015-12-24 13:23 | 311.1667 | 836 | 83232.6667 | 99.5606 | 96.5606 | 0.25168 | 80724.6667 | 0.24409 | 0.0025279 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SD5-135 | CB 2 L/O No flags. Sectionalised & found faulty cable between SD5-135 & Sw/Gear 9031/3. Disconnected cable at SD5-135 & relivened | F3 | DOMAIN RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-12-24 | c | 0.24409 | 0.0025279 | 2016 | 2015-12-24 | C | 836 | 0.24409 | 0.0025279
8803441 | 2015-12-24 12:31 | 2015-12-24 14:22 | 111 | 206 | 22866 | 111 | 108 | 0.069141 | 22248 | 0.067273 | 0.00062289 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 701253 | Car vs Pole. Replaced pole 701253, & crossarms 1xhv & 1xlv complete. NDR 1084 | F3 | BROOKLANDS 9 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-12-24 | c | 0.067273 | 0.0006229 | 2016 | 2015-12-24 | C | 206 | 0.067273 | 0.00062289
8805072 | 2015-12-24 18:56 | 2015-12-24 19:04 | 8 | 1 | 8 | 8 | 5 | 2.419e-05 | 5 | 1.5119e-05 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | SE6-075 | Arrangements made between Affco electical staff & Downers to alter tap positions on transformers TE6-151/1 & 2. Transformer isolated at Sw/gear SE6-075 to carry out tap changes. All supply restored on completion. Chris Maloni was Downer staff who attended | F1 | RANGIURU | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2015-12-24 | c | 1.5119e-05 | 3.024e-06 | 2016 | 2015-12-24 | C | 1 | 1.5119e-05 | 3.0238e-06
8805453 | 2015-12-25 01:13 | 2015-12-25 02:52 | 99.5667 | 903 | 24354.1833 | 26.9703 | 23.9703 | 0.073641 | 21645.1833 | 0.06545 | 0.0027305 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 3086 | CB 3086 Tripped b Ph O/C E/F - Rata sub backfeed and line patrolled with no fault found | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2015-12-25 | c | 0.06545 | 0.0027305 | 2016 | 2015-12-25 | C | 903 | 0.06545 | 0.0027305
8807781 | 2015-12-25 16:19 | 2015-12-25 16:38 | 19.4333 | 215 | 3969.6167 | 18.4633 | 15.4633 | 0.012003 | 3324.6167 | 0.010053 | 0.00065011 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | I1047 | Trees in lines Sparking. Isolated CB 1 between ABS IC588, IC1280 & 9285/4. Isolated CB 2 between ABS 1189 & IC3163. Cut trees from line at pole I1047 & relivened. NDR 048040 | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-25 | c | 0.010053 | 0.00065011 | 2016 | 2015-12-25 | C | 215 | 0.010053 | 0.00065011
8821519 | 2015-12-25 17:33 | 2015-12-25 18:22 | 49.8333 | 684 | 34086 | 49.8333 | 46.8333 | 0.10307 | 32034 | 0.096863 | 0.0020683 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB9 | Section of cable from cb9 to pole P4 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2015-12-25 | c | 0.096863 | 0.0020683 | 2016 | 2015-12-25 | C | 684 | 0.096863 | 0.0020683
8822776 | 2015-12-25 17:44 | 2015-12-25 18:37 | 53.2333 | 1 | 53.2333 | 53.2333 | 50.2333 | 0.00016096 | 50.2333 | 0.00015189 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | GIS Wrong part of Feeder Fault | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-12-25 | c | 0.00015189 | 3.024e-06 | 2016 | 2015-12-25 | C | 1 | 0.00015189 | 3.0238e-06
8822988 | 2015-12-25 22:25 | 2015-12-25 23:10 | 45.55 | 1331 | 31171.8167 | 23.4198 | 20.4198 | 0.094256 | 27178.8167 | 0.082182 | 0.0040246 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | P21560 | CB24 tipped on A ph, O/C and E/F. Report from police of loud bang at Marlborough. Found lantern on top of pole P21560. Removed lantern from pole P21560. NDR N300145 | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-12-25 | c | 0.082182 | 0.0040246 | 2016 | 2015-12-25 | C | 1331 | 0.082182 | 0.0040246
8824515 | 2015-12-25 23:34 | 2015-12-26 02:27 | 172.8167 | 297 | 36741.0167 | 123.7071 | 120.7071 | 0.1111 | 35850.0167 | 0.1084 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733131 | during sectionalising found line down across road between poles 733131 and 733130 section of line between ABS 6040 and 6100 isolated and backfed for repairs materials used aprox 10m 16mm copper and sleves | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2015-12-25 | c | 0.1084 | 0.00089806 | 2016 | 2015-12-25 | C | 297 | 0.1084 | 0.00089806
8825550 | 2015-12-26 05:57 | 2015-12-26 08:35 | 158.6333 | 2337 | 56193.8667 | 24.0453 | 21.0453 | 0.16992 | 49182.8667 | 0.14872 | 0.0070665 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N/A - NOT APPLICABLE | Patrolled Nothing Found Maybe Bird Strike | F1,F2,F3 | HUIRANGI FAULL ROAD 33KV | HUIRANGI | Taranaki | TP_HUIRANGI | Western Electricity | POWERCO | 2015-12-26 | c | 0.14872 | 0.0070665 | 2016 | 2015-12-26 | C | 2337 | 0.14872 | 0.0070665
8827924 | 2015-12-26 07:06 | 2015-12-26 07:21 | 15 | 999 | 10785.1667 | 10.796 | 7.796 | 0.032612 | 7788.1667 | 0.02355 | 0.0030207 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P17064 | Opossum Found at bottom of pole P17064 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-12-26 | c | 0.02355 | 0.0030207 | 2016 | 2015-12-26 | C | 999 | 0.02355 | 0.0030207
8830099 | 2015-12-26 08:55 | 2015-12-26 10:28 | 92.8833 | 1 | 92.8833 | 92.8833 | 89.8833 | 0.00028086 | 89.8833 | 0.00027179 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2203 | Replaced 2 x 6A H/V, O/H fuses ( suspect bird strike ) | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-12-26 | c | 0.00027179 | 3.024e-06 | 2016 | 2015-12-26 | C | 1 | 0.00027179 | 3.0238e-06
8830299 | 2015-12-26 12:29 | 2015-12-26 13:19 | 50.0167 | 26 | 1300.4333 | 50.0167 | 47.0167 | 0.0039322 | 1222.4333 | 0.0036963 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Upper Taumaha Road, Manutahi - Pole 729864 | Check for safety - Floating 11kV insulator. Used 1 X H/T Insulator & Pin. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-12-26 | c | 0.0036963 | 7.8618e-05 | 2016 | 2015-12-26 | C | 26 | 0.0036963 | 7.8618e-05
8830462 | 2015-12-26 13:29 | 2015-12-26 14:06 | 36.9667 | 1 | 36.9667 | 36.9667 | 33.9667 | 0.00011178 | 33.9667 | 0.00010271 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7598 |  | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2015-12-26 | c | 0.00010271 | 3.024e-06 | 2016 | 2015-12-26 | C | 1 | 0.00010271 | 3.0238e-06
8831789 | 2015-12-27 02:03 | 2015-12-27 03:23 | 80 | 20 | 1600 | 80 | 77 | 0.004838 | 1540 | 0.0046566 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 8831766 |  | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-12-27 | c | 0.0046566 | 6.0475e-05 | 2016 | 2015-12-27 | C | 20 | 0.0046566 | 6.0475e-05
8831843 | 2015-12-27 03:41 | 2015-12-27 06:58 | 196.6667 | 540 | 23336.9833 | 43.2166 | 40.2166 | 0.070565 | 21716.9833 | 0.065667 | 0.0016328 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Needs to be recreated | PMA 8 tripped E/F, O/C L/O. feeder sectionalised with line x 1 found at pole 249599. Isolation between Links SE5 030 & ABS IP598 with back feed via Sec 9954. Line repaired all service restored. Materials 4 x meters conductor, 4 x comp sleeves. NDR 53096 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-12-27 | c | 0.065667 | 0.0016328 | 2016 | 2015-12-27 | C | 540 | 0.065667 | 0.0016328
8846637 | 2015-12-27 07:30 | 2015-12-27 08:31 | 61.2 | 13 | 795.6 | 61.2 | 58.2 | 0.0024057 | 756.6 | 0.0022878 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q66 | @ HT Fuses tripped at Q66 (Suspect bird strike). 10A Rating | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-12-27 | c | 0.0022878 | 3.9309e-05 | 2016 | 2015-12-27 | C | 13 | 0.0022878 | 3.9309e-05
8860349 | 2015-12-27 12:34 | 2015-12-27 14:49 | 135.0167 | 416 | 3484.45 | 8.3761 | 5.3761 | 0.010536 | 2236.45 | 0.0067625 | 0.0012579 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | Tripping on SFD 33kV CB2742 on O/C Inv Time causing lossof supply to Motukawa Sub. (Backfed via Huirangi GXP OK). Feeder patrolled and sectionalised but nothing found. All restored OK. (suspect bird strike). | F1,F2,F3 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2015-12-27 | c | 0.0067625 | 0.0012579 | 2016 | 2015-12-27 | C | 416 | 0.0067625 | 0.0012579
8864319 | 2015-12-28 11:38 | 2015-12-28 14:45 | 187.4333 | 348 | 11770.6667 | 33.8238 | 30.8238 | 0.035592 | 10726.6667 | 0.032435 | 0.0010523 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 231024 | Recloser 9875 Trip E/F, O/C. L/O. Caused by rotten tree falling through lines at Pole 321024. Tree removed and Lines pulled back up. 6 Sleeves and 1 mtr of Namu conductor used. NDR # 53057 | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-12-28 | c | 0.032435 | 0.0010523 | 2016 | 2015-12-28 | C | 348 | 0.032435 | 0.0010523
8865302 | 2015-12-28 13:43 | 2015-12-28 14:24 | 41.4167 | 1 | 41.4167 | 41.4167 | 38.4167 | 0.00012523 | 38.4167 | 0.00011616 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 210801 | 1.44pm advised Shan at svs hub Steve has looked at site. Pole is safe but trees will need a trim below lines. Has defected trees to be trimmed at a later date. | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2015-12-28 | c | 0.00011616 | 3.024e-06 | 2016 | 2015-12-28 | C | 1 | 0.00011616 | 3.0238e-06
8866089 | 2015-12-28 20:22 | 2015-12-31 13:01 | 3879 | 566 | 50917.85 | 89.9609 | 86.9609 | 0.15396 | 49219.85 | 0.14883 | 0.0017114 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SD4-333 & TD4 211 | OTU 2 Recloser 9593/2 tripped E/F, L/O. Feeder sectionalised with fault. located beyond fuses SD4 333. Cable fault between Transformer TD4 211 & Link Box TD4 076 H/V cable disconnected between TD4 211 & LB TD4 076. Generator connected to L/V of Transform | F3 | BROOKFIELD TCE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-12-28 | c | 0.14883 | 0.0017114 | 2016 | 2015-12-28 | C | 566 | 0.14883 | 0.0017114
8867586 | 2015-12-29 05:20 | 2015-12-29 07:17 | 117.1667 | 1 | 117.1667 | 117.1667 | 114.1667 | 0.00035428 | 114.1667 | 0.00034521 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP189 | 2 x 6A Fuses and 2 "hockey Sticks" | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0.00034521 | 3.024e-06 | 2016 | 2015-12-29 | C | 1 | 0.00034521 | 3.0238e-06
8867624 | 2015-12-29 07:12 | 2015-12-29 08:48 | 96.4167 | 2 | 192.8333 | 96.4167 | 93.4167 | 0.00058308 | 186.8333 | 0.00056494 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 2634 | 2 x fuses found blown - line patrolled at duck found - used 2 x 8amp fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-12-29 | c | 0.00056494 | 6.048e-06 | 2016 | 2015-12-29 | C | 2 | 0.00056494 | 6.0475e-06
8867875 | 2015-12-25 17:00 | 2016-01-05 12:14 | 15554.0333 | 1 | 15554.0333 | 15554.0333 | 15551.0333 | 0.047032 | 15551.0333 | 0.047023 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1462 | the FM was completed off this job but then this job was merged by the system to oms 8821448. I've now closed this job with the same job notes as for oms 8821448: 2 x 24 amp HV fuses FP1462 replaced. Line had been patrolled with no fault found. Job not clo | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-12-25 | c | 0.047023 | 3.024e-06 | 2016 | 2015-12-25 | C | 1 | 0.047023 | 3.0238e-06
8868293 | 2015-12-29 09:22 | 2015-12-29 13:04 | 222.3 | 3 | 666.9 | 222.3 | 219.3 | 0.0020165 | 657.9 | 0.0019893 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C6485 | System created this job (was OMS 8868066) but cancelled job when tx was offloaded by control 1 x 15kVA Transformer Replaced | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2015-12-29 | c | 0.0019893 | 9.071e-06 | 2016 | 2015-12-29 | C | 3 | 0.0019893 | 9.0713e-06
8868463 | 2015-12-29 11:22 | 2015-12-29 12:31 | 69.4333 | 1 | 69.4333 | 69.4333 | 66.4333 | 0.00020995 | 66.4333 | 0.00020088 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O47 | 2 x fuses found blown at O47 - Used 2x 10 amp fuses and 1 carrier | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-12-29 | c | 0.00020088 | 3.024e-06 | 2016 | 2015-12-29 | C | 1 | 0.00020088 | 3.0238e-06
8868844 | 2015-12-29 12:08 | 2015-12-29 17:45 | 337.3667 | 1527 | 124590.8333 | 81.5919 | 78.5919 | 0.37673 | 120009.8333 | 0.36288 | 0.0046173 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1046 | CB 7 tripped O/C CB 1 Tripped O/C, CB 3 Tripped No Flags CB 4747/3 Tripped E/F. Checks carried out at Peat St Sub. CB's 1,3 and 4747/3 returned to service with no issues . Cable Fault found past Fuse ABS 1046 on CB 7. Cable tested and found to me ok, ligh | F1,F2,F3 | KAI IWI 33KV | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-12-29 | c | 0.36288 | 0.0046173 | 2016 | 2015-12-29 | C | 1527 | 0.36288 | 0.0046173
8870885 | 2015-12-29 12:51 | 2015-12-29 18:50 | 359.1667 | 1 | 359.1667 | 359.1667 | 356.1667 | 0.001086 | 356.1667 | 0.001077 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP274 | Replace faulty transformer TP274 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0.001077 | 3.024e-06 | 2016 | 2015-12-29 | C | 1 | 0.001077 | 3.0238e-06
8870908 | 2015-12-29 13:00 | 2015-12-29 13:40 | 39.95 | 200 | 8026.8833 | 40.1344 | 37.1344 | 0.024271 | 7426.8833 | 0.022457 | 0.00060475 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Paperwork? | Reports of Part Power / No Power found a damaged DDO Carrier and base at Fuses 1112. An Outage was required From ABS 499 and 072 to carryout repairs. Relivened OK. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-12-29 | c | 0.022457 | 0.00060475 | 2016 | 2015-12-29 | C | 200 | 0.022457 | 0.00060475
8871274 | 2015-12-29 15:58 | 2015-12-29 16:03 | 4.9667 | 433 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0013093 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 3 Trip. O/C. Not Patrolled Cause Unknown | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0 | 0.0013093 | 2016 | 2015-12-29 | C | 433 | 0 | 0.0013093
8872240 | 2015-12-29 17:40 | 2015-12-29 21:33 | 233 | 692 | 85622.65 | 123.7322 | 120.7322 | 0.2589 | 83546.65 | 0.25263 | 0.0020924 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 13675 | WHI 1 Recloser 9604/2 tripped E/F L/O. Report of tree in line at pole 13675. Isolation between normal open point ABS IC213 & ABS IC243 ( no back feeds ) Recloser 9604/2 returned to service (also back feeding part of WGM1 at time of tripping, holiday loa | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0.25263 | 0.0020924 | 2016 | 2015-12-29 | C | 692 | 0.25263 | 0.0020924
8872937 | 2015-12-29 17:42 | 2015-12-29 20:40 | 177.15 | 7 | 1240.05 | 177.15 | 174.15 | 0.0037496 | 1219.05 | 0.0036861 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2606 | Replaced 2 x L/V insulators & pins plus 2 x 3A H/V fuses | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0.0036861 | 2.1166e-05 | 2016 | 2015-12-29 | C | 7 | 0.0036861 | 2.1166e-05
8873420 | 2015-12-29 22:00 | 2015-12-30 10:45 | 765 | 391 | 279095 | 713.798 | 710.798 | 0.84392 | 277922 | 0.84037 | 0.0011823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SP010 | Stacey called to complete job - transferred through to control. Line patrol ceased 01:00 30/12 due to terrain & access issues. Supply off over night from SP010. Patrols recommenced 07:00. Problem eventually tracked down to faulty unit at link sectionalise | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-29 | c | 0.84037 | 0.0011823 | 2016 | 2015-12-29 | C | 391 | 0.84037 | 0.0011823
8876468 | 2015-12-30 03:46 | 2015-12-30 16:58 | 791.9333 | 80 | 34554.6667 | 431.9333 | 428.9333 | 0.10449 | 34314.6667 | 0.10376 | 0.0002419 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FP929 | Faulty HV cable identified between fuses FP929 & transformer TC3545. Cable isolated at fuses FP929 @ 03:45. Generator connected at transformer TC3545 @ 10:30 restoring supply. Cable repairs & tests carried out & completed at 16:46. Generator disconnected | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.10376 | 0.0002419 | 2016 | 2015-12-30 | C | 80 | 0.10376 | 0.0002419
8876701 | 2015-12-30 03:36 | 2015-12-30 05:25 | 108.8833 | 31 | 3375.3833 | 108.8833 | 105.8833 | 0.010206 | 3282.3833 | 0.0099251 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH105 | Tripping at Fuses WH105 (2 8 20A). Makoia Rd patrolled, nothing found. Reloaded OK. Advised ORIGIN ENERGY. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-12-30 | c | 0.0099251 | 9.3737e-05 | 2016 | 2015-12-30 | C | 31 | 0.0099251 | 9.3737e-05
8876817 | 2015-12-30 04:36 | 2015-12-30 06:02 | 85.4333 | 37 | 3161.0333 | 85.4333 | 82.4333 | 0.0095582 | 3050.0333 | 0.0092226 | 0.00011188 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10 | 2 HT Fuses found tripped at P10. Coulters Line area patrolled, nothing found. Relivened OK (10A Rating) | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-12-30 | c | 0.0092226 | 0.00011188 | 2016 | 2015-12-30 | C | 37 | 0.0092226 | 0.00011188
8880731 | 2015-12-30 05:58 | 2015-12-30 19:07 | 789.0833 | 131 | 103369.9167 | 789.0833 | 786.0833 | 0.31257 | 102976.9167 | 0.31138 | 0.00039611 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC4-514 | Repaired 1 HV 25mm Cable Joint. 2 x LV Cable Joints | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.31138 | 0.00039611 | 2016 | 2015-12-30 | C | 131 | 0.31138 | 0.00039611
8880742 | 2015-12-30 06:02 | 2015-12-30 06:55 | 53.2833 | 1 | 53.2833 | 53.2833 | 50.2833 | 0.00016112 | 50.2833 | 0.00015204 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8567 | Fuses found blown at Fuses 8567 - cause unknown. Used 2 x 10 amp fuses | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-12-30 | c | 0.00015205 | 3.024e-06 | 2016 | 2015-12-30 | C | 1 | 0.00015204 | 3.0238e-06
8880982 | 2015-12-30 09:00 | 2015-12-30 09:30 | 30.3167 | 38 | 1152.0333 | 30.3167 | 27.3167 | 0.0034835 | 1038.0333 | 0.0031388 | 0.0001149 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3207 | Turned transformer off, blown 200 amp hrc fuse in tx. Replaced 1 x 200 amp hrc fuse and base at TC3207. Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F3 | MOSSOPS RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.0031388 | 0.0001149 | 2016 | 2015-12-30 | C | 38 | 0.0031388 | 0.0001149
8882101 | 2015-12-30 09:45 | 2015-12-30 11:39 | 113.8 | 1715 | 76130.8667 | 44.3912 | 41.3912 | 0.2302 | 70985.8667 | 0.21464 | 0.0051857 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Piako CB 3162 | CB 3162 at Piako sub tripped. Supply lost to Walton & half of 11kV bus at Waharoa. Flags B & C O/C - INST O/C - P2 Ground. Supply restored to 2nd half of 11kV bus via T2. Supply restored to Walton via 11kv backfeeds in stages with the last at 11:39. 33k | F1,F2,F3 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.21464 | 0.0051858 | 2016 | 2015-12-30 | C | 1715 | 0.21464 | 0.0051857
8884870 | 2015-12-30 16:01 | 2015-12-30 16:29 | 28 | 5 | 140 | 28 | 25 | 0.00042333 | 125 | 0.00037797 | 1.5119e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TE4-003 | Isolated lv to replace 100amp fuse and fuse carrier, nothing else repaired or replaced, adjacent assets up to powerco standards | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.00037797 | 1.5119e-05 | 2016 | 2015-12-30 | C | 5 | 0.00037797 | 1.5119e-05
8885415 | 2015-12-30 18:54 | 2015-12-30 19:07 | 13.5 | 100 | 1350 | 13.5 | 10.5 | 0.0040821 | 1050 | 0.0031749 | 0.00030238 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.0031749 | 0.00030238 | 2016 | 2015-12-30 | C | 100 | 0.0031749 | 0.00030238
8885554 | 2015-12-30 19:30 | 2015-12-30 19:56 | 25.5833 | 3 | 76.75 | 25.5833 | 22.5833 | 0.00023207 | 67.75 | 0.00020486 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | FP1653 | 19:15 - ETA of 10 mins given to fire comms. Branch Removed from Line with fuse stick | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.00020486 | 9.071e-06 | 2016 | 2015-12-30 | C | 3 | 0.00020486 | 9.0713e-06
8885559 | 2015-12-30 22:00 | 2015-12-31 13:00 | 900 | 1 | 900 | 900 | 897 | 0.0027214 | 897 | 0.0027123 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1975 | TC1975 Failed will be replaced tomorrow 31/12/15 - Note the faulty transformer differs from what OMS identified (TC1735). 31/12/15 - transformer TC1975 replaced under self isolation & AP. HT lead broke off one of the fuses bases while reloading fuses. Lea | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.0027123 | 3.024e-06 | 2016 | 2015-12-30 | C | 1 | 0.0027123 | 3.0238e-06
8885844 | 2015-12-30 23:00 | 2015-12-31 00:41 | 100.7333 | 4 | 402.9333 | 100.7333 | 97.7333 | 0.0012184 | 390.9333 | 0.0011821 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1666 | 2 x 10A HV Fuses and 1 X 6A HV Fuse | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-12-30 | c | 0.0011821 | 1.2095e-05 | 2016 | 2015-12-30 | C | 4 | 0.0011821 | 1.2095e-05
8886325 | 2015-12-31 07:45 | 2015-12-31 10:05 | 140 | 3 | 420 | 140 | 137 | 0.00127 | 411 | 0.0012428 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726797 | Replaced 1x hv crossarm complete @ pole 726797 Section of line from fuses LI762 isolated for repairs. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-12-31 | c | 0.0012428 | 9.071e-06 | 2016 | 2015-12-31 | C | 3 | 0.0012428 | 9.0713e-06
8886385 | 2015-12-31 07:04 | 2015-12-31 08:14 | 70.0667 | 10183 | 344542.6 | 33.8351 | 30.8351 | 1.0418 | 313993.6 | 0.94944 | 0.030791 |  | 33 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | brunswick | CB 1092 tripped @ Brunswick and auto changeover at Castlecliff operated correctly causing a complete outage to Peat St & Kai Iwi subs . Backfeed put in place from Hatricks Wharf. Line patrol carried out on 33kv and nothing found line re-energised and lef | F1,F2,F3 | PEAT ST 33KV | BRUNSWICK | Wanganui | TP_BRUNSWICK | Western Electricity | POWERCO | 2015-12-31 | c | 0.94944 | 0.030791 | 2016 | 2015-12-31 | C | 10183 | 0.94944 | 0.030791
8896937 | 2015-12-31 08:59 | 2015-12-31 11:06 | 127.6 | 15 | 1785.6667 | 119.0444 | 116.0444 | 0.0053994 | 1740.6667 | 0.0052634 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I44 | pls check oms 8896949 if related. Replaced 2x10a hv fuses | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-12-31 | c | 0.0052634 | 4.5356e-05 | 2016 | 2015-12-31 | C | 15 | 0.0052634 | 4.5356e-05
8897394 | 2015-12-31 10:25 | 2015-12-31 12:32 | 127.1833 | 1 | 127.1833 | 127.1833 | 124.1833 | 0.00038457 | 124.1833 | 0.0003755 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2969 | replaced 2x 8a hv fuses @ 2969 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2015-12-31 | c | 0.0003755 | 3.024e-06 | 2016 | 2015-12-31 | C | 1 | 0.0003755 | 3.0238e-06
8898341 | 2015-12-31 15:59 | 2015-12-31 18:45 | 166.25 | 118 | 18653.5 | 158.0805 | 155.0805 | 0.056404 | 18299.5 | 0.055333 | 0.0003568 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9480 | Recloser 9480/2 on Mikkelsen Rd CB 5 feeder has tripped. Feeder sectionalised and patrolled but no fault found | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-12-31 | c | 0.055333 | 0.0003568 | 2016 | 2015-12-31 | C | 118 | 0.055333 | 0.0003568
8898726 | 2015-12-31 20:01 | 2015-12-31 21:03 | 62 | 48 | 2976 | 62 | 59 | 0.0089987 | 2832 | 0.0085633 | 0.00014514 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2195 | Damaged DDO found at Transformer N2195 - Isolated at ABS's NG 237 & NG248 used 3 x fuse carriers & bases 3 x 6 amp fuses | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-12-31 | c | 0.0085633 | 0.00014514 | 2016 | 2015-12-31 | C | 48 | 0.0085633 | 0.00014514
8899765 | 2015-12-31 20:44 | 2015-12-31 20:54 | 9.9833 | 177 | 1628.2 | 9.1989 | 6.1989 | 0.0049233 | 1097.2 | 0.0033177 | 0.00053521 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 264655 | Feeder de-energised for safety between Recloser 9893 and Sw/gear 9650/3 to reposition x-arm and refit King Bolt on Pole 2646557. | F2/F4 | TE AROHA BOROUGH | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-12-31 | c | 0.0033177 | 0.00053521 | 2016 | 2015-12-31 | C | 177 | 0.0033177 | 0.00053521
8931323 | 2016-01-01 07:03 | 2016-01-01 10:19 | 195.35 | 46 | 8445.2 | 183.5913 | 180.5913 | 0.025536 | 8307.2 | 0.025119 | 0.00013909 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6422 & 4875 | Replaced 1x 15a fuse @ 6422 & 2x 3a fuses @ 4875 | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-01 | c | 0.025119 | 0.00013909 | 2016 | 2016-01-01 | C | 46 | 0.025119 | 0.00013909
8931355 | 2016-01-01 07:39 | 2016-01-01 11:29 | 229.6833 | 41 | 9409.9667 | 229.5114 | 226.5114 | 0.028453 | 9286.9667 | 0.028082 | 0.00012397 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9454 | 10.11am needing to patrol 11kv as tx is out. will call back when he has found out more 11.30 retailer called advising the house has power but the cowshed still doesn't. Called FM he is going back to check as it should all be back on. Found recloser 9454 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.028082 | 0.00012397 | 2016 | 2016-01-01 | C | 41 | 0.028082 | 0.00012397
8931360 | 2016-01-01 03:46 | 2016-01-01 09:40 | 353.6167 | 5688 | 1213056.75 | 213.266 | 210.266 | 3.668 | 1195992.75 | 3.6164 | 0.017199 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 169 | CB 40 L/O O/C C phase. Sectionalised and found faulty insulator. Replaced faulty insulator at pole 169. isolated between ABS 38 & 173. | F1,F2,F3 | WAIHI-WHANGAMATA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 2016-01-01 | c | 3.6164 | 0.017199 | 2016 | 2016-01-01 | C | 5688 | 3.6164 | 0.017199
8938567 | 2016-01-01 10:35 | 2016-01-01 13:30 | 175 | 39 | 3242 | 83.1282 | 80.1282 | 0.009803 | 3125 | 0.0094493 | 0.00011793 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218001 | 10.03am advised hub of 999 and taken to control. Isolated line down between ABS IP515 & SE7-005. Repaired line down at pole 218001 & relivened. Isolated broken jumper on main line at pole 217965 between ABS SE7-008, SE7-007, SE7-005 9513/1 & 9513/6, repai | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.0094493 | 0.00011793 | 2016 | 2016-01-01 | C | 39 | 0.0094493 | 0.00011793
8938961 | 2016-01-01 11:47 | 2016-01-01 12:46 | 58.7667 | 5 | 293.8333 | 58.7667 | 55.7667 | 0.00088848 | 278.8333 | 0.00084313 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4035 | Found 2 x 8 HT fuse blown on TC4035. Check & replaced OK. | F2/F4 | TE AROHA BOROUGH | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.00084313 | 1.5119e-05 | 2016 | 2016-01-01 | C | 5 | 0.00084313 | 1.5119e-05
8946899 | 2016-01-01 15:21 | 2016-01-01 17:33 | 132.45 | 769 | 2566.4333 | 3.3374 | 0.33736 | 0.0077603 | 0 | 0 | 0.0023253 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7-014 | Control advised FM to go check voltages at tx T 4960 which is at start of line. Found jumper broken at ABS SE7-014.Backfeed via ABS SE7-015. CB 4 & CB 3 tripped & L/O when SE7-015 Closed. Reclosed CB 3 to restore all power. Isolated area between CB 4, SE7 | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0 | 0.0023253 | 2016 | 2016-01-01 | C | 769 | 0 | 0.0023253
8962347 | 2016-01-01 20:21 | 2016-01-01 22:01 | 99.4667 | 4 | 397.8667 | 99.4667 | 96.4667 | 0.0012031 | 385.8667 | 0.0011668 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SB2-036 | Fuses Found Blown at SB2-036 - Caused by Bark on lines, cleared using hot sticks Used 2 x 3 amp fuses | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.0011668 | 1.2095e-05 | 2016 | 2016-01-01 | C | 4 | 0.0011668 | 1.2095e-05
8962406 | 2016-01-01 20:51 | 2016-01-02 06:37 | 586.0833 | 5 | 2930.4167 | 586.0833 | 583.0833 | 0.0088609 | 2915.4167 | 0.0088155 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc4035 | Fuses blown, unable to get to fuses do to high winds Faultman to attend in mormning 2 x 8amp fuses replaced | F2/F4 | TE AROHA BOROUGH | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.0088155 | 1.5119e-05 | 2016 | 2016-01-01 | C | 5 | 0.0088155 | 1.5119e-05
8977976 | 2016-01-01 23:00 | 2016-01-02 01:13 | 133.7167 | 6 | 802.3 | 133.7167 | 130.7167 | 0.002426 | 784.3 | 0.0023715 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4688 | 2 x 3amp HV fuses replaced | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-01-01 | c | 0.0023715 | 1.8143e-05 | 2016 | 2016-01-01 | C | 6 | 0.0023715 | 1.8143e-05
8978029 | 2016-01-02 00:03 | 2016-01-02 01:44 | 100.3667 | 138 | 12184.2333 | 88.2915 | 85.2915 | 0.036842 | 11770.2333 | 0.03559 | 0.00041728 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | C937 | Recloser RC11 on Mikkelsen Rd CB 4 feeder tripped to L/O. Line patrolled & sectionalised. Evidence of tree having hit line at pole C937 found. Now all clear of line. All supply restored | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-02 | c | 0.03559 | 0.00041728 | 2016 | 2016-01-02 | C | 138 | 0.03559 | 0.00041728
8978709 | 2016-01-02 06:57 | 2016-01-02 06:58 | 1.1333 | 1519 | 1721.5333 | 1.1333 | -1.8667 | 0.0052055 | 0 | 0 | 0.0045931 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | E/F Flag o CB 2 which went up to Cb Inc T1 So reset right away all good | F1,F2,F3 | CITY NO 1 33KV | CARRINGTON ST 33 | Taranaki | TP_CARRINGTON | Western Electricity | POWERCO | 2016-01-02 | c | 0 | 0.0045931 | 2016 | 2016-01-02 | C | 1519 | 0 | 0.0045931
8982840 | 2016-01-02 08:13 | 2016-01-02 08:23 | 9.4667 | 903 | 7541.8 | 8.3519 | 5.3519 | 0.022805 | 4832.8 | 0.014613 | 0.0027305 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Patrolled nothing found a lot of birds around lines according to Faultman | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2016-01-02 | c | 0.014613 | 0.0027305 | 2016 | 2016-01-02 | C | 903 | 0.014613 | 0.0027305
8983207 | 2016-01-02 09:38 | 2016-01-02 12:23 | 165.1333 | 1 | 165.1333 | 165.1333 | 162.1333 | 0.00049932 | 162.1333 | 0.00049025 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Y165 | Used 1 x H/T Insulator ( Stand Off ) . 2 X 2amp Fuses | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-01-02 | c | 0.00049025 | 3.024e-06 | 2016 | 2016-01-02 | C | 1 | 0.00049025 | 3.0238e-06
8983251 | 2016-01-02 10:00 | 2016-01-02 12:04 | 124.1 | 540 | 57118.2667 | 105.7746 | 102.7746 | 0.17271 | 55498.2667 | 0.16781 | 0.0016328 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | CB 1 L/O on O/C & E/F Sectionalised feeder found no fault | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-02 | c | 0.16781 | 0.0016328 | 2016 | 2016-01-02 | C | 540 | 0.16781 | 0.0016328
8984907 | 2016-01-02 11:16 | 2016-01-02 12:03 | 47.5167 | 1 | 47.5167 | 47.5167 | 44.5167 | 0.00014368 | 44.5167 | 0.00013461 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 200399 | Found branch on line at pole 200399. Opened fuses SD3-191 then removed branch, relivened | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2016-01-02 | c | 0.00013461 | 3.024e-06 | 2016 | 2016-01-02 | C | 1 | 0.00013461 | 3.0238e-06
8985160 | 2016-01-02 15:04 | 2016-01-02 15:15 | 10.85 | 1 | 10.85 | 10.85 | 7.85 | 3.2808e-05 | 7.85 | 2.3737e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4428W | Took readings off transformer Found Sub tap was bit high Have transformer off for total of 10 Min | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-02 | c | 2.3737e-05 | 3.024e-06 | 2016 | 2016-01-02 | C | 1 | 2.3737e-05 | 3.0238e-06
8986727 | 2016-01-02 15:54 | 2016-01-02 16:54 | 59.9667 | 72 | 2252.5 | 31.2847 | 28.2847 | 0.006811 | 2036.5 | 0.0061579 | 0.00021771 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1876 | Jumper at TC1876 broken. Isolated at ABS IC732 to repair jumper. Relivened | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-02 | c | 0.0061579 | 0.00021771 | 2016 | 2016-01-02 | C | 72 | 0.0061579 | 0.00021771
8986979 | 2016-01-02 17:38 | 2016-01-02 19:53 | 134.5333 | 540 | 56147.7333 | 103.9773 | 100.9773 | 0.16978 | 54527.7333 | 0.16488 | 0.0016328 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | O668 | CB 1 tripped to L/O. Report of explosion at transformer TC1846. Site checked out. Problem was a tree branch across line at pole O668. Branch removed. All supply restored. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-02 | c | 0.16488 | 0.0016328 | 2016 | 2016-01-02 | C | 540 | 0.16488 | 0.0016328
8988799 | 2016-01-02 19:50 | 2016-01-02 22:53 | 183 | 777 | 111773 | 143.852 | 140.852 | 0.33797 | 109442 | 0.33093 | 0.0023495 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 754173 | Possible cause cnr of Saltash and Carrington large flame from conductor/pole. Pole 754173 center phase broken kidney strainer. Materials used 1 kidney strain 2 m conductor 2 sleeves 1 dead end | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-02 | c | 0.33093 | 0.0023495 | 2016 | 2016-01-02 | C | 777 | 0.33093 | 0.0023495
8992048 | 2016-01-03 00:58 | 2016-01-03 03:03 | 124.95 | 283 | 23951.6167 | 84.6347 | 81.6347 | 0.072424 | 23102.6167 | 0.069857 | 0.00085572 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Beyond recloser RC01 | Recloser RC01 on Tower Rd CB 1 feeder tripped to L/O. E/F flag. Line sectionalised & patrolled. Initial reclose with ABS IC870 unsuccessful. Backfeed established from recloser 9756/2 to ABS IC870. Rest of line patrolled without success. Reclose attempt su | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.069857 | 0.00085572 | 2016 | 2016-01-03 | C | 283 | 0.069857 | 0.00085572
8992392 | 2016-01-03 04:22 | 2016-01-03 06:31 | 128.8333 | 57 | 7343.5 | 128.8333 | 125.8333 | 0.022205 | 7172.5 | 0.021688 | 0.00017235 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12634 | Recloser RC01 tripped to L/O again. E/F flag. Broken insulator located on pole F12634. Isolations at ABS IC870, IC736, links FP633. Insulator replaced. All supply restored. 1 x 11kV pin & insulator materials required. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.021688 | 0.00017235 | 2016 | 2016-01-03 | C | 57 | 0.021688 | 0.00017235
8992475 | 2016-01-03 05:48 | 2016-01-03 07:04 | 75.6333 | 4 | 302.5333 | 75.6333 | 72.6333 | 0.00091479 | 290.5333 | 0.0008785 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | FC2422 | WHI CB1 replace 2 x 6A H/V, O/H fuses ( trees ) | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.0008785 | 1.2095e-05 | 2016 | 2016-01-03 | C | 4 | 0.0008785 | 1.2095e-05
8993072 | 2016-01-03 10:58 | 2016-01-03 16:46 | 348.5 | 82 | 15239.0333 | 185.8419 | 182.8419 | 0.046079 | 14993.0333 | 0.045335 | 0.00024795 |  | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 392061 | Car v pole, 392061, 392060, 219687. Colin at Fire Comms, 094867948, Event # F1991511. TMA CB5 opened ( Emergency switching ) to isolate damaged poles. Isolation between CB5, ABS SD5 033 & Sw/Gear 9824/4 with 33kV line between TMA 3102 & PMA ABS 66 isolat | F1,F2,F3 | TE MAUNGA 3042-PAPAMOA 72 33KV | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.045335 | 0.00024795 | 2016 | 2016-01-03 | C | 82 | 0.045335 | 0.00024795
8993488 | 2016-01-03 13:04 | 2016-01-03 19:13 | 369 | 260 | 26280.3333 | 101.0782 | 98.0782 | 0.079465 | 25500.3333 | 0.077107 | 0.00078618 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13405 | ( TAI5 ) recloser 9170/2 tripped, E/F, L/O. Feeder sectionalised. Found line down past ABS 323. isolated at ABS 323, Repaired line & relivened | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.077107 | 0.00078618 | 2016 | 2016-01-03 | C | 260 | 0.077107 | 0.00078618
9003314 | 2016-01-03 13:36 | 2016-01-03 15:11 | 95.0333 | 725 | 52003.85 | 71.7294 | 68.7294 | 0.15725 | 49828.85 | 0.15067 | 0.0021922 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Patrolled Nothing found. Chris Naylor was taken off Job 8993415 to help on here. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-03 | c | 0.15067 | 0.0021922 | 2016 | 2016-01-03 | C | 725 | 0.15067 | 0.0021922
9005758 | 2016-01-03 13:57 | 2016-01-03 13:58 | 1.7 | 903 | 1535.1 | 1.7 | -1.3 | 0.0046418 | 0 | 0 | 0.0027305 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F1,F2,F3 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 2016-01-03 | c | 0 | 0.0027305 | 2016 | 2016-01-03 | C | 903 | 0 | 0.0027305
9005860 | 2016-01-03 14:47 | 2016-01-03 19:14 | 266.5833 | 241 | 48 | 0.19917 | -2.8008 | 0.00014514 | 0 | 0 | 0.00072873 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 2 A/R no flags | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0 | 0.00072873 | 2016 | 2016-01-03 | C | 241 | 0 | 0.00072873
9019132 | 2016-01-03 15:03 | 2016-01-03 16:33 | 90.1167 | 2 | 180.2333 | 90.1167 | 87.1167 | 0.00054498 | 174.2333 | 0.00052684 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4007 | ( MAT 3 ) replaced 2 x 3A H/V, O/H fuses & 1 x L/V fuse base | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.00052684 | 6.048e-06 | 2016 | 2016-01-03 | C | 2 | 0.00052684 | 6.0475e-06
9033498 | 2016-01-03 15:52 | 2016-01-03 18:56 | 183.2833 | 397 | 20028 | 50.4484 | 47.4484 | 0.06056 | 18837 | 0.056959 | 0.0012004 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40281 | Recloser K13 tripped on E/F. Replaced insulator on pole P40281 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-01-03 | c | 0.056959 | 0.0012004 | 2016 | 2016-01-03 | C | 397 | 0.056959 | 0.0012004
9034743 | 2016-01-03 16:08 | 2016-01-03 19:14 | 185.8667 | 1 | 185.8667 | 185.8667 | 182.8667 | 0.00056202 | 182.8667 | 0.00055295 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | h1277 | Found branch on line, isolated at fuses FC923, removed branch & checked insulators all OK relivened. NDR 48192was related to 9032200 - wasn't closed off at the same time. spoke to control who advised all related | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-03 | c | 0.00055294 | 3.024e-06 | 2016 | 2016-01-03 | C | 1 | 0.00055295 | 3.0238e-06
9069239 | 2016-01-03 22:17 | 2016-01-04 13:35 | 918.4 | 4 | 3673.6 | 918.4 | 915.4 | 0.011108 | 3661.6 | 0.011072 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 806844 | Line patrolled and found trees in line and burning . Line runs through a gully and tree crew required to attend due to access issues unsafe to carry on in the dark and will be attended in the morning. Section of line from fuses 878 isolated until trees ca | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-03 | c | 0.011072 | 1.2095e-05 | 2016 | 2016-01-03 | C | 4 | 0.011072 | 1.2095e-05
9070663 | 2016-01-04 03:35 | 2016-01-04 05:03 | 88.3167 | 92 | 7817.4167 | 84.9719 | 81.9719 | 0.023638 | 7541.4167 | 0.022803 | 0.00027819 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N21 | CB N21 ARC + Trip B Phase E/F (4 adv). line patrolled and sectionalised and supply restored with no apparent cause found | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.022803 | 0.00027819 | 2016 | 2016-01-04 | C | 92 | 0.022803 | 0.00027819
9070779 | 2016-01-04 06:29 | 2016-01-04 17:00 | 630.9833 | 23 | 8912.6167 | 387.5051 | 384.5051 | 0.02695 | 8843.6167 | 0.026741 | 6.9546e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T293 | Reports of no power found all 3 Fuses tripped at 7850 Glenburn Rd area. Area patrolled / sectionalised but proved difficult to locate fault. Eventually traced to defective Transformer T293 at Glenburn station. Replaced during the day, relivened. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.026741 | 6.9546e-05 | 2016 | 2016-01-04 | C | 23 | 0.026741 | 6.9546e-05
9070947 | 2016-01-04 06:04 | 2016-01-04 09:24 | 200.1333 | 35 | 4088.4 | 116.8114 | 113.8114 | 0.012362 | 3983.4 | 0.012045 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | Leave for OSI to check as there are duplicate ICPs in 9070927 | 2 Fuses initially found tripped at S16. Reloaded OK but another fuse found tripped "upstream" at S15. Patrolled and relivened OK. SAIDI involved with this job. Separate OMS generated for tripping at S15 (No SAIDI). Fuses S16 Rating 10A. Suspect tree. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.012045 | 0.00010583 | 2016 | 2016-01-04 | C | 35 | 0.012045 | 0.00010583
9071003 | 2016-01-04 10:10 | 2016-01-04 11:17 | 67.3667 | 1 | 67.3667 | 67.3667 | 64.3667 | 0.0002037 | 64.3667 | 0.00019463 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718651 | Outage required from Fuses M4365 to repair a low hanging line caused by corrossion. 2 sleeves required. Repaired OK and relivened. | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.00019463 | 3.024e-06 | 2016 | 2016-01-04 | C | 1 | 0.00019463 | 3.0238e-06
9118279 | 2016-01-04 10:19 | 2016-01-04 12:48 | 148.85 | 7 | 1041.95 | 148.85 | 145.85 | 0.0031506 | 1020.95 | 0.0030871 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FP116 | Replace 2 x 6A H/V, O/H fuses ( line clash wind ) | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-01-04 | c | 0.0030871 | 2.1166e-05 | 2016 | 2016-01-04 | C | 7 | 0.0030871 | 2.1166e-05
9118355 | 2016-01-04 10:39 | 2016-01-04 14:28 | 228.5 | 1 | 228.5 | 228.5 | 225.5 | 0.00069093 | 225.5 | 0.00068186 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 210902 | Replace faulty transformer TE4 207, all service restored ( possible lightning strike ) | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-01-04 | c | 0.00068186 | 3.024e-06 | 2016 | 2016-01-04 | C | 1 | 0.00068186 | 3.0238e-06
9118538 | 2016-01-04 14:25 | 2016-01-04 16:18 | 113 | 10 | 1130 | 113 | 110 | 0.0034168 | 1100 | 0.0033261 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12452 | 12.54pm advised smc about tree branch on line at 101 McKeekan Drive - oms 9120847. Customer at this address advised they have power to their house but not to the cottage, pump and electric fence. *** please check if oms 9120847 - 101 McKeekan Drive and om | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-04 | c | 0.0033261 | 3.0238e-05 | 2016 | 2016-01-04 | C | 10 | 0.0033261 | 3.0238e-05
9119688 | 2016-01-04 12:02 | 2016-01-04 15:43 | 220.3667 | 1023 | 42186.3667 | 41.2379 | 38.2379 | 0.12756 | 39117.3667 | 0.11828 | 0.0030933 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 15389 | Tripping on CB24 on E/F IDMT and PU caused by a fallen tree on Cloverlea Rd. The fault current had blown 3 HV jumpers at ABS A22 so an initial outage was required bwteen ABS A1, A2 and A29 to carryout repairs. (Backfeed at Sw/Gear 10173/4). Repairs made a | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.11828 | 0.0030933 | 2016 | 2016-01-04 | C | 1023 | 0.11828 | 0.0030933
9120965 | 2016-01-04 13:09 | 2016-01-04 14:31 | 82.3167 | 1 | 82.3167 | 82.3167 | 79.3167 | 0.00024891 | 79.3167 | 0.00023983 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2657 | 2 HT fuses found tripped at Transformer 4125T. Seperate OMS generated. (Craig Wellington on site - This OMS 9120965 - GPS error, Stated location as 2657T). | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.00023984 | 3.024e-06 | 2016 | 2016-01-04 | C | 1 | 0.00023983 | 3.0238e-06
9121017 | 2016-01-04 13:26 | 2016-01-04 14:07 | 40.85 | 38 | 1552.3 | 40.85 | 37.85 | 0.0046938 | 1438.3 | 0.0043491 | 0.0001149 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 748600 | 1.27pm advised the hub 999..Safety isolation required from Fuses 8107 to remove thin wire tangled in lines. Relivened OK. | F3 | MOTUROA 6 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.0043491 | 0.0001149 | 2016 | 2016-01-04 | C | 38 | 0.0043491 | 0.0001149
9121481 | 2016-01-04 14:29 | 2016-01-04 14:32 | 2.7833 | 6 | 16.7 | 2.7833 | -0.21667 | 5.0497e-05 | 0 | 0 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4125T | 2 HT fuses found tripped at Transformer 4125T. (Craig Wellington on site - OMS 9120965 - GPS error, Stated location as 2657T). Reloaded OK 3A Rating. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0 | 1.8143e-05 | 2016 | 2016-01-04 | C | 6 | 0 | 1.8143e-05
9121498 | 2016-01-04 14:31 | 2016-01-04 15:50 | 78.5 | 3 | 235.5 | 78.5 | 75.5 | 0.0007121 | 226.5 | 0.00068488 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP761 | Replaced 2 x 8A fuses at fuses FP761 bird strike see oms 9122086 | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-01-04 | c | 0.00068488 | 9.071e-06 | 2016 | 2016-01-04 | C | 3 | 0.00068488 | 9.0713e-06
9122255 | 2016-01-05 11:30 | 2016-01-05 12:00 | 30 | 5 | 150 | 30 | 27 | 0.00045356 | 135 | 0.00040821 | 1.5119e-05 | Referral | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12452 | All power restored requires screw anchor replacement in morning. Power taken off transformer for safety while stay was re-terminated. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-05 | c | 0.00040821 | 1.5119e-05 | 2016 | 2016-01-05 | C | 5 | 0.00040821 | 1.5119e-05
9122342 | 2016-01-04 17:00 | 2016-01-04 19:00 | 119.55 | 6 | 717.3 | 119.55 | 116.55 | 0.0021689 | 699.3 | 0.0021145 | 1.8143e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | oms 9122126 possibly relates | OMS 9122126 possibly relates. H/T Fuses to Lite according to Faultman & L/V Fuses to Heavy replaced fuses to correct size | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-04 | c | 0.0021145 | 1.8143e-05 | 2016 | 2016-01-04 | C | 6 | 0.0021145 | 1.8143e-05
9138805 | 2016-01-05 07:34 | 2016-01-05 10:12 | 158.1 | 3 | 474.3 | 158.1 | 155.1 | 0.0014342 | 465.3 | 0.001407 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3688 | 2 HT Fuses found tripped at T3688. Fault traced to LV side at Customer level Isolated OK and Transformer relivened. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-01-05 | c | 0.001407 | 9.071e-06 | 2016 | 2016-01-05 | C | 3 | 0.001407 | 9.0713e-06
9140200 | 2016-01-05 11:34 | 2016-01-05 14:20 | 166.45 | 29 | 4827.05 | 166.45 | 163.45 | 0.014596 | 4740.05 | 0.014333 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3468 | 11.36am advised svs hub of job & and advised control. 15mtrs Squirrel Conductor and 2 Joints | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-01-05 | c | 0.014333 | 8.7689e-05 | 2016 | 2016-01-05 | C | 29 | 0.014333 | 8.7689e-05
9140254 | 2016-01-25 09:10 | 2016-01-25 17:43 | 513 | 102 | 52326 | 513 | 510 | 0.15822 | 52020 | 0.1573 | 0.00030842 | NAPA ID:15185 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5222 | Replace inline H structure T12517/T12518 with 12.5m Busck and replace Pole Mounted Transformer TC5222 with Ground Mount. Relabel existing transformer fuses to FP1753. Work Location: 718 Rolleston Street, Thames. W/O 10148376. | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.078648 | 0.00015421 | 2016 | 2016-01-25 | B | 102 | 0.1573 | 0.00030842
9140796 | 2016-01-05 13:58 | 2016-01-05 14:12 | 14.0667 | 1 | 14.0667 | 14.0667 | 11.0667 | 4.2534e-05 | 11.0667 | 3.3463e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2203 | 2 X 6A HV Fuses Replaced | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-01-05 | c | 3.3463e-05 | 3.024e-06 | 2016 | 2016-01-05 | C | 1 | 3.3463e-05 | 3.0238e-06
9148691 | 2016-01-25 08:59 | 2016-01-25 16:04 | 425 | 6 | 2550 | 425 | 422 | 0.0077106 | 2532 | 0.0076562 | 1.8143e-05 | NAPA ID:15261 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-124 | Replace poles ,hardware & conductor. Between SC2-124 and Temp 68. Work Location: Wainui South Road, Aongatete. W/O 30002547. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.0038281 | 9.071e-06 | 2016 | 2016-01-25 | B | 6 | 0.0076562 | 1.8143e-05
9165633 | 2016-01-06 17:00 | 2016-01-06 17:35 | 35 | 227 | 7945 | 35 | 32 | 0.024024 | 7264 | 0.021965 | 0.00068639 | NAPA ID:15895 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Brooklands Feeder 7, CB7 | Close 11kv Line break. Reinstate 11kV CB7 back into service. 354 Carrington Street New Plymouth. W/O30018710 | F3 | BROOKLANDS 8 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-06 | b | 0.010982 | 0.0003432 | 2016 | 2016-01-06 | B | 227 | 0.021965 | 0.00068639
9240251 | 2016-01-06 07:00 | 2016-01-06 10:29 | 209 | 22 | 4598 | 209 | 206 | 0.013903 | 4532 | 0.013704 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231060 | Line down at Pole 231060. Line re-joined 2 x sleeves. plus short bit of 16mm copper. Faultman noted that the lines are old No8 wire and in extremely poor condition and need urgent replacement. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-06 | c | 0.013704 | 6.6523e-05 | 2016 | 2016-01-06 | C | 22 | 0.013704 | 6.6523e-05
9240323 | 2016-01-05 23:01 | 2016-01-06 00:18 | 77 | 192 | 14784 | 77 | 74 | 0.044703 | 14208 | 0.042962 | 0.00058056 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Faulty fuse holder SC2 134 found, emergency switching to replace faulty fuses at Sectionaliser 9865/2, ABS 9865/1 & links 9865/6. ( no back feeds ) fuse holders x 3 & 3 x 20A fuse links replaced all service restored. | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-05 | c | 0.042962 | 0.00058056 | 2016 | 2016-01-05 | C | 192 | 0.042962 | 0.00058056
9241249 | 2016-01-06 09:47 | 2016-01-06 10:53 | 66.05 | 1 | 66.05 | 66.05 | 63.05 | 0.00019972 | 63.05 | 0.00019065 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 6239 | Fuses found Blown at Fuses 6239 - Suspected bird strike. Used 2 X 10 amp fuses | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-01-06 | c | 0.00019065 | 3.024e-06 | 2016 | 2016-01-06 | C | 1 | 0.00019065 | 3.0238e-06
9241723 | 2016-01-06 07:19 | 2016-01-06 11:00 | 220.7333 | 348 | 7102.1333 | 20.4084 | 17.4084 | 0.021475 | 6058.1333 | 0.018318 | 0.0010523 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H12482 | Jumper off at Pole H12482. Jumper reattached. Isolation between ABS 744, ABS IC747 and ABS 2667. Backfeed via RS 9705 | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-06 | c | 0.018318 | 0.0010523 | 2016 | 2016-01-06 | C | 348 | 0.018318 | 0.0010523
9250512 | 2016-01-27 09:00 | 2016-01-28 07:01 | 1320.5 | 79 | 66816.35 | 845.7766 | 842.7766 | 0.20204 | 66579.35 | 0.20132 | 0.00023888 | NAPA ID:15346 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC-2074 & Temp 67 | Replace poles ,hardware & conductor. Between SC2- 074 & Temp 67, Wainui South Road, Aongatete. W/O 30002547. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-27 | b | 0.10066 | 0.00011944 | 2016 | 2016-01-27 | B | 79 | 0.20132 | 0.00023888
9267979 | 2016-01-06 17:22 | 2016-01-06 17:38 | 16.0667 | 2757 | 34591.65 | 12.5468 | 9.5468 | 0.1046 | 26320.65 | 0.079587 | 0.0083365 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB"s 1272 & 1292 | * Carrying planned switching 15792 to allow Transpower to maintain MGM GXP CB 1272. * On restoration of switching to restore the injection plant back to normal configuration (Close ABS XT15 then Open ABS XT65) * Once ABS XT15 was closed caused MGM GXP 33 | F1,F2,F3 | MANGAMUTU 2 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2016-01-06 | c | 0.079587 | 0.0083365 | 2016 | 2016-01-06 | C | 2757 | 0.079587 | 0.0083365
9327217 | 2016-01-28 09:15 | 2016-01-28 14:25 | 310 | 5 | 1550 | 310 | 307 | 0.0046868 | 1535 | 0.0046415 | 1.5119e-05 | NAPA ID:15420 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4042 | TO REPLACE XARMS & HARDWARE AT Q0282 & TC5051. Wahi Beach Road. W/O 30002513. | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-01-28 | b | 0.0023207 | 7.559e-06 | 2016 | 2016-01-28 | B | 5 | 0.0046415 | 1.5119e-05
9334989 | 2016-01-07 09:02 | 2016-01-07 17:30 | 508.1 | 1 | 508.1 | 508.1 | 505.1 | 0.0015364 | 505.1 | 0.0015273 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7/424 | TX needs to be replaced - FM going to let dispatch know when supply is going to be interrupted Outage added to Dispatch Noticeboard - 1pm to 3pm. Had to get another TX from Palmerston - In that time they restored the power and will be turning it off ag | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-07 | c | 0.0015273 | 3.024e-06 | 2016 | 2016-01-07 | C | 1 | 0.0015273 | 3.0238e-06
9335003 | 2016-01-07 09:04 | 2016-01-07 10:22 | 77.6167 | 1 | 77.6167 | 77.6167 | 74.6167 | 0.00023469 | 74.6167 | 0.00022562 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 4837T | 2 Fuses found blown at Transformer 4837T - Cause Possum. Used 2 x 2 amp fuses | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-07 | c | 0.00022562 | 3.024e-06 | 2016 | 2016-01-07 | C | 1 | 0.00022562 | 3.0238e-06
9335847 | 2016-01-07 10:28 | 2016-01-07 14:12 | 223.5 | 1386 | 3178 | 2.2929 | -0.70707 | 0.0096095 | 0 | 0 | 0.0041909 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | CB 4 | CB 4 A/R O/C Please also check OMS 9337093 - 415 Mill Creek Road and OMS 9337163 - 259 Mill Creek Road 9337318 - 382 Mill Creek Road | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-01-07 | c | 0 | 0.0041909 | 2016 | 2016-01-07 | C | 1386 | 0 | 0.0041909
9339310 | 2016-01-07 14:55 | 2016-01-07 15:36 | 40.9333 | 31 | 1268.9333 | 40.9333 | 37.9333 | 0.003837 | 1175.9333 | 0.0035557 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851533 | Faultman informed by Public of floating conductor, told control it was the cause of OMS 9271808. When Faultman gave location of fault was informed it was not part of the line patrol required for CB3 after A/R Floating Conductor at Pole 851533 - Isolated a | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-07 | c | 0.0035557 | 9.3737e-05 | 2016 | 2016-01-07 | C | 31 | 0.0035557 | 9.3737e-05
9342913 | 2016-01-07 15:50 | 2016-01-07 19:39 | 228.9333 | 21 | 2166.6 | 103.1714 | 100.1714 | 0.0065513 | 2103.6 | 0.0063608 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ma298 | Fuses found blown Fuse MA298 - Cause unknown. Used 2 fuses. Faultman found faulty transformer M2038, line was isolated at Fuses MA298 to remove fuses to faulty transformer M2038, transformer needs to be replaced. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-01-07 | c | 0.0063608 | 6.3499e-05 | 2016 | 2016-01-07 | C | 21 | 0.0063608 | 6.3499e-05
9343188 | 2016-01-07 23:04 | 2016-01-08 05:59 | 414.5833 | 75 | 22536.5 | 300.4867 | 297.4867 | 0.068145 | 22311.5 | 0.067465 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 844203 | Trip on Taupo Quay CB8 (No Flags). Fault caused by Car / Pole on Heads Rd. Isolation required between ABS 262 and Sw/Gear 2056/3. (Backfeed at ABS 780). Pole 205292 replaced along with associated hardware. (No conductors broken). 2 other poles have been | F2 | TAUPO 1 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2016-01-07 | c | 0.067465 | 0.00022678 | 2016 | 2016-01-07 | C | 75 | 0.067465 | 0.00022678
9351709 | 2016-01-08 06:05 | 2016-01-08 07:42 | 96.1667 | 362 | 25506.25 | 70.4593 | 67.4593 | 0.077125 | 24420.25 | 0.073841 | 0.0010946 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB R41 E/F line patrolled nothing found | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.073841 | 0.0010946 | 2016 | 2016-01-08 | C | 362 | 0.073841 | 0.0010946
9352580 | 2016-01-08 07:41 | 2016-01-08 08:21 | 39.6 | 307 | 12157.2 | 39.6 | 36.6 | 0.03676 | 11236.2 | 0.033976 | 0.00092829 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 627 | CB 627 Tripped O/C. Line patrolled and nothing found. | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.033976 | 0.00092829 | 2016 | 2016-01-08 | C | 307 | 0.033976 | 0.00092829
9352930 | 2016-01-08 07:53 | 2016-01-08 13:44 | 351.55 | 333 | 18627.5833 | 55.9387 | 52.9387 | 0.056325 | 17628.5833 | 0.053305 | 0.0010069 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 776526 | CB 284 A/R O/C. Line patrol found trees in line @ pole 776526. Isolated at ABS 724 2687. Backfeed in place at CB7. Tree removed and all power restored. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-01-08 | c | 0.053305 | 0.0010069 | 2016 | 2016-01-08 | C | 333 | 0.053305 | 0.0010069
9353397 | 2016-01-08 08:30 | 2016-01-08 10:30 | 120 | 32 | 3840 | 120 | 117 | 0.011611 | 3744 | 0.011321 | 9.676e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758102 | Line down at 758102 isolated at ABS 407 & 421. 2 x sleeves used. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.011321 | 9.676e-05 | 2016 | 2016-01-08 | C | 32 | 0.011321 | 9.676e-05
9353659 | 2016-01-08 09:38 | 2016-01-08 16:52 | 434.4667 | 154 | 13878.4167 | 90.1196 | 87.1196 | 0.041965 | 13416.4167 | 0.040568 | 0.00046566 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer 3732T | CB H41 E/F. Transformer 3732T found damaged. Line break made at Pole 762132 - Isolation at ABS 5268 Transformer still to be replaced. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.040568 | 0.00046566 | 2016 | 2016-01-08 | C | 154 | 0.040568 | 0.00046566
9353917 | 2016-01-08 10:03 | 2016-01-08 13:33 | 210.05 | 1 | 210.05 | 210.05 | 207.05 | 0.00063514 | 207.05 | 0.00062607 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p13024 | 1003am advised at svs hub & control 11:02 - FM called for 2R to repair 5m conductor OH and replace HV fuses 2 x 6amp fuses Hv 2 x joints lv tractor pulled lines down lines measuered at 4.7 so no ndr | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.00062607 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.00062607 | 3.0238e-06
9355436 | 2016-01-08 10:42 | 2016-01-08 13:17 | 155.05 | 944 | 69247.3333 | 73.3552 | 70.3552 | 0.20939 | 66415.3333 | 0.20082 | 0.0028544 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | CB C894 tripped on O/C . HLT for tree work (NAPA 15407-01). Sectionalised nothing found | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.20082 | 0.0028544 | 2016 | 2016-01-08 | C | 944 | 0.20082 | 0.0028544
9357658 | 2016-01-08 11:02 | 2016-01-08 13:40 | 157.6 | 169 | 12638.6833 | 74.7851 | 71.7851 | 0.038216 | 12131.6833 | 0.036683 | 0.00051102 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 825133 | CB 431 Trip E/F. Found binder at pole 825133 Isolated at Fuses 7576 1 binder used | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.036683 | 0.00051102 | 2016 | 2016-01-08 | C | 169 | 0.036683 | 0.00051102
9357985 | 2016-01-08 13:47 | 2016-01-08 14:05 | 18 | 1 | 18 | 18 | 15 | 5.4428e-05 | 15 | 4.5356e-05 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2439T | Replaced HV jumper under own access permit. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 4.5356e-05 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 4.5356e-05 | 3.0238e-06
9358060 | 2016-01-13 10:20 | 2016-01-13 15:40 | 320 | 5 | 1600 | 320 | 317 | 0.004838 | 1585 | 0.0047927 | 1.5119e-05 | NAPA ID:15913 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C2676 | To replace pole # C2676 and relocate TC5938 from its existing location to this site. Work Location: 145 Strange Road, Te Aroha. Work Order: 30015660. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-13 | b | 0.0023963 | 7.559e-06 | 2016 | 2016-01-13 | B | 5 | 0.0047927 | 1.5119e-05
9358392 | 2016-01-08 19:15 | 2016-01-08 20:38 | 83 | 12 | 996 | 83 | 80 | 0.0030117 | 960 | 0.0029028 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T3222 | 6.18pm emailed svs hub for update as retailer just called for update *** please check if oms 9377952 - 551 PARERA ROAD oms 9373248 - 192 Judds Road are part of this outage *** recloser c640 found tripped line patrolled and d | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0029028 | 3.6285e-05 | 2016 | 2016-01-08 | C | 12 | 0.0029028 | 3.6285e-05
9359811 | 2016-01-08 12:00 | 2016-01-08 19:45 | 464.5667 | 4 | 1858.2667 | 464.5667 | 461.5667 | 0.005619 | 1846.2667 | 0.0055827 | 1.2095e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6219 | 3 x 3 Amp fuses due to lightning. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0055827 | 1.2095e-05 | 2016 | 2016-01-08 | C | 4 | 0.0055827 | 1.2095e-05
9359833 | 2016-01-08 12:03 | 2016-01-08 18:20 | 376.6667 | 65 | 17460 | 268.6154 | 265.6154 | 0.052795 | 17265 | 0.052205 | 0.00019654 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | N/A | Isolated Fault to area past ABS S146. Lines found wrapped round each other, cleared with hot sticks. Relivened OK. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.052205 | 0.00019654 | 2016 | 2016-01-08 | C | 65 | 0.052205 | 0.00019654
9359915 | 2016-01-08 12:05 | 2016-01-09 11:19 | 1394 | 1082 | 45030.7667 | 41.6181 | 38.6181 | 0.13616 | 41784.7667 | 0.12635 | 0.0032717 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P15389 | Power lines down trees have fallen on power lines 107 Cloverlea Road - advised control. NDR#45380. Spoke to control, advise there was an LV line clash in the area. confirmed with tracy on 603 that all power is restored except to 107 cloverlea who has an | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.12635 | 0.0032717 | 2016 | 2016-01-08 | C | 1082 | 0.12635 | 0.0032717
9360999 | 2016-01-08 12:05 | 2016-01-08 13:15 | 69.7833 | 2 | 139.5667 | 69.7833 | 66.7833 | 0.00042202 | 133.5667 | 0.00040387 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH212 | 2 fuses 6 amp Due to wind | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.00040387 | 6.048e-06 | 2016 | 2016-01-08 | C | 2 | 0.00040387 | 6.0475e-06
9361043 | 2016-01-08 12:09 | 2016-01-08 13:51 | 101.4167 | 113 | 11460.0833 | 101.4167 | 98.4167 | 0.034653 | 11121.0833 | 0.033627 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | CB C224 trip O/C E/F. Line patrolled nothing found. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.033627 | 0.00034168 | 2016 | 2016-01-08 | C | 113 | 0.033627 | 0.00034168
9361197 | 2016-01-08 12:13 | 2016-01-08 19:09 | 415.5667 | 1 | 415.5667 | 415.5667 | 412.5667 | 0.0012566 | 412.5667 | 0.0012475 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2437T | 2 x 3amp fuses 2437T | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0012475 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.0012475 | 3.0238e-06
9361676 | 2016-01-08 12:19 | 2016-01-08 14:39 | 140.2 | 5 | 701 | 140.2 | 137.2 | 0.0021197 | 686 | 0.0020743 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1040 | 2 x20 amp fuses weather 1040 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-01-08 | c | 0.0020743 | 1.5119e-05 | 2016 | 2016-01-08 | C | 5 | 0.0020743 | 1.5119e-05
9362581 | 2016-01-08 12:47 | 2016-01-08 16:43 | 235.95 | 2 | 471.9 | 235.95 | 232.95 | 0.0014269 | 465.9 | 0.0014088 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 3421T | 2 x 2amp fuse due to weather | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0014088 | 6.048e-06 | 2016 | 2016-01-08 | C | 2 | 0.0014088 | 6.0475e-06
9362626 | 2016-01-08 14:03 | 2016-01-08 15:43 | 100 | 1 | 100 | 100 | 97 | 0.00030238 | 97 | 0.0002933 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7719 | fuses 7719 found blown remove trees from lines at pole 836422 suspect farmer rang for cow shed no power senario 12.54pm - advise smc. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0002933 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.0002933 | 3.0238e-06
9362642 | 2016-01-08 12:55 | 2016-01-08 15:06 | 131.3333 | 177 | 23246 | 131.3333 | 128.3333 | 0.07029 | 22715 | 0.068685 | 0.00053521 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | Possibly related to house fire alerted hub 9362570. Line patrolled nothing found | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.068685 | 0.00053521 | 2016 | 2016-01-08 | C | 177 | 0.068685 | 0.00053521
9364320 | 2016-01-08 13:07 | 2016-01-08 17:36 | 268.7167 | 46 | 12360.9667 | 268.7167 | 265.7167 | 0.037377 | 12222.9667 | 0.036959 | 0.00013909 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7570 | 2 x 10 amp Fuses 7570 | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.036959 | 0.00013909 | 2016 | 2016-01-08 | C | 46 | 0.036959 | 0.00013909
9364501 | 2016-01-08 13:27 | 2016-01-08 13:28 | 1 | 944 | 944 | 1 | -2 | 0.0028544 | 0 | 0 | 0.0028544 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB C894 A/R No flags. Momentary Loss of Supply - Line not patrolled. Cause of fault unknown. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0 | 0.0028544 | 2016 | 2016-01-08 | C | 944 | 0 | 0.0028544
9365993 | 2016-01-08 13:43 | 2016-01-08 14:09 | 25.6667 | 204 | 5236 | 25.6667 | 22.6667 | 0.015832 | 4624 | 0.013982 | 0.00061685 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | 11kV Recloser 9969 O/C L/O. Closed after 15 mins not patrolled, suspect lightning (weather waring in effect at time). | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.013982 | 0.00061685 | 2016 | 2016-01-08 | C | 204 | 0.013982 | 0.00061685
9366576 | 2016-01-08 13:45 | 2016-01-08 20:56 | 430.5167 | 2 | 861.0333 | 430.5167 | 427.5167 | 0.0026036 | 855.0333 | 0.0025854 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4097T | Replaced 2 ddo's which blew, changed lv fuses to hrc then blew them, isolated property and put the fuses back in and relivened ok. 2x 3amp 63amp 4097T cause weather. Spoke with Todd and he advised ok to complete job. No other assets repaired or replaced | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0025854 | 6.048e-06 | 2016 | 2016-01-08 | C | 2 | 0.0025854 | 6.0475e-06
9366747 | 2016-01-08 13:45 | 2016-01-08 15:10 | 85 | 40 | 3400 | 85 | 82 | 0.010281 | 3280 | 0.0099179 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719011 | Line down at pole 719011. 2 sleeves used. Unknown cause of fault. | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0099179 | 0.00012095 | 2016 | 2016-01-08 | C | 40 | 0.0099179 | 0.00012095
9366875 | 2016-01-08 14:06 | 2016-01-08 16:25 | 139.25 | 102 | 11262.7167 | 110.4188 | 107.4188 | 0.034056 | 10956.7167 | 0.03313 | 0.00030842 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4170 | check OMS 9366796, 9367622, 1641 Port Charles Rd 3.51pm Dean called to advise he has replaced 2x 15amp DDO Fuses. at FC4170 - Dean advised Andrew has spoken to control about this. 2 x 15amp fuse cause - wind. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.03313 | 0.00030842 | 2016 | 2016-01-08 | C | 102 | 0.03313 | 0.00030842
9366938 | 2016-01-08 14:04 | 2016-01-08 15:10 | 66 | 93 | 6138 | 66 | 63 | 0.01856 | 5859 | 0.017716 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | Line closed back in after 45 mins. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.017716 | 0.00028121 | 2016 | 2016-01-08 | C | 93 | 0.017716 | 0.00028121
9367115 | 2016-01-08 14:24 | 2016-01-08 15:43 | 79.4333 | 204 | 11950.1 | 58.5789 | 55.5789 | 0.036134 | 11338.1 | 0.034284 | 0.00061685 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | RS 9969 tripped on O/C, E/F and L/O. Patrolled nothing found | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.034284 | 0.00061685 | 2016 | 2016-01-08 | C | 204 | 0.034284 | 0.00061685
9367776 | 2016-01-08 17:00 | 2016-01-08 18:58 | 118 | 163 | 19234 | 118 | 115 | 0.058159 | 18745 | 0.05668 | 0.00049287 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 797278 | Pole has snapped off at ground level, pole on an angle, lines are holding it up at this stage. Pole is in a paddock, just past the Paraki bridge. Caller is from 2 Te Miha Cresent, Cape Palliser on 063078111. 2.44pm - advise smc. Faultman dug new hole and | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.05668 | 0.00049287 | 2016 | 2016-01-08 | C | 163 | 0.05668 | 0.00049287
9367852 | 2016-01-09 11:16 | 2016-01-09 12:14 | 58 | 7 | 406 | 58 | 55 | 0.0012276 | 385 | 0.0011641 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1192 | Please check if related to 9373562. Faultman found broken fuse holder on transformer 1192, was informed by GTL to return in morning to replace the fuse holder to transformer.Replaced 1 full set of Drop Outs @ transformer 1192. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.0011641 | 2.1166e-05 | 2016 | 2016-01-09 | C | 7 | 0.0011641 | 2.1166e-05
9368028 | 2016-01-08 15:13 | 2016-01-08 18:03 | 169.5833 | 536 | 52933.4167 | 98.7564 | 95.7564 | 0.16006 | 51325.4167 | 0.1552 | 0.0016207 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | b0758 | CB 5 tripped A,B ph, O/C, L/O. Branch on line cleared by hot stick Pole B0758 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.1552 | 0.0016207 | 2016 | 2016-01-08 | C | 536 | 0.1552 | 0.0016207
9369867 | 2016-01-08 15:25 | 2016-01-08 17:42 | 136.5333 | 1 | 136.5333 | 136.5333 | 133.5333 | 0.00041284 | 133.5333 | 0.00040377 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F18 | 2 x 10 amp F18 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.00040377 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.00040377 | 3.0238e-06
9370426 | 2016-01-08 15:26 | 2016-01-08 18:15 | 169.2833 | 536 | 84313.3167 | 157.301 | 154.301 | 0.25494 | 82705.3167 | 0.25008 | 0.0016207 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 384544 | Bark on lines at pole 384544 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.25008 | 0.0016207 | 2016 | 2016-01-08 | C | 536 | 0.25008 | 0.0016207
9372838 | 2016-01-08 15:32 | 2016-01-08 19:45 | 253.0167 | 5 | 1265.0833 | 253.0167 | 250.0167 | 0.0038253 | 1250.0833 | 0.00378 | 1.5119e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC2700 | Pole fuse hanging down. please check if oms 9373596 is related. 16:48 - Transformer faulty. 2 r issued to have replaced. Transformer Replaced TC2700 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.00378 | 1.5119e-05 | 2016 | 2016-01-08 | C | 5 | 0.00378 | 1.5119e-05
9373089 | 2016-01-08 17:20 | 2016-01-08 17:30 | 10 | 4 | 40 | 10 | 7 | 0.00012095 | 28 | 8.4665e-05 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | l4400 | FM requesting a 2R - traffic management/ bucket truck is needed- space out conductors, lines are clashing - 3rd time today | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 8.4665e-05 | 1.2095e-05 | 2016 | 2016-01-08 | C | 4 | 8.4665e-05 | 1.2095e-05
9373143 | 2016-01-08 15:46 | 2016-01-09 | 493.8 | 5 | 2469 | 493.8 | 490.8 | 0.0074657 | 2454 | 0.0074203 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP673 | 2 X 15A HV Fuses Replaced | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.0074203 | 1.5119e-05 | 2016 | 2016-01-08 | C | 5 | 0.0074203 | 1.5119e-05
9373176 | 2016-01-08 17:01 | 2016-01-08 17:38 | 36.6667 | 424 | 15304.95 | 36.0966 | 33.0966 | 0.046279 | 14032.95 | 0.042432 | 0.0012821 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Langdale Road, Masterton | Branches on lines - arcing and on fire, close to a forestry block - urgent. Fire comms event# F1994264. Halfway between Castlepoint rd and Waimimi rd. *** update - it is about 0.5km east of the Blaire Logie Homestead driveway, on the left when heading eas | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.042432 | 0.0012821 | 2016 | 2016-01-08 | C | 424 | 0.042432 | 0.0012821
9373582 | 2016-01-08 15:50 | 2016-01-08 16:45 | 55 | 109 | 5995 | 55 | 52 | 0.018127 | 5668 | 0.017139 | 0.00032959 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223942 | Broken DDO at SE6-062 isolated at ABS SE6-223 & 001 | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.017139 | 0.00032959 | 2016 | 2016-01-08 | C | 109 | 0.017139 | 0.00032959
9374016 | 2016-01-08 17:30 | 2016-01-08 21:00 | 210 | 4 | 840 | 210 | 207 | 0.00254 | 828 | 0.0025037 | 1.2095e-05 |  | 6.6 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3258T | Faultman found a faulty transformer 3258T. Transformer was isolated and replaced. | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0025037 | 1.2095e-05 | 2016 | 2016-01-08 | C | 4 | 0.0025037 | 1.2095e-05
9374082 | 2016-01-08 16:37 | 2016-01-08 22:00 | 323.1167 | 38 | 12278.4333 | 323.1167 | 320.1167 | 0.037127 | 12164.4333 | 0.036782 | 0.0001149 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | V11 | please check if oms 9374272 and 9380788 and 9378695 is related. Faultman found blown fuses at Fuses V11 line was patrolled no fault found suspect line clash due to winds. 2 X 10 amp fuses replaced. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.036782 | 0.0001149 | 2016 | 2016-01-08 | C | 38 | 0.036782 | 0.0001149
9375252 | 2016-01-08 12:42 | 2016-01-08 17:12 | 270 | 3 | 810 | 270 | 267 | 0.0024492 | 801 | 0.002422 | 9.0713e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2298t | 3 x 3 amp fuse due to weather | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.002422 | 9.071e-06 | 2016 | 2016-01-08 | C | 3 | 0.002422 | 9.0713e-06
9378178 | 2016-01-08 18:28 | 2016-01-08 22:15 | 227.0167 | 81 | 13633.6167 | 168.3163 | 165.3163 | 0.041225 | 13390.6167 | 0.04049 | 0.00024492 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L1994 | RC35 Tripped E/F. O/C L/O. Feeder Sectionalised Fault found to be a Cracked Insulator at Pole L1994. Insulator Replaced | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-01-08 | c | 0.04049 | 0.00024493 | 2016 | 2016-01-08 | C | 81 | 0.04049 | 0.00024492
9378522 | 2016-01-08 18:49 | 2016-01-08 21:02 | 133.4667 | 1 | 133.4667 | 133.4667 | 130.4667 | 0.00040357 | 130.4667 | 0.0003945 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 8/39756 | 7.03pm called hub to advise 999 Trees through lines at pole Faultman found tree through lines at pole 839756, line was isolated at Fuses 7864 to repair the line. 20 meters - 16mm copper used 8 sleeves 2 dead ends 2 X 2 amp HV fuses replaced | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.0003945 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.0003945 | 3.0238e-06
9378742 | 2016-01-08 19:17 | 2016-01-08 20:46 | 89.25 | 5 | 446.25 | 89.25 | 86.25 | 0.0013494 | 431.25 | 0.001304 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7228 | Faultman found 2 blown fuses at Fuses 7228, line patrolled no fault found, suspect line clash due to weather. 2 X 10 amp HV fuses replaced | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.001304 | 1.5119e-05 | 2016 | 2016-01-08 | C | 5 | 0.001304 | 1.5119e-05
9379198 | 2016-01-08 21:10 | 2016-01-09 12:57 | 947 | 14 | 2062 | 147.2857 | 144.2857 | 0.006235 | 2020 | 0.006108 | 4.2333e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8673 | Repaired and reattached cable crutch @ ABS 8673 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.006108 | 4.2333e-05 | 2016 | 2016-01-08 | C | 14 | 0.006108 | 4.2333e-05
9380038 | 2016-01-08 20:06 | 2016-01-09 07:30 | 683.9333 | 398 | 58130.15 | 146.0557 | 143.0557 | 0.17577 | 56936.15 | 0.17216 | 0.0012035 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27958 | CB 2 tripped on A & B phase O/C flags, line was patrolled and sectionalised and a blown 11kV jumper was found at ABS U12, when back feed was closed at ABS S12 CB 1 at Parkville auto reclosed on A & B phase O/C flags, line was left isolated until morning t | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.17216 | 0.0012035 | 2016 | 2016-01-08 | C | 398 | 0.17216 | 0.0012035
9380825 | 2016-01-08 20:29 | 2016-01-09 14:22 | 1072.8667 | 1 | 1072.8667 | 1072.8667 | 1069.8667 | 0.0032441 | 1069.8667 | 0.003235 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N/A - NOT APPLICABLE | Tapped transformer down to meet regulation voltages | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-08 | c | 0.003235 | 3.024e-06 | 2016 | 2016-01-08 | C | 1 | 0.003235 | 3.0238e-06
9383826 | 2016-01-09 06:54 | 2016-01-09 14:30 | 456.2333 | 1 | 456.2333 | 456.2333 | 453.2333 | 0.0013795 | 453.2333 | 0.0013705 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X324 | Replaced 2x 10a hv fuses | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.0013705 | 3.024e-06 | 2016 | 2016-01-09 | C | 1 | 0.0013705 | 3.0238e-06
9384232 | 2016-01-09 09:11 | 2016-01-10 19:02 | 2031.1667 | 1 | 1998.2833 | 1998.2833 | 1995.2833 | 0.0060423 | 1995.2833 | 0.0060333 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5169 | Found 2 x 10amp fuses blown, replaced. Fuses re-blew after 4 minutes. Isolated at fuses FC4224, Found tranny TC5169 faulty, to be replaced on Sunday 10/01/16. Transformer Replaced. 10/01/16 18:34 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-01-09 | c | 0.0060333 | 3.024e-06 | 2016 | 2016-01-09 | C | 1 | 0.0060333 | 3.0238e-06
9384297 | 2016-01-09 11:51 | 2016-01-09 12:03 | 12 | 1 | 12 | 12 | 9 | 3.6285e-05 | 9 | 2.7214e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5186E | Repaired HV jumper, no materials used, worked through control. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-01-09 | c | 2.7214e-05 | 3.024e-06 | 2016 | 2016-01-09 | C | 1 | 2.7214e-05 | 3.0238e-06
9384793 | 2016-01-09 10:18 | 2016-01-09 13:38 | 199.65 | 19 | 3793.35 | 199.65 | 196.65 | 0.01147 | 3736.35 | 0.011298 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N30 | Replaced 2x10a fuses | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.011298 | 5.7451e-05 | 2016 | 2016-01-09 | C | 19 | 0.011298 | 5.7451e-05
9385255 | 2016-01-09 11:32 | 2016-01-09 14:15 | 163 | 103 | 16789 | 163 | 160 | 0.050766 | 16480 | 0.049832 | 0.00031145 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 826674 | Has brought tree down through lines. Terry Monk 027 384 1765. Advised HUB. Repaired 2 conductors | F2 | HOLDSWORTH | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.049832 | 0.00031145 | 2016 | 2016-01-09 | C | 103 | 0.049832 | 0.00031145
9387765 | 2016-01-09 12:18 | 2016-01-09 15:49 | 210.95 | 10 | 2109.5 | 210.95 | 207.95 | 0.0063786 | 2079.5 | 0.0062879 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | replaced 2x hv fuses | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.0062879 | 3.0238e-05 | 2016 | 2016-01-09 | C | 10 | 0.0062879 | 3.0238e-05
9388103 | 2016-01-09 13:18 | 2016-01-09 15:31 | 133.2333 | 15 | 1998.5 | 133.2333 | 130.2333 | 0.006043 | 1953.5 | 0.0059069 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2829 | Replaced 2x hv fuse | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.0059069 | 4.5356e-05 | 2016 | 2016-01-09 | C | 15 | 0.0059069 | 4.5356e-05
9388503 | 2016-01-09 14:51 | 2016-01-09 15:02 | 11.1167 | 114 | 1267.3 | 11.1167 | 8.1167 | 0.003832 | 925.3 | 0.0027979 | 0.00034471 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | no paperwork - email sent to Paul | Recloser 1022 tripped. Not patrolled. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-01-09 | c | 0.0027979 | 0.00034471 | 2016 | 2016-01-09 | C | 114 | 0.0027979 | 0.00034471
9388992 | 2016-01-09 21:40 | 2016-01-10 01:05 | 205 | 17 | 3485 | 205 | 202 | 0.010538 | 3434 | 0.010384 | 5.1404e-05 |  | 6.6 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2660 | Fuse found blown at Transformer 2660 - Reload failed, Transformer faulty. Isolated at Fuses 5302. Used 1 x 30 kVA Transformer. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.010384 | 5.1404e-05 | 2016 | 2016-01-09 | C | 17 | 0.010384 | 5.1404e-05
9389039 | 2016-01-09 17:18 | 2016-01-09 20:25 | 187 | 297 | 22788.3333 | 76.7284 | 73.7284 | 0.068906 | 21897.3333 | 0.066212 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 359044 | Lines down at pole 359044 isolated at ABS S514. Used 4 x sleeves and 10mtrs conductor. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.066212 | 0.00089806 | 2016 | 2016-01-09 | C | 297 | 0.066212 | 0.00089806
9389362 | 2016-01-09 15:12 | 2016-01-09 17:00 | 108 | 9 | 972 | 108 | 105 | 0.0029391 | 945 | 0.0028575 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Part of OMS 9384611 NOC rung customer to confirm | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.0028575 | 2.7214e-05 | 2016 | 2016-01-09 | C | 9 | 0.0028575 | 2.7214e-05
9391067 | 2016-01-09 23:46 | 2016-01-10 00:43 | 57.6333 | 334 | 16409.1333 | 49.1291 | 46.1291 | 0.049617 | 15407.1333 | 0.046587 | 0.0010099 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | LI6 | CB LI 6 Tripped O/C E/F L/O. Feeder Sectionlised with no fault found. | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.046587 | 0.0010099 | 2016 | 2016-01-09 | C | 334 | 0.046587 | 0.0010099
9391963 | 2016-01-10 09:05 | 2016-01-10 09:50 | 45 | 35 | 1575 | 45 | 42 | 0.0047624 | 1470 | 0.0044449 | 0.00010583 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719244 | 11kV Insulator out of crossarm at Pole 719244.Materials used: Nut and Washer. | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.0044449 | 0.00010583 | 2016 | 2016-01-10 | C | 35 | 0.0044449 | 0.00010583
9391984 | 2016-01-10 08:18 | 2016-01-10 08:36 | 17.6833 | 362 | 6401.3667 | 17.6833 | 14.6833 | 0.019356 | 5315.3667 | 0.016072 | 0.0010946 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | R41 | CB R41 Auto Reclosed E/F. Line patrolled with nothing found. Maybe Run over Feeder with Camera see if we can see any hot spots. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.016072 | 0.0010946 | 2016 | 2016-01-10 | C | 362 | 0.016072 | 0.0010946
9392988 | 2016-01-10 09:02 | 2016-01-10 11:20 | 137.9833 | 1 | 137.9833 | 137.9833 | 134.9833 | 0.00041723 | 134.9833 | 0.00040816 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7228 | 2 X 10 Amp. Possibly due to Wind. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.00040816 | 3.024e-06 | 2016 | 2016-01-10 | C | 1 | 0.00040816 | 3.0238e-06
9393100 | 2016-01-10 07:36 | 2016-01-10 08:53 | 77.2333 | 1 | 77.2333 | 77.2333 | 74.2333 | 0.00023354 | 74.2333 | 0.00022446 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7719 | 2 X 3 AMP FUSES RESTORED 0853 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.00022446 | 3.024e-06 | 2016 | 2016-01-10 | C | 1 | 0.00022446 | 3.0238e-06
9405716 | 2016-01-10 13:44 | 2016-01-10 16:25 | 161 | 15 | 2415 | 161 | 158 | 0.0073024 | 2370 | 0.0071663 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 2829 | 2 X 15 Amp at Fuse 2829. Paul was about to leave site when it happened again - got Tree Trimmers in and cut trees. NDR047257. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.0071663 | 4.5356e-05 | 2016 | 2016-01-10 | C | 15 | 0.0071663 | 4.5356e-05
9413968 | 2016-01-10 13:24 | 2016-01-10 17:51 | 266.8333 | 2 | 533.6667 | 266.8333 | 263.8333 | 0.0016137 | 527.6667 | 0.0015955 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE6-150 | Transforner blown up FM requesting 2R to replace. Replaced single phase 15kVA transformer, repaired 2 jumpers & 1 x 100 amp cutout unit. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-01-10 | c | 0.0015955 | 6.048e-06 | 2016 | 2016-01-10 | C | 2 | 0.0015955 | 6.0475e-06
9414031 | 2016-01-10 18:26 | 2016-01-10 18:47 | 21 | 1 | 21 | 21 | 18 | 6.3499e-05 | 18 | 5.4428e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L76 | Repaired jumper on fuses L76 via 'Live Line' method. Fuses L76 opened and tagged. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-10 | c | 5.4428e-05 | 3.024e-06 | 2016 | 2016-01-10 | C | 1 | 5.4428e-05 | 3.0238e-06
9422532 | 2016-01-10 15:36 | 2016-01-10 16:58 | 81.6833 | 1 | 81.6833 | 81.6833 | 78.6833 | 0.00024699 | 78.6833 | 0.00023792 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 628 | 2 X 10 Amp Fuses At 628 | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.00023792 | 3.024e-06 | 2016 | 2016-01-10 | C | 1 | 0.00023792 | 3.0238e-06
9434923 | 2016-01-10 20:26 | 2016-01-10 21:08 | 42.1167 | 16 | 673.8667 | 42.1167 | 39.1167 | 0.0020376 | 625.8667 | 0.0018925 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/347 | Isolated at fuses I12 to repair jumper on transformer T9/347 | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.0018925 | 4.838e-05 | 2016 | 2016-01-10 | C | 16 | 0.0018925 | 4.838e-05
9434955 | 2016-01-10 16:59 | 2016-01-10 18:40 | 100.85 | 6 | 605.1 | 100.85 | 97.85 | 0.0018297 | 587.1 | 0.0017752 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2100 | 2 x 6A Fuses Replaced | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-01-10 | c | 0.0017752 | 1.8143e-05 | 2016 | 2016-01-10 | C | 6 | 0.0017752 | 1.8143e-05
9436518 | 2016-01-10 18:00 | 2016-01-10 18:16 | 15.6833 | 726 | 10890 | 15 | 12 | 0.032929 | 8712 | 0.026343 | 0.0021953 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P21914 | during line patrol Found a well done magpie close to pole P21914 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.026343 | 0.0021953 | 2016 | 2016-01-10 | C | 726 | 0.026343 | 0.0021953
9438642 | 2016-01-10 23:30 | 2016-01-11 04:19 | 288.55 | 4 | 240 | 60 | 57 | 0.0007257 | 228 | 0.00068942 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3392 | Replaced 1x transformer | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-01-10 | c | 0.00068942 | 1.2095e-05 | 2016 | 2016-01-10 | C | 4 | 0.00068942 | 1.2095e-05
9439746 | 2016-01-11 07:53 | 2016-01-11 19:40 | 707 | 53 | 37471 | 707 | 704 | 0.1133 | 37312 | 0.11282 | 0.00016026 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cable Fault | Reload reliven at fuses 7747. Fuses blow. Suspected cable Fault. 2:49pm = installing generator sometime this afternoon. 5pm ish - called to speak to Ben regarding what time the generators will be being put on - hub advised Ben Taylor is still onsite but s | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.11282 | 0.00016026 | 2016 | 2016-01-11 | C | 53 | 0.11282 | 0.00016026
9440153 | 2016-01-11 07:25 | 2016-01-11 09:22 | 117.2833 | 306 | 26876.05 | 87.8302 | 84.8302 | 0.081267 | 25958.05 | 0.078491 | 0.00092527 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 739664 | DUG CB D31 tripped O/C, L/O. Branch found on line at pole 739664 with isolation between ABS's 5573 & 5722. Back feeds via sectionaliser 6298 & CB D31 closed. Branch removed, all service restored. NDR No 43211 NOTE trees require trimming in area around p | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.078491 | 0.00092527 | 2016 | 2016-01-11 | C | 306 | 0.078491 | 0.00092527
9441117 | 2016-01-11 08:51 | 2016-01-11 10:00 | 69 | 1 | 69 | 69 | 66 | 0.00020864 | 66 | 0.00019957 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/50 | Replaced Transformer T7/50 Off at 08:51 On at 10:00 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.00019957 | 3.024e-06 | 2016 | 2016-01-11 | C | 1 | 0.00019957 | 3.0238e-06
9441240 | 2016-01-09 10:28 | 2016-01-09 14:11 | 223 | 13 | 2899 | 223 | 220 | 0.0087659 | 2860 | 0.008648 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 799900 | REPLACE POLE 799900 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-09 | c | 0.008648 | 3.9309e-05 | 2016 | 2016-01-09 | C | 13 | 0.008648 | 3.9309e-05
9442035 | 2016-01-11 10:10 | 2016-01-11 11:41 | 91 | 1295 | 76296.8 | 58.9164 | 55.9164 | 0.2307 | 72411.8 | 0.21896 | 0.0039158 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Powerco Authorised Helicopter Line Patrol Due to Accessibility Issues. TP STD CB 2862 tripped O/C Neut time, E/F, L/O. loss of KAP & CAR subs. KAP sub back feed via alt 33kV line & CAP via 11kV back feeds. 33kV line patrolled with chopper due to terrain w | F1,F2,F3 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2016-01-11 | c | 0.21896 | 0.0039158 | 2016 | 2016-01-11 | C | 1295 | 0.21896 | 0.0039158
9445103 | 2016-01-11 12:30 | 2016-01-11 15:10 | 160.1333 | 1 | 160.1333 | 160.1333 | 157.1333 | 0.0004842 | 157.1333 | 0.00047513 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2497T | Replace 2 x 3A fuse & 1 x barrel | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.00047513 | 3.024e-06 | 2016 | 2016-01-11 | C | 1 | 0.00047513 | 3.0238e-06
9446512 | 2016-01-11 15:26 | 2016-01-11 17:25 | 118.55 | 1 | 118.55 | 118.55 | 115.55 | 0.00035847 | 115.55 | 0.0003494 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7244 | 2 X 10 Amp Fuses at Fuses 7244 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.0003494 | 3.024e-06 | 2016 | 2016-01-11 | C | 1 | 0.0003494 | 3.0238e-06
9447636 | 2016-01-11 22:20 | 2016-01-11 22:58 | 37.9 | 24 | 909.6 | 37.9 | 34.9 | 0.0027504 | 837.6 | 0.0025327 | 7.257e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809612 | Repaired conductor @ pole 809612 used 1m conductor and 2 sleeves. Origionaly OMS 9447436 which closed itself off for some reason | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-01-11 | c | 0.0025327 | 7.257e-05 | 2016 | 2016-01-11 | C | 24 | 0.0025327 | 7.257e-05
9448056 | 2016-01-12 01:58 | 2016-01-12 03:02 | 64.3167 | 268 | 17236.8667 | 64.3167 | 61.3167 | 0.05212 | 16432.8667 | 0.049689 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | ABS 5619 | During patrol Found Opossum on ABS 5619 and removed with sticks | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-12 | c | 0.049689 | 0.00081037 | 2016 | 2016-01-12 | C | 268 | 0.049689 | 0.00081037
9449800 | 2016-01-12 06:48 | 2016-01-12 09:40 | 171.9833 | 268 | 39753.3333 | 148.3333 | 145.3333 | 0.1202 | 38949.3333 | 0.11777 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7131 | CB 7131 ; Trip Flags Ph B OC, EF. Feeder sectionalised with no fault found ( rain at time of fault & had cleared possible insulator ). All service restored. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-12 | c | 0.11777 | 0.00081037 | 2016 | 2016-01-12 | C | 268 | 0.11777 | 0.00081037
9452024 | 2016-01-25 09:30 | 2016-01-25 12:03 | 153 | 4 | 612 | 153 | 150 | 0.0018505 | 600 | 0.0018143 | 1.2095e-05 | NAPA ID:15937 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC734 | To replace transformer at TC734. Works location: No. 5 Rd, Springdale. WO 30015154. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-01-25 | b | 0.00090713 | 6.048e-06 | 2016 | 2016-01-25 | B | 4 | 0.0018143 | 1.2095e-05
9454046 | 2016-01-12 12:20 | 2016-01-12 14:15 | 114.5833 | 17 | 1020 | 60 | 57 | 0.0030842 | 969 | 0.00293 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 361188 | 1R - Check for safety. Rural Fire has conducted an inspection following a report on 8/1/2016 of trees growing into lines causing arcing.Inspection has found several branches near or touching power lines plus one dead branch lying on the line, clear eviden | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-12 | c | 0.00293 | 5.1404e-05 | 2016 | 2016-01-12 | C | 17 | 0.00293 | 5.1404e-05
9454177 | 2016-01-12 11:05 | 2016-01-12 11:53 | 48.2167 | 717 | 24495.8333 | 34.1643 | 31.1643 | 0.07407 | 22344.8333 | 0.067565 | 0.002168 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 806430 | CB 1350 Trippd on Ph B OC, EF. 12:39 Referral - Jason Pram to Investigate Control Circuit Issues Bird Strike at Pole 806430. Blown Contol Fuses found at sub. Referal created for Jason Pram to investigate. | F3 | FACTORY | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-12 | c | 0.067565 | 0.002168 | 2016 | 2016-01-12 | C | 717 | 0.067565 | 0.002168
9456377 | 2016-02-02 08:50 | 2016-02-02 16:20 | 450 | 2 | 900 | 450 | 447 | 0.0027214 | 894 | 0.0027032 | 6.0475e-06 | NAPA ID:15740 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5958 | TO REPLACE ABS 229 WITH NEW ABS. Works location: Waitekauri Rd, Waihi. WO 10148222 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-02-02 | b | 0.0013516 | 3.024e-06 | 2016 | 2016-02-02 | B | 2 | 0.0027032 | 6.0475e-06
9456436 | 2016-01-12 11:49 | 2016-01-12 12:01 | 12 | 268 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 7131 Tripped Flag Ph B Oc, And EF. 12:29 - Require IR Camera Patrol of feeder, Suspect faulty insulator. Patrolled all lines that could be seen from road about 60% of Line nothing found | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-12 | c | 0 | 0.00081037 | 2016 | 2016-01-12 | C | 268 | 0 | 0.00081037
9458197 | 2016-02-11 09:25 | 2016-02-11 14:14 | 288.5167 | 2 | 577.0333 | 288.5167 | 285.5167 | 0.0017448 | 571.0333 | 0.0017267 | 6.0475e-06 | NAPA ID:15922 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M12425 | Pole M12425 (TC3481) replace all crossarms and transformer. Pole M1302 & M1303 - replace HV crossarms and remove LV crossarms and LV conductor. Remove 2 x LV poles after pole M1302. Works location: Waotu Rd, Putaruru. WO 30011798 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-02-11 | b | 0.00086333 | 3.024e-06 | 2016 | 2016-02-11 | B | 2 | 0.0017267 | 6.0475e-06
9461240 | 2016-02-09 09:35 | 2016-02-09 18:12 | 517 | 110 | 49418.2 | 449.2564 | 446.2564 | 0.14943 | 49088.2 | 0.14843 | 0.00033261 | NAPA ID:15508 TP_MASTERTON GXP > AKURA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 841274 & 830133 | To replace multiple 11kv poles and wire and run u/g 11kv cables. Mahunga Drive, Miro Street, Masterton. W/O 30013208 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-02-09 | b | 0.074215 | 0.00016631 | 2016 | 2016-02-09 | B | 110 | 0.14843 | 0.00033261
9461243 | 2016-02-02 10:08 | 2016-02-02 15:43 | 335 | 9 | 3015 | 335 | 332 | 0.0091166 | 2988 | 0.009035 | 2.7214e-05 | NAPA ID:15586 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Roads Feeder CB7 | INSTALL NEW FUSE LINKS FP1744. INSTALL TEMP LINKS #19. REPLACE POLES ARMS AND WIRE. No2 Road, Mangatoi Road.W/O30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-02 | b | 0.0045175 | 1.3607e-05 | 2016 | 2016-02-02 | B | 9 | 0.009035 | 2.7214e-05
9461564 | 2016-01-13 09:33 | 2016-01-13 10:26 | 53.0667 | 58 | 3077.8667 | 53.0667 | 50.0667 | 0.0093067 | 2903.8667 | 0.0087806 | 0.00017538 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P17203 | Replace 11kV Crossarm at Pole P17203 | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-01-13 | c | 0.0087806 | 0.00017538 | 2016 | 2016-01-13 | C | 58 | 0.0087806 | 0.00017538
9462120 | 2016-02-03 09:15 | 2016-02-03 14:58 | 343 | 12 | 4116 | 343 | 340 | 0.012446 | 4080 | 0.012337 | 3.6285e-05 | NAPA ID:15760 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Apata Feeder CB3 | Replace poles,hardware & conductor. Wainui South Road. W/O30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-03 | b | 0.0061685 | 1.8143e-05 | 2016 | 2016-02-03 | B | 12 | 0.012337 | 3.6285e-05
9462485 | 2016-02-09 09:55 | 2016-02-09 17:31 | 456 | 20 | 9120 | 456 | 453 | 0.027577 | 9060 | 0.027395 | 6.0475e-05 | NAPA ID:14725 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | Remove existing two pole structure T2/532, change 2 x 33kv/11kv poles and xarms | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-09 | b | 0.013698 | 3.0238e-05 | 2016 | 2016-02-09 | B | 20 | 0.027395 | 6.0475e-05
9462748 | 2016-02-01 09:08 | 2016-02-01 11:57 | 169.05 | 101 | 17074.05 | 169.05 | 166.05 | 0.051628 | 16771.05 | 0.050712 | 0.0003054 | NAPA ID:15838 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G78 | 1Yr Maintenance on Magnefix G69A/B/T. Works location: Hollows Cres. W/O 30003942. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-02-01 | b | 0.025356 | 0.0001527 | 2016 | 2016-02-01 | B | 101 | 0.050712 | 0.0003054
9462871 | 2016-02-01 10:01 | 2016-02-01 11:52 | 110.9167 | 46 | 5102.1667 | 110.9167 | 107.9167 | 0.015428 | 4964.1667 | 0.01501 | 0.00013909 | NAPA ID:15819 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1026 | Repair a section of damaged conductor at pole 784170 holding on by the steel core. Works location: Rangitautau East Rd, Kai Iwi. W/O 30014853. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-02-01 | b | 0.0075052 | 6.9546e-05 | 2016 | 2016-02-01 | B | 46 | 0.01501 | 0.00013909
9462941 | 2016-02-03 09:33 | 2016-02-03 15:28 | 354.55 | 21 | 7445.55 | 354.55 | 351.55 | 0.022514 | 7382.55 | 0.022323 | 6.3499e-05 | NAPA ID:15824 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X4147 | replace 11kv pole and transformer X4147. Works location: Kauarapaoa Rd, Wanganui. WO 30013807 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-03 | b | 0.011162 | 3.1749e-05 | 2016 | 2016-02-03 | B | 21 | 0.022323 | 6.3499e-05
9463534 | 2016-02-05 10:07 | 2016-02-05 11:28 | 81 | 23 | 1863 | 81 | 78 | 0.0056333 | 1794 | 0.0054246 | 6.9546e-05 | NAPA ID:15920 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2525 | Replace TC2525. Works location: Hikuai. WO 30015605 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-02-05 | b | 0.0027123 | 3.4773e-05 | 2016 | 2016-02-05 | B | 23 | 0.0054246 | 6.9546e-05
9464222 | 2016-02-09 09:45 | 2016-02-09 16:53 | 428 | 14 | 5992 | 428 | 425 | 0.018118 | 5950 | 0.017991 | 4.2333e-05 | NAPA ID:15454 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole CREWBH070 | MAKE TEMP BREAK AT CREWBH070 LIVE LINE, ACCESS PERMIT FROM TEMP BREAK CREWBH070 TO REPLACE POLES, XARMS AND HARDWARE FERGUS RD, CLOSE TEMP BREAK CREWBH070 LIVE LINE. Works location: Fergus Rd. WO 30002513 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-02-09 | b | 0.0089957 | 2.1166e-05 | 2016 | 2016-02-09 | B | 14 | 0.017991 | 4.2333e-05
9464337 | 2016-02-10 08:45 | 2016-02-10 13:42 | 297 | 3 | 891 | 297 | 294 | 0.0026942 | 882 | 0.002667 | 9.0713e-06 | NAPA ID:15241 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1567 | Reconductor between pole structures T1567 to T1569. Works location: Thames Coast Rd, Thames. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-10 | b | 0.0013335 | 4.536e-06 | 2016 | 2016-02-10 | B | 3 | 0.002667 | 9.0713e-06
9464434 | 2016-02-11 09:15 | 2016-02-11 16:55 | 460 | 13 | 5980 | 460 | 457 | 0.018082 | 5941 | 0.017964 | 3.9309e-05 | NAPA ID:15761 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SC2-07 | Replace poles ,hardware & conductor. Works location: Wainui South Rd. WO 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-11 | b | 0.0089821 | 1.9654e-05 | 2016 | 2016-02-11 | B | 13 | 0.017964 | 3.9309e-05
9464499 | 2016-02-15 09:15 | 2016-02-15 15:55 | 400 | 26 | 10400 | 400 | 397 | 0.031447 | 10322 | 0.031211 | 7.8618e-05 | NAPA ID:15785 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 205620 | Replace poles ,hardware & conductor. Works location: Wainui South Rd. WO 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-15 | b | 0.015606 | 3.9309e-05 | 2016 | 2016-02-15 | B | 26 | 0.031211 | 7.8618e-05
9464580 | 2016-01-19 09:00 | 2016-01-19 11:00 | 120 | 7 | 840 | 120 | 117 | 0.00254 | 819 | 0.0024765 | 2.1166e-05 | NAPA ID:15978 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2955T | Replace leaking 100kVA Transformer. Work Location: 169 Ngatimaru Road. W/O 30018006. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-01-19 | b | 0.0012382 | 1.0583e-05 | 2016 | 2016-01-19 | B | 7 | 0.0024765 | 2.1166e-05
9464598 | 2016-02-18 09:15 | 2016-02-18 15:06 | 351 | 26 | 9126 | 351 | 348 | 0.027595 | 9048 | 0.027359 | 7.8618e-05 | NAPA ID:15786 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 205620 | Replace poles ,hardware & conductor. Works location: Wainui South Rd. WO 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-18 | b | 0.013679 | 3.9309e-05 | 2016 | 2016-02-18 | B | 26 | 0.027359 | 7.8618e-05
9464684 | 2016-02-24 09:15 | 2016-02-24 15:40 | 385 | 26 | 10010 | 385 | 382 | 0.030268 | 9932 | 0.030032 | 7.8618e-05 | NAPA ID:15787 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 2056920 | Replace poles ,hardware & conductor. Works location: Wainui South Rd. WO 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-24 | b | 0.015016 | 3.9309e-05 | 2016 | 2016-02-24 | B | 26 | 0.030032 | 7.8618e-05
9466101 | 2016-01-14 06:04 | 2016-01-14 09:38 | 214.2667 | 40 | 8570.6667 | 214.2667 | 211.2667 | 0.025916 | 8450.6667 | 0.025553 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | U39 | Check OMS 9466122, 1663 Opaki-Kaipororo Rd possible U39 tripped. 09:28 Wirumu Confirmed U39 tripped OPEN. U39 CLOSED 09:38. Line to be Patrolled. Line Patrolled no fault found. Suspect bird strike. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-01-14 | c | 0.025553 | 0.00012095 | 2016 | 2016-01-14 | C | 40 | 0.025553 | 0.00012095
9468819 | 2016-02-26 09:15 | 2016-02-26 14:50 | 335 | 26 | 8710 | 335 | 332 | 0.026337 | 8632 | 0.026101 | 7.8618e-05 | NAPA ID:15788 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 205620 | Replace poles ,hardware & conductor. Works location: Wainui South Rd. WO 30002547 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-26 | b | 0.013051 | 3.9309e-05 | 2016 | 2016-02-26 | B | 26 | 0.026101 | 7.8618e-05
9469581 | 2016-01-14 10:00 | 2016-01-14 11:37 | 97 | 65 | 6305 | 97 | 94 | 0.019065 | 6110 | 0.018475 | 0.00019654 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O774 | Emergency Isolation to replace crossarm and insulator at pole O774. James Kennerley Replaced HV Crossarm, Insulators and 1 LV Insulators | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-14 | c | 0.018475 | 0.00019654 | 2016 | 2016-01-14 | C | 65 | 0.018475 | 0.00019654
9480466 | 2016-02-03 08:45 | 2016-02-03 15:29 | 404 | 20 | 8080 | 404 | 401 | 0.024432 | 8020 | 0.024251 | 6.0475e-05 | NAPA ID:15091 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F0123 | To replace 11kV lines between pole # F0123 and F0109. Note: TEMP78 is to be removed during the shutdown leaving TEMP59 and 60 to be removed at a latter date. Works location: Puketutu Rd. WO 30002534 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-02-03 | b | 0.012125 | 3.0238e-05 | 2016 | 2016-02-03 | B | 20 | 0.024251 | 6.0475e-05
9480897 | 2016-01-14 12:38 | 2016-01-14 12:44 | 6.4833 | 717 | 4648.55 | 6.4833 | 3.4833 | 0.014056 | 2497.55 | 0.007552 | 0.002168 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 1350 | Flags Ph B OC and EF. Relivened ok. | F3 | FACTORY | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-14 | c | 0.007552 | 0.002168 | 2016 | 2016-01-14 | C | 717 | 0.007552 | 0.002168
9483121 | 2016-02-11 09:20 | 2016-02-11 16:12 | 412 | 4 | 1648 | 412 | 409 | 0.0049832 | 1636 | 0.0049469 | 1.2095e-05 | NAPA ID:15741 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 10131 | to replace 11kv poles and replace to run new 11kv conductor. Works location: Mangatainoka Valley Rd. WO 30014555 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.0024734 | 6.048e-06 | 2016 | 2016-02-11 | B | 4 | 0.0049469 | 1.2095e-05
9483187 | 2016-02-10 09:45 | 2016-02-10 15:08 | 323 | 3 | 969 | 323 | 320 | 0.00293 | 960 | 0.0029028 | 9.0713e-06 | NAPA ID:15321 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 10282 | Replace larch poles with 11m busck poles and run new 11kv conductor to replace #8. Works location: Mangaone Valley Rd. WO 30017084 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-02-10 | b | 0.0014514 | 4.536e-06 | 2016 | 2016-02-10 | B | 3 | 0.0029028 | 9.0713e-06
9483203 | 2016-02-11 10:20 | 2016-02-11 14:50 | 270 | 12 | 3240 | 270 | 267 | 0.009797 | 3204 | 0.0096881 | 3.6285e-05 | NAPA ID:15827 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 1486 | Replace 11kv pole 794600. Works location: Ohaumoko Rd. WO 10161788 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.0048441 | 1.8143e-05 | 2016 | 2016-02-11 | B | 12 | 0.0096881 | 3.6285e-05
9483226 | 2016-02-10 09:11 | 2016-02-10 15:28 | 377.8333 | 180 | 65821.55 | 365.6753 | 362.6753 | 0.19903 | 65281.55 | 0.1974 | 0.00054428 | NAPA ID:15149 TP_GREYTOWN GXP > HAU NUI SUB | 33 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C971 | Protection Testing. Oil Change in C971. Maintenance on T1 Transformer. | F1,F2,F3 | HAU NUI 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2016-02-10 | b | 0.098698 | 0.00027214 | 2016 | 2016-02-10 | B | 180 | 0.1974 | 0.00054428
9483282 | 2016-02-04 09:16 | 2016-02-04 15:01 | 345 | 27 | 9315 | 345 | 342 | 0.028166 | 9234 | 0.027921 | 8.1642e-05 | NAPA ID:15070 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6417 | Run new wire. Works location: Main South Rd, Warea. WO 30010591 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-02-04 | b | 0.013961 | 4.0821e-05 | 2016 | 2016-02-04 | B | 27 | 0.027921 | 8.1642e-05
9483467 | 2016-02-16 08:45 | 2016-02-16 15:05 | 380 | 17 | 6460 | 380 | 377 | 0.019533 | 6409 | 0.019379 | 5.1404e-05 | NAPA ID:15808 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4174 | Replacing crossarms at various sites. Works location: Torehape Rd East. WO 30002467 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-16 | b | 0.0096896 | 2.5702e-05 | 2016 | 2016-02-16 | B | 17 | 0.019379 | 5.1404e-05
9483490 | 2016-02-18 08:45 | 2016-02-18 14:47 | 362 | 14 | 5068 | 362 | 359 | 0.015324 | 5026 | 0.015197 | 4.2333e-05 | NAPA ID:15810 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1184 | Replace cross arms at various sites. Works location: Puhunga Island Rd. WO 30002467 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-18 | b | 0.0075987 | 2.1166e-05 | 2016 | 2016-02-18 | B | 14 | 0.015197 | 4.2333e-05
9483505 | 2016-02-04 10:25 | 2016-02-04 14:42 | 256.2667 | 71 | 18194.9333 | 256.2667 | 253.2667 | 0.055017 | 17981.9333 | 0.054373 | 0.00021469 | NAPA ID:15722 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 6278 | We are removing recloser 6274 and 11kv solid links 6271 - 6265 leaving ABS 6278 as is!! Down the road more at pole 762952 we are installing a new 11m pole with a new das switch 12131/2 And solid links source 12131/4 and load links 12131/6 as you will see | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-04 | b | 0.027187 | 0.00010734 | 2016 | 2016-02-04 | B | 71 | 0.054373 | 0.00021469
9483588 | 2016-01-14 15:52 | 2016-01-14 16:54 | 61.8167 | 1 | 61.8167 | 61.8167 | 58.8167 | 0.00018692 | 58.8167 | 0.00017785 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 700888 and 700894 | Advised svs hub 3:54pm tree in the lines 11 kv lines, will defect to have trees cut back - will need to organise shutdown 700888 and 700894 | F3 | BROOKLANDS 9 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-14 | c | 0.00017785 | 3.024e-06 | 2016 | 2016-01-14 | C | 1 | 0.00017785 | 3.0238e-06
9483970 | 2016-01-14 16:30 | 2016-01-14 17:00 | 30 | 6 | 180 | 30 | 27 | 0.00054428 | 162 | 0.00048985 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9612/2 | ABS SD4-026 opened and tagged to replace fuses at SD unit 9612/2. 1 x 10A Fuse Replaced | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-01-14 | c | 0.00048985 | 1.8143e-05 | 2016 | 2016-01-14 | C | 6 | 0.00048985 | 1.8143e-05
9484147 | 2016-01-14 14:52 | 2016-01-14 17:30 | 157.9167 | 6 | 947.5 | 157.9167 | 154.9167 | 0.002865 | 929.5 | 0.0028106 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4612 |  | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-01-14 | c | 0.0028106 | 1.8143e-05 | 2016 | 2016-01-14 | C | 6 | 0.0028106 | 1.8143e-05
9484294 | 2016-01-14 18:50 | 2016-01-14 21:30 | 160.05 | 302 | 14905.4167 | 49.3557 | 46.3557 | 0.04507 | 13999.4167 | 0.042331 | 0.00091318 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | C6644 | 1R Patrol from recloser CB 6561 Turuturu Rd - getting earth fault pickups on this recloser. CB 6561 Auto-reclosed at 18:50 on B Phase EF. Reports of pole fire and grass fire - CB 6561 open from NOC. Isolation required from ABS CA480 to isolate Transformer | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-01-14 | c | 0.042331 | 0.00091318 | 2016 | 2016-01-14 | C | 302 | 0.042331 | 0.00091318
9485350 | 2016-01-15 05:08 | 2016-01-15 07:38 | 149.9333 | 178 | 16235.9333 | 91.2131 | 88.2131 | 0.049094 | 15701.9333 | 0.047479 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809612 | Cb 4559 Trip E/F Line down caused by corroded conductor mid span Isolated at fuses 144. Materials used: 6mtrs Squirrel, 2 sleeves. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.047479 | 0.00053823 | 2016 | 2016-01-15 | C | 178 | 0.047479 | 0.00053823
9485610 | 2016-01-15 05:17 | 2016-01-15 06:35 | 77.45 | 70 | 4699.5667 | 67.1367 | 64.1367 | 0.01421 | 4489.5667 | 0.013575 | 0.00021166 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812435 | Cb C 613 trip O/C Found tree branch at pole 812435 removed by hot stick | F4 | SOUTH FEATHERSTON | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.013575 | 0.00021166 | 2016 | 2016-01-15 | C | 70 | 0.013575 | 0.00021166
9487622 | 2016-01-15 06:58 | 2016-01-15 09:17 | 139.4167 | 356 | 25592.4167 | 71.8888 | 68.8888 | 0.077385 | 24524.4167 | 0.074156 | 0.0010765 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 371251 | Suspect tree branch contacted the lines at Pole 371251 as it fell from a tree. NDR 21866. Found ABS S384 with broken insulators (DNO 160107) required the Recloser 8097 to be opened in order to operate the ABS in a de-energised state to restore outage area | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.074156 | 0.0010765 | 2016 | 2016-01-15 | C | 356 | 0.074156 | 0.0010765
9488137 | 2016-01-15 07:03 | 2016-01-15 09:33 | 150.1 | 28 | 4202.8 | 150.1 | 147.1 | 0.012708 | 4118.8 | 0.012454 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V16 | 2 x 10 amp fuses unknown cause | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.012454 | 8.4665e-05 | 2016 | 2016-01-15 | C | 28 | 0.012454 | 8.4665e-05
9488500 | 2016-02-10 08:20 | 2016-02-10 16:33 | 493 | 17 | 8381 | 493 | 490 | 0.025342 | 8330 | 0.025188 | 5.1404e-05 | NAPA ID:15640 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P47219 | Replace 11kv crossarms on pole p47219 - run new wire to pole 47153 - replace poles 47153 & 47152. Works location: Mangamutu. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-10 | b | 0.012594 | 2.5702e-05 | 2016 | 2016-02-10 | B | 17 | 0.025188 | 5.1404e-05
9488530 | 2016-01-15 12:00 | 2016-01-15 13:45 | 104.5333 | 99 | 10348.8 | 104.5333 | 101.5333 | 0.031292 | 10051.8 | 0.030394 | 0.00029935 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3793 | Check OMS 9488565, Hospital Pharmacy and Doctors Surgery. Outage required between Sw/Gear IC2026 & IC1462 with back feed from BRN1 via Sw/Gear IC1996. Replace 2 x Fuse Holder, sleeves & lugs. Restored OK. | F3 | RAWHITI AVE | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-15 | c | 0.030394 | 0.00029935 | 2016 | 2016-01-15 | C | 99 | 0.030394 | 0.00029935
9488759 | 2016-01-15 10:40 | 2016-01-15 11:54 | 73.4333 | 7 | 514.0333 | 73.4333 | 70.4333 | 0.0015543 | 493.0333 | 0.0014908 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P12633 | Advised SMC of lines down. 2R request to remove trees and repair broken conductor - To be confirmed at invoicing once scope of work is determined Isolation at S25. 2 x 6amp fuses 20 m conductor 4 joints | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.0014908 | 2.1166e-05 | 2016 | 2016-01-15 | C | 7 | 0.0014908 | 2.1166e-05
9489128 | 2016-01-15 08:19 | 2016-01-15 09:48 | 88.95 | 21 | 1867.95 | 88.95 | 85.95 | 0.0056482 | 1804.95 | 0.0054577 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13327 | Restrain 1 span conductor found hanging low. Materials used: 1 dead end. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-01-15 | c | 0.0054577 | 6.3499e-05 | 2016 | 2016-01-15 | C | 21 | 0.0054577 | 6.3499e-05
9489550 | 2016-02-11 09:38 | 2016-02-11 14:09 | 271 | 39 | 10569 | 271 | 268 | 0.031958 | 10452 | 0.031604 | 0.00011793 | NAPA ID:15768 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGATAINOKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P40600 | Replace pole P40600, ABS, Links and recloser to upgrade network. Works location: Station Hill Rd. WO 10159901 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.015802 | 5.8963e-05 | 2016 | 2016-02-11 | B | 39 | 0.031604 | 0.00011793
9489701 | 2016-02-12 09:39 | 2016-02-12 12:49 | 190 | 14 | 2660 | 190 | 187 | 0.0080432 | 2618 | 0.0079162 | 4.2333e-05 | NAPA ID:15746 TP_MANGAMAIRE GXP > PONGAROA SUB > COAST ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links V52 | To replace cracked insulator at tx t9/167 , remove LT40's from 11kv line and to replace 11kv pole p04360. Works location: Settlement Rd, Pongaroa. WO 10159891 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-02-12 | b | 0.0039581 | 2.1166e-05 | 2016 | 2016-02-12 | B | 14 | 0.0079162 | 4.2333e-05
9490401 | 2016-01-15 11:19 | 2016-01-15 12:50 | 91.0167 | 237 | 19968.2 | 84.254 | 81.254 | 0.060379 | 19257.2 | 0.058229 | 0.00071663 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Also attended by Phil Barnes. safety manager number 539918. CB 3 tripped O/C. See details in safety manager for further details. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.058229 | 0.00071663 | 2016 | 2016-01-15 | C | 237 | 0.058229 | 0.00071663
9490657 | 2016-02-02 09:29 | 2016-02-02 13:10 | 221 | 4 | 884 | 221 | 218 | 0.002673 | 872 | 0.0026367 | 1.2095e-05 | NAPA ID:14009 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2316 | To replace the 11kV Pin Arm, Replace the 11kV D.O.Fuse arm & install a 3 phase 400V Fuse Disconnector. Works location: Campbell Rd. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-02-02 | b | 0.0013184 | 6.048e-06 | 2016 | 2016-02-02 | B | 4 | 0.0026367 | 1.2095e-05
9493320 | 2016-02-11 09:15 | 2016-02-11 14:58 | 343 | 14 | 4802 | 343 | 340 | 0.01452 | 4760 | 0.014393 | 4.2333e-05 | NAPA ID:15053 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5787 | To complete 11kV & 400V Defect repairs beyond fuses TEMP87. Works location: Tramline Rd, Patetonga. WO 30016728 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-02-11 | b | 0.0071966 | 2.1166e-05 | 2016 | 2016-02-11 | B | 14 | 0.014393 | 4.2333e-05
9493354 | 2016-01-15 12:01 | 2016-01-15 14:00 | 118.1833 | 10 | 1181.8333 | 118.1833 | 115.1833 | 0.0035736 | 1151.8333 | 0.0034829 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P27294 | Replace 1 x nut & washer | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.0034829 | 3.0238e-05 | 2016 | 2016-01-15 | C | 10 | 0.0034829 | 3.0238e-05
9493368 | 2016-02-11 09:16 | 2016-02-11 15:00 | 344 | 62 | 21328 | 344 | 341 | 0.064491 | 21142 | 0.063928 | 0.00018747 | NAPA ID:15591 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P46110 | Change pole P46110, 9 cross arms and 24 insulators. Works location: Railway Rd. WO 30014403. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.031964 | 9.3737e-05 | 2016 | 2016-02-11 | B | 62 | 0.063928 | 0.00018747
9493497 | 2016-02-15 09:05 | 2016-02-15 16:38 | 452.8667 | 19 | 8604.4667 | 452.8667 | 449.8667 | 0.026018 | 8547.4667 | 0.025845 | 5.7451e-05 | NAPA ID:15609 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P41966 | Change pole p41966 and 21 x 33kv Xarms, and 11 x 11kv xarms. Works location: Clevely Line. WO 30014403 Note this shut was late coming back from Scanpower. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-15 | b | 0.012923 | 2.8726e-05 | 2016 | 2016-02-15 | B | 19 | 0.025845 | 5.7451e-05
9493894 | 2016-02-17 09:10 | 2016-02-17 15:54 | 404 | 31 | 4802 | 154.9032 | 151.9032 | 0.01452 | 4709 | 0.014239 | 9.3737e-05 | NAPA ID:15619 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/187 | Change 15 x 33kv Xarms, and 10 x 11kv xarms. Works location: Roberts Line. WO 30014403 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-17 | b | 0.0071194 | 4.6868e-05 | 2016 | 2016-02-17 | B | 31 | 0.014239 | 9.3737e-05
9494098 | 2016-01-15 15:25 | 2016-01-15 15:55 | 29.85 | 26 | 776.1 | 29.85 | 26.85 | 0.0023467 | 698.1 | 0.0021109 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812809 | The bolt that holds the cross bar has fallen out and the cross bar is hanging down. Customer stated it is an HV line. Jim Hedley 027 5088449. Replaced bolt straightened up crossarm | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.0021109 | 7.8618e-05 | 2016 | 2016-01-15 | C | 26 | 0.0021109 | 7.8618e-05
9494771 | 2016-02-11 09:30 | 2016-02-11 13:39 | 249 | 45 | 11205 | 249 | 246 | 0.033881 | 11070 | 0.033473 | 0.00013607 | NAPA ID:15728 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV aBS 191 | Replace ABS 191 and cross arms as they are old. Works location: Egmont Rd. WO 30013468 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.016737 | 6.8035e-05 | 2016 | 2016-02-11 | B | 45 | 0.033473 | 0.00013607
9495218 | 2016-01-15 16:30 | 2016-01-15 19:27 | 176.5333 | 76 | 13416.5333 | 176.5333 | 173.5333 | 0.040568 | 13188.5333 | 0.039879 | 0.00022981 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Recloser RS7417 Auto-reclose at 16:23 on E/F Phase A O/C. Reports came in of lines down and RS7417 open from NOC for safety. Some delay in restoration as fault staff in no Comms area. Fuses 8135 open as isolation point (Private Line) and power restored OK | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.039879 | 0.00022981 | 2016 | 2016-01-15 | C | 76 | 0.039879 | 0.00022981
9495761 | 2016-01-15 19:20 | 2016-01-15 21:00 | 100.2667 | 2 | 200.5333 | 100.2667 | 97.2667 | 0.00060636 | 194.5333 | 0.00058822 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7873 | 2 HT Fuses found tripped at Fuses 7873. Line patrol carried out, high winds - suspect line clash. Reclosed OK. (10A Rating). | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2016-01-15 | c | 0.00058822 | 6.048e-06 | 2016 | 2016-01-15 | C | 2 | 0.00058822 | 6.0475e-06
9499318 | 2016-01-16 07:37 | 2016-01-16 07:52 | 14.5333 | 635 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0019201 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | xt56 | During planned switching 15441, operation 24 (closing CB XT 50) 33kV MGM GXP CB 1332 tripped on direct time E/F and locked out (07:34hrs). * Extensive Patrols attempting to ascertain fault located suspect pentagraphs on 33kV CB XT56 at Alfredton Sub. Thes | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-16 | c | 0 | 0.0019201 | 2016 | 2016-01-16 | C | 635 | 0 | 0.0019201
9503368 | 2016-01-17 07:23 | 2016-01-17 15:56 | 513.2 | 1027 | 20930.1333 | 20.3799 | 17.3799 | 0.063288 | 17849.1333 | 0.053972 | 0.0031054 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | During planned switching 15884, operation 21 (closing CB XT 50) 33kV MGM GXP CB 1332 tripped (again) on direct time E/F and locked out (07:21hrs). Further foot patrols done where able to and a Sub Tech sent to investigate protection relays. No 33kV fault | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-17 | c | 0.053972 | 0.0031054 | 2016 | 2016-01-17 | C | 1027 | 0.053972 | 0.0031054
9506151 | 2016-01-17 15:05 | 2016-01-17 15:47 | 42.55 | 1 | 42.55 | 42.55 | 39.55 | 0.00012866 | 39.55 | 0.00011959 | 3.0238e-06 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | Part of HV tripping at Pongaroa/Mangamaire. Cause was found to be 11kV insulator and jumper. | F1,F2,F3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 2016-01-17 | c | 0.00011959 | 3.024e-06 | 2016 | 2016-01-17 | C | 1 | 0.00011959 | 3.0238e-06
9506157 | 2016-01-17 15:16 | 2016-01-17 19:15 | 239.15 | 1 | 239.15 | 239.15 | 236.15 | 0.00072313 | 236.15 | 0.00071406 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 12056/3 | 9506194 & 9506165 LINKED. Cable termination has blown up at Sw/Gear 12056/3. Isolated at Fuse/Sw 58/4. Generators installed by Linepower at Transformers 1861N & 2252N (19:15). | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-17 | c | 0.00071406 | 3.024e-06 | 2016 | 2016-01-17 | C | 1 | 0.00071406 | 3.0238e-06
9506209 | 2016-01-19 13:36 | 2016-01-19 15:34 | 118 | 55 | 6490 | 118 | 115 | 0.019624 | 6325 | 0.019125 | 0.00016631 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 12056 | Customer has been advised to turn main switch off, hv fault in area per Wes. Cable fault caused outage, DNO 160111. Generators connected to Transformers 1861N & 2252N. Jumper placed to restore job. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-19 | c | 0.019125 | 0.00016631 | 2016 | 2016-01-19 | C | 55 | 0.019125 | 0.00016631
9506966 | 2016-01-17 18:48 | 2016-01-17 21:47 | 179.7333 | 720 | 45846.5333 | 63.6757 | 60.6757 | 0.13863 | 43686.5333 | 0.1321 | 0.0021771 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2564 | 2 x A/R on CB 5 was followed by several part power & low power calls from feeder. (A & B Ph O/C flags) CB 5 was opened by NOC to safeguard installations when it became apparent a jumper or something similar had faulted. Faults logged indicated it was in s | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-01-17 | c | 0.1321 | 0.0021771 | 2016 | 2016-01-17 | C | 720 | 0.1321 | 0.0021771
9508786 | 2016-01-17 21:34 | 2016-01-17 21:36 | 2.3667 | 93 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | RS N21 A/R, E/F B Phase. Not patrolled, No fault found | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-17 | c | 0 | 0.00028121 | 2016 | 2016-01-17 | C | 93 | 0 | 0.00028121
9509158 | 2016-01-18 02:38 | 2016-01-18 05:01 | 143.4 | 769 | 6450.9167 | 8.3887 | 5.3887 | 0.019506 | 4143.9167 | 0.01253 | 0.0023253 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217974 | CB 1 Pongakawa tripped to L/O. E/F flag. 9760/2 ABF scheme operated restoring supply to recloser 9548/2 within 1 minute of tripping. Recloser 9513/2 opened by NOC and recloser 9460 closed after 15 min. Line sectionalised & patrolled. Lines down located at | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.01253 | 0.0023253 | 2016 | 2016-01-18 | C | 769 | 0.01253 | 0.0023253
9509866 | 2016-01-18 03:22 | 2016-01-18 06:11 | 169.0667 | 283 | 30245.1667 | 106.8734 | 103.8734 | 0.091454 | 29396.1667 | 0.088887 | 0.00085572 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | RC01 | Recloser RC01 tripped to L/O. E/F flag. Line sectionalised & patrolled. No fault found. All supply restored. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.088887 | 0.00085572 | 2016 | 2016-01-18 | C | 283 | 0.088887 | 0.00085572
9511355 | 2016-02-11 10:09 | 2016-02-11 13:25 | 196 | 51 | 9996 | 196 | 193 | 0.030226 | 9843 | 0.029763 | 0.00015421 | NAPA ID:15762 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS LI716 | Replace hv Conductor between poles 728855 and 728851 (3 spans). Works location; Ball Rd, Alton. WO 30010887 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.014881 | 7.7106e-05 | 2016 | 2016-02-11 | B | 51 | 0.029763 | 0.00015421
9512336 | 2016-01-18 08:42 | 2016-01-18 10:38 | 116.1667 | 433 | 35050.7333 | 80.9486 | 77.9486 | 0.10599 | 33751.7333 | 0.10206 | 0.0013093 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | B0155 | BRD CB3 tripped E/F, L/O feeder sectionalised with possum found on line at pole B0155, possum removed, all service restored. NOTE: Recloser 9867 should have cleared the fault, not CB 3 will require investigation. | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.10206 | 0.0013093 | 2016 | 2016-01-18 | C | 433 | 0.10206 | 0.0013093
9514070 | 2016-01-18 09:08 | 2016-01-18 11:30 | 142.4333 | 4 | 545.3833 | 136.3458 | 133.3458 | 0.0016491 | 533.3833 | 0.0016128 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1460 | Check OMS 9514180 58 Turakina Valley Road. Reload Reliven at Fuses 1460. 2 x 10 A Fuses. Cause: Bird Strike. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.0016128 | 1.2095e-05 | 2016 | 2016-01-18 | C | 4 | 0.0016128 | 1.2095e-05
9515565 | 2016-01-18 10:01 | 2016-01-18 12:31 | 150.3667 | 2 | 300.7333 | 150.3667 | 147.3667 | 0.00090935 | 294.7333 | 0.0008912 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TB1-030 | Reload Reliven. TB1-030 2 x 3A. Possibly tree bark on lines. | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.0008912 | 6.048e-06 | 2016 | 2016-01-18 | C | 2 | 0.0008912 | 6.0475e-06
9517479 | 2016-01-18 11:01 | 2016-01-18 14:48 | 226.6667 | 362 | 34876.6833 | 96.3444 | 93.3444 | 0.10546 | 33790.6833 | 0.10217 | 0.0010946 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732211 | ETL CB R41 tripped E/F, L/O. Feeder sectionalised with faulty insulator & line down found at pole 732211. Isolations between ABS's 6125 & 6042 ( no back feeds ) with rest of feeder returned to service. All repairs completed all service restored. Material | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.10217 | 0.0010946 | 2016 | 2016-01-18 | C | 362 | 0.10217 | 0.0010946
9519935 | 2016-02-15 09:00 | 2016-02-15 15:08 | 367.2167 | 47 | 17259.1833 | 367.2167 | 364.2167 | 0.052188 | 17118.1833 | 0.051761 | 0.00014212 | NAPA ID:15055 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1742 | To complete 11kV & 400V Defect repairs on SH 27 & Tramline Rd. To install Temp fuses TEMP 86. To install new Fuses FP1742. To remove Temp Fuses TEMP87. Works Location: Tramline Road, Patetonga. W/O30016728 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-02-15 | b | 0.025881 | 7.1058e-05 | 2016 | 2016-02-15 | B | 47 | 0.051761 | 0.00014212
9520432 | 2016-01-18 11:50 | 2016-01-18 14:57 | 186.9833 | 20 | 3739.6667 | 186.9833 | 183.9833 | 0.011308 | 3679.6667 | 0.011126 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | L37 | Check OMS 9520422 and 9520440. Reload Reliven at Fuses L37. Nick reported that Loading has increased by 2.5 MW on that line and that the fuses were burning out due to under rating. 3 x 15A Fuses and Candles used. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.011126 | 6.0475e-05 | 2016 | 2016-01-18 | C | 20 | 0.011126 | 6.0475e-05
9521387 | 2016-02-09 09:52 | 2016-02-09 15:24 | 332.2 | 94 | 31226.8 | 332.2 | 329.2 | 0.094422 | 30944.8 | 0.09357 | 0.00028423 | NAPA ID:16086 TP_STRATFORD GXP > MOTUKAWA SUB > TARATA | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 762399 | Treecutting of burnt overhanging trees on main line cnr Tarata Rd and Otoraoa Rd. Work Location: Cnr Tarata Road and Otoraoa Road. W/O 10152474. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-02-09 | b | 0.046785 | 0.00014212 | 2016 | 2016-02-09 | B | 94 | 0.09357 | 0.00028423
9522178 | 2016-02-09 10:16 | 2016-02-09 14:46 | 270 | 1 | 270 | 270 | 267 | 0.00081642 | 267 | 0.00080734 | 3.0238e-06 | NAPA ID:16078 TP_STRATFORD GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 737373 & 737374, Poles 392032 & 393384 | Replace 33Kv conductor/pole over 11Kv lines. 451 East Road, Stratford.W/O30010304 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-02-09 | b | 0.00040367 | 1.512e-06 | 2016 | 2016-02-09 | B | 1 | 0.00080734 | 3.0238e-06
9522824 | 2016-01-18 14:36 | 2016-01-18 18:28 | 232.4833 | 268 | 56413.05 | 210.4965 | 207.4965 | 0.17058 | 55609.05 | 0.16815 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2080T | STM CB7131 tripped B Ph O/C, E/F, L/O feeder sectionalised with faulty insulator found at regulator 2080T site ABS 5238. Isolation at ABS 5229 ( no back feeds ). Jumper cut away and will be repaired at a later date on a Live Line Permit when weather allow | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.16815 | 0.00081037 | 2016 | 2016-01-18 | C | 268 | 0.16815 | 0.00081037
9523594 | 2016-01-18 15:05 | 2016-01-18 17:26 | 140.7167 | 726 | 64272.1 | 88.5291 | 85.5291 | 0.19434 | 62094.1 | 0.18776 | 0.0021953 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P19047 | Part Of 9525056 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.18776 | 0.0021953 | 2016 | 2016-01-18 | C | 726 | 0.18776 | 0.0021953
9530714 | 2016-01-20 08:21 | 2016-01-20 15:26 | 424.85 | 8 | 3398.8 | 424.85 | 421.85 | 0.010277 | 3374.8 | 0.010205 | 2.419e-05 | NAPA ID:16100 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209976 | Urgent work to replace two rotten poles and repair line joints. Work location: 60 Ross Road, Tauranga. Work Order: 30001335 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-01-20 | b | 0.0051023 | 1.2095e-05 | 2016 | 2016-01-20 | B | 8 | 0.010205 | 2.419e-05
9530870 | 2016-02-03 08:45 | 2016-02-03 15:09 | 384 | 37 | 14208 | 384 | 381 | 0.042962 | 14097 | 0.042626 | 0.00011188 | NAPA ID:15423 TP_WAIKINO GXP > WAIHI BEACH SUB > BEACH RD WAIHI BEACH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IP626 | REPLACE XARMS AND HARDWARE ON ASSETS BEYOND FUSES FC4074 & ON 11KV LINES ONLY BETWEEN IP626 & 9719. Works location: Waihi Beach Rd. WO 30002513 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-02-03 | b | 0.021313 | 5.594e-05 | 2016 | 2016-02-03 | B | 37 | 0.042626 | 0.00011188
9531394 | 2016-01-18 16:50 | 2016-01-18 20:16 | 205.8333 | 215 | 28413.1667 | 132.1543 | 129.1543 | 0.085915 | 27768.1667 | 0.083964 | 0.00065011 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730206 | Trip on PH C OC & EF. During sectionalising member of the public approached the fault man and advised of a burning pole on investigation found a burnt insulator on pole 730206. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.083964 | 0.00065011 | 2016 | 2016-01-18 | C | 215 | 0.083964 | 0.00065011
9532166 | 2016-01-18 17:48 | 2016-01-19 10:56 | 1028.1 | 160 | 51534.7333 | 322.0921 | 319.0921 | 0.15583 | 51054.7333 | 0.15438 | 0.0004838 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 229048 | Recloser 9556/2 tripped to L/O. E/F flag. Line sectionalised & patrolled. Tree over line located at pole 229048. Line isolated at ABS 9833/1 & links 9883/6 to remove tree. Recloser 9556 tripped again on relivening line. Another fault on line beyond ABS SF | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.15438 | 0.0004838 | 2016 | 2016-01-18 | C | 160 | 0.15438 | 0.0004838
9533636 | 2016-01-18 19:55 | 2016-01-18 23:43 | 227.4167 | 524 | 75740.85 | 144.5436 | 141.5436 | 0.22902 | 74168.85 | 0.22427 | 0.0015845 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 8 feeder | CB 8 tripped to L/O. E/F flag. Underground section of feeder sectionalised in with staged restoration and overhead patrolled & sectionalised in stages with no fault found. All supply restored. | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.22427 | 0.0015845 | 2016 | 2016-01-18 | C | 524 | 0.22427 | 0.0015845
9535137 | 2016-01-18 23:28 | 2016-01-19 05:23 | 355.4 | 93 | 21386.8833 | 229.9665 | 226.9665 | 0.064669 | 21107.8833 | 0.063825 | 0.00028121 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10052 | Line sectionalised and patrolled found blown insulator on pole P10052 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.063825 | 0.00028121 | 2016 | 2016-01-18 | C | 93 | 0.063825 | 0.00028121
9535233 | 2016-01-18 23:29 | 2016-01-19 06:20 | 411 | 106 | 34238.7833 | 323.0074 | 320.0074 | 0.10353 | 33920.7833 | 0.10257 | 0.00032052 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04884 | during sectionalising and patrol found broken binders on pole P04884 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-18 | c | 0.10257 | 0.00032052 | 2016 | 2016-01-18 | C | 106 | 0.10257 | 0.00032052
9535393 | 2016-01-19 00:43 | 2016-01-19 04:59 | 256.3667 | 524 | 9206.0333 | 17.5688 | 14.5688 | 0.027837 | 7634.0333 | 0.023083 | 0.0015845 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12996 | Further 3 x A/R (E/F flag) on CB 8 following earlier problems on feeder (OMS 9533636). 11kV switching carried out on feeder to shift tie points to narrow down area of transient fault. Arc noticed by faultman on pole M12996. Faulty disc strain insulator id | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.023083 | 0.0015845 | 2016 | 2016-01-19 | C | 524 | 0.023083 | 0.0015845
9536827 | 2016-01-19 01:43 | 2016-01-19 03:10 | 87.3333 | 28 | 2445.3333 | 87.3333 | 84.3333 | 0.0073941 | 2361.3333 | 0.0071401 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | PON1 |  | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-19 | c | 0.0071401 | 8.4665e-05 | 2016 | 2016-01-19 | C | 28 | 0.0071401 | 8.4665e-05
9537437 | 2016-01-19 02:00 | 2016-01-19 09:00 | 419.7667 | 1 | 419.7667 | 419.7667 | 416.7667 | 0.0012693 | 416.7667 | 0.0012602 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1-011 | Reload Reliven 2 x 2A Fuse due to Lightning. | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.0012602 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.0012602 | 3.0238e-06
9541088 | 2016-01-19 04:44 | 2016-01-19 07:11 | 146.7167 | 119 | 12177.0833 | 102.3284 | 99.3284 | 0.036821 | 11820.0833 | 0.035741 | 0.00035983 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | PA0249 | ( MAR 3 ) recloser 9539 tripped E/F, L/O. Tree through line at pole A0249. Isolation at ABS 987 ( spur no back feeds ). Lines x 3 repaired. All service restored. NDR 38537. Materials 9 x H/V sleeves, 10 meters conductor. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.035741 | 0.00035983 | 2016 | 2016-01-19 | C | 119 | 0.035741 | 0.00035983
9542182 | 2016-01-19 05:00 | 2016-01-19 06:10 | 69.2667 | 946 | 65526.2667 | 69.2667 | 66.2667 | 0.19814 | 62688.2667 | 0.18955 | 0.0028605 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P36182 | Report from public that transformer on pole has blown up. Down from 84 Oroua road outside the equestrian centre transformer on pole has blown. Feeder switched out until it can be isolated. Turned out to be a tree branch on the line at pole P36182 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-19 | c | 0.18955 | 0.0028605 | 2016 | 2016-01-19 | C | 946 | 0.18955 | 0.0028605
9543157 | 2016-01-19 05:30 | 2016-01-19 08:00 | 149.6167 | 1 | 149.6167 | 149.6167 | 146.6167 | 0.0004524 | 146.6167 | 0.00044333 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TG6-004 | Reload Reliven. 2 x 5A Fuses due to Weather. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.00044333 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00044333 | 3.0238e-06
9543371 | 2016-01-19 05:53 | 2016-01-19 07:30 | 97.2167 | 1 | 97.2167 | 97.2167 | 94.2167 | 0.00029396 | 94.2167 | 0.00028489 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W5373 and Fuses at Pole 721772 | Reload reliven. Transformer W5373 - 3 x 3A Fuses and at Fuses on Pole 721772 - 1 x 6A Fuse. Unlabelled fuses to be identified and Labelled. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-01-19 | c | 0.00028489 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00028489 | 3.0238e-06
9543441 | 2016-01-19 06:27 | 2016-01-19 09:05 | 158.3167 | 3 | 474.95 | 158.3167 | 155.3167 | 0.0014361 | 465.95 | 0.0014089 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4019 | Reload Reliven 2 x 8A due to Fuses Lightning | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-01-19 | c | 0.0014089 | 9.071e-06 | 2016 | 2016-01-19 | C | 3 | 0.0014089 | 9.0713e-06
9543522 | 2016-01-19 01:30 | 2016-01-19 07:17 | 347 | 60 | 20820 | 347 | 344 | 0.062955 | 20640 | 0.06241 | 0.00018143 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1037 | 3 x 3amp fuse due to lightning | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.06241 | 0.00018143 | 2016 | 2016-01-19 | C | 60 | 0.06241 | 0.00018143
9543665 | 2016-01-18 01:46 | 2016-01-18 04:41 | 175.3833 | 2 | 350.7667 | 175.3833 | 172.3833 | 0.0010606 | 344.7667 | 0.0010425 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2152 | 2 x 2 amp fuse due to lightning | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-18 | c | 0.0010425 | 6.048e-06 | 2016 | 2016-01-18 | C | 2 | 0.0010425 | 6.0475e-06
9543839 | 2016-01-19 07:48 | 2016-01-19 09:50 | 121.5667 | 1 | 121.5667 | 121.5667 | 118.5667 | 0.00036759 | 118.5667 | 0.00035852 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1-017 | RLR 2 x 2A due to lightning. | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.00035852 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00035852 | 3.0238e-06
9543939 | 2016-01-19 08:15 | 2016-01-19 08:36 | 20.3 | 3268 | 57874.0667 | 17.7093 | 14.7093 | 0.175 | 48070.0667 | 0.14535 | 0.0098817 |  | 33 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 704734 & 704754 | Undertaking planned Switching 13394 to isolate and Earth OPK GXP 33kV CB's 1142, & 1122. Cb 1102 was offloaded. When operation 4 was carried out in the field, 33kV CB's 1142 and 1122 both tripped to lock out at 08:17hrs on O/C neutral time. * Resulted in | F1,F2,F3 | OPUNAKE 33KV | OPUNAKE | Taranaki | TP_OPUNAKE | Western Electricity | POWERCO | 2016-01-19 | b | 0.072676 | 0.0049408 | 2016 | 2016-01-19 | B | 3268 | 0.14535 | 0.0098817
9547243 | 2016-01-19 08:21 | 2016-01-19 09:20 | 59.35 | 1 | 59.35 | 59.35 | 56.35 | 0.00017946 | 56.35 | 0.00017039 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC770 | Reload Reliven. 2 x 2A due to Bird Strike. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.00017039 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00017039 | 3.0238e-06
9547381 | 2016-02-11 08:45 | 2016-02-11 09:54 | 69.4 | 41 | 2845.4 | 69.4 | 66.4 | 0.0086038 | 2722.4 | 0.0082319 | 0.00012397 | NAPA ID:15301 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 834313 | Move 11kV Pole 834313. Work location: Kiriwhakapapa Road, Masterton. W/O 30014820. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.0041159 | 6.1987e-05 | 2016 | 2016-02-11 | B | 41 | 0.0082319 | 0.00012397
9547761 | 2016-01-21 06:03 | 2016-01-21 06:39 | 36 | 111 | 3996 | 36 | 33 | 0.012083 | 3663 | 0.011076 | 0.00033564 | NAPA ID:16148 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12056/3 | Connect new 185 HV cable up pole 748242. Install new fusing at magnafix unit 58. HV fault on previous cable - replacing cable from RMU 12056/3 to pole 748242. Original fault: OMS 9506209 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-01-21 | b | 0.005538 | 0.00016782 | 2016 | 2016-01-21 | B | 111 | 0.011076 | 0.00033564
9548374 | 2016-02-12 08:30 | 2016-02-12 15:35 | 425 | 17 | 7225 | 425 | 422 | 0.021847 | 7174 | 0.021692 | 5.1404e-05 | NAPA ID:15648 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/342 | Replace conductor and Transfirner structure T 7/342 and pole 47221 and 11kV crossarms on pole 47219. Works location: Pongaroa Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-12 | b | 0.010846 | 2.5702e-05 | 2016 | 2016-02-12 | B | 17 | 0.021692 | 5.1404e-05
9548628 | 2016-01-19 08:48 | 2016-01-19 14:12 | 323.5667 | 4 | 885.0667 | 221.2667 | 218.2667 | 0.0026762 | 873.0667 | 0.0026399 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | TP1329 | at 11:02, Aongatete Sub, CB 5 Lockington Rd Feeder. Found transformer TP1329 had blown. Own Isolation & AP issued and repairs carried out. All Power Restored on completion. Hayden Bedgood attended. 1x Transformer, 2x HV Fuses. 2x 63A LV Fuses Replaced. Al | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.0026399 | 1.2095e-05 | 2016 | 2016-01-19 | C | 4 | 0.0026399 | 1.2095e-05
9548736 | 2016-02-16 08:15 | 2016-02-16 14:10 | 355 | 11 | 3905 | 355 | 352 | 0.011808 | 3872 | 0.011708 | 3.3261e-05 | NAPA ID:15657 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 47106 | Replace poles and crossarms 47106,47107,47108,47109,47110 & 11kv crossarms on TX 7/333 & 7/334. Works location: Mangaone Valley Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.005854 | 1.6631e-05 | 2016 | 2016-02-16 | B | 11 | 0.011708 | 3.3261e-05
9549316 | 2016-02-10 09:25 | 2016-02-10 14:37 | 312 | 61 | 19032 | 312 | 309 | 0.057548 | 18849 | 0.056995 | 0.00018445 | NAPA ID:15924 TP_CARRINGTON GXP > TP_CARRINGTON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 253 | New conductor install across new 33kV structure's 0012 to 0013. Works location: Ninia Rd. WO 30011788 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-10 | b | 0.028497 | 9.2225e-05 | 2016 | 2016-02-10 | B | 61 | 0.056995 | 0.00018445
9549948 | 2016-02-17 08:31 | 2016-02-17 14:20 | 349 | 16 | 5584 | 349 | 346 | 0.016885 | 5536 | 0.01674 | 4.838e-05 | NAPA ID:15691 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/327 | Replace 11kV cross arms on Transformer T7/327 & T7/326 Structures. Replace LV cross arms on transformers T7/327 & T7/326 Structures. Works location: Hinemoa Valley. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-17 | b | 0.0083698 | 2.419e-05 | 2016 | 2016-02-17 | B | 16 | 0.01674 | 4.838e-05
9549963 | 2016-02-18 08:30 | 2016-02-18 16:08 | 458 | 11 | 5038 | 458 | 455 | 0.015234 | 5005 | 0.015134 | 3.3261e-05 | NAPA ID:15662 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 47470 | Replace pole and cross arms 47470, 47471, 47472, 47473. Replace Transformer T7/333 & Transformer T7/334 LV arms. Works location: Mangaone Valley Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-18 | b | 0.007567 | 1.6631e-05 | 2016 | 2016-02-18 | B | 11 | 0.015134 | 3.3261e-05
9552156 | 2016-02-14 10:23 | 2016-02-14 15:49 | 326 | 1 | 326 | 326 | 323 | 0.00098575 | 323 | 0.00097667 | 3.0238e-06 | NAPA ID:15927 TP_CARRINGTON GXP > TP_CARRINGTON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 419 | New conductor install across new 33kV structure's 0004 to 0005. Works location: Corbett Rd. WO 30011788 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-14 | b | 0.00048834 | 1.512e-06 | 2016 | 2016-02-14 | B | 1 | 0.00097667 | 3.0238e-06
9552159 | 2016-01-19 10:12 | 2016-01-19 12:43 | 151.2667 | 5 | 756.3333 | 151.2667 | 148.2667 | 0.002287 | 741.3333 | 0.0022416 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FC4000 | Replace 2 x 8A Fuses | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.0022416 | 1.5119e-05 | 2016 | 2016-01-19 | C | 5 | 0.0022416 | 1.5119e-05
9552371 | 2016-02-15 08:15 | 2016-02-15 15:45 | 450 | 84 | 28083 | 334.3214 | 331.3214 | 0.084916 | 27831 | 0.084154 | 0.000254 | NAPA ID:15655 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/294 | Shut 1 - Replace structure 45376 and replace crossarms on pole 45717. Shut 2 - Replace cross arms & hardware on Tranformer T7/294 & replace poles and cross arms 45381,45382 &45375. Replace the remainder LV cross arms and Hardware on Transformer T7/294 & | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-15 | b | 0.042077 | 0.000127 | 2016 | 2016-02-15 | B | 84 | 0.084154 | 0.000254
9552429 | 2016-02-02 09:45 | 2016-02-02 14:43 | 298 | 597 | 62415 | 104.5477 | 101.5477 | 0.18873 | 60624 | 0.18331 | 0.0018052 | NAPA ID:16089 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 6 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8310 | We have to replace broken cross arm at 11kv fuses 8310 and cant for safety reasons use 11kv fuses 8372. We cant isolate Magnefix 1325 under load is why we are isolating from 11kv ABS 227. Works location: Veale Rd, New Plymouth. WO 30019120 | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-02-02 | b | 0.091656 | 0.00090259 | 2016 | 2016-02-02 | B | 597 | 0.18331 | 0.0018052
9552432 | 2016-02-13 08:31 | 2016-02-13 14:19 | 347.45 | 20 | 6946 | 347.3 | 344.3 | 0.021003 | 6886 | 0.020822 | 6.0475e-05 | NAPA ID:14444 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Miro Street Feeder CB C810 | To replace 11kv poles and crossarms. Lincoln Road, Masterton. W/O30013208 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-02-13 | b | 0.010411 | 3.0238e-05 | 2016 | 2016-02-13 | B | 20 | 0.020822 | 6.0475e-05
9552737 | 2016-01-19 17:30 | 2016-01-19 17:45 | 15 | 1 | 15 | 15 | 12 | 4.5356e-05 | 12 | 3.6285e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/141 | Removed stand off Insulator at Transformer T2/141. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-01-19 | c | 3.6285e-05 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 3.6285e-05 | 3.0238e-06
9554113 | 2016-01-19 18:04 | 2016-01-19 20:33 | 148.2333 | 1 | 148.2333 | 148.2333 | 145.2333 | 0.00044822 | 145.2333 | 0.00043915 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc2-153 | Replaced 2 x 3amp HT fuses at TC2-153 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.00043915 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00043915 | 3.0238e-06
9554286 | 2016-01-19 20:11 | 2016-01-19 21:35 | 83.6167 | 1 | 83.6167 | 83.6167 | 80.6167 | 0.00025284 | 80.6167 | 0.00024377 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4208 | Replaced 2 x 5amp fuses at FC4208. No outage on this job. The only Transformer affected is TC5710 which shows no ICP's connected but has one ICP. Referral job created to replace 11kV fuse mount - Glove and barrier. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-01-19 | c | 0.00024377 | 3.024e-06 | 2016 | 2016-01-19 | C | 1 | 0.00024377 | 3.0238e-06
9554928 | 2016-01-20 11:17 | 2016-01-20 13:01 | 104.2167 | 97 | 10109.0167 | 104.2167 | 101.2167 | 0.030567 | 9818.0167 | 0.029687 | 0.0002933 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 758535 | An outage was required from ABS 5591 on Salisbury Rd to replace a Pole. It appears there is evidence of a cracked pole causing an insulator to fail. It then burnt through the top of the pole and crossarm. The conductor was floating when found by the fault | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-01-20 | c | 0.029687 | 0.0002933 | 2016 | 2016-01-20 | C | 97 | 0.029687 | 0.0002933
9556027 | 2016-02-10 13:30 | 2016-02-10 14:14 | 44 | 2 | 88 | 44 | 41 | 0.00026609 | 82 | 0.00024795 | 6.0475e-06 | NAPA ID:16124 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Black Stump Feeder CB3 | Replace 11KV Cross Arm. 314 Bell Road, Papamoa. W/O30013429 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-02-10 | b | 0.00012397 | 3.024e-06 | 2016 | 2016-02-10 | B | 2 | 0.00024795 | 6.0475e-06
9556066 | 2016-01-21 18:00 | 2016-01-21 21:00 | 180 | 233 | 41940 | 180 | 177 | 0.12682 | 41241 | 0.1247 | 0.00070454 | NAPA ID:16174 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 18TH AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 383441 | Replace 11kV pole hit by car . | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2016-01-21 | b | 0.062351 | 0.00035227 | 2016 | 2016-01-21 | B | 233 | 0.1247 | 0.00070454
9556320 | 2016-01-20 11:27 | 2016-01-21 00:05 | 758 | 5 | 3790 | 758 | 755 | 0.01146 | 3775 | 0.011415 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | OUTAGE RESTORED | OUTAGE RESTORED | tc2-145 | 10.06am Power pole came down on the property after stay wire was hit with tractor. 10.07am advised Shannon at svs hub & advised control. Check possibly related OMS: 9556547. Isolated at fuses SC2-129. NDR to come from Mike Strange. 1 pole 1 transformer 50 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-20 | c | 0.011415 | 1.5119e-05 | 2016 | 2016-01-20 | C | 5 | 0.011415 | 1.5119e-05
9556415 | 2016-02-12 14:01 | 2016-02-12 14:10 | 9.5667 | 2 | 19.1333 | 9.5667 | 6.5667 | 5.7855e-05 | 13.1333 | 3.9712e-05 | 6.0475e-06 | NAPA ID:16112 TP_OPUNAKE GXP > NGARIKI SUB > SOUTH RD NGARIKI | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 713240 | 11kV Cable going to pole 713240 NG3 side will be reterminated to the TA7 side of ABS NG 306 between the 2 ABS?s NG306 & TA709. ABS TA709 is New Tie open point with NG306 closed in normal operation. South road Oaonui STOS. W/O30007903 | F1 | S.T.O.S. | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-02-12 | b | 1.9856e-05 | 3.024e-06 | 2016 | 2016-02-12 | B | 2 | 3.9712e-05 | 6.0475e-06
9556655 | 2016-01-20 11:21 | 2016-01-20 13:30 | 129.3167 | 1 | 129.3167 | 129.3167 | 126.3167 | 0.00039102 | 126.3167 | 0.00038195 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2620 | Reload reliven. 1 x 2A Fuses replaced. All 3 fuses pulled to repair stay wire. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-01-20 | c | 0.00038195 | 3.024e-06 | 2016 | 2016-01-20 | C | 1 | 0.00038195 | 3.0238e-06
9559768 | 2016-01-20 13:33 | 2016-01-20 13:35 | 2 | 508 | 1016 | 2 | -1 | 0.0030721 | 0 | 0 | 0.0015361 |  | 11 | Unplanned | ZONE SUB EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | CB 17 | CB17 Waharoa T1 Bank Tripped on Oil temp Alarm P Flag. Tripping coincident with removal of Oil Temp Transducer while staff were investigating a T2 Winding Temp Alarm (Low limit). Loss of supply to CBs 1 and 3. Reclosed OK. (2 Minute outage). To be investi | F1,F2,F3 | WALTON-WAHAROA 33KV | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-01-20 | c | 0 | 0.0015361 | 2016 | 2016-01-20 | C | 508 | 0 | 0.0015361
9565616 | 2016-01-21 09:45 | 2016-01-21 10:08 | 23 | 1 | 23 | 23 | 20 | 6.9546e-05 | 20 | 6.0475e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X2602 | Tranformer C2602 Fuses opened 09:45 for Self issue AP to Repair stay wire. Fuses closed 10:08. Gary Fisher attended. Defect Job. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-01-21 | c | 6.0475e-05 | 3.024e-06 | 2016 | 2016-01-21 | C | 1 | 6.0475e-05 | 3.0238e-06
9565648 | 2016-01-21 13:13 | 2016-01-21 13:55 | 42 | 2 | 84 | 42 | 39 | 0.000254 | 78 | 0.00023585 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752681 | Isolation required from Fuses 8446 to repair a floating conductor at Transformer 1336. (Dead ends had come off termination, required one new dead end). | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-01-21 | c | 0.00023585 | 6.048e-06 | 2016 | 2016-01-21 | C | 2 | 0.00023585 | 6.0475e-06
9565840 | 2016-01-22 08:45 | 2016-01-22 13:00 | 255 | 83 | 21165 | 255 | 252 | 0.063998 | 20916 | 0.063245 | 0.00025097 | NAPA ID:16219 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV pole E12881 | Replace pole hit by car. Works location: Harwoods Rd, Tapapa Tirau. WO 30007220 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-01-22 | b | 0.031622 | 0.00012549 | 2016 | 2016-01-22 | B | 83 | 0.063245 | 0.00025097
9565904 | 2016-01-22 07:26 | 2016-01-22 08:32 | 66 | 15 | 990 | 66 | 63 | 0.0029935 | 945 | 0.0028575 | 4.5356e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tauranga CB 20. Transformer TC4-700 | Transformer bushings tracking and needs attention. Shay Deegan to look at this Fri morning. Fm found this under survey work, questioned NOC about how he gets paid for today's visit, advised him discovery of the fault is covered under survey work pack and | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-01-22 | c | 0.0028575 | 4.5356e-05 | 2016 | 2016-01-22 | C | 15 | 0.0028575 | 4.5356e-05
9566272 | 2016-01-21 16:29 | 2016-01-21 17:35 | 66 | 40 | 2640 | 66 | 63 | 0.0079827 | 2520 | 0.0076199 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 831004 | FM advised he needs a bucket truck to do inspections and requested a 2R. Advised Neville to organise the bucket truck through the Downer Hub. Once he's determined the work that needs to happen on site, to give Dispatch a call and then it can be escalated | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-21 | c | 0.0076199 | 0.00012095 | 2016 | 2016-01-21 | C | 40 | 0.0076199 | 0.00012095
9566529 | 2016-01-21 16:46 | 2016-01-21 20:26 | 220.45 | 1 | 220.45 | 220.45 | 217.45 | 0.00066659 | 217.45 | 0.00065752 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t1581 | Lines down in paddock at 1671 Ponatahi Road from pole 819851. 4.46pm advised Dianne at SVS hub 3 X 3 amp Fuses at transformer T1581 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-21 | c | 0.00065752 | 3.024e-06 | 2016 | 2016-01-21 | C | 1 | 0.00065752 | 3.0238e-06
9566543 | 2016-01-21 16:49 | 2016-01-21 18:41 | 112.3833 | 14 | 1573.3667 | 112.3833 | 109.3833 | 0.0047575 | 1531.3667 | 0.0046305 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L3170 | at 17:52, Livingstone Sub, CB LI6 Portland Quay Feeder. Found jumper on bottom of DDO broken at Transformer L3170. Own Isolation & AP issued. Repairs carried out and all power restored on completion. Jared Tito Attended. 1x Jumper & 1x Conductor Joint Rep | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-01-21 | c | 0.0046305 | 4.2333e-05 | 2016 | 2016-01-21 | C | 14 | 0.0046305 | 4.2333e-05
9567572 | 2016-01-21 17:17 | 2016-01-21 18:28 | 70.7333 | 14 | 990.2667 | 70.7333 | 67.7333 | 0.0029943 | 948.2667 | 0.0028673 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5932 | 2HT Fuses tripped at Tree Fuses 5932 .Branch brought down by Tricky Trees working opposite side of Road. (Advised by Finn Parker - phone 027 8691896). Fuses relivened OK. To be investigated. 3 Fuses replaced at 15A. NDR #45803 | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-01-21 | c | 0.0028673 | 4.2333e-05 | 2016 | 2016-01-21 | C | 14 | 0.0028673 | 4.2333e-05
9569472 | 2016-01-29 09:31 | 2016-01-29 15:39 | 368 | 54 | 19872 | 368 | 365 | 0.060088 | 19710 | 0.059598 | 0.00016328 | NAPA ID:15650 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O861 | INSTALL NEW 12.5M POLE & RECONFIGURE 11KV LINES TO ENABLE INSTALL OF REPLACEMENT RECLOSER RC24/2 & LINKS RC24/4 & RC24/1 AT POLE O861. To be commissioned on the day of Install. Works location: Canal West Rd, Waitakaruru. WO 30013602 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-29 | b | 0.029799 | 8.1642e-05 | 2016 | 2016-01-29 | B | 54 | 0.059598 | 0.00016328
9569669 | 2016-02-02 08:30 | 2016-02-02 12:27 | 237 | 47 | 11139 | 237 | 234 | 0.033682 | 10998 | 0.033255 | 0.00014212 | NAPA ID:15970 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 756428 | Replace pole 756428 with a new 11m busck. install new 15 kva pole mount TX with new earthing system | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-02 | b | 0.016628 | 7.1058e-05 | 2016 | 2016-02-02 | B | 47 | 0.033255 | 0.00014212
9570712 | 2016-01-22 14:17 | 2016-01-22 15:33 | 75.6833 | 2 | 151.3667 | 75.6833 | 72.6833 | 0.0004577 | 145.3667 | 0.00043955 | 6.0475e-06 |  | 22 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 2708 | 2 Fuses Found Blown at Fuses 2708 - Cause bird strike. Used 2 x 15 amp | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-01-22 | c | 0.00043955 | 6.048e-06 | 2016 | 2016-01-22 | C | 2 | 0.00043955 | 6.0475e-06
9571360 | 2016-01-22 19:40 | 2016-01-23 13:20 | 1059.7833 | 75 | 42195 | 562.6 | 559.6 | 0.12759 | 41970 | 0.12691 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781564 | Recloser 1406 A/R, L/O, E/F, O/C. Sectionalised and patrolled as far as Fuses 195. Fuses 781 Opened and Fuses 195 closed, which tripped fRS 1406. RS 1406 reclosed and power left off for the night due to terrain making patrol impractical during the night. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-01-22 | c | 0.12691 | 0.00022678 | 2016 | 2016-01-22 | C | 75 | 0.12691 | 0.00022678
9571963 | 2016-01-22 21:16 | 2016-01-23 00:22 | 185.55 | 1997 | 48395.4 | 24.2341 | 21.2341 | 0.14634 | 42404.4 | 0.12822 | 0.0060385 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 3162 | at 21:16, Piako Sub, 33kV CB 3162 Tripped, Ph A B C O/C, INVT O/C, P2 Ph A B C O/C, P2 INVT O/C, L/O. Loss of supply to all of Walton Sub. Loss of Supply to Waharoa CB 1 & CB 3. Backfed WAH 1 & WAH 3 and All of Walton Sub from Hinuera GXP CB 282 Faultmen | F1,F2,F3 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 2016-01-22 | c | 0.12822 | 0.0060384 | 2016 | 2016-01-22 | C | 1997 | 0.12822 | 0.0060385
9573767 | 2016-01-22 21:29 | 2016-01-23 01:00 | 210.8 | 238 | 18233.2333 | 76.6102 | 73.6102 | 0.055133 | 17519.2333 | 0.052974 | 0.00071966 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790834 | CB 10, A/R, L/O, E/F, O/C A-B-C Phase. Line down and blown jumper at Pole 790834. Isolated at ABS 177 & Feeder Relivened. Materials used: 10metres of squirrel conductor, 3 sleeves, & 1 connector. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2016-01-22 | c | 0.052974 | 0.00071966 | 2016 | 2016-01-22 | C | 238 | 0.052974 | 0.00071966
9578799 | 2016-01-23 10:18 | 2016-01-23 12:17 | 118.8333 | 1 | 118.8333 | 118.8333 | 115.8333 | 0.00035932 | 115.8333 | 0.00035025 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2-153 | Replaced 2x 2a HV fuses | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-23 | c | 0.00035025 | 3.024e-06 | 2016 | 2016-01-23 | C | 1 | 0.00035025 | 3.0238e-06
9579794 | 2016-01-23 15:49 | 2016-01-23 18:30 | 161.4 | 1 | 161.4 | 161.4 | 158.4 | 0.00048803 | 158.4 | 0.00047896 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5373E | Fuses found blown at transformer 5373E transformer found to be faulty. Replaced 3 Phase, 11kV, 30kVA Transformer and 2x 2Amp Links. Unknown failure reason. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-01-23 | c | 0.00047896 | 3.024e-06 | 2016 | 2016-01-23 | C | 1 | 0.00047896 | 3.0238e-06
9579853 | 2016-01-23 16:50 | 2016-01-23 21:50 | 299.9667 | 3 | 899.9 | 299.9667 | 296.9667 | 0.0027211 | 890.9 | 0.0026939 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5911 | Replace 1 x 30 kVA 3phase Transformer | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2016-01-23 | c | 0.0026939 | 9.071e-06 | 2016 | 2016-01-23 | C | 3 | 0.0026939 | 9.0713e-06
9579860 | 2016-01-23 16:52 | 2016-01-23 17:32 | 39.95 | 122 | 4873.9 | 39.95 | 36.95 | 0.014738 | 4507.9 | 0.013631 | 0.0003689 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C429 | Recloser C429/ Found tripped - Closed at 17:32. Faultman requested to do line patrol after power restored | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-23 | c | 0.013631 | 0.0003689 | 2016 | 2016-01-23 | C | 122 | 0.013631 | 0.0003689
9580436 | 2016-01-23 22:40 | 2016-01-23 23:45 | 65.2833 | 61 | 3982.2833 | 65.2833 | 62.2833 | 0.012041 | 3799.2833 | 0.011488 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB T41 A/R, L/O, E/F, O/C C Phase. Patrolled with no fault found | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-01-23 | c | 0.011488 | 0.00018445 | 2016 | 2016-01-23 | C | 61 | 0.011488 | 0.00018445
9581689 | 2016-01-24 17:40 | 2016-01-24 19:20 | 100 | 7 | 700 | 100 | 97 | 0.0021166 | 679 | 0.0020531 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2712 | Fuses found blown at Fuses 2712 - line patrolled with no fault found. Used 2 x 8 amp fuses power back on at 19:20. Unable to force up to fuses as faultman had logged himself on site and LV fault so stuck | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-01-24 | c | 0.0020531 | 2.1166e-05 | 2016 | 2016-01-24 | C | 7 | 0.0020531 | 2.1166e-05
9582896 | 2016-01-25 01:53 | 2016-01-25 04:00 | 127 | 24 | 3048 | 127 | 124 | 0.0092164 | 2976 | 0.0089987 | 7.257e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6839 | Broken Dead ends found by faultman - isolated at ABS's KA 749, KA710, KA780,& 6757 with a backfeed via VS 8726. Used 6 x 35mm Dead ends | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 2016-01-25 | c | 0.0089987 | 7.257e-05 | 2016 | 2016-01-25 | C | 24 | 0.0089987 | 7.257e-05
9583922 | 2016-02-24 08:45 | 2016-02-25 13:47 | 1742 | 3 | 141 | 47 | 44 | 0.00042635 | 132 | 0.00039914 | 9.0713e-06 | NAPA ID:15234 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1567 | Reconductor between pole structures T13088 and T1567. Works location: Thames Coast Rd, Thames. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-24 | b | 0.00019957 | 4.536e-06 | 2016 | 2016-02-24 | B | 3 | 0.00039914 | 9.0713e-06
9584075 | 2016-01-30 09:36 | 2016-01-30 12:30 | 174.4333 | 120 | 20932 | 174.4333 | 171.4333 | 0.063293 | 20572 | 0.062205 | 0.00036285 | NAPA ID:16303 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V27 | To install new 10m busck pole and lift 11kv conductor | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-01-30 | b | 0.031102 | 0.00018143 | 2016 | 2016-01-30 | B | 120 | 0.062205 | 0.00036285
9584650 | 2016-02-16 09:15 | 2016-02-16 14:45 | 330 | 41 | 13530 | 330 | 327 | 0.040911 | 13407 | 0.04054 | 0.00012397 | NAPA ID:15818 TP_GREYTOWN GXP > HAU NUI SUB > TUTURUMURI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T4121 | Replace Transformers T4120 and T4121. Works location: Tora Rd, Te Awaiti. WO 30002199 Faultman infirm Control room that only T4121 is going to be replaced. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.02027 | 6.1987e-05 | 2016 | 2016-02-16 | B | 41 | 0.04054 | 0.00012397
9584669 | 2016-02-25 08:09 | 2016-02-25 15:29 | 440.5833 | 35 | 15420.4167 | 440.5833 | 437.5833 | 0.046628 | 15315.4167 | 0.04631 | 0.00010583 | NAPA ID:15907 TP_TAURANGA 33 GXP > KATIKATI SUB > MURAL TOWN | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU 13042 | Replace Link Boxes SB2-025 & SB2-065 with new RMU's 13042 & 13043 and 11kV Cables. Works location: Fairview Rd, Katikati. WO 30011142 | F3 | MURAL TOWN | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2016-02-25 | b | 0.023155 | 5.2916e-05 | 2016 | 2016-02-25 | B | 35 | 0.04631 | 0.00010583
9584672 | 2016-02-16 09:52 | 2016-02-16 13:19 | 207 | 51 | 10557 | 207 | 204 | 0.031922 | 10404 | 0.031459 | 0.00015421 | NAPA ID:15813 TP_MATAROA GXP > WAIOURU SUB > RUAPEHU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1478 | Repair oil leak and top and oil in transformer. Works location: Bullot St, Waiouru. WO 10162468 | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.01573 | 7.7106e-05 | 2016 | 2016-02-16 | B | 51 | 0.031459 | 0.00015421
9584705 | 2016-02-16 08:59 | 2016-02-16 15:10 | 371 | 19 | 7049 | 371 | 368 | 0.021314 | 6992 | 0.021142 | 5.7451e-05 | NAPA ID:15376 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 014 | Replace 11kv poles on the Parapara road. Works location: Parapara Rd. WO 30002305 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-16 | b | 0.010571 | 2.8726e-05 | 2016 | 2016-02-16 | B | 19 | 0.021142 | 5.7451e-05
9585283 | 2016-02-03 09:30 | 2016-02-03 14:26 | 296 | 58 | 16770 | 289.1379 | 286.1379 | 0.050708 | 16596 | 0.050182 | 0.00017538 | NAPA ID:15517 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 308 | Remove ABS190 and Pole745080 and install 12.5m busck with a DAS 12127/2 + Source Links 12127/4 and Load Links 12127/6. Works location: Cross Rd, Lepperton. WO 30001892 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-03 | b | 0.025091 | 8.7689e-05 | 2016 | 2016-02-03 | B | 58 | 0.050182 | 0.00017538
9585321 | 2016-02-16 10:00 | 2016-02-16 11:55 | 115 | 7 | 805 | 115 | 112 | 0.0024341 | 784 | 0.0023706 | 2.1166e-05 | NAPA ID:16128 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10148 | To replace damaged conductor. Works location: Kaituna Rd. WO 10162794 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.0011853 | 1.0583e-05 | 2016 | 2016-02-16 | B | 7 | 0.0023706 | 2.1166e-05
9585363 | 2016-02-16 09:42 | 2016-02-16 11:59 | 137 | 1 | 137 | 137 | 134 | 0.00041426 | 134 | 0.00040518 | 3.0238e-06 | NAPA ID:16127 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V25 | To install deadman stays and pull back badly leaning pole. Works location: Route 52. WO 10162794 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.00020259 | 1.512e-06 | 2016 | 2016-02-16 | B | 1 | 0.00040518 | 3.0238e-06
9585446 | 2016-01-25 14:50 | 2016-01-25 18:15 | 204.75 | 272 | 17480.2 | 64.2654 | 61.2654 | 0.052856 | 16664.2 | 0.050389 | 0.00082246 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | W13402 | Lines down reported on 467 Boat Harbor Road. ( TAI 5 ) recloser 9170/2 tripped E/F, L/O. Line down x 1 at pole W13402. Isolation at ABS 323 ( spur no back feed ) Remainder of feeder returned to service with recloser 9170 closed.Line repaired all service r | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-01-25 | c | 0.050389 | 0.00082246 | 2016 | 2016-01-25 | C | 272 | 0.050389 | 0.00082246
9587198 | 2016-01-25 20:00 | 2016-01-25 23:26 | 205.6167 | 9 | 1850.55 | 205.6167 | 202.6167 | 0.0055956 | 1823.55 | 0.005514 | 2.7214e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 264/2 | 2 x 8A HV Fuse. Check 490, 540 and 869 Mangatoi Rd - OMS 9587229, 9587207 and 9587213 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-01-25 | c | 0.005514 | 2.7214e-05 | 2016 | 2016-01-25 | C | 9 | 0.005514 | 2.7214e-05
9587519 | 2016-01-26 04:55 | 2016-01-26 07:15 | 140.1667 | 2 | 280.3333 | 140.1667 | 137.1667 | 0.00084766 | 274.3333 | 0.00082952 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6393 | reload reliven. 2 x 6A Fuses. Suspect bird strike | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.00082952 | 6.048e-06 | 2016 | 2016-01-26 | C | 2 | 0.00082952 | 6.0475e-06
9588625 | 2016-01-26 09:28 | 2016-01-26 10:40 | 72 | 71 | 5112 | 72 | 69 | 0.015457 | 4899 | 0.014813 | 0.00021469 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 761091 | Somewhere between Midhurst and Croyden Rd Train Driver reported a large explosion and a shower of sparks 0273668860. 06:00 Report from Fire Service that a Truck has taken out a Pole. Brett advised that address is 2729 Mountain Road. Isolated fault betwe | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.014813 | 0.00021469 | 2016 | 2016-01-26 | C | 71 | 0.014813 | 0.00021469
9588653 | 2016-01-26 06:04 | 2016-01-26 07:48 | 103.45 | 1 | 103.45 | 103.45 | 100.45 | 0.00031281 | 100.45 | 0.00030374 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7604 | 2 X 10 Amp at Fuses 7604 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.00030374 | 3.024e-06 | 2016 | 2016-01-26 | C | 1 | 0.00030374 | 3.0238e-06
9588899 | 2016-01-26 07:36 | 2016-01-26 14:07 | 391.3667 | 1 | 391.3667 | 391.3667 | 388.3667 | 0.0011834 | 388.3667 | 0.0011743 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5106E | Found transformer 5106E faulty. Isolated at fuses and changed trany 15kvA | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.0011743 | 3.024e-06 | 2016 | 2016-01-26 | C | 1 | 0.0011743 | 3.0238e-06
9588973 | 2016-01-26 07:51 | 2016-01-26 10:40 | 169.35 | 2 | 338.7 | 169.35 | 166.35 | 0.0010241 | 332.7 | 0.001006 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP668 | Reload Reliven. 2 x 6A. Bird Strike | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-01-26 | c | 0.001006 | 6.048e-06 | 2016 | 2016-01-26 | C | 2 | 0.001006 | 6.0475e-06
9589126 | 2016-01-26 08:31 | 2016-01-26 10:52 | 140.9333 | 1886 | 84131.15 | 44.6082 | 41.6082 | 0.25439 | 78473.15 | 0.23728 | 0.0057028 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | P44856 | Cable Fault at Pole P44856 Red Pin Number 160117 | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.23728 | 0.0057028 | 2016 | 2016-01-26 | C | 1886 | 0.23728 | 0.0057028
9591844 | 2016-01-26 11:56 | 2016-01-26 14:35 | 159 | 14 | 1776 | 126.8571 | 123.8571 | 0.0053702 | 1734 | 0.0052432 | 4.2333e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC3-026 | Fuses SC3-027 Opened to isolate Fuse box SC3-026.. Found cable fault between fuses SC3 026 & transformer TC3 107. 11kV cable disconnected at Fuses SC3 026 & transformer TC3 107. Transformer TC3 107 L/V fuses open & tagged, generator connected. Fuses SC3 0 | F4 | PLUMMERS POINT | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-01-26 | c | 0.0052432 | 4.2333e-05 | 2016 | 2016-01-26 | C | 14 | 0.0052432 | 4.2333e-05
9592718 | 2016-01-26 10:31 | 2016-01-26 15:13 | 282.4 | 575 | 25999.4333 | 45.2164 | 42.2164 | 0.078616 | 24274.4333 | 0.0734 | 0.0017387 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9147/2 | ( TPV 3 ) recloser 9147/2 tripped A, B & C phase O/C, L/O. Report of cable strike beyond Fused/Sw 9345/4 at time of tripping a HLT was applied to recloser 9147/2 (safety measure for planned NAPA job15394. Isolation at Sw/Gear 9418/2 ( report of damage to | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-01-26 | c | 0.0734 | 0.0017387 | 2016 | 2016-01-26 | C | 575 | 0.0734 | 0.0017387
9594001 | 2016-01-26 11:32 | 2016-01-26 12:44 | 72.55 | 474 | 34388.7 | 72.55 | 69.55 | 0.10398 | 32966.7 | 0.099683 | 0.0014333 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 363 | Remote Control Sw/Gear open. is 9595227 linked? Still no sure why it opened. PI Load profile for Denbigh Feeder shows outage initiated at 11:33. | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.099683 | 0.0014333 | 2016 | 2016-01-26 | C | 474 | 0.099683 | 0.0014333
9595949 | 2016-02-19 08:40 | 2016-02-19 13:25 | 285 | 19 | 5415 | 285 | 282 | 0.016374 | 5358 | 0.016201 | 5.7451e-05 | NAPA ID:15497 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 014 | Replace 11kv poles on the Parapara road. WO 30002305 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-19 | b | 0.0081007 | 2.8726e-05 | 2016 | 2016-02-19 | B | 19 | 0.016201 | 5.7451e-05
9596475 | 2016-01-26 17:25 | 2016-01-26 17:33 | 8 | 1 | 8 | 8 | 5 | 2.419e-05 | 5 | 1.5119e-05 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4690W | 2.56pm advised Tallia at svs hub. Tapped Transformer down 2 Taps to get to 236 237 236. Off at 17:25 On at 17:33 | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-01-26 | c | 1.5119e-05 | 3.024e-06 | 2016 | 2016-01-26 | C | 1 | 1.5119e-05 | 3.0238e-06
9598492 | 2016-01-26 17:55 | 2016-01-26 19:56 | 120.45 | 1079 | 38024.4833 | 35.2405 | 32.2405 | 0.11498 | 34787.4833 | 0.10519 | 0.0032626 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P41334 | Line repaired @ pole P41334 and cable disconnected between pole P41336 and switchgear 10173/4 to be replaced on DNO 160120 | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-01-26 | c | 0.10519 | 0.0032626 | 2016 | 2016-01-26 | C | 1079 | 0.10519 | 0.0032626
9602981 | 2016-01-26 17:08 | 2016-01-26 20:12 | 184.4667 | 393 | 72495.4 | 184.4667 | 181.4667 | 0.21921 | 71316.4 | 0.21564 | 0.0011883 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3979 | Emergency isolation at ABS IC2125 to replace HV Fuse Holder at Transformer TC3979. 1 x 10A Fuse and Holder | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-01-26 | c | 0.21564 | 0.0011883 | 2016 | 2016-01-26 | C | 393 | 0.21564 | 0.0011883
9604283 | 2016-01-26 23:33 | 2016-01-27 02:02 | 148.6833 | 6 | 892.1 | 148.6833 | 145.6833 | 0.0026975 | 874.1 | 0.0026431 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7-120 | LV Connections loose. Cleaned up repaired connections | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-26 | c | 0.0026431 | 1.8143e-05 | 2016 | 2016-01-26 | C | 6 | 0.0026431 | 1.8143e-05
9604312 | 2016-01-27 03:52 | 2016-01-27 06:45 | 173.3167 | 424 | 4877.8167 | 11.5043 | 8.5043 | 0.014749 | 3605.8167 | 0.010903 | 0.0012821 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207363 | at 03:51 Waihi Beach Sub, CB 5 Athenree Feeder. Police called in Car v Pole. Isolated lines at SA2-003 & IP631. Backfeed supplied from KPT 2, Recloser 9405 Closed. Permit issued & repairs carried out. All Power Restored on Completion. Pole 207363. NDR 316 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.010903 | 0.0012821 | 2016 | 2016-01-27 | C | 424 | 0.010903 | 0.0012821
9605409 | 2016-01-27 06:07 | 2016-01-27 06:09 | 2.4833 | 1794 | 4455.1 | 2.4833 | -0.51667 | 0.013471 | 0 | 0 | 0.0054246 |  | 33 | Unplanned | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | CB3042 | Opened under SIN 16125 (Switching for Transpower). Abnormal 33kV Network configuration at the time and when opening CB 3042 power was lost to the Waharoa Sub which was being fed from Hinuera and not Piako as would be normal. MABS PC221 Open at Walton. | F1,F2,F3 | HINUERA282-LAKE RD 33KV | HINUERA | Valley | TP_HINUERA | Eastern Electricity | POWERCO | 2016-01-27 | c | 0 | 0.0054246 | 2016 | 2016-01-27 | C | 1794 | 0 | 0.0054246
9607444 | 2016-01-27 23:55 | 2016-01-27 23:57 | 1.7 | 405 | 686.8 | 1.6958 | -1.3042 | 0.0020767 | 0 | 0 | 0.0012246 | Referral | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 207363 | switching to be carried out to return feeders to normal config, feeder returned to normal config see oms 9604312 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0 | 0.0012246 | 2016 | 2016-01-27 | C | 405 | 0 | 0.0012246
9607539 | 2016-02-19 09:09 | 2016-02-19 12:59 | 229.35 | 18 | 4128.3 | 229.35 | 226.35 | 0.012483 | 4074.3 | 0.01232 | 5.4428e-05 | NAPA ID:15753 TP_MASTERTON GXP > AWATOITOI SUB > ROROKOKO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1873 | Replace 2 defective transformer poles t1873 & t891. Once 11kv lines are back up on t/x poles liven the feeder back up and get permit to work below ddo's on t1873 and t891. Works location: Homewood Rd, Masterton. WO 30015875 | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-02-19 | b | 0.0061599 | 2.7214e-05 | 2016 | 2016-02-19 | B | 18 | 0.01232 | 5.4428e-05
9607798 | 2016-01-27 09:11 | 2016-01-27 11:14 | 123 | 250 | 18448.1 | 73.7924 | 70.7924 | 0.055783 | 17698.1 | 0.053515 | 0.00075594 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | R11 | CB R11 L/O on E/F. Sectionalised CB 7 found no fault | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-01-27 | c | 0.053515 | 0.00075594 | 2016 | 2016-01-27 | C | 250 | 0.053515 | 0.00075594
9608997 | 2016-02-11 09:45 | 2016-02-11 15:32 | 347 | 2 | 694 | 347 | 344 | 0.0020985 | 688 | 0.0020803 | 6.0475e-06 | NAPA ID:15201 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Change 33Kv pole 754802 with 11Kv line from DDO8567 on same pole. Second AP is to rebuild 33kV line and to remove 33kV ABS 3305. ABS 3305 will be removed form the network during this AP. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-11 | b | 0.0010402 | 3.024e-06 | 2016 | 2016-02-11 | B | 2 | 0.0020803 | 6.0475e-06
9609508 | 2016-01-27 10:12 | 2016-01-27 12:20 | 127.7 | 1 | 127.7 | 127.7 | 124.7 | 0.00038613 | 124.7 | 0.00037706 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SF5-026 | 10.13am advised Joanne at svs hub. NDR #53062. Branch broke off and landed on 11KV spur line while neighbors were trimming trees. Nothing else repaired or replaced. All surrounding assets are up to Powerco standard FM has also issued a CPP - Permit # FM h | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.00037706 | 3.024e-06 | 2016 | 2016-01-27 | C | 1 | 0.00037706 | 3.0238e-06
9609656 | 2016-02-12 09:45 | 2016-02-18 09:22 | 8617 | 2 | 92 | 46 | 43 | 0.00027819 | 86 | 0.00026004 | 6.0475e-06 | NAPA ID:15202 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754832 | Fitted Generator to Transformer 2043N to install new conductor for dual Circuit 33kv line. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-12 | b | 0.00013002 | 3.024e-06 | 2016 | 2016-02-12 | B | 2 | 0.00026004 | 6.0475e-06
9609823 | 2016-02-19 09:24 | 2016-02-19 18:40 | 556 | 56 | 15029.7 | 268.3875 | 265.3875 | 0.045446 | 14861.7 | 0.044938 | 0.00016933 | NAPA ID:15622 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS D2 | Change 13 x 33kv Xarms, and 30 extra insulators. 6 x 11kv xarms and 21 extra insulators. Works location: Setters Line, Milson. WO 30014403. The job over ran by over 3 hours. This is being followed up. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-19 | b | 0.022469 | 8.4665e-05 | 2016 | 2016-02-19 | B | 56 | 0.044938 | 0.00016933
9610482 | 2016-02-23 09:54 | 2016-02-23 15:00 | 306 | 10 | 3060 | 306 | 303 | 0.0092527 | 3030 | 0.009162 | 3.0238e-05 | NAPA ID:15626 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/247 | Change 2 x 33kV cross arms, and 6 extra insulators. 1 x 11kV cross arms and 12 extra insulators. Transformer T2/247 complete with pole and all hardware. Works location: Milson Line. WO 30014403 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-23 | b | 0.004581 | 1.5119e-05 | 2016 | 2016-02-23 | B | 10 | 0.009162 | 3.0238e-05
9610485 | 2016-02-02 11:05 | 2016-02-02 15:03 | 237.5167 | 3 | 712.55 | 237.5167 | 234.5167 | 0.0021546 | 703.55 | 0.0021274 | 9.0713e-06 | NAPA ID:16419 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Remove transformer cable TE5-247 from Fuses FP1745 and lower to ground. Replace G/M Transformer TE5-247. Replace X-arm and Fuses FP1745 at pole 222869. Reconnect transformer cable to Fuses FP1745. Commission new G/M Transformer TE5-247. | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2016-02-02 | b | 0.0010637 | 4.536e-06 | 2016 | 2016-02-02 | B | 3 | 0.0021274 | 9.0713e-06
9610594 | 2016-02-16 09:15 | 2016-02-16 14:11 | 295.6667 | 118 | 34888.6667 | 295.6667 | 292.6667 | 0.10549 | 34534.6667 | 0.10442 | 0.0003568 | NAPA ID:15831 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 7 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 702594 | Replace 11kV pole 702594 under access permit after putting in live line break at pole702551. Works location: Whitley St, New Plymouth. WO 30008374 | F2 | MOTUROA 7 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.052212 | 0.0001784 | 2016 | 2016-02-16 | B | 118 | 0.10442 | 0.0003568
9610703 | 2016-02-20 06:00 | 2016-02-20 08:13 | 133 | 21 | 2793 | 133 | 130 | 0.0084454 | 2730 | 0.0082549 | 6.3499e-05 | NAPA ID:16354 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 7 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer G189 | 1Yr maintenance on Magnefix G189a/b/t. Works location: Waldergrave St. WO 30003942 | F3 | PASCAL ST 7 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-02-20 | b | 0.0041274 | 3.1749e-05 | 2016 | 2016-02-20 | B | 21 | 0.0082549 | 6.3499e-05
9610841 | 2016-02-21 13:12 | 2016-02-21 15:54 | 161.7667 | 1 | 161.7667 | 161.7667 | 158.7667 | 0.00048914 | 158.7667 | 0.00048007 | 3.0238e-06 | NAPA ID:16103 TP_BUNNYTHORPE GXP > MAIN ST SUB > MAIN ST 12 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer G317 | Change transformer G317 over from old magnefix to new safelink switch. Works location; Princess St. WO 30015862 | F3 | KEITH ST 21 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 2016-02-21 | b | 0.00024004 | 1.512e-06 | 2016 | 2016-02-21 | B | 1 | 0.00048007 | 3.0238e-06
9610859 | 2016-01-27 18:00 | 2016-01-27 19:00 | 60 | 10 | 600 | 60 | 57 | 0.0018143 | 570 | 0.0017235 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 709456. | 342 Matau North Road. Found branch on main line. Isolated at fuses 5514 & removed branch, relivened. Branch on the 11kv lines. Removed branch. Full power restored. Nothing else repaired or replaced. Adjacent assets up to Powerco standards. NDR 15805. | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-27 | c | 0.0017235 | 3.0238e-05 | 2016 | 2016-01-27 | C | 10 | 0.0017235 | 3.0238e-05
9611058 | 2016-01-27 15:40 | 2016-01-27 16:23 | 43 | 14 | 550 | 39.2857 | 36.2857 | 0.0016631 | 508 | 0.0015361 | 4.2333e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC3-026 | Power all restored at 16:23. Tom Brownlee & Shae Deegan Attended. Job is part of DNO 160119. This outage was to reconnect cables at Fuses SC3-026/L1. 1x HV Joint Kit, 2x HV Fuses Replaced. DNO 160119. Cable Replacement. | F4 | PLUMMERS POINT | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.0015361 | 4.2333e-05 | 2016 | 2016-01-27 | C | 14 | 0.0015361 | 4.2333e-05
9611946 | 2016-01-27 17:31 | 2016-01-27 18:37 | 66.3667 | 19 | 1247.65 | 65.6658 | 62.6658 | 0.0037726 | 1190.65 | 0.0036002 | 5.7451e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 450 | 131 Rangitane Rd. Replaced 2x10a HV fuses @ 450 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-01-27 | c | 0.0036002 | 5.7451e-05 | 2016 | 2016-01-27 | C | 19 | 0.0036002 | 5.7451e-05
9612058 | 2016-01-27 17:58 | 2016-01-28 00:42 | 404.4167 | 7 | 2830.9167 | 404.4167 | 401.4167 | 0.00856 | 2809.9167 | 0.0084965 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1754 | Replace faulty transformer TC1754 ( lightning ). Materials 1 x 50KVA | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.0084965 | 2.1166e-05 | 2016 | 2016-01-27 | C | 7 | 0.0084965 | 2.1166e-05
9612169 | 2016-01-27 18:21 | 2016-01-27 23:17 | 295.8 | 4 | 1183.2 | 295.8 | 292.8 | 0.0035777 | 1171.2 | 0.0035414 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1037 | Transformer TC1037 blown due to lightning D Masters own isolation & AP to replace transformer replaced all service restored. Material 1 x 30KVA | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.0035414 | 1.2095e-05 | 2016 | 2016-01-27 | C | 4 | 0.0035414 | 1.2095e-05
9612766 | 2016-01-27 19:20 | 2016-01-27 23:37 | 256.9167 | 121 | 8960.9833 | 74.0577 | 71.0577 | 0.027096 | 8597.9833 | 0.025998 | 0.00036588 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C429 | CB C429 found open on arrival and closed. Line patrolled with no obvious fault found | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-27 | c | 0.025998 | 0.00036587 | 2016 | 2016-01-27 | C | 121 | 0.025998 | 0.00036588
9613171 | 2016-01-27 21:25 | 2016-01-27 23:48 | 142.7667 | 29 | 4140.2333 | 142.7667 | 139.7667 | 0.012519 | 4053.2333 | 0.012256 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1438 | KPE 1 replace 2 x 20A H/V, O/H fuses unknown | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-27 | c | 0.012256 | 8.7689e-05 | 2016 | 2016-01-27 | C | 29 | 0.012256 | 8.7689e-05
9615360 | 2016-01-28 06:04 | 2016-01-28 07:10 | 66.4667 | 43 | 2858.0667 | 66.4667 | 63.4667 | 0.0086421 | 2729.0667 | 0.008252 | 0.00013002 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2984 | Reload Reliven at fuses 2984. 2 x 10 A Fuses. Cause Suspected Bird Strike | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-01-28 | c | 0.008252 | 0.00013002 | 2016 | 2016-01-28 | C | 43 | 0.008252 | 0.00013002
9615390 | 2016-01-28 06:24 | 2016-01-28 08:30 | 125.8 | 2 | 251.6 | 125.8 | 122.8 | 0.00076078 | 245.6 | 0.00074264 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1231 | Reload Reliven at Fuses FP1231. 3 x 6A Fuses. Cause: Lightning. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-28 | c | 0.00074264 | 6.048e-06 | 2016 | 2016-01-28 | C | 2 | 0.00074264 | 6.0475e-06
9619129 | 2016-01-28 08:23 | 2016-01-28 15:01 | 397.9667 | 268 | 93150.0333 | 347.5748 | 344.5748 | 0.28166 | 92346.0333 | 0.27923 | 0.00081037 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 708759 | Tripping on Strathmore CB7131 on A-B Phase. Patrol carried out, livened to ABS 5229. Report of 2 lines down on Ohura Rd (Isolation from ABS 53229). Fault had been caused by a native tree falling through lines which were rehung OK (4 Sleeves used). Also to | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-01-28 | c | 0.27923 | 0.00081037 | 2016 | 2016-01-28 | C | 268 | 0.27923 | 0.00081037
9621102 | 2016-02-17 09:15 | 2016-02-19 13:47 | 3152 | 187 | 11968 | 64 | 61 | 0.036188 | 11407 | 0.034492 | 0.00056544 | NAPA ID:16143 TP_LINTON GXP > TURITEA SUB > MASSEY | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/473 | Cut in new switch 10219 (CCC) between T2/473 and 306, test commission and put into service. Works location: Tennent Dr. WO 10157874 | F1 | SUMMERHILL | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-02-17 | b | 0.017246 | 0.00028272 | 2016 | 2016-02-17 | B | 187 | 0.034492 | 0.00056544
9621343 | 2016-02-17 09:00 | 2016-02-17 12:56 | 236 | 6 | 1416 | 236 | 233 | 0.0042816 | 1398 | 0.0042272 | 1.8143e-05 | NAPA ID:15057 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5896 | To complete line maintenance on SH 27 Patetonga. WO 30016728 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-02-17 | b | 0.0021136 | 9.071e-06 | 2016 | 2016-02-17 | B | 6 | 0.0042272 | 1.8143e-05
9621348 | 2016-01-28 10:04 | 2016-01-28 12:10 | 125.85 | 1 | 125.85 | 125.85 | 122.85 | 0.00038054 | 122.85 | 0.00037147 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2841 | Reload Reliven at Tranformer TC2841. 2 x 3A Fuses. Cause: Lightning. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-28 | c | 0.00037147 | 3.024e-06 | 2016 | 2016-01-28 | C | 1 | 0.00037147 | 3.0238e-06
9621540 | 2016-02-27 09:16 | 2016-02-27 13:34 | 258.3167 | 40 | 10332.6667 | 258.3167 | 255.3167 | 0.031244 | 10212.6667 | 0.030881 | 0.00012095 | NAPA ID:15823 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P39176 | Install new pole between P39176 and P39133 and install new RL15 sectionalizer on it. Works location: Te Arakura Rd. WO 30001891 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-27 | b | 0.01544 | 6.0475e-05 | 2016 | 2016-02-27 | B | 40 | 0.030881 | 0.00012095
9622134 | 2016-01-28 13:08 | 2016-01-28 15:16 | 128.4833 | 9 | 1156.35 | 128.4833 | 125.4833 | 0.0034965 | 1129.35 | 0.0034149 | 2.7214e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4709 | Replace 2 x 3A Fuses 4709. Cause: Bird. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-01-28 | c | 0.0034149 | 2.7214e-05 | 2016 | 2016-01-28 | C | 9 | 0.0034149 | 2.7214e-05
9622237 | 2016-02-19 09:09 | 2016-02-19 16:58 | 469 | 21 | 9849 | 469 | 466 | 0.029781 | 9786 | 0.029591 | 6.3499e-05 | NAPA ID:16386 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV F40 | Cut trees from around the 11kv and check lean pole in spring. Works location: Pohangina Valley East Rd. WO 10161955 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-02-19 | b | 0.014795 | 3.1749e-05 | 2016 | 2016-02-19 | B | 21 | 0.029591 | 6.3499e-05
9622320 | 2016-01-28 13:55 | 2016-01-28 15:20 | 85.3167 | 1 | 85.3167 | 85.3167 | 82.3167 | 0.00025798 | 82.3167 | 0.00024891 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4854 | Replace 2 x 3A Fuse due to lightning. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-01-28 | c | 0.00024891 | 3.024e-06 | 2016 | 2016-01-28 | C | 1 | 0.00024891 | 3.0238e-06
9622457 | 2016-01-28 14:36 | 2016-01-28 15:26 | 49.2333 | 1526 | 30368.1333 | 19.9005 | 16.9005 | 0.091826 | 25790.1333 | 0.077983 | 0.0046143 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 364354 | CB C810 AR O/C trip. Suspect that tripping caused because the lines are on same pole as the lines from C817 which tripped at the same time. A Tree was felled through the lines, no damage to lines but caused the tripping. Lines checked and no other damage | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-01-28 | c | 0.077983 | 0.0046143 | 2016 | 2016-01-28 | C | 1526 | 0.077983 | 0.0046143
9625132 | 2016-01-28 17:54 | 2016-01-28 20:10 | 136.4833 | 1 | 136.4833 | 136.4833 | 133.4833 | 0.00041269 | 133.4833 | 0.00040362 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2940 | 2 X 2 Amp Fuses | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-01-28 | c | 0.00040362 | 3.024e-06 | 2016 | 2016-01-28 | C | 1 | 0.00040362 | 3.0238e-06
9626503 | 2016-01-29 06:17 | 2016-01-29 07:18 | 61.5167 | 304 | 18535.7167 | 60.9728 | 57.9728 | 0.056048 | 17623.7167 | 0.05329 | 0.00091922 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 AON | Feeder sectionalised. no fault found. Feeder Patrolled Nothing found | F4 | LOCKINGTON ROAD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.05329 | 0.00091922 | 2016 | 2016-01-29 | C | 304 | 0.05329 | 0.00091922
9628044 | 2016-01-29 07:05 | 2016-01-29 09:20 | 134.85 | 283 | 37582.6 | 132.8007 | 129.8007 | 0.11364 | 36733.6 | 0.11107 | 0.00085572 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | N1682 | Recloser RC33 Trip. No Flags. Feeder sectionalised fault found to be a bird on the line at pole N1682. Bird removed with fuse stick and feeder re-livened. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.11107 | 0.00085572 | 2016 | 2016-01-29 | C | 283 | 0.11107 | 0.00085572
9629360 | 2016-01-29 08:28 | 2016-01-29 10:35 | 127.1 | 380 | 35336.75 | 92.9914 | 89.9914 | 0.10685 | 34196.75 | 0.1034 | 0.001149 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2883T | Found Lightening arrestor cable touching lines. Removed with hot sticks and site is not clear of any fault. Relivened OK | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-01-29 | c | 0.1034 | 0.001149 | 2016 | 2016-01-29 | C | 380 | 0.1034 | 0.001149
9630727 | 2016-02-23 09:30 | 2016-02-23 12:27 | 177 | 9 | 1593 | 177 | 174 | 0.0048169 | 1566 | 0.0047352 | 2.7214e-05 | NAPA ID:16434 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P01622 | Replace 11kV pole at P01622. Works location: Scott Rd. WO 30017869 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-02-23 | b | 0.0023676 | 1.3607e-05 | 2016 | 2016-02-23 | B | 9 | 0.0047352 | 2.7214e-05
9630768 | 2016-02-23 08:26 | 2016-02-23 15:40 | 434 | 17 | 7378 | 434 | 431 | 0.022309 | 7327 | 0.022155 | 5.1404e-05 | NAPA ID:15649 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/341 | Replace transformer structures T7/341 & transformer structure T7/342. Works location: Pongaroa Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-23 | b | 0.011078 | 2.5702e-05 | 2016 | 2016-02-23 | B | 17 | 0.022155 | 5.1404e-05
9630804 | 2016-02-24 10:00 | 2016-02-24 15:22 | 321.75 | 11 | 3463.25 | 314.8409 | 311.8409 | 0.010472 | 3430.25 | 0.010372 | 3.3261e-05 | NAPA ID:15663 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7-330 | Replace Tx pole 7/330 AND POLE 47450, 47448, 47447 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-24 | b | 0.0051861 | 1.6631e-05 | 2016 | 2016-02-24 | B | 11 | 0.010372 | 3.3261e-05
9631259 | 2016-01-29 10:28 | 2016-01-29 12:39 | 131.3333 | 4 | 525.3333 | 131.3333 | 128.3333 | 0.0015885 | 513.3333 | 0.0015522 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC650 | Check for safety, burnt equipment near lines. Contact: Carman 0272715943. Advised Shannon at svs hub Replace 2 x 3A fuse | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.0015522 | 1.2095e-05 | 2016 | 2016-01-29 | C | 4 | 0.0015522 | 1.2095e-05
9633914 | 2016-01-29 12:34 | 2016-01-29 15:34 | 180.4833 | 1 | 180.4833 | 180.4833 | 177.4833 | 0.00054574 | 177.4833 | 0.00053667 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE3-040 UG EQUIPMENT FAILURE | Cable downstream of Fuses SE3-040 is faulty. Customer (East Pac) is happy for power to be off for a week while repairs are being made. Manager of East Pac is Kerry McRee Ph 0272125048. Cable is isolated and earthed DNO 160124. Will be repaired under DNO | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.00053667 | 3.024e-06 | 2016 | 2016-01-29 | C | 1 | 0.00053667 | 3.0238e-06
9634961 | 2016-01-29 15:50 | 2016-01-29 18:32 | 161.5833 | 1 | 161.5833 | 161.5833 | 158.5833 | 0.00048859 | 158.5833 | 0.00047952 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | TC3563 | Wrong Transformer Should of been Transformer TC3563 fuses found blown at transformer and at Fuses at Pole B0314/1. Used 2 x 3 Amp Fuses and 2 x 6 Amp Fuses. Caused by Lightning. | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.00047952 | 3.024e-06 | 2016 | 2016-01-29 | C | 1 | 0.00047952 | 3.0238e-06
9634985 | 2016-01-29 15:57 | 2016-01-29 21:45 | 348 | 2 | 696 | 348 | 345 | 0.0021045 | 690 | 0.0020864 | 6.0475e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FP1415 | This HV Cable Fault is now to be done under capital works number 552387 Murray Lipinski Powerco has organised this, per Marc Askin at power is provided with Generator. Spoke to warren this is a HV cable fault needs replacing DNO 160201. | F4 | BRUCE RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.0020864 | 6.048e-06 | 2016 | 2016-01-29 | C | 2 | 0.0020864 | 6.0475e-06
9635546 | 2016-01-29 19:09 | 2016-01-29 20:47 | 97.9333 | 425 | 32152.3333 | 75.6525 | 72.6525 | 0.097221 | 30877.3333 | 0.093366 | 0.0012851 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1462 | This job was originally started on OMS: 9635410 but something weird happened when trying to force that job up to these fuses and it closed the job off. Brian Sperling attended. Reloaded Relivened 2x 25A DDO's at Fuses FP1462. All Power Restored on comple | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-01-29 | c | 0.093366 | 0.0012851 | 2016 | 2016-01-29 | C | 425 | 0.093366 | 0.0012851
9636515 | 2016-01-30 08:53 | 2016-01-30 10:07 | 74.3333 | 2 | 148.6667 | 74.3333 | 71.3333 | 0.00044953 | 142.6667 | 0.00043139 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6865 | Faultman found blown fuses at Fuses 6865 due to bird strike. 2 X 6 amp hv fuses replaced | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-01-30 | c | 0.00043139 | 6.048e-06 | 2016 | 2016-01-30 | C | 2 | 0.00043139 | 6.0475e-06
9638591 | 2016-01-30 14:37 | 2016-01-31 16:00 | 1523 | 144 | 42852 | 297.5833 | 294.5833 | 0.12957 | 42420 | 0.12827 | 0.00043542 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 843986 | Recloser 575 tripped on B phase O/C & E/F flags, line was patrolled and sectionalised and faultman found tree had gone through the lines and they also found a broken pole (843986), line was isolated at Fuses 2650, faultman will return in the morning with | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-01-30 | c | 0.12827 | 0.00043542 | 2016 | 2016-01-30 | C | 144 | 0.12827 | 0.00043542
9640827 | 2016-01-30 21:00 | 2016-01-30 22:05 | 65.1333 | 1 | 65.1333 | 65.1333 | 62.1333 | 0.00019695 | 62.1333 | 0.00018788 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7598 | Replaced 2x 10Amp HV Links | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-01-30 | c | 0.00018788 | 3.024e-06 | 2016 | 2016-01-30 | C | 1 | 0.00018788 | 3.0238e-06
9640951 | 2016-01-31 01:16 | 2016-01-31 12:08 | 651.9 | 33 | 6779.7 | 205.4455 | 202.4455 | 0.0205 | 6680.7 | 0.020201 | 9.9784e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 833034 | Car vs Pole. Reported by David (04)8010812. Line was isolated at at Fuses 7031 to replace broken pole 833034. 1 X pole & all 11KV & 400V hardware replaced. NDR : 34739 | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-01-31 | c | 0.020201 | 9.9784e-05 | 2016 | 2016-01-31 | C | 33 | 0.020201 | 9.9784e-05
9645042 | 2016-02-01 05:02 | 2016-02-01 07:15 | 133.2833 | 83 | 10822.5167 | 130.3918 | 127.3918 | 0.032725 | 10573.5167 | 0.031972 | 0.00025097 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | E0047 | Car V Pole. Isolated between ABS 903 & 887, Replaced broken pole & relivened. 1 x Pole, 2 x Crosaarms & 6 x Insulators. NDR 048044. | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.031972 | 0.00025097 | 2016 | 2016-02-01 | C | 83 | 0.031972 | 0.00025097
9645205 | 2016-02-01 06:37 | 2016-02-01 08:10 | 92.9 | 4 | 371.6 | 92.9 | 89.9 | 0.0011236 | 359.6 | 0.0010873 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1666 | Reload Reliven. 2 x 10 A Fuses. Suspect Bird Strike. Ferdie reported that these Fuses have blown several times and its caused by bird strike. These lines run close to local water works that support a large bird population. He will put in a defect suggesti | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.0010873 | 1.2095e-05 | 2016 | 2016-02-01 | C | 4 | 0.0010873 | 1.2095e-05
9646235 | 2016-02-18 10:02 | 2016-02-18 13:00 | 178.0167 | 21 | 3738.2167 | 178.0103 | 175.0103 | 0.011303 | 3675.2167 | 0.011113 | 6.3499e-05 | NAPA ID:15203 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754832 | Change 11kV arm to Double discs at pole 746133 & 746134 and create line breaks at both poles and liven line from both way by closing ASB 299 and 340. Close 11kV Line break after new 33kV dual line has been installed over 11kV crossing. Open 11kV TEMP ABS | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-18 | b | 0.0055565 | 3.1749e-05 | 2016 | 2016-02-18 | B | 21 | 0.011113 | 6.3499e-05
9648335 | 2016-03-01 09:30 | 2016-03-01 15:10 | 340 | 9 | 3060 | 340 | 337 | 0.0092527 | 3033 | 0.0091711 | 2.7214e-05 | NAPA ID:16416 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF4-049 | REPLACE 11KV POLES ARMS AND RECON WIRE. Works location: No. 2 Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-01 | b | 0.0045855 | 1.3607e-05 | 2016 | 2016-03-01 | B | 9 | 0.0091711 | 2.7214e-05
9648338 | 2016-03-03 09:35 | 2016-03-03 14:41 | 306 | 9 | 2754 | 306 | 303 | 0.0083274 | 2727 | 0.0082458 | 2.7214e-05 | NAPA ID:16417 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TF4-094 | REPLACE 11KV POLES ARMS AND RECON WIRE. Works location: No. 2 Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.0041229 | 1.3607e-05 | 2016 | 2016-03-03 | B | 9 | 0.0082458 | 2.7214e-05
9648957 | 2016-02-24 08:45 | 2016-02-24 11:20 | 154.6 | 20 | 3092 | 154.6 | 151.6 | 0.0093495 | 3032 | 0.009168 | 6.0475e-05 | NAPA ID:16439 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P18680 | Replace rotten 11kV cross arm. Work Location: Ngaio Road. W/O30014861 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-02-24 | b | 0.004584 | 3.0238e-05 | 2016 | 2016-02-24 | B | 20 | 0.009168 | 6.0475e-05
9649480 | 2016-02-01 11:47 | 2016-02-01 12:28 | 40.9167 | 26 | 1063.8333 | 40.9167 | 37.9167 | 0.0032168 | 985.8333 | 0.0029809 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 361953 | Robin reported Floating lines at Pole - 361953 1R Request for repair. replaced 3x clamp top insulators on pole 361953 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-02-01 | c | 0.0029809 | 7.8618e-05 | 2016 | 2016-02-01 | C | 26 | 0.0029809 | 7.8618e-05
9650320 | 2016-02-16 09:02 | 2016-02-16 15:18 | 376.6667 | 48 | 18080 | 376.6667 | 373.6667 | 0.05467 | 17936 | 0.054234 | 0.00014514 | NAPA ID:16486 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 206 | Asplundh are clearing trees between 11kv poles 749114 - 749115. Works location: Smart Rd. WO 10152474 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-02-16 | b | 0.027117 | 7.257e-05 | 2016 | 2016-02-16 | B | 48 | 0.054234 | 0.00014514
9650357 | 2016-02-01 14:26 | 2016-02-01 17:47 | 201.4167 | 64 | 4835.8 | 75.5594 | 72.5594 | 0.014622 | 4643.8 | 0.014042 | 0.00019352 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 384433 | Car vs Pole. F2009107. Fire service require ETA. Advised Cindy svs hub 1:58pm. Advised Control Pole had not been broken pole but leaning over on acute angle. A jumper had broken on top of it contacting a crossarm and causing arcing. CB 6 at Waihi sub was | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.014042 | 0.00019352 | 2016 | 2016-02-01 | C | 64 | 0.014042 | 0.00019352
9650368 | 2016-02-01 13:58 | 2016-02-01 16:00 | 122.4333 | 1 | 122.4333 | 122.4333 | 119.4333 | 0.00037021 | 119.4333 | 0.00036114 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O47 | Replace 2 x 6A fuse | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-02-01 | c | 0.00036114 | 3.024e-06 | 2016 | 2016-02-01 | C | 1 | 0.00036114 | 3.0238e-06
9651510 | 2016-02-24 08:40 | 2016-02-24 14:42 | 361.9667 | 24 | 8687.2 | 361.9667 | 358.9667 | 0.026268 | 8615.2 | 0.02605 | 7.257e-05 | NAPA ID:16505 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7046 | Replacing 11kV poles and hardware. Work Location: Nursery and Holesworth Road, Masterton. W/O30017189. | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-02-24 | b | 0.013025 | 3.6285e-05 | 2016 | 2016-02-24 | B | 24 | 0.02605 | 7.257e-05
9652467 | 2016-02-01 16:16 | 2016-02-01 17:59 | 103 | 1 | 103 | 103 | 100 | 0.00031145 | 100 | 0.00030238 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC4465 | (1R) No power Pole fuses have been knocked out and not been put back in | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.00030238 | 3.024e-06 | 2016 | 2016-02-01 | C | 1 | 0.00030238 | 3.0238e-06
9653272 | 2016-02-01 21:35 | 2016-02-02 03:30 | 355.4667 | 348 | 16700.9 | 47.9911 | 44.9911 | 0.0505 | 15656.9 | 0.047343 | 0.0010523 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 231025 | Car V Pole. NDR 53064. 1 11m concrete pole, 1 xarn, 2 pin insulators | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.047343 | 0.0010523 | 2016 | 2016-02-01 | C | 348 | 0.047343 | 0.0010523
9653617 | 2016-02-01 23:18 | 2016-02-02 06:36 | 437.6833 | 183 | 35991.85 | 196.6768 | 193.6768 | 0.10883 | 35442.85 | 0.10717 | 0.00055335 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | F1645 | Car V Pole at pole F1645. Pole Replaced. Used 1mm Pole, 1 x Single HV Crossarm, 1 x Double HV Crossarm, Stay Wire. 5 x LV Fuses. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-02-01 | c | 0.10717 | 0.00055335 | 2016 | 2016-02-01 | C | 183 | 0.10717 | 0.00055335
9653838 | 2016-02-02 07:23 | 2016-02-02 09:30 | 127.25 | 15 | 1908.75 | 127.25 | 124.25 | 0.0057716 | 1863.75 | 0.0056355 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7379 | Reload Reliven. 2 x 10 A Fuses. Suspected Bird Strike | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-02-02 | c | 0.0056355 | 4.5356e-05 | 2016 | 2016-02-02 | C | 15 | 0.0056355 | 4.5356e-05
9653893 | 2016-02-02 07:53 | 2016-02-02 10:40 | 167.1167 | 12 | 2005.4 | 167.1167 | 164.1167 | 0.0060638 | 1969.4 | 0.005955 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | S5283 | *** please check if oms 9654205 - 443 SH33 off tx TF6-107 is part of this issue *** Reload reliven at Fuses S5283. 2 x 10 A Fuses. Cause - Fried rat found at G/M Transformer T4693 which feeds on to transformer TF6-107. Due to E-map errors and ICP data err | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-02-02 | c | 0.005955 | 3.6285e-05 | 2016 | 2016-02-02 | C | 12 | 0.005955 | 3.6285e-05
9654311 | 2016-02-17 09:15 | 2016-02-17 15:07 | 352 | 250 | 88000 | 352 | 349 | 0.26609 | 87250 | 0.26382 | 0.00075594 | NAPA ID:16038 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Burnside Feeder C928 | replace 11kv poles and hardware and re conductor 11kv wires and repairs to defects x 4 on request from power co. Cape Palliser Road, Ngawai. W/O30013464 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-02-17 | b | 0.13191 | 0.00037797 | 2016 | 2016-02-17 | B | 250 | 0.26382 | 0.00075594
9654315 | 2016-02-02 09:14 | 2016-02-02 10:45 | 91.1 | 1 | 91.1 | 91.1 | 88.1 | 0.00027546 | 88.1 | 0.00026639 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X668 | Reload Reliven. 2 x 3A Fuses. Caused by Twisted LV Lines | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-02-02 | c | 0.00026639 | 3.024e-06 | 2016 | 2016-02-02 | C | 1 | 0.00026639 | 3.0238e-06
9654327 | 2016-02-02 10:50 | 2016-02-02 12:00 | 70 | 1 | 70 | 70 | 67 | 0.00021166 | 67 | 0.00020259 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | T8/165 | 1R - FM Required to Isolate and Earth for Removal of Vegetation. Isolated transformer for tree crew to cut away vegetation. off 10:50 - on 12:00 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-02-02 | c | 0.00020259 | 3.024e-06 | 2016 | 2016-02-02 | C | 1 | 0.00020259 | 3.0238e-06
9656028 | 2016-02-22 08:30 | 2016-02-22 13:49 | 319 | 3 | 939 | 313 | 310 | 0.0028393 | 930 | 0.0028121 | 9.0713e-06 | NAPA ID:16562 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2451 | Replace 11kv transformer pole and hardware. Works Location: Cape Palliser Road. W/O30007110 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-02-22 | b | 0.001406 | 4.536e-06 | 2016 | 2016-02-22 | B | 3 | 0.0028121 | 9.0713e-06
9656216 | 2016-02-17 15:46 | 2016-02-17 16:22 | 36 | 16 | 576 | 36 | 33 | 0.0017417 | 528 | 0.0015965 | 4.838e-05 | NAPA ID:16339 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 4 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV ABS 427 | LTOS on switchgear 472, all individual switches. Works locatioN: Port Taranaki. WO 10138687 | F4 | MOTUROA 4 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-17 | b | 0.00079827 | 2.419e-05 | 2016 | 2016-02-17 | B | 16 | 0.0015965 | 4.838e-05
9656969 | 2016-02-04 09:38 | 2016-02-04 13:36 | 237.6667 | 4 | 950.6667 | 237.6667 | 234.6667 | 0.0028746 | 938.6667 | 0.0028383 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | VEGETATION | VEGETATION - INSIDE ZONE | C14346 | No LV Fusing for safety Disconnect. All customers affected were contacted about outage and HV Fuses Opened, Tagged by Perry Hicks. Relivened OK. | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-02-04 | c | 0.0028383 | 1.2095e-05 | 2016 | 2016-02-04 | C | 4 | 0.0028383 | 1.2095e-05
9657482 | 2016-02-02 20:28 | 2016-02-02 21:55 | 86.7333 | 2 | 173.4667 | 86.7333 | 83.7333 | 0.00052452 | 167.4667 | 0.00050638 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP509 | 2 x HT fuses replaced at fuses FP509. Suspected bird strike | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-02 | c | 0.00050638 | 6.048e-06 | 2016 | 2016-02-02 | C | 2 | 0.00050638 | 6.0475e-06
9657787 | 2016-02-03 00:15 | 2016-02-03 01:09 | 53.8833 | 115 | 5895.65 | 51.2665 | 48.2665 | 0.017827 | 5550.65 | 0.016784 | 0.00034773 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | rec 1022 | recloser 1022 trip e/f o/c line patrolled nothing found | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-03 | c | 0.016784 | 0.00034773 | 2016 | 2016-02-03 | C | 115 | 0.016784 | 0.00034773
9688302 | 2016-02-03 11:26 | 2016-02-03 11:33 | 7 | 1 | 7 | 7 | 4 | 2.1166e-05 | 4 | 1.2095e-05 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1483 | The issue was not no power but low voltage. Jason found the voltage to be too low and has tapped the Transformer T1483 up 2 taps. Voltage is now good. Outage was from 1126 - 1133, no outage until Jason isolated the Transformer. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-02-03 | c | 1.2095e-05 | 3.024e-06 | 2016 | 2016-02-03 | C | 1 | 1.2095e-05 | 3.0238e-06
9688404 | 2016-02-04 09:15 | 2016-02-04 15:10 | 355 | 9 | 3195 | 355 | 352 | 0.0096609 | 3168 | 0.0095793 | 2.7214e-05 | NAPA ID:16640 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF5001 | REPLACE 11KV POLES ARMS AND RECON WIRE. NOTE: THIS OUTAGE IS ADVERTISED UNDER THE ORIGINAL NAPA 15597. Works location: NO. 2 Rd, Mangatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-04 | b | 0.0047896 | 1.3607e-05 | 2016 | 2016-02-04 | B | 9 | 0.0095793 | 2.7214e-05
9688575 | 2016-02-10 09:00 | 2016-02-10 13:56 | 296 | 7 | 2072 | 296 | 293 | 0.0062652 | 2051 | 0.0062017 | 2.1166e-05 | NAPA ID:16645 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF5-001 | Replace 11kV poles arms and reconductor wire. This outage is advertised as 15600. Works location: No. 2 Rd, Mangatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-10 | b | 0.0031009 | 1.0583e-05 | 2016 | 2016-02-10 | B | 7 | 0.0062017 | 2.1166e-05
9819179 | 2016-02-03 13:23 | 2016-02-03 18:48 | 324.85 | 587 | 43387.0833 | 73.9133 | 70.9133 | 0.13119 | 41626.0833 | 0.12587 | 0.0017749 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 248470 | RP15 Trip on E/F. Car V Pole 52 Wood Rd South Beyond ABS IC341 Coromandel CB 1. Isolation at ABS IC341 feeder relivened. no back feeds available. Pole 248470 & hardware replaced. 1 x 11m busck pole, 2 x HV crossarms, 2 x LV crossarms, 3 x HV pin & insulat | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-03 | c | 0.12587 | 0.0017749 | 2016 | 2016-02-03 | C | 587 | 0.12587 | 0.0017749
9819797 | 2016-02-12 09:15 | 2016-02-12 14:23 | 308 | 9 | 2772 | 308 | 305 | 0.0083819 | 2745 | 0.0083002 | 2.7214e-05 | NAPA ID:16657 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF5-001 | REPLACE 11KV POLES ARMS AND RECON WIRE. THIS OUTAGE IS ADVERTISED AS 15604. Works location: No. 2 Rd, Mangatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-12 | b | 0.0041501 | 1.3607e-05 | 2016 | 2016-02-12 | B | 9 | 0.0083002 | 2.7214e-05
9837444 | 2016-02-23 09:30 | 2016-02-23 14:56 | 326 | 64 | 20864 | 326 | 323 | 0.063088 | 20672 | 0.062507 | 0.00019352 | NAPA ID:16395 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 701966 | We are replacing all cross arms at pole 701966. Works location: Mangorei Rd. WO 30003451 | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-02-23 | b | 0.031254 | 9.676e-05 | 2016 | 2016-02-23 | B | 64 | 0.062507 | 0.00019352
9837499 | 2016-02-16 09:01 | 2016-02-16 13:14 | 253 | 9 | 2277 | 253 | 250 | 0.0068851 | 2250 | 0.0068035 | 2.7214e-05 | NAPA ID:16661 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF5-001 | REPLACE 11KV POLES ARMS AND RECON WIRE. THIS OUTAGE IS ADVERTISED AS 15607. Works location: No. 2 Rd, Mangatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-16 | b | 0.0034017 | 1.3607e-05 | 2016 | 2016-02-16 | B | 9 | 0.0068035 | 2.7214e-05
9837534 | 2016-02-17 09:20 | 2016-02-17 12:56 | 216 | 9 | 1944 | 216 | 213 | 0.0058782 | 1917 | 0.0057965 | 2.7214e-05 | NAPA ID:16662 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF5-001 | REPLACE 11KV POLES ARMS AND RECON WIRE. THIS OUTAGE IS ADVERTISED AS 15610. Works location: No. 2 Rd, Managatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-17 | b | 0.0028983 | 1.3607e-05 | 2016 | 2016-02-17 | B | 9 | 0.0057965 | 2.7214e-05
9838288 | 2016-02-03 20:09 | 2016-02-03 21:20 | 71 | 14 | 994 | 71 | 68 | 0.0030056 | 952 | 0.0028786 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1424 | 2 x HV fuses replaced at fuses FC1424 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-02-03 | c | 0.0028786 | 4.2333e-05 | 2016 | 2016-02-03 | C | 14 | 0.0028786 | 4.2333e-05
9838342 | 2016-02-03 21:20 | 2016-02-03 21:47 | 26.8833 | 1793 | 41653.4667 | 23.2312 | 20.2312 | 0.12595 | 36274.4667 | 0.10969 | 0.0054216 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB3162 | CB 3162 Piako tripped losing supply to Walton sub and T1 side of bus at Waharoa sub. Supply restored to Waharoa by opening Sectionaliser 3114 & closing Sectionaliser 3246. Supply then restored to Walton by opening MABS PC221 and 11kV CB,s, closing sectio | F1,F2,F3 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 2016-02-03 | c | 0.10969 | 0.0054216 | 2016 | 2016-02-03 | C | 1793 | 0.10969 | 0.0054216
9840820 | 2016-02-04 14:50 | 2016-02-04 15:14 | 24 | 10 | 240 | 24 | 21 | 0.0007257 | 210 | 0.00063499 | 3.0238e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | T4927 | Address amended to 105 CASUARINA DRIVE. 2 Phases at transformer, are only giving 130 volts, HV fault request 2R, possible cable fault. Found Fuses blown and two rodent infestations. Cleared rodents and replaced 2 x 16A fuses | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-02-04 | c | 0.00063499 | 3.0238e-05 | 2016 | 2016-02-04 | C | 10 | 0.00063499 | 3.0238e-05
9841034 | 2016-02-25 09:49 | 2016-02-25 12:49 | 179.6333 | 19 | 3413.0333 | 179.6333 | 176.6333 | 0.01032 | 3356.0333 | 0.010148 | 5.7451e-05 | NAPA ID:16581 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2441 | Replace transformer X2441 for new 200/11/3 padmount due to oil leak.There is no LV backfeed available. Works location: Walker Cres, Bulls. WO 30007021 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-02-25 | b | 0.0050739 | 2.8726e-05 | 2016 | 2016-02-25 | B | 19 | 0.010148 | 5.7451e-05
9841251 | 2016-02-26 08:30 | 2016-02-26 15:09 | 399 | 11 | 4389 | 399 | 396 | 0.013271 | 4356 | 0.013172 | 3.3261e-05 | NAPA ID:16506 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7651 | replacing 11kv poles and hardware. Works location: Pokohowi Rd, Masterton. WO 30017189 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-02-26 | b | 0.0065858 | 1.6631e-05 | 2016 | 2016-02-26 | B | 11 | 0.013172 | 3.3261e-05
9841347 | 2016-02-25 08:30 | 2016-02-25 13:51 | 321 | 16 | 5136 | 321 | 318 | 0.01553 | 5088 | 0.015385 | 4.838e-05 | NAPA ID:15698 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P46956 | Replace poles and crossarms on P46956,46330,46328. Works location: Hinemoa Valley. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-25 | b | 0.0076924 | 2.419e-05 | 2016 | 2016-02-25 | B | 16 | 0.015385 | 4.838e-05
9842046 | 2016-02-04 12:51 | 2016-02-04 16:49 | 238.2667 | 723 | 55528.6167 | 76.8031 | 73.8031 | 0.16791 | 53359.6167 | 0.16135 | 0.0021862 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | M67 | CB 5 trip o/c. Found cable between ABS m67 and M69 faulty, line break cut and DNO'd for repair. Backfeed applied from abs M73 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-02-04 | c | 0.16135 | 0.0021862 | 2016 | 2016-02-04 | C | 723 | 0.16135 | 0.0021862
9846355 | 2016-02-04 16:31 | 2016-02-04 18:03 | 91.7 | 1 | 91.7 | 91.7 | 88.7 | 0.00027728 | 88.7 | 0.00026821 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7598 | 2 HT fuses tripped at 7598. Relivened OK - 10A. Bird strike | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-04 | c | 0.00026821 | 3.024e-06 | 2016 | 2016-02-04 | C | 1 | 0.00026821 | 3.0238e-06
9846814 | 2016-02-04 13:24 | 2016-02-04 19:30 | 366.3833 | 6 | 2198.3 | 366.3833 | 363.3833 | 0.0066471 | 2180.3 | 0.0065927 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Need Paperwork - email sent to Andrew | Replaced transformer T1/233. Have taken times from history log as no paperwork. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-02-04 | c | 0.0065927 | 1.8143e-05 | 2016 | 2016-02-04 | C | 6 | 0.0065927 | 1.8143e-05
9846852 | 2016-02-04 19:59 | 2016-02-04 22:55 | 176.5833 | 663 | 116186.45 | 175.2435 | 172.2435 | 0.35132 | 114197.45 | 0.34531 | 0.0020048 |  | 11 | Unplanned | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 3 | CB 3 Trip B & C O/C Feeder patrolled, CB 3 will not close Via SCADA Subs tech called into attend to fault. no LFI's on feeder couldn't put back feed in with out risk to donor feeder. No auto reclose occurred on the feeder. Subs tech removed CB cleaned up | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-02-04 | c | 0.34531 | 0.0020048 | 2016 | 2016-02-04 | C | 663 | 0.34531 | 0.0020048
9849143 | 2016-02-05 08:40 | 2016-02-05 09:31 | 50.75 | 1793 | 45249.0167 | 25.2365 | 22.2365 | 0.13682 | 39870.0167 | 0.12056 | 0.0054216 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Walton Sub | Unplanned outage occured during planned switching 13138 due to incomer cable fault. Brent Williams and Marty went to investigate. Incomer Cable Fault. Will be Replaced | F1,F2,F3 | WALTON-KEREONE 33KV | PIAKO | Valley | TP_PIAKO | Eastern Electricity | POWERCO | 2016-02-05 | c | 0.12056 | 0.0054216 | 2016 | 2016-02-05 | C | 1793 | 0.12056 | 0.0054216
9853445 | 2016-02-11 09:23 | 2016-02-11 14:07 | 284 | 9 | 2556 | 284 | 281 | 0.0077287 | 2529 | 0.0076471 | 2.7214e-05 | NAPA ID:16756 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP264/1 | Replace 11kV pole arrms and reconductor wire. Works Location: No2 Mangatoi Road, Te Puke. Works Order 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-11 | b | 0.0038235 | 1.3607e-05 | 2016 | 2016-02-11 | B | 9 | 0.0076471 | 2.7214e-05
9854287 | 2016-02-05 19:33 | 2016-02-06 11:10 | 937.4667 | 121 | 21673.6333 | 179.1209 | 176.1209 | 0.065536 | 21310.6333 | 0.064438 | 0.00036588 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E12803 | 11kV Sectionaliser SP15 tripped L/O. Resource being sent from Tauranga. Line patrol and sensationalizing done. Cut a line break at pole E12804 and left off for the night.Fault resource was required in TGA for Balance Ag fault on OMS 9854410.Saturday 06th | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-05 | c | 0.064438 | 0.00036587 | 2016 | 2016-02-05 | C | 121 | 0.064438 | 0.00036588
9854410 | 2016-02-05 19:33 | 2016-02-06 12:46 | 1032.7667 | 1 | 1032.7667 | 1032.7667 | 1029.7667 | 0.0031228 | 1029.7667 | 0.0031138 | 3.0238e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Triton CB6 | CB 6 Trip 19:33, no Flags. NOC rung Balance to advise of Trip. Balance Ag advised they were attempting to ascertain the cause of the issue & go through their shut down procedures. 20:35 Escalated to NCTL, due to severity and resourcing issues. Fault noti | F1 | FERT WORKS | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 2016-02-05 | c | 0.0031138 | 3.024e-06 | 2016 | 2016-02-05 | C | 1 | 0.0031138 | 3.0238e-06
9854914 | 2016-02-06 08:10 | 2016-02-06 08:51 | 41 | 5 | 205 | 41 | 38 | 0.00061987 | 190 | 0.00057451 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | V13109 | Check for safety tress are touching lines and lines are arcing, Contact Abby 021352486. 21.28 advised Glo at svs hub Will assess in the morning not safe to do tonight. Will arrange with SMC. 0851 tree branches removed from lines at pole V13109. NDR 047806 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-06 | c | 0.00057452 | 1.5119e-05 | 2016 | 2016-02-06 | C | 5 | 0.00057451 | 1.5119e-05
9856384 | 2016-02-06 02:26 | 2016-02-06 02:28 | 1.9833 | 926 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0028 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | R/S 4949 Tripped A Ph O/C E/F A/R not patrolled | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-06 | c | 0 | 0.0028 | 2016 | 2016-02-06 | C | 926 | 0 | 0.0028
9858721 | 2016-02-06 11:15 | 2016-02-06 15:00 | 225.3333 | 3 | 676 | 225.3333 | 222.3333 | 0.0020441 | 667 | 0.0020168 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE5-277 | Transformer TE5-277 replaced | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-06 | c | 0.0020168 | 9.071e-06 | 2016 | 2016-02-06 | C | 3 | 0.0020168 | 9.0713e-06
9859061 | 2016-02-06 15:45 | 2016-02-06 19:30 | 225.25 | 4 | 901 | 225.25 | 222.25 | 0.0027244 | 889 | 0.0026881 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X373 | Fuses 373 found tripped. Replaced 1 x 30kVA transformer. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-02-06 | c | 0.0026881 | 1.2095e-05 | 2016 | 2016-02-06 | C | 4 | 0.0026881 | 1.2095e-05
9860079 | 2016-02-06 21:10 | 2016-02-06 21:12 | 1.3667 | 926 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0028 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | R/S 4949 Tripped B Ph O/C E/F A/R | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-06 | c | 0 | 0.0028 | 2016 | 2016-02-06 | C | 926 | 0 | 0.0028
9861017 | 2016-02-06 21:15 | 2016-02-06 22:21 | 65.5 | 1 | 65.5 | 65.5 | 62.5 | 0.00019806 | 62.5 | 0.00018899 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD4-078 | DDO arching on bottom, all 3 DDO's need to be replaced G & B on Tuesday 9/2/16 | F3 | BROOKFIELD TCE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2016-02-06 | c | 0.00018898 | 3.024e-06 | 2016 | 2016-02-06 | C | 1 | 0.00018899 | 3.0238e-06
9861024 | 2016-02-06 21:19 | 2016-02-07 05:09 | 469.35 | 433 | 83435.3667 | 192.6914 | 189.6914 | 0.25229 | 82136.3667 | 0.24836 | 0.0013093 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | B0167 | CB 3 Trip E/F No Flags from Recloser 9867. Recloser 9867 NOC Open Back feed applied from CB 6 via ABS 2559. Feed CB 6 A/R & recloser 13024 Tripped. ABS 2559 Open Recloser 13024 Closed. Recloser 9867 Needs protection review. Line Past recloser 9867 patroll | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-02-06 | c | 0.24836 | 0.0013093 | 2016 | 2016-02-06 | C | 433 | 0.24836 | 0.0013093
9861861 | 2016-02-06 22:48 | 2016-02-07 00:35 | 107 | 16 | 1712 | 107 | 104 | 0.0051767 | 1664 | 0.0050315 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 743053 | Cross arm found burnt on Pole 743053 - Isolated at fuses 5265. Used 1x crossarm complete | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-06 | c | 0.0050315 | 4.838e-05 | 2016 | 2016-02-06 | C | 16 | 0.0050315 | 4.838e-05
9861955 | 2016-02-07 01:36 | 2016-02-07 01:39 | 2.9667 | 10 | 29.6667 | 2.9667 | -0.033333 | 8.9705e-05 | 0 | 0 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S5288 | 1x Blown fuse at S5288. ABS IP 26 Opened Fuse replaced ABS IP26 Closed (8amp fuse)Unknown Cause | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-02-07 | c | 0 | 3.0238e-05 | 2016 | 2016-02-07 | C | 10 | 0 | 3.0238e-05
9864424 | 2016-02-07 10:26 | 2016-02-07 10:35 | 8.9167 | 68 | 606.3333 | 8.9167 | 5.9167 | 0.0018334 | 402.3333 | 0.0012166 | 0.00020562 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Q27 | Faultman found blown fuses at Q27 caused by a bird stuck between the fuses. 2 X 6 amp HV fuses replaced. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-07 | c | 0.0012166 | 0.00020562 | 2016 | 2016-02-07 | C | 68 | 0.0012166 | 0.00020562
9865003 | 2016-02-07 15:35 | 2016-02-07 16:52 | 77.05 | 992 | 56934.3167 | 57.3935 | 54.3935 | 0.17216 | 53958.3167 | 0.16316 | 0.0029996 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 5917 | CB S41 tripped on O/C flags line was sectionalisd and patrolled and faultman found the cable crutch at ABS 5917 from the CB had blown itself open, line was isolated at CB S41 and ABS 5917.Cable has been DNOd and will be repaired via a NAPA application on | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-02-07 | c | 0.16316 | 0.0029996 | 2016 | 2016-02-07 | C | 992 | 0.16316 | 0.0029996
9866779 | 2016-02-07 18:41 | 2016-02-07 21:56 | 195 | 18 | 3510 | 195 | 192 | 0.010613 | 3456 | 0.01045 | 5.4428e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/927 | Replaced blown 20kvA transformer T2/927 with new 30kVA/3 Ph/11kV. Replaced 2x 3Amp HV Links | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-02-07 | c | 0.01045 | 5.4428e-05 | 2016 | 2016-02-07 | C | 18 | 0.01045 | 5.4428e-05
9867186 | 2016-02-07 22:52 | 2016-02-08 00:48 | 116.7167 | 465 | 8574.1333 | 18.439 | 15.439 | 0.025926 | 7179.1333 | 0.021708 | 0.001406 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 9932/2 | 1 x A/R on recloser 9969/2. Sectionaliser 9923/2 tripped to L/O. Line sectionalised & patrolled. No fault found. All supply restored | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-07 | c | 0.021708 | 0.001406 | 2016 | 2016-02-07 | C | 465 | 0.021708 | 0.001406
9867681 | 2016-02-07 21:49 | 2016-02-07 22:35 | 46.2667 | 12 | 555.2 | 46.2667 | 43.2667 | 0.0016788 | 519.2 | 0.0015699 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | WH831 | Replaced 2x 10A HV Links. Dead Swan found by a customer | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-02-07 | c | 0.0015699 | 3.6285e-05 | 2016 | 2016-02-07 | C | 12 | 0.0015699 | 3.6285e-05
9867848 | 2016-02-08 02:33 | 2016-02-08 20:24 | 1070.95 | 4799 | 1317758.2333 | 274.5902 | 271.5902 | 3.9846 | 1303361.2333 | 3.9411 | 0.014511 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224876 | 02:33 Te Matai GXP 33kV CB 1122 Tripped to L/O, A, B C O/C. Also tripped Te Puke 11kV CB 1 on same flags to lock out, details on OMS 8972325. Originally it was suspected we had a 33 to 11kV contact, however was discounted once TPV CB 1 sectionalised and r | F1,F2,F3 | TE MATAI1122-PONGAKAWA2007 33KV | TE MATAI | Tauranga | TP_TE MATAI | Eastern Electricity | POWERCO | 2016-02-08 | c | 3.9411 | 0.014511 | 2016 | 2016-02-08 | C | 4799 | 3.9411 | 0.014511
9874282 | 2016-02-08 09:54 | 2016-02-08 11:15 | 80.7333 | 1 | 80.7333 | 80.7333 | 77.7333 | 0.00024412 | 77.7333 | 0.00023505 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F88 | Faultman found blown fuses at Fuses F88 caused by bird strike. 2 X 6 amp HV fuses replaced | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-02-08 | c | 0.00023505 | 3.024e-06 | 2016 | 2016-02-08 | C | 1 | 0.00023505 | 3.0238e-06
9875773 | 2016-02-08 15:36 | 2016-02-08 18:16 | 159.7667 | 5 | 798.8333 | 159.7667 | 156.7667 | 0.0024155 | 783.8333 | 0.0023701 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1312470 - need paperwork - emailed to Paul | Advised SMC of 999. Car/truck hit pole clashing 400v blowing 2 x 3A h/V, O/H fuses transformer TC2894 Replaced H/V fuses all service restored | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-02-08 | c | 0.0023701 | 1.5119e-05 | 2016 | 2016-02-08 | C | 5 | 0.0023701 | 1.5119e-05
9876721 | 2016-02-09 05:36 | 2016-02-09 14:13 | 516.7167 | 149 | 19652.3833 | 131.8952 | 128.8952 | 0.059424 | 19205.3833 | 0.058072 | 0.00045054 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 778432 | 09-02-16 - Chris Winters advised that tree Removal required.- 2R Request. Outage required between ABS 014 & ABS 596. Momentary outage required to restore due to a non-parallel point at the backfeed Recloser 4621/1 where break before make switching is requ | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-09 | c | 0.058072 | 0.00045054 | 2016 | 2016-02-09 | C | 149 | 0.058072 | 0.00045054
9877494 | 2016-02-09 06:45 | 2016-02-09 07:40 | 55.1667 | 1 | 55.1667 | 55.1667 | 52.1667 | 0.00016681 | 52.1667 | 0.00015774 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7598 | Reload Reliven. 2 x 10A Fuses. Caused by Duck Strike. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-09 | c | 0.00015774 | 3.024e-06 | 2016 | 2016-02-09 | C | 1 | 0.00015774 | 3.0238e-06
9877533 | 2016-02-09 06:54 | 2016-02-09 09:00 | 126.5 | 17 | 2150.5 | 126.5 | 123.5 | 0.0065026 | 2099.5 | 0.0063484 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 663 | Reload Reliven at Fuses 663. All 3 Fuses upgraded to 10A. Gary reports that there has been a 300MVA transformer installed for irrigation at the end of the spur line. The fuse rating at 663 is too low to run all transformers on load during milking. Gary to | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-02-09 | c | 0.0063484 | 5.1404e-05 | 2016 | 2016-02-09 | C | 17 | 0.0063484 | 5.1404e-05
9878047 | 2016-02-09 08:44 | 2016-02-09 11:20 | 156 | 2 | 311.6 | 155.8 | 152.8 | 0.0009422 | 305.6 | 0.00092406 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | D88 | Reload Reliven at Fuses D88. 2 X 10 Amp Fuses. Caused by Bird Strike. | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 2016-02-09 | c | 0.00092406 | 6.048e-06 | 2016 | 2016-02-09 | C | 2 | 0.00092406 | 6.0475e-06
9878235 | 2016-02-23 10:08 | 2016-02-23 15:21 | 313 | 12 | 3756 | 313 | 310 | 0.011357 | 3720 | 0.011248 | 3.6285e-05 | NAPA ID:16499 TP_HAWERA GXP > MANAIA SUB > OTAKEHO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6710 | Install new Nova Recloser 12137/1/2/4/6 & new pole at existing ABS MA272 site. Works location: South Rd, Manaia. WO 30009756 | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-02-23 | b | 0.0056242 | 1.8143e-05 | 2016 | 2016-02-23 | B | 12 | 0.011248 | 3.6285e-05
9879354 | 2016-02-25 10:10 | 2016-02-25 16:05 | 355 | 77 | 27335 | 355 | 352 | 0.082654 | 27104 | 0.081956 | 0.00023283 | NAPA ID:16517 TP_HAWERA GXP > MANAIA SUB > AUROA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS KA120 | Install new Nova recloser 12139/1/2/4/6 & new pole at old Abs MA109 site. Works location: Skeet Rd. WO 30009756 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-02-25 | b | 0.040978 | 0.00011642 | 2016 | 2016-02-25 | B | 77 | 0.081956 | 0.00023283
9881767 | 2016-02-25 09:04 | 2016-02-25 10:45 | 101.2 | 21 | 2125.2 | 101.2 | 98.2 | 0.0064261 | 2062.2 | 0.0062356 | 6.3499e-05 | NAPA ID:16237 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E1375 | Replace 11kv Termination arms at pole E1375. Works location: Highway 29, Piaere. WO 30018907 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-25 | b | 0.0031178 | 3.1749e-05 | 2016 | 2016-02-25 | B | 21 | 0.0062356 | 6.3499e-05
9881793 | 2016-02-09 12:00 | 2016-02-09 17:33 | 332.8667 | 179 | 30036.7333 | 167.803 | 164.803 | 0.090824 | 29499.7333 | 0.0892 | 0.00054125 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 201922 | Recloser S6040 Trip flag EF and Ph B OC. Report of geese flying into O/H line beyond. ABS IP443. Isolation at ABS IP443 ( no back feed spur line ) with rest of feeder returned to service via recloser S6040. Delay due to extra staff & equipment required t | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-09 | c | 0.0892 | 0.00054125 | 2016 | 2016-02-09 | C | 179 | 0.0892 | 0.00054125
9884085 | 2016-02-09 19:11 | 2016-02-09 20:56 | 104.6 | 113 | 11043.5333 | 97.7304 | 94.7304 | 0.033393 | 10704.5333 | 0.032368 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | C217/2 | Recloser C217/2 tripped on A & c phase O/C flags, received call of line in the trees on Waterfall Rd. Customer was cutting branch and a branch fell and hit the lines.Customer informed Colin Winch of what he had done. NDR No: 37867. 3 X Binders used. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-02-09 | c | 0.032368 | 0.00034168 | 2016 | 2016-02-09 | C | 113 | 0.032368 | 0.00034168
9885502 | 2016-02-10 01:24 | 2016-02-10 06:19 | 295.1 | 598 | 32347.9333 | 54.0935 | 51.0935 | 0.097812 | 30553.9333 | 0.092388 | 0.0018082 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1265 | CB TA 1 tripped on E/F flags, line was patrolled and sectionalised and a faulty transformer T1265 was found, transformer to be replaced. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.092388 | 0.0018082 | 2016 | 2016-02-10 | C | 598 | 0.092388 | 0.0018082
9886863 | 2016-02-10 02:08 | 2016-02-10 04:43 | 155.1333 | 178 | 22922.4833 | 128.778 | 125.778 | 0.069312 | 22388.4833 | 0.067697 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4659/2 | Recloser 4659/2 tripped on B phase O/C & E/F flags line was patrolled and sectionalised and no fault was found. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.067697 | 0.00053823 | 2016 | 2016-02-10 | C | 178 | 0.067697 | 0.00053823
9888053 | 2016-02-10 03:04 | 2016-02-10 10:46 | 462.4333 | 238 | 37328.3 | 156.8416 | 153.8416 | 0.11287 | 36614.3 | 0.11071 | 0.00071966 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790778 | CB 10 tripped on B phase O/C & E/F flags, Line was sectionalised and patrolled and lines down was found at pole 790778. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.11071 | 0.00071966 | 2016 | 2016-02-10 | C | 238 | 0.11071 | 0.00071966
9889328 | 2016-02-10 10:55 | 2016-02-10 11:11 | 16 | 4 | 64 | 16 | 13 | 0.00019352 | 52 | 0.00015724 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2315t | Isolate TX 2315T to carry out repairs on neutral cable UPDATED NOTES: Allan Rarere told Control that he still needed to checks at the house, shed and cowshed after he isolated the tx and will sign the job off with Dispatch. However, they?ve closed the | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.00015724 | 1.2095e-05 | 2016 | 2016-02-10 | C | 4 | 0.00015724 | 1.2095e-05
9889591 | 2016-02-25 09:04 | 2016-02-25 14:39 | 335.5 | 76 | 25498 | 335.5 | 332.5 | 0.0771 | 25270 | 0.07641 | 0.00022981 | NAPA ID:15592 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Recloser 7417 | repair multiple defects. Works location: Te Wharau Rd, Carterton. WO 30016940 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-02-25 | b | 0.038205 | 0.0001149 | 2016 | 2016-02-25 | B | 76 | 0.07641 | 0.00022981
9890179 | 2016-02-10 09:33 | 2016-02-10 16:50 | 437 | 25 | 10925 | 437 | 434 | 0.033035 | 10850 | 0.032808 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1488 | Fuse FC1488 reload & livened No power at TC758. Line isolated at Fuse FC1488 Line patrolled fault found to be Fuse at FC1474 blown but didn't drop out. Jumper also replaced at this site. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-10 | c | 0.032808 | 7.5594e-05 | 2016 | 2016-02-10 | C | 25 | 0.032808 | 7.5594e-05
9890277 | 2016-02-10 10:10 | 2016-02-10 13:26 | 196.15 | 37 | 7257.55 | 196.15 | 193.15 | 0.021945 | 7146.55 | 0.021609 | 0.00011188 | NAPA ID:16813 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P14158 | Replace 11kV pole P14158 after car v. pole. NAPA job created to advise retailers of emergency switching. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-02-10 | b | 0.010805 | 5.594e-05 | 2016 | 2016-02-10 | B | 37 | 0.021609 | 0.00011188
9891211 | 2016-02-10 13:36 | 2016-02-10 16:23 | 166.9167 | 68 | 9136.2 | 134.3559 | 131.3559 | 0.027626 | 8932.2 | 0.027009 | 0.00020562 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Recloser O83 | Recloser O83 Tripped - Lock Out. James Prime Patrolled lines. Nothing Found. successfully Relivened | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.027009 | 0.00020562 | 2016 | 2016-02-10 | C | 68 | 0.027009 | 0.00020562
9891548 | 2016-02-29 09:30 | 2016-02-29 14:33 | 303 | 3 | 909 | 303 | 300 | 0.0027486 | 900 | 0.0027214 | 9.0713e-06 | NAPA ID:16213 TP_OPUNAKE GXP > TASMAN SUB > IHAIA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA181 | We are replacing 9 Hardwood poles and 2 badly spalding poles. Works Location:Arawhata Rd, Opunake. WO 30019159 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-02-29 | b | 0.0013607 | 4.536e-06 | 2016 | 2016-02-29 | B | 3 | 0.0027214 | 9.0713e-06
9891650 | 2016-02-19 09:03 | 2016-02-19 16:15 | 432.5333 | 116 | 50173.8667 | 432.5333 | 429.5333 | 0.15171 | 49825.8667 | 0.15066 | 0.00035076 | NAPA ID:15642 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace 300mtr of new conductor with old. Install 2 new poles (1 to replace old), and remedy defects. replace 11kV Fuse FP1201 for new 11kV ABS IP648. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2016-02-19 | b | 0.075331 | 0.00017538 | 2016 | 2016-02-19 | B | 116 | 0.15066 | 0.00035076
9891696 | 2016-02-10 17:25 | 2016-02-10 20:00 | 155 | 1 | 155 | 155 | 152 | 0.00046868 | 152 | 0.00045961 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE5-232 | Transformer TE5-232 Blown and needs replaceing. Transformer Replaced & Voltages checked | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2016-02-10 | c | 0.00045961 | 3.024e-06 | 2016 | 2016-02-10 | C | 1 | 0.00045961 | 3.0238e-06
9891867 | 2016-02-10 16:48 | 2016-02-10 16:54 | 6.3833 | 8 | 51.0667 | 6.3833 | 3.3833 | 0.00015441 | 27.0667 | 8.1843e-05 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4204 | Line Patrolled & fuse at FC4204 blown. Replaced with 8amp link tested & checked | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-10 | c | 8.1843e-05 | 2.419e-05 | 2016 | 2016-02-10 | C | 8 | 8.1843e-05 | 2.419e-05
9892143 | 2016-02-10 19:00 | 2016-02-10 20:30 | 90 | 1 | 90 | 90 | 87 | 0.00027214 | 87 | 0.00026307 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Advised Sammy at hub. 9892143 possibly linked. ndr 30781 irrigation hit pole and tx. Changed transformer worked through control. WAS LINKED TO OMS 9892062 | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-02-10 | c | 0.00026307 | 3.024e-06 | 2016 | 2016-02-10 | C | 1 | 0.00026307 | 3.0238e-06
9895662 | 2016-02-10 22:51 | 2016-02-10 23:55 | 63.85 | 4 | 255.4 | 63.85 | 60.85 | 0.00077227 | 243.4 | 0.00073598 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc4045 | Actual fault at fuses FC 4045 replaced 2 x 3amp fuses unknown cause | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-02-10 | c | 0.00073598 | 1.2095e-05 | 2016 | 2016-02-10 | C | 4 | 0.00073598 | 1.2095e-05
9898791 | 2016-02-11 03:09 | 2016-02-11 04:32 | 82.6167 | 105 | 7100.3833 | 67.6227 | 64.6227 | 0.02147 | 6785.3833 | 0.020517 | 0.00031749 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | E33 | Recloser E33 tripped on B phase O/C & E/F flags, line was patrolled and sectionalised and a Opossum was found on pole P13886, opossum was removed with hot line sticks. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-02-11 | c | 0.020517 | 0.00031749 | 2016 | 2016-02-11 | C | 105 | 0.020517 | 0.00031749
9899835 | 2016-02-12 10:00 | 2016-02-12 12:08 | 127.7333 | 72 | 9196.8 | 127.7333 | 124.7333 | 0.027809 | 8980.8 | 0.027156 | 0.00021771 | NAPA ID:16875 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2564 | Replace ABS 2564 - DNO 160109. Work location: SH1, Tirau. Work Order 30019339 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-02-12 | b | 0.013578 | 0.00010886 | 2016 | 2016-02-12 | B | 72 | 0.027156 | 0.00021771
9901970 | 2016-03-08 08:54 | 2016-03-08 10:30 | 96.0833 | 1 | 96.0833 | 96.0833 | 93.0833 | 0.00029053 | 93.0833 | 0.00028146 | 3.0238e-06 | NAPA ID:16467 TP_WANGANUI GXP > TAUPO QUAY SUB > GONVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV RMU 2011 | Isolate X179 Wanganui hospital to Re calibrate 11kv metering unit, Hospital will run on Generator during shutdown. Works location: Wanganui Base Hospital. WO 30007502 | F1 | GONVILLE | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.00014073 | 1.512e-06 | 2016 | 2016-03-08 | B | 1 | 0.00028146 | 3.0238e-06
9902266 | 2016-03-01 08:30 | 2016-03-01 13:40 | 310 | 40 | 12400 | 310 | 307 | 0.037495 | 12280 | 0.037132 | 0.00012095 | NAPA ID:16703 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | H34 | Cut trees around the 11kV. Works location: Turitea Rd & Pinedale Dr. WO 10152357 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.018566 | 6.0475e-05 | 2016 | 2016-03-01 | B | 40 | 0.037132 | 0.00012095
9902283 | 2016-03-01 10:15 | 2016-03-01 15:30 | 315 | 25 | 7875 | 315 | 312 | 0.023812 | 7800 | 0.023585 | 7.5594e-05 | NAPA ID:16259 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TA857 | Replace existing pole 717404 for a new 11m busck pole and replace existing TX T5395 for a new 50 kva pole mounted TX and upgrade earthing system. Works location: Omutarangi Rd. WO 10159770 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.011793 | 3.7797e-05 | 2016 | 2016-03-01 | B | 25 | 0.023585 | 7.5594e-05
9902318 | 2016-03-02 09:47 | 2016-03-02 13:22 | 214.6 | 43 | 9227.8 | 214.6 | 211.6 | 0.027903 | 9098.8 | 0.027513 | 0.00013002 | NAPA ID:16801 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 745045 | We are installing a new 11m pole mid span to raise the height of the lines for road clearance. Works location: Ackworth Rd. WO 30016543 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.013756 | 6.5011e-05 | 2016 | 2016-03-02 | B | 43 | 0.027513 | 0.00013002
9902324 | 2016-03-02 08:45 | 2016-03-02 11:49 | 184 | 224 | 41216 | 184 | 181 | 0.12463 | 40544 | 0.1226 | 0.00067732 | NAPA ID:16129 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10170 | Install new 300mm U/G cable from RMU 10170/2 to T6/530. Works location: JFK & Milson Line. WO 30015861 | F2 | ARMSTRONG ST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.061298 | 0.00033866 | 2016 | 2016-03-02 | B | 224 | 0.1226 | 0.00067732
9902334 | 2016-03-01 10:30 | 2016-03-01 14:40 | 250 | 3 | 750 | 250 | 247 | 0.0022678 | 741 | 0.0022406 | 9.0713e-06 | NAPA ID:16037 TP_MARTON GXP > PUKEPAPA SUB > LEEDSTOWN 22KV | 22 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 188 | Replace 22kv Transformer Z188 | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.0011203 | 4.536e-06 | 2016 | 2016-03-01 | B | 3 | 0.0022406 | 9.0713e-06
9902387 | 2016-03-02 10:15 | 2016-03-02 16:17 | 362 | 97 | 8315.1 | 85.7227 | 82.7227 | 0.025143 | 8024.1 | 0.024263 | 0.0002933 | NAPA ID:16809 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4806T | We have to upgrade a 50kvVA to a 100kVA for voltage complaints. Works location: Croyden Rd. WO 30020435 When faultman closed Fuses 5445 one of the fuse holders broke off, line needed to be isolated at ABS"s 5343 & 5591 to replace them.REF to OMS 10110086. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.012131 | 0.00014665 | 2016 | 2016-03-02 | B | 97 | 0.024263 | 0.0002933
9902412 | 2016-03-02 09:30 | 2016-03-02 10:20 | 50 | 24 | 1200 | 50 | 47 | 0.0036285 | 1128 | 0.0034108 | 7.257e-05 | NAPA ID:16332 TP_KINLEITH GXP > BAIRD ROAD SUB > CAMPBELL ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B0226 | Replace 2 x 11kV term arms at pole B0226. Works Location: Sloss ROad, Tokoroa. Work Order 30017433. This job was cancelled as the hospital receives info from the Colsons Hill PRT site no generator was arranged to be installed. Cancellation Reason: Michael | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-03-02 | b | 0.0017054 | 3.6285e-05 | 2016 | 2016-03-02 | B | 24 | 0.0034108 | 7.257e-05
9902414 | 2016-03-01 10:30 | 2016-03-01 11:54 | 84 | 8 | 672 | 84 | 81 | 0.002032 | 648 | 0.0019594 | 2.419e-05 | NAPA ID:16189 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V32 | To replace rotten larch pole with 10m busck pole. Works location: Manahara Rd. WO 10162794 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.0009797 | 1.2095e-05 | 2016 | 2016-03-01 | B | 8 | 0.0019594 | 2.419e-05
9902420 | 2016-03-02 10:30 | 2016-03-02 14:28 | 238 | 141 | 33558 | 238 | 235 | 0.10147 | 33135 | 0.10019 | 0.00042635 | NAPA ID:16277 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P11059 | To change 11kV cross arms at poles P11059 and P44372. Works location: Doughertys Rd & Kopikopiko Rd. WO 10162324 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.050096 | 0.00021317 | 2016 | 2016-03-02 | B | 141 | 0.10019 | 0.00042635
9902426 | 2016-03-02 08:45 | 2016-03-02 15:25 | 400 | 17 | 6800 | 400 | 397 | 0.020562 | 6749 | 0.020407 | 5.1404e-05 | NAPA ID:16593 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 840 | Treescape to remove over hanging trees around 11kV line. Works location: Papanui Junction, Taihape. WO 10152359 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.010204 | 2.5702e-05 | 2016 | 2016-03-02 | B | 17 | 0.020407 | 5.1404e-05
9902435 | 2016-03-02 09:33 | 2016-03-02 12:59 | 206.25 | 690 | 4125 | 5.9783 | 2.9783 | 0.012473 | 2055 | 0.0062138 | 0.0020864 | NAPA ID:16081 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P31690 | Replace 11kV pole P31690 hit by truck. Works location: Wylie Rd, Himitangi. WO 30016849 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-03-02 | b | 0.0031069 | 0.0010432 | 2016 | 2016-03-02 | B | 690 | 0.0062138 | 0.0020864
9903948 | 2016-03-01 09:15 | 2016-03-01 15:36 | 381 | 28 | 10668 | 381 | 378 | 0.032257 | 10584 | 0.032003 | 8.4665e-05 | NAPA ID:15832 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC482 | Replace cross arms at various sites. Works location: Kaihere Rd. WO 30002467 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-01 | b | 0.016002 | 4.2333e-05 | 2016 | 2016-03-01 | B | 28 | 0.032003 | 8.4665e-05
9903969 | 2016-03-03 09:18 | 2016-03-03 17:00 | 462 | 40 | 18480 | 462 | 459 | 0.055879 | 18360 | 0.055516 | 0.00012095 | NAPA ID:15836 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replac HV XArms Various Locations | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.027758 | 6.0475e-05 | 2016 | 2016-03-03 | B | 40 | 0.055516 | 0.00012095
9903994 | 2016-03-02 10:00 | 2016-03-02 14:45 | 285 | 1 | 285 | 285 | 282 | 0.00086177 | 282 | 0.0008527 | 3.0238e-06 | NAPA ID:16175 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1729 | Upgrade 50kVA transformer to 200kVA transformer. Works location: Pakaraka Rd, Putaruru. WO 30011625 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-02 | b | 0.00042635 | 1.512e-06 | 2016 | 2016-03-02 | B | 1 | 0.0008527 | 3.0238e-06
9904830 | 2016-02-11 15:47 | 2016-02-11 17:16 | 89 | 530 | 45580 | 86 | 83 | 0.13782 | 43990 | 0.13302 | 0.0016026 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 394591 | * 15:47 11kV CB 4 tripped to lock out, no flags. * Short duration later HEB construction contacted Powerco advising of Digger contacting lines. (Steve HEB construction 0275 060364) Safety Manager report No.586249 and NDR 51761 * 15.55 NOC advised SMC of | F4 | KAIRUA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-02-11 | c | 0.13302 | 0.0016026 | 2016 | 2016-02-11 | C | 530 | 0.13302 | 0.0016026
9905957 | 2016-02-11 15:51 | 2016-02-11 17:23 | 92.2167 | 303 | 8449.8 | 27.8871 | 24.8871 | 0.02555 | 7540.8 | 0.022802 | 0.0009162 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722147 | Truck Hit Conductors at pole 722147. Used 80 m Conductor 6 Sleeves. NDR Number N10098 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-02-11 | c | 0.022802 | 0.0009162 | 2016 | 2016-02-11 | C | 303 | 0.022802 | 0.0009162
9908048 | 2016-02-11 20:42 | 2016-02-12 03:54 | 431.7167 | 133 | 18615.2167 | 139.964 | 136.964 | 0.056288 | 18216.2167 | 0.055081 | 0.00040216 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 725111 | CB 6560 tripped. NZ FIRE ADVISE CAR V POLE 683 ARARATA RD NEAR TANGAHOE VALLEY RD CNR EVENT NUMBER F2015751 Replaced pole 725111 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-02-11 | c | 0.055081 | 0.00040216 | 2016 | 2016-02-11 | C | 133 | 0.055081 | 0.00040216
9909115 | 2016-03-02 07:38 | 2016-03-02 08:43 | 65.0667 | 1615 | 22067.15 | 13.6639 | 10.6639 | 0.066726 | 17222.15 | 0.052076 | 0.0048834 | NAPA ID:15990 TP_TE MATAI GXP > TE PUKE SUB > MANGOREWA | 33 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 221102 | Replace Poles hardware and conductors between poles 221102 and 230325. Works location: Rangiuru Rd. WO 30002585. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-03-02 | b | 0.026038 | 0.0024417 | 2016 | 2016-03-02 | B | 1615 | 0.052076 | 0.0048834
9909219 | 2016-02-12 10:50 | 2016-02-12 10:52 | 2 | 1 | 2 | 2 | -1 | 6.0475e-06 | 0 | 0 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Opened 9956/2 for testing generator, Reclosed. Contact Peter Lichfeild on site at 1030 to isolate building. | F2 | SPRING ST | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 2016-02-12 | c | 0 | 3.024e-06 | 2016 | 2016-02-12 | C | 1 | 0 | 3.0238e-06
9909226 | 2016-03-03 11:31 | 2016-03-03 13:20 | 109.3 | 42 | 4590.6 | 109.3 | 106.3 | 0.013881 | 4464.6 | 0.0135 | 0.000127 | NAPA ID:16458 TP_STRATFORD GXP > DOUGLAS SUB > HUIROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4973 | Replace HV Fuses 4973 (burning out). Works location: Bredow Rd, Toko. WO 30018344 | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.0067499 | 6.3499e-05 | 2016 | 2016-03-03 | B | 42 | 0.0135 | 0.000127
9909241 | 2016-03-02 10:00 | 2016-03-02 11:59 | 119 | 30 | 3570 | 119 | 116 | 0.010795 | 3480 | 0.010523 | 9.0713e-05 | NAPA ID:16689 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4396W | Replace & upgrade red tag Transformer pole. Works location: Wanganui River Rd. WO 30007491 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-03-02 | b | 0.0052613 | 4.5356e-05 | 2016 | 2016-03-02 | B | 30 | 0.010523 | 9.0713e-05
9909369 | 2016-03-03 10:16 | 2016-03-03 15:45 | 328.1833 | 62 | 20347.3667 | 328.1833 | 325.1833 | 0.061526 | 20161.3667 | 0.060963 | 0.00018747 | NAPA ID:16774 TP_OPUNAKE GXP > PUNGAREHU SUB > PARIHAKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 710903 | We are replacing pole 710903. Works location: Parihaka Rd. WO 30015343 | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.030482 | 9.3737e-05 | 2016 | 2016-03-03 | B | 62 | 0.060963 | 0.00018747
9909967 | 2016-02-17 10:30 | 2016-02-17 12:05 | 95 | 4 | 380 | 95 | 92 | 0.001149 | 368 | 0.0011127 | 1.2095e-05 | NAPA ID:16877 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1683 | Replace Transformer X1683. Work Location: Mokonui Road, Ranana. Works Order 30011328. Off 10:30 ON 12:05 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-17 | b | 0.00055637 | 6.048e-06 | 2016 | 2016-02-17 | B | 4 | 0.0011127 | 1.2095e-05
9910388 | 2016-02-12 10:18 | 2016-02-12 11:42 | 84 | 33 | 2772 | 84 | 81 | 0.0083819 | 2673 | 0.0080825 | 9.9784e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P2345 | Replace 1 X H/T Crossarm at Pole P2345. 3 X H/T Insulator as well. | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-02-12 | c | 0.0080825 | 9.9784e-05 | 2016 | 2016-02-12 | C | 33 | 0.0080825 | 9.9784e-05
9910464 | 2016-03-03 10:23 | 2016-03-03 13:55 | 212 | 3 | 636 | 212 | 209 | 0.0019231 | 627 | 0.0018959 | 9.0713e-06 | NAPA ID:16227 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X1301 | Remove T/F X1301 and replace rotten lv arms and hardware. Locks Rd, Hunterville. WO 10161742 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.00094795 | 4.536e-06 | 2016 | 2016-03-03 | B | 3 | 0.0018959 | 9.0713e-06
9910665 | 2016-03-03 09:00 | 2016-03-03 14:41 | 341 | 53 | 18073 | 341 | 338 | 0.054648 | 17914 | 0.054168 | 0.00016026 | NAPA ID:16688 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV E46 | Treescape are cutting trees from around the 11kv on Valley rd. Works location: Valley Rd. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.027084 | 8.013e-05 | 2016 | 2016-03-03 | B | 53 | 0.054168 | 0.00016026
9910734 | 2016-03-07 10:33 | 2016-03-07 14:58 | 265 | 48 | 8464 | 176.3333 | 173.3333 | 0.025593 | 8320 | 0.025158 | 0.00014514 | NAPA ID:16461 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 729322 | Replace blown surge arrestors at pole 726322. Works location: Allen Rd, Meremere. WO 10161227 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.012579 | 7.257e-05 | 2016 | 2016-03-07 | B | 48 | 0.025158 | 0.00014514
9911012 | 2016-03-04 08:50 | 2016-03-04 12:54 | 244 | 19 | 4636 | 244 | 241 | 0.014018 | 4579 | 0.013846 | 5.7451e-05 | NAPA ID:16457 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 773513 | Tree trimming and felling between poles 773513 and 773510, also rebind 11kv conductor at pole 773500. Works location: Pakaraka Rd, Waitotara. WO 30011321 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-04 | b | 0.0069229 | 2.8726e-05 | 2016 | 2016-03-04 | B | 19 | 0.013846 | 5.7451e-05
9911019 | 2016-03-04 09:30 | 2016-03-04 12:15 | 164.7333 | 10 | 1647.3333 | 164.7333 | 161.7333 | 0.0049811 | 1617.3333 | 0.0048904 | 3.0238e-05 | NAPA ID:16292 TP_MANGAMAIRE GXP > ALFREDTON SUB > CASTLEHILL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I21 | To change burnt off softwood pole. Works location: Castle Hill Rd. WO 30012046 | F5 | CASTLEHILL | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-04 | b | 0.0024452 | 1.5119e-05 | 2016 | 2016-03-04 | B | 10 | 0.0048904 | 3.0238e-05
9911037 | 2016-03-03 09:13 | 2016-03-03 10:30 | 77 | 2 | 154 | 77 | 74 | 0.00046566 | 148 | 0.00044752 | 6.0475e-06 | NAPA ID:16851 TP_GREYTOWN GXP > TUHITARATA SUB > OTARAIA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 810714 | To install 11kv fuses liveline. Works location: Lake Ferry Rd, Martinborough. WO 30003067 | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.00022376 | 3.024e-06 | 2016 | 2016-03-03 | B | 2 | 0.00044752 | 6.0475e-06
9911161 | 2016-03-11 10:22 | 2016-03-11 14:37 | 255 | 1 | 255 | 255 | 252 | 0.00077106 | 252 | 0.00076199 | 3.0238e-06 | NAPA ID:16010 TP_TE MATAI GXP > PAENGAROA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 230325 | Replace poles hardware and conductors between poles 230325 and 852956. Works location: Gulliver Rd, Paengoroa. WO 30002585 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-11 | b | 0.00038099 | 1.512e-06 | 2016 | 2016-03-11 | B | 1 | 0.00076199 | 3.0238e-06
9913757 | 2016-03-03 09:17 | 2016-03-03 14:25 | 308.3167 | 43 | 13257.6167 | 308.3167 | 305.3167 | 0.040088 | 13128.6167 | 0.039698 | 0.00013002 | NAPA ID:16566 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E12914 | LLP 1: To Br the jumpers supplying Switch 905. AP: To replace the hardware, arms & Switch (905) on pole E12914. LLP 2: To replace the jumpers supplying Switch 905. Works location: Summerville Rd, Te Poi. WO 30018759 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.019849 | 6.5011e-05 | 2016 | 2016-03-03 | B | 43 | 0.039698 | 0.00013002
9913886 | 2016-03-05 05:34 | 2016-03-05 07:45 | 131.25 | 100 | 13125 | 131.25 | 128.25 | 0.039687 | 12825 | 0.03878 | 0.00030238 | NAPA ID:16579 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G84 | 1Yr Maintance on Magnefix G84A/B/C/T. Works location: Botanical Rd. WO 30004182 | F3 | PASCAL ST 5 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-03-05 | b | 0.01939 | 0.00015119 | 2016 | 2016-03-05 | B | 100 | 0.03878 | 0.00030238
9914193 | 2016-03-01 10:27 | 2016-03-01 13:35 | 188 | 6 | 1128 | 188 | 185 | 0.0034108 | 1110 | 0.0033564 | 1.8143e-05 | NAPA ID:16094 TP_STRATFORD GXP > ELTHAM SUB > RAWHITIROA | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6029 | Remove faulty, redundant HV fuses 6827 and first span of redundant HV spur line as Requested. Works location: Rawhitiroa Rd. WO 30015087 | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.0016782 | 9.071e-06 | 2016 | 2016-03-01 | B | 6 | 0.0033564 | 1.8143e-05
9914231 | 2016-03-05 15:28 | 2016-03-05 18:21 | 173 | 1 | 173 | 173 | 170 | 0.00052311 | 170 | 0.00051404 | 3.0238e-06 | NAPA ID:16797 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV OS551 | Meter calibration. Works location: Mihaere Dr, Palmerston North. WO 30014570 | F3 | KARAMEA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-05 | b | 0.00025702 | 1.512e-06 | 2016 | 2016-03-05 | B | 1 | 0.00051404 | 3.0238e-06
9914242 | 2016-03-06 09:37 | 2016-03-06 11:31 | 113.1 | 5 | 565.5 | 113.1 | 110.1 | 0.0017099 | 550.5 | 0.0016646 | 1.5119e-05 | NAPA ID:16793 TP_BUNNYTHORPE GXP > FEILDING SUB > CROWN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | J93 | Meter Calibration. Works location: Kawakawa Rd, Feilding. WO 30007499 | F2 | CROWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-03-06 | b | 0.00083229 | 7.559e-06 | 2016 | 2016-03-06 | B | 5 | 0.0016646 | 1.5119e-05
9914248 | 2016-03-07 08:59 | 2016-03-07 15:58 | 418.6833 | 29 | 12141.8167 | 418.6833 | 415.6833 | 0.036714 | 12054.8167 | 0.036451 | 8.7689e-05 | NAPA ID:16595 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 2611 | Treescape to fell and remove trees around 11kV line. Works location: Ruanui Rd, Taihape. WO 10152359 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.018225 | 4.3845e-05 | 2016 | 2016-03-07 | B | 29 | 0.036451 | 8.7689e-05
9914254 | 2016-03-07 08:49 | 2016-03-07 14:22 | 332.6333 | 60 | 19958 | 332.6333 | 329.6333 | 0.060348 | 19778 | 0.059804 | 0.00018143 | NAPA ID:16435 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P15014 | Replace hardwood P15014. Works location; Tui St, Pahiatua. WO 30012838 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.029902 | 9.0713e-05 | 2016 | 2016-03-07 | B | 60 | 0.059804 | 0.00018143
9914268 | 2016-03-07 10:30 | 2016-03-07 14:50 | 260 | 2 | 520 | 260 | 257 | 0.0015724 | 514 | 0.0015542 | 6.0475e-06 | NAPA ID:15952 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/255 | To resag 11kV conductors. Works location: Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.00077711 | 3.024e-06 | 2016 | 2016-03-07 | B | 2 | 0.0015542 | 6.0475e-06
9914295 | 2016-03-07 10:04 | 2016-03-07 13:36 | 212 | 37 | 7844 | 212 | 209 | 0.023718 | 7733 | 0.023383 | 0.00011188 | NAPA ID:16832 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 139 | Change 11kV pole and hardware. Works location: Mangaone Valley Rd. WO 30015364 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.011691 | 5.594e-05 | 2016 | 2016-03-07 | B | 37 | 0.023383 | 0.00011188
9914333 | 2016-03-14 09:15 | 2016-03-14 20:20 | 665 | 1 | 665 | 665 | 662 | 0.0020108 | 662 | 0.0020017 | 3.0238e-06 | NAPA ID:16031 TP_TE MATAI GXP > PAENGAROA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 230325 | Replace poles hardware and conductors between poles 230325 and 852956. Works location: Gulliver Rd. WO 30002585 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-14 | b | 0.0010009 | 1.512e-06 | 2016 | 2016-03-14 | B | 1 | 0.0020017 | 3.0238e-06
9916928 | 2016-02-12 18:08 | 2016-02-12 23:02 | 294 | 344 | 101136 | 294 | 291 | 0.30581 | 100104 | 0.30269 | 0.0010402 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 706459 | CAR V POLE LINE DOWN NZ FIRE REQUIRE ETA 04 801 0812 EVENT F2016337. ADVISED HUB AND CONTROL ETA 10 MINUTES , FIRE SERVICE ADVISED. Replaced 11m pole with 1x HV Cross arm, & 2x LV Cross arms. NDR 41985. | F3 | SPRINGVALE | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2016-02-12 | c | 0.30269 | 0.0010402 | 2016 | 2016-02-12 | C | 344 | 0.30269 | 0.0010402
9917651 | 2016-02-12 19:20 | 2016-02-13 11:51 | 990.9 | 17 | 16845.1167 | 990.8892 | 987.8892 | 0.050936 | 16794.1167 | 0.050781 | 5.1404e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5302 | Previously replaced fuse @ Fused ABS 5291 and would appear there is another problem. Large tree branch fell through lines breaking all three at Pole 762285. Power isolated at Fuses 5302 & left off overnight. Returned 13/02/16 with tricky trees to cut tree | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-02-12 | c | 0.050781 | 5.1404e-05 | 2016 | 2016-02-12 | C | 17 | 0.050781 | 5.1404e-05
9918541 | 2016-02-13 07:48 | 2016-02-13 09:20 | 91.6667 | 16 | 1466.6667 | 91.6667 | 88.6667 | 0.0044348 | 1418.6667 | 0.0042897 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | WH184 | Replaced 2x 15Amp HV Links. Dead Swan found | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-02-13 | c | 0.0042897 | 4.838e-05 | 2016 | 2016-02-13 | C | 16 | 0.0042897 | 4.838e-05
9919341 | 2016-02-13 14:56 | 2016-02-14 05:13 | 856.8167 | 778 | 52564.1167 | 67.5631 | 64.5631 | 0.15894 | 50230.1167 | 0.15188 | 0.0023525 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 396 | Car V Pole at transformer 396 - Isolated at ABS's 6748 & 484 with backfeed via CB 2. See NDR 100100 for equipment used. Loss of pil from transformer was contained to avoid oil entering the nearby waterway. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-13 | c | 0.15188 | 0.0023525 | 2016 | 2016-02-13 | C | 778 | 0.15188 | 0.0023525
9929705 | 2016-02-13 19:55 | 2016-02-13 20:55 | 60.55 | 850 | 29635.3 | 34.8651 | 31.8651 | 0.08961 | 27085.3 | 0.081899 | 0.0025702 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB C865 | Feeder Sectionlised with no fault found | F3 | HIGH ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2016-02-13 | c | 0.081899 | 0.0025702 | 2016 | 2016-02-13 | C | 850 | 0.081899 | 0.0025702
9932343 | 2016-02-14 07:00 | 2016-02-14 08:56 | 116.1167 | 29 | 3367.3833 | 116.1167 | 113.1167 | 0.010182 | 3280.3833 | 0.0099191 | 8.7689e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 6746 | Replaced 2 x 15Amp HV Links | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-02-14 | c | 0.0099191 | 8.7689e-05 | 2016 | 2016-02-14 | C | 29 | 0.0099191 | 8.7689e-05
9942014 | 2016-02-14 18:22 | 2016-02-14 19:07 | 45.05 | 34 | 1531.7 | 45.05 | 42.05 | 0.0046315 | 1429.7 | 0.0043231 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6748 | LV lines low after repairs from car vs pole on 13/02/16 (within MAD). Isolated and rehung. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-14 | c | 0.0043231 | 0.00010281 | 2016 | 2016-02-14 | C | 34 | 0.0043231 | 0.00010281
9944417 | 2016-02-14 19:33 | 2016-02-14 19:53 | 19.7833 | 1 | 19.7833 | 19.7833 | 16.7833 | 5.982e-05 | 16.7833 | 5.0749e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 133 | Feed off Transformer X248 Fuses found Blown at Fuses 133 - cause unknown. Used 2 x 3amp fuses. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2016-02-14 | c | 5.0749e-05 | 3.024e-06 | 2016 | 2016-02-14 | C | 1 | 5.0749e-05 | 3.0238e-06
9945441 | 2016-02-15 01:05 | 2016-02-15 01:45 | 40.4 | 199 | 7286.4833 | 36.6155 | 33.6155 | 0.022033 | 6689.4833 | 0.020227 | 0.00060173 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | R31 | CB R31 Tripped - E/F. Recloser 4832 Tripped E/F. Line patrolled - cause of fault unknown. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-15 | c | 0.020227 | 0.00060173 | 2016 | 2016-02-15 | C | 199 | 0.020227 | 0.00060173
9946286 | 2016-02-15 08:34 | 2016-02-15 10:28 | 114.1 | 250 | 24682.2 | 98.7288 | 95.7288 | 0.074633 | 23932.2 | 0.072365 | 0.00075594 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | R11 | Photos taken of trees potentially causing the issue. CB R11 Tripped - Lline sectionalised nothing found. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-15 | c | 0.072365 | 0.00075594 | 2016 | 2016-02-15 | C | 250 | 0.072365 | 0.00075594
9946948 | 2016-02-23 09:18 | 2016-02-23 19:28 | 610.3667 | 1802 | 154059.5667 | 85.4937 | 82.4937 | 0.46584 | 148653.5667 | 0.44949 | 0.0054488 | NAPA ID:15510 TP_WAIKINO GXP | 11 | Planned | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 22 | TO RENEW 33 & 11KV POLES, X-ARMS & HARDWARE Downstream from pole CREWBH058. Refer to Methodology sheet for required switching and connection of 11kV Generation. Generators Tripped at 17:54 - Loss of Supply to Waihi Beach Sub. All Power Restored to Waihi | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-02-23 | b | 0.22475 | 0.0027244 | 2016 | 2016-02-23 | B | 1802 | 0.44949 | 0.0054488
9948674 | 2016-03-03 09:30 | 2016-03-03 15:43 | 373 | 30 | 11190 | 373 | 370 | 0.033836 | 11100 | 0.033564 | 9.0713e-05 | NAPA ID:16712 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole W1977 | AP FOR TREE WORKERS FROM POLE W1977 TO EOL. Works location: Boat Harbour Rd, Tairua. WO 30007130 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.016782 | 4.5356e-05 | 2016 | 2016-03-03 | B | 30 | 0.033564 | 9.0713e-05
9948677 | 2016-02-19 10:15 | 2016-02-19 14:45 | 270 | 6 | 1620 | 270 | 267 | 0.0048985 | 1602 | 0.0048441 | 1.8143e-05 | NAPA ID:16963 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 312 | we are replacing low voltage lines under 11kv lines to improve voltage to affected houses as requested by Greg Turner. Works location: Lincoln Rd. WO 30019897 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-19 | b | 0.002422 | 9.071e-06 | 2016 | 2016-02-19 | B | 6 | 0.0048441 | 1.8143e-05
9950329 | 2016-03-04 09:45 | 2016-03-04 15:12 | 327 | 43 | 14061 | 327 | 324 | 0.042517 | 13932 | 0.042127 | 0.00013002 | NAPA ID:16571 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2409 | To replace pole S0156, Fit for a 100kVA Transformer & relocate/upgrade transformer TC2409. Works location: Matatoki Rd, Thames. WO 30019715 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-03-04 | b | 0.021064 | 6.5011e-05 | 2016 | 2016-03-04 | B | 43 | 0.042127 | 0.00013002
9953132 | 2016-02-16 07:35 | 2016-02-16 07:43 | 8 | 2 | 16 | 8 | 5 | 4.838e-05 | 10 | 3.0238e-05 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3465 | Transformer TC3465 Isolated and Earthed under Own AP. Off time 07:35. On time 07:43. Repair LV lug on tranformer. 1 x LV Crimp Lug | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-02-16 | c | 3.0238e-05 | 6.048e-06 | 2016 | 2016-02-16 | C | 2 | 3.0238e-05 | 6.0475e-06
9953341 | 2016-02-16 08:50 | 2016-02-16 10:11 | 81 | 12 | 972 | 81 | 78 | 0.0029391 | 936 | 0.0028302 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 776648 | Tree branch through lines at pole 776648, line was isolated at Links 254 to repair the line. 3 meters - 16mm copper used. 2 X sleeves used. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-16 | c | 0.0028302 | 3.6285e-05 | 2016 | 2016-02-16 | C | 12 | 0.0028302 | 3.6285e-05
9953581 | 2016-02-29 09:45 | 2016-02-29 13:58 | 252.4667 | 49 | 12370.8667 | 252.4667 | 249.4667 | 0.037407 | 12223.8667 | 0.036962 | 0.00014816 | NAPA ID:16811 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P46493 | Install new temporary regulator site 1 at P46493. Works location: Titoki Rd, Makuri. WO 10157280 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-29 | b | 0.018481 | 7.4082e-05 | 2016 | 2016-02-29 | B | 49 | 0.036962 | 0.00014816
9954433 | 2016-02-19 10:15 | 2016-02-19 13:10 | 175 | 19 | 3325 | 175 | 172 | 0.010054 | 3268 | 0.0098817 | 5.7451e-05 | NAPA ID:16983 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses T24 | Replace poles and crossarms 45381 and 45382. Works location: Mangaramarama Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-19 | b | 0.0049408 | 2.8726e-05 | 2016 | 2016-02-19 | B | 19 | 0.0098817 | 5.7451e-05
9954687 | 2016-03-03 09:15 | 2016-03-03 10:45 | 90.3 | 6 | 541.8 | 90.3 | 87.3 | 0.0016383 | 523.8 | 0.0015838 | 1.8143e-05 | NAPA ID:17018 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2744 | Perform 6 earth tests on de-energized SWER line via Helicopter and quad bike. Works location: Pakaraka Rd. WO 30005857 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.00079192 | 9.071e-06 | 2016 | 2016-03-03 | B | 6 | 0.0015838 | 1.8143e-05
9954988 | 2016-02-16 12:31 | 2016-02-16 19:30 | 418.75 | 12 | 5025 | 418.75 | 415.75 | 0.015194 | 4989 | 0.015086 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 805530 | Car V pole, lines down causing a fire. Fire comms, eta required, F2018562. Advised fire comms -40mins 6.32pm 16/2 emailed svs hub for update. 19.15pm Sammy advised that she has contacted faultman and they are still onsite, they are working with control a | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-02-16 | c | 0.015086 | 3.6285e-05 | 2016 | 2016-02-16 | C | 12 | 0.015086 | 3.6285e-05
9956108 | 2016-03-04 09:15 | 2016-03-04 11:46 | 151 | 84 | 12684 | 151 | 148 | 0.038353 | 12432 | 0.037591 | 0.000254 | NAPA ID:16719 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 9 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 836T | We are replacing 11kV Fuses at transformer 836T and replacing the cross arm they are mounted on. NOTE!! Transformer 836T will be isolated to take load off so will need outages noticed. Works location: Massey St, New Plymouth. WO 30000865 | F3 | BROOKLANDS 9 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-04 | b | 0.018796 | 0.000127 | 2016 | 2016-03-04 | B | 84 | 0.037591 | 0.000254
9956643 | 2016-02-16 20:14 | 2016-02-16 20:46 | 32.9667 | 898 | 29604.0667 | 32.9667 | 29.9667 | 0.089516 | 26910.0667 | 0.08137 | 0.0027153 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Q12442 | Trip CB 3, E/F. L/O. Report from locals of a bird strike at Pole Q12442. Dead bird found at bottom of pole. Locals say that there has been numerous dead birds found at the base of poles in this area. I suggest that bird deterrent spikes be considered for | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-02-16 | c | 0.08137 | 0.0027153 | 2016 | 2016-02-16 | C | 898 | 0.08137 | 0.0027153
9959557 | 2016-02-17 05:44 | 2016-02-17 10:33 | 289.4667 | 199 | 35076.3667 | 176.2631 | 173.2631 | 0.10606 | 34479.3667 | 0.10426 | 0.00060173 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736150 | Replaced 2x pin and insulators on pole 736150 and 1x pin and insulator on pole 736471 | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.10426 | 0.00060173 | 2016 | 2016-02-17 | C | 199 | 0.10426 | 0.00060173
9960282 | 2016-02-17 07:25 | 2016-02-17 09:50 | 145.3833 | 1 | 145.3833 | 145.3833 | 142.3833 | 0.0004396 | 142.3833 | 0.00043053 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4019 | Faultman unable to get through to control. HV Fuses 4019 replaced 2 x 8amp Fuses. Cause - birds. Nothing else repaired or replaced. Adjacent assets up to Powerco standard. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.00043053 | 3.024e-06 | 2016 | 2016-02-17 | C | 1 | 0.00043053 | 3.0238e-06
9960287 | 2016-02-17 07:21 | 2016-02-17 11:20 | 239 | 22 | 5258 | 239 | 236 | 0.015899 | 5192 | 0.015699 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231061 | (PKW 4) Line x 1 down at pole 231061. Isolation at fuses SG7 001 (spur - no back feed). Line repaired all service restored. Materials 10 meters conductor, 4 x H/V sleeves. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-02-17 | c | 0.015699 | 6.6523e-05 | 2016 | 2016-02-17 | C | 22 | 0.015699 | 6.6523e-05
9960329 | 2016-02-17 09:20 | 2016-02-17 11:47 | 147 | 25 | 2555 | 102.2 | 99.2 | 0.0077257 | 2480 | 0.0074989 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2820T | Pole 759264 transformer 2820T. FM advise: he needs to isolate the line to replace a broken DDO (in half) and another one up the pole does not look too good and will need replacement, also extending jumpers. Advised FM this is still 1R work. He also reques | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.0074989 | 7.5594e-05 | 2016 | 2016-02-17 | C | 25 | 0.0074989 | 7.5594e-05
9960630 | 2016-03-04 09:30 | 2016-03-04 12:40 | 190 | 3 | 570 | 190 | 187 | 0.0017235 | 561 | 0.0016963 | 9.0713e-06 | NAPA ID:16256 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W2010 | Replace existing TX W2010 for new 30 kva pole mounted TX, replace LV crossarms and upgrade earthing. Works location: South Rd, Hawera. WO 10159770 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-04 | b | 0.00084817 | 4.536e-06 | 2016 | 2016-03-04 | B | 3 | 0.0016963 | 9.0713e-06
9960637 | 2016-02-17 09:13 | 2016-02-17 11:27 | 134.1333 | 386 | 27764.3 | 71.9282 | 68.9282 | 0.083953 | 26606.3 | 0.080451 | 0.0011672 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | parent of 9960359 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-02-17 | c | 0.080451 | 0.0011672 | 2016 | 2016-02-17 | C | 386 | 0.080451 | 0.0011672
9961603 | 2016-03-08 13:00 | 2016-03-08 14:47 | 107 | 25 | 2675 | 107 | 104 | 0.0080886 | 2600 | 0.0078618 | 7.5594e-05 | NAPA ID:16802 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | OS446 | Calibration of 11kV Metering. Oil testing of Transformer so Powerco can take ownership. Works location: Olive Tree Village, Palmerston North. WO 30007501 | F3 | PASCAL ST 6 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.0039309 | 3.7797e-05 | 2016 | 2016-03-08 | B | 25 | 0.0078618 | 7.5594e-05
9961782 | 2016-03-04 11:00 | 2016-03-04 12:15 | 75 | 7 | 525 | 75 | 72 | 0.0015875 | 504 | 0.001524 | 2.1166e-05 | NAPA ID:16222 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 984 | Remove existing TX 984 and replace with a new 30 kva TX, upgrade earthing system to comply with powerco standards. Works location: Carrington Rd. WO 10159770 | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-04 | b | 0.00076199 | 1.0583e-05 | 2016 | 2016-03-04 | B | 7 | 0.001524 | 2.1166e-05
9962150 | 2016-03-10 09:30 | 2016-03-10 14:54 | 324 | 598 | 192750 | 322.3244 | 319.3244 | 0.58283 | 190956 | 0.57741 | 0.0018082 | NAPA ID:16741 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 6 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 6639 | We are installing a new 11kv Sectos switch with in line 11kv solid links on the source side for visual break options. A generator will supply a kindergarden at 147a Govett Ave. The generator will be connected to the service cable only and will be connecte | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-10 | b | 0.2887 | 0.0009041 | 2016 | 2016-03-10 | B | 598 | 0.57741 | 0.0018082
9962523 | 2016-02-17 13:45 | 2016-02-17 14:10 | 25 | 1 | 25 | 25 | 22 | 7.5594e-05 | 22 | 6.6523e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | TP1052 | Transformer TP1052 Isolated and Earth to lower HV Taps OFF 13:45 ON 14:10 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-02-17 | c | 6.6523e-05 | 3.024e-06 | 2016 | 2016-02-17 | C | 1 | 6.6523e-05 | 3.0238e-06
9962533 | 2016-02-17 12:55 | 2016-02-17 15:01 | 126.35 | 142 | 14157.2333 | 99.6988 | 96.6988 | 0.042808 | 13731.2333 | 0.04152 | 0.00042937 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 575 | Recloser 575 tripped on Ph A & B OC. Line Patrolled. No Fault found. Relivened successfully. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.04152 | 0.00042937 | 2016 | 2016-02-17 | C | 142 | 0.04152 | 0.00042937
9964060 | 2016-02-17 13:47 | 2016-02-17 18:05 | 258 | 233 | 20339.1833 | 87.2926 | 84.2926 | 0.061501 | 19640.1833 | 0.059387 | 0.00070454 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Recloser 6497 - Eltham R51 | 1R - Line Patrol Required. 16:22 - 2R For tree Removal.Cut trees away at pole 733325 and untangled lines | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.059387 | 0.00070454 | 2016 | 2016-02-17 | C | 233 | 0.059387 | 0.00070454
9964988 | 2016-02-17 14:32 | 2016-02-17 19:08 | 275.1667 | 1 | 275.1667 | 275.1667 | 272.1667 | 0.00083204 | 272.1667 | 0.00082297 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3445T | Cut away lightning arrestor a transformer 3445T | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.00082297 | 3.024e-06 | 2016 | 2016-02-17 | C | 1 | 0.00082297 | 3.0238e-06
9967329 | 2016-02-17 15:50 | 2016-02-17 17:21 | 90.7 | 6 | 544.2 | 90.7 | 87.7 | 0.0016455 | 526.2 | 0.0015911 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC1408 | ** check with FM whether this would affect 1477B Piako Road (9967674) Replace 2 x 6A H/V, O/H fuses ( bird strike ) | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-02-17 | c | 0.0015911 | 1.8143e-05 | 2016 | 2016-02-17 | C | 6 | 0.0015911 | 1.8143e-05
9967399 | 2016-02-17 15:44 | 2016-02-17 16:25 | 41.05 | 65 | 2666.2 | 41.0185 | 38.0185 | 0.008062 | 2471.2 | 0.0074723 | 0.00019654 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4994 | ABS 5455 opened and tagged to repair jumper at fuses 4994 | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.0074723 | 0.00019654 | 2016 | 2016-02-17 | C | 65 | 0.0074723 | 0.00019654
9967715 | 2016-02-17 20:20 | 2016-02-18 15:30 | 1150 | 2 | 2300 | 1150 | 1147 | 0.0069546 | 2294 | 0.0069365 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 425788 | Faultman found blown fuse at Fuses WH212, left. The network past Fuses WH212 has been isolated & earthed and a CACD issued for work to be completed by Asphlund. Crew completed and will make new request to get crew to attend to restore the network on compl | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.0069365 | 6.048e-06 | 2016 | 2016-02-17 | C | 2 | 0.0069365 | 6.0475e-06
9968206 | 2016-02-17 18:30 | 2016-02-17 22:22 | 232 | 32 | 7424 | 232 | 229 | 0.022448 | 7328 | 0.022158 | 9.676e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 841125 | Mark has left site to attend to arcing lines in East Beach, will return to this job when complete there.Faultman found trees in the lines at pole 841125 and at 2 other sites, line was isolated at Fuses 5194 so tree contractor can cut the trees. Tree contr | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.022158 | 9.676e-05 | 2016 | 2016-02-17 | C | 32 | 0.022158 | 9.676e-05
9968327 | 2016-02-17 18:00 | 2016-02-17 19:03 | 63 | 13 | 819 | 63 | 60 | 0.0024765 | 780 | 0.0023585 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3445T | Fuses 4965 opened and tagged. Cut away faulty lightening arrestor | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.0023585 | 3.9309e-05 | 2016 | 2016-02-17 | C | 13 | 0.0023585 | 3.9309e-05
9968567 | 2016-02-17 18:59 | 2016-02-17 20:50 | 110.5333 | 5 | 552.6667 | 110.5333 | 107.5333 | 0.0016711 | 537.6667 | 0.0016258 | 1.5119e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 4129T | Faultman found blown fuse at transformer 4129T caused by tree, faultman will inform tree cutters of location in morning to have it cut. 2 X 2 amp hv fuses replaced. | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.0016258 | 1.5119e-05 | 2016 | 2016-02-17 | C | 5 | 0.0016258 | 1.5119e-05
9968738 | 2016-02-17 19:15 | 2016-02-17 20:46 | 91 | 122 | 7279.4333 | 59.6675 | 56.6675 | 0.022011 | 6913.4333 | 0.020905 | 0.0003689 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 821098 | Todd in control advised FM is requesting another faultman to attend, Non scadarised area. Sent through CR and this can be sorted at invoicing. Faultman found Recloser C429/2 open, line was patrolled and sectionalised and branches at transformer T3182 and | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.020905 | 0.0003689 | 2016 | 2016-02-17 | C | 122 | 0.020905 | 0.0003689
9969202 | 2016-02-17 21:57 | 2016-02-18 14:05 | 968 | 13 | 12584 | 968 | 965 | 0.038051 | 12545 | 0.037933 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 346 | Has shelter belt of trees which is clashing the low tension lines and this has caused HV fuse to blow. There is approx. 100m of shelter belt that will need to be cut tonight. Possibly owned by Tegal Chickens unsure. FM will organise for Tree Contractor to | F1 | BELL BLOCK 3 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.037933 | 3.9309e-05 | 2016 | 2016-02-17 | C | 13 | 0.037933 | 3.9309e-05
9969271 | 2016-02-17 20:12 | 2016-02-17 21:31 | 78.7333 | 1 | 78.7333 | 78.7333 | 75.7333 | 0.00023807 | 75.7333 | 0.000229 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | W13840 | Advised svs hub 8:14pm Has been inspected looks like salt spray. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-02-17 | c | 0.000229 | 3.024e-06 | 2016 | 2016-02-17 | C | 1 | 0.000229 | 3.0238e-06
9969309 | 2016-02-17 20:20 | 2016-02-18 00:10 | 230.4833 | 239 | 22635.4833 | 94.7091 | 91.7091 | 0.068444 | 21918.4833 | 0.066276 | 0.00072268 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780231 | CB 6 tripped on C phase O/C & E/F flags, line was patrolled and sectionalised and a line down was found at pole 780213, line was isolated at ABS's O53 & 249 to repair the lines.2 mters 25mm copper conductor used. 4 X sleeves used. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-02-17 | c | 0.066276 | 0.00072268 | 2016 | 2016-02-17 | C | 239 | 0.066276 | 0.00072268
9971909 | 2016-02-18 00:30 | 2016-02-18 01:53 | 83 | 72 | 5976 | 83 | 80 | 0.01807 | 5760 | 0.017417 | 0.00021771 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 771443 | Trees catching fire due to clashing with lines opp this address - halfway between Waverley and Patea - Luptons truck depot, 9.49pm advised Glo & control. Faultman found trees in the line, contacted tree contractor to come cut the trees.Line was isolated a | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-02-18 | c | 0.017417 | 0.00021771 | 2016 | 2016-02-18 | C | 72 | 0.017417 | 0.00021771
9972376 | 2016-02-18 00:52 | 2016-02-18 06:28 | 336.2333 | 551 | 18658.25 | 33.8625 | 30.8625 | 0.056418 | 17005.25 | 0.05142 | 0.0016661 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 384101 | CB1 Trip. E/F. L/O. Backfeed up to RS9548 via RS 9760. Line down at Pole 384101. Isolated between ABS's IP153, IP514 and SE7005. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.05142 | 0.0016661 | 2016 | 2016-02-18 | C | 551 | 0.05142 | 0.0016661
9972944 | 2016-02-18 01:15 | 2016-02-18 01:31 | 15.6 | 152 | 2366.1333 | 15.5667 | 12.5667 | 0.0071546 | 1910.1333 | 0.0057758 | 0.00045961 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 5 | CB 5 Trip. O/C. L/O. Backfeed up to Recloser 9664 via Sectionaliser 9836. Closed back in after 15 min. Suspect Line Clash. High winds in the area at the time. | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.0057758 | 0.00045961 | 2016 | 2016-02-18 | C | 152 | 0.0057758 | 0.00045961
9973705 | 2016-02-18 02:07 | 2016-02-18 06:55 | 288.2667 | 211 | 27074.95 | 128.3173 | 125.3173 | 0.081868 | 26441.95 | 0.079954 | 0.00063801 |  | 6.6 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 843560 | CB I21 tripped on phase to phase O/C flags, Feeder sectionalised and isolated past ABS 6511, no backfeeds Replace 1 x dead end & 1 x binder. Relivened OK | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.079954 | 0.00063801 | 2016 | 2016-02-18 | C | 211 | 0.079954 | 0.00063801
9975751 | 2016-02-18 02:12 | 2016-02-18 05:17 | 185.0167 | 496 | 51536.1333 | 103.9035 | 100.9035 | 0.15583 | 50048.1333 | 0.15133 | 0.0014998 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758028 | CB 6 tripped on E/F flags,line was patrolled and sectionalised and a floating wire was found at pole 758028 line was isolated at ABS's 252 & 407 to repair it. 1 X binder used | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.15133 | 0.0014998 | 2016 | 2016-02-18 | C | 496 | 0.15133 | 0.0014998
9977500 | 2016-02-18 02:21 | 2016-02-18 12:52 | 630.7833 | 178 | 32442.5667 | 182.2616 | 179.2616 | 0.098099 | 31908.5667 | 0.096484 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809563 | SMC called to advise Jeremy and Paul left site around 7.30am. Have requested CR for the new crew who replaced them this morning Tripping on Recloser CB4659/2 on B Phase E/F. Some difficulty in tracking down fault - eventually traced to defective insulato | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.096484 | 0.00053823 | 2016 | 2016-02-18 | C | 178 | 0.096484 | 0.00053823
9978533 | 2016-02-18 03:07 | 2016-02-18 03:31 | 23.4833 | 205 | 4814.0833 | 23.4833 | 20.4833 | 0.014557 | 4199.0833 | 0.012697 | 0.00061987 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9198/2 | Recloser 9198 Trip. No Flags. L/O. Closed back in OK. Suspect Line Clash. High winds in the area at the time. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.012697 | 0.00061987 | 2016 | 2016-02-18 | C | 205 | 0.012697 | 0.00061987
9978880 | 2016-02-18 03:09 | 2016-02-18 03:12 | 2.9667 | 133 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00040216 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Cb 6560 A/r | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00040216 | 2016 | 2016-02-18 | C | 133 | 0 | 0.00040216
9980420 | 2016-02-18 03:16 | 2016-02-18 03:26 | 9.5167 | 235 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00071058 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB NG 2 a/r | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00071058 | 2016 | 2016-02-18 | C | 235 | 0 | 0.00071058
9980657 | 2016-02-18 03:26 | 2016-02-18 07:29 | 242.8333 | 252 | 27227.3833 | 108.0452 | 105.0452 | 0.082329 | 26471.3833 | 0.080043 | 0.00076199 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3790 - on your desk Joanne | Tripping on CB C927 on A Phae O/C, E/F. A Broken HT Lead found at Transformer T3790. Isolation between ABS S512 and S588 with backfeed at ABS S525. Reaired OK and relivened. NOTE: This transformer not on SCADA. GIS advised. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.080043 | 0.00076199 | 2016 | 2016-02-18 | C | 252 | 0.080043 | 0.00076199
9981787 | 2016-02-18 03:39 | 2016-02-19 12:57 | 1998 | 5 | 9986.6667 | 1997.3333 | 1994.3333 | 0.030197 | 9971.6667 | 0.030152 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | CA465 | Tree across road, unable to access. Contractors on way before can get to job. 20.29 Retailer calling for customer at 614 Morea Road, Called Cindy at svs hub asking if faultman still enroute since 3.30pm. Cindy to call FM and check what is happening and s | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.030152 | 1.5119e-05 | 2016 | 2016-02-18 | C | 5 | 0.030152 | 1.5119e-05
9981810 | 2016-02-18 03:06 | 2016-02-18 03:46 | 40.5333 | 142 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00042937 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | cb 575 A/r | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00042937 | 2016 | 2016-02-18 | C | 142 | 0 | 0.00042937
9982046 | 2016-02-18 03:48 | 2016-02-18 10:54 | 426 | 33 | 14056.4 | 425.9515 | 422.9515 | 0.042503 | 13957.4 | 0.042204 | 9.9784e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5194 | Check 9982046: Line is down at #238 but causing no power at #438. FM has put cone out there and advised customer it is all safe to drive over the lines. Isolated at fuses 5194 3 x 20 amp fuses 100m copper conductor 6 sleeves. Materials used: 3 x 20A Lugs, | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.042204 | 9.9784e-05 | 2016 | 2016-02-18 | C | 33 | 0.042204 | 9.9784e-05
9983644 | 2016-02-18 04:16 | 2016-02-18 05:36 | 80.2833 | 122 | 9768.1333 | 80.0667 | 77.0667 | 0.029536 | 9402.1333 | 0.02843 | 0.0003689 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 375424 | Recloser 4236/2 tripped on A, B & C phase O/C flags, line was patrolled and faultman found a branch on the line at pole 375424, branch was remove with hot line stickes. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.02843 | 0.0003689 | 2016 | 2016-02-18 | C | 122 | 0.02843 | 0.0003689
9984047 | 2016-02-18 03:55 | 2016-02-18 04:59 | 64.6333 | 149 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00045054 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 284 a/r | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00045054 | 2016 | 2016-02-18 | C | 149 | 0 | 0.00045054
9984202 | 2016-02-18 05:04 | 2016-02-18 05:09 | 4.8333 | 154 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00046566 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB H41 A/r | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00046566 | 2016 | 2016-02-18 | C | 154 | 0 | 0.00046566
9984926 | 2016-02-18 05:31 | 2016-02-18 10:12 | 280.55 | 175 | 38902.2333 | 222.2985 | 219.2985 | 0.11763 | 38377.2333 | 0.11604 | 0.00052916 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 832047 | Tripping on CB C948 (No flags - Non Scada). Feeder sectionalised / patrolled with a conductor found down. (Tree branch broke and fell through due to heavy rain). Isolation requiredfrom ABS C420/1. Conductor repair required 10 metres and 2 jointers. NDR 3 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.11604 | 0.00052916 | 2016 | 2016-02-18 | C | 175 | 0.11604 | 0.00052916
9984932 | 2016-02-18 05:32 | 2016-02-18 11:18 | 346 | 1 | 346 | 346 | 343 | 0.0010462 | 343 | 0.0010371 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5590 | No Power to Waihapa Wellsite. NDR 43433. 2x 15amp Fuses. Cause: possibly trees. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.0010371 | 3.024e-06 | 2016 | 2016-02-18 | C | 1 | 0.0010371 | 3.0238e-06
9984936 | 2016-02-18 05:04 | 2016-02-18 05:34 | 29.8667 | 114 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00034471 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 564 | CB 564 Auto Reclose. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0 | 0.00034471 | 2016 | 2016-02-18 | C | 114 | 0 | 0.00034471
9985448 | 2016-02-18 06:38 | 2016-02-18 15:34 | 535.8 | 1 | 535.8 | 535.8 | 532.8 | 0.0016201 | 532.8 | 0.0016111 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746 | 2.24pm - customer advise power still off. Tx 746 has failed - POCO has installed a generator and tx will need to be replaced. Affects 40-50 houses. FM has finished on site, *** waiting to hear back from Neil whether it will be him or another crew to do | F3 | BELL BLOCK 7 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.0016111 | 3.024e-06 | 2016 | 2016-02-18 | C | 1 | 0.0016111 | 3.0238e-06
9986379 | 2016-02-18 07:05 | 2016-02-18 09:35 | 150.2833 | 6 | 901.7 | 150.2833 | 147.2833 | 0.0027265 | 883.7 | 0.0026721 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1922 | 2 x 3 amp Fuses due to weather. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-18 | c | 0.0026721 | 1.8143e-05 | 2016 | 2016-02-18 | C | 6 | 0.0026721 | 1.8143e-05
9986556 | 2016-02-18 10:12 | 2016-02-18 11:50 | 98 | 86 | 8428 | 98 | 95 | 0.025484 | 8170 | 0.024704 | 0.00026004 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3280 | pls check if 9986711 is related (192 Kina Road). Outage required between ABS NG310 & ABS NG326, No back feeds available. Replace 3 x Fuses, 3 x 6A fuse links, 3 x bolts & washers. Relivened OK. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.024704 | 0.00026004 | 2016 | 2016-02-18 | C | 86 | 0.024704 | 0.00026004
9986565 | 2016-02-18 07:24 | 2016-02-18 12:40 | 316 | 6 | 1896 | 316 | 313 | 0.0057331 | 1878 | 0.0056786 | 1.8143e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 5482 | Retailer has rung to say that this the cow shed and that there are 400 cows waiting to be milked. Have advised SMC. Reload Reliven at fuses 5482. 2 x 10 A Fuses. Caused by Wind. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.0056786 | 1.8143e-05 | 2016 | 2016-02-18 | C | 6 | 0.0056786 | 1.8143e-05
9986591 | 2016-02-18 07:29 | 2016-02-18 10:11 | 162.15 | 27 | 4378.05 | 162.15 | 159.15 | 0.013238 | 4297.05 | 0.012993 | 8.1642e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5193 | 2 x 15 amp fuse. Cause = weather. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.012993 | 8.1642e-05 | 2016 | 2016-02-18 | C | 27 | 0.012993 | 8.1642e-05
9987181 | 2016-02-18 09:05 | 2016-02-18 10:40 | 95 | 1 | 95 | 95 | 92 | 0.00028726 | 92 | 0.00027819 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1143 | 8.11am advised hub of 999. 749127 retension wire x2. Materials Used:3 mtrs wire, 2 x sleeves & 2 x binders. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.00027819 | 3.024e-06 | 2016 | 2016-02-18 | C | 1 | 0.00027819 | 3.0238e-06
9987740 | 2016-03-03 10:06 | 2016-03-03 14:47 | 280.6333 | 1 | 280.6333 | 280.6333 | 277.6333 | 0.00084857 | 277.6333 | 0.0008395 | 3.0238e-06 | NAPA ID:16993 TP_MARTON GXP > RATA SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2565 | Change out Defective CT Terminal Box, Discussed and Emailed with Ravensdown Rata and Denise Wood Provide Standalone Generator for the 1 ICP / Customer on this feeder. Works location: Rata Sub. WO 30003351 | F3 | FACTORY | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.00041975 | 1.512e-06 | 2016 | 2016-03-03 | B | 1 | 0.0008395 | 3.0238e-06
9987807 | 2016-03-06 09:20 | 2016-03-06 11:41 | 140.7333 | 15 | 2111 | 140.7333 | 137.7333 | 0.0063832 | 2066 | 0.0062471 | 4.5356e-05 | NAPA ID:16597 TP_HAWERA GXP > MANAIA SUB > MANAIA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 719519 | Replace badly spalling pole 719519. Works location: Karaka St, Manaia. WO 10161439 | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-06 | b | 0.0031235 | 2.2678e-05 | 2016 | 2016-03-06 | B | 15 | 0.0062471 | 4.5356e-05
9990267 | 2016-03-09 09:33 | 2016-03-09 15:03 | 329.6333 | 37 | 12196.4333 | 329.6333 | 326.6333 | 0.036879 | 12085.4333 | 0.036543 | 0.00011188 | NAPA ID:16438 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/841 | Replace 33kV and 11kV pole P41456 & 11kV transformer pole T2/841. Works location: Clevely Rd, Bunnythorpe. WO 10157245 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.018272 | 5.594e-05 | 2016 | 2016-03-09 | B | 37 | 0.036543 | 0.00011188
9990324 | 2016-02-18 12:10 | 2016-02-18 12:46 | 35.8 | 146 | 5203.8 | 35.6425 | 32.6425 | 0.015735 | 4765.8 | 0.014411 | 0.00044147 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736468 | Outage required past ABS 6188 to repair jumper at Pole 736468. No back feeds available. Replaced 2 x sheer bolts, 1m 35mm conductor. Relivened OK. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.014411 | 0.00044147 | 2016 | 2016-02-18 | C | 146 | 0.014411 | 0.00044147
9990490 | 2016-02-18 12:13 | 2016-02-18 13:50 | 96.8667 | 1 | 96.8667 | 96.8667 | 93.8667 | 0.0002929 | 93.8667 | 0.00028383 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7598 | Reload Reliven at Fuses 7598. 2 x 10 A Fuses. Cause by Bird strike. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.00028383 | 3.024e-06 | 2016 | 2016-02-18 | C | 1 | 0.00028383 | 3.0238e-06
9990541 | 2016-02-18 12:29 | 2016-02-18 17:28 | 299.05 | 105 | 4848.5667 | 46.1768 | 43.1768 | 0.014661 | 4533.5667 | 0.013708 | 0.00031749 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 833739 | Received initial auto-reclose on CB C828 on Phase A-C O/C. Received report of digger bringing down lines and breaking a pole. CB C828 open from NOC for safety. Fault isolated via Fuses 7832 and remainder of feeder restored. Required pole replacement inclu | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.013708 | 0.00031749 | 2016 | 2016-02-18 | C | 105 | 0.013708 | 0.00031749
9991103 | 2016-03-08 10:24 | 2016-03-08 12:26 | 121.55 | 1 | 121.55 | 121.55 | 118.55 | 0.00036754 | 118.55 | 0.00035847 | 3.0238e-06 | NAPA ID:16529 TP_HAWERA GXP > MANAIA SUB > OKAIAWA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 718457 | Replace faulty arrestors at Manaia sub on Okaiawa feeder , and repair Hv cable earth lead at pole 718457. Works location: Manaia Sub, Normanby Rd. WO 30015129 | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.00017923 | 1.512e-06 | 2016 | 2016-03-08 | B | 1 | 0.00035847 | 3.0238e-06
9991617 | 2016-02-18 15:06 | 2016-02-18 15:40 | 34 | 40 | 1360 | 34 | 31 | 0.0041123 | 1240 | 0.0037495 | 0.00012095 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1251 | North Power repoerted Broken 11kV Crosswarm at Pole E1251. 2R - Replace Broken 11kV Crossarm. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.0037495 | 0.00012095 | 2016 | 2016-02-18 | C | 40 | 0.0037495 | 0.00012095
9991706 | 2016-02-18 13:39 | 2016-02-18 16:36 | 176.8667 | 16 | 2829.8667 | 176.8667 | 173.8667 | 0.0085568 | 2781.8667 | 0.0084117 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K1183 | Advised Shannon at Hub. Advised Control. Isolated at Fuses FP1322. Outage required past Fuses FP1322 to repiar lines. No back feed available. Replaced 6 x sleeves, 2m 16mm copper & 3 x 25A fuses | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.0084117 | 4.838e-05 | 2016 | 2016-02-18 | C | 16 | 0.0084117 | 4.838e-05
9992118 | 2016-03-07 10:36 | 2016-03-07 13:35 | 179 | 5 | 895 | 179 | 176 | 0.0027063 | 880 | 0.0026609 | 1.5119e-05 | NAPA ID:16876 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4556W | Upgrade earthing and install MDI meters on transformer 4556W. Works location: Beamish Rd, Bulls. WO 10162187 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.0013305 | 7.559e-06 | 2016 | 2016-03-07 | B | 5 | 0.0026609 | 1.5119e-05
9992406 | 2016-02-18 15:01 | 2016-02-18 16:09 | 67.8333 | 291 | 15230.6167 | 52.3389 | 49.3389 | 0.046054 | 14357.6167 | 0.043414 | 0.00087991 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | na | Cb 5 tripped patrolled nothing found | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.043414 | 0.00087991 | 2016 | 2016-02-18 | C | 291 | 0.043414 | 0.00087991
9992824 | 2016-02-18 15:16 | 2016-02-18 21:08 | 352.4167 | 75 | 26431.25 | 352.4167 | 349.4167 | 0.079922 | 26206.25 | 0.079241 | 0.00022678 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 780375 | Tripping on CB 1406 on E/F. Fault caused by small tree falling through all 3 conductors. Isolation required from the Recloser 1406. 20 meters of Squirrel conductor was used. 6 sleeves. 6 binders used. NDR: 22690 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-02-18 | c | 0.079241 | 0.00022678 | 2016 | 2016-02-18 | C | 75 | 0.079241 | 0.00022678
9993328 | 2016-02-18 15:57 | 2016-02-18 17:39 | 102.45 | 27 | 2742.4667 | 101.5728 | 98.5728 | 0.0082926 | 2661.4667 | 0.0080476 | 8.1642e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 595 | Please check if OMS 9993686, 9994058 is related. 2 HT Fuses Tripped at 595. Reloaded OK. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.0080476 | 8.1642e-05 | 2016 | 2016-02-18 | C | 27 | 0.0080476 | 8.1642e-05
9993643 | 2016-02-19 13:04 | 2016-02-19 17:45 | 281 | 44 | 12364 | 281 | 278 | 0.037386 | 12232 | 0.036987 | 0.00013305 | Referral | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Sw/Gear 450/2 | To replace Transformer 261 on 19/02/16. 1:48pm Wes advised taking generator away and replacing TX which will take 4-5 hours will send out Emergency outage. Transformer replaced, relivened OK | F3 | BELL BLOCK 7 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.036987 | 0.00013305 | 2016 | 2016-02-19 | C | 44 | 0.036987 | 0.00013305
9993759 | 2016-02-18 19:04 | 2016-02-18 19:22 | 18 | 69 | 1242 | 18 | 15 | 0.0037555 | 1035 | 0.0031296 | 0.00020864 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 219815 | Advised svs hub 4:37pm. Jumper burnt off at transformer fuses TD5-027. Isolations at ABS SD5-008 & SD5-009. Back feed from TMA 5 via ABS SD5-016. Jumper repaired all service restored. Materials 1 x fuse holder & 6A fuse, 1 x meter conductor, 1 x copper sl | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.0031296 | 0.00020864 | 2016 | 2016-02-18 | C | 69 | 0.0031296 | 0.00020864
9994779 | 2016-02-18 20:00 | 2016-02-18 21:18 | 78 | 1 | 78 | 78 | 75 | 0.00023585 | 75 | 0.00022678 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7719 | 999 - 1R - Check for safety. Lines down - unable to log via ICP. 027 438 5529 - Richard Advised svs hub 7:12. Faultman removed trees and repaired lines down, line was isolated at Fuses 7719. 40 meters - 16mm copper conductor used & 6 sleeves. NDR: to foll | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.00022678 | 3.024e-06 | 2016 | 2016-02-18 | C | 1 | 0.00022678 | 3.0238e-06
9995112 | 2016-02-18 19:51 | 2016-02-18 20:09 | 18.0167 | 179 | 3224.9833 | 18.0167 | 15.0167 | 0.0097516 | 2687.9833 | 0.0081278 | 0.00054125 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | ( AON 1 ) Recloser S6040 tripped E/F, L/O ( Matakana Island ) closed & held after 15 Min not patrolled high wind & rain at time of tripping | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.0081278 | 0.00054125 | 2016 | 2016-02-18 | C | 179 | 0.0081278 | 0.00054125
9995595 | 2016-02-18 20:06 | 2016-02-18 23:23 | 197.45 | 152 | 9534.3167 | 62.7258 | 59.7258 | 0.028829 | 9078.3167 | 0.027451 | 0.00045961 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G0235 | 51 Bowlers Road, Matamata - power pole on fire, thinks it only feeds his cowshed and house? advised control. ( BRN 5 ) CB 5 tripped A Ph O/C, E/F, L/O Report of pole on fire Bowlers Rd. Isolation at fuses FC1407 (spur - no back feed). CB5 closed with res | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.027451 | 0.00045961 | 2016 | 2016-02-18 | C | 152 | 0.027451 | 0.00045961
9996546 | 2016-02-18 19:29 | 2016-02-19 17:26 | 1317 | 3 | 3951 | 1317 | 1314 | 0.011947 | 3942 | 0.01192 | 9.0713e-06 | Referral | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Y26 | To replace Transformer Y26 Fri 19/2. Used 1 x 30 kVA 6.6 kV transformer, 2 x connectors and 5 mtrs of conductor | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-18 | c | 0.01192 | 9.071e-06 | 2016 | 2016-02-18 | C | 3 | 0.01192 | 9.0713e-06
9996675 | 2016-02-18 21:44 | 2016-02-19 02:32 | 288.1667 | 274 | 65411.7333 | 238.729 | 235.729 | 0.19779 | 64589.7333 | 0.1953 | 0.00082851 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 202085 | 10.26pm advised control about emergency in attached contact. ( AON1 ) CB1 tripped L/O (no flags) report of transformer blown TP1359. TP1359 H/V isolated & remainder of feeder returned to service. CB1 tripped again appears insulator x 2 at pole 202085 faul | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-02-18 | c | 0.1953 | 0.00082851 | 2016 | 2016-02-18 | C | 274 | 0.1953 | 0.00082851
10002054 | 2016-02-19 04:51 | 2016-02-19 11:27 | 395.9167 | 638 | 41450.1833 | 64.9689 | 61.9689 | 0.12534 | 39536.1833 | 0.11955 | 0.0019292 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R1058 | ( WGM1 ) CB1 tripped A Ph O/C, E/F, L/O feeder sectionalised. Blown lightning arrestor at pole R1508. isolated at IC251 and 2070. | F4 | WHIRITOA | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-02-19 | c | 0.11955 | 0.0019292 | 2016 | 2016-02-19 | C | 638 | 0.11955 | 0.0019292
10003629 | 2016-02-19 07:38 | 2016-02-19 11:05 | 207.7667 | 6 | 1246.6 | 207.7667 | 204.7667 | 0.0037694 | 1228.6 | 0.003715 | 1.8143e-05 |  | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 875 | 2 x amp fuse weather | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.003715 | 1.8143e-05 | 2016 | 2016-02-19 | C | 6 | 0.003715 | 1.8143e-05
10003781 | 2016-03-07 09:16 | 2016-03-07 14:05 | 289.0333 | 19 | 5491.6333 | 289.0333 | 286.0333 | 0.016605 | 5434.6333 | 0.016433 | 5.7451e-05 | NAPA ID:16727 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | U0355 | AP FOR TREE WORK. BETWEEN POLES U0355 TO U12605. Works location: Pumpkinhill Rd, Tairua. WO 10152354 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-03-07 | b | 0.0082165 | 2.8726e-05 | 2016 | 2016-03-07 | B | 19 | 0.016433 | 5.7451e-05
10003845 | 2016-02-19 08:18 | 2016-02-19 15:31 | 432.7833 | 534 | 141984.2167 | 265.888 | 262.888 | 0.42933 | 140382.2167 | 0.42448 | 0.0016147 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x684 | Cb 262 Tripped Flags O/C. NDR 30466. Trees on line caused HV to touch LV Isolated at ABS 098 & 499 no backfeed available. Power restored. LV to be tested at tx X684. Large contingent from depot & 3 inspectors as 53 icp off on tx inc local electricians. | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-02-19 | c | 0.42448 | 0.0016147 | 2016 | 2016-02-19 | C | 534 | 0.42448 | 0.0016147
10004789 | 2016-03-07 08:43 | 2016-03-07 13:30 | 287.4667 | 187 | 53756.2667 | 287.4667 | 284.4667 | 0.16255 | 53195.2667 | 0.16085 | 0.00056544 | NAPA ID:16796 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2703 | Replace cross arms and Fargo links in HV Line. Works location: Hahei Whitianga. WO 30007220 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-03-07 | b | 0.080425 | 0.00028272 | 2016 | 2016-03-07 | B | 187 | 0.16085 | 0.00056544
10006143 | 2016-02-19 12:18 | 2016-02-19 13:36 | 78 | 13 | 1014 | 78 | 75 | 0.0030661 | 975 | 0.0029482 | 3.9309e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5254 | Blown Jumper Fuses 5254. Opened and earthed at Fuses 5303 for repairs. Jumper repaired, relivened OK | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.0029482 | 3.9309e-05 | 2016 | 2016-02-19 | C | 13 | 0.0029482 | 3.9309e-05
10007389 | 2016-02-19 13:21 | 2016-02-19 14:12 | 51.1333 | 285 | 14573 | 51.1333 | 48.1333 | 0.044065 | 13718 | 0.04148 | 0.00086177 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V13628 | Broken crossarm Isolated at Links IP 79 temp repairs done and defected pole | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-02-19 | c | 0.04148 | 0.00086177 | 2016 | 2016-02-19 | C | 285 | 0.04148 | 0.00086177
10008871 | 2016-02-19 16:56 | 2016-02-19 17:46 | 50 | 1 | 50 | 50 | 47 | 0.00015119 | 47 | 0.00014212 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T847 | Damaged LV connections found at Transformer T847 - Transformer Isolated for repairs | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.00014212 | 3.024e-06 | 2016 | 2016-02-19 | C | 1 | 0.00014212 | 3.0238e-06
10009080 | 2016-02-19 16:18 | 2016-02-19 17:34 | 75.65 | 1 | 75.65 | 75.65 | 72.65 | 0.00022875 | 72.65 | 0.00021968 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | T7/245 | Fuse found Blown at Transformer T7/245 - cause bird strike. Used 2 x 2 amp fuses | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.00021968 | 3.024e-06 | 2016 | 2016-02-19 | C | 1 | 0.00021968 | 3.0238e-06
10009364 | 2016-02-19 17:00 | 2016-02-19 18:35 | 94.55 | 2 | 189.1 | 94.55 | 91.55 | 0.00057179 | 183.1 | 0.00055365 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE5-128 | 2x2amp HV fuses blown. replaced and transformer relivened. Unknown Cause | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-02-19 | c | 0.00055365 | 6.048e-06 | 2016 | 2016-02-19 | C | 2 | 0.00055365 | 6.0475e-06
10009506 | 2016-02-19 17:31 | 2016-02-19 19:51 | 140.3 | 11 | 1486.5833 | 135.1439 | 132.1439 | 0.0044951 | 1453.5833 | 0.0043953 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8158 | 1 x 30A HV Fuse Replaced at Fuses 8158. These fuses do not show up on e-map but are showing on OSI SCADA. Fuses 7167 opened to enable the job to be completed. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-02-19 | c | 0.0043953 | 3.3261e-05 | 2016 | 2016-02-19 | C | 11 | 0.0043953 | 3.3261e-05
10011075 | 2016-02-20 02:44 | 2016-02-20 07:35 | 291.4667 | 132 | 22717.7167 | 172.1039 | 169.1039 | 0.068693 | 22321.7167 | 0.067496 | 0.00039914 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P003292 | Line Down Found at Pole P03292 during sectionalising - Isolated at Fuses V77. Line Repaired - used 2 x sleeves and 2 mtrs conductor | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-02-20 | c | 0.067496 | 0.00039914 | 2016 | 2016-02-20 | C | 132 | 0.067496 | 0.00039914
10011355 | 2016-02-20 05:28 | 2016-02-20 07:11 | 103.3667 | 1 | 103.3667 | 103.3667 | 100.3667 | 0.00031256 | 100.3667 | 0.00030348 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6488 | 2 Fuse found blown at Fuses 6488 - Suspected bird Strike. Used 2 x 6 amp fuses | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-20 | c | 0.00030348 | 3.024e-06 | 2016 | 2016-02-20 | C | 1 | 0.00030348 | 3.0238e-06
10011373 | 2016-02-20 11:28 | 2016-02-20 15:45 | 257 | 6 | 1542 | 257 | 254 | 0.0046626 | 1524 | 0.0046082 | 1.8143e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736394 | Faultman could not find fault, requested open on Fuses 6029 so he could check them fuses ok but fault man replaced anyway, Still issues at property. Line patrolled and line down found at pole 736394 - isolated at fuses 6029 - line repaired - cause Cracked | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-02-20 | c | 0.0046082 | 1.8143e-05 | 2016 | 2016-02-20 | C | 6 | 0.0046082 | 1.8143e-05
10011753 | 2016-02-20 09:25 | 2016-02-20 10:05 | 40 | 7 | 280 | 40 | 37 | 0.00084665 | 259 | 0.00078315 | 2.1166e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3685 | Faulty transformer replaced | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-02-20 | c | 0.00078315 | 2.1166e-05 | 2016 | 2016-02-20 | C | 7 | 0.00078315 | 2.1166e-05
10012840 | 2016-02-20 15:14 | 2016-02-20 16:44 | 89.6333 | 2 | 114.85 | 57.425 | 54.425 | 0.00034728 | 108.85 | 0.00032914 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1177 | 2 fuses found blown at Fuses 1177 - Cause unknown. Used 2 x 6 amp fuses | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2016-02-20 | c | 0.00032914 | 6.048e-06 | 2016 | 2016-02-20 | C | 2 | 0.00032914 | 6.0475e-06
10013711 | 2016-02-20 19:51 | 2016-02-21 02:29 | 398 | 54 | 21492 | 398 | 395 | 0.064987 | 21330 | 0.064497 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 788777 | Poplar Tree fallen through lines at Pole 788777. Isolation at Fuses 2589. 1 x 11mtr pole. 6 2mtr Term' Arms. 300 mtrs Squirel conductor. 12 Squirrel Sleeves. 2 Rabbit Sleeves. NDR N300168 | F2 | TAIHAPE TOWN SOUTH | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-02-20 | c | 0.064497 | 0.00016328 | 2016 | 2016-02-20 | C | 54 | 0.064497 | 0.00016328
10015631 | 2016-02-21 15:32 | 2016-02-22 17:16 | 1544.0667 | 142 | 19701.35 | 138.7419 | 135.7419 | 0.059572 | 19275.35 | 0.058284 | 0.00042937 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | E13020 | Recloser 9779/2 tripped to L/O. Transformer pole down. transformer Structure replaced. 30kVA Transformer Replaced. 2 HV Arms replaced. 1r feeder fault 1532. 2r line patrol 1706. 2r repair 1732 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-21 | c | 0.058284 | 0.00042937 | 2016 | 2016-02-21 | C | 142 | 0.058284 | 0.00042937
10015858 | 2016-03-08 08:59 | 2016-03-08 15:19 | 380.3167 | 3 | 1114.65 | 371.55 | 368.55 | 0.0033704 | 1105.65 | 0.0033432 | 9.0713e-06 | NAPA ID:15849 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIROA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 200506 | 1/ LIVE LINE BREAK AT POLE 200506. 2/ AP TO RECON FEEDER REPLACE POLES, INSTALL REPLACEMENT 11KV CABLES UP NEW POLES. 3/ CONNECT NEW CFC RMU 13034 /1 -/3 INTO THE NETWORK. 4/ INSTALL NEW FUSED ABS AT SITE SD3-083 [ SAME NUMBER TO REMAIN ] 5/ CONNECT TX T | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2016-03-08 | b | 0.0016716 | 4.536e-06 | 2016 | 2016-03-08 | B | 3 | 0.0033432 | 9.0713e-06
10015889 | 2016-03-08 10:20 | 2016-03-08 15:43 | 323.3667 | 3 | 970.1 | 323.3667 | 320.3667 | 0.0029334 | 961.1 | 0.0029061 | 9.0713e-06 | NAPA ID:16873 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC380 | Change Cross Arms. Works location: Thames Coast Rd, Thames. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-08 | b | 0.0014531 | 4.536e-06 | 2016 | 2016-03-08 | B | 3 | 0.0029061 | 9.0713e-06
10015895 | 2016-03-09 09:30 | 2016-03-09 15:32 | 362 | 11 | 3982 | 362 | 359 | 0.012041 | 3949 | 0.011941 | 3.3261e-05 | NAPA ID:15919 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC823 | 11kV cross arms various locations. Works location: Puhunga South, Ngatea. WO 30002467 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-09 | b | 0.0059704 | 1.6631e-05 | 2016 | 2016-03-09 | B | 11 | 0.011941 | 3.3261e-05
10016468 | 2016-02-22 02:37 | 2016-02-22 03:07 | 30.6833 | 2998 | 86742.6333 | 28.9335 | 25.9335 | 0.26229 | 77748.6333 | 0.23509 | 0.0090652 |  | 33 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 366923 | Cable 33kV blown at Pole 366923 DNO 160214 | F1,F2,F3 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 2016-02-22 | c | 0.23509 | 0.0090652 | 2016 | 2016-02-22 | C | 2998 | 0.23509 | 0.0090652
10019878 | 2016-02-22 07:14 | 2016-02-22 09:51 | 157.35 | 4 | 629.4 | 157.35 | 154.35 | 0.0019032 | 617.4 | 0.0018669 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 141 | pls check if 10020264 is related - 2x 10amp fuse. Unknown cause. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.0018669 | 1.2095e-05 | 2016 | 2016-02-22 | C | 4 | 0.0018669 | 1.2095e-05
10019936 | 2016-02-22 07:42 | 2016-02-22 10:20 | 157.9833 | 25 | 3949.5833 | 157.9833 | 154.9833 | 0.011943 | 3874.5833 | 0.011716 | 7.5594e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2327 | pls check if OMS 10020447 is related. 2x 15amp fuse. Cause unknown. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-02-22 | c | 0.011716 | 7.5594e-05 | 2016 | 2016-02-22 | C | 25 | 0.011716 | 7.5594e-05
10020125 | 2016-03-09 09:30 | 2016-03-09 15:05 | 334.55 | 20 | 6691 | 334.55 | 331.55 | 0.020232 | 6631 | 0.020051 | 6.0475e-05 | NAPA ID:16521 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 827901 | Replace 3 x 11kV defective poles. 827901, 827902 & 827904. Works location: Ngahapi Rd, Masterton. WO 10153902 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.010025 | 3.0238e-05 | 2016 | 2016-03-09 | B | 20 | 0.020051 | 6.0475e-05
10020243 | 2016-03-09 09:46 | 2016-03-09 16:06 | 379.8167 | 39 | 14812.85 | 379.8167 | 376.8167 | 0.044791 | 14695.85 | 0.044437 | 0.00011793 | NAPA ID:15954 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/256 | To remove Temp ABS58 and Temp Fuses 69 and install 11kV poles. Works location; Waihoki Valley Rd. WO 10134517 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.022218 | 5.8963e-05 | 2016 | 2016-03-09 | B | 39 | 0.044437 | 0.00011793
10020452 | 2016-02-22 09:16 | 2016-02-22 15:58 | 402.3 | 5 | 2011.5 | 402.3 | 399.3 | 0.0060823 | 1996.5 | 0.0060369 | 1.5119e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2255 | transformer TC2255 Blown. To be replaced. Replaced and livened at 1558 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-02-22 | c | 0.0060369 | 1.5119e-05 | 2016 | 2016-02-22 | C | 5 | 0.0060369 | 1.5119e-05
10020471 | 2016-02-22 09:20 | 2016-02-22 10:41 | 81.0667 | 533 | 20092.45 | 37.6969 | 34.6969 | 0.060755 | 18493.45 | 0.05592 | 0.0016117 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 | CB 5 Trip. E/F. L/O. Feeder sectionalised and no fault found. Cause Unknown. Initial backfeed immediatly after tripping up to recloser 9779 by closing RS 9790. 1r feeder fault 0924. 2r line patrol 0949. 2r repair no fault found | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-02-22 | c | 0.05592 | 0.0016117 | 2016 | 2016-02-22 | C | 533 | 0.05592 | 0.0016117
10021041 | 2016-03-09 08:46 | 2016-03-09 14:16 | 330.0833 | 29 | 9572.4167 | 330.0833 | 327.0833 | 0.028945 | 9485.4167 | 0.028682 | 8.7689e-05 | NAPA ID:16834 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/476 | Change 11kV transformer pole and hardware. Reuse existing transformer T9/476. Works location: Mangaone Valley Rd. WO 30015364 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.014341 | 4.3845e-05 | 2016 | 2016-03-09 | B | 29 | 0.028682 | 8.7689e-05
10022625 | 2016-03-09 08:32 | 2016-03-09 15:19 | 406.9167 | 20 | 8138.3333 | 406.9167 | 403.9167 | 0.024608 | 8078.3333 | 0.024427 | 6.0475e-05 | NAPA ID:16135 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P45965 | Replacing various hardwood poles P45965 through to P48613 inclusive. Works location: Dews Rd, Pahiatua. WO 30012838 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.012213 | 3.0238e-05 | 2016 | 2016-03-09 | B | 20 | 0.024427 | 6.0475e-05
10022980 | 2016-02-22 10:46 | 2016-02-22 11:53 | 67.1 | 1227 | 51985.3667 | 42.3679 | 39.3679 | 0.15719 | 48304.3667 | 0.14606 | 0.0037102 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 14 | CB14 E/F B Phase. lINE Patrolled. No Fault Found. | F3 | RESIDENTIAL | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.14606 | 0.0037102 | 2016 | 2016-02-22 | C | 1227 | 0.14606 | 0.0037102
10026119 | 2016-02-22 10:40 | 2016-02-22 12:35 | 115 | 10 | 1150 | 115 | 112 | 0.0034773 | 1120 | 0.0033866 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2589 | Repair Centre Phase Damaged Conductor. Isolated beyond Fuses 2589. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.0033866 | 3.0238e-05 | 2016 | 2016-02-22 | C | 10 | 0.0033866 | 3.0238e-05
10026383 | 2016-02-25 09:55 | 2016-02-25 11:50 | 115 | 1 | 115 | 115 | 112 | 0.00034773 | 112 | 0.00033866 | 3.0238e-06 | NAPA ID:17129 TP_STRATFORD GXP > KAPONGA SUB > DUTHIE RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 4251T | Replace existing TX 4251T as is leaking oil. Works location; Palmer Rd. WO 30020859 | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-02-25 | b | 0.00016933 | 1.512e-06 | 2016 | 2016-02-25 | B | 1 | 0.00033866 | 3.0238e-06
10027037 | 2016-02-22 13:20 | 2016-02-22 15:13 | 113 | 1 | 113 | 113 | 110 | 0.00034168 | 110 | 0.00033261 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 21353 | Emergency 11kV Shut to rectify CAA radio interference as per details below cut from email. This is a significant safety issue for CAA, has been discussed with Nigel Timms, Please liaise with Nigel for which attending. Nigel has a complete copy of the emai | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.00033261 | 3.024e-06 | 2016 | 2016-02-22 | C | 1 | 0.00033261 | 3.0238e-06
10027126 | 2016-03-09 09:32 | 2016-03-09 14:49 | 316.2833 | 27 | 8539.65 | 316.2833 | 313.2833 | 0.025822 | 8458.65 | 0.025577 | 8.1642e-05 | NAPA ID:16605 TP_STRATFORD GXP > CARDIFF SUB > CARDIFF RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5728 | Replace Transformer 2681T structure pole 737686 and HV cross arm at pole 737657. Works location: Waingongoro Rd. WO 30011229 | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.012788 | 4.0821e-05 | 2016 | 2016-03-09 | B | 27 | 0.025577 | 8.1642e-05
10027429 | 2016-02-22 16:00 | 2016-02-22 17:25 | 85.3667 | 1 | 85.3667 | 85.3667 | 82.3667 | 0.00025813 | 82.3667 | 0.00024906 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | E27 - Joanne and Drew are working through this job and the cancelled job - leave at complete | 5.42pm spoke to glen in control he advised faultman attended and replaced 2x 10amp hv fuses cause bird strike. Glen is unsure why this job has unlinked. Glen advised ok to complete job 5.43pm,5.51pm,6pm,6.20pm called customer to confirm if power restored | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.00024906 | 3.024e-06 | 2016 | 2016-02-22 | C | 1 | 0.00024906 | 3.0238e-06
10027477 | 2016-02-22 15:37 | 2016-02-22 17:25 | 108.0333 | 1 | 108.0333 | 108.0333 | 105.0333 | 0.00032667 | 105.0333 | 0.0003176 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | E27 | 5.42pm spoke to glen in control he advised faultman attended and replaced 2x 10amp hv fuses cause bird strike. Glen is unsure why this job has unlinked. Glen advised ok to complete job. - called customer to confirm power restored customer advised their po | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.0003176 | 3.024e-06 | 2016 | 2016-02-22 | C | 1 | 0.0003176 | 3.0238e-06
10027492 | 2016-02-22 18:19 | 2016-02-22 19:44 | 84.7833 | 92 | 7762.8833 | 84.3792 | 81.3792 | 0.023473 | 7486.8833 | 0.022639 | 0.00027819 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/347 | Replace H/T Fuse at Transformer T1/347 Dave Thomson On Way. 11kV line isolated at CB 4 Sanson, ABS M4, ABS M30, Fuses M29 to replace broken fuse base at transformer T1/347. 1 broken but all 3 replaced. All supply restored. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.022639 | 0.00027819 | 2016 | 2016-02-22 | C | 92 | 0.022639 | 0.00027819
10028165 | 2016-02-22 22:08 | 2016-02-23 05:46 | 457.9667 | 31 | 9608.5667 | 309.9538 | 306.9538 | 0.029054 | 9515.5667 | 0.028773 | 9.3737e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 12115 | Fire Comms event # F2023254. Fire Comms advise line down on cnr Corbett and Connett Roads. Katere CB 7 tripped to L/O. O/C & E/F flag. car v pole at links 12115. Line isolated at sw/gear 12116/3 & ABS 247 to change pole. All HV restored following pole rep | F2 | KATERE 7 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 2016-02-22 | c | 0.028773 | 9.3737e-05 | 2016 | 2016-02-22 | C | 31 | 0.028773 | 9.3737e-05
10032609 | 2016-03-09 08:03 | 2016-03-09 10:20 | 137.25 | 1 | 137.25 | 137.25 | 134.25 | 0.00041501 | 134.25 | 0.00040594 | 3.0238e-06 | NAPA ID:16942 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | OS574 | Meter calibration. Works location: PNCC Treatment Plant. WO 30007499 | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.00020297 | 1.512e-06 | 2016 | 2016-03-09 | B | 1 | 0.00040594 | 3.0238e-06
10032648 | 2016-02-23 08:46 | 2016-02-23 11:25 | 159.4667 | 542 | 38750.2833 | 71.495 | 68.495 | 0.11717 | 37124.2833 | 0.11225 | 0.0016389 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 8 | Papamoa CB 8 Tripped on Earth Fault. Patrolled - no fault found. 1r feeder fault 0846 2r line patrol 0915 2r repair NO Fault found | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-02-23 | c | 0.11225 | 0.0016389 | 2016 | 2016-02-23 | C | 542 | 0.11225 | 0.0016389
10039466 | 2016-03-08 09:24 | 2016-03-08 14:55 | 331.3667 | 6 | 1988.2 | 331.3667 | 328.3667 | 0.0060118 | 1970.2 | 0.0059574 | 1.8143e-05 | NAPA ID:16706 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1319 | Replace transformer pole X1319. Works location: Watershed Rd, Hunterville. WO 10161752 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.0029787 | 9.071e-06 | 2016 | 2016-03-08 | B | 6 | 0.0059574 | 1.8143e-05
10039831 | 2016-02-23 12:25 | 2016-02-23 13:42 | 77 | 81 | 6237 | 77 | 74 | 0.018859 | 5994 | 0.018124 | 0.00024492 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE4-022 | Check for safety - 11kV cross arm cracked and hanging. Outage required beyond ABS SE4-022, no backfeeds available. Replaced 1 x crossarm. Relivened OK. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-02-23 | c | 0.018124 | 0.00024493 | 2016 | 2016-02-23 | C | 81 | 0.018124 | 0.00024492
10039834 | 2016-03-10 09:30 | 2016-03-10 14:20 | 290 | 8 | 2320 | 290 | 287 | 0.0070151 | 2296 | 0.0069426 | 2.419e-05 | NAPA ID:16839 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X98 | Replace rusty and earths at X98. Works location: Hwy 3, Waitotara. WO 30014691 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-10 | b | 0.0034713 | 1.2095e-05 | 2016 | 2016-03-10 | B | 8 | 0.0069426 | 2.419e-05
10040120 | 2016-03-08 08:34 | 2016-03-08 15:15 | 400.8667 | 30 | 12026 | 400.8667 | 397.8667 | 0.036364 | 11936 | 0.036092 | 9.0713e-05 | NAPA ID:16709 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P14123 | Cutting trees around the 11kV. Works location: Pohangina Valley. WO 10152357 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.018046 | 4.5356e-05 | 2016 | 2016-03-08 | B | 30 | 0.036092 | 9.0713e-05
10040333 | 2016-03-16 09:34 | 2016-03-16 15:08 | 334 | 6 | 2004 | 334 | 331 | 0.0060596 | 1986 | 0.0060052 | 1.8143e-05 | NAPA ID:16847 TP_MARTON GXP > PUKEPAPA SUB > LEEDSTOWN 22KV | 22 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 805035 | Replace 22kV two hardwood pole number 805035 and 805037. Works location: Saunders Rd, Marton. WO 30014695 | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.0030026 | 9.071e-06 | 2016 | 2016-03-16 | B | 6 | 0.0060052 | 1.8143e-05
10040902 | 2016-02-23 14:30 | 2016-02-23 15:32 | 62 | 26 | 1612 | 62 | 59 | 0.0048743 | 1534 | 0.0046384 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S11 | Replace 2 x 10A fuse | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-02-23 | c | 0.0046384 | 7.8618e-05 | 2016 | 2016-02-23 | C | 26 | 0.0046384 | 7.8618e-05
10043700 | 2016-03-12 09:22 | 2016-03-12 11:55 | 153 | 1 | 153 | 153 | 150 | 0.00046264 | 150 | 0.00045356 | 3.0238e-06 | NAPA ID:15798 TP_TE MATAI GXP > TE PUKE SUB > MOEHAU ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13027 | Connect new RMU 13027/1 to existing RMU 9971/3. Connect existing RMU SE5-150 to RMU 13027/3. Cable between 9971/3 and 9972/1 disconnected. TP2899 and TP2898 livened & commissioned. | F3 | MOEHAU ST | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-12 | b | 0.00022678 | 1.512e-06 | 2016 | 2016-03-12 | B | 1 | 0.00045356 | 3.0238e-06
10043724 | 2016-03-11 10:48 | 2016-03-11 13:58 | 190 | 15 | 2850 | 190 | 187 | 0.0086177 | 2805 | 0.0084816 | 4.5356e-05 | NAPA ID:16837 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/482 | Change 11kv transformer pole and hardware. Reuse existing transformer T9/482. Works location: Mangaone Valley Rd. WO 30015364 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-11 | b | 0.0042408 | 2.2678e-05 | 2016 | 2016-03-11 | B | 15 | 0.0084816 | 4.5356e-05
10044076 | 2016-03-01 12:30 | 2016-03-01 13:55 | 85 | 21 | 1785 | 85 | 82 | 0.0053974 | 1722 | 0.0052069 | 6.3499e-05 | NAPA ID:17061 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 2034N | Complete application is to replace switching 15203 due to reworks on anchor stay. Staged switching to accommodate single spur line, connect generator, Richmond Road crossing & SH3a road crossing & testing new cable and lines. Works location: Te Arel Rd, | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-01 | b | 0.0026035 | 3.1749e-05 | 2016 | 2016-03-01 | B | 21 | 0.0052069 | 6.3499e-05
10047881 | 2016-03-15 09:33 | 2016-03-15 11:32 | 119 | 12 | 1428 | 119 | 116 | 0.0043179 | 1392 | 0.0042091 | 3.6285e-05 | NAPA ID:17108 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 804547 | replace 11kV cross arm on pole 804547 due to poor condition. Works location: Mt. Curl Rd, Hunterville. WO 30000928 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-15 | b | 0.0021045 | 1.8143e-05 | 2016 | 2016-03-15 | B | 12 | 0.0042091 | 3.6285e-05
10047941 | 2016-02-24 07:56 | 2016-02-24 09:18 | 81.2167 | 5 | 406.0833 | 81.2167 | 78.2167 | 0.0012279 | 391.0833 | 0.0011825 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1362 | 2 x 6amp fuse unknown. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-02-24 | c | 0.0011825 | 1.5119e-05 | 2016 | 2016-02-24 | C | 5 | 0.0011825 | 1.5119e-05
10047964 | 2016-03-15 09:33 | 2016-03-15 15:15 | 342 | 1 | 342 | 342 | 339 | 0.0010341 | 339 | 0.0010251 | 3.0238e-06 | NAPA ID:17150 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1003 | Replacing two 11kV poles and install new 30/11/3 transformer to supply new comms hut. Works location: Mt. Curl Rd, Rata. WO 10162646. Note the outage commenced at 09:33 when this transformer was isolated in condjunction with Planned Works being undertake | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-15 | b | 0.00051253 | 1.512e-06 | 2016 | 2016-03-15 | B | 1 | 0.0010251 | 3.0238e-06
10048249 | 2016-03-14 09:12 | 2016-03-14 15:24 | 371.8667 | 113 | 42020.9333 | 371.8667 | 368.8667 | 0.12706 | 41681.9333 | 0.12604 | 0.00034168 | NAPA ID:16463 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 780170 | Tree trimming and felling naer 11kv poles 780170 (Waitotara Valley Rd) & 850996 (Makakaho Valley Rd), also replace 11kv pole 780529 (Ngamatapouri Rd). Works location: Waitotara Valley Rd. WO 30011324 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-14 | b | 0.063018 | 0.00017084 | 2016 | 2016-03-14 | B | 113 | 0.12604 | 0.00034168
10048260 | 2016-03-11 09:15 | 2016-03-11 14:00 | 285 | 65 | 18525 | 285 | 282 | 0.056015 | 18330 | 0.055426 | 0.00019654 | NAPA ID:16250 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace pole 745628 for a new 11m busk pole and install a new 30kva pole mounted TX and up grade the earthing system. | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-11 | b | 0.027713 | 9.8272e-05 | 2016 | 2016-03-11 | B | 65 | 0.055426 | 0.00019654
10048306 | 2016-02-24 10:25 | 2016-02-24 10:30 | 5 | 4 | 20 | 5 | 2 | 6.0475e-05 | 8 | 2.419e-05 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X997 | Fuses X997 opened to fasten strap on transformer bushing. Later in the day transformer had to be replaced. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-02-24 | c | 2.419e-05 | 1.2095e-05 | 2016 | 2016-02-24 | C | 4 | 2.419e-05 | 1.2095e-05
10048412 | 2016-03-09 10:00 | 2016-03-09 13:30 | 210 | 13 | 2730 | 210 | 207 | 0.0082549 | 2691 | 0.0081369 | 3.9309e-05 | NAPA ID:16568 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1628 | To replace/upgrade the transformer & replace 400V arms & Hardware. Works location: Pukekauri Rd, Waihi. WO 30019506 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-03-09 | b | 0.0040685 | 1.9654e-05 | 2016 | 2016-03-09 | B | 13 | 0.0081369 | 3.9309e-05
10048630 | 2016-03-03 10:11 | 2016-03-03 15:05 | 294 | 12 | 3528 | 294 | 291 | 0.010668 | 3492 | 0.010559 | 3.6285e-05 | NAPA ID:16108 TP_MARTON GXP > RATA SUB > PUTORINO | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X1218 | Replace defect fused ABS 4172, also replace transformer pole X1218 (NDR41986, OMS 9954988). Works location: Hwy 1, Rata. WO 30013709 | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-03 | b | 0.0052795 | 1.8143e-05 | 2016 | 2016-03-03 | B | 12 | 0.010559 | 3.6285e-05
10048881 | 2016-03-09 18:46 | 2016-03-09 20:38 | 112.25 | 1 | 112.25 | 112.25 | 109.25 | 0.00033942 | 109.25 | 0.00033035 | 3.0238e-06 | NAPA ID:17265 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 6250 | 11kV Metering calibration for major customer. Communication for outage was done by Russel Mann fron Accucal. Works location: Hakirua St. WO 30007495 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-03-09 | b | 0.00016517 | 1.512e-06 | 2016 | 2016-03-09 | B | 1 | 0.00033035 | 3.0238e-06
10049315 | 2016-02-24 12:24 | 2016-02-24 14:36 | 131.55 | 2 | 263.1 | 131.55 | 128.55 | 0.00079555 | 257.1 | 0.00077741 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 12012 - Paperwork has been requested | Call from retailer to advise job as emergency. Svs hub advised 12:27 - 2 x 2A HV Fuses replaced. NDR N100108 Digger touched Lines. No Damage or anyone hurt. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-02-24 | c | 0.00077741 | 6.048e-06 | 2016 | 2016-02-24 | C | 2 | 0.00077741 | 6.0475e-06
10049334 | 2016-02-24 13:48 | 2016-02-24 14:36 | 48.35 | 18 | 870.3 | 48.35 | 45.35 | 0.0026316 | 816.3 | 0.0024683 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 835017 | F2024314 ETA requested. Svs hub advised 12:32 ETA 10mins, F/Comms advised. **Will require Safety Manager - Environment ** Faultman found a broken jumper on pole 835017 to Fuses 7862, line was isolated at ABS's S19 , S103 & S736 to repair the jumper. 1 x | F5 | ROROKOKO | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-02-24 | c | 0.0024683 | 5.4428e-05 | 2016 | 2016-02-24 | C | 18 | 0.0024683 | 5.4428e-05
10052195 | 2016-03-10 08:36 | 2016-03-10 13:29 | 293 | 1 | 293 | 293 | 290 | 0.00088596 | 290 | 0.00087689 | 3.0238e-06 | NAPA ID:17073 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE3-133 | Replace tranformer structure TE3-133. Works location: Belk Rd South. WO 30001481 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-10 | b | 0.00043844 | 1.512e-06 | 2016 | 2016-03-10 | B | 1 | 0.00087689 | 3.0238e-06
10052315 | 2016-03-16 08:30 | 2016-03-16 15:45 | 435 | 127 | 55245 | 435 | 432 | 0.16705 | 54864 | 0.1659 | 0.00038402 | NAPA ID:16024 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 829301 | 11kv pole and hardware replacements. Works location: Te Whiti Rd, Masterton. WO 30017189. NOTE: 17:06 Matthew Patrick (027 345 6568) at 269 Te Whiti Road, Masterton called the emergency line to advised all his cow shed and pumps were running backwards | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.082948 | 0.00019201 | 2016 | 2016-03-16 | B | 127 | 0.1659 | 0.00038402
10052320 | 2016-03-12 13:00 | 2016-03-12 13:55 | 55 | 31 | 1705 | 55 | 52 | 0.0051555 | 1612 | 0.0048743 | 9.3737e-05 | NAPA ID:16534 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E0301 | To replace 11kV cross arm & hardware. Works location: Bayley Rd, Tirau. WO 30019331 | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-12 | b | 0.0024372 | 4.6868e-05 | 2016 | 2016-03-12 | B | 31 | 0.0048743 | 9.3737e-05
10052339 | 2016-03-15 13:10 | 2016-03-15 13:37 | 27 | 5 | 135 | 27 | 24 | 0.00040821 | 120 | 0.00036285 | 1.5119e-05 | NAPA ID:16524 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4461 | To install a 400V Fuse disconnector to TC4461. Works location: Landsdown Rd, Walton. WO 10147849 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-15 | b | 0.00018143 | 7.559e-06 | 2016 | 2016-03-15 | B | 5 | 0.00036285 | 1.5119e-05
10052350 | 2016-03-15 09:48 | 2016-03-15 14:57 | 309 | 3 | 927 | 309 | 306 | 0.002803 | 918 | 0.0027758 | 9.0713e-06 | NAPA ID:16850 TP_OPUNAKE GXP > TASMAN SUB > IHAIA RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA181 | We are replacing 9 Hardwood poles and 2 badly spalding poles. Works location: Arawhata Rd, Opunake. WO 30019159 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-15 | b | 0.0013879 | 4.536e-06 | 2016 | 2016-03-15 | B | 3 | 0.0027758 | 9.0713e-06
10052364 | 2016-03-16 09:15 | 2016-03-16 14:49 | 334.5 | 35 | 11707.5 | 334.5 | 331.5 | 0.035401 | 11602.5 | 0.035083 | 0.00010583 | NAPA ID:16855 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGATAINOKA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R30 | Change 11kV pole, and while the line is isolated, we will cut trees as required. Works location: Mangahao Pahiatua Rd. WO 30015364 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.017542 | 5.2916e-05 | 2016 | 2016-03-16 | B | 35 | 0.035083 | 0.00010583
10052372 | 2016-03-15 09:30 | 2016-03-15 14:27 | 297 | 15 | 4455 | 297 | 294 | 0.013471 | 4410 | 0.013335 | 4.5356e-05 | NAPA ID:16253 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 653 | Replace existing pole 745504 and Transformer 653 for a new 11m busck and new pole mounted 50 kVA transformer with a new earthing system. Works location: Mountain Rd. WO 10159770 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-15 | b | 0.0066674 | 2.2678e-05 | 2016 | 2016-03-15 | B | 15 | 0.013335 | 4.5356e-05
10052375 | 2016-03-15 09:15 | 2016-03-15 10:56 | 100.6333 | 18 | 1811.4 | 100.6333 | 97.6333 | 0.0054772 | 1757.4 | 0.005314 | 5.4428e-05 | NAPA ID:16561 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F1715 | To replace a double pin arm & hardware. Works location: Hwy 24 Tauranga Rd, Matamata. WO 30018756 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-03-15 | b | 0.002657 | 2.7214e-05 | 2016 | 2016-03-15 | B | 18 | 0.005314 | 5.4428e-05
10052378 | 2016-03-12 09:15 | 2016-03-12 14:37 | 322 | 1 | 322 | 322 | 319 | 0.00097365 | 319 | 0.00096458 | 3.0238e-06 | NAPA ID:16917 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K13261 | To replace a damaged pole. Works location: Tramline Rd, Patetonga. WO 30016728 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-12 | b | 0.00048229 | 1.512e-06 | 2016 | 2016-03-12 | B | 1 | 0.00096458 | 3.0238e-06
10052380 | 2016-03-11 09:15 | 2016-03-11 11:24 | 129 | 17 | 2193 | 129 | 126 | 0.0066311 | 2142 | 0.0064769 | 5.1404e-05 | NAPA ID:16540 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1246 | To isolate the cable at FP1246, Remove, Repair, Test & Replace. Works location: Banks Rd, Matamata. WO 30018796 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-03-11 | b | 0.0032384 | 2.5702e-05 | 2016 | 2016-03-11 | B | 17 | 0.0064769 | 5.1404e-05
10052383 | 2016-03-16 09:54 | 2016-03-16 14:45 | 291.5833 | 117 | 34115.25 | 291.5833 | 288.5833 | 0.10316 | 33764.25 | 0.1021 | 0.00035378 | NAPA ID:15958 TP_MANGAMAIRE GXP > PONGAROA SUB > COAST ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P04829 | To replace 11kV pole and install extra 11kV pole to get extra height. Works location: Coast Rd. WO 10162152 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.051048 | 0.00017689 | 2016 | 2016-03-16 | B | 117 | 0.1021 | 0.00035378
10052403 | 2016-03-10 09:15 | 2016-03-10 12:28 | 193 | 109 | 21037 | 193 | 190 | 0.063611 | 20710 | 0.062622 | 0.00032959 | NAPA ID:16869 TP_TAURANGA 33 GXP > MATUA SUB > BEACH RD MATUA | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 13060/2 | Matua Additional Feeder Stage 7. Change feed to transformers TC4-058 & TD4-079 from SC4-408 to 13060/2 | F3 | BEACH RD MATUA | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2016-03-10 | b | 0.031311 | 0.00016479 | 2016 | 2016-03-10 | B | 109 | 0.062622 | 0.00032959
10052433 | 2016-03-14 10:36 | 2016-03-14 15:30 | 294 | 62 | 18228 | 294 | 291 | 0.055117 | 18042 | 0.054555 | 0.00018747 | NAPA ID:16422 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | M1599 | Tree Cutting by Asplundh. Works location: Old Taupo Rd, Putaruru. WO 10152355 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-03-14 | b | 0.027277 | 9.3737e-05 | 2016 | 2016-03-14 | B | 62 | 0.054555 | 0.00018747
10052513 | 2016-03-16 09:45 | 2016-03-16 14:06 | 260.6 | 34 | 8860.4 | 260.6 | 257.6 | 0.026792 | 8758.4 | 0.026483 | 0.00010281 | NAPA ID:17044 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 756261 | Replace Pole 756261 [top broken]. Pole Damaged [NDR on The 13.2.16 MV v Transformer Structure }. Note: Access Difficult Digger to Cut Track into Pole Site Through Bush. Works location: South Rd, Oakura. WO 30020895 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.013242 | 5.1404e-05 | 2016 | 2016-03-16 | B | 34 | 0.026483 | 0.00010281
10052572 | 2016-03-12 08:45 | 2016-03-12 10:18 | 93 | 32 | 2976 | 93 | 90 | 0.0089987 | 2880 | 0.0087084 | 9.676e-05 | NAPA ID:16532 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D1134 | To Replace 11kV arms & Hardware. Works location: Roberts Rd Maungatutari, Tirau. WO 30018760 | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-03-12 | b | 0.0043542 | 4.838e-05 | 2016 | 2016-03-12 | B | 32 | 0.0087084 | 9.676e-05
10053805 | 2016-02-24 16:38 | 2016-02-24 17:51 | 72.7833 | 543 | 39521.35 | 72.7833 | 69.7833 | 0.1195 | 37892.35 | 0.11458 | 0.0016419 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TE3 007 | Recloser 9275 Tripped open on E/F. Line patrolled found 1 x 6A H/V O/H fuse blown at fuses SE3 034. Dead turkey found at transformer TE3 007, reload reliven all in service | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-02-24 | c | 0.11458 | 0.0016419 | 2016 | 2016-02-24 | C | 543 | 0.11458 | 0.0016419
10054801 | 2016-02-25 01:00 | 2016-02-27 18:23 | 3923.0833 | 631 | 743502.5333 | 1178.2924 | 1175.2924 | 2.2482 | 741609.5333 | 2.2424 | 0.001908 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3811 | CB 1 L/O on E/F & O/C. 11kV CB 1 tripped to lock out, protection flagging was Earth fault and over current. It is suspected we have an 11kV Cable fault 08:30 NOC requested generation to be installed to the remaining 199 ICP's still affected as the locatio | F1 | ARAPUNI ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-02-25 | c | 2.2424 | 0.001908 | 2016 | 2016-02-25 | C | 631 | 2.2424 | 0.001908
10055434 | 2016-02-25 01:00 | 2016-02-25 02:49 | 108.65 | 811 | 47248.1833 | 58.2592 | 55.2592 | 0.14287 | 44815.1833 | 0.13551 | 0.0024523 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 9 Trip, O/C. Feeder sectionalised and patrolled with no fault found. 1r feeder fault 0100. 2r line patrol 0145 2r r3pair nothing found | F3 | MOTUROA 9 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-02-25 | c | 0.13551 | 0.0024523 | 2016 | 2016-02-25 | C | 811 | 0.13551 | 0.0024523
10059564 | 2016-03-16 10:00 | 2016-03-16 11:11 | 70.85 | 24 | 1700.4 | 70.85 | 67.85 | 0.0051416 | 1628.4 | 0.0049239 | 7.257e-05 | NAPA ID:16964 TP_HAWERA GXP > MANAIA SUB > AUROA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 716790 | Replace Rotten Hv cross arms at pole 716790 Skeet Rd Auroa. Works location: Skeet Rd. WO 10161171 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-16 | b | 0.0024619 | 3.6285e-05 | 2016 | 2016-03-16 | B | 24 | 0.0049239 | 7.257e-05
10059859 | 2016-03-06 08:10 | 2016-03-06 18:26 | 616 | 4 | 1510 | 377.5 | 374.5 | 0.0045659 | 1498 | 0.0045296 | 1.2095e-05 | NAPA ID:16644 TP_KOPU GXP > KEREPEHI SUB > COUNTY WATER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | An A.P. at 08.00 to 08.45 to Isloate Feeder Cable CB4 and disconnect cable from FC5010 to IC1429. At 09.00 turn back on CB4 to feed Cool stores. Get AP to connect in new Safe Link unit. 15.30 all work completed CB4 Closed into Circuit Earth Cable reconnec | F1 | COUNTY WATER | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-06 | b | 0.0022648 | 6.048e-06 | 2016 | 2016-03-06 | B | 4 | 0.0045296 | 1.2095e-05
10060616 | 2016-03-11 08:36 | 2016-03-11 11:10 | 154 | 4 | 616 | 154 | 151 | 0.0018626 | 604 | 0.0018264 | 1.2095e-05 | NAPA ID:16800 TP_KOPU GXP > COROMANDEL SUB > KAPANGA ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP960 | Install LV Fusing for transformer. Works location: Coromandel. WO 30013141 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-11 | b | 0.00091318 | 6.048e-06 | 2016 | 2016-03-11 | B | 4 | 0.0018264 | 1.2095e-05
10060634 | 2016-03-11 12:30 | 2016-03-11 13:08 | 38 | 4 | 152 | 38 | 35 | 0.00045961 | 140 | 0.00042333 | 1.2095e-05 | NAPA ID:16804 TP_KOPU GXP > COROMANDEL SUB > KAPANGA ROAD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3367 | Install LV Fusing Deenergised. Works location: Coromandel. WO 30013141 | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-11 | b | 0.00021166 | 6.048e-06 | 2016 | 2016-03-11 | B | 4 | 0.00042333 | 1.2095e-05
10061598 | 2016-03-15 09:15 | 2016-03-15 10:26 | 71 | 5 | 355 | 71 | 68 | 0.0010734 | 340 | 0.0010281 | 1.5119e-05 | NAPA ID:15987 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4842 | To relocate the 11kV Fuse arm up 400mm (approx.). Works location: Campbell Rd, Walton. WO 10147849 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-15 | b | 0.00051404 | 7.559e-06 | 2016 | 2016-03-15 | B | 5 | 0.0010281 | 1.5119e-05
10061708 | 2016-03-04 12:30 | 2016-03-04 13:48 | 78 | 1 | 78 | 78 | 75 | 0.00023585 | 75 | 0.00022678 | 3.0238e-06 | NAPA ID:17348 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3115 | We are replacing the pole under NAPA 17063 on the 21/3/16 but PowerCo have asked if we could replace the transformer urgently before hand. Works location: Opua Rd. WO 30002892 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-04 | b | 0.00011339 | 1.512e-06 | 2016 | 2016-03-04 | B | 1 | 0.00022678 | 3.0238e-06
10061831 | 2016-03-15 11:09 | 2016-03-15 15:50 | 281 | 2 | 562 | 281 | 278 | 0.0016994 | 556 | 0.0016812 | 6.0475e-06 | NAPA ID:17124 TP_STRATFORD GXP > DOUGLAS SUB > TOKO | 6.6 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 740231 | LLP Install 6.6Kv line break at pole 740231. AP move ABS 4996 pole as only 600mm into ground. LLP close 6.6Kv LLB @ pole 740231. Works location: Toko Rd, Stratford. WO 10161945 | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-15 | b | 0.00084061 | 3.024e-06 | 2016 | 2016-03-15 | B | 2 | 0.0016812 | 6.0475e-06
10061958 | 2016-03-17 10:46 | 2016-03-17 12:05 | 78.7833 | 4 | 315.1333 | 78.7833 | 75.7833 | 0.00095289 | 303.1333 | 0.0009166 | 1.2095e-05 | NAPA ID:16970 TP_HAWERA GXP > MANAIA SUB > OTAKEHO | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 717924 | Replace broken, rusted stay wire. Works location: Rama Rd, Manaia. WO 30015122 | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-17 | b | 0.0004583 | 6.048e-06 | 2016 | 2016-03-17 | B | 4 | 0.0009166 | 1.2095e-05
10062069 | 2016-03-21 09:54 | 2016-03-21 12:04 | 130 | 27 | 3510 | 130 | 127 | 0.010613 | 3429 | 0.010368 | 8.1642e-05 | NAPA ID:16973 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 840173 | Replace rotten cross arm. Works location: Namu Rd, Opunake. WO 30015376 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-21 | b | 0.0051842 | 4.0821e-05 | 2016 | 2016-03-21 | B | 27 | 0.010368 | 8.1642e-05
10062605 | 2016-03-18 09:57 | 2016-03-18 14:55 | 298.5167 | 4 | 1194.0667 | 298.5167 | 295.5167 | 0.0036106 | 1182.0667 | 0.0035743 | 1.2095e-05 | NAPA ID:17130 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5241 | Replacing transformer structure 3082T. Works location: Waiau Rd. WO 30015828 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-03-18 | b | 0.0017871 | 6.048e-06 | 2016 | 2016-03-18 | B | 4 | 0.0035743 | 1.2095e-05
10064141 | 2016-02-25 16:15 | 2016-02-26 02:36 | 621.4667 | 332 | 87247.6833 | 262.7942 | 259.7942 | 0.26382 | 86251.6833 | 0.2608 | 0.0010039 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | LI284 | Cnr high st glouster st. 4.38pm advised control about lines down outside 222 Egmont st Patea which is the same area as this job. Faultman isolated lines at ABS's LI283, LI284, LI294, to replace 2 poles & lv line due to a truck vs car accident. 2 X poles & | F4 | PATEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-02-25 | c | 0.2608 | 0.0010039 | 2016 | 2016-02-25 | C | 332 | 0.2608 | 0.0010039
10065220 | 2016-02-25 20:58 | 2016-02-26 00:09 | 191.2833 | 165 | 20552.85 | 124.5627 | 121.5627 | 0.062147 | 20057.85 | 0.06065 | 0.00049892 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | RC4 | Recloser RC04 L/O on E/F. Sectionalised and found possum on pole 013283. Removed & relivened. 1r Feeder fault 2057. 2r line patrol 2205. 2r repair Removed by line stick. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-25 | c | 0.06065 | 0.00049892 | 2016 | 2016-02-25 | C | 165 | 0.06065 | 0.00049892
10066083 | 2016-02-26 00:17 | 2016-02-26 14:17 | 839.8167 | 423 | 4979.7333 | 11.7724 | 8.7724 | 0.015058 | 3710.7333 | 0.01122 | 0.0012791 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 2742 tripped on E/F flags line was isolated at ABS 511, line will be patrolled in morning as line goes cross country and faultman can not see the line, in is also fogging in the area.Lines patrolled, sectionalised and restored to service. No fault. 2r | F1,F2,F3 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 2016-02-26 | c | 0.01122 | 0.0012791 | 2016 | 2016-02-26 | C | 423 | 0.01122 | 0.0012791
10066672 | 2016-02-26 03:02 | 2016-02-26 11:36 | 513.7833 | 757 | 65637.4667 | 86.7074 | 83.7074 | 0.19847 | 63366.4667 | 0.19161 | 0.002289 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 204032 | Car vs pole 204032, isolated at SB2-010 & IP414. Back fed from ABS SA2-052. Preliminary back feed from Sectionalizer 9223/2 up to 9606/2 then 13021/3. Pole replaced crossarms reused as they are new. NDR 53651 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2016-02-26 | c | 0.19161 | 0.002289 | 2016 | 2016-02-26 | C | 757 | 0.19161 | 0.002289
10069229 | 2016-03-21 09:19 | 2016-03-21 13:42 | 262.7667 | 124 | 32582.3 | 262.7605 | 259.7605 | 0.098521 | 32210.3 | 0.097396 | 0.00037495 | NAPA ID:16470 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P40994 | Remove old cable from 10172/1 cut and cap each end. connect new 11kV U/G cable from pole P40994 to 10172/1 and liven. Works location: Kentucky Way. WO 30017928 | F3 | PASCAL ST 6 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 2016-03-21 | b | 0.048698 | 0.00018747 | 2016 | 2016-03-21 | B | 124 | 0.097396 | 0.00037495
10069892 | 2016-03-22 09:42 | 2016-03-22 13:31 | 229 | 64 | 14656 | 229 | 226 | 0.044316 | 14464 | 0.043736 | 0.00019352 | NAPA ID:16473 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/255 | remove old cable from 10172/2 cut and cap each end. connect new 11kv U/G cable from 10172/2 to T6/255 and liven. Works location: Kentucky Way. WO 30017928 | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-03-22 | b | 0.021868 | 9.676e-05 | 2016 | 2016-03-22 | B | 64 | 0.043736 | 0.00019352
10070190 | 2016-03-19 09:58 | 2016-03-19 12:53 | 175 | 17 | 2975 | 175 | 172 | 0.0089957 | 2924 | 0.0088415 | 5.1404e-05 | NAPA ID:15959 TP_MANGAMAIRE GXP > ALFREDTON SUB > IHURAUA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS I7 | To change 11kv pins and insulators and install11kv stay to straighten pole. Works location: Bartons Line. WO 30000998 | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-19 | b | 0.0044207 | 2.5702e-05 | 2016 | 2016-03-19 | B | 17 | 0.0088415 | 5.1404e-05
10070264 | 2016-02-26 12:01 | 2016-02-26 14:01 | 119.9333 | 61 | 7315.9333 | 119.9333 | 116.9333 | 0.022122 | 7132.9333 | 0.021568 | 0.00018445 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 735473 | Isolate Cable between CB T41 & Pole 735473 outside sub. Backfeed whole feeder via ABS 6069. Will need it order a cable jointing kit before final repairs can be made. DNO 160216. 1r feeder fault 1201. 2r line patrol 1532 2r repair not repaired sent to dno | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-02-26 | c | 0.021568 | 0.00018445 | 2016 | 2016-02-26 | C | 61 | 0.021568 | 0.00018445
10070634 | 2016-02-26 13:49 | 2016-02-26 15:40 | 111 | 39 | 4329 | 111 | 108 | 0.01309 | 4212 | 0.012736 | 0.00011793 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782617 | Advised at HUB. Advised Control. Plwase check if 10070672 is related (15 Campbell Road). NDR # 41989. Pole 782617. Repaired HV line, used 45 m of conductor and 6 connectors and 3 x 10 amp fuse and 3 HV pin insulators. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-02-26 | c | 0.012736 | 0.00011793 | 2016 | 2016-02-26 | C | 39 | 0.012736 | 0.00011793
10072824 | 2016-03-23 10:05 | 2016-03-23 13:00 | 175 | 2 | 350 | 175 | 172 | 0.0010583 | 344 | 0.0010402 | 6.0475e-06 | NAPA ID:16252 TP_WAVERLEY GXP > TP_WAVERLEY > WAVERLEY | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 4649W | Replace transformer 4649W for new tx. Works location: Waipip Waverly. WO 30000411 | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-23 | b | 0.00052009 | 3.024e-06 | 2016 | 2016-03-23 | B | 2 | 0.0010402 | 6.0475e-06
10072943 | 2016-03-22 09:00 | 2016-03-22 11:19 | 139.45 | 42 | 5856.9 | 139.45 | 136.45 | 0.01771 | 5730.9 | 0.017329 | 0.000127 | NAPA ID:16784 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C1441 | Replace cross arms at pole C1441,1442 remove live line clamps from TP128. Works location: Hwy 26, Te Aroha. WO 30002440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-03-22 | b | 0.0086644 | 6.3499e-05 | 2016 | 2016-03-22 | B | 42 | 0.017329 | 0.000127
10072954 | 2016-03-24 08:30 | 2016-03-24 15:52 | 442 | 64 | 28288 | 442 | 439 | 0.085536 | 28096 | 0.084956 | 0.00019352 | NAPA ID:16027 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 74 | 11kV pole and hardware replacements. Works location: Mania Rd, Masterton. WO 30017189 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-24 | b | 0.042478 | 9.676e-05 | 2016 | 2016-03-24 | B | 64 | 0.084956 | 0.00019352
10073055 | 2016-03-14 09:02 | 2016-03-14 16:06 | 424 | 136 | 57556 | 423.2059 | 420.2059 | 0.17404 | 57148 | 0.1728 | 0.00041123 | NAPA ID:15858 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R12759 | To install 11kV break by removing 1 span of 11kV conductor between pole # R12759 and R0586 and replace cross arms at pole # R12759 L/Line. Under access permit the remaining arms and hardware will be replaced at poles R0586, 587 and 590. Works location: Is | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-14 | b | 0.086401 | 0.00020562 | 2016 | 2016-03-14 | B | 136 | 0.1728 | 0.00041123
10073132 | 2016-03-22 12:30 | 2016-03-22 13:48 | 78 | 112 | 8736 | 78 | 75 | 0.026416 | 8400 | 0.0254 | 0.00033866 | NAPA ID:16785 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole C1924 | Replace X arms at pole C1924. Works location: Wyatt St, Te Aroha. WO 300024440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-03-22 | b | 0.0127 | 0.00016933 | 2016 | 2016-03-22 | B | 112 | 0.0254 | 0.00033866
10073137 | 2016-03-19 13:15 | 2016-03-19 14:30 | 75 | 7 | 525 | 75 | 72 | 0.0015875 | 504 | 0.001524 | 2.1166e-05 | NAPA ID:16539 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC282 | To replace transformer TC2282. Works location: Taihoa South Rd. WO 30018799 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-03-19 | b | 0.00076199 | 1.0583e-05 | 2016 | 2016-03-19 | B | 7 | 0.001524 | 2.1166e-05
10073143 | 2016-03-19 09:03 | 2016-03-19 11:21 | 138.6 | 51 | 6979 | 136.8431 | 133.8431 | 0.021103 | 6826 | 0.02064 | 0.00015421 | NAPA ID:16537 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F1873 | To replace termination arms on Pole F1873. Works location: Hwy 29, Matamata. WO 30018755 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-03-19 | b | 0.01032 | 7.7106e-05 | 2016 | 2016-03-19 | B | 51 | 0.02064 | 0.00015421
10073194 | 2016-02-26 17:01 | 2016-02-26 17:29 | 28 | 7 | 196 | 28 | 25 | 0.00059266 | 175 | 0.00052916 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD5-122 | Jumper out at fuses TD5-122. Isolation at fuses SD5-056. No Back feeds available. Jumper repaired. | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2016-02-26 | c | 0.00052916 | 2.1166e-05 | 2016 | 2016-02-26 | C | 7 | 0.00052916 | 2.1166e-05
10073346 | 2016-02-26 15:29 | 2016-02-26 16:10 | 40.95 | 1 | 40.95 | 40.95 | 37.95 | 0.00012382 | 37.95 | 0.00011475 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | na | 3.30pm - advise smc 3.33pm Shannon advised eta 20min - called and advised Fire service *** complete safety manager *** 4.08pm Grant called to advise that the area is all safe, fire service where onsite and area is safe. FM has advised that there are m | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-02-26 | c | 0.00011475 | 3.024e-06 | 2016 | 2016-02-26 | C | 1 | 0.00011475 | 3.0238e-06
10074739 | 2016-02-26 18:50 | 2016-02-27 00:23 | 332.6167 | 851 | 40255.6833 | 47.304 | 44.304 | 0.12172 | 37702.6833 | 0.114 | 0.0025732 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 364633 | Car vs pole. Event F2026232.ETA required. 6.58pm - advise SMC. CB 2 opened by control room as report of car vs pole and line on the ground, line was isolated at ABS's, 443 & 6505 to replace pole 364633. 7.06pm advise Paulette at Fire Comms of 10-15 minu | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-02-26 | c | 0.114 | 0.0025732 | 2016 | 2016-02-26 | C | 851 | 0.114 | 0.0025732
10077092 | 2016-02-27 08:35 | 2016-02-27 09:10 | 35 | 4 | 140 | 35 | 32 | 0.00042333 | 128 | 0.00038704 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1608 | LV floater at T1608, rebound. Replaced jumper from LV conductor to Transformer/ Used 1 x IPC connector and 16mm conductor, deterioration, OH LV. Nothing else repaired or replaced. Adjacent assets up to Powerco standards. Fault man has requested a 2R. To b | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-02-27 | c | 0.00038704 | 1.2095e-05 | 2016 | 2016-02-27 | C | 4 | 0.00038704 | 1.2095e-05
10077717 | 2016-02-27 20:30 | 2016-02-28 08:13 | 703 | 1 | 703 | 703 | 700 | 0.0021257 | 700 | 0.0021166 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-27 | c | 0.0021166 | 3.024e-06 | 2016 | 2016-02-27 | C | 1 | 0.0021166 | 3.0238e-06
10077767 | 2016-02-27 21:25 | 2016-02-29 00:30 | 1625.0833 | 273 | 11600.9833 | 42.4944 | 39.4944 | 0.035079 | 10781.9833 | 0.032602 | 0.00082549 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | W13933 | ( TAI5 ) recloser 9170 tripped E/F, L/O. ( heavy rain at time of tripping ) Recloser RC 20 opened & back feed closed via Sectionaliser 9721 ( WHT4 ). Feeder sectionalised . Found tree in line at pole. W13933. Isolation at ABS 323 ( spur no back feed ) jum | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-02-27 | c | 0.032602 | 0.00082549 | 2016 | 2016-02-27 | C | 273 | 0.032602 | 0.00082549
10078766 | 2016-02-27 20:30 | 2016-02-28 08:13 | 703 | 4 | 2812 | 703 | 700 | 0.0085028 | 2800 | 0.0084665 | 1.2095e-05 | Referral | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 777219 | Too Dark to see in Pine Trees will go back in Morning. Isolated at Fuses 279 Branch found on lines at Pole 777219, cleared using hot sticks | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-27 | c | 0.0084665 | 1.2095e-05 | 2016 | 2016-02-27 | C | 4 | 0.0084665 | 1.2095e-05
10078792 | 2016-02-27 23:17 | 2016-02-28 05:00 | 343 | 8 | 2744 | 343 | 340 | 0.0082972 | 2720 | 0.0082246 | 2.419e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD44 187 | B Sperling own isolations & AP to replace faulty transformer TD4 187. Transformer replaced all service restored Materials 1 x 2Ph transformer, 2 x transformer support arms, 4 x 100A L/V fuse bases, | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-02-27 | c | 0.0082246 | 2.419e-05 | 2016 | 2016-02-27 | C | 8 | 0.0082246 | 2.419e-05
10079489 | 2016-02-28 08:29 | 2016-02-28 10:18 | 108.5833 | 327 | 25285.8167 | 77.3267 | 74.3267 | 0.076458 | 24304.8167 | 0.073492 | 0.00098877 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | O12770 | at 08:29, Kerepehi Sub, CB 3 Hauraki Rd Feeder, Recloser 9161 Tripped, PROT Trip, L/O. Faultmen dispatched and investigation began. Began sectionalising. Backfeed supplied from KPE 6 - Sectionaliser 9724 Closed, ABS IC423 Opened. Customer advised of Magpi | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-02-28 | c | 0.073492 | 0.00098877 | 2016 | 2016-02-28 | C | 327 | 0.073492 | 0.00098877
10080836 | 2016-02-28 09:09 | 2016-02-28 10:46 | 97 | 115 | 6471.6833 | 56.2755 | 53.2755 | 0.019569 | 6126.6833 | 0.018526 | 0.00034773 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1022 | RS 1022 Tripped B,C Ph O/C E/F - No Fault found, possible bird strike as Lake in area. 1r feeder fault 0908 2r line patrol 0930. No repair | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-02-28 | c | 0.018526 | 0.00034773 | 2016 | 2016-02-28 | C | 115 | 0.018526 | 0.00034773
10081831 | 2016-02-28 14:33 | 2016-02-28 16:11 | 98.2167 | 23 | 2258.9833 | 98.2167 | 95.2167 | 0.0068306 | 2189.9833 | 0.006622 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/188 | 2 x Damaged crossarms found at Transformer T5/188 - Isoaled at ABS's P20, P13, & K61 with backfeeds via ABS's P6 & K60. Faultman replaced 2 x DDO units complete and 2 x 3 amp fuses - whole structure to be defected by faultman | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-02-28 | c | 0.006622 | 6.9546e-05 | 2016 | 2016-02-28 | C | 23 | 0.006622 | 6.9546e-05
10082029 | 2016-03-16 09:57 | 2016-03-16 12:18 | 141 | 57 | 8037 | 141 | 138 | 0.024302 | 7866 | 0.023785 | 0.00017235 | NAPA ID:17223 TP_KAITIMAKO GXP > WELCOME BAY SUB > OHAUITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212722 | Replace 11kV pole No.212722. Works location: Ohauiti Rd. WO 30012260 | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-03-16 | b | 0.011892 | 8.6177e-05 | 2016 | 2016-03-16 | B | 57 | 0.023785 | 0.00017235
10082321 | 2016-02-29 05:28 | 2016-02-29 07:08 | 99.7333 | 12 | 1196.8 | 99.7333 | 96.7333 | 0.0036188 | 1160.8 | 0.00351 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA189 | 3 x 10A Fuses Replaced | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.00351 | 3.6285e-05 | 2016 | 2016-02-29 | C | 12 | 0.00351 | 3.6285e-05
10082337 | 2016-02-29 05:39 | 2016-02-29 10:50 | 311 | 196 | 15483.0833 | 78.9953 | 75.9953 | 0.046817 | 14895.0833 | 0.045039 | 0.00059266 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P47264 | RS Q61 Trip, O/C A & C Phase. Sectionalised & Patrolled. Temp Line Break created in last section of line left off to aid with location of hard to find fault. Blown glass strain insulator found at Pole P47264. Replaced 1x Strain with new polymer, 1x Deaden | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.045039 | 0.00059266 | 2016 | 2016-02-29 | C | 196 | 0.045039 | 0.00059266
10083293 | 2016-02-29 07:20 | 2016-02-29 09:55 | 154.8 | 240 | 17369.6 | 72.3733 | 69.3733 | 0.052522 | 16649.6 | 0.050344 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 6 A/R, L/O, E/F, O/C B Phase. Sectionalised & Patrolled. No fault found. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.050344 | 0.0007257 | 2016 | 2016-02-29 | C | 240 | 0.050344 | 0.0007257
10084440 | 2016-03-21 10:01 | 2016-03-21 12:43 | 162 | 62 | 10044 | 162 | 159 | 0.030371 | 9858 | 0.029808 | 0.00018747 | NAPA ID:17063 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA720 | To change existing transformer pole to new 11m pole plus upgrade transformer from a 10kVA to a new 30kVA as there has been a request from Powerco to change this transformer as soon possible. We also have another crew working down the road at another sight | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-21 | b | 0.014904 | 9.3737e-05 | 2016 | 2016-03-21 | B | 62 | 0.029808 | 0.00018747
10084962 | 2016-03-22 10:40 | 2016-03-22 13:26 | 165.75 | 435 | 72101.25 | 165.75 | 162.75 | 0.21802 | 70796.25 | 0.21407 | 0.0013153 | NAPA ID:16815 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 202214 | Levers Rd Conductor Upgrade Stage 1 Shut 0. Install temporary ABS Temp28 for use during subsequent outages. Works location: Levers Rd, Tauranga. WO 30015220 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2016-03-22 | b | 0.10704 | 0.00065767 | 2016 | 2016-03-22 | B | 435 | 0.21407 | 0.0013153
10085053 | 2016-03-08 09:17 | 2016-03-08 14:27 | 309.55 | 23 | 7119.65 | 309.55 | 306.55 | 0.021528 | 7050.65 | 0.021319 | 6.9546e-05 | NAPA ID:16191 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | To replace 11kV poles and hardware between ABS 2588 and TEMP05 inpreparation for conductor upgrade. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-08 | b | 0.01066 | 3.4773e-05 | 2016 | 2016-03-08 | B | 23 | 0.021319 | 6.9546e-05
10085331 | 2016-02-29 09:26 | 2016-02-29 12:03 | 156.6167 | 562 | 31142.1167 | 55.413 | 52.413 | 0.094166 | 29456.1167 | 0.089068 | 0.0016994 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | I2119 | CB3 tripped on E/F and O/C. Feeder sectionalised Fault found to be a cracked insulator at Pole I2119. Insulator replaced. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-02-29 | c | 0.089068 | 0.0016994 | 2016 | 2016-02-29 | C | 562 | 0.089068 | 0.0016994
10086064 | 2016-03-10 09:00 | 2016-03-10 15:32 | 392 | 23 | 9016 | 392 | 389 | 0.027262 | 8947 | 0.027054 | 6.9546e-05 | NAPA ID:16193 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2588 | To replace existing 11kV conductor between ABS 2588 and TEMP05. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-10 | b | 0.013527 | 3.4773e-05 | 2016 | 2016-03-10 | B | 23 | 0.027054 | 6.9546e-05
10086124 | 2016-03-14 08:45 | 2016-03-14 14:52 | 367 | 23 | 8441 | 367 | 364 | 0.025524 | 8372 | 0.025315 | 6.9546e-05 | NAPA ID:16199 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 296568 | To replace poles and hardware between TEMP05 and TEMP14 in preparation for 11kV conductor upgrade. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-14 | b | 0.012657 | 3.4773e-05 | 2016 | 2016-03-14 | B | 23 | 0.025315 | 6.9546e-05
10086204 | 2016-03-16 09:15 | 2016-03-16 15:08 | 353 | 23 | 8119 | 353 | 350 | 0.02455 | 8050 | 0.024341 | 6.9546e-05 | NAPA ID:16200 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 393568 | To replace 11kV conductors between TEMP05 and TEMP14. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-16 | b | 0.012171 | 3.4773e-05 | 2016 | 2016-03-16 | B | 23 | 0.024341 | 6.9546e-05
10086267 | 2016-02-29 10:49 | 2016-03-08 16:10 | 11840.1333 | 12 | 13065.5333 | 1088.7944 | 1085.7944 | 0.039507 | 13029.5333 | 0.039398 | 3.6285e-05 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 184 Hikuai School Road t4885 | Still power off to Tx T4485 - either a cable fault to the Tx or a faulty Tx. Will need to leave disconnected overnight and is checking with customer to see whether customer is happy with this and I will confirm with retailer. Called Mercury 2:56pm to get | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-02-29 | c | 0.039398 | 3.6285e-05 | 2016 | 2016-02-29 | C | 12 | 0.039398 | 3.6285e-05
10086699 | 2016-02-29 10:39 | 2016-02-29 16:03 | 324.1833 | 39 | 8618.65 | 220.991 | 217.991 | 0.026061 | 8501.65 | 0.025707 | 0.00011793 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P07471 | Tree branch broke off and fell through lines, clashing lines together. Needs to be assessed as tree is crossing driveway and so is the live wire. No power or phone. Advised control and SMC of lines down. Removed tree from lines at Pole P07471 using Hot St | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.025707 | 0.00011793 | 2016 | 2016-02-29 | C | 39 | 0.025707 | 0.00011793
10087144 | 2016-03-21 08:45 | 2016-03-21 15:06 | 380.9 | 9 | 3428.1 | 380.9 | 377.9 | 0.010366 | 3401.1 | 0.010284 | 2.7214e-05 | NAPA ID:16251 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP622 | To replace 11kV poles and hardware between TEMP14 and IP622 in preparation for conductor upgrade. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-21 | b | 0.0051421 | 1.3607e-05 | 2016 | 2016-03-21 | B | 9 | 0.010284 | 2.7214e-05
10087238 | 2016-03-23 09:00 | 2016-03-23 14:37 | 337 | 9 | 3033 | 337 | 334 | 0.0091711 | 3006 | 0.0090894 | 2.7214e-05 | NAPA ID:16261 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP622 | To replace 11kV conductor between TEMP14 and IP622. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-23 | b | 0.0045447 | 1.3607e-05 | 2016 | 2016-03-23 | B | 9 | 0.0090894 | 2.7214e-05
10087260 | 2016-03-29 09:00 | 2016-03-29 14:55 | 355 | 9 | 3195 | 355 | 352 | 0.0096609 | 3168 | 0.0095793 | 2.7214e-05 | NAPA ID:16265 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP622 | To replace 11kV conductor between TEMP14 and IP622. Works location: Totman Rd. WO 30015388 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2016-03-29 | b | 0.0047896 | 1.3607e-05 | 2016 | 2016-03-29 | B | 9 | 0.0095793 | 2.7214e-05
10087360 | 2016-03-29 22:00 | 2016-03-29 22:50 | 50 | 165 | 8250 | 50 | 47 | 0.024946 | 7755 | 0.023449 | 0.00049892 | NAPA ID:16525 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 832670 | make temp line break between pole 832670 and transformer T588 for use in shutdown on the 30/03/16. Works location: Chamberlain Rd, Masterton. WO 30012201 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-03-29 | b | 0.011725 | 0.00024946 | 2016 | 2016-03-29 | B | 165 | 0.023449 | 0.00049892
10087474 | 2016-03-30 09:30 | 2016-03-30 15:35 | 365 | 39 | 14235 | 365 | 362 | 0.043043 | 14118 | 0.042689 | 0.00011793 | NAPA ID:16527 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 832520 | replace defective 33kv/11kv pole 832520. Works location: Chamberlain Rd, Masterton. WO 30012201 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-03-30 | b | 0.021345 | 5.8963e-05 | 2016 | 2016-03-30 | B | 39 | 0.042689 | 0.00011793
10088013 | 2016-02-29 13:28 | 2016-02-29 14:55 | 87.0833 | 2527 | 219007.7333 | 86.6671 | 83.6671 | 0.66223 | 211426.7333 | 0.6393 | 0.007641 |  | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 744126 | Huirangi GXP CB 1282 Tripped causing LOS to Waitara West Substation. Caused by Seagull in Lines at Pole 744126. Seagull removed and everything relivened. No Damage to Network. Customer called to advise that they heard a big bang and blue smoke came off a | F1,F2,F3 | WAITARA WEST 33KV | HUIRANGI | Taranaki | TP_HUIRANGI | Western Electricity | POWERCO | 2016-02-29 | c | 0.6393 | 0.007641 | 2016 | 2016-02-29 | C | 2527 | 0.6393 | 0.007641
10091471 | 2016-03-31 21:36 | 2016-03-31 22:35 | 59 | 165 | 9735 | 59 | 56 | 0.029436 | 9240 | 0.02794 | 0.00049892 | NAPA ID:16528 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 832670 | close temp line break made at pole 832670 made under napa# 16525 on 29/03/16. Works location: Chamberlain Rd, Masterton. WO 30012201 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-03-31 | b | 0.01397 | 0.00024946 | 2016 | 2016-03-31 | B | 165 | 0.02794 | 0.00049892
10091511 | 2016-03-29 08:51 | 2016-03-29 15:25 | 394 | 40 | 15760 | 394 | 391 | 0.047654 | 15640 | 0.047292 | 0.00012095 | NAPA ID:17184 TP_MASTERTON GXP > CHAPEL SUB > HIGH ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T333 | Like for like replacement of T333. Works location: Manchester St, Masterton. WO 30017316 | F3 | HIGH ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2016-03-29 | b | 0.023646 | 6.0475e-05 | 2016 | 2016-03-29 | B | 40 | 0.047292 | 0.00012095
10091612 | 2016-03-29 09:00 | 2016-03-29 14:37 | 337 | 41 | 13817 | 337 | 334 | 0.041779 | 13694 | 0.041407 | 0.00012397 | NAPA ID:16845 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P10400 | Change 11kv poles p10400, p12623, p12819, p12663. Works location: Te Awe Awe Rd. WO 30015364 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-29 | b | 0.020704 | 6.1987e-05 | 2016 | 2016-03-29 | B | 41 | 0.041407 | 0.00012397
10091649 | 2016-03-29 08:30 | 2016-03-29 15:30 | 420 | 22 | 9240 | 420 | 417 | 0.02794 | 9174 | 0.02774 | 6.6523e-05 | NAPA ID:16692 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P15776 | Tree removal between pole P15776 and P15710. Works location: Station Rd. WO 10163116 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-03-29 | b | 0.01387 | 3.3261e-05 | 2016 | 2016-03-29 | B | 22 | 0.02774 | 6.6523e-05
10091698 | 2016-03-30 08:55 | 2016-03-30 15:40 | 405 | 14 | 5670 | 405 | 402 | 0.017145 | 5628 | 0.017018 | 4.2333e-05 | NAPA ID:16693 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | p15770 | Tree removal at poles p15770 and p15776 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-03-30 | b | 0.0085089 | 2.1166e-05 | 2016 | 2016-03-30 | B | 14 | 0.017018 | 4.2333e-05
10092249 | 2016-02-29 17:06 | 2016-02-29 18:10 | 63.7 | 1 | 63.7 | 63.7 | 60.7 | 0.00019261 | 60.7 | 0.00018354 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6488 | Two fuses blown. Caused by Hawk. 2 x 6A Fuses Replaced. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.00018354 | 3.024e-06 | 2016 | 2016-02-29 | C | 1 | 0.00018354 | 3.0238e-06
10092258 | 2016-03-02 10:54 | 2016-03-02 11:51 | 57 | 1 | 57 | 57 | 54 | 0.00017235 | 54 | 0.00016328 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | Transformer X3010 - Mangamahu Rd | Nigel Bouston from Customer Works in Palmerston reported that Voltage at X3010 has been logged at 250 V. Customer sayint that Lamps are blowing all the time 1R - Require Faultman to Tap X3010 down.( 01/03/16 will be ok) 01/03/16 - James Prime to Attend on | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-02 | c | 0.00016328 | 3.024e-06 | 2016 | 2016-03-02 | C | 1 | 0.00016328 | 3.0238e-06
10092297 | 2016-02-29 17:33 | 2016-02-29 21:33 | 239.3667 | 999 | 71651.35 | 71.7231 | 68.7231 | 0.21666 | 68654.35 | 0.20759 | 0.0030207 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P45547 | Lines down found at Pole P45547 - Isolated at ABS's E46 & F67 plus Fuses E50, backfeed installed via ABS E31. Used 4 metres conductor 1 x clamp top insulator and 2 x sleeves. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-02-29 | c | 0.20759 | 0.0030207 | 2016 | 2016-02-29 | C | 999 | 0.20759 | 0.0030207
10096466 | 2016-03-01 04:28 | 2016-03-01 07:02 | 154.4667 | 303 | 19778.6 | 65.2759 | 62.2759 | 0.059806 | 18869.6 | 0.057057 | 0.0009162 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 329148 | Recloser 6561 Trip. E/F. L/O. Caused by line down at pole 329148. Very old repair gave way. Sleeve deteriorated. 5 mtrs 16mm copper and 2 crimp sleeves. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-03-01 | c | 0.057057 | 0.0009162 | 2016 | 2016-03-01 | C | 303 | 0.057057 | 0.0009162
10097860 | 2016-03-01 08:20 | 2016-03-01 09:00 | 40 | 1 | 40 | 40 | 37 | 0.00012095 | 37 | 0.00011188 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4234 | Fuses At TC4234 Opened for Safety to Repair stay Wire. OFF 08:20 / ON - 09:00 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-01 | c | 0.00011188 | 3.024e-06 | 2016 | 2016-03-01 | C | 1 | 0.00011188 | 3.0238e-06
10098253 | 2016-03-01 13:53 | 2016-03-01 14:40 | 47 | 1 | 47 | 47 | 44 | 0.00014212 | 44 | 0.00013305 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | LV Pump | Brett did reload reliven but fuse blew again. 1R Completed and 2R Request for Fault Find and Repair. Found Faulty Pump at TE6-202. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-01 | c | 0.00013305 | 3.024e-06 | 2016 | 2016-03-01 | C | 1 | 0.00013305 | 3.0238e-06
10098998 | 2016-03-31 09:50 | 2016-03-31 13:41 | 231 | 4 | 924 | 231 | 228 | 0.002794 | 912 | 0.0027577 | 1.2095e-05 | NAPA ID:17024 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 10131 | To replace 11kv poles and replace to run new 11kv conductor. Works location: Mangatainoka Valley Rd. WO 30014555 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-03-31 | b | 0.0013788 | 6.048e-06 | 2016 | 2016-03-31 | B | 4 | 0.0027577 | 1.2095e-05
10099725 | 2016-03-08 09:09 | 2016-03-08 16:40 | 451.35 | 142 | 21863.2667 | 153.9667 | 150.9667 | 0.066109 | 21437.2667 | 0.064821 | 0.00042937 | NAPA ID:17486 TP_STRATFORD GXP > KAPONGA SUB | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 735473 | Isolate double circuit - Remove Faulty T41 Hv cable - Reliven double circuit - Repair Hv cable - Isolate double circuit reinstall T41 cable - test. Swadling Street,Kaponga. W/O 30007226. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.032411 | 0.00021469 | 2016 | 2016-03-08 | B | 142 | 0.064821 | 0.00042937
10100450 | 2016-03-01 21:38 | 2016-03-02 00:14 | 156 | 66 | 9552 | 144.7273 | 141.7273 | 0.028883 | 9354 | 0.028284 | 0.00019957 |  | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 221512 | at 21:47, Paengaroa Sub, CB 1 Gulliver Rd Feeder. Report came in of Car vs Pole. Faultmen dispatched & Found that HV Pole 221512 had been broken. Backfeed supplied from PGA 3, ABS SE6-035 Closed, ABS SE6-083 Opened. Isolated Lines at 9689/4, 9689/1, IP637 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-01 | c | 0.028284 | 0.00019957 | 2016 | 2016-03-01 | C | 66 | 0.028284 | 0.00019957
10100564 | 2016-03-01 20:13 | 2016-03-01 20:29 | 15.8667 | 115 | 1390.55 | 12.0917 | 9.0917 | 0.0042047 | 1045.55 | 0.0031615 | 0.00034773 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | RS 1022 | RS 1022 tripped B,C Ph O/C E/F - No Fault found, possible bird strike as lake in area | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-03-01 | c | 0.0031615 | 0.00034773 | 2016 | 2016-03-01 | C | 115 | 0.0031615 | 0.00034773
10101173 | 2016-03-02 04:16 | 2016-03-02 05:23 | 66.5333 | 524 | 34863.4667 | 66.5333 | 63.5333 | 0.10542 | 33291.4667 | 0.10067 | 0.0015845 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | T1544 | Possum found at base of Transformer T1544 | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2016-03-02 | c | 0.10067 | 0.0015845 | 2016 | 2016-03-02 | C | 524 | 0.10067 | 0.0015845
10101844 | 2016-03-02 06:47 | 2016-03-02 09:55 | 187.6167 | 2 | 375.2333 | 187.6167 | 184.6167 | 0.0011346 | 369.2333 | 0.0011165 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 3726T | Faultman found blown fuse on transforner 3726T due to a Opossum. 2 x 2A Fuse | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-02 | c | 0.0011165 | 6.048e-06 | 2016 | 2016-03-02 | C | 2 | 0.0011165 | 6.0475e-06
10106881 | 2016-03-02 11:38 | 2016-03-02 12:30 | 51.6167 | 7 | 357.8 | 51.1143 | 48.1143 | 0.0010819 | 336.8 | 0.0010184 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X756 | This requires a shutdown at 11.30am this is 11kV which has blown off line. Steve requesting 2R. Faultman has advised all the industry and Perry Hill is working with control. This is affecting all of Kirk Street from 11.30 to approx 1.00pm emergency outag | F1 | BRYCE ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2016-03-02 | c | 0.0010184 | 2.1166e-05 | 2016 | 2016-03-02 | C | 7 | 0.0010184 | 2.1166e-05
10109971 | 2016-03-31 09:10 | 2016-03-31 13:37 | 267 | 48 | 12816 | 267 | 264 | 0.038753 | 12672 | 0.038317 | 0.00014514 | NAPA ID:16144 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S198 | Replace 11kv take-off pole and hardware. Works location: Annedale Rd, Tinui. WO 30018302 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2016-03-31 | b | 0.019159 | 7.257e-05 | 2016 | 2016-03-31 | B | 48 | 0.038317 | 0.00014514
10110039 | 2016-03-03 08:50 | 2016-03-03 13:10 | 260 | 1 | 260 | 260 | 257 | 0.00078618 | 257 | 0.00077711 | 3.0238e-06 | NAPA ID:17577 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9312/5 | Disconnect cable that feeds TP2110 from Fuse/Sw 9312/5 and reconnect to Fuse/Sw 13039/2 | F1/F4 | TE PUKE QUARRY RD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2016-03-03 | b | 0.00038855 | 1.512e-06 | 2016 | 2016-03-03 | B | 1 | 0.00077711 | 3.0238e-06
10110221 | 2016-03-02 18:00 | 2016-03-02 19:45 | 104.5667 | 4 | 418.2667 | 104.5667 | 101.5667 | 0.0012647 | 406.2667 | 0.0012285 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3577 | At 18:00, Walton Sub, CB 2 Campbell Rd Feeder. Faultman dispatched to flickering power calls. Transformer TC3577 was faulty. Isolated lines at Fuses FC1430. Permit issued & repairs carried out. All power restored on completion. Perry Hicks Attended. Mater | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-02 | c | 0.0012285 | 1.2095e-05 | 2016 | 2016-03-02 | C | 4 | 0.0012285 | 1.2095e-05
10113583 | 2016-03-01 18:40 | 2016-03-01 19:25 | 45 | 2 | 90 | 45 | 42 | 0.00027214 | 84 | 0.000254 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4146 | High voltage - Electrician tested lines and sitting at 250 volts plus. 5.27pm advised Cindy at svs hub. Transformer taken offline and tapped down to correct voltage. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-03-01 | c | 0.000254 | 6.048e-06 | 2016 | 2016-03-01 | C | 2 | 0.000254 | 6.0475e-06
10113865 | 2016-03-02 21:00 | 2016-03-03 00:30 | 210.4667 | 2 | 420.9333 | 210.4667 | 207.4667 | 0.0012728 | 414.9333 | 0.0012547 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V83 | Transformer T9/285 Faulty and will need to be replaced . Customer happy to have it replaced Thursday Morning. Turned out to be Fuses V83 Blown. 2 x 10A Fuses Replaced. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-02 | c | 0.0012547 | 6.048e-06 | 2016 | 2016-03-02 | C | 2 | 0.0012547 | 6.0475e-06
10115781 | 2016-03-03 10:44 | 2016-03-03 12:14 | 90 | 21 | 1890 | 90 | 87 | 0.0057149 | 1827 | 0.0055244 | 6.3499e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717515 | Faultman found line down at pole 717515, line was isolated at Fuses MA 298. 3 m of namu conductor. 2 x sleeves | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-03 | c | 0.0055244 | 6.3499e-05 | 2016 | 2016-03-03 | C | 21 | 0.0055244 | 6.3499e-05
10115820 | 2016-03-03 08:29 | 2016-03-03 16:00 | 450.7 | 1 | 450.7 | 450.7 | 447.7 | 0.0013628 | 447.7 | 0.0013537 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | TC4424 | Transformer TC4424 replaced. Isolated and Earthed under own AP. On 16:00 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 2016-03-03 | c | 0.0013537 | 3.024e-06 | 2016 | 2016-03-03 | C | 1 | 0.0013537 | 3.0238e-06
10115867 | 2016-03-30 09:15 | 2016-03-30 12:52 | 217 | 80 | 17360 | 217 | 214 | 0.052492 | 17120 | 0.051767 | 0.0002419 | NAPA ID:17164 TP_BUNNYTHORPE GXP > KEITH ST SUB > KEITH ST 21 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 10302/7 | Change transformer G221 cable feed from G254/T2 over to new switch gear 10302/7. Works location: Pahiatua St. WO 30008622 | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2016-03-30 | b | 0.025883 | 0.00012095 | 2016 | 2016-03-30 | B | 80 | 0.051767 | 0.0002419
10116389 | 2016-03-03 07:06 | 2016-03-03 09:25 | 138.55 | 4 | 554.2 | 138.55 | 135.55 | 0.0016758 | 542.2 | 0.0016395 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | i30 | 2 x 6amp fuses replaced unknown reason | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-03 | c | 0.0016395 | 1.2095e-05 | 2016 | 2016-03-03 | C | 4 | 0.0016395 | 1.2095e-05
10117329 | 2016-03-31 09:56 | 2016-03-31 13:04 | 188 | 13 | 2444 | 188 | 185 | 0.0073901 | 2405 | 0.0072721 | 3.9309e-05 | NAPA ID:17303 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV M67 | Install new 11KV pole & 2 spans of overhead to replace faulty 11KV underground. Works location: Tokorangi Rd, Halcombe. WO 30020396 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-03-31 | b | 0.0036361 | 1.9654e-05 | 2016 | 2016-03-31 | B | 13 | 0.0072721 | 3.9309e-05
10117682 | 2016-03-10 10:22 | 2016-03-10 16:05 | 343 | 1 | 343 | 343 | 340 | 0.0010371 | 340 | 0.0010281 | 3.0238e-06 | NAPA ID:16177 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1739 | Upgrade 100KVA pole mount transfromer to a 200KVA ground mount transformer. Works location: Wiltsdown Rd. WO 30002790 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-03-10 | b | 0.00051404 | 1.512e-06 | 2016 | 2016-03-10 | B | 1 | 0.0010281 | 3.0238e-06
10118012 | 2016-03-03 16:49 | 2016-03-03 18:24 | 95 | 1 | 95 | 95 | 92 | 0.00028726 | 92 | 0.00027819 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Advised svs hub 12:19. Red defect on TX - 15KVA. FM will return this afternoon with replacement TX and bucket truck to complete work | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-03 | c | 0.00027819 | 3.024e-06 | 2016 | 2016-03-03 | C | 1 | 0.00027819 | 3.0238e-06
10118823 | 2016-03-03 15:30 | 2016-03-03 16:11 | 41 | 22 | 902 | 41 | 38 | 0.0027274 | 836 | 0.0025279 | 6.6523e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718454 | Extra crew reqd - Brett will call svs hub to organise this, and will inform Control to let them know they will need to do a quick outage to pull the HV crossarm over safely.Faultman found that king pin had broken on pole 718454, line was isolated at ABS's | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-03 | c | 0.0025279 | 6.6523e-05 | 2016 | 2016-03-03 | C | 22 | 0.0025279 | 6.6523e-05
10119438 | 2016-03-09 09:00 | 2016-03-09 15:18 | 378.1167 | 9 | 3403.05 | 378.1167 | 375.1167 | 0.01029 | 3376.05 | 0.010208 | 2.7214e-05 | NAPA ID:17628 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF5-001 | Replace 11kV pole arms and reconductor wire. Works location: No. 2 Rd, Mangatoi Rd. WO 30002454 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-09 | b | 0.0051042 | 1.3607e-05 | 2016 | 2016-03-09 | B | 9 | 0.010208 | 2.7214e-05
10120973 | 2016-03-07 09:15 | 2016-03-07 11:34 | 139.15 | 118 | 16419.7 | 139.15 | 136.15 | 0.049649 | 16065.7 | 0.048579 | 0.0003568 | NAPA ID:17634 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | C1269 | Replace very rotten cross arms at pole C1269. Works location: Ngutumanga & Gratton Rds, Waihou. WO 30007220 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-03-07 | b | 0.024289 | 0.0001784 | 2016 | 2016-03-07 | B | 118 | 0.048579 | 0.0003568
10121127 | 2016-03-23 10:15 | 2016-03-23 14:43 | 268 | 61 | 16348 | 268 | 265 | 0.049432 | 16165 | 0.048879 | 0.00018445 | NAPA ID:17139 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6438 | We are replacing transformer 3315 and 2-11kV cross arms poles 712970 and 712997 that are missing nuts. Works location: Arawhata Rd. WO 10143182 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-23 | b | 0.02444 | 9.2225e-05 | 2016 | 2016-03-23 | B | 61 | 0.048879 | 0.00018445
10121163 | 2016-03-21 09:00 | 2016-03-21 15:30 | 390 | 30 | 11700 | 390 | 387 | 0.035378 | 11610 | 0.035106 | 9.0713e-05 | NAPA ID:17641 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP398 | LLWP TO INSTALL GAP POLE 223765. REMOVE TP398, FP264/1, FP 264/2. REPLACE 11KV POLES ARMS AND RECON WIRE. RELOCATE SF5-001 TO NEW DOUBLE POLE SITE [ OLD TP398 SITE]. CHANGE SWER TX TO 2 PHASES SET UP UNDER AP. REMOVE LINKS TEMP19. REMAKE GAP AT POLE 2237 | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-21 | b | 0.017553 | 4.5356e-05 | 2016 | 2016-03-21 | B | 30 | 0.035106 | 9.0713e-05
10122806 | 2016-03-03 19:04 | 2016-03-03 22:01 | 176.9833 | 2 | 353.9667 | 176.9833 | 173.9833 | 0.0010703 | 347.9667 | 0.0010522 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD3-166 | Replace 2 x 3 amp HT fuses at trany & 2 x 6 amp at beginning of line at SD3-080. Bird on trany | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-03 | c | 0.0010522 | 6.048e-06 | 2016 | 2016-03-03 | C | 2 | 0.0010522 | 6.0475e-06
10122941 | 2016-03-03 23:09 | 2016-03-04 00:28 | 79.05 | 15 | 1185.75 | 79.05 | 76.05 | 0.0035854 | 1140.75 | 0.0034494 | 4.5356e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717335 | Check for safety - Murray from Downer advised a HV crossarm is on an angle - the arm braces have rusted through & broken. Fm requesting 2R to replace cross arm and braces | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-03 | c | 0.0034494 | 4.5356e-05 | 2016 | 2016-03-03 | C | 15 | 0.0034494 | 4.5356e-05
10124514 | 2016-03-06 09:25 | 2016-03-06 15:06 | 341.15 | 258 | 88016.7 | 341.15 | 338.15 | 0.26614 | 87242.7 | 0.2638 | 0.00078013 | NAPA ID:17653 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12085 | Install three new sectionalisers 12085, 12086, 12087 at various sites on the Strathmore feeder and commission. Also carry out red defect repairs and Asplundh to cut trees within isolation area. Design request to remove 11kV Fuse 5390. Applicant has reques | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-06 | b | 0.1319 | 0.00039006 | 2016 | 2016-03-06 | B | 258 | 0.2638 | 0.00078013
10126604 | 2016-03-04 12:46 | 2016-03-04 18:02 | 315.9167 | 579 | 65771.35 | 113.5947 | 110.5947 | 0.19888 | 64034.35 | 0.19362 | 0.0017508 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217002 | ( TGA12 ) Sectionaliser 9208 tripped E/F, L/O feeder sectionalised witn no obvious fault found. (Tree cutters were working in area but claim to have had no effect ) all back in service. Sectionaliser 9208 tripped again, feeder sectionalised again LFI's fl | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-04 | c | 0.19362 | 0.0017508 | 2016 | 2016-03-04 | C | 579 | 0.19362 | 0.0017508
10130361 | 2016-03-19 09:37 | 2016-03-19 14:38 | 301 | 1 | 301 | 301 | 298 | 0.00091015 | 298 | 0.00090108 | 3.0238e-06 | NAPA ID:16194 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 205641 | Replace poles ,hardware & conductor between poles 205641 & 205659. Live Line connection of Lines to TEMP66 & TEMP62. WOrks location: Wainui South Rd, Aongatete. WO 30015247 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-03-19 | b | 0.00045054 | 1.512e-06 | 2016 | 2016-03-19 | B | 1 | 0.00090108 | 3.0238e-06
10130565 | 2016-03-21 09:05 | 2016-03-21 17:50 | 525 | 47 | 24675 | 525 | 522 | 0.074611 | 24534 | 0.074185 | 0.00014212 | NAPA ID:16522 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP17527 | Remove TC4101 & Re[place the transformer & Pad with a new 200kVA Transformer. Works location: Ocean Rd, Whangamata. WO 30002527. Outage overran predicted time as there was a faulty cable. This will be repaired 22.03.16. | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-21 | b | 0.037092 | 7.1058e-05 | 2016 | 2016-03-21 | B | 47 | 0.074185 | 0.00014212
10130693 | 2016-03-20 08:30 | 2016-03-20 17:11 | 521 | 49 | 25529 | 521 | 518 | 0.077194 | 25382 | 0.076749 | 0.00014816 | NAPA ID:16321 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-192 | Replace TD4-192 (like for like). Works location: Barberry St. Tauranga. WO 30002526 | F2 | WAIHI RD | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 2016-03-20 | b | 0.038375 | 7.4082e-05 | 2016 | 2016-03-20 | B | 49 | 0.076749 | 0.00014816
10133864 | 2016-03-04 18:18 | 2016-03-04 21:20 | 182.65 | 1 | 182.65 | 182.65 | 179.65 | 0.00055229 | 179.65 | 0.00054322 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TF4-020 | *** please check if oms 10133871 - 1956 Pyes Pa Road off tx TP1088 is related *** please check 10133987/10133944/10133929 and 10133914 are related also Blair advised part of the fault earlier in the day - everything is restored now. He didn't need to do | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-04 | c | 0.00054322 | 3.024e-06 | 2016 | 2016-03-04 | C | 1 | 0.00054322 | 3.0238e-06
10133881 | 2016-03-04 20:45 | 2016-03-04 22:30 | 105 | 1 | 105 | 105 | 102 | 0.00031749 | 102 | 0.00030842 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3210T | Replaced Transformer 3210T 15 kVA | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-03-04 | c | 0.00030842 | 3.024e-06 | 2016 | 2016-03-04 | C | 1 | 0.00030842 | 3.0238e-06
10136372 | 2016-03-05 13:00 | 2016-03-05 16:30 | 210 | 2 | 420 | 210 | 207 | 0.00127 | 414 | 0.0012518 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T812 | Check for safety. Digger has hit lines, causing them to spark. Mcauleys Transport. Contact Daniel 0274664608. Down a gravel driveway into a yard. 12.25 advised Sammy at svs hub. Inspection found Digger had caused 1 LV Phase to wrap around Neutral Conduc | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 2016-03-05 | c | 0.0012518 | 6.048e-06 | 2016 | 2016-03-05 | C | 2 | 0.0012518 | 6.0475e-06
10136500 | 2016-03-05 14:04 | 2016-03-05 14:58 | 54.4333 | 24 | 1306.4 | 54.4333 | 51.4333 | 0.0039502 | 1234.4 | 0.0037325 | 7.257e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 446654 | Check for safety. Cutting trees which has come down on the power lines. Lines still attached but have no power. Contact: Jonathon 0274486645. Have advised Sammy at svs hub and Control. PLease check poss related 10136523 and 10136516. 2 HT fuses found trip | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-05 | c | 0.0037325 | 7.257e-05 | 2016 | 2016-03-05 | C | 24 | 0.0037325 | 7.257e-05
10136897 | 2016-03-05 17:32 | 2016-03-05 21:34 | 241.6333 | 717 | 46724.35 | 65.1665 | 62.1665 | 0.14128 | 44573.35 | 0.13478 | 0.002168 |  | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 804863 | Tree in line at Pole 804863. Used 8 M 25mm Copper 1 X LV Insulator. NDR 047401 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-05 | c | 0.13478 | 0.002168 | 2016 | 2016-03-05 | C | 717 | 0.13478 | 0.002168
10138586 | 2016-03-06 10:51 | 2016-03-06 14:45 | 234.2333 | 420 | 28660.2 | 68.2386 | 65.2386 | 0.086662 | 27400.2 | 0.082852 | 0.00127 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Cable fault after cable wrongly spiked on Planned job 16644. will be repaired 7/3/16 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-06 | c | 0.082852 | 0.00127 | 2016 | 2016-03-06 | C | 420 | 0.082852 | 0.00127
10140466 | 2016-03-06 16:25 | 2016-03-06 17:45 | 80.4833 | 1 | 80.4833 | 80.4833 | 77.4833 | 0.00024336 | 77.4833 | 0.00023429 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | PU474 | Fuses found blown at Fuses PU474 - Cause Bird strike. Used 2 x 10 amp fuses | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-06 | c | 0.00023429 | 3.024e-06 | 2016 | 2016-03-06 | C | 1 | 0.00023429 | 3.0238e-06
10140744 | 2016-03-06 19:46 | 2016-03-06 23:09 | 203.4167 | 114 | 19479.4667 | 170.8725 | 167.8725 | 0.058901 | 19137.4667 | 0.057867 | 0.00034471 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 807156 | Recloser 564 tripped on C phase O/C & E/F flags, line was patrolled and sectionalised and line down was found at pole 807156, line was isolated at ABS 027 to repair the lines caused by a tree. 15 meters 10mm Copper conductor used. 4 X sleeves used.NDR: 41 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-06 | c | 0.057867 | 0.00034471 | 2016 | 2016-03-06 | C | 114 | 0.057867 | 0.00034471
10141959 | 2016-03-07 07:11 | 2016-03-07 10:51 | 219.35 | 463 | 31092.7333 | 67.1549 | 64.1549 | 0.094017 | 29703.7333 | 0.089817 | 0.0014 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 248657 | Matatoki CB 3 tripped to L/O. Bird on Lines at pole 248657 Caused lines to burn down. Lines Repaired. Used 40M 16mm Copper. 4 x Hi Commpression Crimp Sleeves. Sectionaliser 9696 would not close for backfeed during fault - had comms problems - OMS 10143923 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-03-07 | c | 0.089817 | 0.0014 | 2016 | 2016-03-07 | C | 463 | 0.089817 | 0.0014
10143771 | 2016-03-22 09:15 | 2016-03-22 14:30 | 315 | 98 | 30870 | 315 | 312 | 0.093343 | 30576 | 0.092455 | 0.00029633 | NAPA ID:16428 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole R12614 | To replace pole # R12614 and install two replacement LV cables from TC3937 to the overhead lines. Works location: Ocean Rd, Whangamata. WO 30003265 | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-22 | b | 0.046227 | 0.00014816 | 2016 | 2016-03-22 | B | 98 | 0.092455 | 0.00029633
10143874 | 2016-03-08 10:13 | 2016-03-08 15:58 | 345.1167 | 51 | 17600.95 | 345.1167 | 342.1167 | 0.053221 | 17447.95 | 0.052758 | 0.00015421 | NAPA ID:17694 TP_MATAROA GXP > WAIOURU SUB > IRIRANGI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 779930 | replace pole 779930 due to burnt xarms and pole leaning badly | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2016-03-08 | b | 0.026379 | 7.7106e-05 | 2016 | 2016-03-08 | B | 51 | 0.052758 | 0.00015421
10144419 | 2016-03-07 09:59 | 2016-03-09 14:40 | 3160.7 | 4 | 12642.8 | 3160.7 | 3157.7 | 0.038229 | 12630.8 | 0.038193 | 1.2095e-05 | NAPA ID:17710 TP_STRATFORD GXP > CARDIFF SUB > CARDIFF RD | 11 | Planned | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 8837/2 | 6.6kv cable exposed in walking track from Pembroke Rd plato up to skifield. Customer advised by Tony Watt (civil contactor) of what is to be done and happy with power off till before the weekend. Works location: Pembroke Rd. WO 30024515 | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-03-07 | b | 0.019096 | 6.048e-06 | 2016 | 2016-03-07 | B | 4 | 0.038193 | 1.2095e-05
10144674 | 2016-03-24 10:14 | 2016-03-24 14:25 | 251 | 10 | 2510 | 251 | 248 | 0.0075896 | 2480 | 0.0074989 | 3.0238e-05 | NAPA ID:17534 TP_LINTON GXP > KAIRANGA SUB > AWAPUNI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace Transformer Crossarms T6/248 | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-03-24 | b | 0.0037495 | 1.5119e-05 | 2016 | 2016-03-24 | B | 10 | 0.0074989 | 3.0238e-05
10144789 | 2016-03-29 11:22 | 2016-03-29 14:26 | 184 | 3 | 552 | 184 | 181 | 0.0016691 | 543 | 0.0016419 | 9.0713e-06 | NAPA ID:17514 TP_MANGAMAIRE GXP > ALFREDTON SUB > BROOKLANDS | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P08281 | Change 11KV Xarms & Tx on TX pole T9/384. Works location: Route 52. WO 30010306 | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-29 | b | 0.00082095 | 4.536e-06 | 2016 | 2016-03-29 | B | 3 | 0.0016419 | 9.0713e-06
10144963 | 2016-03-30 09:31 | 2016-03-30 13:40 | 249 | 23 | 5727 | 249 | 246 | 0.017317 | 5658 | 0.017108 | 6.9546e-05 | NAPA ID:16856 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 140 | We are replacing 11kv ABS 155 and the cross arms. Works location: Davies Rd. WO 30000496 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-30 | b | 0.0085542 | 3.4773e-05 | 2016 | 2016-03-30 | B | 23 | 0.017108 | 6.9546e-05
10148211 | 2016-03-17 08:54 | 2016-03-17 15:39 | 405 | 14 | 5670 | 405 | 402 | 0.017145 | 5628 | 0.017018 | 4.2333e-05 | NAPA ID:16639 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 7074 | Isolation for tree trimming from fuses 7074 to end of line between poles 839801 839804.Also safety measure required on 33kV Awatoitoi Tinui line on CB 809. Works location: Bute Rd. WO 10152356 | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-03-17 | b | 0.0085089 | 2.1166e-05 | 2016 | 2016-03-17 | B | 14 | 0.017018 | 4.2333e-05
10148256 | 2016-03-07 18:40 | 2016-03-07 19:48 | 68 | 40 | 2720 | 68 | 65 | 0.0082246 | 2600 | 0.0078618 | 0.00012095 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761694 | Outage required from Fuses 5489 to straighten a badly leaning pole. One breast block used and several sleeves as the LV had to be lowered during the job. Relivened OK. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2016-03-07 | c | 0.0078618 | 0.00012095 | 2016 | 2016-03-07 | C | 40 | 0.0078618 | 0.00012095
10148688 | 2016-03-22 08:30 | 2016-03-22 15:53 | 443 | 63 | 27909 | 443 | 440 | 0.08439 | 27720 | 0.083819 | 0.0001905 | NAPA ID:16026 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | S74 | 11kv pole and hardware replacements | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-22 | b | 0.041909 | 9.5248e-05 | 2016 | 2016-03-22 | B | 63 | 0.083819 | 0.0001905
10149116 | 2016-03-20 08:50 | 2016-03-22 19:37 | 3526.5667 | 8 | 1391.6 | 173.95 | 170.95 | 0.0042079 | 1367.6 | 0.0041353 | 2.419e-05 | NAPA ID:17685 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 725268 | TP 110Kv o/h circuit is being re-routed and the crosses over Tawhiti feeder 11Kv line. So for safety 11Kv needs to be de-enregised and earthed. So installing new 11Kv termination Xarm at pole 725268 with line Break cut for isolation. To be reconnected on | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-03-20 | b | 0.0020676 | 1.2095e-05 | 2016 | 2016-03-20 | B | 8 | 0.0041353 | 2.419e-05
10149915 | 2016-03-07 17:46 | 2016-03-07 20:39 | 172.5833 | 319 | 36308.6333 | 113.8202 | 110.8202 | 0.10979 | 35351.6333 | 0.10689 | 0.00096458 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222080 | CB 9168 tripped O/C & E/F during sectionalising found lines down @ pole 222080 isolated @ ABS SE4-007 and repaired lines down betweem transformer T4712 and pole 222080. Materials used: 10m conductor and 2 joints. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-03-07 | c | 0.10689 | 0.00096458 | 2016 | 2016-03-07 | C | 319 | 0.10689 | 0.00096458
10150613 | 2016-03-07 20:30 | 2016-03-07 22:24 | 113.7833 | 1 | 113.7833 | 113.7833 | 110.7833 | 0.00034405 | 110.7833 | 0.00033498 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 223275 | Replaced x2 3amp DDO fuses at the top of the Rd at the Spur line. Cause unknown - possibly due to wind. Switch # SE5289. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok. Full power restored. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2016-03-07 | c | 0.00033498 | 3.024e-06 | 2016 | 2016-03-07 | C | 1 | 0.00033498 | 3.0238e-06
10150797 | 2016-03-08 07:03 | 2016-03-08 12:05 | 302.2167 | 28 | 8185.0667 | 292.3238 | 289.3238 | 0.02475 | 8101.0667 | 0.024496 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | V16 | Fuses V16 - found tripped. Replaced 2 x 10 Amp Fuse Links. Line sectionalised an patrolled with cause of fault located. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.024496 | 8.4665e-05 | 2016 | 2016-03-08 | C | 28 | 0.024496 | 8.4665e-05
10150865 | 2016-03-08 07:27 | 2016-03-08 08:58 | 90.8667 | 34 | 3089.4667 | 90.8667 | 87.8667 | 0.0093418 | 2987.4667 | 0.0090334 | 0.00010281 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8423 | Replace 3 x 40A fuses. Cause = Bird | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.0090334 | 0.00010281 | 2016 | 2016-03-08 | C | 34 | 0.0090334 | 0.00010281
10150906 | 2016-03-08 07:35 | 2016-03-08 08:45 | 69.75 | 7 | 488.25 | 69.75 | 66.75 | 0.0014764 | 467.25 | 0.0014129 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7506 | Replace 2 x 10A fuse. Due to Wind. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.0014129 | 2.1166e-05 | 2016 | 2016-03-08 | C | 7 | 0.0014129 | 2.1166e-05
10153032 | 2016-03-08 13:16 | 2016-03-08 16:15 | 179 | 37 | 6623 | 179 | 176 | 0.020026 | 6512 | 0.019691 | 0.00011188 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P10 | Remove trees from lines and repair. NDR 45163 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.019691 | 0.00011188 | 2016 | 2016-03-08 | C | 37 | 0.019691 | 0.00011188
10153128 | 2016-03-08 17:29 | 2016-03-08 17:45 | 15.7833 | 4 | 63.1333 | 15.7833 | 12.7833 | 0.0001909 | 51.1333 | 0.00015461 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 832288 | HV fault need to replace 2 of 3 fuses requesting another 1r as very windy and want to patrol to see if any other issues. Remove tree branch from the lines at Pole 832288. Replace 2 x 10A fuses. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.00015462 | 1.2095e-05 | 2016 | 2016-03-08 | C | 4 | 0.00015461 | 1.2095e-05
10153151 | 2016-03-10 09:00 | 2016-03-10 15:47 | 407 | 193 | 78551 | 407 | 404 | 0.23752 | 77972 | 0.23577 | 0.00058359 | NAPA ID:17714 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | 11kv pole and hardware replacements | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-10 | b | 0.11788 | 0.00029179 | 2016 | 2016-03-10 | B | 193 | 0.23577 | 0.00058359
10153320 | 2016-03-29 09:00 | 2016-03-29 15:34 | 394.1333 | 255 | 100431.4167 | 393.8487 | 390.8487 | 0.30368 | 99666.4167 | 0.30137 | 0.00077106 | NAPA ID:16830 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 202233 | Levers Rd Conductor Upgrade Stage 2 Shut 1. Remove 11kV wires between poles 202233 and 202240. Replace Poles 202203, 202207, 202208, 202213, 202230, 202232, 202233. Recloser 9592/2, and links 9592/4 will not be reinstated at the end of this outage. ABS | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2016-03-29 | b | 0.15068 | 0.00038553 | 2016 | 2016-03-29 | B | 255 | 0.30137 | 0.00077106
10153414 | 2016-03-08 14:37 | 2016-03-08 14:40 | 3.15 | 1 | 3.15 | 3.15 | 0.15 | 9.5248e-06 | 0 | 0 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0 | 3.024e-06 | 2016 | 2016-03-08 | C | 1 | 0 | 3.0238e-06
10153498 | 2016-03-08 10:04 | 2016-03-08 14:53 | 289.5 | 2 | 579 | 289.5 | 286.5 | 0.0017508 | 573 | 0.0017326 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.0017326 | 6.048e-06 | 2016 | 2016-03-08 | C | 2 | 0.0017326 | 6.0475e-06
10153870 | 2016-03-31 09:15 | 2016-03-31 12:00 | 165 | 14 | 2310 | 165 | 162 | 0.0069849 | 2268 | 0.0068579 | 4.2333e-05 | NAPA ID:16852 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 229 | We are replacing 11kv ABS 229 and crossarms. Works location: Hursthouse Rd. WO 30000496 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-31 | b | 0.0034289 | 2.1166e-05 | 2016 | 2016-03-31 | B | 14 | 0.0068579 | 4.2333e-05
10154038 | 2016-03-08 15:45 | 2016-03-08 17:32 | 107 | 237 | 9855.8 | 41.5857 | 38.5857 | 0.029802 | 9144.8 | 0.027652 | 0.00071663 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 499 | Blown insulator causing line down 1 x insulator and 10m conductor | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.027652 | 0.00071663 | 2016 | 2016-03-08 | C | 237 | 0.027652 | 0.00071663
10154650 | 2016-03-08 16:34 | 2016-03-08 17:31 | 56.4833 | 641 | 28606.7167 | 44.6283 | 41.6283 | 0.0865 | 26683.7167 | 0.080685 | 0.0019382 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | CB 7 | CB 7 A/R, L/O. Tripping coincided with setting Regulators 10214 to Auto after planned shutdown (NAPA 17154). Feeder livened up to ABS K20 before the Regulators. Faultman asked to check state of Regulators on site and also Switchgear on site. Switchgear 10 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.080685 | 0.0019382 | 2016 | 2016-03-08 | C | 641 | 0.080685 | 0.0019382
10155625 | 2016-03-08 17:27 | 2016-03-08 20:04 | 156.8667 | 12 | 1882.4 | 156.8667 | 153.8667 | 0.0056919 | 1846.4 | 0.0055831 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 481 Welcome Bay Road Tauranga | Tree has pulled lines down - address fed from TX TD4-174 pole 220305 ? Called in by Fire Comms Event # F2033449. ETA please 09 486 7949. 5:03pm called through to SMC - Shannon. 5:08pm ETA 30mins advised Colin @ Fire Service as advised by Cindy from | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-03-08 | c | 0.0055831 | 3.6285e-05 | 2016 | 2016-03-08 | C | 12 | 0.0055831 | 3.6285e-05
10156179 | 2016-03-08 19:32 | 2016-03-08 20:37 | 64.7333 | 3 | 194.2 | 64.7333 | 61.7333 | 0.00058721 | 185.2 | 0.00056 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P45076 | 2r request to help as have floating wires on HV and possible broken binders - advised Zane to call SMC to get help. Found floating wire at pole P45076 repaired with 1 m conductor 2 sleeves and 1 x 3amp fuse. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-03-08 | c | 0.00056 | 9.071e-06 | 2016 | 2016-03-08 | C | 3 | 0.00056 | 9.0713e-06
10156307 | 2016-03-08 19:11 | 2016-03-08 19:30 | 18.9667 | 1 | 18.9667 | 18.9667 | 15.9667 | 5.7351e-05 | 15.9667 | 4.8279e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 5450E | Arching pole 7:12pm called through to SMC - Glo no fault found no power off | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-03-08 | c | 4.8279e-05 | 3.024e-06 | 2016 | 2016-03-08 | C | 1 | 4.8279e-05 | 3.0238e-06
10157690 | 2016-03-09 07:40 | 2016-03-09 09:04 | 84.0833 | 3 | 252.25 | 84.0833 | 81.0833 | 0.00076274 | 243.25 | 0.00073553 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI747 | Replace 2 x 6A fuses due to bird. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-03-09 | c | 0.00073553 | 9.071e-06 | 2016 | 2016-03-09 | C | 3 | 0.00073553 | 9.0713e-06
10158379 | 2016-03-11 09:46 | 2016-03-11 14:58 | 312 | 3 | 936 | 312 | 309 | 0.0028302 | 927 | 0.002803 | 9.0713e-06 | NAPA ID:17772 TP_KINLEITH GXP > BAIRD ROAD SUB > KAURI ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Replace rotten /broken X arms | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-03-11 | b | 0.0014015 | 4.536e-06 | 2016 | 2016-03-11 | B | 3 | 0.002803 | 9.0713e-06
10158411 | 2016-03-09 10:12 | 2016-03-09 12:01 | 109.4667 | 110 | 10865.3333 | 98.7758 | 95.7758 | 0.032854 | 10535.3333 | 0.031856 | 0.00033261 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Sectionalised, & Patrolled, no fault found. Relivened OK 1r 1014 2r line patrol 1127 2r repair none | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-09 | c | 0.031856 | 0.00033261 | 2016 | 2016-03-09 | C | 110 | 0.031856 | 0.00033261
10162557 | 2016-03-09 16:51 | 2016-03-09 18:24 | 92.7833 | 1 | 92.7833 | 92.7833 | 89.7833 | 0.00028055 | 89.7833 | 0.00027148 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | this transformer needs to be replaced and will do this tomorrow tc 2/137 pole 207976 the oil it getting very hot and the tx is very old and rusty it looks like an original and it does get very hot when in use 14:43 - Spoke to Tahlia at the SMC and she | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-03-09 | c | 0.00027148 | 3.024e-06 | 2016 | 2016-03-09 | C | 1 | 0.00027148 | 3.0238e-06
10164334 | 2016-03-10 01:42 | 2016-03-10 04:05 | 142.4 | 3394 | 223856 | 65.9564 | 62.9564 | 0.67689 | 213674 | 0.6461 | 0.010263 |  | 33 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB 2212 | CB 2212 tripped on O/C time causing LOS of Baird Rd Substation. Line and cables were test and patrolled and the Faultman has found a cable fault on 33KV cable between CB 2212 and ABS PC 5 at ripple plant.The cable is isolated at both ends. DNO 160305 ha | F1,F2,F3 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 2016-03-10 | c | 0.6461 | 0.010263 | 2016 | 2016-03-10 | C | 3394 | 0.6461 | 0.010263
10167845 | 2016-03-10 04:42 | 2016-03-10 07:01 | 138.35 | 17 | 2351.95 | 138.35 | 135.35 | 0.0071117 | 2300.95 | 0.0069575 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4174 | 2 x 15 amp fuses unknown reason | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-10 | c | 0.0069575 | 5.1404e-05 | 2016 | 2016-03-10 | C | 17 | 0.0069575 | 5.1404e-05
10167934 | 2016-03-10 07:42 | 2016-03-10 17:56 | 613.4667 | 304 | 19293.8667 | 63.4667 | 60.4667 | 0.05834 | 18381.8667 | 0.055582 | 0.00091922 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P49350 | Parkville 33kV XT40 tripped on B and C phase affecting Alfredton feeder. Patrol found Tree in line at P48124. This was repaired on 10th. There were also two floating conductors found on pole P47721. These were repaired on 11th. | F1,F2,F3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.055582 | 0.00091922 | 2016 | 2016-03-10 | C | 304 | 0.055582 | 0.00091922
10168321 | 2016-03-29 09:10 | 2016-03-29 15:42 | 392 | 18 | 7056 | 392 | 389 | 0.021336 | 7002 | 0.021172 | 5.4428e-05 | NAPA ID:16203 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 205659 | Replace poles, hardware and conductor between poles 205659 & 205669. Works location: Wainui South Rd. WO 30015247 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-03-29 | b | 0.010586 | 2.7214e-05 | 2016 | 2016-03-29 | B | 18 | 0.021172 | 5.4428e-05
10168328 | 2016-03-10 08:24 | 2016-03-10 09:35 | 71.1667 | 766 | 43019 | 56.1606 | 53.1606 | 0.13008 | 40721 | 0.12313 | 0.0023162 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C953 | CB C953 Tripped. Line patrolled nothing found. 1r 0824. 2r line patrol 0910. 2r repair none. | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.12313 | 0.0023162 | 2016 | 2016-03-10 | C | 766 | 0.12313 | 0.0023162
10169208 | 2016-03-14 09:00 | 2016-03-14 11:08 | 128 | 1 | 128 | 128 | 125 | 0.00038704 | 125 | 0.00037797 | 3.0238e-06 | NAPA ID:17818 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I1839 | Replace broken cross arm at pole I1839. Works location: Tahuroa Rd, Morrinsville. WO 30007220 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-03-14 | b | 0.00018898 | 1.512e-06 | 2016 | 2016-03-14 | B | 1 | 0.00037797 | 3.0238e-06
10169242 | 2016-03-31 09:36 | 2016-03-31 15:14 | 338.5 | 312 | 82656 | 264.9231 | 261.9231 | 0.24993 | 81720 | 0.2471 | 0.00094341 | NAPA ID:16844 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 202215 | Levers Rd Conductor Upgrade Stage 3 Shut 2. Upgrade hardware between pole 202214 and 202227. Replace Poles 202215, 202216, 202217, 202218, 202219, 202220, 202221, 202222, 202224, 202226. Works location: Levers Rd, Tauranga. WO 30015220 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2016-03-31 | b | 0.12355 | 0.00047171 | 2016 | 2016-03-31 | B | 312 | 0.2471 | 0.00094341
10169796 | 2016-03-10 09:31 | 2016-03-10 14:33 | 301.8833 | 981 | 50821 | 51.8053 | 48.8053 | 0.15367 | 47878 | 0.14477 | 0.0029663 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | 33kv reclosers 3139 & 3141 trip O/C E/F line patrolled nothing found | F1,F2,F3 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2016-03-10 | c | 0.14477 | 0.0029663 | 2016 | 2016-03-10 | C | 981 | 0.14477 | 0.0029663
10171343 | 2016-03-31 09:10 | 2016-03-31 11:37 | 147 | 24 | 3528 | 147 | 144 | 0.010668 | 3456 | 0.01045 | 7.257e-05 | NAPA ID:17745 TP_KINLEITH GXP > BAIRD ROAD SUB > CAMPBELL ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B0226 | Replace 2 x 11kV term arms at pole B0226. Works location: Sloss Rd, Tokoroa. WO 30017433 | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 2016-03-31 | b | 0.0052251 | 3.6285e-05 | 2016 | 2016-03-31 | B | 24 | 0.01045 | 7.257e-05
10172192 | 2016-03-31 09:15 | 2016-03-31 13:40 | 265 | 15 | 3975 | 265 | 262 | 0.012019 | 3930 | 0.011883 | 4.5356e-05 | NAPA ID:16805 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1kV Transformer TC1210 | Replace DDOs HV Xarms at TC1210 and Lightning Arrestors. Works location: Coromandel. WO 30013130 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-31 | b | 0.0059417 | 2.2678e-05 | 2016 | 2016-03-31 | B | 15 | 0.011883 | 4.5356e-05
10173345 | 2016-03-10 11:43 | 2016-03-10 15:02 | 198.5167 | 179 | 31492.7333 | 175.9371 | 172.9371 | 0.095226 | 30955.7333 | 0.093603 | 0.00054125 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27759 | CB 3 tripped on B Phase, O/C and E/F. Conductor down at Pole P27759. 5m Conductor and 1 binder used for repairs. . 1r. 2r line patrol 1321. 2 r repair 1321 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.093603 | 0.00054125 | 2016 | 2016-03-10 | C | 179 | 0.093603 | 0.00054125
10174622 | 2016-03-10 12:44 | 2016-03-10 15:19 | 155 | 233 | 7406.3 | 31.7867 | 28.7867 | 0.022395 | 6707.3 | 0.020281 | 0.00070454 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731493 | Recloser 6497 tripped on C phase O/C & E/F flags, line was patrolled and sectionalised and the faultman found a broken cross arm on pole 731493, line was isolated at fuses 5264 to replace the cross arm. 1 X 11KV cross arm & all hardware replaced. 1r 2r li | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.020281 | 0.00070454 | 2016 | 2016-03-10 | C | 233 | 0.020281 | 0.00070454
10176052 | 2016-03-21 09:30 | 2016-03-21 15:41 | 371 | 532 | 197125.15 | 370.536 | 367.536 | 0.59606 | 195529.15 | 0.59123 | 0.0016086 | NAPA ID:17188 TP_MASTERTON GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Tinui Sub | REPLACING 33KV TWO POLE STRUTURE OUTSIDE TINUI SUB WITH 11KV C935 UNDER 33KV CIRCUIT | F1,F2,F3 | TINUI 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 2016-03-21 | b | 0.29562 | 0.00080432 | 2016 | 2016-03-21 | B | 532 | 0.59123 | 0.0016086
10176064 | 2016-03-10 13:57 | 2016-03-10 20:28 | 390.65 | 92 | 12497.2167 | 135.8393 | 132.8393 | 0.037789 | 12221.2167 | 0.036954 | 0.00027819 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 817059 | Feeder Fault RS 8156 A/R, L/O, E/F B Phase. Lines down at Pole 817059. SS C637/2 found open. Isolated at ABS S1204 & repaired using 6mtrs 16mm PVC Cu conductor, 4x 16mm sleeves, & 2mtrs Cu Binder. 2r line patrol 1458. 2r repair 1632 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.036954 | 0.00027819 | 2016 | 2016-03-10 | C | 92 | 0.036954 | 0.00027819
10179785 | 2016-03-10 15:30 | 2016-03-10 18:14 | 163.6667 | 36 | 2599.6333 | 72.212 | 69.212 | 0.0078607 | 2491.6333 | 0.0075341 | 0.00010886 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737035 | Faultman found blown fuses at Fuses 6082 & 6027, Fuses 6082 were reloaded and livened at 17:03, Fuses 6027 were isolated as faultman found a floating wire at pole 737035 caused by a broken insulator. 2 X 20 Amp HV fuses replaced at Fuses 6082. 1 x 11KV in | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.0075341 | 0.00010886 | 2016 | 2016-03-10 | C | 36 | 0.0075341 | 0.00010886
10180348 | 2016-03-10 16:32 | 2016-03-10 17:02 | 30.05 | 181 | 5439.05 | 30.05 | 27.05 | 0.016446 | 4896.05 | 0.014804 | 0.0005473 |  | 33 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | C885 | Tree on line. Removed with hot stick. NDR# 23281. Re-liven. Checked with Control, ok to be signed off by Dispatch. 2r line patrol 1702 2r repair no | F1,F2,F3 | PAHAUTEA 33KV TIE | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2016-03-10 | c | 0.014804 | 0.0005473 | 2016 | 2016-03-10 | C | 181 | 0.014804 | 0.0005473
10180785 | 2016-03-10 19:09 | 2016-03-10 19:25 | 16.2333 | 6 | 97.4 | 16.2333 | 13.2333 | 0.00029451 | 79.4 | 0.00024009 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4612 | Replaced 2x 6Amp HV Links | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.00024009 | 1.8143e-05 | 2016 | 2016-03-10 | C | 6 | 0.00024009 | 1.8143e-05
10182059 | 2016-03-10 17:10 | 2016-03-10 19:55 | 164.7 | 11 | 1811.7 | 164.7 | 161.7 | 0.0054781 | 1778.7 | 0.0053784 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | U34 | Replaced 2x 10Amp HV Links | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.0053784 | 3.3261e-05 | 2016 | 2016-03-10 | C | 11 | 0.0053784 | 3.3261e-05
10182270 | 2016-03-10 18:00 | 2016-03-11 10:49 | 1008.75 | 294 | 100500.8167 | 341.8395 | 338.8395 | 0.30389 | 99618.8167 | 0.30122 | 0.00088899 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 359180 | CB C945 found tripped O/C B & C Phase, as was Sectionaliser C423/2. CB C945 close/trip. Auto reclose function not working on CB C945 & requires investigation. Feeder sectionalised and patrolled and fault determined as being between ABS S333 & ABS S67. Lin | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.30122 | 0.00088899 | 2016 | 2016-03-10 | C | 294 | 0.30122 | 0.00088899
10182302 | 2016-03-10 20:44 | 2016-03-10 20:54 | 9.8 | 62 | 607.6 | 9.8 | 6.8 | 0.0018372 | 421.6 | 0.0012748 | 0.00018747 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3110 | 7.50pm - advise smc. 7.59pm - David from Fire Comms in Wellington advise the transformer is on fire now and they are now onsite. Event # F2035282. He was under the impression Contact Energy would have advised Powerco of the tx on fire. ETA required. 8.01 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.0012748 | 0.00018747 | 2016 | 2016-03-10 | C | 62 | 0.0012748 | 0.00018747
10182922 | 2016-03-11 07:46 | 2016-03-11 10:46 | 180 | 8 | 1439.0667 | 179.8833 | 176.8833 | 0.0043514 | 1415.0667 | 0.0042788 | 2.419e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2750 | Faultman replaced 2x 3Amp HV fuses but they have blown & Transformer T2750 is faulty. Requires replacement. OMS says transformer is T2980 but that is incorrect. Crew required to replace tomorrow. Believed to be 30kVA. This is Transformer T2750 | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.0042788 | 2.419e-05 | 2016 | 2016-03-11 | C | 8 | 0.0042788 | 2.419e-05
10183271 | 2016-03-10 21:34 | 2016-03-11 12:40 | 906.1167 | 179 | 162032.7167 | 905.2107 | 902.2107 | 0.48995 | 161495.7167 | 0.48832 | 0.00054125 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04338 | CB 3 A/R, L/O O/C A & B Phase. Next A/R flaggings became E/F. Sectionalised with fault being between Sub & ABS V54. Left off overnight as suspect line down and line is mainly cross country. Faultman to return at first light. Please also check 10187043 - | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.48832 | 0.00054125 | 2016 | 2016-03-10 | C | 179 | 0.48832 | 0.00054125
10183911 | 2016-03-10 23:05 | 2016-03-11 01:21 | 135.6667 | 61 | 8275.6667 | 135.6667 | 132.6667 | 0.025024 | 8092.6667 | 0.02447 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T41 | CB T41 A/R, L/O, E/F, O/C C Phase. Sectionalised & Patrolled with no fault found. 2r line patrol 2359 no 2r repair | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.02447 | 0.00018445 | 2016 | 2016-03-10 | C | 61 | 0.02447 | 0.00018445
10184006 | 2016-03-10 23:57 | 2016-03-11 03:17 | 199.6167 | 240 | 28978.6667 | 120.7444 | 117.7444 | 0.087625 | 28258.6667 | 0.085447 | 0.0007257 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773591 | CB 6 A/R, L/O, O/C A & B Phase. Sectionalised & Patrolled. Line down found & repaired. Materials used: 2x 11kV pins & insulators, 3mtrs squrrel conductor, 2 sleeves, 2 binders. 2r line patrol 0037. 2r repair 0058 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-03-10 | c | 0.085447 | 0.0007257 | 2016 | 2016-03-10 | C | 240 | 0.085447 | 0.0007257
10185271 | 2016-03-11 03:09 | 2016-03-11 12:39 | 569.6833 | 327 | 29088.9667 | 88.9571 | 85.9571 | 0.087958 | 28107.9667 | 0.084992 | 0.00098877 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | K1243 | Report from fire service Truck vs Pole at 2393 SH27 Tahuna. CB 4 had Auto reclosed. O/C A-B-C Phase, E/F. Feeder immediately de-energised for safety by NOC Operator when notified of accident. Accident location identified at pole 269952. HV ties on pole | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-11 | c | 0.084992 | 0.00098877 | 2016 | 2016-03-11 | C | 327 | 0.084992 | 0.00098877
10186804 | 2016-03-11 11:18 | 2016-03-11 12:21 | 62.7833 | 66 | 4143.7 | 62.7833 | 59.7833 | 0.01253 | 3945.7 | 0.011931 | 0.00019957 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | H1490 | Car v pole, Police comms, PO24511075. Also called in by Peter Malone. Pole H1490. 08:05 - ETA of 15 minutes given to police comms. NDR # 55705. Check 444 Landsdowne Rd - OMS 10187934. Line was isolated at ABS's 768 & 1206 to replace pole H1490 hit by car. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-11 | c | 0.011931 | 0.00019957 | 2016 | 2016-03-11 | C | 66 | 0.011931 | 0.00019957
10187402 | 2016-03-11 11:32 | 2016-03-11 14:05 | 153 | 1 | 153 | 153 | 150 | 0.00046264 | 150 | 0.00045356 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 228075 | Branch has hit an 11kV and 400V, knocked a DDO out. NDR #400101. This is to be used only to fix the no power fault. NOTE - The transformer replacement is to be treated as a separate part of the job. Fault man has requested a 2R, due to a rusted transforme | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-11 | c | 0.00045356 | 3.024e-06 | 2016 | 2016-03-11 | C | 1 | 0.00045356 | 3.0238e-06
10187414 | 2016-03-11 09:26 | 2016-03-11 11:40 | 134.7167 | 8 | 876.6667 | 109.5833 | 106.5833 | 0.0026508 | 852.6667 | 0.0025783 | 2.419e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6551/2 | Recloser 6551/2 tripped on A phase O/C flags, line was sectionalised and patrolled no found was found. 2r line patrol 1036. No repair. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.0025783 | 2.419e-05 | 2016 | 2016-03-11 | C | 8 | 0.0025783 | 2.419e-05
10187770 | 2016-03-11 11:37 | 2016-03-11 15:05 | 208 | 229 | 47632 | 208 | 205 | 0.14403 | 46945 | 0.14195 | 0.00069244 |  | 11 | Unplanned | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 1598 | Check for safety. Car has ran over gryo box. F2035669. Fire service require eta. 10.31am - advise Karen of 20 min eta. Fault man has asked for a 2R to help to move transformer. To be decided at invoicing level if meets criteria of 2R work after scope of w | F2/F3 | PORT RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-11 | c | 0.14195 | 0.00069244 | 2016 | 2016-03-11 | C | 229 | 0.14195 | 0.00069244
10188779 | 2016-03-11 13:01 | 2016-03-11 15:00 | 119.5 | 6 | 717 | 119.5 | 116.5 | 0.002168 | 699 | 0.0021136 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7435 | Advised SMC of 999. 2x 10 amp. cause: wind / trees | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.0021136 | 1.8143e-05 | 2016 | 2016-03-11 | C | 6 | 0.0021136 | 1.8143e-05
10188948 | 2016-03-11 13:08 | 2016-03-11 16:49 | 221.4333 | 113 | 21911.2 | 193.9044 | 190.9044 | 0.066254 | 21572.2 | 0.065229 | 0.00034168 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 837073 | Lines down due to trees felled by third party. NDR Number 21819. Used 35m 16mm Copper conductor | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.065229 | 0.00034168 | 2016 | 2016-03-11 | C | 113 | 0.065229 | 0.00034168
10189970 | 2016-03-11 14:31 | 2016-03-11 16:53 | 142.5 | 1 | 142.5 | 142.5 | 139.5 | 0.00043089 | 139.5 | 0.00042181 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7046 | Called SMC re update Glo to follow up. Adam cleared with Pete in conrtol at 5pm. x2 HV fuses due to bird strike 10amp - at HV fuse 7046. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.00042182 | 3.024e-06 | 2016 | 2016-03-11 | C | 1 | 0.00042181 | 3.0238e-06
10191078 | 2016-03-15 08:45 | 2016-03-16 16:24 | 1899 | 3 | 123 | 41 | 38 | 0.00037192 | 114 | 0.00034471 | 9.0713e-06 | NAPA ID:17956 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T13088 | Reconductor between pole structures T13088 and T1567 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-15 | b | 0.00017235 | 4.536e-06 | 2016 | 2016-03-15 | B | 3 | 0.00034471 | 9.0713e-06
10192223 | 2016-03-11 23:08 | 2016-03-11 23:35 | 27 | 48 | 1296 | 27 | 24 | 0.0039188 | 1152 | 0.0034834 | 0.00014514 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/285 | at 20:08, Pongaroa Sub, CB 4 Tiraumea Feeder. Faultman advised that jumper on top of DDO at Transformer T9/285 had blown. Requested to leave off overnight as believed that no customer lived at the property. Later, customer called in as someone was apparen | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.0034834 | 0.00014514 | 2016 | 2016-03-11 | C | 48 | 0.0034834 | 0.00014514
10193043 | 2016-03-11 17:57 | 2016-03-11 18:39 | 41.6667 | 59 | 2458.3333 | 41.6667 | 38.6667 | 0.0074334 | 2281.3333 | 0.0068982 | 0.0001784 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715983 | Broken cross arm on pole outside property, line looks like it is going to fall down pole. Craig 027 331 3559. Faultman found a cross arm that the nut had come off the kingpin and is loss, line was isolated at ABS's TA876, TA914, TA916 to replace kingpin n | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.0068982 | 0.0001784 | 2016 | 2016-03-11 | C | 59 | 0.0068982 | 0.0001784
10193095 | 2016-03-11 18:35 | 2016-03-11 20:37 | 122.1 | 54 | 6593.4 | 122.1 | 119.1 | 0.019937 | 6431.4 | 0.019447 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44645 | at 17:29 Kelvin Grove Sub, CB 8 Pohangina Feeder. Report came in of broken crossarm at Pole P44645. Isolate lines at ABS F67, Fuses E50 & ABS E46. Backfeed supplied from FEI 13, Closed ABS E31. Permit issued & repairs carried out. All Power restored on co | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.019447 | 0.00016328 | 2016 | 2016-03-11 | C | 54 | 0.019447 | 0.00016328
10193480 | 2016-03-11 19:10 | 2016-03-11 21:00 | 110 | 1 | 110 | 110 | 107 | 0.00033261 | 107 | 0.00032354 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2469 | 5pm called through to SMC - Shannon. Faultman requesting 2R for broken cross arm. 8:58pm follow up with SMC to see if Stu still onsite - Dianne to follow up. Found broken cross arm at pole N2469. Isolated at fuses FC2146, replaced arm and relivened. | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-03-11 | c | 0.00032354 | 3.024e-06 | 2016 | 2016-03-11 | C | 1 | 0.00032354 | 3.0238e-06
10195061 | 2016-03-11 19:17 | 2016-03-12 01:49 | 392.9167 | 1555 | 5066.35 | 3.2581 | 0.2581 | 0.015319 | 0 | 0 | 0.0047019 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3786 | at 18:44, Whareroa Sub. A lot of calls were coming in of Low Power/Part Power. Faultmen sent to Whareroa sub to investigate. Believed there was a blown jumper on the 33kV Line from Hawera to Whareroa (CB 412). Backfed sub via 11kV backfeeds from Cambria s | F1,F2,F3 | WHITE 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 2016-03-11 | c | 0 | 0.0047019 | 2016 | 2016-03-11 | C | 1555 | 0 | 0.0047019
10198662 | 2016-03-12 04:56 | 2016-03-12 11:05 | 368.9667 | 54 | 15377.9833 | 284.7775 | 281.7775 | 0.046499 | 15215.9833 | 0.046009 | 0.00016328 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | D1520 | Emergency switching to repair lines x 2 brought down by tree at pole D1520. Isolation at ABS 821 (spur no back feeds). Lines repaired all service restored. Materials 15 meters conductor, 6 x H/V sleeves. NDR Number to follow | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-03-12 | c | 0.046009 | 0.00016328 | 2016 | 2016-03-12 | C | 54 | 0.046009 | 0.00016328
10200630 | 2016-03-12 06:57 | 2016-03-12 11:40 | 283.4167 | 1142 | 16326.3667 | 14.2963 | 11.2963 | 0.049367 | 12900.3667 | 0.039008 | 0.0034531 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798398 | Tripping on Recloser CB C634 on E/F. Fault caused by conductor breaking midspan (Deteriated) and cusing grass fire underneath (Fire service on site). Isolationj between ABS S505 and S526 with backfeeds at CB C634 and VS 11035. 20m Conductor replaced with | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2016-03-12 | c | 0.039008 | 0.0034531 | 2016 | 2016-03-12 | C | 1142 | 0.039008 | 0.0034531
10200862 | 2016-03-12 07:52 | 2016-03-12 07:53 | 1.3 | 635 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0019201 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P366965 | Tripping on Pongaroa CB XT50 on Phase A-C O/C, E/F while carrying out switching on SIN 16776. This caused a short loss of Supply to Alfredton Sub and Parkville CB3 and CB4 which were being backfed. (CB XT50 was closed during the switching to supply Alfred | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-12 | c | 0 | 0.0019201 | 2016 | 2016-03-12 | C | 635 | 0 | 0.0019201
10203473 | 2016-03-12 12:21 | 2016-03-12 14:01 | 99.9 | 4 | 399.6 | 99.9 | 96.9 | 0.0012083 | 387.6 | 0.001172 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1482 | Replaced 2 x 6A H/V, O/H fuses ( line clash ) | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 2016-03-12 | c | 0.001172 | 1.2095e-05 | 2016 | 2016-03-12 | C | 4 | 0.001172 | 1.2095e-05
10203499 | 2016-03-12 12:45 | 2016-03-12 18:35 | 349.9167 | 3 | 668.0167 | 222.6722 | 219.6722 | 0.0020199 | 659.0167 | 0.0019927 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Fuses SF6 026 Open & tagged due to possible cable fault ( low readings ) Generator to be connected until cable fault resolved. 18 march finished. abs fuses and cable used . ndr | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-12 | c | 0.0019927 | 9.071e-06 | 2016 | 2016-03-12 | C | 3 | 0.0019927 | 9.0713e-06
10204340 | 2016-03-12 22:35 | 2016-03-13 00:12 | 97.1667 | 327 | 25774.5667 | 78.8213 | 75.8213 | 0.077936 | 24793.5667 | 0.07497 | 0.00098877 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 01516 | Sectionalised & found possum on pole 01516. removed possum & relivened | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2016-03-12 | c | 0.07497 | 0.00098877 | 2016 | 2016-03-12 | C | 327 | 0.07497 | 0.00098877
10209045 | 2016-03-13 23:36 | 2016-03-14 01:59 | 143.9 | 776 | 45248.45 | 58.3099 | 55.3099 | 0.13682 | 42920.45 | 0.12978 | 0.0023464 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701857 | CB7 tripped on C phase E/F. 1 x H/T Insulator at Pole 701857 | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-13 | c | 0.12978 | 0.0023464 | 2016 | 2016-03-13 | C | 776 | 0.12978 | 0.0023464
10211715 | 2016-03-14 04:05 | 2016-03-14 10:05 | 360.0833 | 178 | 47186.9333 | 265.0951 | 262.0951 | 0.14268 | 46652.9333 | 0.14107 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809540 | Burnt Cross arm found at Pole 809540 during sectionlising, Isolated at ABS 4462/1 and Links 4462/6. Used 2 x HV insulators and pins and 4 mtrs of binder. Faultman to defect crossarms | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.14107 | 0.00053823 | 2016 | 2016-03-14 | C | 178 | 0.14107 | 0.00053823
10212086 | 2016-03-14 07:40 | 2016-03-14 09:40 | 120.1667 | 3 | 360.5 | 120.1667 | 117.1667 | 0.0010901 | 351.5 | 0.0010629 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4019 | 2 Fuses found Blown at Fuses 4019 - cause unknown. Used 2 x 8 amp fuses. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.0010629 | 9.071e-06 | 2016 | 2016-03-14 | C | 3 | 0.0010629 | 9.0713e-06
10212205 | 2016-03-14 08:34 | 2016-03-14 10:07 | 93.0333 | 1 | 93.0333 | 93.0333 | 90.0333 | 0.00028131 | 90.0333 | 0.00027224 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | oms 10212086 possibly relates | Fault man check customer as part of OMS 10212086 with no fault found and customer had not contacted supplier | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.00027224 | 3.024e-06 | 2016 | 2016-03-14 | C | 1 | 0.00027224 | 3.0238e-06
10212210 | 2016-03-14 08:42 | 2016-03-14 17:56 | 553.8167 | 623 | 36643.3667 | 58.8176 | 55.8176 | 0.1108 | 34774.3667 | 0.10515 | 0.0018838 |  | 11 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | R47 | Tripping caused by incorrect phasing at ABS R47 after changes made in planned switching NAPA 17908. ICPs on this one are included in 10219032. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.10515 | 0.0018838 | 2016 | 2016-03-14 | C | 623 | 0.10515 | 0.0018838
10212275 | 2016-03-14 08:40 | 2016-03-14 11:03 | 142.7 | 6 | 79.7833 | 13.2972 | 10.2972 | 0.00024125 | 61.7833 | 0.00018682 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X40 | replaced 2 x 5 amp ht fuses. Power off: 9.00 - this is when FM received the job. Power on: 10.00am. Cause: unknown but suspect possible line clash due to rain and wind over night. tx X40 and pole 782688. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.00018682 | 1.8143e-05 | 2016 | 2016-03-14 | C | 6 | 0.00018682 | 1.8143e-05
10212369 | 2016-03-14 10:35 | 2016-03-14 18:48 | 493 | 2 | 986 | 493 | 490 | 0.0029814 | 980 | 0.0029633 | 6.0475e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SD5-239 | Revitaliser Fertiliser. 1km down the road from Downer depot. Yardsman from this property walek in the door to advise the pillar box has buned down and no power since early yeaterday morning. Dave James on 02747185058 2R - Damaged Transformer (possibly nee | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 2016-03-14 | c | 0.0029633 | 6.048e-06 | 2016 | 2016-03-14 | C | 2 | 0.0029633 | 6.0475e-06
10213207 | 2016-03-14 09:46 | 2016-03-14 18:28 | 522.1 | 578 | 30006.7 | 51.9147 | 48.9147 | 0.090733 | 28272.7 | 0.08549 | 0.0017477 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 217017 | Recloser 13004 A/R E/F Sectionaliser 9208 Tripped. lines down past fuses SF 3-003 due to farmer & digger. Isolation at fuses SF3-003 No back feeds available. Material 1x15kVA 2 phase transformer, 1x 11m concrete pole 1x double strain arm, insulators & po | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-14 | c | 0.08549 | 0.0017477 | 2016 | 2016-03-14 | C | 578 | 0.08549 | 0.0017477
10220065 | 2016-03-14 20:25 | 2016-03-14 22:01 | 96.2667 | 1 | 96.2667 | 96.2667 | 93.2667 | 0.00029109 | 93.2667 | 0.00028202 | 3.0238e-06 |  | 22 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2962 | 2 HT fuses found tripped at 2962. Relivened OK. Bird strike. (Rating 6A). | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-14 | c | 0.00028202 | 3.024e-06 | 2016 | 2016-03-14 | C | 1 | 0.00028202 | 3.0238e-06
10220913 | 2016-03-15 07:35 | 2016-03-15 08:47 | 72.2667 | 3 | 216.8 | 72.2667 | 69.2667 | 0.00065555 | 207.8 | 0.00062834 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4019 | Reload Reliven 2 x 8A Fuses, no cause | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-15 | c | 0.00062834 | 9.071e-06 | 2016 | 2016-03-15 | C | 3 | 0.00062834 | 9.0713e-06
10270038 | 2016-03-11 12:20 | 2016-03-11 12:45 | 25 | 4 | 100 | 25 | 22 | 0.00030238 | 88 | 0.00026609 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE |  | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 2016-03-11 | c | 0.00026609 | 1.2095e-05 | 2016 | 2016-03-11 | C | 4 | 0.00026609 | 1.2095e-05
10270098 | 2016-03-22 09:47 | 2016-03-22 15:09 | 322 | 3 | 966 | 322 | 319 | 0.002921 | 957 | 0.0028937 | 9.0713e-06 | NAPA ID:16240 TP_MATAROA GXP > WAIOURU SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 168 | replace 33 xarms and 5 poles on waiouru 33 kv feeder from pole no 779134 to 779010 end of line. Works location: Hwy 1, Taihape Waiouru. WO 30001181 | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2016-03-22 | b | 0.0014469 | 4.536e-06 | 2016 | 2016-03-22 | B | 3 | 0.0028937 | 9.0713e-06
10270261 | 2016-03-31 09:05 | 2016-03-31 15:51 | 406 | 18 | 7308 | 406 | 403 | 0.022098 | 7254 | 0.021934 | 5.4428e-05 | NAPA ID:16204 TP_TAURANGA 33 GXP | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 205659 | Replace poles, hardware and conductor between poles 205659 & 205669. Works location: Wainui South Rd. WO 30015247 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-03-31 | b | 0.010967 | 2.7214e-05 | 2016 | 2016-03-31 | B | 18 | 0.021934 | 5.4428e-05
10270758 | 2016-03-19 09:06 | 2016-03-19 15:10 | 364 | 1 | 364 | 364 | 361 | 0.0011006 | 361 | 0.0010916 | 3.0238e-06 | NAPA ID:18032 TP_TE MATAI GXP > TE PUKE SUB > MOEHAU ST | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | Connect new RMU 13027/1 to existing RMU 9971/3. Connect existing RMU SE5-150 to RMU 13027/3. Cable between 9971/3 and 9972/1 disconnected. TP2899 and TP2898 Livened & commissioned. | F3 | MOEHAU ST | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-19 | b | 0.00054579 | 1.512e-06 | 2016 | 2016-03-19 | B | 1 | 0.0010916 | 3.0238e-06
10271415 | 2016-03-23 08:41 | 2016-03-23 15:39 | 418 | 126 | 52108 | 413.5556 | 410.5556 | 0.15756 | 51730 | 0.15642 | 0.00038099 | NAPA ID:17484 TP_MANGAMAIRE GXP > MANGAMUTU SUB | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | VS10237 | (Scarbrough Rd)11kV isolation is for safety, work will be on the new 33kV line above.(Bridge Rd) Reconfigure 11kV new section to correct phasing issue beyond ABS R47. Install new links 10237/4 on source side of VS 10237 - Complete cable terminations at | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-23 | b | 0.07821 | 0.0001905 | 2016 | 2016-03-23 | B | 126 | 0.15642 | 0.00038099
10271933 | 2016-03-15 21:34 | 2016-03-15 22:39 | 65.9 | 18 | 1186.2 | 65.9 | 62.9 | 0.0035868 | 1132.2 | 0.0034235 | 5.4428e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | V83 | Advised control and SMC of 999 . 2 HT fuses found tripped at V83. Reloaded OK. (10A Rating) | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-15 | c | 0.0034235 | 5.4428e-05 | 2016 | 2016-03-15 | C | 18 | 0.0034235 | 5.4428e-05
10272439 | 2016-03-16 01:11 | 2016-03-16 03:02 | 110.65 | 320 | 26458.5333 | 82.6829 | 79.6829 | 0.080004 | 25498.5333 | 0.077101 | 0.0009676 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB C830 | CB C830 Weraiti feeder auto-reclosed. Flags Phase A-B E/F. Feeder patrolled and sectionalised but nothing found. All restored OK. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.077101 | 0.0009676 | 2016 | 2016-03-16 | C | 320 | 0.077101 | 0.0009676
10272802 | 2016-03-16 02:46 | 2016-03-16 05:11 | 145.0667 | 61 | 7833.4167 | 128.4167 | 125.4167 | 0.023686 | 7650.4167 | 0.023133 | 0.00018445 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2386T | Tripping on 11kV CBT41 on Phase A-C O/C, E/F. Patrol carried out. Suspect HT fuse at Transformer 2386T. Fuses removed and feeder restored. Further insulator started to flare up. Feeder isolated from ABS 6069 to ABS 5715 and repairs carried out. (1 HT fuse | F4 | PALMER RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.023133 | 0.00018445 | 2016 | 2016-03-16 | C | 61 | 0.023133 | 0.00018445
10275142 | 2016-03-16 10:39 | 2016-03-16 10:42 | 3.0333 | 3391 | 9217.2 | 2.7181 | -0.28186 | 0.027871 | 0 | 0 | 0.010254 |  | 33 | Unplanned | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 40 | Human error - Bucholtz CB40 trip causing LOS to all feeders from Paeroa Substation when working on adjacent T1 under planned works NAPA 16415. Safety Manager 604156. | F1,F2,F3 | WAIKINO242-PAEROA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 2016-03-16 | c | 0 | 0.010254 | 2016 | 2016-03-16 | C | 3391 | 0 | 0.010254
10280756 | 2016-03-16 11:45 | 2016-03-16 13:15 | 89.5167 | 4 | 358.0667 | 89.5167 | 86.5167 | 0.0010827 | 346.0667 | 0.0010464 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1666 | 2 x 10A HV Fuses. Suspect Bird Strike | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-03-16 | c | 0.0010464 | 1.2095e-05 | 2016 | 2016-03-16 | C | 4 | 0.0010464 | 1.2095e-05
10280998 | 2016-03-16 13:43 | 2016-03-16 13:50 | 7.0667 | 46 | 325.0667 | 7.0667 | 4.0667 | 0.00098292 | 187.0667 | 0.00056564 | 0.00013909 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 769140 | At TX X3073 on pole 769140 the HV line has come away from the pole opp 101 Alma Rd. Please check for safety as this is next door to Gonzille Kindergaten called in by Mike 027 706 8908. 12:34pm called through to SMC - Tallia. 13.25 FM called to reque | F3 | CARLTON | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.00056565 | 0.00013909 | 2016 | 2016-03-16 | C | 46 | 0.00056564 | 0.00013909
10281333 | 2016-03-16 12:36 | 2016-03-17 14:45 | 1568.8833 | 120 | 10132.7 | 84.4392 | 81.4392 | 0.030639 | 9772.7 | 0.02955 | 0.00036285 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P30095 - SEE TRAVIS TO FIND OUT WHERE PAPER WORK IS FOR THIS JOB | Please check poss related OMS: 10282664 (1652 GLENORA ROAD and 1508 River Road) from tap level V45 Tree found across lines unable to clear before it got to dark to work safely Temp Line break made at Pole P04968 Transformer T9/143 off line Over Night Cus | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.02955 | 0.00036285 | 2016 | 2016-03-16 | C | 120 | 0.02955 | 0.00036285
10281437 | 2016-03-16 13:40 | 2016-03-17 00:10 | 629.8167 | 308 | 162030.2667 | 526.0723 | 523.0723 | 0.48994 | 161106.2667 | 0.48715 | 0.00093132 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797194 | Isolated at Links C639/6 and ABS C639/1 - Recloser C637 Closed. Complete Structure at Transformer T1501 replaced (Pole Crossarms ETC) Also Pole Replaced at Pole 797194. Faultman to Supply full list of Materials used Have advised SMC and asked for ETA. Cus | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.48715 | 0.00093132 | 2016 | 2016-03-16 | C | 308 | 0.48715 | 0.00093132
10282839 | 2016-03-16 15:58 | 2016-03-16 16:50 | 52.3 | 1099 | 57399.1667 | 52.2285 | 49.2285 | 0.17356 | 54102.1667 | 0.16359 | 0.0033231 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 847527 | Feeder sectionalised to restore Dairy Factory. Following report from contractor trees were removed from the lines with hot sticks. No damage to the lines, restored OK. NDR 30469. | F2 | GILBERD ST | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.16359 | 0.0033231 | 2016 | 2016-03-16 | C | 1099 | 0.16359 | 0.0033231
10284917 | 2016-03-17 00:09 | 2016-03-17 03:47 | 218.2667 | 218 | 47582.1333 | 218.2667 | 215.2667 | 0.14388 | 46928.1333 | 0.1419 | 0.00065918 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 205309 | Car vs pole and there are lines down, not sure if its on the vehicle (1 person trapped in vehicle), cannot proceed until Powerco are onsite Casey - Fire comms Auckland F2039669 ETA required - SMC advised 15mins ans FM coming from Papamoa - Fire Comms advi | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-03-17 | c | 0.1419 | 0.00065918 | 2016 | 2016-03-17 | C | 218 | 0.1419 | 0.00065918
10284939 | 2016-03-16 22:59 | 2016-03-17 02:02 | 183.0833 | 1535 | 116121.5 | 75.6492 | 72.6492 | 0.35112 | 111516.5 | 0.3372 | 0.0046415 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6824 | CB 8 Tripped Ph A,B,C O/C E/F - Arcing line reported by Public. Broken dead end found at ABS 6824 - Isolated at Links CA722, ABS's CA787, 6807 and CA112. Used 1 x dead end. On restoring feeder Link Broke at Links CA722 _ Isolated at Sw/Gear CA703, ABS's C | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 2016-03-16 | c | 0.3372 | 0.0046415 | 2016 | 2016-03-16 | C | 1535 | 0.3372 | 0.0046415
10287072 | 2016-03-17 02:56 | 2016-03-17 10:28 | 451.9167 | 362 | 119559.9 | 330.276 | 327.276 | 0.36152 | 118473.9 | 0.35824 | 0.0010946 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 808756 | Replace 1 x 33kV Insulator at pole 808756 | F1,F2,F3 | PAHAUTEA 33KV TIE | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 2016-03-17 | c | 0.35824 | 0.0010946 | 2016 | 2016-03-17 | C | 362 | 0.35824 | 0.0010946
10288922 | 2016-03-17 10:50 | 2016-03-17 13:00 | 130 | 17 | 2210 | 130 | 127 | 0.0066825 | 2159 | 0.0065283 | 5.1404e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/341 | Blown jumper reported by passing FM at Transformer T7/341. 1R Request to repair. Outage required between ABS T28 & Recloser T42. Backfeed from PON1 via ABS V19. Jumper repaired, relivened OK | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-17 | c | 0.0065283 | 5.1404e-05 | 2016 | 2016-03-17 | C | 17 | 0.0065283 | 5.1404e-05
10289963 | 2016-03-17 14:35 | 2016-03-17 15:00 | 25 | 7 | 175 | 25 | 22 | 0.00052916 | 154 | 0.00046566 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11678 | Call from public to advise there is a cross arm hanging from a power pole and it may just need another bolt to fix it. This power pole is in a paddock at No.3 Line in the Pohangina Valley. The pole is in the paddock about 3-4km before the end of No.3 Line | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2016-03-17 | c | 0.00046566 | 2.1166e-05 | 2016 | 2016-03-17 | C | 7 | 0.00046566 | 2.1166e-05
10290027 | 2016-03-17 13:18 | 2016-03-17 20:16 | 418.1 | 135 | 18273 | 135.3556 | 132.3556 | 0.055253 | 17868 | 0.054029 | 0.00040821 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01713 | Recloser P61 tripped B & C Phase OC EF, line was patrolled and sectionalised and a broken cross arm was found on ple P01713, line was isolated at ABS's N41 & N43 to replace the cross arm. 1 X 11KV X-arm & all its hardware & stays. 12r line patrol 1400. 2r | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-17 | c | 0.054029 | 0.00040821 | 2016 | 2016-03-17 | C | 135 | 0.054029 | 0.00040821
10291137 | 2016-03-18 11:52 | 2016-03-18 15:04 | 191.8333 | 10 | 1918.3333 | 191.8333 | 188.8333 | 0.0058006 | 1888.3333 | 0.0057099 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 746577 | Advised control and SMC of 999. Car vs pole, pole cracked at bottom. Cnr Corbett Road and Manutahi Road. Event # P024579073. Could not specified whether a eta is required. Used closest ICP to log emergency job. 4.40pm Neil called to advise that NDR # 4755 | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-18 | c | 0.0057099 | 3.0238e-05 | 2016 | 2016-03-18 | C | 10 | 0.0057099 | 3.0238e-05
10291842 | 2016-03-17 15:47 | 2016-03-17 16:32 | 45 | 585 | 26325 | 45 | 42 | 0.079601 | 24570 | 0.074294 | 0.0017689 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | V1333 | RP15 L/O on E/F. 4.24pm advised Control about sparking line contact hazard. Removed bark from pole V1333, relivened | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-17 | c | 0.074294 | 0.0017689 | 2016 | 2016-03-17 | C | 585 | 0.074294 | 0.0017689
10294436 | 2016-03-17 17:19 | 2016-03-17 18:46 | 87.5 | 379 | 28633.95 | 75.5513 | 72.5513 | 0.086582 | 27496.95 | 0.083144 | 0.001146 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB PU2 | CB PU2 tripped on E/F , O/C A, B & C phase, line was patrolled ans sectionalised ans no fault was found. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-17 | c | 0.083144 | 0.001146 | 2016 | 2016-03-17 | C | 379 | 0.083144 | 0.001146
10305030 | 2016-03-18 05:50 | 2016-03-18 09:48 | 238.2167 | 1 | 238.2167 | 238.2167 | 235.2167 | 0.00072031 | 235.2167 | 0.00071124 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 5016E | Suspect Customers ICP is on Transformer M3220. Transformer 5016E is being replaced because it feeds the customers cow shed. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-18 | c | 0.00071124 | 3.024e-06 | 2016 | 2016-03-18 | C | 1 | 0.00071124 | 3.0238e-06
10305091 | 2016-03-18 07:15 | 2016-03-18 08:51 | 95.6333 | 779 | 35774.3167 | 45.9234 | 42.9234 | 0.10817 | 33437.3167 | 0.10111 | 0.0023555 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | MRA3 | Moturoa CB 3 Tripped on E/F. Sectionalised & Patrolled with no fault found. 2r line patrol 0743 2r repair no fault found | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2016-03-18 | c | 0.10111 | 0.0023555 | 2016 | 2016-03-18 | C | 779 | 0.10111 | 0.0023555
10306852 | 2016-03-23 10:04 | 2016-03-23 13:24 | 200.1833 | 55 | 11010.0833 | 200.1833 | 197.1833 | 0.033292 | 10845.0833 | 0.032793 | 0.00016631 | NAPA ID:17936 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1633 | We have a planned L/V shut on TC1633 Ref 2735, Need to have 11kv between pole R12760 to Fc1467 isolated for live line work at pole R12760 and safely replace all hard wear. Works location: Given Rd, Whangamata. WO 30003265 | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-23 | b | 0.016396 | 8.3153e-05 | 2016 | 2016-03-23 | B | 55 | 0.032793 | 0.00016631
10308617 | 2016-03-18 10:00 | 2016-03-18 13:43 | 222.5667 | 23 | 5119.0333 | 222.5667 | 219.5667 | 0.015479 | 5050.0333 | 0.01527 | 6.9546e-05 |  | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 783444 | Planned NAPA 18158 to replace defect Pole 783444 on Parapara Rd. WO 30014334 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-03-18 | b | 0.007635 | 3.4773e-05 | 2016 | 2016-03-18 | B | 23 | 0.01527 | 6.9546e-05
10312452 | 2016-03-18 11:26 | 2016-03-18 16:27 | 300.75 | 160 | 16178.7667 | 101.1173 | 98.1173 | 0.048921 | 15698.7667 | 0.047469 | 0.0004838 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 229074 | Recloser 9556 L/O Sectionalised & found 2 lines down at pole 229074 Isolated at SF7-025. Repaired lines & relivened. 10 meters 0f wire & 9 joints used. 2r line patrol 1210. 2r repair 1243 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-03-18 | c | 0.047469 | 0.0004838 | 2016 | 2016-03-18 | C | 160 | 0.047469 | 0.0004838
10319802 | 2016-03-18 14:43 | 2016-03-18 17:24 | 160.3167 | 379 | 33284.8667 | 87.8229 | 84.8229 | 0.10065 | 32147.8667 | 0.097207 | 0.001146 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | PU2 - Pungarehu - E/F A Phase. Sectionalised & Patrolled with no fault found. 2r line patrol 1605. 2r repair no fault found | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-18 | c | 0.097207 | 0.001146 | 2016 | 2016-03-18 | C | 379 | 0.097207 | 0.001146
10322945 | 2016-03-18 17:06 | 2016-03-18 19:16 | 130.45 | 2 | 226.1833 | 113.0917 | 110.0917 | 0.00068392 | 220.1833 | 0.00066578 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/159 | Check to see if OMS 10323007 (2950 POHANGINA VALLEY EAST ROAD) is related | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-18 | c | 0.00066578 | 6.048e-06 | 2016 | 2016-03-18 | C | 2 | 0.00066578 | 6.0475e-06
10323750 | 2016-03-19 11:36 | 2016-03-19 13:15 | 99 | 14 | 1386 | 99 | 96 | 0.0041909 | 1344 | 0.0040639 | 4.2333e-05 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P04968 | Cut away trees from Pole P04968 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2016-03-19 | c | 0.0040639 | 4.2333e-05 | 2016 | 2016-03-19 | C | 14 | 0.0040639 | 4.2333e-05
10325357 | 2016-03-19 20:14 | 2016-03-19 22:19 | 125.2667 | 1 | 125.2667 | 125.2667 | 122.2667 | 0.00037878 | 122.2667 | 0.00036971 | 3.0238e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 579 | Replaced 2x 8 Amp HV Fuses | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-19 | c | 0.00036971 | 3.024e-06 | 2016 | 2016-03-19 | C | 1 | 0.00036971 | 3.0238e-06
10325862 | 2016-03-20 14:15 | 2016-03-20 16:00 | 105 | 3 | 315 | 105 | 102 | 0.00095248 | 306 | 0.00092527 | 9.0713e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/224 | Fault caused by defective Transformer T5/224. Transformer replaced 15kVA and relivened / tested OK. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-20 | c | 0.00092527 | 9.071e-06 | 2016 | 2016-03-20 | C | 3 | 0.00092527 | 9.0713e-06
10327111 | 2016-03-20 14:00 | 2016-03-20 21:05 | 425 | 70 | 29750 | 425 | 422 | 0.089957 | 29540 | 0.089322 | 0.00021166 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 10172/4 | Reports of no power / part power found a fuse had tripped at Fuse/Sw 10172/4. Further tests proved we had an 11kV Cable fault. The decision was made to fully replace the Cable (Work had been planned for next week and Cable was ready). Cable replaced and a | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2016-03-20 | c | 0.089322 | 0.00021166 | 2016 | 2016-03-20 | C | 70 | 0.089322 | 0.00021166
10327338 | 2016-03-20 15:20 | 2016-03-20 16:00 | 40 | 3 | 120 | 40 | 37 | 0.00036285 | 111 | 0.00033564 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | I0274 | Replace 2 x 6A H/V, O/H fuses at Fuses FP642. Branch removed from lines at pole I0274. Defect No 93475 - tree requires cutting at pole I0274. | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-03-20 | c | 0.00033564 | 9.071e-06 | 2016 | 2016-03-20 | C | 3 | 0.00033564 | 9.0713e-06
10327357 | 2016-03-20 14:46 | 2016-03-20 16:02 | 76.0333 | 593 | 45087.7667 | 76.0333 | 73.0333 | 0.13633 | 43308.7667 | 0.13096 | 0.0017931 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 797686 | Ron advised twig lying across two lines at 2552 Lake Ferry Road. Control advised. Branch removed outside 2552 Lake ferry Rd - Wind Blown. Relivened OK. (No Damage). 1r feeder fault branch removed from line no 2r | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 2016-03-20 | c | 0.13096 | 0.0017931 | 2016 | 2016-03-20 | C | 593 | 0.13096 | 0.0017931
10327997 | 2016-03-20 16:55 | 2016-03-20 17:40 | 45 | 198 | 8910 | 45 | 42 | 0.026942 | 8316 | 0.025146 | 0.0005987 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 821232 | Outage required between ABS S370 and S365 to replace 3 broken HV fuse holders (T1447). Repaired OK. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-03-20 | c | 0.025146 | 0.00059871 | 2016 | 2016-03-20 | C | 198 | 0.025146 | 0.0005987
10328145 | 2016-03-20 16:34 | 2016-03-20 17:02 | 27.9 | 1 | 27.9 | 27.9 | 24.9 | 8.4363e-05 | 24.9 | 7.5292e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | X135 | Notes from contact: Car vs pole last night - pole seemed sound last night but police have now reassessed. Follow the skidmarks and the white paint to find the correct pole mkh508@police.govt.nz for more details (e.g. if need driver details for NDR) Adv | F3 | PITT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2016-03-20 | c | 7.5292e-05 | 3.024e-06 | 2016 | 2016-03-20 | C | 1 | 7.5292e-05 | 3.0238e-06
10328535 | 2016-03-20 19:23 | 2016-03-22 22:47 | 3083.8167 | 47 | 7552.05 | 160.6819 | 157.6819 | 0.022836 | 7411.05 | 0.022409 | 0.00014212 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 8733 | This is back feed from Transformer 5255E and has been for some time Fuses 8733 Fuses 8733 Should have been open 7 Tagged but only 1 was open Dennis Embling was on the job that Back feed this when it was done THe cable between Fuses 8733 & Transofrmer L | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2016-03-20 | c | 0.022409 | 0.00014212 | 2016 | 2016-03-20 | C | 47 | 0.022409 | 0.00014212
10328738 | 2016-03-20 21:34 | 2016-03-20 22:07 | 33.1333 | 379 | 719.8333 | 1.8993 | -1.1007 | 0.0021766 | 0 | 0 | 0.001146 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 604 | Found ABS 604 sparking badly. CB 3 was opened, ABS was then opened & relosed then CB 3 reclosed. ABS looked OK. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-20 | c | 0 | 0.001146 | 2016 | 2016-03-20 | C | 379 | 0 | 0.001146
10329354 | 2016-03-21 07:30 | 2016-03-21 14:00 | 389.6833 | 3 | 1107.15 | 369.05 | 366.05 | 0.0033478 | 1098.15 | 0.0033205 | 9.0713e-06 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SA2-022 | HV Cable fault. Cable repaired by Tom. Generator on Transformer TA2-063 at 14:00 21/03/16. 1321 Wayne clearing site, Tom will sign job off. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2016-03-21 | c | 0.0033205 | 9.071e-06 | 2016 | 2016-03-21 | C | 3 | 0.0033205 | 9.0713e-06
10329414 | 2016-03-21 07:46 | 2016-03-21 08:02 | 15.6 | 143 | 2230.8 | 15.6 | 12.6 | 0.0067454 | 1801.8 | 0.0054482 | 0.0004324 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Recloser RP 11 tripped on under volts when backfeeding up to SE6-012 NAPA 17887. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-21 | c | 0.0054482 | 0.0004324 | 2016 | 2016-03-21 | C | 143 | 0.0054482 | 0.0004324
10339808 | 2016-03-21 17:25 | 2016-03-21 17:51 | 26 | 133 | 3458 | 26 | 23 | 0.010456 | 3059 | 0.0092497 | 0.00040216 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7162 | Paengaroa CB 3 Between ABS's SE7-029 and SE7-031. 11.03am - advise smc. HV Joints Tightened at Transformer TE7162 | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-21 | c | 0.0092497 | 0.00040216 | 2016 | 2016-03-21 | C | 133 | 0.0092497 | 0.00040216
10340353 | 2016-03-21 11:28 | 2016-03-21 12:43 | 75.1167 | 445 | 23299.9333 | 52.3594 | 49.3594 | 0.070453 | 21964.9333 | 0.066417 | 0.0013456 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2 | CB 2 Trip. O/C. INVT L/O. Feeder sectionalised. No Fault Found. 2r line patrol 1204 2 r repair nothing founfd | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 2016-03-21 | c | 0.066417 | 0.0013456 | 2016 | 2016-03-21 | C | 445 | 0.066417 | 0.0013456
10343381 | 2016-03-30 08:45 | 2016-03-30 14:43 | 358 | 133 | 47614 | 358 | 355 | 0.14397 | 47215 | 0.14277 | 0.00040216 | NAPA ID:17656 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G12413 | Replace pole G12413 and G12411. Works Location: 32 Peria Road, Matamata. W/O 30002466 | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2016-03-30 | b | 0.071383 | 0.00020108 | 2016 | 2016-03-30 | B | 133 | 0.14277 | 0.00040216
10343498 | 2016-03-21 15:09 | 2016-03-21 15:52 | 43.4167 | 71 | 3082.5833 | 43.4167 | 40.4167 | 0.009321 | 2869.5833 | 0.0086769 | 0.00021469 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 378780 | Tripping on CB12 on Phase C O/C and EF. Fault caused by Contractor clashing line with digger. Area inspected 7 no damage found. Reclosed OK. Contractor details ":Composting NZ Ltd". Ph 0800 888200. NDR N300174. Safety Manager: 605325 | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-03-21 | c | 0.0086769 | 0.00021469 | 2016 | 2016-03-21 | C | 71 | 0.0086769 | 0.00021469
10343787 | 2016-03-21 15:16 | 2016-03-21 17:14 | 117.2333 | 394 | 33110.4 | 84.0365 | 81.0365 | 0.10012 | 31928.4 | 0.096544 | 0.0011914 |  | 11 | Unplanned | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | K13 | Recloser K13 Tripped on PH B & PH C OC. Feeder patrolled / sectionalised but nothing found. Restored OK. 2r line patrol 1614. 2r repair nothing found | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-03-21 | c | 0.096544 | 0.0011914 | 2016 | 2016-03-21 | C | 394 | 0.096544 | 0.0011914
10344421 | 2016-03-21 15:24 | 2016-03-21 16:50 | 86.3333 | 20 | 1726.6667 | 86.3333 | 83.3333 | 0.005221 | 1666.6667 | 0.0050396 | 6.0475e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 12109 | Truck from Taranaki Civil construction contacted lines while spreading metal. 2 fuses blown at 12109. No CAC for site. Fuses reloaded & livened. Driver Dean Corkill, NDR 47557. Safety Manager: 605219 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-03-21 | c | 0.0050396 | 6.0475e-05 | 2016 | 2016-03-21 | C | 20 | 0.0050396 | 6.0475e-05
10347213 | 2016-03-21 17:30 | 2016-03-21 18:23 | 53 | 52 | 2756 | 53 | 50 | 0.0083335 | 2600 | 0.0078618 | 0.00015724 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716671 | King bolt out at pole 716671. Isolation at ABS MA239 & MA170 to straighten crossarm. No Back feeds available. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-21 | c | 0.0078618 | 0.00015724 | 2016 | 2016-03-21 | C | 52 | 0.0078618 | 0.00015724
10348626 | 2016-03-22 00:56 | 2016-03-22 04:27 | 210.85 | 257 | 23961.0167 | 93.2335 | 90.2335 | 0.072452 | 23190.0167 | 0.070121 | 0.00077711 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 819201 | Small bit of Branch on line at Pole 819201 Not sure if that is what it was. 2r line patrol 0139. 2r repair branch removed by hot stick | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.070121 | 0.00077711 | 2016 | 2016-03-22 | C | 257 | 0.070121 | 0.00077711