10357518 | 2016-03-22 01:39 | 2016-03-22 02:20 | 40.9167 | 1 | 40.9167 | 40.9167 | 37.9167 | 0.00012372 | 37.9167 | 0.00011465 | 3.0238e-06 |  | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4350W | Bird On Top Of Transformer, 4350W Replaced 2 x 3amp fuses. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.00011465 | 3.024e-06 | 2016 | 2016-03-22 | C | 1 | 0.00011465 | 3.0238e-06
10359133 | 2016-03-22 07:07 | 2016-03-22 10:10 | 182.7833 | 257 | 4 | 0.015564 | -2.9844 | 1.2095e-05 | 0 | 0 | 0.00077711 |  | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | T4031 | Branch removed from Lines at Transformer T4031. 2r line patrol from start. Flag - Protection Trip. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0 | 0.00077711 | 2016 | 2016-03-22 | C | 257 | 0 | 0.00077711
10359494 | 2016-03-22 07:49 | 2016-03-22 09:10 | 80.9167 | 1 | 80.9167 | 80.9167 | 77.9167 | 0.00024467 | 77.9167 | 0.0002356 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | K78 | Reload Reliven at Fuses K78. 2 x 6A Fuses and 1 x Candle. Cause: Bird Strike. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.0002356 | 3.024e-06 | 2016 | 2016-03-22 | C | 1 | 0.0002356 | 3.0238e-06
10359591 | 2016-03-22 08:11 | 2016-03-22 08:15 | 4.0667 | 2 | 8.1333 | 4.0667 | 1.0667 | 2.4593e-05 | 2.1333 | 6.4507e-06 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7150 | 2 x 6amp fuses unknown | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2016-03-22 | c | 6.451e-06 | 6.048e-06 | 2016 | 2016-03-22 | C | 2 | 6.4507e-06 | 6.0475e-06
10361266 | 2016-03-22 11:07 | 2016-03-22 12:20 | 72.7667 | 11 | 800.4333 | 72.7667 | 69.7667 | 0.0024203 | 767.4333 | 0.0023205 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7614 | Advised control and SMC of 999. Reload Reliven 2 x 15 A Fuses. Cause: Bird Strike. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.0023205 | 3.3261e-05 | 2016 | 2016-03-22 | C | 11 | 0.0023205 | 3.3261e-05
10361317 | 2016-03-22 10:46 | 2016-03-22 12:48 | 122 | 11 | 1342 | 122 | 119 | 0.0040579 | 1309 | 0.0039581 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | PU355 | 2x10amp HV fuses blown at PU355. Line patrolled fuses reloaded & livened suspect bird strike. | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.0039581 | 3.3261e-05 | 2016 | 2016-03-22 | C | 11 | 0.0039581 | 3.3261e-05
10361476 | 2016-03-22 12:00 | 2016-03-22 12:26 | 26 | 3 | 78 | 26 | 23 | 0.00023585 | 69 | 0.00020864 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 8168 | Check for safety, truck has hit lines, lines are down. Driver is out but truck is still touching lines. Contact; Rebecca 0275218341 11.42 have advised Shannon at svs hub and Control Isolation at fuses 8168 to allow the truck to be removed from the lines | F2 | BELL BLOCK 5 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.00020864 | 9.071e-06 | 2016 | 2016-03-22 | C | 3 | 0.00020864 | 9.0713e-06
10362091 | 2016-03-22 13:16 | 2016-03-22 15:15 | 119.4167 | 16 | 1910.6667 | 119.4167 | 116.4167 | 0.0057774 | 1862.6667 | 0.0056323 | 4.838e-05 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5335 | 2 x 10amp HV fuses blown at Fuses 5335. Line patrolled unknown cause. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.0056323 | 4.838e-05 | 2016 | 2016-03-22 | C | 16 | 0.0056323 | 4.838e-05
10362114 | 2016-03-22 13:23 | 2016-03-22 15:20 | 116.95 | 283 | 14971.8167 | 52.9039 | 49.9039 | 0.045271 | 14122.8167 | 0.042704 | 0.00085572 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 712783 | Tasman TA 1 tripped open - No Flags Truck through the lines at Rangatiki Quarries 1167 Wiremu Road. Isolation at ABS TA101 & ABS NG425. NDR 100121 Material 9 x 16mm Sleeves, 50meters Cu bare conductor | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.042704 | 0.00085572 | 2016 | 2016-03-22 | C | 283 | 0.042704 | 0.00085572
10363172 | 2016-03-22 17:15 | 2016-03-22 18:30 | 75 | 7 | 525 | 75 | 72 | 0.0015875 | 504 | 0.001524 | 2.1166e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TE MIMI ROAD | Replace broken pole after tractor accident. Isolation at fuses FP1219. NDR . Materials 1x11m concrete pole 1 x HV crossarm. 3 x HV Pin insulators. NDR 048049. Paul Cooper | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-03-22 | c | 0.001524 | 2.1166e-05 | 2016 | 2016-03-22 | C | 7 | 0.001524 | 2.1166e-05
10364560 | 2016-03-22 16:15 | 2016-03-22 18:00 | 104.9 | 1 | 104.9 | 104.9 | 101.9 | 0.00031719 | 101.9 | 0.00030812 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7401 | Two Fuse found blown at Fuses 7401 - Cause Load customer has electicrian looking at balancing load Used 2 x 20 amp fuses | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.00030812 | 3.024e-06 | 2016 | 2016-03-22 | C | 1 | 0.00030812 | 3.0238e-06
10365733 | 2016-03-22 18:42 | 2016-03-22 20:00 | 78.3833 | 6 | 470.3 | 78.3833 | 75.3833 | 0.0014221 | 452.3 | 0.0013676 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4612 | 3 HT fuses found tripped. Patrolled, suspect bird. Reclosed OK (15A Rating) | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.0013676 | 1.8143e-05 | 2016 | 2016-03-22 | C | 6 | 0.0013676 | 1.8143e-05
10366070 | 2016-03-22 21:09 | 2016-03-22 23:23 | 133.5167 | 198 | 25970.7333 | 131.1653 | 128.1653 | 0.078529 | 25376.7333 | 0.076733 | 0.0005987 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB9 | Tripping on CB9 Massey feeder on O/C, E/F Flaggings. Massey University initially backfed from ABS H25 and Sw/Gear 305 to CBs 4 / 5. . Overhead patrolled with nothing found. Feeder sectionalised but all restored OK. (Suspect Bird strike). Feeder restored t | F2 | MASSEY | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-03-22 | c | 0.076733 | 0.00059871 | 2016 | 2016-03-22 | C | 198 | 0.076733 | 0.0005987
10366910 | 2016-03-23 04:59 | 2016-03-24 07:42 | 1602.25 | 311 | 140486.1667 | 451.724 | 448.724 | 0.4248 | 139553.1667 | 0.42198 | 0.00094039 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | V0911 | ( COR1 ) recloser 9736/2 tripped A, B & C Ph O/C, E/F, L/O feeder sectionalised. 2R - Request for tree removal from Lines. 11kV hit LV O/H Lines. Shane Walker to accompany Inspector for LV Inspector at Transformer TC1457 isolated at LV Fuses. Shane to re | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.42198 | 0.00094039 | 2016 | 2016-03-23 | C | 311 | 0.42198 | 0.00094039
10368015 | 2016-03-23 09:59 | 2016-03-23 17:26 | 447.3333 | 1 | 447.3333 | 447.3333 | 444.3333 | 0.0013526 | 444.3333 | 0.0013436 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | TD4-104 | EMAIL and Phone call to HUB. Dave to get bucket truck out to trim trees. NDR TBC. Has isolated HV FUSES AT TX TO ALLOW TREES TO BE CUT. FM has replaced the HV fuses and all power is restored. Maurice in control asked me to link up TX job and close this on | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.0013436 | 3.024e-06 | 2016 | 2016-03-23 | C | 1 | 0.0013436 | 3.0238e-06
10368252 | 2016-03-23 07:55 | 2016-03-23 10:36 | 160.9833 | 41 | 4799.85 | 117.0695 | 114.0695 | 0.014514 | 4676.85 | 0.014142 | 0.00012397 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Line patrolled nothing found. 2r line patrol 930. 2r repair nothing found | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.014142 | 0.00012397 | 2016 | 2016-03-23 | C | 41 | 0.014142 | 0.00012397
10368848 | 2016-03-23 10:30 | 2016-03-23 12:15 | 105 | 5 | 525 | 105 | 102 | 0.0015875 | 510 | 0.0015421 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714614 | Check for safety - crossarm has dropped down from pole, resting on the brackets. Site is about 400m up from the 5 road junction of (Opunake Road, Wiremu Road and Oeo Road). Contact: Trevor 062745664 09.42 advised and emailed SMC. Crossarm straightened & r | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.0015421 | 1.5119e-05 | 2016 | 2016-03-23 | C | 5 | 0.0015421 | 1.5119e-05
10370115 | 2016-03-23 10:39 | 2016-03-23 14:15 | 216.3 | 3 | 466.1333 | 155.3778 | 152.3778 | 0.0014095 | 457.1333 | 0.0013823 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3465 | Please check poss related OMS: 10370483 - 163 Bulltown Road, Waihi. Reloaded reliven 2 x 3A Fuses. Caused by Wind | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.0013823 | 9.071e-06 | 2016 | 2016-03-23 | C | 3 | 0.0013823 | 9.0713e-06
10370218 | 2016-03-23 12:01 | 2016-03-24 14:47 | 1606.0167 | 12 | 7800 | 650 | 647 | 0.023585 | 7764 | 0.023476 | 3.6285e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 805511 | Check for safety - car vs truck, lines are down. About 15mins south of SH1 Hunterville. F2044096. Fire service require eta. NZ FIRE ETA as advised by Hub 40 Minutes , Fire Service advised Faultman Found Truck in lines and pole broken - Fuses in FABS 4172 | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.023476 | 3.6285e-05 | 2016 | 2016-03-23 | C | 12 | 0.023476 | 3.6285e-05
10370672 | 2016-03-23 12:51 | 2016-03-23 13:57 | 65.3333 | 388 | 15950.5833 | 41.1098 | 38.1098 | 0.048231 | 14786.5833 | 0.044711 | 0.0011732 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 8 | CB 8 Trip. No auto reclose due to CAC 17236-01 being worked on. Asplundh rung, advised to stand down. Fault not caused by Asplundh. Flags A,B Fault. Back feeds RP04 Opened, Sectionaliser 9885 Close. Time delayed in closing of Sectionaliser 9885 due to wea | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.044711 | 0.0011732 | 2016 | 2016-03-23 | C | 388 | 0.044711 | 0.0011732
10371344 | 2016-03-23 12:56 | 2016-03-23 23:35 | 638.6167 | 167 | 8437.4 | 50.5234 | 47.5234 | 0.025513 | 7936.4 | 0.023998 | 0.00050497 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 766010 | Power pole smoking and lots of sparking, fuse dangling from crossarm - customer has part power and neighbours have no power. 1.08pm advised Shannon at svs hub & control. Check poss related OMS:10371568 - 344 MANGAHIA ROAD and OMS: 10371678 - 2174 Mokau R | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.023998 | 0.00050497 | 2016 | 2016-03-23 | C | 167 | 0.023998 | 0.00050497
10371376 | 2016-03-23 13:10 | 2016-03-23 16:40 | 210.3667 | 144 | 18218.1667 | 126.515 | 123.515 | 0.055087 | 17786.1667 | 0.053781 | 0.00043542 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Recloser S6029 | NDR 51709. Pole 227579. Trees through Lines. Trees Removed. Used 30m Namu Conductor. 7 x Sleeves. 2r line patrol 1419. 2r repair 1514 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.053781 | 0.00043542 | 2016 | 2016-03-23 | C | 144 | 0.053781 | 0.00043542
10371710 | 2016-03-23 13:38 | 2016-03-23 15:55 | 137 | 651 | 56099 | 86.1736 | 83.1736 | 0.16963 | 54146 | 0.16372 | 0.0019685 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Recloser 9228 - need Paul to recreate stages | Recloser 9228 Tripped on Lock Out. 9871 Flag on PH B & C O/C. 2x big flashes from outside 18 Trotters Avenue (new pole from 2 weeks ago) - Stuart Davies (021) 998 040 ONC advised. Sectionalised. Patrolled.No fault found. 2r line patrol 1415. 2r repair no | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.16372 | 0.0019685 | 2016 | 2016-03-23 | C | 651 | 0.16372 | 0.0019685
10373271 | 2016-03-23 15:27 | 2016-03-23 17:45 | 138.2333 | 26 | 3594.0667 | 138.2333 | 135.2333 | 0.010868 | 3516.0667 | 0.010632 | 7.8618e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R57 | Check 85 Gardners Rd, OMS 10373302 is related. And Check 41 Gardners Rd, OMS 10373469 Check 130 GARDNERS ROAD, OMS 10373562. 2 Fuses found blown at Fuses R57 - Cause Unknown. Used 2 x 15 amp Fuses | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.010632 | 7.8618e-05 | 2016 | 2016-03-23 | C | 26 | 0.010632 | 7.8618e-05
10373362 | 2016-03-23 16:38 | 2016-03-23 20:48 | 249.55 | 4 | 998.2 | 249.55 | 246.55 | 0.0030183 | 986.2 | 0.002982 | 1.2095e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TD5-047 | at 16:38, Papamoa Sub, CB 3 Black Stump Feeder. LV Lines have been pulled down by a truck passing through. Faultmen has to isolate HV to repair LV Lines at Transformer TD5-047. Repairs were carried out to LV Lines. On relivening the transformer, found tha | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.002982 | 1.2095e-05 | 2016 | 2016-03-23 | C | 4 | 0.002982 | 1.2095e-05
10373655 | 2016-03-30 13:14 | 2016-03-30 14:05 | 51 | 2 | 102 | 51 | 48 | 0.00030842 | 96 | 0.00029028 | 6.0475e-06 | Referral | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 155 Williams Road North, Tauranga | Follow up job to repair, rehang lines. Ted called to advise that because of weather they are unable to access the property as the truck will get stuck going into and out of the property. Ted had spoken to the customer and Stephen Ogier and advised that t | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2016-03-30 | c | 0.00029028 | 6.048e-06 | 2016 | 2016-03-30 | C | 2 | 0.00029028 | 6.0475e-06
10373660 | 2016-03-23 16:45 | 2016-03-23 19:12 | 146.7167 | 123 | 18046.15 | 146.7167 | 143.7167 | 0.054567 | 17677.15 | 0.053451 | 0.00037192 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | I32 | Reports of no power on the Rongomai feeder found CB I32 had tripped. Patrol found nothing. Suspect this CB had tripped during the breaking of parallel during planned switching earlier (SIN17484). Times consistent with switching and trip time in control bo | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.053451 | 0.00037192 | 2016 | 2016-03-23 | C | 123 | 0.053451 | 0.00037192
10376443 | 2016-03-23 19:38 | 2016-03-24 11:25 | 947 | 1 | 947 | 947 | 944 | 0.0028635 | 944 | 0.0028544 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T4779 | 1R, no power, elderly customer onsite so please attend asap. Replaced faulty Transformer TC4779. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.0028544 | 3.024e-06 | 2016 | 2016-03-23 | C | 1 | 0.0028544 | 3.0238e-06
10376602 | 2016-03-23 20:14 | 2016-03-23 22:02 | 108.4667 | 285 | 27444.5 | 96.2965 | 93.2965 | 0.082986 | 26589.5 | 0.0804 | 0.00086177 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | RP14 | at 20:13, Coromandel Sub, CB 7 Kapanga Rd Feeder, Recloser RP14 Tripped, No Flags, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. No Fault Found. Was strong wind in the area at time of tripping. 2r line patrol 2054. 2 r repair - no | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.0804 | 0.00086177 | 2016 | 2016-03-23 | C | 285 | 0.0804 | 0.00086177
10377310 | 2016-03-23 21:05 | 2016-03-23 22:42 | 96.45 | 284 | 21633.5 | 76.1743 | 73.1743 | 0.065415 | 20781.5 | 0.062838 | 0.00085875 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9736 | at 21:01 Coromandel Sub, CB 1 Colville Feeder, Recloser 9736 Tripped, No Flags, L/O. At time of tripping there was no comms - Duty NC had an AC Fail alarm for sectionaliser 9776 and had A B O/C Flags for this also. Faultmen dispatched and investigation be | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.062838 | 0.00085875 | 2016 | 2016-03-23 | C | 284 | 0.062838 | 0.00085875
10377719 | 2016-03-23 21:34 | 2016-03-24 01:55 | 260.65 | 170 | 18827.1 | 110.7476 | 107.7476 | 0.056929 | 18317.1 | 0.055387 | 0.00051404 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9320 | Sectionalised nothing found. 2r line patrol 2251. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.055387 | 0.00051404 | 2016 | 2016-03-23 | C | 170 | 0.055387 | 0.00051404
10377893 | 2016-03-23 21:35 | 2016-03-24 00:52 | 197.3833 | 236 | 28259.8667 | 119.7452 | 116.7452 | 0.085451 | 27551.8667 | 0.08331 | 0.00071361 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712041 | Tripping on CB NG2 on E/F B Phase. Feeder sectionalised / patrolled with a broken binder found on Kahui Rd. Isolation required between ABS NG237 and NG248. Binder replaced along with 1 Pin Insulator. Relivened OK. 2r line patrol 2253. 2r repair 2312 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-23 | c | 0.08331 | 0.00071361 | 2016 | 2016-03-23 | C | 236 | 0.08331 | 0.00071361
10379343 | 2016-03-23 22:24 | 2016-03-24 14:19 | 955.6 | 327 | 65402.8 | 200.0086 | 197.0086 | 0.19776 | 64421.8 | 0.1948 | 0.00098877 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | I2929 | Recloser 9121 tripped, isolation required between ABS IP531 & ABS 2630 with backfeed from LAK5 via VS 9718. Trees in the lines removed. Replaced 1 x crossarm, 3 x insulaors, bolts, bracket & 5 x links. NDR 55706 & 17988 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2016-03-23 | c | 0.1948 | 0.00098877 | 2016 | 2016-03-23 | C | 327 | 0.1948 | 0.00098877
10380397 | 2016-03-24 00:25 | 2016-03-24 05:08 | 283.8 | 2 | 514.15 | 257.075 | 254.075 | 0.0015547 | 508.15 | 0.0015365 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7-156 | Replaced Transformer TE7-156. Materials used: 1 transformer & 2 joints. Reload/Relivened. DDO blew. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0015365 | 6.048e-06 | 2016 | 2016-03-24 | C | 2 | 0.0015365 | 6.0475e-06
10380785 | 2016-03-24 00:46 | 2016-03-24 00:47 | 1.5833 | 108 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00032657 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Auto-reclose on Cb4196 Phase B-C O/C. High winds | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0 | 0.00032657 | 2016 | 2016-03-24 | C | 108 | 0 | 0.00032657
10380922 | 2016-03-24 01:44 | 2016-03-24 04:57 | 192.25 | 790 | 99531.1 | 125.9887 | 122.9887 | 0.30096 | 97161.1 | 0.29379 | 0.0023888 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 214217 | CB 6 tripped 2 insulator at pole 214217. 2r line patrol 0246 2r repair 0303. | F3 | GOLF RD | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.29379 | 0.0023888 | 2016 | 2016-03-24 | C | 790 | 0.29379 | 0.0023888
10382369 | 2016-03-24 01:55 | 2016-03-24 09:46 | 471 | 638 | 50907.25 | 79.7919 | 76.7919 | 0.15393 | 48993.25 | 0.14814 | 0.0019292 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12369 | 8.15am Tallia called to adviser Ferdi has finished this job he is now on standown, she has other faultman onsite now, requesting CR - sent this through. Whangamata CB 1 (Whiritoa) Tripped C Phase O/C E/F. Line patrolled. Line and hardware burnt at Tran | F4 | WHIRITOA | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.14814 | 0.0019292 | 2016 | 2016-03-24 | C | 638 | 0.14814 | 0.0019292
10383559 | 2016-03-24 02:17 | 2016-03-24 14:14 | 716.4833 | 153 | 42843.4833 | 280.0228 | 277.0228 | 0.12955 | 42384.4833 | 0.12816 | 0.00046264 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 711689 | Lines on road outside 188-177 Ngariki Road, advised Control. 2.44pm Bevan called to advise he has completed this job with control. NDR 22906 tree through the lines breaking hv crossarm at pole 711786 - hv lines broken. 1x hv crossarm, 30m of 35mil of ali | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.12816 | 0.00046263 | 2016 | 2016-03-24 | C | 153 | 0.12816 | 0.00046264
10383959 | 2016-03-24 02:49 | 2016-03-24 11:13 | 503.9667 | 338 | 53604.95 | 158.5945 | 155.5945 | 0.16209 | 52590.95 | 0.15902 | 0.001022 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N12781 | 8.38am - SVS hub advised Paul James now on stand down. Crew replacement. RC17 tripped - No Flags. Line patrolled. Branch on line brought line down at pole N12781. | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.15902 | 0.001022 | 2016 | 2016-03-24 | C | 338 | 0.15902 | 0.001022
10384302 | 2016-03-24 02:53 | 2016-03-24 05:39 | 165.75 | 301 | 22731.15 | 75.5188 | 72.5188 | 0.068734 | 21828.15 | 0.066003 | 0.00091015 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 3 tripped sectionalised nothing found. 2r line patrol 0427 2r repair non applicable | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.066003 | 0.00091015 | 2016 | 2016-03-24 | C | 301 | 0.066003 | 0.00091015
10384921 | 2016-03-24 03:03 | 2016-03-24 03:58 | 54.6667 | 1026 | 56088 | 54.6667 | 51.6667 | 0.1696 | 53010 | 0.16029 | 0.0031024 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 2 tripped line clash outside sub. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-03-24 | c | 0.16029 | 0.0031024 | 2016 | 2016-03-24 | C | 1026 | 0.16029 | 0.0031024
10387059 | 2016-03-24 03:17 | 2016-03-24 12:11 | 533.9 | 143 | 21819.8667 | 152.5865 | 149.5865 | 0.065978 | 21390.8667 | 0.064681 | 0.0004324 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 2032 | Kai Iwi CB7 / Waterworks Rd CB 2032 Tripped A-B Phase. Sectionalised. supply restored with no cause of fault located. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.064681 | 0.0004324 | 2016 | 2016-03-24 | C | 143 | 0.064681 | 0.0004324
10387419 | 2016-03-24 03:19 | 2016-03-24 13:00 | 580.7 | 6 | 3484.2 | 580.7 | 577.7 | 0.010535 | 3466.2 | 0.010481 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FC2297 | Reload Reliven 2 x 6A due to Wind. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.010481 | 1.8143e-05 | 2016 | 2016-03-24 | C | 6 | 0.010481 | 1.8143e-05
10387521 | 2016-03-24 03:22 | 2016-03-24 11:04 | 461.4833 | 498 | 89077.2 | 178.8699 | 175.8699 | 0.26935 | 87583.2 | 0.26483 | 0.0015058 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757349 | CB 6 Trip found broken crossarm and conductor At pole 757349. 2r Line patrol 0501. 2r repair 0856 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.26483 | 0.0015058 | 2016 | 2016-03-24 | C | 498 | 0.26483 | 0.0015058
10390627 | 2016-03-24 04:09 | 2016-03-24 05:48 | 98.7667 | 1209 | 117770.6833 | 97.4116 | 94.4116 | 0.35611 | 114143.6833 | 0.34514 | 0.0036557 |  | 33 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720543 | CB 342 & CB 3422 tripped. Lines patrolled and outage required between CB 342 & ABS 3586 with supply restored via KAP 3422. Replace 1 x binder. Relivened OK. | F1,F2,F3 | KAPUNI NO 2 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 2016-03-24 | c | 0.34514 | 0.0036557 | 2016 | 2016-03-24 | C | 1209 | 0.34514 | 0.0036557
10391873 | 2016-03-24 04:19 | 2016-03-24 17:06 | 766.7167 | 402 | 74790.6 | 186.0463 | 183.0463 | 0.22615 | 73584.6 | 0.2225 | 0.0012156 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2917 | 9.25am Pole down advised hub of 999, emailed. Taken to control Part power reported at 8836 STATE HIGHWAY 26 (OMS 10408596). OMS(10412369) Pole down - Rebecca from Thames District Council called to advised lines down, at the top of the road. Replace Trans | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.2225 | 0.0012156 | 2016 | 2016-03-24 | C | 402 | 0.2225 | 0.0012156
10394000 | 2016-03-24 04:39 | 2016-03-24 11:28 | 409 | 2221 | 323224.7 | 145.5312 | 142.5312 | 0.97735 | 316561.7 | 0.95721 | 0.0067158 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 707638 | CB 5 tripped on B and C phase O/C. Backfeeding sections of Peat St 9 due to TEMP Line breaks. 20m conductor 6 sleeves tree brought line down at pole 707688. | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.95721 | 0.0067158 | 2016 | 2016-03-24 | C | 2221 | 0.95721 | 0.0067158
10396348 | 2016-03-24 04:47 | 2016-03-24 08:16 | 208.7 | 4 | 834.8 | 208.7 | 205.7 | 0.0025242 | 822.8 | 0.002488 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | se6-061 | 2 x 6amp fuse weather | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.002488 | 1.2095e-05 | 2016 | 2016-03-24 | C | 4 | 0.002488 | 1.2095e-05
10397073 | 2016-03-24 05:21 | 2016-03-24 08:53 | 212.1333 | 112 | 23758.9333 | 212.1333 | 209.1333 | 0.071841 | 23422.9333 | 0.070825 | 0.00033866 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 780187 | CB513 tripped O/C. Line patrolled and branch removed from pole 780187. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-24 | c | 0.070825 | 0.00033866 | 2016 | 2016-03-24 | C | 112 | 0.070825 | 0.00033866
10397191 | 2016-03-24 05:23 | 2016-03-24 06:27 | 64.0833 | 1026 | 65749.5 | 64.0833 | 61.0833 | 0.19881 | 62671.5 | 0.1895 | 0.0031024 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB 2 A/R on O/C. Suspected line clashing at start of feeder. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2016-03-24 | c | 0.1895 | 0.0031024 | 2016 | 2016-03-24 | C | 1026 | 0.1895 | 0.0031024
10398594 | 2016-03-24 05:35 | 2016-03-24 16:48 | 673.35 | 601 | 80476.6833 | 133.9046 | 130.9046 | 0.24334 | 78673.6833 | 0.23789 | 0.0018173 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714681 | Major storm in area - CB TA8 tripped on O/C and there were several faults found. Feeder Sectionalised & Patrolled with faults being found near ABS 6810 (Twisted Cross arm) and at Pole 714681(Tree through lines). 8.18am Broken Cross arm, advised control 40 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.23789 | 0.0018173 | 2016 | 2016-03-24 | C | 601 | 0.23789 | 0.0018173
10402373 | 2016-03-24 06:13 | 2016-03-24 14:21 | 487.6667 | 717 | 64368.7833 | 89.7752 | 86.7752 | 0.19464 | 62217.7833 | 0.18813 | 0.002168 |  | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 807063 | Lines down - Murray has put a road cone near the lines - no sparking so assumes not live. Take the left hand fork of Gibbon Road and about half way up ETA appreciated. Control advised. Cindy from hub confirmed FM has left site and en route to another job | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.18813 | 0.002168 | 2016 | 2016-03-24 | C | 717 | 0.18813 | 0.002168
10404711 | 2016-03-24 06:40 | 2016-03-24 10:08 | 207.6333 | 123 | 24051.9 | 195.5439 | 192.5439 | 0.072727 | 23682.9 | 0.071611 | 0.00037192 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB I32 tripped line sectionalised nothing found | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.071611 | 0.00037192 | 2016 | 2016-03-24 | C | 123 | 0.071611 | 0.00037192
10404811 | 2016-03-24 06:50 | 2016-03-24 07:26 | 36.25 | 207 | 7503.75 | 36.25 | 33.25 | 0.02269 | 6882.75 | 0.020812 | 0.00062592 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ng307 | Fuses at ng307 replaced 2 x 3amp weather. 2.14pm retailer calling to advise customer still has part power. called svs hub and advised even though this job has been restored customer still has part power for cowshed - advised Tans at svs hub. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.020812 | 0.00062592 | 2016 | 2016-03-24 | C | 207 | 0.020812 | 0.00062592
10405342 | 2016-03-24 07:05 | 2016-03-24 11:10 | 245.6333 | 751 | 101672.5333 | 135.3829 | 132.3829 | 0.30743 | 99419.5333 | 0.30062 | 0.0022708 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713863 | Cb 2 trip Removed branch from lines at pole 713863. 08:52am High way 45 4 square reporting they are still without power -= everyone around them come on. Please ensure these customers are back on before closing job Murray 027 248 4147. (If control close | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.30062 | 0.0022708 | 2016 | 2016-03-24 | C | 751 | 0.30062 | 0.0022708
10406395 | 2016-03-24 07:13 | 2016-03-24 12:05 | 291.9667 | 439 | 50900.9333 | 115.9475 | 112.9475 | 0.15391 | 49583.9333 | 0.14993 | 0.0013274 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 768099 | 46 Pauls Road, Wanganui - Sparking Lines and pole is swinging in the wind. Repaired lines @ pole 768099 and supply restored to all except LV on transformer X1855. Replaced binders, jumpers, 1 x insulator & conductor. NDR 47452. | F3 | KIWI ST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.14993 | 0.0013274 | 2016 | 2016-03-24 | C | 439 | 0.14993 | 0.0013274
10407260 | 2016-03-24 07:18 | 2016-03-24 09:39 | 141.0833 | 257 | 23082.5 | 89.8152 | 86.8152 | 0.069796 | 22311.5 | 0.067465 | 0.00077711 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819434 | Tree debris in line - smouldering - near 102 Papawai Road: Control advised. CB 955 Trippred. 1 fault was tree on line at pole 819434. 2nd fault bark on line at pole 819434. Materials used 1 terminator (not arnie). NDR 54301 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.067465 | 0.00077711 | 2016 | 2016-03-24 | C | 257 | 0.067465 | 0.00077711
10408486 | 2016-03-24 07:38 | 2016-03-24 13:30 | 352.3667 | 20 | 7047.3333 | 352.3667 | 349.3667 | 0.021309 | 6987.3333 | 0.021128 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6293 | EMAIL SENT , TALLIA AT HUB ADVISED. Control Advised. 2 x 8 amp fuses,1 binder & 2 sleeves. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.021128 | 6.0475e-05 | 2016 | 2016-03-24 | C | 20 | 0.021128 | 6.0475e-05
10408718 | 2016-03-24 15:00 | 2016-03-24 16:40 | 100 | 1 | 100 | 100 | 97 | 0.00030238 | 97 | 0.0002933 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4664 | FM confirmed safe but still no power - needs to go to probably 2R - Faulty Transformer - FM contacted Colin - extra crew will be organised to attend, test for transformer fault and repair/replace as necessary. Changed transformer TC4664 and livened all s | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0002933 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.0002933 | 3.0238e-06
10408845 | 2016-03-24 06:20 | 2016-03-24 13:48 | 448.6833 | 20 | 8622.9833 | 431.1492 | 428.1492 | 0.026074 | 8562.9833 | 0.025892 | 6.0475e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 713234 | Repaired line down. Used 2x Ali sleeves & 1mtr of Poco Conductor. Also 3x 12Amp HV LinksControl know about this, advised Joanne svs hub Onsite time: 11am. Made safe - made sure it was isolated by seeing the DDO's were out and tested the line that was down | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.025892 | 6.0475e-05 | 2016 | 2016-03-24 | C | 20 | 0.025892 | 6.0475e-05
10409001 | 2016-03-24 09:29 | 2016-03-24 10:45 | 75.5833 | 24 | 1812.8333 | 75.5347 | 72.5347 | 0.0054816 | 1740.8333 | 0.0052639 | 7.257e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701687 | SVS hub advised via email 8:21. Replace king bolt on cross arm 701687. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0052639 | 7.257e-05 | 2016 | 2016-03-24 | C | 24 | 0.0052639 | 7.257e-05
10409042 | 2016-03-24 08:18 | 2016-03-24 13:10 | 291.95 | 1 | 291.95 | 291.95 | 288.95 | 0.00088279 | 288.95 | 0.00087372 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223753 | Replace 2 x 3amp hv fuses. cause: 2 burned up jumpers in conduit on pipe on cross arm. phase to phase contact on two jumpers. cut pipe back and re-taped jumpers. cause: deterioration, insulation broken down by uv. pole 223753. No other assets repaired or | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.00087372 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.00087372 | 3.0238e-06
10409131 | 2016-03-24 08:34 | 2016-03-24 10:19 | 104.7667 | 891 | 21927.9 | 24.6104 | 21.6104 | 0.066305 | 19254.9 | 0.058222 | 0.0026942 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t4451 | 10.09am Andrew King attending instead of Shane Walker. Wind caused damage. 2 x Full Tension Joints. 3m Squirrel Conductor. 1 x Insulator and Stem | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.058222 | 0.0026942 | 2016 | 2016-03-24 | C | 891 | 0.058222 | 0.0026942
10409161 | 2016-03-24 08:24 | 2016-03-24 13:22 | 298.15 | 201 | 30287.35 | 150.6833 | 147.6833 | 0.091582 | 29684.35 | 0.089758 | 0.00060778 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223453 | CB RP 10 tripped lines down at pole 223453 | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.089758 | 0.00060778 | 2016 | 2016-03-24 | C | 201 | 0.089758 | 0.00060778
10411153 | 2016-03-24 08:47 | 2016-03-24 10:58 | 130.7667 | 197 | 22251.25 | 112.9505 | 109.9505 | 0.067282 | 21660.25 | 0.065495 | 0.00059568 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | RC28 | CB RC28 Tripped. Line patrolled - Nothing found. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.065495 | 0.00059568 | 2016 | 2016-03-24 | C | 197 | 0.065495 | 0.00059568
10412284 | 2016-03-24 09:18 | 2016-03-25 13:35 | 1696.6167 | 1 | 1696.6167 | 1696.6167 | 1693.6167 | 0.0051302 | 1693.6167 | 0.0051211 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1355 | Bruce called requesting a 2r - to replaced transformer 15kVA, 3 x DDO's and a cross arm. As HV advised Paul in NOC Control. Josh Phillips 027 633 4908 (Customer) called to find out when we will be replacing this TX. SMC have advised this will not be happ | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0051211 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.0051211 | 3.0238e-06
10413297 | 2016-03-24 10:16 | 2016-03-24 12:57 | 161.0333 | 1116 | 83962.1 | 75.2349 | 72.2349 | 0.25388 | 80614.1 | 0.24376 | 0.0033745 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W12725 | CB 4 tripped to L/O. O/C flag. Back feed initially established by opening Recloser 9278 & closing sectionaliser RP17. No other backfeed available due to no telemetry control at Recloser 9512. Tree branch located and removed from line at pole W12725 and CB | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.24376 | 0.0033745 | 2016 | 2016-03-24 | C | 1116 | 0.24376 | 0.0033745
10418044 | 2016-03-24 11:16 | 2016-03-24 14:35 | 198.7833 | 4 | 795.1333 | 198.7833 | 195.7833 | 0.0024043 | 783.1333 | 0.002368 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TC4476 | Replace 2 x 2A fuse | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.002368 | 1.2095e-05 | 2016 | 2016-03-24 | C | 4 | 0.002368 | 1.2095e-05
10418107 | 2016-03-24 11:33 | 2016-03-24 12:17 | 43.9167 | 28 | 1229.6667 | 43.9167 | 40.9167 | 0.0037182 | 1145.6667 | 0.0034642 | 8.4665e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P4125 | Repair Lines down at P4125. Used LV Insulator. 2 x 16mm Sleeves. 3 m 16mm Conductor. 1 x Binder. 3 x 60A LV Fuses. 3 x Complete HV Fuses. 3 x 5A HV Fuses | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0034642 | 8.4665e-05 | 2016 | 2016-03-24 | C | 28 | 0.0034642 | 8.4665e-05
10418529 | 2016-03-24 11:53 | 2016-03-24 15:08 | 195.6667 | 1 | 195.6667 | 195.6667 | 192.6667 | 0.00059165 | 192.6667 | 0.00058258 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6769 | 2 x 3amp fuses at 6769 feeding tx 5287 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.00058258 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.00058258 | 3.0238e-06
10419670 | 2016-03-24 12:20 | 2016-03-24 15:51 | 211.7833 | 1 | 211.7833 | 211.7833 | 208.7833 | 0.00064038 | 208.7833 | 0.00063131 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TP1680 | (1R) No power - pump station located off the end of Kaimarama road , please attend asap as it supplies water to the township. Part of CB4 feeder fault | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.00063131 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.00063131 | 3.0238e-06
10419693 | 2016-03-24 10:50 | 2016-03-24 18:20 | 450.4167 | 11 | 4954.5833 | 450.4167 | 447.4167 | 0.014981 | 4921.5833 | 0.014882 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | MA404 | Call from retailer requesting update - customer is getting irate. I spoke to Shan at the hub who confirmed that there are FM in the area and they are aware of this job - they will attend to it as soon as they possibly can. Replace 3 x 8A fuses | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.014882 | 3.3261e-05 | 2016 | 2016-03-24 | C | 11 | 0.014882 | 3.3261e-05
10419750 | 2016-03-24 12:30 | 2016-03-24 14:30 | 120.3833 | 4 | 481.5333 | 120.3833 | 117.3833 | 0.001456 | 469.5333 | 0.0014198 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ng380 | 2 x 3amp fuse weather | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0014198 | 1.2095e-05 | 2016 | 2016-03-24 | C | 4 | 0.0014198 | 1.2095e-05
10419853 | 2016-03-24 12:39 | 2016-03-24 13:00 | 20.6667 | 1 | 20.6667 | 20.6667 | 17.6667 | 6.2491e-05 | 17.6667 | 5.342e-05 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 5055T | Have spoken with ONC ok to put fault job through. LV Clash Caused HV Fuse Outage. Reload Reliven at 5055T 1 x 3A Fuse due to Wind. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-24 | c | 5.342e-05 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 5.342e-05 | 3.0238e-06
10420596 | 2016-03-24 14:07 | 2016-03-24 19:45 | 338.2 | 1 | 338.2 | 338.2 | 335.2 | 0.0010226 | 335.2 | 0.0010136 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | TD5-028 | (nearest ICP) outside #35 Reid Rd, Colin Winch advised tree has come through the LV service line. The transformer is hanging onto the pole - just. TD5-28 Pole #219840. 1.33pm advised hub of 999 (unable to email as email is down). FM advises tree has come | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0010136 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.0010136 | 3.0238e-06
10420909 | 2016-03-24 13:48 | 2016-03-24 15:15 | 86.6 | 1 | 86.6 | 86.6 | 83.6 | 0.00026186 | 83.6 | 0.00025279 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | None | possibly due to HV switching | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.00025279 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.00025279 | 3.0238e-06
10423326 | 2016-03-24 15:27 | 2016-03-24 20:00 | 273.2833 | 2 | 546.5667 | 273.2833 | 270.2833 | 0.0016527 | 540.5667 | 0.0016345 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4007 | 2 x 6 A Fuses replaced due to weather. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0016345 | 6.048e-06 | 2016 | 2016-03-24 | C | 2 | 0.0016345 | 6.0475e-06
10423714 | 2016-03-24 16:12 | 2016-03-24 19:40 | 208.0333 | 3 | 624.1 | 208.0333 | 205.0333 | 0.0018871 | 615.1 | 0.0018599 | 9.0713e-06 |  | 6.6 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2882 | 2 HT fuses found tripped at Fuses 2882. Reloaded OK, suspect clash in high winds. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0018599 | 9.071e-06 | 2016 | 2016-03-24 | C | 3 | 0.0018599 | 9.0713e-06
10423736 | 2016-03-24 16:15 | 2016-03-24 18:04 | 108.7667 | 1 | 108.7667 | 108.7667 | 105.7667 | 0.00032888 | 105.7667 | 0.00031981 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5301E | Outage required from Fuses PU303. Outage job attached, no outage under this job. Replace 3 x HV Fuses, 3 x fuse links. Relivened OK. 1R, no power, Patto (contractor) has asked us to log a job with Powerco as there are two HV fuses hanging down on a transf | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.00031981 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.00031981 | 3.0238e-06
10423781 | 2016-03-24 16:18 | 2016-03-24 23:21 | 422.75 | 1 | 422.75 | 422.75 | 419.75 | 0.0012783 | 419.75 | 0.0012692 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF6-104 | TF6-104 Transformer Blown. Transformer Replaced. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0012692 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.0012692 | 3.0238e-06
10424420 | 2016-03-24 16:20 | 2016-03-24 19:26 | 186.3833 | 586 | 93431.6167 | 159.4396 | 156.4396 | 0.28251 | 91673.6167 | 0.2772 | 0.0017719 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V13497 | Fault found to be a jumper had blown down onto the pin of an insulator at pole V13497. Jumper pushed out of the way with fuse stick. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.2772 | 0.0017719 | 2016 | 2016-03-24 | C | 586 | 0.2772 | 0.0017719
10426636 | 2016-03-24 17:03 | 2016-03-24 19:33 | 149.4833 | 297 | 19941.2167 | 67.1421 | 64.1421 | 0.060297 | 19050.2167 | 0.057603 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T11 | Kaponga CB T11 trip on O/C, E/F. Reports of arcing pole along Upper Palmer Rd. Isolation from ABS 5972 with a patrol carried out. Nothing found. Feeder restored to normal. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.057603 | 0.00089806 | 2016 | 2016-03-24 | C | 297 | 0.057603 | 0.00089806
10427452 | 2016-03-24 17:26 | 2016-03-24 21:15 | 229.45 | 319 | 38002.2833 | 119.1294 | 116.1294 | 0.11491 | 37045.2833 | 0.11202 | 0.00096458 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222163 | Lines down called in by fire comms ETA please Event # F2045496 crn Glu Pot and Oropi Rd. Replaced OH line and restrained - 15mtrs 11kV Namu conductor and 8 Namu Sleeves. Pole 222163 to 222164. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.11202 | 0.00096458 | 2016 | 2016-03-24 | C | 319 | 0.11202 | 0.00096458
10427789 | 2016-03-24 17:29 | 2016-03-24 18:04 | 35.3833 | 16 | 566.1333 | 35.3833 | 32.3833 | 0.0017119 | 518.1333 | 0.0015667 | 4.838e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5301E |  | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0015667 | 4.838e-05 | 2016 | 2016-03-24 | C | 16 | 0.0015667 | 4.838e-05
10429018 | 2016-03-24 19:18 | 2016-03-25 00:50 | 331.75 | 482 | 36307.85 | 75.3275 | 72.3275 | 0.10979 | 34861.85 | 0.10541 | 0.0014575 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H1826 | CB 3 tripped on O/C E/F and L/O. 1 x HV Crossarm 3 x HV Pin insulators | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.10541 | 0.0014575 | 2016 | 2016-03-24 | C | 482 | 0.10541 | 0.0014575
10430872 | 2016-03-24 22:23 | 2016-03-24 22:40 | 17 | 2 | 34 | 17 | 14 | 0.00010281 | 28 | 8.4665e-05 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | ADVERSE WEATHER | ADVERSE WEATHER - WIND | X392 | 9.17am - advise smc. Fault caused by broken HT lead at the Transformer X392. Isolation made and lead reattached. Relivened. Suspect high winds. Also needed 1 HT fuse replaced (2A) | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 2016-03-24 | c | 8.4665e-05 | 6.048e-06 | 2016 | 2016-03-24 | C | 2 | 8.4665e-05 | 6.0475e-06
10430974 | 2016-03-24 21:36 | 2016-03-25 12:08 | 872 | 1 | 872 | 872 | 869 | 0.0026367 | 869 | 0.0026276 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sf8-032 | Changed faulty trany sf8-032 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.0026276 | 3.024e-06 | 2016 | 2016-03-24 | C | 1 | 0.0026276 | 3.0238e-06
10431557 | 2016-03-24 19:22 | 2016-03-24 22:44 | 201.7167 | 3 | 605.15 | 201.7167 | 198.7167 | 0.0018298 | 596.15 | 0.0018026 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1534 | 2 HT fuses tripped at X1534. Reloaded OK. Cause by wind. 2A | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.0018026 | 9.071e-06 | 2016 | 2016-03-24 | C | 3 | 0.0018026 | 9.0713e-06
10432576 | 2016-03-24 23:48 | 2016-03-25 00:36 | 47.4333 | 1409 | 52302.5333 | 37.1203 | 34.1203 | 0.15815 | 48075.5333 | 0.14537 | 0.0042605 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | X20 | Received 2 trippings simultaneously - 33kV CB X20 tripping at Feilding (Loss of Supply to Kimbolton) on Phase A-B. Also had a tripping on CB P61 on A-B O/C. Substation checked and 33kV / Sub and feeders all restored OK. NOTE: At the time of Tripping, the | F1,F2,F3 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.14537 | 0.0042605 | 2016 | 2016-03-24 | C | 1409 | 0.14537 | 0.0042605
10435598 | 2016-03-25 00:10 | 2016-03-25 04:28 | 257.8 | 1 | 257.8 | 257.8 | 254.8 | 0.00077953 | 254.8 | 0.00077045 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Bruce went to site and found a faulty Transformer 5043E requires changing - this OMS incorrect. New OMS 10434759 issued for TX change | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.00077045 | 3.024e-06 | 2016 | 2016-03-25 | C | 1 | 0.00077045 | 3.0238e-06
10435759 | 2016-03-25 04:10 | 2016-03-25 15:20 | 670 | 1 | 670 | 670 | 667 | 0.0020259 | 667 | 0.0020168 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 6378 | Replaced LV Fuse Holders. 2R request for transformer 5043E to be changed. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.0020168 | 3.024e-06 | 2016 | 2016-03-25 | C | 1 | 0.0020168 | 3.0238e-06
10436632 | 2016-03-25 04:08 | 2016-03-26 15:54 | 2146.1 | 297 | 25995.2833 | 87.5262 | 84.5262 | 0.078604 | 25104.2833 | 0.075909 | 0.00089806 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731779 | Line sectionalised and patrolled with no obvious fault found. Isolated to between ABS 5972 and 5992. Line break created @ pole 731779 and backfed from ABS 5992 .Section from ABS 6040 backfed from R51 via ABS 8903/1. Found blown insulator at pole 731779. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.075909 | 0.00089806 | 2016 | 2016-03-25 | C | 297 | 0.075909 | 0.00089806
10436972 | 2016-03-25 04:40 | 2016-03-25 07:50 | 190.4667 | 178 | 18516.4 | 104.0247 | 101.0247 | 0.055989 | 17982.4 | 0.054374 | 0.00053823 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 809642 | Repaired lines brought down by branch @ pole 809642. NDR 30427. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.054374 | 0.00053823 | 2016 | 2016-03-25 | C | 178 | 0.054374 | 0.00053823
10437293 | 2016-03-25 05:41 | 2016-03-25 13:10 | 449.15 | 82 | 19011.2667 | 231.8447 | 228.8447 | 0.057486 | 18765.2667 | 0.056742 | 0.00024795 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739335 | Sectionalised and patrolled found line down @ pole 739335 and repaired used 1x sleeve and replaced 1x HV Fuse @ 54453 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.056742 | 0.00024795 | 2016 | 2016-03-25 | C | 82 | 0.056742 | 0.00024795
10437919 | 2016-03-25 06:00 | 2016-03-25 08:30 | 149.7333 | 2 | 299.4667 | 149.7333 | 146.7333 | 0.00090552 | 293.4667 | 0.00088737 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sc3-035 | Replaced 2 x 15amp Fuses replaced at SC3-035 | F4 | PLUMMERS POINT | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-03-25 | c | 0.00088737 | 6.048e-06 | 2016 | 2016-03-25 | C | 2 | 0.00088737 | 6.0475e-06
10438267 | 2016-03-25 06:44 | 2016-03-25 09:11 | 146.9167 | 11 | 1616.0833 | 146.9167 | 143.9167 | 0.0048866 | 1583.0833 | 0.0047869 | 3.3261e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | wh831 | Replaced 2 x 6amp fuses at WH831 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.0047869 | 3.3261e-05 | 2016 | 2016-03-25 | C | 11 | 0.0047869 | 3.3261e-05
10440340 | 2016-03-25 08:53 | 2016-03-25 11:43 | 169.2333 | 1 | 169.2333 | 169.2333 | 166.2333 | 0.00051172 | 166.2333 | 0.00050265 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t5/95 | Replaced 2x hV fuses @ t5/95 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.00050265 | 3.024e-06 | 2016 | 2016-03-25 | C | 1 | 0.00050265 | 3.0238e-06
10440347 | 2016-03-25 08:56 | 2016-03-25 14:28 | 331.65 | 1 | 331.65 | 331.65 | 328.65 | 0.0010028 | 328.65 | 0.00099376 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 965W | replaed 2x3a hv fuses & 1x100a lv fuse@transformer 965W | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.00099376 | 3.024e-06 | 2016 | 2016-03-25 | C | 1 | 0.00099376 | 3.0238e-06
10440428 | 2016-03-25 11:02 | 2016-03-25 11:44 | 42 | 1 | 42 | 42 | 39 | 0.000127 | 39 | 0.00011793 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715230 | Repaired floating conductor on pole 715230 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.00011793 | 3.024e-06 | 2016 | 2016-03-25 | C | 1 | 0.00011793 | 3.0238e-06
10451510 | 2016-03-25 13:54 | 2016-03-25 14:21 | 26.6333 | 10 | 266.3333 | 26.6333 | 23.6333 | 0.00080533 | 236.3333 | 0.00071462 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718328 | CB 8 Manaia. Repaired twisted cross arm on Pole 718328. | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.00071462 | 3.0238e-05 | 2016 | 2016-03-25 | C | 10 | 0.00071462 | 3.0238e-05
10452075 | 2016-03-25 15:55 | 2016-03-25 16:21 | 26.1 | 355 | 9265.5 | 26.1 | 23.1 | 0.028017 | 8200.5 | 0.024796 | 0.0010734 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K707686 | 1.44pm advised hub of 999. Isolated area between IC470, IP545 & 9122. Replaced 1 faulty insulator on pole K707686. Relivened. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-25 | c | 0.024796 | 0.0010734 | 2016 | 2016-03-25 | C | 355 | 0.024796 | 0.0010734
10452188 | 2016-03-24 14:51 | 2016-03-25 14:03 | 1392.4667 | 15 | 20887 | 1392.4667 | 1389.4667 | 0.063157 | 20842 | 0.063021 | 4.5356e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc885 - need paperwork | Replace transformer TC885 under own SIS and AP. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-03-24 | c | 0.063021 | 4.5356e-05 | 2016 | 2016-03-24 | C | 15 | 0.063021 | 4.5356e-05
10453324 | 2016-03-25 15:55 | 2016-03-25 22:15 | 380 | 41 | 13892.85 | 338.85 | 335.85 | 0.042009 | 13769.85 | 0.041637 | 0.00012397 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | poss related to 10453330 | Repair lines brought down by trees at Pole P44489. Police comms, P024669341. ETA required, 15 mins. Notified SMC. NDR N300176. Pole number P44489. Materials crossarm compleet X2 20m conductor 12 sleeves binder and fuses. Contractor angee kahang 063552725 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.041637 | 0.00012397 | 2016 | 2016-03-25 | C | 41 | 0.041637 | 0.00012397
10454249 | 2016-03-25 17:16 | 2016-03-25 20:57 | 220.5 | 5 | 1102.5 | 220.5 | 217.5 | 0.0033337 | 1087.5 | 0.0032883 | 1.5119e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/113 | 2 HT fuses tripped at T5/113, reloaded OK (2A Rating) | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-25 | c | 0.0032883 | 1.5119e-05 | 2016 | 2016-03-25 | C | 5 | 0.0032883 | 1.5119e-05
10466887 | 2016-03-25 19:34 | 2016-03-25 23:49 | 254.7833 | 187 | 20749.4833 | 110.9598 | 107.9598 | 0.062741 | 20188.4833 | 0.061045 | 0.00056544 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | K2262 | Recloser RP05 tripped to L/O. A, B & C Ph O/C flags. Line sectionalised & patrolled. Magpie eventually located on pole K2262 caught between conductor & crossarm. Removed with hot line stick. All supply restored. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-25 | c | 0.061045 | 0.00056544 | 2016 | 2016-03-25 | C | 187 | 0.061045 | 0.00056544
10467895 | 2016-03-26 04:26 | 2016-03-26 08:22 | 235.6333 | 474 | 33439.6167 | 70.5477 | 67.5477 | 0.10111 | 32017.6167 | 0.096814 | 0.0014333 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 366028 | Recloser 687 Trip o/c found branch on line at pole 366028 also blown jumper at recloser 687 jumper repaired live line branch removed under ap with isolation's at abs 581 &892. Was backfed via CB 912. NDR 30428 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 2016-03-26 | c | 0.096814 | 0.0014333 | 2016 | 2016-03-26 | C | 474 | 0.096814 | 0.0014333
10468860 | 2016-03-26 07:39 | 2016-03-26 08:36 | 56.8 | 362 | 17678.4833 | 48.8356 | 45.8356 | 0.053456 | 16592.4833 | 0.050172 | 0.0010946 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB r41 trip E/f patrolled nothing found | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2016-03-26 | c | 0.050172 | 0.0010946 | 2016 | 2016-03-26 | C | 362 | 0.050172 | 0.0010946
10472071 | 2016-03-26 18:05 | 2016-03-26 19:56 | 111.0167 | 2 | 222.0333 | 111.0167 | 108.0167 | 0.00067138 | 216.0333 | 0.00065323 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5661 | 2 x 3A HV Fuses replaced. Unknown Cause | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 2016-03-26 | c | 0.00065323 | 6.048e-06 | 2016 | 2016-03-26 | C | 2 | 0.00065323 | 6.0475e-06
10475608 | 2016-03-27 11:21 | 2016-03-27 13:09 | 108.3 | 6 | 649.8 | 108.3 | 105.3 | 0.0019648 | 631.8 | 0.0019104 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 292 | 1 x 6amp fuse at 292 and 2 x 3amp fuses at X2347 unknown reason | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-27 | c | 0.0019104 | 1.8143e-05 | 2016 | 2016-03-27 | C | 6 | 0.0019104 | 1.8143e-05
10476427 | 2016-03-27 14:58 | 2016-03-27 17:39 | 161.55 | 2 | 150.0167 | 75.0083 | 72.0083 | 0.00045361 | 144.0167 | 0.00043547 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2149 | Replace 2 x 3A H/V O/H fuses ( bird strike ) | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 2016-03-27 | c | 0.00043547 | 6.048e-06 | 2016 | 2016-03-27 | C | 2 | 0.00043547 | 6.0475e-06
10477230 | 2016-03-27 19:56 | 2016-03-27 22:40 | 164.1167 | 2 | 328.2333 | 164.1167 | 161.1167 | 0.0009925 | 322.2333 | 0.00097436 | 6.0475e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 834872 | Line Down at Pole 834872 Isolation at Fuses 7475. 6mtrs 7064 and 2 sleeves used. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2016-03-27 | c | 0.00097436 | 6.048e-06 | 2016 | 2016-03-27 | C | 2 | 0.00097436 | 6.0475e-06
10486013 | 2016-03-27 22:18 | 2016-03-28 13:23 | 905 | 4 | 3620 | 905 | 902 | 0.010946 | 3608 | 0.01091 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC578 | Replaced faulty 30kVA transformer TC578 x 1 ( old age ). D Sanders own isolation & AP to replace | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2016-03-27 | c | 0.01091 | 1.2095e-05 | 2016 | 2016-03-27 | C | 4 | 0.01091 | 1.2095e-05
10486067 | 2016-03-28 04:44 | 2016-03-28 07:00 | 136.5 | 6 | 819 | 136.5 | 133.5 | 0.0024765 | 801 | 0.002422 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L38 | 2 HT Fuses tripped at L38. Reloaded OK (15A Rating) | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2016-03-28 | c | 0.002422 | 1.8143e-05 | 2016 | 2016-03-28 | C | 6 | 0.002422 | 1.8143e-05
10486194 | 2016-03-28 09:53 | 2016-03-28 10:42 | 49.2333 | 6 | 295.4 | 49.2333 | 46.2333 | 0.00089322 | 277.4 | 0.00083879 | 1.8143e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 54W | Repaired connector at lv bushing, Took off HV for safety - | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-28 | c | 0.00083879 | 1.8143e-05 | 2016 | 2016-03-28 | C | 6 | 0.00083879 | 1.8143e-05
10486690 | 2016-03-28 11:04 | 2016-03-28 11:29 | 25.4333 | 1750 | 33403.45 | 19.0877 | 16.0877 | 0.101 | 28153.45 | 0.085129 | 0.0052916 |  | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 3112 | PGA CB 3112 tripped E/F, B Ph O/C, L/O ( loss of PKW sub ). PKW backfed PKW 1 fed via Rec 9513 ( PGA 3 ) PKW 4 fed via Rec 9463 ( PGA 5 ) PKW 2 fed via Sec 9761 ( PKW 1 - PGA 3 ) PKW 3 fed via ( PKW4 - PGA- 5 ) 33kV line patrolled no obvious fault found | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2016-03-28 | c | 0.085129 | 0.0052916 | 2016 | 2016-03-28 | C | 1750 | 0.085129 | 0.0052916
10498737 | 2016-03-28 14:46 | 2016-03-28 22:17 | 450.4833 | 1005 | 6021.0333 | 5.9911 | 2.9911 | 0.018206 | 3006.0333 | 0.0090895 | 0.0030389 |  | 6.6 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 760485 | Trailer has come off car and has hit pole, pole and lines are down. About 1km out of Inglewood, Fire service require eta. F2047379. Police have also called, have advised both fire and police of eta of 15mins. Police also advised that trailer was full of s | F3 | ELLIOT ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 2016-03-28 | c | 0.0090895 | 0.0030389 | 2016 | 2016-03-28 | C | 1005 | 0.0090895 | 0.0030389
10499120 | 2016-03-28 16:28 | 2016-03-28 18:08 | 100.4333 | 1 | 100.4333 | 100.4333 | 97.4333 | 0.00030369 | 97.4333 | 0.00029462 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/192 | This OMS shows incorrect transformer - should be T5/192. (On the same farm).2 HT fuses tripped, reloaded OK. Suspect lightning from storm other night. NOTE Transformer single phase, 2 Fuses tripped | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2016-03-28 | c | 0.00029462 | 3.024e-06 | 2016 | 2016-03-28 | C | 1 | 0.00029462 | 3.0238e-06
10499990 | 2016-03-28 20:06 | 2016-03-28 22:04 | 118.1833 | 1 | 118.1833 | 118.1833 | 115.1833 | 0.00035736 | 115.1833 | 0.00034829 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 6510 | Please check poss related OMS: 10500009 - 1305A SOUTH. 10500003 - 1303 South Road. 2 X 3 Amp Fuses. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 2016-03-28 | c | 0.00034829 | 3.024e-06 | 2016 | 2016-03-28 | C | 1 | 0.00034829 | 3.0238e-06
10500237 | 2016-03-29 04:00 | 2016-03-29 06:41 | 161 | 30 | 4830 | 161 | 158 | 0.014605 | 4740 | 0.014333 | 9.0713e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC2-057 | Suspect faulty trany TC2-112, Own SIS & AP. Customer reported no power on different trany, Check fuses SC2-057 , found all closed, check fuses with stick & found 1 blown, Replaced fuse Reconnected TC2-112 Off 04:00 On 06:41 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 2016-03-29 | c | 0.014333 | 9.0713e-05 | 2016 | 2016-03-29 | C | 30 | 0.014333 | 9.0713e-05
10517472 | 2016-03-29 04:35 | 2016-03-29 06:10 | 95.2167 | 10 | 952.1667 | 95.2167 | 92.2167 | 0.0028791 | 922.1667 | 0.0027884 | 3.0238e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7543 | 2 HT fuses tripped at 7543. Reloaded OK. Bird strike. (10A Rating). | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 2016-03-29 | c | 0.0027884 | 3.0238e-05 | 2016 | 2016-03-29 | C | 10 | 0.0027884 | 3.0238e-05
10517490 | 2016-03-29 06:15 | 2016-03-29 16:15 | 600.2167 | 3 | 1799.1 | 599.7 | 596.7 | 0.00544 | 1790.1 | 0.0054128 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X417 | 2 HT fuses found tripped at X417. (Caused by LV Cable fault). Reloaded OK.however, no voltage on 1 LV Bushing. Faulty Transformer requires change. HT fuses reopened. Replacement transformer to be done on OMS 10521004 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2016-03-29 | c | 0.0054128 | 9.071e-06 | 2016 | 2016-03-29 | C | 3 | 0.0054128 | 9.0713e-06
10518240 | 2016-03-24 18:05 | 2016-03-24 18:36 | 31 | 316 | 9468 | 29.962 | 26.962 | 0.028629 | 8520 | 0.025762 | 0.00095551 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Major storm in area - CB TA8 tripped on O/C and there were several faults found. Feeder Sectionalised & Patrolled with faults being found near ABS 6810 (Twisted Cross arm) and at Pole 714681(Tree through lines). 8.18am Broken Cross arm, advised control 40 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-24 | c | 0.025762 | 0.00095551 | 2016 | 2016-03-24 | C | 316 | 0.025762 | 0.00095551
10520695 | 2016-03-29 09:29 | 2016-03-29 11:54 | 145.1 | 4 | 580.4 | 145.1 | 142.1 | 0.001755 | 568.4 | 0.0017187 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 356520 | 2x6am fuses blown at Fuses 8605 Bird strike. Reloaded & replaced. Pole 356520 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-29 | c | 0.0017187 | 1.2095e-05 | 2016 | 2016-03-29 | C | 4 | 0.0017187 | 1.2095e-05
10521708 | 2016-03-29 23:00 | 2016-03-30 | 60 | 86 | 5160 | 60 | 57 | 0.015603 | 4902 | 0.014822 | 0.00026004 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 31A MILLARD AVENUE | Fluctuating power, requires 2R to be able to resolve. Loop impedence test has pointed towards to a cooked joint or cable in the box on the Tx - will be dropping the Tx via the HV line. Emergency shutdown (perhaps at night) - on the LV side, via HV. Trans | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 2016-03-29 | c | 0.014822 | 0.00026004 | 2016 | 2016-03-29 | C | 86 | 0.014822 | 0.00026004
10522004 | 2016-03-29 13:29 | 2016-03-29 13:35 | 6.4667 | 8 | 51.7333 | 6.4667 | 3.4667 | 0.00015643 | 27.7333 | 8.3859e-05 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | O25 | Reload reliven at Fuses O25. Used 2 x 10A Fuses. Cause Unknown. See 10521589 fro Crew assignment. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2016-03-29 | c | 8.3859e-05 | 2.419e-05 | 2016 | 2016-03-29 | C | 8 | 8.3859e-05 | 2.419e-05
10522253 | 2016-03-29 13:56 | 2016-03-29 14:30 | 34 | 4 | 136 | 34 | 31 | 0.00041123 | 124 | 0.00037495 | 1.2095e-05 |  | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H1808 | Replaced rotten crossarm at pole H1808. Isolation at Fuses FC2338. Crossarm identified during line patrol. Perry Hicks attended | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 2016-03-29 | c | 0.00037495 | 1.2095e-05 | 2016 | 2016-03-29 | C | 4 | 0.00037495 | 1.2095e-05
10522290 | 2016-03-30 09:00 | 2016-03-30 17:27 | 507 | 255 | 129285 | 507 | 504 | 0.39093 | 128520 | 0.38861 | 0.00077106 | NAPA ID:16849 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 202233 | Levers Rd Conductor Upgrade Stage 4 Shut 3. Replace 11kV conductor between poles 202203 and 202214. Also replace 11kV conductor between poles 202207 and 202233. | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2016-03-30 | b | 0.19431 | 0.00038553 | 2016 | 2016-03-30 | B | 255 | 0.38861 | 0.00077106
10523933 | 2016-03-29 21:03 | 2016-03-29 23:00 | 116.9833 | 1 | 116.9833 | 116.9833 | 113.9833 | 0.00035373 | 113.9833 | 0.00034466 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2580 | 2 X 6 Amp | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 2016-03-29 | c | 0.00034466 | 3.024e-06 | 2016 | 2016-03-29 | C | 1 | 0.00034466 | 3.0238e-06
10526341 | 2016-03-30 15:00 | 2016-03-30 15:01 | 1.5 | 3 | 4.5 | 1.5 | -1.5 | 1.3607e-05 | 0 | 0 | 9.0713e-06 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 269905 | Pole No. 269905 wire are hanging and touching the ground, possible issue affecting customers who are without power. 9.47am advised Joanne at SVS hub & emailed & advised Control. LV Conductor 2 Phases are very badly damaged. 2R - one LV span ( 2 Conductor | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 2016-03-30 | c | 0 | 9.071e-06 | 2016 | 2016-03-30 | C | 3 | 0 | 9.0713e-06
10528359 | 2016-03-30 11:49 | 2016-03-30 13:52 | 123.1 | 1 | 123.1 | 123.1 | 120.1 | 0.00037222 | 120.1 | 0.00036315 | 3.0238e-06 |  | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 8493 | Reload Relivn at Fuses 8493. 2 x 3A Fuses. Cause Unknown. | F3 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2016-03-30 | c | 0.00036315 | 3.024e-06 | 2016 | 2016-03-30 | C | 1 | 0.00036315 | 3.0238e-06
10531199 | 2016-03-31 00:30 | 2016-03-31 02:00 | 90 | 107 | 7480 | 69.9065 | 66.9065 | 0.022618 | 7159 | 0.021647 | 0.00032354 |  | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3733 | 22.55 FM requested a 2R needing a electrical fitter, he is unable to do the work. Not quite sure what work is needed and have advised FM to contact the hub for extra crew and that the work is to be decided at invoicing level if meets criteria of 2R work a | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 2016-03-31 | c | 0.021647 | 0.00032354 | 2016 | 2016-03-31 | C | 107 | 0.021647 | 0.00032354
10533617 | 2016-03-31 10:14 | 2016-03-31 10:30 | 16 | 2 | 32 | 16 | 13 | 9.676e-05 | 26 | 7.8618e-05 | 6.0475e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | 1833W | Transformer 1833W was tapped down by faultman James Prime on request from Powerco due to high voltages causing trippings on equipment, under works order No: 30024512. | F3 | IKITARA RD | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 2016-03-31 | c | 7.8618e-05 | 6.048e-06 | 2016 | 2016-03-31 | C | 2 | 7.8618e-05 | 6.0475e-06
10535924 | 2016-03-31 18:14 | 2016-04-01 01:21 | 427.4667 | 8 | 3419.7333 | 427.4667 | 424.4667 | 0.01034 | 3395.7333 | 0.010268 | 2.419e-05 |  | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 708420 | Broken Pole (Corner of Mauku Road and Whitianga Road, WHANGAMOMONA) on ground caused all 3 HT Fuses to trip at 6304. Fault caused by pole subsiding near side of Road and eventually falling. Replaced OK and relivened. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 2016-03-31 | c | 0.010268 | 2.419e-05 | 2016 | 2016-03-31 | C | 8 | 0.010268 | 2.419e-05
10535951 | 2016-03-31 18:08 | 2016-04-01 00:19 | 371.1333 | 5 | 1855.6667 | 371.1333 | 368.1333 | 0.0056111 | 1840.6667 | 0.0055657 | 1.5119e-05 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5584E | Defective transformer 5584E replaced, Relivened OK. Isolation from Fuses NG324 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2016-03-31 | c | 0.0055657 | 1.5119e-05 | 2016 | 2016-03-31 | C | 5 | 0.0055657 | 1.5119e-05
10536540 | 2016-03-31 17:55 | 2016-03-31 22:40 | 285 | 1 | 285 | 285 | 282 | 0.00086177 | 282 | 0.0008527 | 3.0238e-06 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5133E | HV fuse found blown at Transformer 5133E. Replaced & Relivened OK. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2016-03-31 | c | 0.0008527 | 3.024e-06 | 2016 | 2016-03-31 | C | 1 | 0.0008527 | 3.0238e-06
10536887 | 2016-03-31 18:15 | 2016-03-31 19:32 | 76.6667 | 23 | 1763.3333 | 76.6667 | 73.6667 | 0.0053319 | 1694.3333 | 0.0051233 | 6.9546e-05 |  | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SC3-035 | 2 x 15A HV Fuses Replaced. Suspect Bird Strike. | F4 | PLUMMERS POINT | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2016-03-31 | c | 0.0051233 | 6.9546e-05 | 2016 | 2016-03-31 | C | 23 | 0.0051233 | 6.9546e-05
10537380 | 2016-03-31 22:49 | 2016-04-01 01:10 | 141 | 119 | 16779 | 141 | 138 | 0.050736 | 16422 | 0.049656 | 0.00035983 |  | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G140T - Need more info from Bernie | 2R - 1 HT fuse found tripped at Fuse/Sw 10165/2. Transformer G140T Megger tested and found to be faulty. LV Backfeeds put in place to liven all customers by 01:10 am. Transformer to be replaced during daylight hours. 13:00 Contact SMC to request ETA. | F3 | MAIN ST 21 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2016-03-31 | c | 0.049656 | 0.00035983 | 2016 | 2016-03-31 | C | 119 | 0.049656 | 0.00035983
3131192949 | 2015-08-06 09:01 | 2015-08-06 15:40 | 399.1667 | 103 | 41114.1667 | 399.1667 | 396.1667 | 0.12432 | 40805.1667 | 0.12339 | 0.00031145 | NAPA ID:10946 TP_MASTERTON GXP > AKURA SUB > CORADINE ST | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1464 | Replace transformer pole T1464. Works location: Villa Street. WO 10059773. | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 2015-08-06 | b | 0.061693 | 0.00015572 | 2016 | 2015-08-06 | B | 103 | 0.12339 | 0.00031145
3131193289 | 2015-07-16 17:59 | 2015-07-16 18:01 | 1.7667 | 1 | 1.7667 | 1.7667 | -1.2333 | 5.342e-06 | 0 | 0 | 3.0238e-06 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Whiritoa Repeater | RTU PS Major alarm activated. Technician required.2 x HV fuses replaced st FC2347. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0 | 3.024e-06 | 2016 | 2015-07-16 | C | 1 | 0 | 3.0238e-06
3131223386 | 2015-07-16 17:20 | 2015-07-16 17:52 | 32.35 | 1066 | 34485.1 | 32.35 | 29.35 | 0.10427 | 31287.1 | 0.094605 | 0.0032233 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 10083 | recloser tripped - Closed after 15 min - line patrolled with no fault found | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.094605 | 0.0032233 | 2016 | 2015-07-16 | C | 1066 | 0.094605 | 0.0032233
3131224615 | 2015-07-16 22:14 | 2015-07-16 23:14 | 60 | 1 | 60 | 60 | 57 | 0.00018143 | 57 | 0.00017235 | 3.0238e-06 | Restore Supply on Device T3122 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3122 | Sparks coming from the Pole fuse. The water pump at the shed is not going. 6.33pm advised Sammy at svs hub & control. 369 Opua Road, Opunake. Fuses for Transfomer T3122 found to be burnt , Isolated at ABS's TA119 & TA720 - used 3 x DDO's, 3x 3 amp fuses | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.00017235 | 3.024e-06 | 2016 | 2015-07-16 | C | 1 | 0.00017235 | 3.0238e-06
3131224644 | 2015-07-16 09:19 | 2015-07-16 18:43 | 564.1833 | 1 | 206.3333 | 206.3333 | 203.3333 | 0.0006239 | 203.3333 | 0.00061483 | 3.0238e-06 | Restore Supply on Device FP358 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fp358 | 3x 10Amp HV Fuses. Attended by Don Watson | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 2015-07-16 | c | 0.00061483 | 3.024e-06 | 2016 | 2015-07-16 | C | 1 | 0.00061483 | 3.0238e-06
3131235571 | 2015-07-16 22:34 | 2015-07-16 23:15 | 40.4333 | 61 | 2466.4333 | 40.4333 | 37.4333 | 0.0074579 | 2283.4333 | 0.0069046 | 0.00018445 | Restore Supply on Device TA720 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | Ref OMS 3131224615 | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-07-16 | c | 0.0069046 | 0.00018445 | 2016 | 2015-07-16 | C | 61 | 0.0069046 | 0.00018445
3131235891 | 2015-07-17 12:01 | 2015-07-17 12:56 | 55 | 5 | 271.1333 | 54.2267 | 51.2267 | 0.00081984 | 256.1333 | 0.00077449 | 1.5119e-05 | Restore Supply on Device T9/280 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20904 | Repaired HV jumper with existing connection and reconnected. Power restored. Nothing else repaired or replaced All other assets up to Powerco standard | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-17 | c | 0.00077449 | 1.5119e-05 | 2016 | 2015-07-17 | C | 5 | 0.00077449 | 1.5119e-05
3131236317 | 2015-07-17 11:18 | 2015-07-17 13:24 | 126.4167 | 1 | 126.4167 | 126.4167 | 123.4167 | 0.00038225 | 123.4167 | 0.00037318 | 3.0238e-06 | Restore Supply on Device T5055 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5055 | TX needs to be replaced - This will be next week and the customer has been informed of the time frame | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-07-17 | c | 0.00037318 | 3.024e-06 | 2016 | 2015-07-17 | C | 1 | 0.00037318 | 3.0238e-06
3131236503 | 2015-07-17 13:18 | 2015-07-17 15:37 | 139.1667 | 1 | 139.1667 | 139.1667 | 136.1667 | 0.00042081 | 136.1667 | 0.00041174 | 3.0238e-06 | Restore Supply on Device T1232 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7385 & 7997 | same As 3131236530 fuse link 7385 Replaced 2X 10a & 2X 15a hV Fuses and 2X holders | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-07-17 | c | 0.00041173 | 3.024e-06 | 2016 | 2015-07-17 | C | 1 | 0.00041174 | 3.0238e-06
3131237238 | 2015-07-17 15:56 | 2015-07-17 19:24 | 208.1 | 293 | 55409 | 189.1092 | 186.1092 | 0.16754 | 54530 | 0.16489 | 0.00088596 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P31232 | f 1883390. car v pole. eta required for fire. int Tangimoana road and Rosina road Tangimoana Palmerston North. advised Shan at hub and control. 4.22pm eta 30mins advised fire comms. ndr # 046702. pole # p31232. RS L 10 Tripped fault isolated at ABS L13 - | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-17 | c | 0.16489 | 0.00088596 | 2016 | 2015-07-17 | C | 293 | 0.16489 | 0.00088596
3131240079 | 2015-07-18 01:10 | 2015-07-18 03:18 | 128 | 1 | 128 | 128 | 125 | 0.00038704 | 125 | 0.00037797 | 3.0238e-06 | Restore Supply on Device TB1-104 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208326 | Lines down located at pole 208326. No trip initiated as supply side of line still in air. Line isolated at ABS SB1-036 for repairs. 2 metres of Namu cond, 2 Namu joint sleeves & 1 binder materials required*** please check if oms 3131240084 - 6 Killen Rd f | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.00037797 | 3.024e-06 | 2016 | 2015-07-18 | C | 1 | 0.00037797 | 3.0238e-06
3131240111 | 2015-07-17 22:18 | 2015-07-18 03:19 | 300.75 | 103 | 30977.25 | 300.75 | 297.75 | 0.093668 | 30668.25 | 0.092733 | 0.00031145 | Restore Supply on Device SB1-036 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208326 | Lines down located at pole 208326. No trip initiated as supply side of line still in air. Line isolated at ABS SB1-036 for repairs. 2 metres of Namu cond, 2 Namu joint sleeves & 1 binder materials required*** please check if oms 3131240084 - 6 Killen Rd f | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 2015-07-17 | c | 0.092733 | 0.00031145 | 2016 | 2015-07-17 | C | 103 | 0.092733 | 0.00031145
3131240246 | 2015-07-18 08:07 | 2015-07-18 10:40 | 153 | 30 | 4582.2667 | 152.7422 | 149.7422 | 0.013856 | 4492.2667 | 0.013584 | 9.0713e-05 | Restore Supply on Device 3658T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738526 | Line Down At Pole 738526. Isolated at fuses 6130 and repairs made. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.013584 | 9.0713e-05 | 2016 | 2015-07-18 | C | 30 | 0.013584 | 9.0713e-05
3131242791 | 2015-07-18 11:35 | 2015-07-19 03:57 | 982 | 1773 | 682919.7667 | 385.1775 | 382.1775 | 2.065 | 677600.7667 | 2.0489 | 0.0053611 | Restore Supply on Device 4 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T0907 | CB 4 Thames sub tripped to L/O. Lines down and broken pole at pole T0907. Line isolated at CB 4 Thames sub, ABS 9871/1 & links 9871/4 to replace broken pole & lines. Backfeed to recloser 9228/2. Another fault initially suspected between 9871 & 9228 but p | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 2.0489 | 0.0053611 | 2016 | 2015-07-18 | C | 1773 | 2.0489 | 0.0053611
3131244834 | 2015-07-18 11:44 | 2015-07-18 12:41 | 56.5833 | 327 | 18152.4833 | 55.5122 | 52.5122 | 0.054889 | 17171.4833 | 0.051922 | 0.00098877 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 9161 | Tree touching the lines causing sparks and arcing. 77 HAURAKI ROAD | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.051922 | 0.00098877 | 2016 | 2015-07-18 | C | 327 | 0.051922 | 0.00098877
3131245310 | 2015-07-18 14:52 | 2015-07-18 15:40 | 47.6 | 143 | 6683.4 | 46.7371 | 43.7371 | 0.020209 | 6254.4 | 0.018912 | 0.0004324 | Restore Supply on Device TC1986 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W1064 | at 14:52, Whitianga Sub, CB 3 Kuaotunu Feeder. Found Pole W1064 had been blown over onto a 45 degree angle due to high winds. Isolated Lines at ABS 337 & 381 for safety. Hiab attached to pole, re straightened and held up by hiab truck. Lines was then reli | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.018912 | 0.0004324 | 2016 | 2015-07-18 | C | 143 | 0.018912 | 0.0004324
3131245314 | 2015-07-19 13:08 | 2015-07-19 14:59 | 111 | 63 | 6963 | 110.5238 | 107.5238 | 0.021054 | 6774 | 0.020483 | 0.0001905 | Restore Supply on Device TC435 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | Found blown jumper at transformer TC435. Isolation's between ABS IC482 & Sw/Gear 9459/1 with back feed via Sw/Gear 9045/1. Jumper repaired all service restored. Material 1 x 3A H/V, O/H fuse, LINKED TO 3131276361 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.020483 | 0.0001905 | 2016 | 2015-07-19 | C | 63 | 0.020483 | 0.0001905
3131245952 | 2015-07-18 14:54 | 2015-07-18 16:10 | 76.4667 | 4 | 305.8667 | 76.4667 | 73.4667 | 0.00092487 | 293.8667 | 0.00088858 | 1.2095e-05 | Restore Supply on Device T4/139 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | Pole | 17 GEANGES ROAD, APITI. Powerpole has fallen over - lines are very low approx 2 metres from the ground. 12.25pm advised svs hub of 999 and taken to control. Installed Temp Stay wire & anchor to hold in place until it can be moved to better Position | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.00088858 | 1.2095e-05 | 2016 | 2015-07-18 | C | 4 | 0.00088858 | 1.2095e-05
3131245959 | 2015-07-18 12:36 | 2015-07-18 17:03 | 267.4167 | 867 | 204701.3333 | 236.103 | 233.103 | 0.61897 | 202100.3333 | 0.6111 | 0.0026216 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 263458 | Matua CB3 Tripped/ Wire sitting on cross arm at pole 263458. | F3 | BEACH RD MATUA | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.6111 | 0.0026216 | 2016 | 2015-07-18 | C | 867 | 0.6111 | 0.0026216
3131246827 | 2015-07-18 12:39 | 2015-07-18 16:45 | 246 | 1023 | 183828.2833 | 179.6953 | 176.6953 | 0.55585 | 180759.2833 | 0.54657 | 0.0030933 | Restore Supply on Device 14 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD4-207 | Power lines down on the corner of 23rd ave & Rimu St, on 23rd Ave P021882970 eta required - advised control. | F3 | GATE PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.54657 | 0.0030933 | 2016 | 2015-07-18 | C | 1023 | 0.54657 | 0.0030933
3131247854 | 2015-07-18 12:43 | 2015-07-18 17:17 | 274.3167 | 839 | 202175.2333 | 240.9717 | 237.9717 | 0.61133 | 199658.2333 | 0.60372 | 0.0025369 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 389624 | Sectionalised CB found Tree fell through line between pole 389426 & 389517. Check all ok | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.60372 | 0.0025369 | 2016 | 2015-07-18 | C | 839 | 0.60372 | 0.0025369
3131259243 | 2015-07-18 12:45 | 2015-07-18 16:31 | 225.6833 | 4548 | 321184.45 | 70.621 | 67.621 | 0.97118 | 307540.45 | 0.92993 | 0.013752 | Restore Supply on Device 1122 | 33 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 1122 | Te Matai CB 1122 and CB1102 tripped. Reclosed CB 1122. No patrol, on livening 2 11kv feeders tripped on fault which was handled as separate jobs. | F1,F2,F3 | TE MATAI1122-PONGAKAWA2007 33KV | TE MATAI | Tauranga | TP_TE MATAI | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.92993 | 0.013752 | 2016 | 2015-07-18 | C | 4548 | 0.92993 | 0.013752
3131263159 | 2015-07-18 12:55 | 2015-07-19 01:06 | 731.3333 | 562 | 92260.75 | 164.165 | 161.165 | 0.27897 | 90574.75 | 0.27388 | 0.0016994 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224249 | Te Puke 11kV CB 3 tripped to L/O. Severe weather conditions. 2 x faults found on line during sectionalising and patrolling. Lines down between ABS SE6-052 & SD6-011. More lines down between ABS SD6-011 & SE5-221. All supply restored following repairs. lin | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.27388 | 0.0016994 | 2016 | 2015-07-18 | C | 562 | 0.27388 | 0.0016994
3131263750 | 2015-07-19 11:04 | 2015-07-19 11:48 | 43.5833 | 29 | 1258.6667 | 43.4023 | 40.4023 | 0.0038059 | 1171.6667 | 0.0035428 | 8.7689e-05 | Restore Supply on Device TC2045 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12772 | Blown jumper at pole o12772. Isolation required between ABS IC452 & ABS IC442 with back feed via ABS IC469. Jumper repaired all service restored. Materials Nil | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.0035428 | 8.7689e-05 | 2016 | 2015-07-19 | C | 29 | 0.0035428 | 8.7689e-05
3131263858 | 2015-07-18 13:43 | 2015-07-18 13:44 | 1.3167 | 149 | 0 | 0 | -3 | 0 | 0 | 0 | 0.00045054 | Restore Supply on Device 284 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N284 | A/RE/F O/C C Phase | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-18 | c | 0 | 0.00045054 | 2016 | 2015-07-18 | C | 149 | 0 | 0.00045054
3131264325 | 2015-07-18 13:54 | 2015-07-19 05:42 | 947.7833 | 141 | 39395.4 | 279.4 | 276.4 | 0.11912 | 38972.4 | 0.11784 | 0.00042635 | Restore Supply on Device 1 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218037 | CB 1 tripped to L/O. Lines down at pole 218037. Isolation at ABS SE7-005 & IP515. All supply restored following repairs. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.11784 | 0.00042635 | 2016 | 2015-07-18 | C | 141 | 0.11784 | 0.00042635
3131264469 | 2015-07-18 13:54 | 2015-07-19 17:05 | 1630.6333 | 420 | 140188.6 | 333.7824 | 330.7824 | 0.4239 | 138928.6 | 0.42009 | 0.00127 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 229230 | 19/7 2.29pm - FM attending the feeder fault of last night found this pole 227887 down and advise smc. Not sure why a follow-up request for a pole replacement has not been sent through. SMC knew about the job and send a FM out to attend so Dispatch put fol | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.42009 | 0.00127 | 2016 | 2015-07-18 | C | 420 | 0.42009 | 0.00127
3131265041 | 2015-07-18 14:00 | 2015-07-18 21:30 | 449.65 | 1 | 449.65 | 449.65 | 446.65 | 0.0013596 | 446.65 | 0.0013506 | 3.0238e-06 | Restore Supply on Device TD5-013 | 11 | Unplanned | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 219975 and 390382 | 2.08pm - called svs hub to advise 999. 20/7 1.23pm called TJ to find out what work was done for this job so i can clear this job - lft msge TJ. 2.49pm emailed svs hub asking for faultman to call dispatch to get completion details. ie what was replaced and | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.0013506 | 3.024e-06 | 2016 | 2015-07-18 | C | 1 | 0.0013506 | 3.0238e-06
3131265046 | 2015-07-18 14:00 | 2015-07-18 16:31 | 150.5667 | 11 | 1648.95 | 149.9045 | 146.9045 | 0.004986 | 1615.95 | 0.0048862 | 3.3261e-05 | Restore Supply on Device TC5571 | 11 | Unplanned | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | I12964 | at 15:37, Piako Sub, CB 6 Kereone Feeder. Faultman was dispatched to No Power Calls. Found Fuses FP523 had blown on all 3 phases. Patrolled line and found tree across 11kV Lines at Pole I12964. Lines had not been damaged. Removed trees from line. Reloaded | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.0048862 | 3.3261e-05 | 2016 | 2015-07-18 | C | 11 | 0.0048862 | 3.3261e-05
3131265049 | 2015-07-18 14:43 | 2015-07-18 17:55 | 192 | 2 | 384 | 192 | 189 | 0.0011611 | 378 | 0.001143 | 6.0475e-06 | Restore Supply on Device TD4-083 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD4-083 | Pls check if 3131268279 (low voltage) is related. REPLACED 2 HV FUSES AT TWO DIFFERENT LOCATIONS WORKED THROUGH CONTROL. | F3 | CENTRAL OTUMOETAI | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.001143 | 6.048e-06 | 2016 | 2015-07-18 | C | 2 | 0.001143 | 6.0475e-06
3131265216 | 2015-07-18 14:16 | 2015-07-18 15:28 | 71.65 | 1 | 71.65 | 71.65 | 68.65 | 0.00021665 | 68.65 | 0.00020758 | 3.0238e-06 | Restore Supply on Device 1706N | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 6068 | 2 X 3 AMP FUSES , DUE TO WEATHER, WORKED THROUGH CONTROL. No other assets repaired or replaced Adjacent assets ok | F4 | BELL BLOCK 8 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.00020758 | 3.024e-06 | 2016 | 2015-07-18 | C | 1 | 0.00020758 | 3.0238e-06
3131268251 | 2015-07-18 15:24 | 2015-07-19 12:52 | 1287.7 | 3 | 347.7 | 115.9 | 112.9 | 0.0010514 | 338.7 | 0.0010241 | 9.0713e-06 | Restore Supply on Device 4031T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5234 | fault on spur line feeding tx, going through valley. spoke to guy behind her property and he is happy to be off till tomorrow when it can be fixed. too dangerous to attend at night and access issues. Transformer 4038T still off | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.0010241 | 9.071e-06 | 2016 | 2015-07-18 | C | 3 | 0.0010241 | 9.0713e-06
3131269031 | 2015-07-18 17:20 | 2015-07-18 20:15 | 175.4167 | 2 | 350.8333 | 175.4167 | 172.4167 | 0.0010608 | 344.8333 | 0.0010427 | 6.0475e-06 | Restore Supply on Device 793 | 11 | Unplanned | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 793 | 7.29pm - advise smc to assign Mark Patterson to attend in the lower part of Upland Rd as he is waiting for the tx to arrive that they need to replace int he upper part of Upland Road. Mark has seen multiple fuses out on his way, therefore made it a straig | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.0010427 | 6.048e-06 | 2016 | 2015-07-18 | C | 2 | 0.0010427 | 6.0475e-06
3131270013 | 2015-07-18 17:50 | 2015-07-18 18:09 | 19 | 28 | 532 | 19 | 16 | 0.0016086 | 448 | 0.0013546 | 8.4665e-05 | Restore Supply on Device 8293 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8293 | tx 696 outside #1167 has blown, mark patterson working through control to replace tonight. Also replace fuses at following tx: tx 1516 - replace 2 x 3 amp loads - power on 18:30pm. tx 1597 - replace 3 x 2 amp loads - power on 6:46pm. FM advise: lightning | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.0013546 | 8.4665e-05 | 2016 | 2015-07-18 | C | 28 | 0.0013546 | 8.4665e-05
3131270034 | 2015-07-18 17:42 | 2015-07-19 00:48 | 426.1667 | 7 | 2975.6 | 425.0857 | 422.0857 | 0.0089975 | 2954.6 | 0.008934 | 2.1166e-05 | Restore Supply on Device 3930T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764960 | Repair lines @ pole 764960 Found recloser 6274 open and reclosed | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-18 | c | 0.008934 | 2.1166e-05 | 2016 | 2015-07-18 | C | 7 | 0.008934 | 2.1166e-05
3131271084 | 2015-07-18 19:04 | 2015-07-18 20:59 | 114.8167 | 4 | 459.2667 | 114.8167 | 111.8167 | 0.0013887 | 447.2667 | 0.0013524 | 1.2095e-05 | Restore Supply on Device SD5-162 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 390382 | Lines down at pole 390382. Line isolated at fuses SD5-162 for repairs. All supply restored following repairs. 30 metres namu conductor & 8 namu joint sleeves materials required. is part of 3131265041 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.0013524 | 1.2095e-05 | 2016 | 2015-07-18 | C | 4 | 0.0013524 | 1.2095e-05
3131271125 | 2015-07-18 19:28 | 2015-07-18 21:00 | 91.95 | 236 | 16517.2 | 69.9881 | 66.9881 | 0.049944 | 15809.2 | 0.047803 | 0.00071361 | Restore Supply on Device SC4-423 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC4-430 | Emergency shutdown. Arcing on 11kv cable at sw/gear SC4-430. Temp repairs made to cable termination making discharge noise. DNO created to have urgent maintenance carried out. | F3 | CHERRYWOOD DRIVE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.047803 | 0.00071361 | 2016 | 2015-07-18 | C | 236 | 0.047803 | 0.00071361
3131273961 | 2015-07-18 17:31 | 2015-07-18 19:56 | 145.3167 | 472 | 1943.0667 | 4.1167 | 1.1167 | 0.0058754 | 527.0667 | 0.0015937 | 0.0014272 | Restore Supply on Device KPT-CB2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | a/r suspected tree in line | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.0015937 | 0.0014272 | 2016 | 2015-07-18 | C | 472 | 0.0015937 | 0.0014272
3131274908 | 2015-07-18 19:57 | 2015-07-18 23:52 | 234.3667 | 472 | 66264 | 140.3898 | 137.3898 | 0.20037 | 64848 | 0.19608 | 0.0014272 | Restore Supply on Device KPT-CB2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB2 | CB 2 tripped to L/O. Precluded by several A/R. The A/R was disabled by NOC locking out the CB. Line was sectionalosed & patrolled. No fault found. All supply restored. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.19608 | 0.0014272 | 2016 | 2015-07-18 | C | 472 | 0.19608 | 0.0014272
3131276357 | 2015-07-19 10:36 | 2015-07-20 14:50 | 1694 | 3 | 5082 | 1694 | 1691 | 0.015367 | 5073 | 0.01534 | 9.0713e-06 | Restore Supply on Device 298 | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 8275 | Suspect Cable or transformer faulty to be tested. Cable faulty. Repairs carried out. Material 2 through joint kits, 25mm AL SC XLPE Cable | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-07-19 | c | 0.01534 | 9.071e-06 | 2016 | 2015-07-19 | C | 3 | 0.01534 | 9.0713e-06
3131276759 | 2015-07-18 22:09 | 2015-07-19 13:05 | 896.0167 | 2 | 1792.0333 | 896.0167 | 893.0167 | 0.0054187 | 1786.0333 | 0.0054005 | 6.0475e-06 | Restore Supply on Device SD6-007 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 220657 | Broken pole at 220654. Isolated at fuses SD6-007. To be replaced tomorrow 19/07/15 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.0054005 | 6.048e-06 | 2016 | 2015-07-18 | C | 2 | 0.0054005 | 6.0475e-06
3131277146 | 2015-07-18 22:20 | 2015-07-19 11:55 | 815.4833 | 301 | 56760.4 | 188.5728 | 185.5728 | 0.17163 | 55857.4 | 0.1689 | 0.00091015 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 264433 | CB 3 tripped to L/O. OMS job rolled into 3131276737 that was previously created for a P/P job. New OMS created for feeder trip. Line sectionalised & patrolled. Tree branch located over line at pole 264433. Branch removed and all supply restored. | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0.1689 | 0.00091015 | 2016 | 2015-07-18 | C | 301 | 0.1689 | 0.00091015
3131277550 | 2015-07-19 00:43 | 2015-07-19 17:55 | 1031.3167 | 154 | 61693.9833 | 400.6103 | 397.6103 | 0.18655 | 61231.9833 | 0.18515 | 0.00046566 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P13676 | Recloser 9604/2 tripped to L/O. E/F flag. Lines down at P13676 | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.18515 | 0.00046566 | 2016 | 2015-07-19 | C | 154 | 0.18515 | 0.00046566
3131278240 | 2015-07-18 17:30 | 2015-07-19 02:01 | 511.3167 | 521 | 0 | 0 | -3 | 0 | 0 | 0 | 0.0015754 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | N/A - NOT APPLICABLE | A/R | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-18 | c | 0 | 0.0015754 | 2016 | 2015-07-18 | C | 521 | 0 | 0.0015754
3131278520 | 2015-07-19 02:24 | 2015-07-19 12:37 | 613.65 | 212 | 63252.85 | 298.3625 | 295.3625 | 0.19126 | 62616.85 | 0.18934 | 0.00064104 | Restore Supply on Device 2 | 22 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844243 | Tree In Lines | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-07-19 | c | 0.18934 | 0.00064104 | 2016 | 2015-07-19 | C | 212 | 0.18934 | 0.00064104
3131278740 | 2015-07-19 03:06 | 2015-07-19 03:09 | 2.8333 | 105 | 297.5 | 2.8333 | -0.16667 | 0.00089957 | 0 | 0 | 0.00031749 | Restore Supply on Device 3 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 264433 | a/r not patrolled | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0 | 0.00031749 | 2016 | 2015-07-19 | C | 105 | 0 | 0.00031749
3131279459 | 2015-07-19 06:27 | 2015-07-19 11:39 | 312 | 296 | 44292.6333 | 149.6373 | 146.6373 | 0.13393 | 43404.6333 | 0.13125 | 0.00089503 | Restore Supply on Device C917 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812812 | Featherston. DAiry Factory CB C917 Auto Reclosed and Tripped E/F. Line patrolled and located lines down at pole 812812. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-07-19 | c | 0.13125 | 0.00089503 | 2016 | 2015-07-19 | C | 296 | 0.13125 | 0.00089503
3131280650 | 2015-07-19 12:35 | 2015-07-19 14:15 | 100.3833 | 9 | 901.2 | 100.1333 | 97.1333 | 0.002725 | 874.2 | 0.0026434 | 2.7214e-05 | Restore Supply on Device T545 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 137169 | Floating conductor at Pole 137169 - repaired. No other assets repaired or replaced at site. Adjacent assets all up to Powerco Standard. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-07-19 | c | 0.0026434 | 2.7214e-05 | 2016 | 2015-07-19 | C | 9 | 0.0026434 | 2.7214e-05
3131281131 | 2015-07-19 14:50 | 2015-07-19 16:38 | 108 | 8 | 864 | 108 | 105 | 0.0026125 | 840 | 0.00254 | 2.419e-05 | Restore Supply on Device T369 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7103 | Tree in Lines after Fuse 7103. pole 357252. NDR 21857. Also check 3131281161 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 2015-07-19 | c | 0.00254 | 2.419e-05 | 2016 | 2015-07-19 | C | 8 | 0.00254 | 2.419e-05
3131281242 | 2015-07-19 09:46 | 2015-07-19 14:44 | 298.5167 | 2 | 525.9833 | 262.9917 | 259.9917 | 0.0015904 | 519.9833 | 0.0015723 | 6.0475e-06 | Restore Supply on Device X260 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X260 | Also check 3131281242 & 3131280793 2 X 20 amp fuses | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-19 | c | 0.0015723 | 6.048e-06 | 2016 | 2015-07-19 | C | 2 | 0.0015723 | 6.0475e-06
3131283254 | 2015-07-19 10:33 | 2015-07-19 15:36 | 303.0667 | 1 | 303.0667 | 303.0667 | 300.0667 | 0.0009164 | 300.0667 | 0.00090733 | 3.0238e-06 | Restore Supply on Device 4287 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 4287 | was part of oms 3131281242 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-19 | c | 0.00090733 | 3.024e-06 | 2016 | 2015-07-19 | C | 1 | 0.00090733 | 3.0238e-06
3131283285 | 2015-07-19 15:15 | 2015-07-19 16:20 | 65.2333 | 4 | 260.9333 | 65.2333 | 62.2333 | 0.000789 | 248.9333 | 0.00075271 | 1.2095e-05 | Restore Supply on Device TC4164 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2259 | Found blown fuse af fuses FC2184. Line down found at pole M2259. Line repaired all service restored. Material 1 x 6A H/V fuse, 1 x meter conductor, 2 x sleeves | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.00075272 | 1.2095e-05 | 2016 | 2015-07-19 | C | 4 | 0.00075271 | 1.2095e-05
3131284466 | 2015-07-19 15:29 | 2015-07-19 18:30 | 181.3 | 370 | 57755.1167 | 156.0949 | 153.0949 | 0.17464 | 56645.1167 | 0.17128 | 0.0011188 | Restore Supply on Device KPT-CB2 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 207068 | ABS SA2009 opened and tagged it at 17:21, SA2008 opened and tagged at 17:21. SA2009 closed at 17:55, SA2007 opened at 18:21, SA2008 closed at 18:22 SA2007 closed at 18:32 - full power restored | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.17128 | 0.0011188 | 2016 | 2015-07-19 | C | 370 | 0.17128 | 0.0011188
3131286878 | 2015-07-19 17:50 | 2015-07-19 20:55 | 185 | 29 | 5365 | 185 | 182 | 0.016222 | 5278 | 0.015959 | 8.7689e-05 | Restore Supply on Device 2 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3052 | Blown transformer TC3052, isolate & earth for generator. FM has installed generator, full power going, will need to return tomorrow to replace tx. Generator installed to get power on, referral for TX replacement. Works completed on 28.07.15. After initia | F1/F3 | LOMOND AVE | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.015959 | 8.7689e-05 | 2016 | 2015-07-19 | C | 29 | 0.015959 | 8.7689e-05
3131287938 | 2015-07-19 20:09 | 2015-07-19 22:23 | 133.6333 | 1 | 133.6333 | 133.6333 | 130.6333 | 0.00040408 | 130.6333 | 0.000395 | 3.0238e-06 | Restore Supply on Device TC5-008 | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | another FM already on site doing a cable fault - is a part of OMS 3131281580 | F2 | BAYFAIR | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 2015-07-19 | c | 0.000395 | 3.024e-06 | 2016 | 2015-07-19 | C | 1 | 0.000395 | 3.0238e-06
3131288038 | 2015-07-20 00:32 | 2015-07-20 16:45 | 973 | 11 | 10703 | 973 | 970 | 0.032363 | 10670 | 0.032264 | 3.3261e-05 | Electric Job | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5972 | Replace faulty transformer. 10.13am Lucy called to advise Malcolm Sheild is onsite and they are waiting for Metering Solutions to attend. Fisrt transformer installed found to be faulty, replacement sourced & installed, all in service Materials 3 x 160A L/ | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 2015-07-20 | c | 0.032264 | 3.3261e-05 | 2016 | 2015-07-20 | C | 11 | 0.032264 | 3.3261e-05
3131289904 | 2015-07-20 09:00 | 2015-07-20 12:51 | 230.7333 | 15 | 2058.3 | 137.22 | 134.22 | 0.0062238 | 2013.3 | 0.0060877 | 4.5356e-05 | Restore Supply on Device WH270 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725780 | Repair Lines down past fuses WH212. Isolation at Fuses WH270 as they need to terminate the line to the fuses WH212. No Back feeds available. Materials 200m squirrel conductor, 2xfull tension sleeves 3x6amp HV Fuses. Line down at Pole 725782 as well. Isol | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.0060877 | 4.5356e-05 | 2016 | 2015-07-20 | C | 15 | 0.0060877 | 4.5356e-05
3131290016 | 2015-07-20 10:45 | 2015-07-20 13:16 | 151 | 75 | 11325 | 151 | 148 | 0.034244 | 11100 | 0.033564 | 0.00022678 | Restore Supply on Device 2429T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736212 | lines down across the Driveway - 1410 Rawhitiroa Rd - Eltham. 9:38am called through to hub - Tallia. Repaired line down at Pole 736212. Isolated at ABS 6121 no back feeds available Material 2 copper sleeves, 8m 7-064 copper conductor | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.033564 | 0.00022678 | 2016 | 2015-07-20 | C | 75 | 0.033564 | 0.00022678
3131293199 | 2015-07-20 08:36 | 2015-07-20 11:35 | 178.7667 | 62 | 11083.5333 | 178.7667 | 175.7667 | 0.033514 | 10897.5333 | 0.032952 | 0.00018747 | Restore Supply on Device TA720 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713420 | Replace Broken polymer strain insulator at pole 713420. Isolation at ABS TA119 & TA720 No Back feeds available. Materials 1 11kV polymer strain insulator, 1x16mm pre formed dead end, 1 eye bolt | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.032952 | 0.00018747 | 2016 | 2015-07-20 | C | 62 | 0.032952 | 0.00018747
3131293655 | 2015-07-20 15:15 | 2015-07-22 15:00 | 2865.0333 | 28 | 5006.8667 | 178.8167 | 175.8167 | 0.01514 | 4922.8667 | 0.014886 | 8.4665e-05 | Restore Supply on Device G26T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G26T | tx g24, tripped on the hv side of the tx. Control did not want to re-liven as there may be a cable fault. back fed through lv. someone will do testing tomorrow. 21/7 - sent e-mail to smc for an update. 27/7 emailed svs hub for update Disconnected transfor | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.014886 | 8.4665e-05 | 2016 | 2015-07-20 | C | 28 | 0.014886 | 8.4665e-05
3131293742 | 2015-07-20 17:34 | 2015-07-20 18:30 | 56.0333 | 26 | 1456.8667 | 56.0333 | 53.0333 | 0.0044052 | 1378.8667 | 0.0041694 | 7.8618e-05 | Referral: Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224259 | Follow-Up job - replace insulator and possible crossarm at Pole 224259, Te Puke CB 3 Maketu Feeder. Clint Johnstone knows about this job. Materials Replaced 1 x 11kV crossarm & 3 x H/V insulators | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 2015-07-20 | c | 0.0041694 | 7.8618e-05 | 2016 | 2015-07-20 | C | 26 | 0.0041694 | 7.8618e-05
3131293799 | 2015-07-20 18:40 | 2015-07-20 19:05 | 25 | 33 | 825 | 25 | 22 | 0.0024946 | 726 | 0.0021953 | 9.9784e-05 | Restore Supply on Device T1/19 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M9 | plz check if oms 3131293806 related 479 Ngaio Road part power. and oms 3131293853 512 Ngaio Road, Part power 1 X 10 Amp Fuse At M9. Isolated at M7 for Satefy | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.0021953 | 9.9784e-05 | 2016 | 2015-07-20 | C | 33 | 0.0021953 | 9.9784e-05
3131294021 | 2015-07-20 18:19 | 2015-07-20 19:26 | 66.3333 | 4 | 265.3333 | 66.3333 | 63.3333 | 0.0008023 | 253.3333 | 0.00076602 | 1.2095e-05 | Restore Supply on Device X2484 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2930 | was 3131293870 at tap level, split into two - 2930 2 x 15 amp 11kv fuses. cause wind. FM worked through control Nothing else repaired or replaced. Adjacent assets up to Powerco standard | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.00076602 | 1.2095e-05 | 2016 | 2015-07-20 | C | 4 | 0.00076602 | 1.2095e-05
3131294744 | 2015-07-20 21:09 | 2015-07-20 23:42 | 152.3833 | 1 | 152.3833 | 152.3833 | 149.3833 | 0.00046077 | 149.3833 | 0.0004517 | 3.0238e-06 | Restore Supply on Device X887 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 899 | 9.46pm called svs hub to advise of 999 2 X 6 am Fuses H/T | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.0004517 | 3.024e-06 | 2016 | 2015-07-20 | C | 1 | 0.0004517 | 3.0238e-06
3131294763 | 2015-07-20 21:38 | 2015-07-21 12:42 | 904.25 | 58 | 36261.45 | 625.1974 | 622.1974 | 0.10965 | 36087.45 | 0.10912 | 0.00017538 | Restore Supply on Device X2273 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786707 | Tripping on recloser CB4230. Feeder patrolled during night time which proved difficult with terrain and snowy conditions. Area left off from fuses 893 until daylight patrol carried out. Broken conductor found down near Napier-Taihape Rd. Required 30m cond | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-07-20 | c | 0.10912 | 0.00017538 | 2016 | 2015-07-20 | C | 58 | 0.10912 | 0.00017538
3131295055 | 2015-07-21 01:11 | 2015-07-21 01:23 | 12.1667 | 296 | 3601.3333 | 12.1667 | 9.1667 | 0.01089 | 2713.3333 | 0.0082045 | 0.00089503 | Restore Supply on Device C917 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C917 | Featherston C917 tripped at 0111. Line not patrolled. Cause unknown. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-07-21 | c | 0.0082045 | 0.00089503 | 2016 | 2015-07-21 | C | 296 | 0.0082045 | 0.00089503
3131295463 | 2015-07-21 07:11 | 2015-07-21 09:13 | 121.7333 | 33 | 4017.2 | 121.7333 | 118.7333 | 0.012147 | 3918.2 | 0.011848 | 9.9784e-05 | Restore Supply on Device X248 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 939 | Also check 3131295477 (113 SNELLGROVE ROAD) & 3131295499 & 3131295509 (641 & 702 FERN FLATS ROAD) . Patrol carried out, 2 Fuses found tripped at 939. Reclosed OK. suspect bird strike. 2 X 15A fuses replaced. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-07-21 | c | 0.011848 | 9.9784e-05 | 2016 | 2015-07-21 | C | 33 | 0.011848 | 9.9784e-05
3131296343 | 2015-07-21 09:41 | 2015-07-21 10:43 | 62.3833 | 1 | 62.3833 | 62.3833 | 59.3833 | 0.00018863 | 59.3833 | 0.00017956 | 3.0238e-06 | Restore Supply on Device X776 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | X776 | 3 HT fuses tripped. Reloaded OK. Lightning in area. (2A rating). Completed by J.Prime (On 2R job for all fuses in area) | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-07-21 | c | 0.00017956 | 3.024e-06 | 2016 | 2015-07-21 | C | 1 | 0.00017956 | 3.0238e-06
3131296435 | 2015-07-21 08:57 | 2015-07-21 10:17 | 80.8167 | 5 | 404.0833 | 80.8167 | 77.8167 | 0.0012219 | 389.0833 | 0.0011765 | 1.5119e-05 | Restore Supply on Device X984 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | X984 | 1 HT fuse tripped at X984, Reloaded OK. Suspect lightning. (2A Rating). Also replaced upon patrol: 1x 5A DDO candle at fuse 1041, 1x 2A DDO Candle at TX X984, 3x 2A Fuses at TX X776, 1x 2A DDO candle at TX X1433 - signed off Control so will have on/off ti | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 2015-07-21 | c | 0.0011765 | 1.5119e-05 | 2016 | 2015-07-21 | C | 5 | 0.0011765 | 1.5119e-05
3131297106 | 2015-07-21 12:46 | 2015-07-21 15:08 | 142.3167 | 149 | 13212.8667 | 88.677 | 85.677 | 0.039953 | 12765.8667 | 0.038601 | 0.00045054 | Restore Supply on Device 284 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 284 | Tripping on Recloser CB284 on E/F, Phase C O/C. Feeder patrolled / sectionalised but all restored OK. Cause unknown. emailed Paul for sign off stuck job 24/7 12.53pm - SMC advise FM was not signed off by Control but he has closed the job off with Control. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-21 | c | 0.038601 | 0.00045054 | 2016 | 2015-07-21 | C | 149 | 0.038601 | 0.00045054
3131300965 | 2015-07-22 10:30 | 2015-07-22 11:00 | 30 | 1 | 30 | 30 | 27 | 9.0713e-05 | 27 | 8.1642e-05 | 3.0238e-06 | Restore Supply on Device T9/292 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T9/290 | full supply at main switch board, however it is low voltage of 225V - 226V. causing 3 phase equipment not working properly. FM needs to do an internal tap change, has never done one before and will go back first thing tomorrow morning with supervisor to d | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-22 | c | 8.1642e-05 | 3.024e-06 | 2016 | 2015-07-22 | C | 1 | 8.1642e-05 | 3.0238e-06
3131301208 | 2015-07-21 19:03 | 2015-07-21 20:40 | 96.9167 | 2 | 175.2833 | 87.6417 | 84.6417 | 0.00053001 | 169.2833 | 0.00051187 | 6.0475e-06 | Restore Supply on Device 2057W | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2057W | *** please check if oms 3131301212 - end of Kaitoke Road is affected *** - yes affected - 2 blown hv fuses feeding whole line. worked through control. replaced 2 x 10 amp hv fuses. Nothing else repaired or replaced. Adjacent assets up to Powerco standar | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 2015-07-21 | c | 0.00051187 | 6.048e-06 | 2016 | 2015-07-21 | C | 2 | 0.00051187 | 6.0475e-06
3131301271 | 2015-07-21 21:53 | 2015-07-21 23:44 | 111.4667 | 139 | 14150.0667 | 101.799 | 98.799 | 0.042786 | 13733.0667 | 0.041526 | 0.0004203 | Restore Supply on Device 2 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | G0282 | BRN 5 recloser 9664 tripped E/F, C Ph O/C, L/O feeder sectionalised & possum found on line at pole G0282 ( no possum guards on any poles ) possum removed all service restored | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 2015-07-21 | c | 0.041526 | 0.0004203 | 2016 | 2015-07-21 | C | 139 | 0.041526 | 0.0004203
3131301640 | 2015-07-22 11:18 | 2015-07-22 12:11 | 52.5 | 37 | 1934.2 | 52.2757 | 49.2757 | 0.0058486 | 1823.2 | 0.0055129 | 0.00011188 | Restore Supply on Device TC2478 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2478 | Burnt Jumper found at Transformer TC2478 - Isolated at ABS's 579 & 593 - Jumper Repaired - No Materials used | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2015-07-22 | c | 0.0055129 | 0.00011188 | 2016 | 2015-07-22 | C | 37 | 0.0055129 | 0.00011188
3131303730 | 2015-07-22 13:10 | 2015-07-22 14:05 | 55 | 7 | 385 | 55 | 52 | 0.0011641 | 364 | 0.0011006 | 2.1166e-05 | Electric Job | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 359589 | Carry out line patrol.Faultman found a broken king bolt on pole 359589 and a missing bolt to arm strap on pole 818716, line was isolated at Fuses 7215 to make the repairs. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.0011006 | 2.1166e-05 | 2016 | 2015-07-22 | C | 7 | 0.0011006 | 2.1166e-05
3131303828 | 2015-07-22 11:06 | 2015-07-22 14:16 | 189.7 | 1 | 189.7 | 189.7 | 186.7 | 0.00057361 | 186.7 | 0.00056454 | 3.0238e-06 | Restore Supply on Device 5548E | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8804 | 2 fuses found blown at Fuses 8804 - Line Patrolled with no fault - used 2 x 10 amp fuses | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.00056454 | 3.024e-06 | 2016 | 2015-07-22 | C | 1 | 0.00056454 | 3.0238e-06
3131305919 | 2015-07-22 14:48 | 2015-07-22 15:56 | 68 | 35 | 2380 | 68 | 65 | 0.0071966 | 2275 | 0.0068791 | 0.00010583 | Restore Supply on Device R54 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P43178 | Faultman found a broken cross arm on pole P43178 & part of the pole is burnt off and will need to be replace at a later date. Line was isolated at Fuses R54 to replace the cross arm & hardware only. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.0068791 | 0.00010583 | 2016 | 2015-07-22 | C | 35 | 0.0068791 | 0.00010583
3131305979 | 2015-07-22 17:17 | 2015-07-22 19:20 | 123.4333 | 19 | 2345.2333 | 123.4333 | 120.4333 | 0.0070914 | 2288.2333 | 0.0069191 | 5.7451e-05 | Restore Supply on Device T462 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811995 | Broken conductor found beyond ABS S546. Isolation made from there with 3.5m conductor replaced, rehung. Livened OK. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.0069191 | 5.7451e-05 | 2016 | 2015-07-22 | C | 19 | 0.0069191 | 5.7451e-05
3131306057 | 2015-07-22 15:57 | 2015-07-22 17:17 | 79.8 | 1 | 79.8 | 79.8 | 76.8 | 0.0002413 | 76.8 | 0.00023222 | 3.0238e-06 | Restore Supply on Device X2516 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2516 | possum on tx replaced 2 x 2 amp fuses. X2516 Nothing else repaired or replaced. Adjacent assets up to Powerco standard. Spoke to control, they hadn't heard from FM. Ok'ed to sign off job. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.00023222 | 3.024e-06 | 2016 | 2015-07-22 | C | 1 | 0.00023222 | 3.0238e-06
3131306196 | 2015-07-22 18:43 | 2015-07-23 01:33 | 409.7333 | 4 | 1638.9333 | 409.7333 | 406.7333 | 0.0049557 | 1626.9333 | 0.0049195 | 1.2095e-05 | Restore Supply on Device TC3052 | 11 | Unplanned | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC3052 | 7.35pm Fault with generator. FM has another generator coming in from tauranga - another couple of hours before up and running - (approx 9.30-10pm) coops called advising generator is coming from Hamilton now, estimated time to be running is 11.30pm Coops | F1/F3 | LOMOND AVE | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 2015-07-22 | c | 0.0049195 | 1.2095e-05 | 2016 | 2015-07-22 | C | 4 | 0.0049195 | 1.2095e-05
3131306344 | 2015-07-22 22:16 | 2015-07-22 23:51 | 94.9167 | 137 | 13003.5833 | 94.9167 | 91.9167 | 0.03932 | 12592.5833 | 0.038077 | 0.00041426 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6345 | 8.17pm advised hub of 999. HV fuse burning up - may need to change whole set of ddo's, FM is speaking to control.. Outage required from ABS 4930 to change all 3 DDOs at Fuses 6345. (Rating 40A). Relivened OK. | F2 | BROWNE ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.038077 | 0.00041425 | 2016 | 2015-07-22 | C | 137 | 0.038077 | 0.00041426
3131306370 | 2015-07-22 20:56 | 2015-07-22 22:28 | 91.7167 | 19 | 1742.6167 | 91.7167 | 88.7167 | 0.0052693 | 1685.6167 | 0.0050969 | 5.7451e-05 | Restore Supply on Device 4428W | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 495 | Patrol carried out - 2 HT fuses reloaded at 495. Suspect bird. (10A Rating). Please check if 3131306370 & 3131306374 &3131306388 are related . | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.0050969 | 5.7451e-05 | 2016 | 2015-07-22 | C | 19 | 0.0050969 | 5.7451e-05
3131306378 | 2015-07-22 20:55 | 2015-07-22 22:27 | 92 | 5 | 460 | 92 | 89 | 0.0013909 | 445 | 0.0013456 | 1.5119e-05 | Restore Supply on Device 243 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3131306370 poss related | Associated with 3131306370 - failed to unlock | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 2015-07-22 | c | 0.0013456 | 1.5119e-05 | 2016 | 2015-07-22 | C | 5 | 0.0013456 | 1.5119e-05
3131309808 | 2015-07-23 21:13 | 2015-07-23 23:56 | 162.7667 | 770 | 66027 | 85.7494 | 82.7494 | 0.19965 | 63717 | 0.19266 | 0.0023283 | Restore Supply on Device 6 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 748283 | Tripping on CB6 on E/F. (Car / Pole). Isolation required between ABS 384 and 283 with backfeed at ABS 105. One Broken HT crossarm replaced along with associated hardware. Relivened OK. NDR 45710 | F3 | MOTUROA 6 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 2015-07-23 | c | 0.19266 | 0.0023283 | 2016 | 2015-07-23 | C | 770 | 0.19266 | 0.0023283
3131310752 | 2015-07-24 07:22 | 2015-07-24 09:27 | 125.45 | 22 | 2759.9 | 125.45 | 122.45 | 0.0083453 | 2693.9 | 0.0081457 | 6.6523e-05 | Restore Supply on Device X439 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | X439 | Advised hub and control of 999 - Possibly related to 3131310745 - poss lost HV fuses 2813 check to see if oms 3131312067 (4979 Manui Road, Mangaweka) is related. Fuses 2813 found blown. A tree has come down through the LV lines from Transformer X439 and | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 2015-07-24 | c | 0.0081457 | 6.6523e-05 | 2016 | 2015-07-24 | C | 22 | 0.0081457 | 6.6523e-05
3131310774 | 2015-07-24 07:45 | 2015-07-24 09:17 | 91.9 | 472 | 28684.1333 | 60.7715 | 57.7715 | 0.086734 | 27268.1333 | 0.082452 | 0.0014272 | Restore Supply on Device KPT-CB2 | 11 | Unplanned | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CB 2 Kauri Point sub | CB 2 Kauri Point sub tripped to L/O. No flags. 2 x 1 r requested. Line sectionalised & patrolled. No apparent line fault found. All supply restored via backfeeds with CB 2 being left out of service. Another 1 r created to have tech check out CB for operat | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 2015-07-24 | c | 0.082452 | 0.0014272 | 2016 | 2015-07-24 | C | 472 | 0.082452 | 0.0014272
3131313003 | 2015-07-24 09:30 | 2015-07-24 13:40 | 250 | 68 | 17000 | 250 | 247 | 0.051404 | 16796 | 0.050787 | 0.00020562 | Restore Supply on Device E24 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P17314 | NAPA 11428 to intall new 11kV pole away from slip. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-07-24 | b | 0.025394 | 0.00010281 | 2016 | 2015-07-24 | B | 68 | 0.050787 | 0.00020562
3131313209 | 2015-07-24 11:00 | 2015-07-24 13:17 | 137 | 35 | 4795 | 137 | 134 | 0.014499 | 4690 | 0.014181 | 0.00010583 | Restore Supply on Device R54 | 11 | Unplanned | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | P43178 | Replace pole P43178 only, top of pole is burnt off faultman may replace pole 23/07/15 will notify NOC Control. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 2015-07-24 | c | 0.014181 | 0.00010583 | 2016 | 2015-07-24 | C | 35 | 0.014181 | 0.00010583
3131313280 | 2015-07-20 09:51 | 2015-07-24 12:14 | 5903.2 | 3 | 269.2 | 89.7333 | 86.7333 | 0.000814 | 260.2 | 0.00078678 | 9.0713e-06 | Restore Supply on Device 5234 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 5234 | Replace transformer 4038T. W/O 10207332. Job Generated from planned work NAPA 11329 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-20 | b | 0.00039339 | 4.536e-06 | 2016 | 2015-07-20 | B | 3 | 0.00078678 | 9.0713e-06
3131314597 | 2015-07-24 19:22 | 2015-07-26 11:31 | 2408.6833 | 46 | 28787.6333 | 625.8181 | 622.8181 | 0.087047 | 28649.6333 | 0.08663 | 0.00013909 | Restore Supply on Device T9/407 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27933 | Faultman found CB I23 open when checking no power complaints, line was patrolled and sectionalised at ABS I27, faultman will return in morning as line go over cross country and can no see any at night. Line patrolled with no obvious fault found. Line brea | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-07-24 | c | 0.08663 | 0.00013909 | 2016 | 2015-07-24 | C | 46 | 0.08663 | 0.00013909
3131318742 | 2015-07-25 11:30 | 2015-07-25 13:50 | 140 | 3 | 420 | 140 | 137 | 0.00127 | 411 | 0.0012428 | 9.0713e-06 | Restore Supply on Device TC4521 | 11 | Planned | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC4521 | Repair trany tc4521 NAPA 11444 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 2015-07-25 | b | 0.00062138 | 4.536e-06 | 2016 | 2015-07-25 | B | 3 | 0.0012428 | 9.0713e-06
3131318763 | 2015-07-25 12:01 | 2015-07-25 14:02 | 121.1167 | 799 | 46559.55 | 58.2723 | 55.2723 | 0.14078 | 44162.55 | 0.13354 | 0.002416 | Restore Supply on Device 6321 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5712 | Fire advised 45 Pembroke Stratford pole 734044. advised Glo and control. used close ICP. ETA 5 mins fire advised. CLO S51 tripped C Ph O/C, E/F L/O Recloser 6942 ( CLO S41 tripped same time. Report of kids tampering with ABS 5712 ( found with broken handl | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-07-25 | c | 0.13354 | 0.002416 | 2016 | 2015-07-25 | C | 799 | 0.13354 | 0.002416
3131318873 | 2015-07-25 12:03 | 2015-07-25 13:13 | 70.4667 | 2 | 140.9333 | 70.4667 | 67.4667 | 0.00042615 | 134.9333 | 0.00040801 | 6.0475e-06 | Restore Supply on Device 6942 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 6942 | CLO S51 tripped C Ph O/C E/F causing Recloser 6942 to trip. O/H to Cheal A checked ok Recloser 6942 returned to service Cheal A advised ok to resume generation see oms 3131318763 | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 2015-07-25 | c | 0.00040801 | 6.048e-06 | 2016 | 2015-07-25 | C | 2 | 0.00040801 | 6.0475e-06
3131319774 | 2015-07-25 12:29 | 2015-07-25 12:30 | 1 | 189 | 189 | 1 | -2 | 0.00057149 | 0 | 0 | 0.00057149 | Restore Supply on Device 12 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 12 | KAR 12 tripped E/F, A/R line patrolled no fault found | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-07-25 | c | 0 | 0.00057149 | 2016 | 2015-07-25 | C | 189 | 0 | 0.00057149
3131320505 | 2015-07-25 14:36 | 2015-07-25 16:43 | 126.9833 | 1 | 126.9833 | 126.9833 | 123.9833 | 0.00038397 | 123.9833 | 0.0003749 | 3.0238e-06 | Restore Supply on Device X1407 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | advised hub and control 235 WAITANGI ROAD , WAVERLEY Disconnect for safety private line, customer advised | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-25 | c | 0.0003749 | 3.024e-06 | 2016 | 2015-07-25 | C | 1 | 0.0003749 | 3.0238e-06
3131320669 | 2015-07-25 18:19 | 2015-07-25 19:10 | 50.8 | 10 | 508 | 50.8 | 47.8 | 0.0015361 | 478 | 0.0014454 | 3.0238e-05 | Restore Supply on Device 852 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6571 | Faultman found 2 blown fuse at Fuses 6571, line was patrolled and suspect lines hit by ducks from pond near lines. 2 x 40 amp HV fuses replaced. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 2015-07-25 | c | 0.0014454 | 3.0238e-05 | 2016 | 2015-07-25 | C | 10 | 0.0014454 | 3.0238e-05
3131346180 | 2015-07-26 03:50 | 2015-07-26 06:00 | 130 | 235 | 19877.4333 | 84.5848 | 81.5848 | 0.060105 | 19172.4333 | 0.057973 | 0.00071058 | Restore Supply on Device NG2 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712185 | CB NG 2 tripped on A phase E/F flags, line was patrolled and sectionalised and a broken insulator on pole 712185, line was isolated at Fuses NG269. 1 x 11kV insulator replaced. 1 x Binder used. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-07-26 | c | 0.057973 | 0.00071058 | 2016 | 2015-07-26 | C | 235 | 0.057973 | 0.00071058
3131347286 | 2015-07-26 09:49 | 2015-07-26 11:03 | 74.4 | 1 | 74.4 | 74.4 | 71.4 | 0.00022497 | 71.4 | 0.0002159 | 3.0238e-06 | Restore Supply on Device X1338 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1338 | 3 x 2amp hv fuses x1338 worked through control cause unknown No other assets repaired or replaced, all adjacent assets checked and are up to Powerco Standard | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 2015-07-26 | c | 0.0002159 | 3.024e-06 | 2016 | 2015-07-26 | C | 1 | 0.0002159 | 3.0238e-06
3131347704 | 2015-07-26 15:51 | 2015-07-26 18:02 | 131.1 | 1 | 131.1 | 131.1 | 128.1 | 0.00039642 | 128.1 | 0.00038734 | 3.0238e-06 | Restore Supply on Device TD2-019 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD2-019 | 2 6 amp fuses and 1 carrier HT replace | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 2015-07-26 | c | 0.00038734 | 3.024e-06 | 2016 | 2015-07-26 | C | 1 | 0.00038734 | 3.0238e-06
3131349492 | 2015-07-27 07:44 | 2015-07-27 14:26 | 401.95 | 1 | 401.95 | 401.95 | 398.95 | 0.0012154 | 398.95 | 0.0012063 | 3.0238e-06 | Restore Supply on Device TC397 | 11 | Unplanned | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC397 | Replace blown 15kVA transformer ( B Sperling own isolation & AP ). Materials 1 x transformer , 3 x L/V 100A fuses & bases, 1 x mounting bracket | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 2015-07-27 | c | 0.0012063 | 3.024e-06 | 2016 | 2015-07-27 | C | 1 | 0.0012063 | 3.0238e-06
3131349766 | 2015-07-27 09:22 | 2015-07-27 11:22 | 119.8667 | 1 | 119.8667 | 119.8667 | 116.8667 | 0.00036245 | 116.8667 | 0.00035338 | 3.0238e-06 | Restore Supply on Device T9/486 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I44 | Check to see if 3131349773 (544 Alfredton Road) is related check to see if 3131349936 - (842 Alfredton Road) is related | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 2015-07-27 | c | 0.00035338 | 3.024e-06 | 2016 | 2015-07-27 | C | 1 | 0.00035338 | 3.0238e-06
3131350826 | 2015-07-27 18:15 | 2015-07-27 21:04 | 169.0333 | 1 | 169.0333 | 169.0333 | 166.0333 | 0.00051112 | 166.0333 | 0.00050205 | 3.0238e-06 | Restore Supply on Device 4504W | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Kohi Road | Check 1 and 68 NGAMOTU ROAD. Replaced 2x 8A Temp 03 HV fuse. Nothing else repaired or replaced All other assets up to Powerco standard. Called the hub at 8:50pm as FM had not called in and signed off - Steve called 9:00pm to complete | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 2015-07-27 | c | 0.00050205 | 3.024e-06 | 2016 | 2015-07-27 | C | 1 | 0.00050205 | 3.0238e-06
3131353201 | 2015-07-27 21:37 | 2015-07-28 01:06 | 209 | 1394 | 89159 | 63.9591 | 60.9591 | 0.2696 | 84977 | 0.25695 | 0.0042151 | Electric Job | 11 | Unplanned | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T3/133 | Job to be recreated. CB Tripped C Ph O/C E/F - Cable fault found between Transformers T3/133 and T3/281 - Isolated at Sw/Gear 257 & 378 - Line breaks installed at Transformers | F3 | RESIDENTIAL | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 2015-07-27 | c | 0.25695 | 0.0042151 | 2016 | 2015-07-27 | C | 1394 | 0.25695 | 0.0042151
3131353229 | 2015-07-28 00:15 | 2015-07-28 01:15 | 60.05 | 4 | 239.25 | 59.8125 | 56.8125 | 0.00072343 | 227.25 | 0.00068715 | 1.2095e-05 | Restore Supply on Device T4008 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 827798 | Lines down found at Pole 827798 - Isolated at fuses 7110 - repairs made - used 5 mtr conductor 2x sleeves | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.00068715 | 1.2095e-05 | 2016 | 2015-07-28 | C | 4 | 0.00068715 | 1.2095e-05
3131354355 | 2015-07-28 05:35 | 2015-07-28 07:20 | 105.1 | 7 | 735.7 | 105.1 | 102.1 | 0.0022246 | 714.7 | 0.0021611 | 2.1166e-05 | Restore Supply on Device 2292T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4982 | Replace 2 x 8A H/V, O/H fuses | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.0021611 | 2.1166e-05 | 2016 | 2015-07-28 | C | 7 | 0.0021611 | 2.1166e-05
3131355661 | 2015-07-28 06:20 | 2015-07-28 06:55 | 35 | 189 | 756 | 4 | 1 | 0.002286 | 189 | 0.00057149 | 0.00057149 | Restore Supply on Device T6/100 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T6/100 | a/r caused by blown insulator on job 3131355860 | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.00057149 | 0.00057149 | 2016 | 2015-07-28 | C | 189 | 0.00057149 | 0.00057149
3131355860 | 2015-07-28 06:51 | 2015-07-28 09:42 | 171.0167 | 38 | 3257.5167 | 85.7241 | 82.7241 | 0.00985 | 3143.5167 | 0.0095052 | 0.0001149 | Restore Supply on Device T6/100 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p43604 | blow insulator at pole p43604 zane marshal attended | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.0095052 | 0.0001149 | 2016 | 2015-07-28 | C | 38 | 0.0095052 | 0.0001149
3131355897 | 2015-07-28 07:41 | 2015-07-28 09:58 | 137.0333 | 1 | 137.0333 | 137.0333 | 134.0333 | 0.00041436 | 134.0333 | 0.00040528 | 3.0238e-06 | Restore Supply on Device T9/235 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V74 | Replaced 2 x HV fuses at V74 and 2 x HV fuses at the transfrmer replaced. Due to lightning. NOte Completed in morning (0800), OMS completed in Afternoon. KPI's met | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.00040529 | 3.024e-06 | 2016 | 2015-07-28 | C | 1 | 0.00040528 | 3.0238e-06
3131355905 | 2015-07-28 07:45 | 2015-07-28 07:47 | 1.9833 | 3 | 5.95 | 1.9833 | -1.0167 | 1.7991e-05 | 0 | 0 | 9.0713e-06 | Restore Supply on Device H122 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | part of insulator fault on kairanga | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0 | 9.071e-06 | 2016 | 2015-07-28 | C | 3 | 0 | 9.0713e-06
3131359330 | 2015-07-28 08:11 | 2015-07-28 15:36 | 444.55 | 41 | 18226.55 | 444.55 | 441.55 | 0.055113 | 18103.55 | 0.054741 | 0.00012397 | Restore Supply on Device 6 | 11 | Planned | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | - | Restring the 11kV and the 33kV conductor between poles 706756 and pole 706750. Five spans with a helicopter. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 2015-07-28 | b | 0.02737 | 6.1987e-05 | 2016 | 2015-07-28 | B | 41 | 0.054741 | 0.00012397
3131359591 | 2015-07-28 10:01 | 2015-07-28 10:08 | 7.1167 | 3 | 21.35 | 7.1167 | 4.1167 | 6.4557e-05 | 12.35 | 3.7343e-05 | 9.0713e-06 | Restore Supply on Device V74 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V74 | Blown fuse V74. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 3.7343e-05 | 9.071e-06 | 2016 | 2015-07-28 | C | 3 | 3.7343e-05 | 9.0713e-06
3131359606 | 2015-07-28 12:03 | 2015-07-28 12:14 | 11.6833 | 44 | 514.0667 | 11.6833 | 8.6833 | 0.0015544 | 382.0667 | 0.0011553 | 0.00013305 | Site Inspection - Report From Public on Device NA | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 711854 | ADVISED CONTROL AND HUB. Magpie on line at pole 711854. Emergency switching required for removal, between normal open points ABS's NG248, NG479 & ABS NG426. Bird removed and all service restored. Nil materials. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.0011553 | 0.00013305 | 2016 | 2015-07-28 | C | 44 | 0.0011553 | 0.00013305
3131359805 | 2015-07-28 19:08 | 2015-07-28 19:26 | 18.1667 | 47 | 726.2333 | 15.4518 | 12.4518 | 0.002196 | 585.2333 | 0.0017696 | 0.00014212 | Restore Supply on Device 2167T | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2167T | Replace Faulty Fuses at Transformer 2167T. 1 DDO At Transformer 2167T | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.0017696 | 0.00014212 | 2016 | 2015-07-28 | C | 47 | 0.0017696 | 0.00014212
3131359975 | 2015-07-28 13:20 | 2015-07-28 16:47 | 207 | 118 | 24426 | 207 | 204 | 0.073858 | 24072 | 0.072788 | 0.0003568 | Restore Supply on Device V61 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04629 | Recloser V61 A/R, L/O, E/F. Recloser remained closed on Scada due to Comms fault so was not apparent at first that it was an HV fault. Found floating conductor due to broken binders. Rebound conductor to pole and replaced 3x Binders (6mtrs of Ali Binder) | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.072788 | 0.0003568 | 2016 | 2015-07-28 | C | 118 | 0.072788 | 0.0003568
3131360112 | 2015-07-28 13:30 | 2015-07-28 16:41 | 191 | 113 | 21583 | 191 | 188 | 0.065262 | 21244 | 0.064237 | 0.00034168 | Restore Supply on Device T10 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837852 | RS C224/2 A/R, L/O, E/F. Patrol carried out with floating conductor and end burnt of crossarm found at Pole 837852. Crossarm replaced complete with 3Pins & Insulators, Arm Straps, Binders, & Bolts | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.064237 | 0.00034168 | 2016 | 2015-07-28 | C | 113 | 0.064237 | 0.00034168
3131360149 | 2015-07-28 01:16 | 2015-07-29 14:47 | 2251.2167 | 118 | 10092 | 85.5254 | 82.5254 | 0.030516 | 9738 | 0.029445 | 0.0003568 | Restore Supply on Device T9/226 | 11 | Unplanned | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | T9/226 | There are no outage notes located at this point but checking customer notes confirms there was an outage. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 2015-07-28 | c | 0.029445 | 0.0003568 | 2016 | 2015-07-28 | C | 118 | 0.029445 | 0.0003568
3131366859 | 2015-07-28 17:56 | 2015-07-28 20:07 | 131.0833 | 3 | 393.25 | 131.0833 | 128.0833 | 0.0011891 | 384.25 | 0.0011619 | 9.0713e-06 | Restore Supply on Device TC688 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IP416 | Advised hub and control of 999. Found 2 x 8amp fuses blown at IP416, Check line OK Replaced fuses No Fault found. Have reclosed - power is back on | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 2015-07-28 | c | 0.0011619 | 9.071e-06 | 2016 | 2015-07-28 | C | 3 | 0.0011619 | 9.0713e-06
3131367319 | 2015-07-29 02:05 | 2015-07-29 02:53 | 48 | 471 | 11853 | 25.1656 | 22.1656 | 0.035841 | 10440 | 0.031568 | 0.0014242 | Partial Supply/Supply Quality Issue on Device NA | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 5044 | Replaced all 3 Jumper Joins 1 Was blown off replaced other 2 as looked like they were no better at ABS 5044 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 2015-07-29 | c | 0.031568 | 0.0014242 | 2016 | 2015-07-29 | C | 471 | 0.031568 | 0.0014242
3131367888 | 2015-07-29 03:49 | 2015-07-29 04:15 | 26 | 1230 | 30160 | 24.5203 | 21.5203 | 0.091197 | 26470 | 0.080039 | 0.0037192 | Electric Job | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 776529 | CAR V POLE L/V. Service Pole to House No one lives in so Made safe will look at when Men come to work in Morning . NDR 22323. Ohakune police attended | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 2015-07-29 | c | 0.080039 | 0.0037192 | 2016 | 2015-07-29 | C | 1230 | 0.080039 | 0.0037192
3131369500 | 2015-07-29 08:34 | 2015-07-29 10:13 | 98.8833 | 2 | 27.9333 | 13.9667 | 10.9667 | 8.4464e-05 | 21.9333 | 6.6321e-05 | 6.0475e-06 | Restore Supply on Device TC2265 | 11 | Unplanned | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC1049 | Bird strike replace 2 x 20A H/V, O/H fuses | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 2015-07-29 | c | 6.6321e-05 | 6.048e-06 | 2016 | 2015-07-29 | C | 2 | 6.6321e-05 | 6.0475e-06
3131370084 | 2015-07-29 13:49 | 2015-07-29 14:41 | 51.6 | 15 | 774 | 51.6 | 48.6 | 0.0023404 | 729 | 0.0022043 | 4.5356e-05 | Restore Supply on Device 7379 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 817138 | Outage required from Fuses 7379 on Whakarua Rd to repair a floating conductor. (Fault advised by a Tanker Driver to faultman who was on another job). 2 Broken binders and 1 HV Insulator replaced. Relivened OK. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 2015-07-29 | c | 0.0022043 | 4.5356e-05 | 2016 | 2015-07-29 | C | 15 | 0.0022043 | 4.5356e-05
3131370358 | 2015-07-29 19:19 | 2015-07-29 20:25 | 65.9667 | 9544 | 522375.15 | 54.7334 | 51.7334 | 1.5795 | 493743.15 | 1.493 | 0.028859 | Restore Supply on Device 222 | 33 | Unplanned | ZONE SUB EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 102 | at 19:18 Greerton Sub, CB 222, Tripped, O/C, L/O. Bethlehem Sub, CB 172 Tripped, Distance Flag, L/O. Matua Sub, CB 72 T7 Transformer Bank, Tripped, No Flags, L/O. Faultmen dispatched and investigation began. 33kV BHM-OTE Line was patrolled as faultmen adv | F1,F2,F3 | GREERTON222-OTUMOETAI76 33KV | TAURANGA 31 | Tauranga | GREERTON | Eastern Electricity | POWERCO | 2015-07-29 | c | 1.493 | 0.028859 | 2016 | 2015-07-29 | C | 9544 | 1.493 | 0.028859
3131381461 | 2015-07-29 21:20 | 2015-07-29 22:25 | 65.4167 | 1 | 65.4167 | 65.4167 | 62.4167 | 0.0001978 | 62.4167 | 0.00018873 | 3.0238e-06 | Restore Supply on Device TE7-109 | 11 | Unplanned | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP892 | Ted Glasgow Attended. Found 2x Blown DDO's at Fuses FP892. Patrolled line, reloaded relivened 2x DDO's. All OK. OMS Job was not created for Fuses FP892. Unsure why job would not create when dressing fuses open on SCADA. reloaded, relivened at 22:25. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 2015-07-29 | c | 0.00018873 | 3.024e-06 | 2016 | 2015-07-29 | C | 1 | 0.00018873 | 3.0238e-06
[9 empty] | Total | 220.0289 | 2.1869 | [16 empty] | Total | 195.9649 | 2.0715
[9 empty] | Check to DPP | 220.029 | 2.187 | [15 empty] | Check to DPP disclosure |  | #REF! | #REF!
Formulas:
Date and time converted to Date only = INT([Reg Outage Start Date Time])
date = INT([Reg Outage Start Date Time])

## 2015
# | Fault Record ID | Interruption Date/Time | Restoration Date / Time | Duration | Sum of Customers affected | Sum of Customer Minutes | SAIDI | SAIFI | Fault Description | Voltage | Planned / Unplanned | System | MOC Classification | Cause of Fault | Defective Component | Reason and Comments | Feeder Security | Feeder | Substation | GXP | Network | Region | Owner | Nominal Duration | Adjusted Duration (Shave) | Adjusted Customer Minutes | Adjusted Saidi | Adjusted Saifi | Date and time converted to Date only | Class | SAIDI with planned at 50% weighting | SAIFI with planned at 50% weighting | disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
1 | 139866 | 2014-04-01 13:03 | 2014-04-01 13:48 | 45 | 6 | 270 | 0.00082469 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component - Found 2 burnt out DDO units at TA123. Isolated between ABS NG 425 & TA 101. Replaced all 3 units and relivened | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 252 | 0.00076971 | 1.8327e-05 | 2014-04-01 | C | 0.00076972 | 1.8327e-05 | 2015 | 2014-04-01 | C | 6 | 0.00076971 | 1.8327e-05
1 | 139868 | 2014-04-01 09:30 | 2014-04-01 14:19 | 289 | 54 | 15606 | 0.047667 | 0.00016494 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 13/85784 - Stage 8 of 10: Replace various pole and arms between pole 741971 and 741962. Isolation points: 11kV ABS 238, line break at pole 849767. PD 18.03.14 | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 289 | 286 | 15444 | 0.047173 | 0.00016494 | 2014-04-01 | B | 0.023586 | 8.2469e-05 | 2015 | 2014-04-01 | B | 54 | 0.047173 | 0.00016494
1 | 139871 | 2014-04-01 11:45 | 2014-04-01 12:19 | 34 | 1 | 34 | 0.00010385 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | No Power - Kerepehi Cb 2 No Trip. Isolation at fuses FP14213 to allow silage wrapper to be removed from the lines using hotsticks. Pole 383029. Faultman Stu Simpson. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 31 | 9.4687e-05 | 3.0544e-06 | 2014-04-01 | C | 9.4687e-05 | 3.054e-06 | 2015 | 2014-04-01 | C | 1 | 9.4687e-05 | 3.0544e-06
1 | 139875 | 2014-04-01 09:20 | 2014-04-01 15:22 | 362 | 35 | 12670 | 0.0387 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90252 - Change 11kV poles, X arms and reconductor. Refer to LLP 14/90250 (Create LLB) and LLP 14/90251 (Close LLB). Isolation points: 11kV ABS TEMP19 and Line Break at pole 217590. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 362 | 359 | 12565 | 0.038379 | 0.0001069 | 2014-04-01 | B | 0.019189 | 5.3452e-05 | 2015 | 2014-04-01 | B | 35 | 0.038379 | 0.0001069
1 | 139876 | 2014-04-01 09:51 | 2014-04-01 14:09 | 258 | 10 | 2580 | 0.0078804 | 3.0544e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90915 - Repair structure poles due to softwood pole burning down to ground level, pole no 785061. Isolation points: Fuses 154 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 258 | 255 | 2550 | 0.0077888 | 3.0544e-05 | 2014-04-01 | B | 0.0038944 | 1.5272e-05 | 2015 | 2014-04-01 | B | 10 | 0.0077888 | 3.0544e-05
1 | 139879 | 2014-04-01 09:20 | 2014-04-01 15:52 | 392 | 463 | 181496 | 0.55437 | 0.0014142 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90432 - Move poles for intersection re-alignment Arnott St. Isolation points: J41, 4444/1, 4444/4. Defered from March | F3 | RESIDENTIAL | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 392 | 389 | 180107 | 0.55012 | 0.0014142 | 2014-04-01 | B | 0.27506 | 0.0007071 | 2015 | 2014-04-01 | B | 463 | 0.55012 | 0.0014142
1 | 139880 | 2014-04-01 17:39 | 2014-04-01 18:58 | 79 | 24 | 1896 | 0.0057912 | 7.3306e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Faultman found a burnt cross arm on pole 805613 at transformer X1837 while attending a fault call, line was isolated at Fuses 495 to replace the burnt cross arm.Allen Cox attended | F4 | PUTORINO | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 79 | 76 | 1824 | 0.0055713 | 7.3306e-05 | 2014-04-01 | C | 0.0055713 | 7.3306e-05 | 2015 | 2014-04-01 | C | 24 | 0.0055713 | 7.3306e-05
1 | 139882 | 2014-04-02 08:56 | 2014-04-02 09:36 | 40 | 25 | 1000 | 0.0030544 | 7.6361e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | No Power -Lines Down at Pole 717421 Isolation Point Fuses TA857 No Back Feed Used 3m 7/16 Conductor & 2 selvees Henry Hood Attended | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 925 | 0.0028253 | 7.6361e-05 | 2014-04-02 | C | 0.0028253 | 7.6361e-05 | 2015 | 2014-04-02 | C | 25 | 0.0028253 | 7.6361e-05
1 | 139883 | 2014-04-01 17:00 | 2014-04-01 20:21 | 201 | 1 | 201 | 0.00061394 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Emergency switching to replace Transformer T2611 damaged by fire. Jason Hall issues own AP & isolations for Transformer replacement. Material 1 x Transformer | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 201 | 198 | 198 | 0.00060478 | 3.0544e-06 | 2014-04-01 | C | 0.00060478 | 3.054e-06 | 2015 | 2014-04-01 | C | 1 | 0.00060478 | 3.0544e-06
1 | 139884 | 2014-04-02 09:00 | 2014-04-02 11:15 | 135 | 45 | 6075 | 0.018556 | 0.00013745 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/87502 - Replacing 6.6kV TX Canopy/Kiosk, TX 2972T. Isolation points: 6.6kV ABS 5472. PD 19.03.2014 | F3 | BROOKES ST | INGLEWOOD SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 5940 | 0.018143 | 0.00013745 | 2014-04-02 | B | 0.0090716 | 6.8725e-05 | 2015 | 2014-04-02 | B | 45 | 0.018143 | 0.00013745
1 | 139887 | 2014-04-02 08:45 | 2014-04-02 13:00 | 255 | 56 | 17640 | 0.05388 | 0.00017105 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/90276 - Isolate 11kV Tx to lower oil level to repair leak. 11kV. Isolation points 11kV CB 47/3. Saidi not approved MR WH | F4 | MOTUROA 2 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 315 | 312 | 17472 | 0.053367 | 0.00017105 | 2014-04-02 | B | 0.026683 | 8.5524e-05 | 2015 | 2014-04-02 | B | 56 | 0.053367 | 0.00017105
1 | 139888 | 2014-04-02 08:47 | 2014-04-02 13:07 | 260 | 326 | 24900 | 0.076055 | 0.00099574 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | No Power - Kerepehi CB 3 No trip. Recloser RS9161 Trip No Flags. Line down at pole O1507 from suspect high load. LV Service line snap & wrapped up into HV. Isolation at ABS IC442 & IC452. Back fed from Kerepeki CB 6 via Sectionalizer 9724 NDR 31947 Faultm | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 76.3804 | 73.3804 | 23922 | 0.073068 | 0.00099574 | 2014-04-02 | C | 0.073068 | 0.00099574 | 2015 | 2014-04-02 | C | 326 | 0.073068 | 0.00099574
1 | 139889 | 2014-04-02 08:15 | 2014-04-02 09:06 | 51 | 8644 | 440844 | 1.3465 | 0.026402 | No Power | 66000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Third Party Damage - Kopu CB 1092 Trip E/F causing Loss of supply to Whitianga & Coromandel Substations. Reports received of Logging operation felling a tree that contacted the 66kV line Re: Blackjacks logging with CAC16453 logged on to network at 06:45 | F1,F2,F3 | Not entered | Not entered | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 51 | 48 | 414912 | 1.2673 | 0.026402 | 2014-04-02 | C | 1.2673 | 0.026402 | 2015 | 2014-04-02 | C | 8644 | 1.2673 | 0.026402
1 | 139890 | 2014-04-02 08:15 | 2014-04-02 10:37 | 142 | 2651 | 296736 | 0.90636 | 0.0080973 | No Power | 66000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Third Party Damage - Kopu CB 1092 Trip E/F causing Loss of supply to Whitianga & Coromandel Substations. Reports received of Logging operation felling a tree that contacted the 66kV line Re: Blackjacks logging with CAC16453 logged on to network at 06:45 | F1,F2,F3 | Not entered | Not entered | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 111.9336 | 108.9336 | 288783 | 0.88207 | 0.0080973 | 2014-04-02 | C | 0.88207 | 0.0080973 | 2015 | 2014-04-02 | C | 2651 | 0.88207 | 0.0080973
1 | 139891 | 2014-04-02 13:35 | 2014-04-02 16:35 | 180 | 69 | 12420 | 0.037936 | 0.00021076 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/87504 - Replacing TX canopy/kiosk, TX 443. Isolation points: Fuse 6589. PD 19.03.2014 | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 12213 | 0.037304 | 0.00021076 | 2014-04-02 | B | 0.018652 | 0.00010538 | 2015 | 2014-04-02 | B | 69 | 0.037304 | 0.00021076
1 | 139893 | 2014-04-02 09:15 | 2014-04-02 12:47 | 212 | 35 | 7420 | 0.022664 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90257 - Change 11kV poles, X-arms and reconductor. Isolation Points: 11kV ABS TEMP19 & SE3-015. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 212 | 209 | 7315 | 0.022343 | 0.0001069 | 2014-04-02 | B | 0.011172 | 5.3452e-05 | 2015 | 2014-04-02 | B | 35 | 0.022343 | 0.0001069
1 | 139901 | 2014-04-02 10:00 | 2014-04-02 14:00 | 240 | 35 | 8400 | 0.025657 | 0.0001069 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | CAPITAL WORKS | CABLE | SIN: 14/90465 - Reliven 11kV cable between poles 766401 and 766403 and remove tie between Makirikiri and Cemetary feeders. | F3 | CEMETERY | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 8295 | 0.025336 | 0.0001069 | 2014-04-02 | B | 0.012668 | 5.3452e-05 | 2015 | 2014-04-02 | B | 35 | 0.025336 | 0.0001069
1 | 139904 | 2014-04-03 09:00 | 2014-04-03 09:40 | 40 | 2 | 80 | 0.00024435 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90269 - Install LV fuses on existing pole mounted transformer. Transformers to be isolated via 11kV Transformer fuses and new 400V disconnector to be fitted. This is to be followed with an 400V Shut Down to complete cross arm replacement. W/O 1 | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 74 | 0.00022603 | 6.1088e-06 | 2014-04-03 | B | 0.00011301 | 3.054e-06 | 2015 | 2014-04-03 | B | 2 | 0.00022603 | 6.1088e-06
1 | 139905 | 2014-04-03 10:25 | 2014-04-03 12:11 | 106 | 2928 | 172329 | 0.52637 | 0.0089434 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 10:25 Welcome Bay Sub, CB 3 Welcome Bay Feeder, Tripped, No Flags L/O. Recloser 9412 also tripped, B Ph O/C, L/O. This feeder was also backfeeding majority of CB 2 Mangatapu feeder, ABS SD4-359 Closed & ABS SD4-360 is Open. Faultmen were disp | F3 | WELCOME BAY | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 58.8555 | 55.8555 | 163545 | 0.49954 | 0.0089434 | 2014-04-03 | C | 0.49954 | 0.0089434 | 2015 | 2014-04-03 | C | 2928 | 0.49954 | 0.0089434
1 | 139906 | 2014-04-03 08:15 | 2014-04-03 12:30 | 255 | 3 | 765 | 0.0023366 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | ISOLATION FOR SAFETY | CROSSARM | SIN: 14/90741 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Isolate 11kV Transformer TC760 to allow 400V X-arm replacement. Isolation point: 11kV transformer fuses TC760. | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 255 | 252 | 756 | 0.0023091 | 9.1633e-06 | 2014-04-03 | B | 0.0011546 | 4.582e-06 | 2015 | 2014-04-03 | B | 3 | 0.0023091 | 9.1633e-06
1 | 139908 | 2014-04-03 07:42 | 2014-04-03 09:21 | 99 | 456 | 44728 | 0.13662 | 0.0013928 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - CB 3062 at Browne St Sub tripped on O/ C. Supply to CB 7 & 9 was lost at Browne St Sub due to swtching that was done early on SIS 14/90759. Walton & Waharoa also lost supply. Reported fire at Lake Rd sub. Faultman sent to investigate | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 98.0877 | 95.0877 | 43360 | 0.13244 | 0.0013928 | 2014-04-03 | C | 0.13244 | 0.0013928 | 2015 | 2014-04-03 | C | 456 | 0.13244 | 0.0013928
1 | 139909 | 2014-04-03 09:15 | 2014-04-03 14:40 | 325 | 1 | 325 | 0.00099269 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/90339 - Tree work near 11kV pole 763622. 11kV. Isolation points 11kV fuse 5883. PPPD 38278. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 325 | 322 | 322 | 0.00098352 | 3.0544e-06 | 2014-04-03 | B | 0.00049176 | 1.527e-06 | 2015 | 2014-04-03 | B | 1 | 0.00098352 | 3.0544e-06
1 | 139910 | 2014-04-03 07:08 | 2014-04-03 15:14 | 486 | 691 | 63472 | 0.19387 | 0.0021106 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | HT Line - at 07:08, Whitianga Sub, CB 3 Kuaotunu Feeder, Recloser 9226 Tripped, No Flags L/O. Sectionaliser 9632 also Tripped, O/C, E/F. Faultmen Dispatched and Investigation Began. Backfeed was put in place at 07:26 from WHT CB 1 Owera Rd Feeder, Sw/gear | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 91.8553 | 88.8553 | 61399 | 0.18754 | 0.0021106 | 2014-04-03 | C | 0.18754 | 0.0021106 | 2015 | 2014-04-03 | C | 691 | 0.18754 | 0.0021106
1 | 139911 | 2014-04-03 10:19 | 2014-04-03 14:21 | 242 | 678 | 70978 | 0.2168 | 0.0020709 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - at 10:19 Whitianga Sub, CB 3 Kuaotunu Feeder, Tripped, No Flags, L/O. Sectionaliser 9219 Also Tripped, No Flags, L/O. Faultman Dispatched & Investigation Began. Feeder Sectionalised. Member of public advised faultman of seeing a big flash from ove | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 104.6873 | 101.6873 | 68944 | 0.21058 | 0.0020709 | 2014-04-03 | C | 0.21058 | 0.0020709 | 2015 | 2014-04-03 | C | 678 | 0.21058 | 0.0020709
1 | 139916 | 2014-04-03 07:42 | 2014-04-03 08:24 | 42 | 1119 | 46998 | 0.14355 | 0.0034179 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - CB 3062 at Browne St Sub tripped on O/C. Supply to CB 7 & 9 was lost at Browne St Sub due to swtching that was done early on SIS 14/90759. Walton & Waharoa also lost supply. Reported fire at Lake Rd sub. Faultman sent to investigate | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 43641 | 0.1333 | 0.0034179 | 2014-04-03 | C | 0.1333 | 0.0034179 | 2015 | 2014-04-03 | C | 1119 | 0.1333 | 0.0034179
1 | 139917 | 2014-04-03 07:42 | 2014-04-03 09:21 | 99 | 1336 | 130620 | 0.39897 | 0.0040807 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | JOINT FAILURE | CABLE | Defective Component - CB 3062 at Browne St Sub tripped on O/C. Supply to CB 7 & 9 was lost at Browne St Sub due to swtching that was done early on SIS 14/90759. Walton & Waharoa also lost supply. Reported fire at Lake Rd sub. Faultman sent to investigate | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 97.7695 | 94.7695 | 126612 | 0.38673 | 0.0040807 | 2014-04-03 | C | 0.38673 | 0.0040807 | 2015 | 2014-04-03 | C | 1336 | 0.38673 | 0.0040807
1 | 139920 | 2014-04-04 09:30 | 2014-04-04 12:58 | 208 | 1 | 208 | 0.00063532 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90675 - Replace rotten TX Xarms at TX T7/121. Isolation points: Fuses R61 | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 208 | 205 | 205 | 0.00062616 | 3.0544e-06 | 2014-04-04 | B | 0.00031308 | 1.527e-06 | 2015 | 2014-04-04 | B | 1 | 0.00062616 | 3.0544e-06
1 | 139921 | 2014-04-04 11:52 | 2014-04-04 12:48 | 56 | 20 | 1120 | 0.003421 | 6.1088e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component -Faultman patrolling for fault found a broken insulator at Pole P10158. Work area shutdown at Fuses N30 and the insulator was removed from the crossarm. Replacement not required as insulator was on a double arm. Relivened ok. Nil mater | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56 | 53 | 1060 | 0.0032377 | 6.1088e-05 | 2014-04-04 | C | 0.0032377 | 6.1088e-05 | 2015 | 2014-04-04 | C | 20 | 0.0032377 | 6.1088e-05
1 | 139922 | 2014-04-04 09:32 | 2014-04-04 17:15 | 463 | 25 | 11575 | 0.035355 | 7.6361e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90565 - Replace 11kV hardwood pole 210821 Live line, feeding G/M Transformer TD4-213 which will need to be isolated. Refer to LLP 14/90388. This Job went overtime by 3 hours. This was due to extra LV work on same pole and problems with conductors | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 463 | 460 | 11500 | 0.035126 | 7.6361e-05 | 2014-04-04 | B | 0.017563 | 3.818e-05 | 2015 | 2014-04-04 | B | 25 | 0.035126 | 7.6361e-05
1 | 139924 | 2014-04-04 23:05 | 2014-04-05 10:07 | 662 | 418 | 80272 | 0.24518 | 0.0012767 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident -CB C862 Trip, O/C C Phase. Car vs Pole. Work area isolated at CB C862, ABS S84 and ABS S180. Backfeeds put in via ABS S99 and S199. Temp repairs made and pole held in place with a hiab until the morning when a line crew could come and replace po | F3 | ESSEX ST | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 192.0383 | 189.0383 | 79018 | 0.24135 | 0.0012767 | 2014-04-04 | C | 0.24135 | 0.0012767 | 2015 | 2014-04-04 | C | 418 | 0.24135 | 0.0012767
1 | 139925 | 2014-04-05 09:09 | 2014-04-05 10:20 | 71 | 11 | 781 | 0.0023855 | 3.3599e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component -Faultman found a broken dropout fuse at Transformer 3190. Isolated at Fuses 5626 and fuse holder replaced. Relivened ok. Attended by Alan Rarere. Materials: 1x dropout fuse complete. | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 748 | 0.0022847 | 3.3599e-05 | 2014-04-05 | C | 0.0022847 | 3.3599e-05 | 2015 | 2014-04-05 | C | 11 | 0.0022847 | 3.3599e-05
1 | 139926 | 2014-04-05 11:20 | 2014-04-05 15:52 | 272 | 58 | 14281 | 0.04362 | 0.00017716 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird RS V27 A/R, E/F-B phase. No power faults began coming in so faultman dispatched to investigate. On arrival found Sectionaliser V41 tripped. Line sectionalised and patrolled and magpie found to be contacting line and crossarm. Magpie removed | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 246.2241 | 243.2241 | 14107 | 0.043089 | 0.00017716 | 2014-04-05 | C | 0.043089 | 0.00017716 | 2015 | 2014-04-05 | C | 58 | 0.043089 | 0.00017716
1 | 139927 | 2014-04-05 09:27 | 2014-04-05 13:29 | 242 | 33 | 7986 | 0.024393 | 0.0001008 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/88089 - To replace damaged 11kV & 33kV pole and cross arms on Hinuera to Tower Rd line. Isolation points: 33kV: 48 Lake Rd, 43 Lake Rd, 32 Tower Rd, 34 Tower Rd, 11kV: IC845, IC2666, IC787 | F3 | FIRTH ST | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 242 | 239 | 7887 | 0.02409 | 0.0001008 | 2014-04-05 | B | 0.012045 | 5.0398e-05 | 2015 | 2014-04-05 | B | 33 | 0.02409 | 0.0001008
1 | 139930 | 2014-04-04 10:13 | 2014-04-04 13:20 | 187 | 6 | 1122 | 0.0034271 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90482 - Replace burnt down 11kV pole in the swamp area of this spur line. Temporary repairs made during the storm to place supply back on. Isolation point: 11kV Fuses SD5-005 | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 187 | 184 | 1104 | 0.0033721 | 1.8327e-05 | 2014-04-04 | B | 0.001686 | 9.163e-06 | 2015 | 2014-04-04 | B | 6 | 0.0033721 | 1.8327e-05
1 | 139931 | 2014-04-06 00:05 | 2014-04-06 07:40 | 455 | 6 | 2730 | 0.0083386 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird 2 HT Fuses at 7495 found tripped. When reclosed a red glow was seen in distance. Patrol found very cooked up Magpie. Supply Restored OK. | F4 | MOROA | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 455 | 452 | 2712 | 0.0082836 | 1.8327e-05 | 2014-04-06 | C | 0.0082836 | 1.8327e-05 | 2015 | 2014-04-06 | C | 6 | 0.0082836 | 1.8327e-05
1 | 139933 | 2014-04-06 20:28 | 2014-04-06 21:56 | 88 | 5 | 440 | 0.0013439 | 1.5272e-05 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | MAINTENANCE | CABLE TERMINATION | SIN: 14/90966 - Urgent repair pitch leak from 11kV switch G30T. Isolation points: G30T | F3 | PASCAL ST 12 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 425 | 0.0012981 | 1.5272e-05 | 2014-04-06 | B | 0.00064906 | 7.636e-06 | 2015 | 2014-04-06 | B | 5 | 0.0012981 | 1.5272e-05
1 | 139937 | 2014-04-07 08:45 | 2014-04-07 11:08 | 143 | 2 | 286 | 0.00087357 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89403 - Replace defective 11kV poles 810909. Isolation points: Links 7428 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 143 | 140 | 280 | 0.00085524 | 6.1088e-06 | 2014-04-07 | B | 0.00042762 | 3.054e-06 | 2015 | 2014-04-07 | B | 2 | 0.00085524 | 6.1088e-06
1 | 139938 | 2014-04-07 11:07 | 2014-04-07 11:23 | 16 | 180 | 2880 | 0.0087967 | 0.0005498 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component -Faultman found the conductor on pole P00590 to be damaged while doing live line permit to replace 11KV insulators, CB 3 had to be opened as it was to dangerous to repair the conductor with the line alive under the live line permit.Rob | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 16 | 13 | 2340 | 0.0071474 | 0.0005498 | 2014-04-07 | C | 0.0071474 | 0.0005498 | 2015 | 2014-04-07 | C | 180 | 0.0071474 | 0.0005498
1 | 139939 | 2014-04-07 11:37 | 2014-04-07 12:30 | 53 | 5 | 265 | 0.00080942 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89404 - Replace defective 11kV poles 798958. Isolation points: Links 7347 | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 250 | 0.00076361 | 1.5272e-05 | 2014-04-07 | B | 0.0003818 | 7.636e-06 | 2015 | 2014-04-07 | B | 5 | 0.00076361 | 1.5272e-05
1 | 139942 | 2014-04-07 09:15 | 2014-04-07 13:20 | 245 | 35 | 8575 | 0.026192 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90264 - Change 11kV poles, X-arms and reconductor. Isolation Points: 11kV ABS SE3-016 & TEMP19. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 245 | 242 | 8470 | 0.025871 | 0.0001069 | 2014-04-07 | B | 0.012935 | 5.3452e-05 | 2015 | 2014-04-07 | B | 35 | 0.025871 | 0.0001069
1 | 139943 | 2014-04-07 12:58 | 2014-04-07 14:33 | 95 | 810 | 68245 | 0.20845 | 0.0024741 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird CB 8 L/O on E/F Sectionalised and found dead bird at ABS 51. Checked all OK and and relivened | F3 | KATERE 8 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 84.2531 | 81.2531 | 65815 | 0.20103 | 0.0024741 | 2014-04-07 | C | 0.20103 | 0.0024741 | 2015 | 2014-04-07 | C | 810 | 0.20103 | 0.0024741
1 | 139944 | 2014-04-03 13:00 | 2014-04-03 15:07 | 127 | 125 | 15875 | 0.048489 | 0.0003818 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CUSTOMER REQUEST | DISTRIBUTION TRANSFORMER | SIN: 14/89177 - Replace damaged 11kV TX 924 and TX 1223 canopy. Isolation points: 11kV Fuse 8332 DEFERRED FROM MARCH. | F4 | MOTUROA 4 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 127 | 124 | 15500 | 0.047344 | 0.0003818 | 2014-04-03 | B | 0.023672 | 0.0001909 | 2015 | 2014-04-03 | B | 125 | 0.047344 | 0.0003818
1 | 139945 | 2014-04-07 14:00 | 2014-04-07 15:00 | 60 | 1 | 60 | 0.00018327 | 3.0544e-06 | No Power | 6600 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Found 400v line down. Isolated transformer 3344T for safety while line pulled up Relivened once job completed | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 57 | 0.0001741 | 3.0544e-06 | 2014-04-07 | C | 0.0001741 | 3.054e-06 | 2015 | 2014-04-07 | C | 1 | 0.0001741 | 3.0544e-06
1 | 139946 | 2014-04-07 13:54 | 2014-04-07 15:03 | 69 | 862 | 59478 | 0.18167 | 0.0026329 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | CONDUCTOR | Accident - CB18 tripped O/C, L/O. Report of hiab truck clipping L/V lines ( redundant ) & flicking them up into H/V at pole 203662. Feeder patrolled for futher damage, all ok only H/V lines twisted together at pole 203662 ( untwisted live line stick ) CB | F3 | CAMBRIDGE RD TAURANGA | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 69 | 66 | 56892 | 0.17377 | 0.0026329 | 2014-04-07 | C | 0.17377 | 0.0026329 | 2015 | 2014-04-07 | C | 862 | 0.17377 | 0.0026329
1 | 139950 | 2014-04-08 00:10 | 2014-04-08 01:30 | 80 | 705 | 25226 | 0.077051 | 0.0021534 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -CB 9 A/R, L/O, O/C B and C Phase, E/F. Sectionalised and Patrolled, No fault found. Attended by Shazil Khan / Nev Morris | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 35.7816 | 32.7816 | 23111 | 0.070591 | 0.0021534 | 2014-04-08 | C | 0.070591 | 0.0021534 | 2015 | 2014-04-08 | C | 705 | 0.070591 | 0.0021534
1 | 139951 | 2014-04-08 01:54 | 2014-04-08 03:06 | 72 | 766 | 44718 | 0.13659 | 0.0023397 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees -CB U20 Trip, No flags. Faultman dispatched to sectionalise and patrol. Partial backfeed installed by opening RS 4989 and closing VS 8801. Feeder sectionalised and patrolled with tree branch found sitting on lines at Pole 739730. Branch cleared usi | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 58.3786 | 55.3786 | 42420 | 0.12957 | 0.0023397 | 2014-04-08 | C | 0.12957 | 0.0023397 | 2015 | 2014-04-08 | C | 766 | 0.12957 | 0.0023397
1 | 139952 | 2014-04-07 13:54 | 2014-04-07 15:03 | 69 | 6 | 414 | 0.0012645 | 1.8327e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - UG | SIN: 14/90969 - Maintain and replace oil after failed LTOS test at 11kV Sw/Gear SE5-211 /-215 /-217 and Fuse/Sw SE5-213 & SE5-285. Isolation points: 11kV Sw/Gear 9382/2 & 9479/4 | F3 | JELLICOE ST | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 69 | 66 | 396 | 0.0012096 | 1.8327e-05 | 2014-04-07 | B | 0.00060478 | 9.163e-06 | 2015 | 2014-04-07 | B | 6 | 0.0012096 | 1.8327e-05
1 | 139953 | 2014-04-08 01:32 | 2014-04-08 03:15 | 103 | 87 | 8961 | 0.027371 | 0.00026573 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | CONDUCTOR | No Power - Kumenga RS C630 A/R and L/O on E/F and O/C on A-B-C phase. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 103 | 100 | 8700 | 0.026573 | 0.00026573 | 2014-04-08 | C | 0.026573 | 0.00026574 | 2015 | 2014-04-08 | C | 87 | 0.026573 | 0.00026573
1 | 139954 | 2014-04-08 01:30 | 2014-04-08 05:48 | 258 | 371 | 36979 | 0.11295 | 0.0011332 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | No Power -CB 6900/6 ( CB 6 Manaia) Tripped E/F Patrolled Found Insulator at Pole 717931 Floating Isolated at ABS MA272 ABS MA208 ABS MA273 Backfeed in at ABS TA801 Put insulator back in Crossarm Nothing used Jade Williams & Kane Mackay Attended | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 99.6739 | 96.6739 | 35866 | 0.10955 | 0.0011332 | 2014-04-08 | C | 0.10955 | 0.0011332 | 2015 | 2014-04-08 | C | 371 | 0.10955 | 0.0011332
1 | 139959 | 2014-04-08 10:21 | 2014-04-08 13:00 | 159 | 232 | 23832 | 0.072793 | 0.00070863 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Wind - CB t31 L/O No Flags Sectionalised CB & found binder broken at pole 730288. Isolated between ABS 5968. ABS 5977 Back feed rest of area. Repaired binder and restored power | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 102.7241 | 99.7241 | 23136 | 0.070667 | 0.00070863 | 2014-04-08 | C | 0.070667 | 0.00070863 | 2015 | 2014-04-08 | C | 232 | 0.070667 | 0.00070863
1 | 139960 | 2014-04-08 09:33 | 2014-04-08 12:10 | 157 | 4 | 1080 | 0.0032988 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90599 - Relocate 11kV pole 854147. Isolation point: 11kV Line break at pole W1161. Refer to LLPs 14/90597 (create LLB) and 14/90598 (Close LLB). | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 270 | 267 | 1068 | 0.0032621 | 1.2218e-05 | 2014-04-08 | B | 0.0016311 | 6.109e-06 | 2015 | 2014-04-08 | B | 4 | 0.0032621 | 1.2218e-05
1 | 139961 | 2014-04-08 11:20 | 2014-04-08 11:42 | 22 | 42 | 924 | 0.0028223 | 0.00012829 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Wind - Found jumper broken at transformer 1205. Isolated at ABS 523. Repaired jumper and relivened | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 798 | 0.0024374 | 0.00012829 | 2014-04-08 | C | 0.0024374 | 0.00012829 | 2015 | 2014-04-08 | C | 42 | 0.0024374 | 0.00012829
1 | 139962 | 2014-04-08 09:30 | 2014-04-08 10:55 | 85 | 2 | 170 | 0.00051925 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | UNKNOWN | Wind - Found tree in line in Barry rd Isolated at fuses 6655 Removed tree & relivened | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 85 | 82 | 164 | 0.00050093 | 6.1088e-06 | 2014-04-08 | C | 0.00050093 | 6.109e-06 | 2015 | 2014-04-08 | C | 2 | 0.00050093 | 6.1088e-06
1 | 139963 | 2014-04-08 10:36 | 2014-04-08 12:20 | 104 | 639 | 50691 | 0.15483 | 0.0019518 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - CB 5 at Mangorea Regulator L/O. Setionalised and found Metal bracket at pole 747938 found touching line. Isolated at ABS 580 and repaired bracket. Relivened | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 79.3286 | 76.3286 | 48774 | 0.14898 | 0.0019518 | 2014-04-08 | C | 0.14898 | 0.0019518 | 2015 | 2014-04-08 | C | 639 | 0.14898 | 0.0019518
1 | 139965 | 2014-04-08 09:15 | 2014-04-08 14:38 | 323 | 35 | 12600 | 0.038486 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90265 - Change 11kV poles, X-arms and reconductor. Isolation Points: 11kV ABS SE3-016 & TEMP19. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 12495 | 0.038165 | 0.0001069 | 2014-04-08 | B | 0.019083 | 5.3452e-05 | 2015 | 2014-04-08 | B | 35 | 0.038165 | 0.0001069
1 | 139966 | 2014-04-08 09:36 | 2014-04-08 15:06 | 330 | 11 | 3630 | 0.011088 | 3.3599e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90241 - Install new poles & conductor | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 3597 | 0.010987 | 3.3599e-05 | 2014-04-08 | B | 0.0054934 | 1.6799e-05 | 2015 | 2014-04-08 | B | 11 | 0.010987 | 3.3599e-05
1 | 139967 | 2014-04-08 15:15 | 2014-04-08 15:49 | 34 | 2 | 68 | 0.0002077 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Wind - Found line down in Riffle Range Rd Isolated at Fuses WH819 repaired line & relivened | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 62 | 0.00018937 | 6.1088e-06 | 2014-04-08 | C | 0.00018937 | 6.109e-06 | 2015 | 2014-04-08 | C | 2 | 0.00018937 | 6.1088e-06
1 | 139969 | 2014-04-08 09:00 | 2014-04-08 15:37 | 397 | 104 | 41288 | 0.12611 | 0.00031766 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90446 - Replace 33kV, 11kV 400V arms between P32370 to P34052. Isolation points: 33kV: X51. Z28, 1076, 11kV: E8, E7, J96, J90, OS147 | F2 | WORKS | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 397 | 394 | 40976 | 0.12516 | 0.00031766 | 2014-04-08 | B | 0.062579 | 0.00015883 | 2015 | 2014-04-08 | B | 104 | 0.12516 | 0.00031766
1 | 139970 | 2014-04-08 15:00 | 2014-04-08 17:03 | 123 | 21 | 2583 | 0.0078896 | 6.4143e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Wind -Found 1 line down caused by tree & wind Isolated at fuses 5209. Repaired line & relivened | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 123 | 120 | 2520 | 0.0076971 | 6.4143e-05 | 2014-04-08 | C | 0.0076971 | 6.4143e-05 | 2015 | 2014-04-08 | C | 21 | 0.0076971 | 6.4143e-05
1 | 139971 | 2014-04-08 15:20 | 2014-04-08 16:10 | 50 | 59 | 2950 | 0.0090105 | 0.00018021 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | Wind - Found DDO unit floating at transformer T5235. Isolated between ABS 6388, ABS TA828 & TA824. Backfeed rest of area. Repaired DDO unit & relivened | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 2773 | 0.0084699 | 0.00018021 | 2014-04-08 | C | 0.0084699 | 0.00018021 | 2015 | 2014-04-08 | C | 59 | 0.0084699 | 0.00018021
1 | 139972 | 2014-04-08 10:58 | 2014-04-08 13:47 | 169 | 37 | 6253 | 0.019099 | 0.00011301 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | Wind - Found Fuses units at transformer T5065 & T5085 hanging off cross arm Isolated between ABS TA876, ABS TA869 & 6751. Back feed rest of area. Replaced fuse holders at both sites & relivened 6 x fuse holders | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 169 | 166 | 6142 | 0.01876 | 0.00011301 | 2014-04-08 | C | 0.01876 | 0.00011301 | 2015 | 2014-04-08 | C | 37 | 0.01876 | 0.00011301
1 | 139973 | 2014-04-08 13:00 | 2014-04-08 14:00 | 60 | 8 | 480 | 0.0014661 | 2.4435e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89408 - Install 400V fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new LV disconected to be fitted w/in the 1 hr HV shutdown. If required, an LV shutdown may be carried out after the HV is restored to complet | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 456 | 0.0013928 | 2.4435e-05 | 2014-04-08 | B | 0.00069641 | 1.2218e-05 | 2015 | 2014-04-08 | B | 8 | 0.0013928 | 2.4435e-05
1 | 139974 | 2014-04-08 11:15 | 2014-04-08 12:15 | 60 | 3 | 180 | 0.0005498 | 9.1633e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89407 - Install 400V fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new 400V disconnector to be fitted w/in the 1 hr HV shutdown. If required an 400V shutdown may be carried out after HV is restored to complet | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 171 | 0.00052231 | 9.1633e-06 | 2014-04-08 | B | 0.00026115 | 4.582e-06 | 2015 | 2014-04-08 | B | 3 | 0.00052231 | 9.1633e-06
1 | 139975 | 2014-04-08 09:00 | 2014-04-08 10:30 | 90 | 6 | 540 | 0.0016494 | 1.8327e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89406 - Install 400V fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new 400V disconnector to be fitted w/in the 1 hr HV shutdown. If required an 400V shutdown may be carried out after the HV Is restored to com | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 522 | 0.0015944 | 1.8327e-05 | 2014-04-08 | B | 0.00079721 | 9.163e-06 | 2015 | 2014-04-08 | B | 6 | 0.0015944 | 1.8327e-05
1 | 139976 | 2014-04-08 11:00 | 2014-04-08 11:50 | 50 | 7 | 350 | 0.001069 | 2.1381e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89325 - Install 400V fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new 400V disconnector to be iftted w/in the 1 hr HV shutdown. If required, an 400V shutdown may be carried out after the HV is restored to co | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 329 | 0.0010049 | 2.1381e-05 | 2014-04-08 | B | 0.00050245 | 1.069e-05 | 2015 | 2014-04-08 | B | 7 | 0.0010049 | 2.1381e-05
1 | 139977 | 2014-04-08 10:10 | 2014-04-08 11:50 | 100 | 57 | 5643 | 0.017236 | 0.0001741 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90968 - Replace 11kV leaking ground mounted TX TC3426. Isolation points: 11kV Sw/Gear 9312/2 | F3 | BALMORAL DR | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 99 | 96 | 5472 | 0.016714 | 0.0001741 | 2014-04-08 | B | 0.0083569 | 8.7051e-05 | 2015 | 2014-04-08 | B | 57 | 0.016714 | 0.0001741
1 | 139978 | 2014-04-08 19:33 | 2014-04-08 20:40 | 67 | 26 | 1742 | 0.0053208 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component -Faultman found damaged 11KV insulators on pole 772476, line was isolated at Fuses O38 to replace the 2 insulators.Karl Rodgers | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 67 | 64 | 1664 | 0.0050826 | 7.9415e-05 | 2014-04-08 | C | 0.0050826 | 7.9415e-05 | 2015 | 2014-04-08 | C | 26 | 0.0050826 | 7.9415e-05
1 | 139979 | 2014-04-08 19:31 | 2014-04-08 22:30 | 179 | 436 | 9519 | 0.029075 | 0.0013317 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Ohangai Rd Recloser 6837/2 tripped on E/F C-phase flags, faultman found a broken cross arm on pole 722437, line was isolated at ABS's CA 403 424, 421 and 463 to replace the cross arm and 3 insulators. Allan Rarere attended. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 21.8326 | 18.8326 | 8211 | 0.02508 | 0.0013317 | 2014-04-08 | C | 0.02508 | 0.0013317 | 2015 | 2014-04-08 | C | 436 | 0.02508 | 0.0013317
1 | 139980 | 2014-04-08 22:57 | 2014-04-08 23:19 | 22 | 62 | 1364 | 0.0041662 | 0.00018937 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | HT Transformer Fuse -Faultman isolated line at Fuses TA720 for safety to check fuse holder on transformer T3115 as it was to dangerous with line live in the rain and wind.Jade Williams attended. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 1178 | 0.0035981 | 0.00018937 | 2014-04-08 | C | 0.0035981 | 0.00018937 | 2015 | 2014-04-08 | C | 62 | 0.0035981 | 0.00018937
1 | 139981 | 2014-04-08 23:50 | 2014-04-09 03:03 | 193 | 4 | 772 | 0.002358 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Faultman found a broken cross arm and fuse holder at transformer L1060while attending a fault call, line was isolated at Fuses LI747 to replace the cross arm and fuse holder at transformer L1060 on pole 726782. Henry Hood attended. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 193 | 190 | 760 | 0.0023214 | 1.2218e-05 | 2014-04-08 | C | 0.0023214 | 1.2218e-05 | 2015 | 2014-04-08 | C | 4 | 0.0023214 | 1.2218e-05
1 | 139982 | 2014-04-09 00:29 | 2014-04-09 00:43 | 14 | 1088 | 15232 | 0.046525 | 0.0033232 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component -Received at call from Fire Services of a transformer on fire, faultman found transformer C1190 on fire, CB 8 was opened to off load feeder while fire services put out the fire, transformer C1190 needs to be replaced in morning by fiel | F3 | ARGYLE ST | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 11968 | 0.036555 | 0.0033232 | 2014-04-09 | C | 0.036555 | 0.0033232 | 2015 | 2014-04-09 | C | 1088 | 0.036555 | 0.0033232
1 | 139983 | 2014-04-09 05:56 | 2014-04-09 07:38 | 102 | 244 | 18434 | 0.056305 | 0.00074528 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | No Power -CB LI1 Tripped Patrolled nothing found Reliven OK Kane MacKay Attended | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 75.5492 | 72.5492 | 17702 | 0.054069 | 0.00074528 | 2014-04-09 | C | 0.054069 | 0.00074528 | 2015 | 2014-04-09 | C | 244 | 0.054069 | 0.00074528
1 | 139984 | 2014-04-09 10:38 | 2014-04-09 11:40 | 62 | 4 | 248 | 0.0007575 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90578 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Upgrade 11kV Transformer TF7-044 to 50kVA. Isolation point: 11kV transformer Fuses TF7-044. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 236 | 0.00072084 | 1.2218e-05 | 2014-04-09 | B | 0.00036042 | 6.109e-06 | 2015 | 2014-04-09 | B | 4 | 0.00072084 | 1.2218e-05
1 | 139985 | 2014-04-09 09:25 | 2014-04-09 11:49 | 144 | 14 | 2016 | 0.0061577 | 4.2762e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90384 - Replace 3 x 11kV cross arms on P17860/P17866/P17863 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 144 | 141 | 1974 | 0.0060294 | 4.2762e-05 | 2014-04-09 | B | 0.0030147 | 2.1381e-05 | 2015 | 2014-04-09 | B | 14 | 0.0060294 | 4.2762e-05
1 | 139986 | 2014-04-09 14:00 | 2014-04-09 14:18 | 18 | 62 | 1116 | 0.0034087 | 0.00018937 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | Defective Component - CB 9 A/R on E/F. Shazil Kahn patrolled line and found fault to be a cracked insulator on a jumper from the line down to Fuses D67 and was not required. Outage required between ABS D80 & ABS E8 to remove cracked insulator. Relivened O | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 18 | 15 | 930 | 0.0028406 | 0.00018937 | 2014-04-09 | C | 0.0028406 | 0.00018937 | 2015 | 2014-04-09 | C | 62 | 0.0028406 | 0.00018937
1 | 139987 | 2014-04-09 09:30 | 2014-04-09 11:04 | 94 | 239 | 8130 | 0.024832 | 0.00073001 | No Power | 11000 | Unplanned | Distribution Equip. | HUMAN ELEMENT | SWITCHING ERROR | RECLOSER | No Power -Recloser 9665/2 Tripped when we were doing SIS 14/90046 at 09:30 & as we were trying to see Why Sectionaliser 9704 Tripped 10:43 which was back feeding the area Found to be a fault in the SIS so we stopped the SIS put things Back to normal eve | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 34.0167 | 31.0167 | 7413 | 0.022642 | 0.00073001 | 2014-04-09 | C | 0.022642 | 0.00073001 | 2015 | 2014-04-09 | C | 239 | 0.022642 | 0.00073001
1 | 139988 | 2014-04-09 09:09 | 2014-04-09 15:13 | 364 | 57 | 20748 | 0.063373 | 0.0001741 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/90381 - Tree trimming and felling between pole 791171 and 791182 - Mangamahu Road - (PPPD 43782) | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 364 | 361 | 20577 | 0.062851 | 0.0001741 | 2014-04-09 | B | 0.031425 | 8.7051e-05 | 2015 | 2014-04-09 | B | 57 | 0.062851 | 0.0001741
1 | 139991 | 2014-04-09 19:13 | 2014-04-09 21:14 | 121 | 489 | 36240 | 0.11069 | 0.0014936 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | CONDUCTOR | Lightning - suspected Recloser 9275/2 tripped E/F, L/O. Feeder sectionalised with no obvious fault found ( lightning in the area ) all service restored, Steve Doran & Denis Ngatai attended. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 74.1104 | 71.1104 | 34773 | 0.10621 | 0.0014936 | 2014-04-09 | C | 0.10621 | 0.0014936 | 2015 | 2014-04-09 | C | 489 | 0.10621 | 0.0014936
1 | 139992 | 2014-04-09 20:18 | 2014-04-09 21:36 | 78 | 1337 | 60124 | 0.18364 | 0.0040838 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | CONDUCTOR | Lightning - Recloser RC25 trip flags operated E/F, O/C ( did not trip ) 11kV CB17 ( WLN ) tripped L/O with loss of Walton sub. Sub checked out ok with all feeders being restored in turn, Tama Pene attended. Several transformer H/V fuses blown beyond REC R | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 44.9693 | 41.9693 | 56113 | 0.17139 | 0.0040838 | 2014-04-09 | C | 0.17139 | 0.0040838 | 2015 | 2014-04-09 | C | 1337 | 0.17139 | 0.0040838
1 | 139993 | 2014-04-09 23:36 | 2014-04-10 01:55 | 139 | 732 | 62271 | 0.1902 | 0.0022358 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | Lightning - Tripping on CB7 on E/f. Feeder patrolled / sectionalised with Blown insulator found between ABS 37 and ABS 535. (Backfeed at Sw/Gear 264/3). Insulator replaced / relivened OK. Severe lightning storm in area. | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 85.0697 | 82.0697 | 60075 | 0.18349 | 0.0022358 | 2014-04-09 | C | 0.18349 | 0.0022358 | 2015 | 2014-04-09 | C | 732 | 0.18349 | 0.0022358
1 | 139994 | 2014-04-10 00:18 | 2014-04-10 00:53 | 35 | 417 | 14595 | 0.044579 | 0.0012737 | No Power | 33000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | CONDUCTOR | Lightning - Tripping on SFD GXP 33kV CB2742 on O/C. (Loss of Supply to Motukawa Sub). Impractical to patrol during the night with heavy fog and lightning storm. Sub backfed at MABS 253 with isolation at ABS 511 to restore the Injection plant. To be patrol | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 13344 | 0.040758 | 0.0012737 | 2014-04-10 | C | 0.040758 | 0.0012737 | 2015 | 2014-04-10 | C | 417 | 0.040758 | 0.0012737
1 | 139995 | 2014-04-10 00:34 | 2014-04-10 01:40 | 66 | 823 | 53502 | 0.16342 | 0.0025138 | No Power | 33000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | CONDUCTOR | Lightning - Tripping on SFD GXP 33kV CB 2862 on O/C causing Loss of supply to both Kaponga and cardiff Subs. This fault record refers to outage at Kaponga Sub. Impractical to patrol the line at night due to fog and lightning in area. Sub backfeed via 33kV | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 65.0085 | 62.0085 | 51033 | 0.15588 | 0.0025138 | 2014-04-10 | C | 0.15588 | 0.0025138 | 2015 | 2014-04-10 | C | 823 | 0.15588 | 0.0025138
1 | 139996 | 2014-04-10 00:34 | 2014-04-10 02:12 | 98 | 517 | 50666 | 0.15476 | 0.0015791 | No Power | 33000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | UNKNOWN | Lightning - Tripping on SFD GXP 33kV CB 2862 on O/C causing Loss of supply to both Kaponga and Cardiff Subs. This fault record refers to outage at Cardiff Sub. Impractical to patrol the line at night due to fog and lightning in area. Sub backfeed via 33 | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 98 | 95 | 49115 | 0.15002 | 0.0015791 | 2014-04-10 | C | 0.15002 | 0.0015791 | 2015 | 2014-04-10 | C | 517 | 0.15002 | 0.0015791
1 | 139997 | 2014-04-09 21:58 | 2014-04-10 04:00 | 362 | 9 | 3258 | 0.0099513 | 2.749e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - Faulty transformer TC1761 replaced due to lightning, Pete Mangin attended, all service restored. | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 362 | 359 | 3231 | 0.0098688 | 2.749e-05 | 2014-04-09 | C | 0.0098688 | 2.749e-05 | 2015 | 2014-04-09 | C | 9 | 0.0098688 | 2.749e-05
1 | 139998 | 2014-04-09 21:58 | 2014-04-10 05:55 | 477 | 5 | 2385 | 0.0072848 | 1.5272e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - faulty transformer TC2758 replaced due to lightning, all service restored, Pete Mangin attended. | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 477 | 474 | 2370 | 0.007239 | 1.5272e-05 | 2014-04-09 | C | 0.007239 | 1.5272e-05 | 2015 | 2014-04-09 | C | 5 | 0.007239 | 1.5272e-05
1 | 139999 | 2014-04-10 00:06 | 2014-04-10 08:03 | 477 | 115 | 28264 | 0.08633 | 0.00035126 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - Tripping on recloser 8763/2 on O/C2 Ph A. Feeder patrolled and sectionalise but unable to locate fault during night time. (To be patrolled during daylight hours). Fault in area between fuses 5607 and 8888 on centre Phase. (Lightning in area at | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 245.7739 | 242.7739 | 27919 | 0.085276 | 0.00035126 | 2014-04-10 | C | 0.085276 | 0.00035126 | 2015 | 2014-04-10 | C | 115 | 0.085276 | 0.00035126
1 | 140001 | 2014-04-10 01:22 | 2014-04-10 07:15 | 353 | 489 | 42505 | 0.12983 | 0.0014936 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | Defective Component - Recloser 9275 Tripped, E/F. Line patrols & sectionalising located faulty insulator at pole 217685. Isolated past ABS SE3-002, insulator replaced, supply restored. Note: Intermittant fault proved difficult to locate. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 86.9223 | 83.9223 | 41038 | 0.12535 | 0.0014936 | 2014-04-10 | C | 0.12535 | 0.0014936 | 2015 | 2014-04-10 | C | 489 | 0.12535 | 0.0014936
1 | 140003 | 2014-04-10 08:45 | 2014-04-10 11:25 | 160 | 21 | 3360 | 0.010263 | 6.4143e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | Wind - Found line down at transformer TG7-005. Isolated at fuses SG7-001. Repaired line & relivened | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 3297 | 0.01007 | 6.4143e-05 | 2014-04-10 | C | 0.01007 | 6.4143e-05 | 2015 | 2014-04-10 | C | 21 | 0.01007 | 6.4143e-05
1 | 140004 | 2014-04-10 09:18 | 2014-04-10 11:54 | 156 | 17 | 2652 | 0.0081003 | 5.1925e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | No Power -Fuse Switch 5010/2 Tripped 0918 Blair Gregg Checked out Transformer 3101T found to be OK For Safety As Transformer & Switchgear in Same Room we openned ABS 5109 Closed Fuse switch 5010/2 Then Closed ABS 5109 Power Off For 1 Minute in Total | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 156 | 153 | 2601 | 0.0079446 | 5.1925e-05 | 2014-04-10 | C | 0.0079446 | 5.1925e-05 | 2015 | 2014-04-10 | C | 17 | 0.0079446 | 5.1925e-05
1 | 140006 | 2014-04-10 09:45 | 2014-04-10 11:07 | 82 | 4 | 328 | 0.0010019 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | No Power -Transformer 988 Found Blown up Replaced by Germanine Anaha Off at 0945 On at 1107 | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 82 | 79 | 316 | 0.0009652 | 1.2218e-05 | 2014-04-10 | C | 0.0009652 | 1.2218e-05 | 2015 | 2014-04-10 | C | 4 | 0.0009652 | 1.2218e-05
1 | 140007 | 2014-04-10 09:30 | 2014-04-10 11:15 | 105 | 2 | 210 | 0.00064143 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90706 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP.Install 400V fuses on existing pole mounted TX. TXs to be isolated via transformer fuses and new 400V disconnector to be fitted w/in the 1 hr HV | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 204 | 0.0006231 | 6.1088e-06 | 2014-04-10 | B | 0.00031155 | 3.054e-06 | 2015 | 2014-04-10 | B | 2 | 0.0006231 | 6.1088e-06
1 | 140008 | 2014-04-10 09:15 | 2014-04-10 13:55 | 280 | 27 | 7560 | 0.023091 | 8.2469e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90949 - Replace burnt of 11kV pole P46575. Isolation points: Fuses T32 | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 280 | 277 | 7479 | 0.022844 | 8.2469e-05 | 2014-04-10 | B | 0.011422 | 4.1235e-05 | 2015 | 2014-04-10 | B | 27 | 0.022844 | 8.2469e-05
1 | 140012 | 2014-04-10 14:10 | 2014-04-10 15:59 | 109 | 239 | 7072 | 0.021601 | 0.00073001 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | Defective Component - CB 10 Tripped L/O Broken Insulator found during sectionlising on Pole 790731 - Isolated at ABS's 299, 177 &, 039 with a backfeed install via MABS 1487 - Cross arm and all hardware replaced due to the end of the crossarm being burnt - | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 29.59 | 26.59 | 6355 | 0.019411 | 0.00073001 | 2014-04-10 | C | 0.019411 | 0.00073001 | 2015 | 2014-04-10 | C | 239 | 0.019411 | 0.00073001
1 | 140013 | 2014-04-10 16:45 | 2014-04-10 16:54 | 9 | 575 | 5175 | 0.015807 | 0.0017563 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - 1 Jumper between DDO's and Transformer X2966, found as part of Dispatch job - isolated at transformer DDO's - Jumper reconnected - Attended by Garry Fisher - no equipment used | F3 | DURIE HILL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 3450 | 0.010538 | 0.0017563 | 2014-04-10 | C | 0.010538 | 0.0017563 | 2015 | 2014-04-10 | C | 575 | 0.010538 | 0.0017563
1 | 140016 | 2014-04-10 17:09 | 2014-04-10 17:30 | 21 | 66 | 1386 | 0.0042334 | 0.00020159 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Floating Jumper at Fuses 7218 found as part of dispatch job - Isolated at ABS's S570 & S549 - Jumper reconnected to Fuse base - Feeder returned to service - attended by Adam Whale - No Equipment used | F3/F4 | WAITE ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 21 | 18 | 1188 | 0.0036287 | 0.00020159 | 2014-04-10 | C | 0.0036287 | 0.00020159 | 2015 | 2014-04-10 | C | 66 | 0.0036287 | 0.00020159
1 | 140017 | 2014-04-10 17:11 | 2014-04-10 18:03 | 52 | 240 | 12480 | 0.038119 | 0.00073306 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | FUSE HOLDER | Defective Component - Floating jumper found on feed side of fuses for transformer X1975 - Isolated at ABS 4232/1 & Links 4232/6 - Replaced blown fuse carrier and base - Attended by Te Maire Hawira - Used 1 X Fuse Base & Carrier | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 11760 | 0.03592 | 0.00073306 | 2014-04-10 | C | 0.03592 | 0.00073306 | 2015 | 2014-04-10 | C | 240 | 0.03592 | 0.00073306
1 | 140018 | 2014-04-10 19:15 | 2014-04-10 22:29 | 194 | 41 | 7954 | 0.024295 | 0.00012523 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | CROSSARM | Lightning - Emergency switching to replace cross arm & fuse holders damaged by lightning at pole M13446. Isolation at ABS 952 ( no back feeds ) repairs completed, all service restored, Glen Whyte attended. Materials 1 x double arm, 3 x fuse holders 6 x i | F4 | TAUMANGI RD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 194 | 191 | 7831 | 0.023919 | 0.00012523 | 2014-04-10 | C | 0.023919 | 0.00012523 | 2015 | 2014-04-10 | C | 41 | 0.023919 | 0.00012523
1 | 140019 | 2014-04-10 18:26 | 2014-04-10 21:49 | 203 | 244 | 34002 | 0.10386 | 0.00074528 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | No Power -11kV CB LI1 ARC & Trip during sectionalising found 2 insulators blown on pole 727752 section of line between ABS LI 179 & ABDS LI 106 isolated for repairs balance of line backfed for duration of repairs (attended by Allan Rarere & Henry Hood) | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 139.3525 | 136.3525 | 33270 | 0.10162 | 0.00074528 | 2014-04-10 | C | 0.10162 | 0.00074528 | 2015 | 2014-04-10 | C | 244 | 0.10162 | 0.00074528
1 | 140020 | 2014-04-10 17:55 | 2014-04-10 20:25 | 150 | 124 | 9694 | 0.02961 | 0.00037875 | No Power | 6600 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | No Power -Section of line from Fuses 5525 Isolated to repair insulators on pole 761302 (redrilled crossarm) (Attended by Jade Williams) | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 78.1774 | 75.1774 | 9322 | 0.028473 | 0.00037875 | 2014-04-10 | C | 0.028473 | 0.00037875 | 2015 | 2014-04-10 | C | 124 | 0.028473 | 0.00037875
1 | 140022 | 2014-04-10 19:16 | 2014-04-11 01:41 | 385 | 280 | 48138 | 0.14703 | 0.00085524 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | No Power -11kV CB TA9 ARC & Tripped Def Time E/F . Report received of pole top on fire on Waitino road Section of line between ABS TA914 , ABS TA 916 and ABS TA 876 Isolated to effect repairs. On investigation found fuse holders on pole 715994 damaged and | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 171.9214 | 168.9214 | 47298 | 0.14447 | 0.00085524 | 2014-04-10 | C | 0.14447 | 0.00085524 | 2015 | 2014-04-10 | C | 280 | 0.14447 | 0.00085524
1 | 140024 | 2014-04-10 20:01 | 2014-04-11 01:05 | 304 | 149 | 19700 | 0.060172 | 0.00045511 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power -11kV CB 284 ARC & Tripped C phase SEF line sectionalised and patrolled between ABS 014 and ABS 965 .Section to ABS 965 backfed via VS 4621 (Attended By TeMaire Hawira)Section between CB 284 and ABS 965 to be patroled in daylight | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 132.2148 | 129.2148 | 19253 | 0.058807 | 0.00045511 | 2014-04-10 | C | 0.058807 | 0.00045511 | 2015 | 2014-04-10 | C | 149 | 0.058807 | 0.00045511
1 | 140026 | 2014-04-10 07:09 | 2014-04-10 17:16 | 607 | 405 | 140390 | 0.42881 | 0.001237 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | RECLOSER | No Power -Recloser 9665/2 tripped 3 Times over the day patrolled Found Nothing each time .Then found that the Recloser Closed by it Self .Think may Be faulty Recloser Safety manger 356948 & Red pin Done . Back feed part of Area at Sectionaler 9704 for a w | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 346.642 | 343.642 | 139175 | 0.4251 | 0.001237 | 2014-04-10 | C | 0.4251 | 0.001237 | 2015 | 2014-04-10 | C | 405 | 0.4251 | 0.001237
1 | 140027 | 2014-04-11 08:08 | 2014-04-11 08:38 | 30 | 3 | 90 | 0.0002749 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | HT Line - at 08:08 Whitianga Sub, CB 1 Owera Rd Feeder. Found a blown jumper at Pole W0766. Offloaded Transformers by Opening Fuses FC1065 & FC4250. Live Line Permit Issued & Repairs Carried out using Live Line Techniques. All Power Restored on Completion | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 81 | 0.00024741 | 9.1633e-06 | 2014-04-11 | C | 0.00024741 | 9.163e-06 | 2015 | 2014-04-11 | C | 3 | 0.00024741 | 9.1633e-06
1 | 140028 | 2014-04-11 09:15 | 2014-04-11 10:26 | 71 | 8 | 568 | 0.0017349 | 2.4435e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90450 - Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP.Install 400V fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new LV disconnector to be fitted. This is to be foll | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 544 | 0.0016616 | 2.4435e-05 | 2014-04-11 | B | 0.0008308 | 1.2218e-05 | 2015 | 2014-04-11 | B | 8 | 0.0016616 | 2.4435e-05
1 | 140029 | 2014-04-10 08:28 | 2014-04-10 11:54 | 206 | 405 | 40156 | 0.12265 | 0.001237 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | No Power -CB 4 tripped, O/C. Investigations locate faulty insulater at Pole M1200, cracked. Isolation Points ABS 9665/1 Links 9665/4 & ABS 1118 Back Feed in at Sectionliser 9704. Replaced Insulater, Reliven OK. Used 1x H/T Insutaor. Don Masters & Greg W | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 99.1506 | 96.1506 | 38941 | 0.11894 | 0.001237 | 2014-04-10 | C | 0.11894 | 0.001237 | 2015 | 2014-04-10 | C | 405 | 0.11894 | 0.001237
1 | 140030 | 2014-04-11 11:00 | 2014-04-11 12:10 | 70 | 4 | 280 | 0.00085524 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90451 - Install LV fuses on existing pole mounted TX. TXs to be isolated via drop-out fuses and new LV disconnector to be fitted. This is to be followed w/ an LV shutdown to replace 400V arms. Isolation points: 11kV Transformer fuse.TC976 NOTE: Co | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 268 | 0.00081859 | 1.2218e-05 | 2014-04-11 | B | 0.00040929 | 6.109e-06 | 2015 | 2014-04-11 | B | 4 | 0.00081859 | 1.2218e-05
1 | 140031 | 2014-04-08 10:12 | 2014-04-08 12:03 | 111 | 13 | 1443 | 0.0044075 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/90607 - Repair sleeves in 11kV line. Isolation point: 11kV ABS IC396. | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 111 | 108 | 1404 | 0.0042884 | 3.9708e-05 | 2014-04-08 | B | 0.0021442 | 1.9854e-05 | 2015 | 2014-04-08 | B | 13 | 0.0042884 | 3.9708e-05
1 | 140032 | 2014-04-11 10:00 | 2014-04-11 10:05 | 5 | 58 | 290 | 0.00088578 | 0.00017716 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | WA: 14/90684 - Change Tap Change setting on 11kV G/M Transformer TC3333. Isolation point: 11kV Fuses FC2441. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 5 | 2 | 116 | 0.00035431 | 0.00017716 | 2014-04-11 | B | 0.00017716 | 8.8578e-05 | 2015 | 2014-04-11 | B | 58 | 0.00035431 | 0.00017716
1 | 140033 | 2014-04-10 23:35 | 2014-04-11 12:55 | 800 | 76 | 14880 | 0.04545 | 0.00023214 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - RS 7417 Tripped B/Ph O/C E/F - Fault found to be past Fuses 7904 during sectionlising - Faultman could not locate cause of fault on cross country in the dark - spur line left Isolated over night - in the morning a tree was found cross the lines at | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 195.7895 | 192.7895 | 14652 | 0.044753 | 0.00023214 | 2014-04-10 | C | 0.044753 | 0.00023214 | 2015 | 2014-04-10 | C | 76 | 0.044753 | 0.00023214
1 | 140034 | 2014-04-11 11:30 | 2014-04-11 12:12 | 42 | 661 | 27762 | 0.084797 | 0.002019 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - at 10:23 Tauranga GXP, CB 14 Gate Pa Feeder. Faultman Advised of a Car Vs Pole at Pole 203394 11kV Lines needed Isolating. Backfeeds put in and then Lines Isolated. Isolated 11kV at Sw/gear 9753/3, ABS SD4-582, SD4-034 & SD4-033 - Power Off at | F3 | GATE PA | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 25779 | 0.07874 | 0.002019 | 2014-04-11 | C | 0.07874 | 0.002019 | 2015 | 2014-04-11 | C | 661 | 0.07874 | 0.002019
1 | 140035 | 2014-04-11 09:15 | 2014-04-11 13:20 | 245 | 65 | 15925 | 0.048642 | 0.00019854 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/90856 - Install new 11kV termination arms on pole 823042 and terminate 11kV | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 245 | 242 | 15730 | 0.048046 | 0.00019854 | 2014-04-11 | B | 0.024023 | 9.9269e-05 | 2015 | 2014-04-11 | B | 65 | 0.048046 | 0.00019854
1 | 140036 | 2014-04-11 08:51 | 2014-04-11 13:37 | 286 | 1 | 286 | 0.00087357 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Arcing Transformer reported by public to dispatch - Fused ABS 2871 Opened - Transformer checked and Damaged insolating bush found - Bush replaced and transformer returned to service - Attended by Karl Rodgers - used 1x bush | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 286 | 283 | 283 | 0.0008644 | 3.0544e-06 | 2014-04-11 | C | 0.0008644 | 3.054e-06 | 2015 | 2014-04-11 | C | 1 | 0.0008644 | 3.0544e-06
1 | 140038 | 2014-04-10 10:07 | 2014-04-10 14:02 | 235 | 1 | 235 | 0.00071779 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/90801 - Shutdown X2476 Bridge St Bulls to repair oil leak. Isolation points: FABS 1419. Change to alt date due to other works being shifted due to weather. MR 10/04/2014 | F4 | RACECOURSE | BULLS SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 235 | 232 | 232 | 0.00070863 | 3.0544e-06 | 2014-04-10 | B | 0.00035431 | 1.527e-06 | 2015 | 2014-04-10 | B | 1 | 0.00070863 | 3.0544e-06
1 | 140039 | 2014-04-10 10:20 | 2014-04-10 12:34 | 134 | 1 | 134 | 0.00040929 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90885 - Fit new LV panel to TX T3/575 to allow for second connection. Isolation points: FS 193. Moved to alt date. | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 134 | 131 | 131 | 0.00040013 | 3.0544e-06 | 2014-04-10 | B | 0.00020007 | 1.527e-06 | 2015 | 2014-04-10 | B | 1 | 0.00040013 | 3.0544e-06
1 | 140043 | 2014-04-11 21:36 | 2014-04-11 23:47 | 131 | 96 | 6031 | 0.018421 | 0.00029322 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | No Power -11kV CB 3 tripped during sectionalising and backfeeding report received of a transformer that had an 'explosion' on investigation found an insulator had been damaged by lightning on pole 743527 (Attended by Chris Vivier & Craig Wellington) | F1 | BELL BLOCK 3 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 62.8229 | 59.8229 | 5743 | 0.017542 | 0.00029322 | 2014-04-11 | C | 0.017542 | 0.00029322 | 2015 | 2014-04-11 | C | 96 | 0.017542 | 0.00029322
1 | 140048 | 2014-04-12 09:30 | 2014-04-12 11:00 | 90 | 40 | 3600 | 0.010996 | 0.00012218 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/90855 - Close line breaks at poles P15275 and P15828 on the Mauriceville feeder to put Mauriceville and Ihuraua feeders back to normal. Isolation points: U39, U42, U41, ABS 10169 | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 3480 | 0.010629 | 0.00012218 | 2014-04-12 | B | 0.0053147 | 6.1088e-05 | 2015 | 2014-04-12 | B | 40 | 0.010629 | 0.00012218
1 | 140051 | 2014-04-11 14:57 | 2014-04-11 17:58 | 181 | 20 | 3620 | 0.011057 | 6.1088e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 14:57, Pongakawa Sub, CB 4 Old Coach Rd Feeder. Found Lines down at Pole 231056. Lines Isolated at Fuses SG7-001. Permit Issued & Repairs Carried out. All Power Restored on Completion. Dave Ngatai Attended. Still Need to Enquire about Materia | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 181 | 178 | 3560 | 0.010874 | 6.1088e-05 | 2014-04-11 | C | 0.010874 | 6.1088e-05 | 2015 | 2014-04-11 | C | 20 | 0.010874 | 6.1088e-05
1 | 140052 | 2014-04-12 01:50 | 2014-04-12 06:00 | 250 | 6 | 1500 | 0.0045816 | 1.8327e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | No Power - Omokoroa CB 2 No Trip. Transformer TD2-040 Blown due to Lightning. Isolation at Transformer Fuses TD2-040. No Back feeds available. All works complete. 3ph 50kVA Transformer. Faultman Steve Doran | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 1482 | 0.0045267 | 1.8327e-05 | 2014-04-12 | C | 0.0045267 | 1.8327e-05 | 2015 | 2014-04-12 | C | 6 | 0.0045267 | 1.8327e-05
1 | 140053 | 2014-04-12 01:28 | 2014-04-12 05:33 | 245 | 34 | 5169 | 0.015788 | 0.00010385 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | No Power - Triton CB5 Trip No Flags. Port of Tauranga Forklift driven through O/Head Lines on corner of Tataroa St/Hull Rd.CB 7 Tripped also, double circuit. Lines down. Faultman Dennis Ngtai. Isolation Points CB 5, ABS SC4-275 Sw/Gear S4600. back feed v | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 152.0294 | 149.0294 | 5067 | 0.015477 | 0.00010385 | 2014-04-12 | C | 0.015477 | 0.00010385 | 2015 | 2014-04-12 | C | 34 | 0.015477 | 0.00010385
1 | 140054 | 2014-04-12 01:28 | 2014-04-12 04:19 | 171 | 1118 | 93172 | 0.28459 | 0.0034148 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | No Power - Triton CB7 Trip No Flags. Port of Tauranga Forklift driven through O/Head Lines on corner of Tataroa St/Hull Rd.CB 5 Tripped also, double circuit. Lines down. Faultman Dennis Ngtai. Isolation Points CB 7, ABS SC4-293 SC4-066. back feed via ABS | F3 | TOTARA ST NORTH | TRITON SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 83.3381 | 80.3381 | 89818 | 0.27434 | 0.0034148 | 2014-04-12 | C | 0.27434 | 0.0034148 | 2015 | 2014-04-12 | C | 1118 | 0.27434 | 0.0034148
1 | 140058 | 2014-04-13 09:00 | 2014-04-13 15:25 | 385 | 10 | 3850 | 0.01176 | 3.0544e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/89670 - Replace 11kV G/M Transformer TC4-394 (leaking oil). Isolation point: 11kV fused ABS SC4-829 | F2 | HULL RD | TRITON SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 385 | 382 | 3820 | 0.011668 | 3.0544e-05 | 2014-04-13 | B | 0.0058339 | 1.5272e-05 | 2015 | 2014-04-13 | B | 10 | 0.011668 | 3.0544e-05
1 | 140060 | 2014-04-13 16:46 | 2014-04-13 16:58 | 12 | 1 | 12 | 3.6653e-05 | 3.0544e-06 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT BIRD | UNKNOWN | Unknown Cause -CB 2782 Trip, O/C Neutral Time. Not patrolled. No fault found. Line was still alive due to being part of ring, so RCC instructed to close CB. Suspect bird strike. | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 12 | 9 | 9 | 2.749e-05 | 3.0544e-06 | 2014-04-13 | C | 2.749e-05 | 3.054e-06 | 2015 | 2014-04-13 | C | 1 | 2.749e-05 | 3.0544e-06
1 | 140061 | 2014-04-12 17:43 | 2014-04-12 18:34 | 51 | 134 | 5160 | 0.015761 | 0.00040929 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | LV FAULT - OTHER | LT Transformer Fuse - at 17:43 Tairua Sub, CB 4 Pauanui Feeder. Faultman called to part power calls. Found burnt out LV fuse holder at Transformer TC3745. Needed to Isolate Transformer to carry out repairs to LV fuse holder. Isolated at Transformer T Blad | F3 | PAUANUI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 38.5075 | 35.5075 | 4758 | 0.014533 | 0.00040929 | 2014-04-12 | C | 0.014533 | 0.00040929 | 2015 | 2014-04-12 | C | 134 | 0.014533 | 0.00040929
1 | 140062 | 2014-04-12 11:09 | 2014-04-12 18:30 | 441 | 6 | 2646 | 0.008082 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - at 11:09 Pongakawa Sub, CB 3 Rotoehu Feeder. Faultman Dispatched to No Power Calls. Found 11kV Lines Down at Pole 229155. Isolated Lines at Fuses SF7-025. Repairs Carried Out. All Power Restored on Completion. Robin McClean Attended. 6x Links repl | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 441 | 438 | 2628 | 0.008027 | 1.8327e-05 | 2014-04-12 | C | 0.008027 | 1.8327e-05 | 2015 | 2014-04-12 | C | 6 | 0.008027 | 1.8327e-05
1 | 140063 | 2014-04-12 15:08 | 2014-04-12 17:49 | 161 | 378 | 24570 | 0.075047 | 0.0011546 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | HT Line - at 15:08 Omokoroa Sub, CB 1 Te Puna Feeder, Recloser 9804 Tripped, Ph A,B,C O/C, L/O. CB 1 Tripped, Ph A,B,C O/C, Auto Reclosed. CB 36 Tripped, No Flags, L/O, CB 62 Tripped, Ph B & C O/C, REV O/C, L/O. Aongatete Sub CB 82 Tripped, No Flags, L/O. | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 23436 | 0.071583 | 0.0011546 | 2014-04-12 | C | 0.071583 | 0.0011546 | 2015 | 2014-04-12 | C | 378 | 0.071583 | 0.0011546
1 | 140066 | 2014-04-14 05:43 | 2014-04-14 05:59 | 16 | 237 | 3792 | 0.011582 | 0.0007239 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | Unknown Cause - Cb 3 Tripped no Flags - Held in on reclose - Not Patrolled - Trevor Pocock called out then stood down | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 16 | 13 | 3081 | 0.0094107 | 0.0007239 | 2014-04-14 | C | 0.0094107 | 0.0007239 | 2015 | 2014-04-14 | C | 237 | 0.0094107 | 0.0007239
1 | 140068 | 2014-04-09 00:29 | 2014-04-13 17:17 | 6768 | 72 | 20376 | 0.062237 | 0.00021992 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Replace transformer C1190. LV supplied from generator. Materials 3ph 300kVA transformer, 25m of 35mm XLPE 3ph cable (dogbone). | F3 | ARGYLE ST | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 283 | 280 | 20160 | 0.061577 | 0.00021992 | 2014-04-09 | C | 0.061577 | 0.00021992 | 2015 | 2014-04-09 | C | 72 | 0.061577 | 0.00021992
1 | 140069 | 2014-04-12 16:34 | 2014-04-12 21:29 | 295 | 45 | 6997 | 0.021372 | 0.00013745 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - Recloser284 L/O Reclosed after 15 minutes. This happened 6 times. Recloser L/O again. Sectionalised and left isolated transformer X1927. Left off suspected faulty. Relivened next day when found protection fault on recloser 248 | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 155.4889 | 152.4889 | 6862 | 0.020959 | 0.00013745 | 2014-04-12 | C | 0.020959 | 0.00013745 | 2015 | 2014-04-12 | C | 45 | 0.020959 | 0.00013745
1 | 140070 | 2014-04-13 18:11 | 2014-04-13 21:22 | 191 | 35 | 5922 | 0.018088 | 0.0001069 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | RECLOSER | Defective Component - Recloser 284 L/O. Sectionalised and found no fault. Found sensitive E/F protection enabled on recloser. Could not disable so closed by pass ABS 259. Reinstated isolated transformers. Area already backfeed to ABS 965. NOC investigatin | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 169.2 | 166.2 | 5817 | 0.017768 | 0.0001069 | 2014-04-13 | C | 0.017768 | 0.0001069 | 2015 | 2014-04-13 | C | 35 | 0.017768 | 0.0001069
1 | 140072 | 2014-04-14 09:45 | 2014-04-14 11:50 | 125 | 2 | 250 | 0.00076361 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component -Faultman found a faulty transformer X4026 while attending a fault call, transformer was isolated at it's 11KV Fuses and transformer was changed.Garry Fischer attended | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 125 | 122 | 244 | 0.00074528 | 6.1088e-06 | 2014-04-14 | C | 0.00074528 | 6.109e-06 | 2015 | 2014-04-14 | C | 2 | 0.00074528 | 6.1088e-06
1 | 140073 | 2014-04-14 11:46 | 2014-04-14 13:16 | 90 | 221 | 15766 | 0.048156 | 0.00067503 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause -CB 3 tripped on flags, line was sectionalised and patrolled and no fault was found.Trevor Pocock attended | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.3394 | 68.3394 | 15103 | 0.046131 | 0.00067503 | 2014-04-14 | C | 0.046131 | 0.00067503 | 2015 | 2014-04-14 | C | 221 | 0.046131 | 0.00067503
1 | 140074 | 2014-04-14 09:37 | 2014-04-14 15:45 | 368 | 28 | 10304 | 0.031473 | 8.5524e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90874 - Change 11kV poles, install temp ABS 58 at pole P00701 and to install temp fuse links 69 at pole P04144. Isolation points: ABS V76, ABS V73 | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 368 | 365 | 10220 | 0.031216 | 8.5524e-05 | 2014-04-14 | B | 0.015608 | 4.2762e-05 | 2015 | 2014-04-14 | B | 28 | 0.031216 | 8.5524e-05
1 | 140075 | 2014-04-14 10:27 | 2014-04-14 15:00 | 273 | 4 | 1092 | 0.0033354 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/90707 - To complete 11kV line maintenance from FP6914 to end of spur line. Isolation points: 11kV Fuse FP691 | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 273 | 270 | 1080 | 0.0032988 | 1.2218e-05 | 2014-04-14 | B | 0.0016494 | 6.109e-06 | 2015 | 2014-04-14 | B | 4 | 0.0032988 | 1.2218e-05
1 | 140076 | 2014-04-14 13:20 | 2014-04-14 18:12 | 292 | 113 | 15828 | 0.048345 | 0.00034515 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -Recloser C224 tripped on O/C Cphase and E/F flags, line was sectionalised and patrolled and a pine tree was found that had gone through the line at pole 845448. Jason Hall attended.Materials used: 1x sleeve for No.8 wire conductor. NDR 37951 | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 140.0708 | 137.0708 | 15489 | 0.04731 | 0.00034515 | 2014-04-14 | C | 0.04731 | 0.00034515 | 2015 | 2014-04-14 | C | 113 | 0.04731 | 0.00034515
1 | 140078 | 2014-04-14 13:12 | 2014-04-14 16:22 | 190 | 33 | 6270 | 0.019151 | 0.0001008 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90824 - Remove 11kV cables from Fuses SC3-019 suppling Transformer TC3-161 and re terminate into Fuse/Sw 9801/2. Isolation Points: 11kV Cable removed from Fuses SC3-019 & Fuse/Sw 9801/2. | F3 | MATUA POINT | MATUA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 190 | 187 | 6171 | 0.018849 | 0.0001008 | 2014-04-14 | B | 0.0094244 | 5.0398e-05 | 2015 | 2014-04-14 | B | 33 | 0.018849 | 0.0001008
1 | 140079 | 2014-04-14 12:52 | 2014-04-14 15:43 | 171 | 60 | 10260 | 0.031338 | 0.00018327 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90825 - Remove 11kV cables from Fuses SC3-072 suppling Transformers TC3-067 & TC3-062 and re terminate Transformer TC3-067 into Fuse/Sw 9802/2. Isolation Points: 11kV Cable removed from Fuses SC3-072 & Fuse/Sw 9802/2. | F3 | MATUA POINT | MATUA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 171 | 168 | 10080 | 0.030789 | 0.00018327 | 2014-04-14 | B | 0.015394 | 9.1633e-05 | 2015 | 2014-04-14 | B | 60 | 0.030789 | 0.00018327
1 | 140080 | 2014-04-15 01:57 | 2014-04-15 04:12 | 135 | 241 | 26296 | 0.080319 | 0.00073612 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum RS 4141 A/R, L/O, E/F. Faultman dispatched to sectionalise and patrol found an Opossum on lines at Pole 808594. Opossum removed with Hot stick and feeder restored to normal. Attended by Kevin Anderson. Nil materials used.Note: Pole had o | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 109.112 | 106.112 | 25573 | 0.078111 | 0.00073612 | 2014-04-15 | C | 0.078111 | 0.00073612 | 2015 | 2014-04-15 | C | 241 | 0.078111 | 0.00073612
1 | 140083 | 2014-04-15 10:35 | 2014-04-15 10:57 | 22 | 34 | 748 | 0.0022847 | 0.00010385 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Faultman found a loose cross arm at pole 817083, line was isolated at Fuses 7383 to re-fasten the cross arm. Lee Wilton attended. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 646 | 0.0019732 | 0.00010385 | 2014-04-15 | C | 0.0019732 | 0.00010385 | 2015 | 2014-04-15 | C | 34 | 0.0019732 | 0.00010385
1 | 140084 | 2014-04-15 09:30 | 2014-04-15 13:30 | 240 | 1 | 300 | 0.00091633 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90987 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Upgrade 11kV TransformerTC5351. Isolation point: 11kV transformer fuses TC5351 | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 300 | 297 | 297 | 0.00090716 | 3.0544e-06 | 2014-04-15 | B | 0.00045358 | 1.527e-06 | 2015 | 2014-04-15 | B | 1 | 0.00090716 | 3.0544e-06
1 | 140085 | 2014-04-15 09:19 | 2014-04-15 14:15 | 296 | 37 | 13320 | 0.040685 | 0.00011301 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90047 - Replace X-arms within the isolated area. Isolation point: 11kV Fuses FP878 | F3 | ROLLESTON ST | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 13209 | 0.040346 | 0.00011301 | 2014-04-15 | B | 0.020173 | 5.6507e-05 | 2015 | 2014-04-15 | B | 37 | 0.040346 | 0.00011301
1 | 140086 | 2014-04-15 09:00 | 2014-04-15 15:00 | 360 | 18 | 6480 | 0.019793 | 5.498e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/90681 - Remove trees grown up through 11kV lines between poles 777081-777084. Isolation points: Links 562 | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 6426 | 0.019628 | 5.498e-05 | 2014-04-15 | B | 0.0098139 | 2.749e-05 | 2015 | 2014-04-15 | B | 18 | 0.019628 | 5.498e-05
1 | 140087 | 2014-04-15 08:35 | 2014-04-15 15:18 | 403 | 25 | 10075 | 0.030773 | 7.6361e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89343 - AP to erect poles from 785333 through to 785239, change X arms. Isolation points: ABS 4620 Oneils Rd, 4621/2 Links, 4621/4, Links, 4621/1 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 403 | 400 | 10000 | 0.030544 | 7.6361e-05 | 2014-04-15 | B | 0.015272 | 3.818e-05 | 2015 | 2014-04-15 | B | 25 | 0.030544 | 7.6361e-05
1 | 140088 | 2014-04-15 10:00 | 2014-04-15 14:00 | 240 | 32 | 7680 | 0.023458 | 9.7742e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/88739 - Replacing a number of 11kV crossarms and change pole. .Between 11kV Pole l13274 & l13297. (Between 11kV Transformer TC5965 and 11kV Fuse FC2242). Isolation points: 11kV ABS 600. | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 7584 | 0.023165 | 9.7742e-05 | 2014-04-15 | B | 0.011582 | 4.8871e-05 | 2015 | 2014-04-15 | B | 32 | 0.023165 | 9.7742e-05
1 | 140089 | 2014-04-15 08:50 | 2014-04-15 14:20 | 330 | 4 | 1320 | 0.0040318 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/88635 - Create 11kV Live Line break at pole WHUPKO079 To disconnect 11kV fuses FC2222 LL, replace 11kV cross arms beyond pole WHUPKO079 to C1703. Including 11kV arm and fuses at FC2222. Isolation points: 11kV break at pole WHUPKO079. REF LLP 14/90 | F4 | TOWNSHIP & LS | FARMER ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 1308 | 0.0039952 | 1.2218e-05 | 2014-04-15 | B | 0.0019976 | 6.109e-06 | 2015 | 2014-04-15 | B | 4 | 0.0039952 | 1.2218e-05
1 | 140090 | 2014-04-15 16:21 | 2014-04-15 17:13 | 52 | 239 | 9790 | 0.029903 | 0.00073001 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT BIRD | CONDUCTOR | Animals - bird CB 10 tripped on B and C phase O/C flags line was patrolled and sectionalised and no fault was found suspect cause of fault was ducks as a lot of duck are flying around over the lines.Ben Englebretsen and Paul Webster attended. | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 40.9623 | 37.9623 | 9073 | 0.027713 | 0.00073001 | 2014-04-15 | C | 0.027713 | 0.00073001 | 2015 | 2014-04-15 | C | 239 | 0.027713 | 0.00073001
1 | 140091 | 2014-04-15 08:30 | 2014-04-15 13:30 | 300 | 21 | 6300 | 0.019243 | 6.4143e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91323 - 11kV safety disconnection for tree removal, possibility need to unbind conductor for clearance to drop trees from . Isolation points: 11kV Links 5209 | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 300 | 297 | 6237 | 0.01905 | 6.4143e-05 | 2014-04-15 | B | 0.0095252 | 3.2071e-05 | 2015 | 2014-04-15 | B | 21 | 0.01905 | 6.4143e-05
1 | 140092 | 2014-04-15 08:45 | 2014-04-15 17:04 | 499 | 194 | 82473 | 0.25191 | 0.00059256 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90700 - STAGED RESTORATION: Replace 11kV pole (ABS SC2-021). Replace X-arms on poles 209097, 209096, 209091, 2090852, 209010, 2090695, 209055, 2099054. Replace transformer pole 209067. Isolation points: 11kV: IP566, Line Break at pole TC2-055, I | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 425.1186 | 422.1186 | 81891 | 0.25013 | 0.00059256 | 2014-04-15 | B | 0.12506 | 0.00029628 | 2015 | 2014-04-15 | B | 194 | 0.25013 | 0.00059256
1 | 140093 | 2014-04-15 17:08 | 2014-04-15 18:10 | 62 | 1078 | 46402 | 0.14173 | 0.0032927 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB 22 tripped on A phase O/C and E/F flags, line was patrolled and sectionalised and no fault was found. Shazil Khan and Dave Whale attended. | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 43.0445 | 40.0445 | 43168 | 0.13185 | 0.0032927 | 2014-04-15 | C | 0.13185 | 0.0032927 | 2015 | 2014-04-15 | C | 1078 | 0.13185 | 0.0032927
1 | 140094 | 2014-04-15 08:57 | 2014-04-15 18:36 | 579 | 3 | 1737 | 0.0053055 | 9.1633e-06 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | MAINTENANCE | CABLE | SIN: 14/91132 - Lower existing 11kV U/G cables between, Sw/Gear S4610 and S4612, between Fuse/Sw S4618 and Transformer TC4-281 and between Fuse/Sw S4616 and Transformer TC4-252. Isolation points: 11kV Sw/gear S4610, S4612, Fuse/Sw S4616 & S4618. | F1 | CRANE SUPPLY | TRITON SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 579 | 576 | 1728 | 0.005278 | 9.1633e-06 | 2014-04-15 | B | 0.002639 | 4.582e-06 | 2015 | 2014-04-15 | B | 3 | 0.005278 | 9.1633e-06
1 | 140095 | 2014-04-15 21:01 | 2014-04-15 21:35 | 34 | 36 | 1224 | 0.0037386 | 0.00010996 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | Defective Component - Emergency isolation to replace 1 HV fuse Holder to Transformer TC2656 at Pole 13598. Tamatu Pene Faultman. Isolation between ABS's 699, 1361 and 837 | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 1116 | 0.0034087 | 0.00010996 | 2014-04-15 | C | 0.0034087 | 0.00010996 | 2015 | 2014-04-15 | C | 36 | 0.0034087 | 0.00010996
1 | 140096 | 2014-04-15 17:36 | 2014-04-15 20:20 | 164 | 8 | 1312 | 0.0040074 | 2.4435e-05 | No Power | 6600 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Other/miscellaneous cause -RS 6551 A/R, L/O, No flags. Faultman dispatched to patrol found crossarm had come free from pole and twisted over causing conductors to touch. Work area isolated at Links 6540 and crossarm reattached to pole. Attended by Nick We | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 164 | 161 | 1288 | 0.0039341 | 2.4435e-05 | 2014-04-15 | C | 0.0039341 | 2.4435e-05 | 2015 | 2014-04-15 | C | 8 | 0.0039341 | 2.4435e-05
1 | 140097 | 2014-04-15 20:50 | 2014-04-15 22:34 | 104 | 37 | 3848 | 0.011753 | 0.00011301 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident -Report came in of car hitting pole. Faultman dispatched found pole needed to be replaced. Backfeed installed via ABS S576 and then work area isolated between ABS S553 and ABS S41. Pole replaced and relivened ok. Attended by Brad Keating. NDR # 3 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 104 | 101 | 3737 | 0.011414 | 0.00011301 | 2014-04-15 | C | 0.011414 | 0.00011301 | 2015 | 2014-04-15 | C | 37 | 0.011414 | 0.00011301
1 | 140099 | 2014-04-15 23:12 | 2014-04-16 02:26 | 194 | 70 | 10984 | 0.03355 | 0.00021381 | No Power | 6600 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum CB H21 A/R, L/O, No flags. Faultmen dispatched to sectionalise and patrol found an opossum on the lines at Pole 760156. Removed using Hot Stick and feeder relivened ok. Attended by Craig Wellington / Brent Moratti. Nil materials used. | F4 | KOHETE RD | MOTUKAWA SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 156.9143 | 153.9143 | 10774 | 0.032908 | 0.00021381 | 2014-04-15 | C | 0.032908 | 0.00021381 | 2015 | 2014-04-15 | C | 70 | 0.032908 | 0.00021381
1 | 140100 | 2014-04-15 21:15 | 2014-04-16 03:45 | 390 | 172 | 67080 | 0.20489 | 0.00052536 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | POLE | Animals - bird Faultman patrolling for No Power fault found top of a softwood pole on fire due to a bird strike. Work area isolated at Fuses 7635 and fire extinguished. Temporary fix carried out by replacing crossarm with a new one mounted lower on the po | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 390 | 387 | 66564 | 0.20331 | 0.00052536 | 2014-04-15 | C | 0.20331 | 0.00052536 | 2015 | 2014-04-15 | C | 172 | 0.20331 | 0.00052536
1 | 140104 | 2014-04-15 23:00 | 2014-04-15 23:15 | 15 | 1686 | 19147 | 0.058483 | 0.0051498 | No Power | 33000 | Unplanned | Zone Sub Equip. | UNKNOWN | NO FAULT FOUND | ZONE TRANSFORMER | Unknown Cause -33kV Incomer CB 342 TRIP, O/C A and C Phase, DIR O/C, INST O/C. This caused a total outage of Taupo Quay Substation. Backfeed of Sub carried out by Isolating suspect fault area at INC1 and INC2, and Closing CB 0 (Bus Tie). Faultman dispatc | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 11.3565 | 8.3565 | 14089 | 0.043034 | 0.0051498 | 2014-04-15 | C | 0.043034 | 0.0051498 | 2015 | 2014-04-15 | C | 1686 | 0.043034 | 0.0051498
1 | 140106 | 2014-04-14 16:40 | 2014-04-14 20:40 | 240 | 2583 | 248320 | 0.75847 | 0.0078896 | No Power | 33000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Trip to L/O on CB 2212 @ TPWR KIN wit h loss of all supply to Baird Rd sub - O/C neutral time flag - unsuccessful attempt of reclose on 2212 following initial cursory line patrol that found all LFI's had operated but no obvious fault found, reclose attem | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 96.1363 | 93.1363 | 240571 | 0.73481 | 0.0078896 | 2014-04-14 | C | 0.73481 | 0.0078896 | 2015 | 2014-04-14 | C | 2583 | 0.73481 | 0.0078896
1 | 140107 | 2014-04-14 16:40 | 2014-04-14 17:50 | 70 | 234 | 16380 | 0.050031 | 0.00071474 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Maraetai CB 4 - Mossops Rd. Feeder from 9598/3 backfed from Baird Rd CB 8 - Dalmeny St and was affected by cable fault which caused LOS to Baird Rd Substation. See FR 140106 for main fault. | F3 | MOSSOPS RD | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 15678 | 0.047887 | 0.00071474 | 2014-04-14 | C | 0.047887 | 0.00071473 | 2015 | 2014-04-14 | C | 234 | 0.047887 | 0.00071474
1 | 140108 | 2014-04-16 08:30 | 2014-04-16 12:30 | 240 | 26 | 6240 | 0.01906 | 7.9415e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91026 - Tree felling around power lines. Isolation points: 7233 | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 6162 | 0.018821 | 7.9415e-05 | 2014-04-16 | B | 0.0094107 | 3.9708e-05 | 2015 | 2014-04-16 | B | 26 | 0.018821 | 7.9415e-05
1 | 140110 | 2014-04-16 12:35 | 2014-04-16 12:55 | 20 | 5 | 100 | 0.00030544 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - Short outage required along Rata St / Manfield Park area to replace a broken Insulator (No trippings, insulator arcing and sparking). Isolation between ABS J1 and J11. Replaced one 11kV insulator and relivened. | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 20 | 17 | 85 | 0.00025963 | 1.5272e-05 | 2014-04-16 | C | 0.00025963 | 1.5272e-05 | 2015 | 2014-04-16 | C | 5 | 0.00025963 | 1.5272e-05
1 | 140112 | 2014-04-16 10:30 | 2014-04-16 11:35 | 65 | 9 | 585 | 0.0017868 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | Defective Component - Emergency switching to repair jumper x 1 at pole 0129. Isolation at ABS 1245 ( no back feeds ) jumper repaired all service restored, Stu Simpson attended. Materials nil Note see F ID 140111 | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 558 | 0.0017044 | 2.749e-05 | 2014-04-16 | C | 0.0017044 | 2.749e-05 | 2015 | 2014-04-16 | C | 9 | 0.0017044 | 2.749e-05
1 | 140113 | 2014-04-16 08:59 | 2014-04-16 14:23 | 324 | 40 | 15000 | 0.045816 | 0.00012218 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90796 - Replace damaged 11kV dead end strain pole WHOGC055 and replace all X-arms on "H" structure P2217 - P13134. Isolation points: 11kV Links 9454/4 & by-pass ABS IC2126. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 375 | 372 | 14880 | 0.04545 | 0.00012218 | 2014-04-16 | B | 0.022725 | 6.1088e-05 | 2015 | 2014-04-16 | B | 40 | 0.04545 | 0.00012218
1 | 140116 | 2014-04-16 08:45 | 2014-04-16 12:48 | 243 | 9 | 3780 | 0.011546 | 2.749e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90858 - Change 11kV pole 209291 (ABS SC2-063) and pole 209525. Isolation points:11kV Jumpers disconnected from Recloser RP08, Line Break at Transformer pole 268157. School to be supplied with Generator. Refer to LLP's 14/90237, 14/90238 & 14/90 | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 420 | 417 | 3753 | 0.011463 | 2.749e-05 | 2014-04-16 | B | 0.0057316 | 1.3745e-05 | 2015 | 2014-04-16 | B | 9 | 0.011463 | 2.749e-05
1 | 140117 | 2014-04-16 09:30 | 2014-04-16 13:40 | 250 | 67 | 16080 | 0.049115 | 0.00020465 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90748 - Replace 11kV G/M Transformer TC4833. Isolation point: 11kV Sw/Gear IC3018. | F3 | PAUANUI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 15879 | 0.048501 | 0.00020465 | 2014-04-16 | B | 0.024251 | 0.00010232 | 2015 | 2014-04-16 | B | 67 | 0.048501 | 0.00020465
1 | 140119 | 2014-04-16 13:00 | 2014-04-16 16:00 | 180 | 35 | 6300 | 0.019243 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90958 - LLP to change 33xarm by g/b method on pole 779274 on Wiaouru 33 feeder. AP to change 11kV Xarm on pole 779274. This arm cannot be changed by g/b method so a small shutdown time is needed. Isolation points: 33kV TP1112, ABS 312, 11kV ABS 13 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 6195 | 0.018922 | 0.0001069 | 2014-04-16 | B | 0.0094611 | 5.3452e-05 | 2015 | 2014-04-16 | B | 35 | 0.018922 | 0.0001069
1 | 140120 | 2014-04-16 09:00 | 2014-04-16 12:18 | 198 | 2 | 720 | 0.0021992 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90934 - Create line break on pole F0354 to allow works to commence. Ref LLP 14/90790 Relocate fuse FC2262 to pole F0355 for existing supply to TC4074. Install new 11kV Fuses on pole F12497 for new 11kV Transformer TP2603. Close Line Break at pole | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 714 | 0.0021809 | 6.1088e-06 | 2014-04-16 | B | 0.0010904 | 3.054e-06 | 2015 | 2014-04-16 | B | 2 | 0.0021809 | 6.1088e-06
1 | 140121 | 2014-04-16 09:15 | 2014-04-16 13:30 | 255 | 24 | 6120 | 0.018693 | 7.3306e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/86423 - Replace rotten termination arms on river crossing at Lake Karapiro from 11kV pole D1489. Note: These cross arms are in poor condition and need to be replaced. Isolation points: 11kV IC722. PD 26.03.14 | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 255 | 252 | 6048 | 0.018473 | 7.3306e-05 | 2014-04-16 | B | 0.0092366 | 3.6653e-05 | 2015 | 2014-04-16 | B | 24 | 0.018473 | 7.3306e-05
1 | 140122 | 2014-04-15 10:20 | 2014-04-15 13:24 | 184 | 40 | 7360 | 0.022481 | 0.00012218 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91395 - Reconnect 11kV cable to HV bushing of TX TC4310. Phasing to be checked across switch 9598/3. Recommend soaking the cable for 12-24 hrs before restoring switching to normal. Isolation points: 11kV Sw/Gear 9598/3, IC3068. Change to alternati | F3 | MOSSOPS RD | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 184 | 181 | 7240 | 0.022114 | 0.00012218 | 2014-04-15 | B | 0.011057 | 6.1088e-05 | 2015 | 2014-04-15 | B | 40 | 0.022114 | 0.00012218
1 | 140123 | 2014-04-16 16:30 | 2014-04-16 19:44 | 194 | 7 | 1358 | 0.0041479 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident -Received a call from the police of a car vs pole, faultman found Fuses 7654 to be open on arrival, line was isolated at Fuses 7654 and the pole 817777 was straightened, pole was not broken. NDR 37682, Brad Keating attended. | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 194 | 191 | 1337 | 0.0040838 | 2.1381e-05 | 2014-04-16 | C | 0.0040838 | 2.1381e-05 | 2015 | 2014-04-16 | C | 7 | 0.0040838 | 2.1381e-05
1 | 140124 | 2014-04-16 18:32 | 2014-04-16 20:23 | 111 | 236 | 18047 | 0.055123 | 0.00072084 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component -CB 3 tripped on no flags, line was patrolled and sectionalised, received a call from customer of a flash, faultman found a damaged insulator at pole P46981, line was isolated at ABS's U31 and U36 to remove the insulator, had double in | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 76.4703 | 73.4703 | 17339 | 0.052961 | 0.00072084 | 2014-04-16 | C | 0.052961 | 0.00072084 | 2015 | 2014-04-16 | C | 236 | 0.052961 | 0.00072084
1 | 140126 | 2014-04-16 10:15 | 2014-04-16 11:17 | 62 | 40 | 2480 | 0.007575 | 0.00012218 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | No Power -Section of line from Fuses WH140 isolated to replace broken dead end on pole 844519 (Attended by Bruce Kerr) | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 2360 | 0.0072084 | 0.00012218 | 2014-04-16 | C | 0.0072084 | 0.00012218 | 2015 | 2014-04-16 | C | 40 | 0.0072084 | 0.00012218
1 | 140128 | 2014-04-16 12:50 | 2014-04-16 13:15 | 25 | 5 | 125 | 0.0003818 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | No Power -Section of line from Fuses 6745 Isolated to replace 3 x dead ends at pole 846142 (Attended by Bruce Kerr) | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 25 | 22 | 110 | 0.00033599 | 1.5272e-05 | 2014-04-16 | C | 0.00033599 | 1.5272e-05 | 2015 | 2014-04-16 | C | 5 | 0.00033599 | 1.5272e-05
1 | 140129 | 2014-04-16 10:31 | 2014-04-16 16:00 | 329 | 13 | 4277 | 0.013064 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90287 - Replace 11kV poles & crossarms. Between 11kV poles M0315 & M12839.Deays caused by emergency repairs required on ABS 922 (Carried out Live Line) | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 329 | 326 | 4238 | 0.012945 | 3.9708e-05 | 2014-04-16 | B | 0.0064723 | 1.9854e-05 | 2015 | 2014-04-16 | B | 13 | 0.012945 | 3.9708e-05
1 | 140130 | 2014-04-16 09:17 | 2014-04-16 13:06 | 229 | 28 | 6412 | 0.019585 | 8.5524e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89956 - Install new double 11kV tap off arms on existing net work pole 854727 fitted w/ new Fuse 8988 for supply to new 11kV spur line and TX 5067T to be livened same day. Confirm Pre Commissioning & Inspection Certificate Completed & Equipment R | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 229 | 226 | 6328 | 0.019328 | 8.5524e-05 | 2014-04-16 | B | 0.0096642 | 4.2762e-05 | 2015 | 2014-04-16 | B | 28 | 0.019328 | 8.5524e-05
1 | 140131 | 2014-04-17 05:47 | 2014-04-17 07:30 | 103 | 92 | 9476 | 0.028944 | 0.00028101 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - Reports of "No Powers" found CB632 (Non Scada) half tripped. Area patrolled and CB reclosed OK. Suspect wind clash with high winds / rain. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 103 | 100 | 9200 | 0.028101 | 0.00028101 | 2014-04-17 | C | 0.028101 | 0.00028101 | 2015 | 2014-04-17 | C | 92 | 0.028101 | 0.00028101
1 | 140133 | 2014-04-17 05:36 | 2014-04-17 09:20 | 224 | 114 | 13656 | 0.041711 | 0.0003482 | No Power | 6600 | Unplanned | Overhead Line | ADVERSE WEATHER | LAND SLIPPAGE - TREES | CONDUCTOR | Defective Component - Tripping on recloser CB1022. Area sectionalised / patrolled with large Gum tree found to have fallen through a conductor. Tree was 30m or so away from line but heavy rain caused tree ro fall over. Conductor rejointed after tree cut a | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 119.7895 | 116.7895 | 13314 | 0.040667 | 0.0003482 | 2014-04-17 | C | 0.040667 | 0.0003482 | 2015 | 2014-04-17 | C | 114 | 0.040667 | 0.0003482
1 | 140134 | 2014-04-17 05:46 | 2014-04-17 06:02 | 16 | 277 | 4432 | 0.013537 | 0.00084608 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Tower Rd - Gordon Rd feeder recloser RC01 tripped on O/C and L/O. NOC disabled A/R. Waited 15 mins and reclosed sucessfully. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 16 | 13 | 3601 | 0.010999 | 0.00084608 | 2014-04-17 | C | 0.010999 | 0.00084607 | 2015 | 2014-04-17 | C | 277 | 0.010999 | 0.00084608
1 | 140135 | 2014-04-17 08:31 | 2014-04-17 12:59 | 268 | 157 | 22651 | 0.069186 | 0.00047954 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Mikkelsen CB5 tripped, A/R disabled. Lines down at pole C163. | F4 | NGARUA | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 144.2739 | 141.2739 | 22180 | 0.067747 | 0.00047954 | 2014-04-17 | C | 0.067747 | 0.00047955 | 2015 | 2014-04-17 | C | 157 | 0.067747 | 0.00047954
1 | 140136 | 2014-04-17 10:57 | 2014-04-17 12:25 | 88 | 283 | 24904 | 0.076067 | 0.0008644 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Recloser 9674 L/O on O/C. Lines down found at pole 208781. | F3 | OMOKOROA RD | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 24055 | 0.073474 | 0.0008644 | 2014-04-17 | C | 0.073474 | 0.0008644 | 2015 | 2014-04-17 | C | 283 | 0.073474 | 0.0008644
1 | 140140 | 2014-04-18 01:20 | 2014-04-18 01:57 | 37 | 183 | 6771 | 0.020682 | 0.00055896 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | NOT PATROLLED | UNKNOWN | NO POWER - Recloser V61 Tripped. Not Patrolled - Fault Unknown. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 6222 | 0.019005 | 0.00055896 | 2014-04-18 | C | 0.019005 | 0.00055896 | 2015 | 2014-04-18 | C | 183 | 0.019005 | 0.00055896
1 | 140141 | 2014-04-17 13:04 | 2014-04-17 16:38 | 214 | 266 | 49712 | 0.15184 | 0.00081248 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Recloser 9222 L/O - Line patrolled - Line down, one phase, due to adverse winds. Shane Pipal attended. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 186.8872 | 183.8872 | 48914 | 0.1494 | 0.00081248 | 2014-04-17 | C | 0.1494 | 0.00081248 | 2015 | 2014-04-17 | C | 266 | 0.1494 | 0.00081248
1 | 140143 | 2014-04-17 08:59 | 2014-04-18 13:10 | 1691 | 413 | 183758 | 0.56127 | 0.0012615 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | CB3 Tripped, L/O during severe storm event causing multiple feeder faults. 1/ Line patrol located lines down at pole near transformer TF7-019 Old Coach Rd, Isolated at ABS SF7-026 & CB3. 2/ Recloser 9556 tripped due to lines down at ABS SF7-025. Isolated | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 444.9346 | 441.9346 | 182519 | 0.55749 | 0.0012615 | 2014-04-17 | C | 0.55749 | 0.0012615 | 2015 | 2014-04-17 | C | 413 | 0.55749 | 0.0012615
1 | 140144 | 2014-04-17 15:10 | 2014-04-17 15:45 | 35 | 4 | 140 | 0.00042762 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Line Patrolled - Lines Down. Adverse Weather - Extreme Wind. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 128 | 0.00039097 | 1.2218e-05 | 2014-04-17 | C | 0.00039097 | 1.2218e-05 | 2015 | 2014-04-17 | C | 4 | 0.00039097 | 1.2218e-05
1 | 140154 | 2014-04-17 16:06 | 2014-04-17 19:56 | 230 | 1159 | 120829 | 0.36906 | 0.0035401 | No Power | 33000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - LOS to Kimbolton Substation. Multiple areas of bark on the line. Repair floating line at pole P13821. | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 104.2528 | 101.2528 | 117352 | 0.35844 | 0.0035401 | 2014-04-17 | C | 0.35844 | 0.0035401 | 2015 | 2014-04-17 | C | 1159 | 0.35844 | 0.0035401
1 | 140156 | 2014-04-17 12:04 | 2014-04-17 16:22 | 258 | 232 | 59738 | 0.18247 | 0.00070863 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - CB3 tripped. No fault found. Adverse Weather/Extreme Wind. | F4 | THOMAS RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 257.4914 | 254.4914 | 59042 | 0.18034 | 0.00070863 | 2014-04-17 | C | 0.18034 | 0.00070863 | 2015 | 2014-04-17 | C | 232 | 0.18034 | 0.00070863
1 | 140162 | 2014-04-17 15:27 | 2014-04-17 19:39 | 252 | 565 | 142380 | 0.43489 | 0.0017257 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Recloser 9593 Tripped - Line Patrolled - Branch Located On Line. Adverse Weather/Extreme Wind. | F3 | BROOKFIELD TCE | OTUMOETAI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 252 | 249 | 140685 | 0.42971 | 0.0017257 | 2014-04-17 | C | 0.42971 | 0.0017257 | 2015 | 2014-04-17 | C | 565 | 0.42971 | 0.0017257
1 | 140165 | 2014-04-17 18:03 | 2014-04-17 19:30 | 87 | 15 | 1305 | 0.003986 | 4.5816e-05 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - Car vs Pole. NDR 37914. Replace 1 pole and associated equipment. Pole 824602 | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 87 | 84 | 1260 | 0.0038486 | 4.5816e-05 | 2014-04-17 | C | 0.0038486 | 4.5816e-05 | 2015 | 2014-04-17 | C | 15 | 0.0038486 | 4.5816e-05
1 | 140166 | 2014-04-17 15:54 | 2014-04-18 16:15 | 1461 | 205 | 107697 | 0.32895 | 0.00062616 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Pongakawa CB4 - Recloser RS9463 found tripped following relivening of Pongakawa Sub during severe storm event. Multiple faults found. 1/ Line Patrol found Trees on line at Pole # 228683. Isolated at SF6-014. Tree cleared, lines cleared, supply res | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 525.3512 | 522.3512 | 107082 | 0.32707 | 0.00062616 | 2014-04-17 | C | 0.32707 | 0.00062616 | 2015 | 2014-04-17 | C | 205 | 0.32707 | 0.00062616
1 | 140168 | 2014-04-17 11:11 | 2014-04-17 19:23 | 492 | 137 | 59540 | 0.18186 | 0.00041846 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Kimbolton CB5; Recloser P61 Tripped O/C. Line Patrolled - No Fault Located. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 434.5985 | 431.5985 | 59129 | 0.18061 | 0.00041846 | 2014-04-17 | C | 0.18061 | 0.00041846 | 2015 | 2014-04-17 | C | 137 | 0.18061 | 0.00041846
1 | 140170 | 2014-04-17 11:22 | 2014-04-17 14:59 | 217 | 887 | 72236 | 0.22064 | 0.0027093 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Welcome Bay CB1 tripped. L/O. Line patrolled. Lines down loctaed. Isolated at pole 210858. Adverse Weather/Extreme Wind. Hilton Gardiner & Ken Douglas attended. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 81.4386 | 78.4386 | 69575 | 0.21251 | 0.0027093 | 2014-04-17 | C | 0.21251 | 0.0027093 | 2015 | 2014-04-17 | C | 887 | 0.21251 | 0.0027093
1 | 140171 | 2014-04-17 12:56 | 2014-04-17 14:50 | 114 | 344 | 22296 | 0.068101 | 0.0010507 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Turitea CB4 Recloser RC10050 E/F - Line Patrolled - Trees on Line Located. Removed by Hot Stick. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 64.814 | 61.814 | 21264 | 0.064949 | 0.0010507 | 2014-04-17 | C | 0.064949 | 0.0010507 | 2015 | 2014-04-17 | C | 344 | 0.064949 | 0.0010507
1 | 140173 | 2014-04-17 09:42 | 2014-04-17 14:27 | 285 | 313 | 65383 | 0.19971 | 0.00095603 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Welcome Bay CB1 tripped. L/O. Line Patrolled. No Fault Located. Adverse Weather/Extreme Wind. Hilton Gardiner Attended. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 208.8914 | 205.8914 | 64444 | 0.19684 | 0.00095603 | 2014-04-17 | C | 0.19684 | 0.00095604 | 2015 | 2014-04-17 | C | 313 | 0.19684 | 0.00095603
1 | 140174 | 2014-04-17 12:35 | 2014-04-17 20:19 | 464 | 106 | 42434 | 0.12961 | 0.00032377 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power -Kelvin Grove CB8 Recloser E33 Tripped O/C - Line Patrolled - No Fault Found. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 400.3208 | 397.3208 | 42116 | 0.12864 | 0.00032377 | 2014-04-17 | C | 0.12864 | 0.00032377 | 2015 | 2014-04-17 | C | 106 | 0.12864 | 0.00032377
1 | 140175 | 2014-04-17 08:47 | 2014-04-17 13:26 | 279 | 359 | 87985 | 0.26874 | 0.0010965 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | FUSE | No Power - Piako CB5 tripped on B phase and E/F and L/O. ABS IC775 and IC783 were opened. CB5 closed. No fault found. | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 245.0836 | 242.0836 | 86908 | 0.26545 | 0.0010965 | 2014-04-17 | C | 0.26545 | 0.0010965 | 2015 | 2014-04-17 | C | 359 | 0.26545 | 0.0010965
1 | 140176 | 2014-04-17 20:43 | 2014-04-17 23:46 | 183 | 176 | 29243 | 0.089321 | 0.00053758 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Pongaroa CB3 Tripped - No Flags - Line Patrolled and Tree Branch found as Pole # P04599. Removed with Hot Stick. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 166.1534 | 163.1534 | 28715 | 0.087708 | 0.00053758 | 2014-04-17 | C | 0.087708 | 0.00053758 | 2015 | 2014-04-17 | C | 176 | 0.087708 | 0.00053758
1 | 140178 | 2014-04-18 10:40 | 2014-04-18 11:14 | 34 | 42 | 1428 | 0.0043617 | 0.00012829 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Repair jumper at ABS E87.Bruce Mehrtens attended. | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 1302 | 0.0039769 | 0.00012829 | 2014-04-18 | C | 0.0039769 | 0.00012829 | 2015 | 2014-04-18 | C | 42 | 0.0039769 | 0.00012829
1 | 140179 | 2014-04-17 18:50 | 2014-04-17 23:32 | 282 | 125 | 22117 | 0.067555 | 0.0003818 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Blink Bonnie CB4 Recloser RS4200 - Line Patrolled - Branch found at Pole 791235. Knocked off by hotstick. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 176.936 | 173.936 | 21742 | 0.066409 | 0.0003818 | 2014-04-17 | C | 0.066409 | 0.0003818 | 2015 | 2014-04-17 | C | 125 | 0.066409 | 0.0003818
1 | 140180 | 2014-04-17 09:43 | 2014-04-17 13:34 | 231 | 272 | 46006 | 0.14052 | 0.0008308 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Gordon Feeder RC01 Tripped. Line patrolled and lines down located at pole F1126. Line repiared and 3x insulators replaced. Adverse Weather/Extreme Wind. Greg Whyte attended. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 169.1397 | 166.1397 | 45190 | 0.13803 | 0.0008308 | 2014-04-17 | C | 0.13803 | 0.0008308 | 2015 | 2014-04-17 | C | 272 | 0.13803 | 0.0008308
1 | 140181 | 2014-04-17 13:45 | 2014-04-17 15:20 | 95 | 59 | 5605 | 0.01712 | 0.00018021 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Reports received of HT line down. Back feed applied from RC 10082 KEG10. Isolated between ABS E65 & ABS F69. Line repaired, supply restored. Re-joined 10 meters of conductor. Jeff Roberts attended. Note: Recloser RC10082 Tripped wh | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 95 | 92 | 5428 | 0.016579 | 0.00018021 | 2014-04-17 | C | 0.016579 | 0.00018021 | 2015 | 2014-04-17 | C | 59 | 0.016579 | 0.00018021
1 | 140182 | 2014-04-17 15:50 | 2014-04-17 18:17 | 147 | 1021 | 147315 | 0.44996 | 0.0031186 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Kelvin Grove CB8 - E/F; Line Patrolled - 2 Lines Down at Pole P39533. Isolated at ABS E65, F70 & F69. No Backfeed Applied. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 144.285 | 141.285 | 144252 | 0.44061 | 0.0031186 | 2014-04-17 | C | 0.44061 | 0.0031186 | 2015 | 2014-04-17 | C | 1021 | 0.44061 | 0.0031186
1 | 140183 | 2014-04-17 08:55 | 2014-04-17 16:28 | 453 | 424 | 77624 | 0.2371 | 0.0012951 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Mikelsen CB8 tripped and L/O. NOC disabled A/R. 11kV ABS 578 opened and tagged. Downed lines found at Pole C2815. ABS closed and A/R enabled. SCADA updated. Jason Deans attended. | F4/F5 | MOUNTAIN | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 183.0755 | 180.0755 | 76352 | 0.23321 | 0.0012951 | 2014-04-17 | C | 0.23321 | 0.0012951 | 2015 | 2014-04-17 | C | 424 | 0.23321 | 0.0012951
1 | 140184 | 2014-04-18 09:26 | 2014-04-18 10:40 | 74 | 6 | 444 | 0.0013562 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | FUSE | Waituna fuses 10185 opened and tagged to remove tree from lines. Tracy Hall attended. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 74 | 71 | 426 | 0.0013012 | 1.8327e-05 | 2014-04-18 | C | 0.0013012 | 1.8327e-05 | 2015 | 2014-04-18 | C | 6 | 0.0013012 | 1.8327e-05
1 | 140185 | 2014-04-17 14:19 | 2014-04-17 16:04 | 105 | 1422 | 149310 | 0.45606 | 0.0043434 | No Power | 33000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | UNKNOWN | No Power - Loss of Supply to Kimbolton Substation. Line Patrolled - Wind Blown Branch Located. Removed. Adverse Weather/Extreme Wind. | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 145044 | 0.44303 | 0.0043434 | 2014-04-17 | C | 0.44303 | 0.0043434 | 2015 | 2014-04-17 | C | 1422 | 0.44303 | 0.0043434
1 | 140186 | 2014-04-17 14:08 | 2014-04-17 15:37 | 89 | 885 | 78765 | 0.24058 | 0.0027032 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - Recloser RC10082 Tripped while back feeding to make repairs due to HT line down. Investigations reveal Tree branch on lines at pole P40107 during severe gales. Cleared branch from lines, supply restored. Also refer FR 140181 | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 89 | 86 | 76110 | 0.23247 | 0.0027032 | 2014-04-17 | C | 0.23247 | 0.0027032 | 2015 | 2014-04-17 | C | 885 | 0.23247 | 0.0027032
1 | 140187 | 2014-04-18 09:00 | 2014-04-18 10:06 | 66 | 50 | 2535 | 0.007743 | 0.00015272 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | FUSE | Bideford C218 found open. Line patrolled and nothing found. C218 closed. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 50.7 | 47.7 | 2385 | 0.0072848 | 0.00015272 | 2014-04-18 | C | 0.0072848 | 0.00015272 | 2015 | 2014-04-18 | C | 50 | 0.0072848 | 0.00015272
1 | 140189 | 2014-04-17 14:02 | 2014-04-17 17:04 | 182 | 693 | 117186 | 0.35794 | 0.0021167 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Waitara West F11 Circuit Breaker Tripped - Line Patrolled - HV Sleeve Damaged resulting in LV Line Down. Adverse Weather/Extreme Wind. | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 169.0996 | 166.0996 | 115107 | 0.35159 | 0.0021167 | 2014-04-17 | C | 0.35159 | 0.0021167 | 2015 | 2014-04-17 | C | 693 | 0.35159 | 0.0021167
1 | 140190 | 2014-04-17 11:16 | 2014-04-17 13:04 | 108 | 1882 | 73080 | 0.22322 | 0.0057484 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - CB7 Tripped. Line patrols & sectionalising located loose Xarm / king pin & broken conductor at same pole P44139. Replaced King pin, repaired conductor, restored supply. Shaz & Mike Thompson attended. Note: NOC could not remotely cl | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 38.831 | 35.831 | 67434 | 0.20597 | 0.0057484 | 2014-04-17 | C | 0.20597 | 0.0057484 | 2015 | 2014-04-17 | C | 1882 | 0.20597 | 0.0057484
1 | 140191 | 2014-04-17 15:08 | 2014-04-17 15:49 | 41 | 110 | 4510 | 0.013775 | 0.00033599 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | Defective Component - Reports received of sparking at head of pole Hammond Rd. Investigations reveal broken HT Fuse holder at transformer T1/73. Back feed applied from ABS L23. Isolated between ABS O62 & ABS O67. Fuse holder replaced, supply restored. Ni | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 41 | 38 | 4180 | 0.012767 | 0.00033599 | 2014-04-17 | C | 0.012767 | 0.00033599 | 2015 | 2014-04-17 | C | 110 | 0.012767 | 0.00033599
1 | 140192 | 2014-04-17 21:40 | 2014-04-17 22:19 | 39 | 1 | 39 | 0.00011912 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | No Power - Papamoa CB5 - Line Patrolled - Blown Jumper at Pole # 219469: Adverse Weather/Extreme Wind. | F3 | PAPAMOA BEACH WEST | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 39 | 36 | 36 | 0.00010996 | 3.0544e-06 | 2014-04-17 | C | 0.00010996 | 3.054e-06 | 2015 | 2014-04-17 | C | 1 | 0.00010996 | 3.0544e-06
1 | 140193 | 2014-04-17 10:38 | 2014-04-17 20:21 | 583 | 84 | 40492 | 0.12368 | 0.00025657 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Aongatere CB1 Tripped L/O - Line Patrolled. Branch On Line Located. Removed. Materials Used: 10m conductor & 4 full Namu sleeves. Adverse Weather/Extreme Wind. | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 482.0476 | 479.0476 | 40240 | 0.12291 | 0.00025657 | 2014-04-17 | C | 0.12291 | 0.00025657 | 2015 | 2014-04-17 | C | 84 | 0.12291 | 0.00025657
1 | 140195 | 2014-04-17 11:54 | 2014-04-17 19:00 | 426 | 235 | 77133 | 0.2356 | 0.00071779 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Circuit Breaker Ngariki NG2 Tripped A & B Phase O/C and E/F. Line Patrolled - Lines Down at Pole Number 912073. Adverse Weather/Extreme Wind. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 328.2255 | 325.2255 | 76428 | 0.23344 | 0.00071779 | 2014-04-17 | C | 0.23344 | 0.00071779 | 2015 | 2014-04-17 | C | 235 | 0.23344 | 0.00071779
1 | 140197 | 2014-04-17 16:49 | 2014-04-17 18:33 | 104 | 1445 | 62528 | 0.19099 | 0.0044136 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS | FUSE | No Power - Recloser 10083 Tripped - Line Patrolled - Broken HT Fuses found at pole P07329, caused by flying trampoline. | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 43.272 | 40.272 | 58193 | 0.17775 | 0.0044136 | 2014-04-17 | C | 0.17775 | 0.0044136 | 2015 | 2014-04-17 | C | 1445 | 0.17775 | 0.0044136
1 | 140198 | 2014-04-17 17:09 | 2014-04-18 14:01 | 1252 | 12 | 15024 | 0.04589 | 3.6653e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | No Power - Line Patrolled and fault located at Pole 711788. Trees removed from lines. | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 1252 | 1249 | 14988 | 0.04578 | 3.6653e-05 | 2014-04-17 | C | 0.04578 | 3.6653e-05 | 2015 | 2014-04-17 | C | 12 | 0.04578 | 3.6653e-05
1 | 140199 | 2014-04-17 14:20 | 2014-04-18 10:39 | 1219 | 10 | 12190 | 0.037233 | 3.0544e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Strathmore CB7111 Tripped. Isolated at Fuses 5483 and customers left off overnight. (10 ICP's) Fault Unknown. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 1219 | 1216 | 12160 | 0.037142 | 3.0544e-05 | 2014-04-17 | C | 0.037142 | 3.0544e-05 | 2015 | 2014-04-17 | C | 10 | 0.037142 | 3.0544e-05
1 | 140201 | 2014-04-18 09:00 | 2014-04-18 20:00 | 660 | 118 | 42737 | 0.13054 | 0.00036042 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Recloser V61 found tripped after reports of no power. Feeder sectionalised and patrolled with fault located at T9/214. (Faulty Transformer). Presently on a Generator - to be replaced 22nd April. Rest of feeder Relivened remainder OK. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 362.178 | 359.178 | 42383 | 0.12946 | 0.00036042 | 2014-04-18 | C | 0.12946 | 0.00036042 | 2015 | 2014-04-18 | C | 118 | 0.12946 | 0.00036042
1 | 140202 | 2014-04-18 20:40 | 2014-04-18 21:20 | 40 | 116 | 4640 | 0.014173 | 0.00035431 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Outage required between ABS A81, A62 and sw/Gear 10172/1 to repair a loose jumper at T6/517. (Needed to be reconnected to top of DDO). No materials required. Relivened OK. | F3 | PASCAL ST 9 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 4292 | 0.01311 | 0.00035431 | 2014-04-18 | C | 0.01311 | 0.00035431 | 2015 | 2014-04-18 | C | 116 | 0.01311 | 0.00035431
1 | 140203 | 2014-04-17 12:40 | 2014-04-17 13:50 | 70 | 216 | 14910 | 0.045541 | 0.00065976 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Recloser RP40 Tripped during severe storm event. Line sectionalised & supply restored, No Fault Found. Marty Keenan faultman. | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 69.0278 | 66.0278 | 14262 | 0.043562 | 0.00065976 | 2014-04-17 | C | 0.043562 | 0.00065976 | 2015 | 2014-04-17 | C | 216 | 0.043562 | 0.00065976
1 | 140204 | 2014-04-17 11:29 | 2014-04-17 14:11 | 162 | 326 | 44869 | 0.13705 | 0.00099574 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Recloser RP09 Tripped during severe storm event. Line sectionalised & restored with no fault found. Faultman Josh Reid. | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 137.635 | 134.635 | 43891 | 0.13406 | 0.00099574 | 2014-04-17 | C | 0.13406 | 0.00099574 | 2015 | 2014-04-17 | C | 326 | 0.13406 | 0.00099574
1 | 140205 | 2014-04-17 05:56 | 2014-04-17 09:30 | 214 | 412 | 31299 | 0.0956 | 0.0012584 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB1 Tripped L/O. Line patrols, sectionalising located Tree thru lines at pole C13371 Manawaru Rd area. Isolated between ABS 1098, 772 & IC676. Back feeds applied from Recloser 9705 & 9715. Tree cleared, lines repaired, supply restored. Attended by | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 75.9684 | 72.9684 | 30063 | 0.091825 | 0.0012584 | 2014-04-17 | C | 0.091825 | 0.0012584 | 2015 | 2014-04-17 | C | 412 | 0.091825 | 0.0012584
1 | 140206 | 2014-04-19 10:19 | 2014-04-19 10:58 | 39 | 43 | 1677 | 0.0051223 | 0.00013134 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | FUSE | No Power -Shutdown requied to put wire back in Top of Fuses Isolation Pointt ABS K25 & K26 Back Feed in at ABS K31 Jeff Roberts Attanded | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39 | 36 | 1548 | 0.0047282 | 0.00013134 | 2014-04-19 | C | 0.0047282 | 0.00013134 | 2015 | 2014-04-19 | C | 43 | 0.0047282 | 0.00013134
1 | 140207 | 2014-04-19 08:50 | 2014-04-19 10:50 | 120 | 9 | 1080 | 0.0032988 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | No Power -Fuses 5369 opened at unknown time Jade Williams attended 19/04/14. Had tree trimming there cleaned out trees rehung conducto.r Isoaltion Point Fuses 5369 No back feed | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 1053 | 0.0032163 | 2.749e-05 | 2014-04-19 | C | 0.0032163 | 2.749e-05 | 2015 | 2014-04-19 | C | 9 | 0.0032163 | 2.749e-05
1 | 140208 | 2014-04-17 10:50 | 2014-04-17 12:30 | 100 | 76 | 7600 | 0.023214 | 0.00023214 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | Defective Component - Reports received of Part Powers. Line Patrol located broken jumper at HT fuses to transformer TC5-008. Isolated at fuses, jumper repaired, supply restored. Mike Strange attended. | F3 | CONCORDE AVE | OMANU SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 7372 | 0.022517 | 0.00023214 | 2014-04-17 | C | 0.022517 | 0.00023214 | 2015 | 2014-04-17 | C | 76 | 0.022517 | 0.00023214
1 | 140210 | 2014-04-19 08:26 | 2014-04-19 09:30 | 64 | 4 | 256 | 0.00078193 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 08:26 Lake Rd Sub, CB 5 Buckland Rd Feeder. Found Transformer TC3913 had blown due to lightning in the area. Own Isolation & Access Permit. Transformer Replaced & All Power Restored on Completion. Jason Deans Attended. 1x Transformer Replac | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 244 | 0.00074528 | 1.2218e-05 | 2014-04-19 | C | 0.00074528 | 1.2218e-05 | 2015 | 2014-04-19 | C | 4 | 0.00074528 | 1.2218e-05
1 | 140211 | 2014-04-19 12:11 | 2014-04-19 12:26 | 15 | 126 | 1890 | 0.0057729 | 0.00038486 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | No Power -Recloser F26 Tripped E/F Just after it Started to rain Closed back in 15 minutes later all good Not Patrolled | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 1512 | 0.0046183 | 0.00038486 | 2014-04-19 | C | 0.0046183 | 0.00038486 | 2015 | 2014-04-19 | C | 126 | 0.0046183 | 0.00038486
1 | 140212 | 2014-04-19 16:00 | 2014-04-20 10:30 | 1110 | 3 | 3330 | 0.010171 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 16:00, Waihi Sub, CB 6 Waitawheta Feeder. Found Transformer TC903 Blown. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. 1x Transformer & 2x 11kV Fuses Replaced. Wayne Seath Attended. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 1110 | 1107 | 3321 | 0.010144 | 9.1633e-06 | 2014-04-19 | C | 0.010144 | 9.163e-06 | 2015 | 2014-04-19 | C | 3 | 0.010144 | 9.1633e-06
1 | 140213 | 2014-04-19 10:09 | 2014-04-19 13:03 | 174 | 245 | 40634 | 0.12411 | 0.00074833 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | JOINT FAILURE | CABLE | No Power -Shutdown required to run 1 Span of Conductor as underground cable blown up. Isolation points CB 4 Roberts Ave Sub ABS 494 ABS 1457 & ABS 4210 Back Feeds in at MABS 688 Recloser 4616 & MABS 1487. Day before James Prime Did switching. Garry | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 165.8531 | 162.8531 | 39899 | 0.12187 | 0.00074833 | 2014-04-19 | C | 0.12187 | 0.00074833 | 2015 | 2014-04-19 | C | 245 | 0.12187 | 0.00074833
1 | 140214 | 2014-04-19 07:16 | 2014-04-19 11:38 | 262 | 5 | 1310 | 0.0040013 | 1.5272e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 07:16 Kerepehi Sub, CB 5 Mangatarata Feeder. Found Transformer TC1796 Blown due to lightning in area. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. 1x Transformer Replaced, 3x LV Fuse Carriers & Fuses Replaced | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 262 | 259 | 1295 | 0.0039555 | 1.5272e-05 | 2014-04-19 | C | 0.0039555 | 1.5272e-05 | 2015 | 2014-04-19 | C | 5 | 0.0039555 | 1.5272e-05
1 | 140215 | 2014-04-19 12:49 | 2014-04-19 13:57 | 68 | 6 | 408 | 0.0012462 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power - Fuses 4015 opened due to Lines down. Made temp line Break at Pole 807925. Transformer X250 Still Off. Neville Ashton & Paul Osbourne Attended. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 390 | 0.0011912 | 1.8327e-05 | 2014-04-19 | C | 0.0011912 | 1.8327e-05 | 2015 | 2014-04-19 | C | 6 | 0.0011912 | 1.8327e-05
1 | 140216 | 2014-04-19 10:58 | 2014-04-19 12:00 | 62 | 3 | 186 | 0.00056812 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 10:58, Pongakawa Sub, CB 3 Rotoehu Feeder. Found Transformer TF7-023 Blown. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. 1x Transformer Replaced, 2x HV fuses replaced. Hayden Bedgood Attended. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 177 | 0.00054063 | 9.1633e-06 | 2014-04-19 | C | 0.00054063 | 9.163e-06 | 2015 | 2014-04-19 | C | 3 | 0.00054063 | 9.1633e-06
1 | 140217 | 2014-04-17 16:00 | 2014-04-18 14:15 | 1335 | 2 | 2670 | 0.0081553 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power -Fuses F30 Open Due to Lines down Dave Whale Attended Replaced 60 m Conductor & 1 x H/T insulator. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1335 | 1332 | 2664 | 0.008137 | 6.1088e-06 | 2014-04-17 | C | 0.008137 | 6.109e-06 | 2015 | 2014-04-17 | C | 2 | 0.008137 | 6.1088e-06
1 | 140218 | 2014-04-19 11:42 | 2014-04-19 15:43 | 241 | 492 | 114452 | 0.34958 | 0.0015028 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | No Power -CB C850 tripped Patrolled Found Mappie at Pole 835389 removed with Hot Stickes Reliven Ok | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 232.626 | 229.626 | 112976 | 0.34508 | 0.0015028 | 2014-04-19 | C | 0.34508 | 0.0015028 | 2015 | 2014-04-19 | C | 492 | 0.34508 | 0.0015028
1 | 140219 | 2014-04-19 09:57 | 2014-04-19 13:06 | 189 | 581 | 60164 | 0.18377 | 0.0017746 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 09:57 Coromandel Sub, CB 5 Manaia Feeder, Recloser RC12 Tripped, No Flags, L/O. Faultman Dispatched. Sectionalising Began. Report of Line Down came through. Faultman dispatched to lines down at Pole T1417. Isolated Lines at ABS IC380, ABS 923 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 103.5525 | 100.5525 | 58421 | 0.17844 | 0.0017746 | 2014-04-19 | C | 0.17844 | 0.0017746 | 2015 | 2014-04-19 | C | 581 | 0.17844 | 0.0017746
1 | 140220 | 2014-04-19 15:34 | 2014-04-19 16:01 | 27 | 253 | 6831 | 0.020865 | 0.00077277 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | No Power -CB 11 tripped. Faultman spoke to a man who said a bird had hit the line. Reliven OK. Dave Thompson & Shazil Khan Attended | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 6072 | 0.018546 | 0.00077277 | 2014-04-19 | C | 0.018546 | 0.00077277 | 2015 | 2014-04-19 | C | 253 | 0.018546 | 0.00077277
1 | 140222 | 2014-04-19 06:46 | 2014-04-19 16:57 | 611 | 44 | 26884 | 0.082115 | 0.00013439 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | No Power -Recloser 6413 Tripped. Patrolled found trees in lines. All single Phase transformers so put all on the 2 phases still up on poles. Made rest safe & relivened. Trees will take 2 or 3 days to remove. Phil Webby is arranging this. | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 611 | 608 | 26752 | 0.081712 | 0.00013439 | 2014-04-19 | C | 0.081712 | 0.00013439 | 2015 | 2014-04-19 | C | 44 | 0.081712 | 0.00013439
1 | 140223 | 2014-04-19 12:02 | 2014-04-19 18:55 | 413 | 65 | 20432 | 0.062408 | 0.00019854 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power -Recloser V5 tripped Patrolled Found Conductor Down at Pole P28857 Isolation point Fuses V14 . Robin Smith Attended. Broken conductor repaired (Only 2 sleeves required). Relivened OK. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 314.3385 | 311.3385 | 20237 | 0.061812 | 0.00019854 | 2014-04-19 | C | 0.061812 | 0.00019854 | 2015 | 2014-04-19 | C | 65 | 0.061812 | 0.00019854
1 | 140224 | 2014-04-19 20:38 | 2014-04-19 21:55 | 77 | 424 | 17416 | 0.053196 | 0.0012951 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - Tripping on CB8 on E/F. SCADA Controlled Sw/Gear 10173 used for backfeed initially then feeder patrolled and sectionalised. All restored OK. Suspect intermittent fault on overhead along Rangitikei / Flygers Line area. | F2 | RANGITIKEI | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 41.0755 | 38.0755 | 16144 | 0.049311 | 0.0012951 | 2014-04-19 | C | 0.049311 | 0.0012951 | 2015 | 2014-04-19 | C | 424 | 0.049311 | 0.0012951
1 | 140225 | 2014-04-19 10:26 | 2014-04-19 19:12 | 526 | 247 | 49058 | 0.14984 | 0.00075444 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 10:26, Tairua Sub, CB 3 Hikuai Feeder, Recloser 9643 Tripped, Ph C O/C, E/F, L/O. Faultman Dispatched & Investigation Began. Feeder Sectionalised. Found Line down at Pole U0563. Lines Isolated at Links LC4181. Permit Issued & Repairs Carried | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 198.6154 | 195.6154 | 48317 | 0.14758 | 0.00075444 | 2014-04-19 | C | 0.14758 | 0.00075444 | 2015 | 2014-04-19 | C | 247 | 0.14758 | 0.00075444
1 | 140226 | 2014-04-18 19:51 | 2014-04-18 21:45 | 114 | 4 | 456 | 0.0013928 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 19:51, Pongakawa Sub, CB 3 Rotoehu Feeder. Found Transformer TF7-133 Blown due to lightning in the area. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. Hayden Bedgood Attended. 1x Transformer Replaced. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 114 | 111 | 444 | 0.0013562 | 1.2218e-05 | 2014-04-18 | C | 0.0013562 | 1.2218e-05 | 2015 | 2014-04-18 | C | 4 | 0.0013562 | 1.2218e-05
1 | 140227 | 2014-04-20 10:15 | 2014-04-20 11:05 | 50 | 2 | 100 | 0.00030544 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - at 10:15, Pongakawa Sub, CB 3 Rotoehu Feeder. Found Transformer TG7-012 Blown due to lightning in the area. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. Ted Glasgow Attended. 1x Transformer & 3 HV Fuses Replaced | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 94 | 0.00028712 | 6.1088e-06 | 2014-04-20 | C | 0.00028712 | 6.109e-06 | 2015 | 2014-04-20 | C | 2 | 0.00028712 | 6.1088e-06
1 | 140228 | 2014-04-20 12:56 | 2014-04-20 13:54 | 58 | 359 | 20822 | 0.063599 | 0.0010965 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - at 12:56, Piako Sub, CB 5 Kiwitahi Feeder, Tripped, Ph B & C O/C, E/F, L/O. Call received on emergency line of large flash across the road running along the lines. Faultman Dispatched to investigate. Found that a tree branch had been blown into th | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 58 | 55 | 19745 | 0.06031 | 0.0010965 | 2014-04-20 | C | 0.06031 | 0.0010965 | 2015 | 2014-04-20 | C | 359 | 0.06031 | 0.0010965
1 | 140229 | 2014-04-19 18:51 | 2014-04-19 21:51 | 180 | 4 | 720 | 0.0021992 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | LV FAULT - OTHER | Defective Component - at 18:51, Atuaroa Sub, CB 2 No. 3 Rd Feeder. LV Lines had come down fed from Transformer TE5-101. Faultman Required to Isolate LV Lines at 11kV Transformer Fuses TE5-101 and repairs be carried out in the morning. Isolated Transformer | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 708 | 0.0021625 | 1.2218e-05 | 2014-04-19 | C | 0.0021625 | 1.2218e-05 | 2015 | 2014-04-19 | C | 4 | 0.0021625 | 1.2218e-05
1 | 140230 | 2014-04-20 17:18 | 2014-04-20 18:12 | 54 | 73 | 3942 | 0.012041 | 0.00022297 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power -Shutdown required at Fuses 1112 Due to Lines down No Back Feed used Used 10M 16mm Copper Conductor 2 Sleeves James Prime Attended | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 3723 | 0.011372 | 0.00022297 | 2014-04-20 | C | 0.011372 | 0.00022297 | 2015 | 2014-04-20 | C | 73 | 0.011372 | 0.00022297
1 | 140231 | 2014-04-20 17:35 | 2014-04-20 18:00 | 25 | 13 | 325 | 0.00099269 | 3.9708e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | No Power -Shutdown Required at Fuses P26 Branches on Line removed with Hotstick Shazil Khan Attended | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 25 | 22 | 286 | 0.00087357 | 3.9708e-05 | 2014-04-20 | C | 0.00087356 | 3.9708e-05 | 2015 | 2014-04-20 | C | 13 | 0.00087357 | 3.9708e-05
1 | 140232 | 2014-04-20 10:42 | 2014-04-20 16:04 | 322 | 783 | 78254 | 0.23902 | 0.0023916 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | No Power -CB 23 Tripped E/F Patrolled found Lines Down Islotion points ABS A91 ABS B43 ABS B14 ABS B3 Back Feed in at Recloser 10041 And ABS B23 Repaired Line Using 5M Conductor Shane Robinson & Anjay Prasad Attended | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 99.9413 | 96.9413 | 75905 | 0.23185 | 0.0023916 | 2014-04-20 | C | 0.23185 | 0.0023916 | 2015 | 2014-04-20 | C | 783 | 0.23185 | 0.0023916
1 | 140235 | 2014-04-19 16:29 | 2014-04-20 10:56 | 1107 | 109 | 98531 | 0.30096 | 0.00033293 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | POLE | Animals - bird. RS 513 A/R, L/O, O/C. Faultman dispatched to sectionalise and patrol found a pole that been on fire due to a bird strike and the crossarm had detached from the pole, twisted over and caused line clash. Fault isolated at ABS 199 and power l | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 903.9541 | 900.9541 | 98204 | 0.29996 | 0.00033293 | 2014-04-19 | C | 0.29996 | 0.00033293 | 2015 | 2014-04-19 | C | 109 | 0.29996 | 0.00033293
1 | 140236 | 2014-04-17 16:33 | 2014-04-20 16:12 | 4299 | 7 | 1575 | 0.0048107 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -Faultman dispatched to No power faults found tree had come down across lines tripping fuses F84. Line break made at pole P39564 leaving power off to Transformer T4/427 until tree could be cleared and lines repaired. Line crew returned on 20/04/14 a | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 225 | 222 | 1554 | 0.0047466 | 2.1381e-05 | 2014-04-17 | C | 0.0047466 | 2.1381e-05 | 2015 | 2014-04-17 | C | 7 | 0.0047466 | 2.1381e-05
1 | 140237 | 2014-04-21 08:30 | 2014-04-21 09:35 | 65 | 62 | 4030 | 0.012309 | 0.00018937 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT BIRD | UNKNOWN | Unknown Cause -CB C917 A/R, No flags. No power faults started to come in after this so faultman dispatched to investigate found non scadarised sectionaliser C641/2 open on arrival. SS C641/2 closed and line patrolled with no fault or cause found. Attended | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 3844 | 0.011741 | 0.00018937 | 2014-04-21 | C | 0.011741 | 0.00018937 | 2015 | 2014-04-21 | C | 62 | 0.011741 | 0.00018937
1 | 140238 | 2014-04-21 11:20 | 2014-04-21 11:37 | 17 | 44 | 748 | 0.0022847 | 0.00013439 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees -Faultman noticed tree branch sitting across HV lines at Pole 716115. Work area de energised between ABS TA919 and ABS TA971, and branch removed using hot stick. Attended by Bevan Hughes. Nil materials used. | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 616 | 0.0018815 | 0.00013439 | 2014-04-21 | C | 0.0018815 | 0.00013439 | 2015 | 2014-04-21 | C | 44 | 0.0018815 | 0.00013439
1 | 140239 | 2014-04-20 09:31 | 2014-04-20 12:05 | 154 | 1260 | 36663 | 0.11198 | 0.0038486 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning -CB5 TRIP, O/C-A phase. Faultmen dispatched to patrol with no fault found. CB 5 relivened ok. It was later discovered that Transformer 1829N was blown as was associated lightning arrestor, and dropout fuse damaged. This transformer is local supp | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 29.0976 | 26.0976 | 32883 | 0.10044 | 0.0038486 | 2014-04-20 | C | 0.10044 | 0.0038486 | 2015 | 2014-04-20 | C | 1260 | 0.10044 | 0.0038486
1 | 140240 | 2014-04-18 15:37 | 2014-04-21 13:20 | 4183 | 8 | 4673 | 0.014273 | 2.4435e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Transformer TF6-109 found faulty, isolated on 18/04/14 Due to access fuses SF6-008 used to isolate area so transformer could be changed. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 584.125 | 581.125 | 4649 | 0.0142 | 2.4435e-05 | 2014-04-18 | C | 0.0142 | 2.4435e-05 | 2015 | 2014-04-18 | C | 8 | 0.0142 | 2.4435e-05
1 | 140241 | 2014-04-21 11:52 | 2014-04-21 12:10 | 18 | 337 | 6066 | 0.018528 | 0.0010293 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | Unknown Cause - Recloser RC 17 L/O. No flags. Not patrolled. Reclosed after no reports | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 18 | 15 | 5055 | 0.01544 | 0.0010293 | 2014-04-21 | C | 0.01544 | 0.0010293 | 2015 | 2014-04-21 | C | 337 | 0.01544 | 0.0010293
1 | 140242 | 2014-04-17 09:10 | 2014-04-17 12:55 | 225 | 14 | 1806 | 0.0055163 | 4.2762e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91540 - Emergency shutdown to remove tree in lines. Isolate from S174 to make break at 838131 to keep 5 TX on and only 3 off, make break close S174 drop lines from pole 838134 to remove trees, isolate at S174 to return break at pole 838131 to rest | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 129 | 126 | 1764 | 0.005388 | 4.2762e-05 | 2014-04-17 | B | 0.002694 | 2.1381e-05 | 2015 | 2014-04-17 | B | 14 | 0.005388 | 4.2762e-05
1 | 140243 | 2014-04-17 21:56 | 2014-04-18 09:43 | 707 | 425 | 171717 | 0.5245 | 0.0012981 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | JUMPER | No Power - Regulator 9220 tripped - Fault patrolled and found jumper off at Transformer TFD4-020. Pole #217058. Trees located at Pole 384144. | F2/F4 | MALEME ST | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 404.04 | 401.04 | 170442 | 0.5206 | 0.0012981 | 2014-04-17 | C | 0.5206 | 0.0012981 | 2015 | 2014-04-17 | C | 425 | 0.5206 | 0.0012981
1 | 140244 | 2014-04-17 13:47 | 2014-04-17 13:56 | 9 | 295 | 2538 | 0.0077521 | 0.00090105 | No Power | 33000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - Te Matai 33kV CB 1102 (Te Puke B) & CB1122 (Te Puke C) tripped causing Loss of supply to Pongakawa & Atuaroa Substations. CB1102 restored successfully at 11:18 with no loss of supply to Te Puke Sub. Investigations reveal tree bark blown across 33 | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 8.6034 | 5.6034 | 1653 | 0.005049 | 0.00090105 | 2014-04-17 | C | 0.005049 | 0.00090105 | 2015 | 2014-04-17 | C | 295 | 0.005049 | 0.00090105
1 | 140245 | 2014-04-17 11:15 | 2014-04-17 15:44 | 269 | 1094 | 83350 | 0.25459 | 0.0033415 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Recloser RP14 Tripped L/O. A short time later CB1 Tripped L/O. Investigations located Tree thru lines at Pole V0685. Isolated past ABS 298 & restored supply to CB1 & RP14 up to ABS 298. Tree cleared, lines repaired, supply restored. Note: Protect | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 76.1883 | 73.1883 | 80068 | 0.24456 | 0.0033415 | 2014-04-17 | C | 0.24456 | 0.0033415 | 2015 | 2014-04-17 | C | 1094 | 0.24456 | 0.0033415
1 | 140246 | 2014-04-17 12:47 | 2014-04-17 15:46 | 179 | 471 | 58479 | 0.17862 | 0.0014386 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - Te Puke CB 8. Recloser 9502 tripped. NOC disabled both. CB8 and Recloser 9502 closed and enabled. Ted Glasgow attended. | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 124.1592 | 121.1592 | 57066 | 0.1743 | 0.0014386 | 2014-04-17 | C | 0.1743 | 0.0014386 | 2015 | 2014-04-17 | C | 471 | 0.1743 | 0.0014386
1 | 140248 | 2014-04-17 14:18 | 2014-04-17 18:32 | 254 | 490 | 44370 | 0.13552 | 0.0014967 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power - Baird Rd CB3 tripped. Patrol found pole and lines needing replacement. | F3/F4 | KAURI ST | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 90.551 | 87.551 | 42900 | 0.13103 | 0.0014967 | 2014-04-17 | C | 0.13103 | 0.0014967 | 2015 | 2014-04-17 | C | 490 | 0.13103 | 0.0014967
1 | 140249 | 2014-04-17 09:50 | 2014-04-17 14:35 | 285 | 303 | 84873 | 0.25924 | 0.00092549 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power - Whitianga CB3. 9495/1 opened. Broken pole and xarms replaced. Steve Johnson and Shane Walker attended. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 280.1089 | 277.1089 | 83964 | 0.25646 | 0.00092549 | 2014-04-17 | C | 0.25646 | 0.00092549 | 2015 | 2014-04-17 | C | 303 | 0.25646 | 0.00092549
1 | 140250 | 2014-04-17 16:30 | 2014-04-17 22:00 | 330 | 711 | 137700 | 0.42059 | 0.0021717 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Recloser 9226 tripped. L/O. Fault unknown. Adverse Weather/Extreme Wind. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 193.6709 | 190.6709 | 135567 | 0.41408 | 0.0021717 | 2014-04-17 | C | 0.41408 | 0.0021717 | 2015 | 2014-04-17 | C | 711 | 0.41408 | 0.0021717
1 | 140252 | 2014-04-17 18:00 | 2014-04-17 19:00 | 60 | 45 | 1776 | 0.0054247 | 0.00013745 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Recloser C218 Tripped - Patrolled - No Fault Located. Adverse Weather/Extreme Wind. Ben Taylor Attended. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 39.4667 | 36.4667 | 1641 | 0.0050123 | 0.00013745 | 2014-04-17 | C | 0.0050123 | 0.00013745 | 2015 | 2014-04-17 | C | 45 | 0.0050123 | 0.00013745
1 | 140253 | 2014-04-17 14:07 | 2014-04-18 10:32 | 1225 | 94 | 55472 | 0.16943 | 0.00028712 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | UNKNOWN | No Power - CB N21 Tripped. Line Patrolled - Lines Down Found At Mangamako Road. Temporary Line Break at Pole Number P10122. | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 590.1277 | 587.1277 | 55190 | 0.16857 | 0.00028712 | 2014-04-17 | C | 0.16857 | 0.00028712 | 2015 | 2014-04-17 | C | 94 | 0.16857 | 0.00028712
1 | 140254 | 2014-04-17 11:03 | 2014-04-17 13:31 | 148 | 1 | 148 | 0.00045205 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | FUSE | Wind - Reports received of No Power Rangitanuku Rd during severe winds. Investigations located blown HT fuses at FP983. 2x 5A Fuses replaced, supply restored. Suspect line clash during storm event. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 148 | 145 | 145 | 0.00044289 | 3.0544e-06 | 2014-04-17 | C | 0.00044289 | 3.054e-06 | 2015 | 2014-04-17 | C | 1 | 0.00044289 | 3.0544e-06
1 | 140256 | 2014-04-17 11:58 | 2014-04-18 15:34 | 1656 | 213 | 122789 | 0.37505 | 0.00065059 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Wind - Recloser S6031 tripped, no flags. Feeder sectionalised and multiple line down faults found. Lines isolated between ABS SF6-009 & ABS S6011 with backfeed at ABS SF6-039. Also isolated past Fuses SF6-008. Faults repair and relivened OK. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 576.4742 | 573.4742 | 122150 | 0.3731 | 0.00065059 | 2014-04-17 | C | 0.3731 | 0.00065059 | 2015 | 2014-04-17 | C | 213 | 0.3731 | 0.00065059
1 | 140257 | 2014-04-17 14:27 | 2014-04-17 18:00 | 213 | 205 | 14278 | 0.043611 | 0.00062616 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - CB7 Tripped on E/F. Line Patrolled. Lines down due to tree. Adverse Weather/Extreme Wind. Kevin Henderson attended. 2 Phases rehung/4 Sleeves. NDR to follow. | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 69.6488 | 66.6488 | 13663 | 0.041733 | 0.00062616 | 2014-04-17 | C | 0.041733 | 0.00062616 | 2015 | 2014-04-17 | C | 205 | 0.041733 | 0.00062616
1 | 140258 | 2014-04-17 12:22 | 2014-04-17 15:00 | 158 | 1031 | 32824 | 0.10026 | 0.0031491 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | UNKNOWN | No Power - CB1022 Tripped. E/F. Line patrolled. Tree through line at ABS2682 Adverse Weather/Extreme Wind. DNO assigned. NDR to Follow. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 31.8371 | 28.8371 | 29731 | 0.090811 | 0.0031491 | 2014-04-17 | C | 0.090811 | 0.0031491 | 2015 | 2014-04-17 | C | 1031 | 0.090811 | 0.0031491
1 | 140259 | 2014-04-17 11:45 | 2014-04-17 13:22 | 97 | 281 | 4889 | 0.014933 | 0.00085829 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Recloser 9122/2 Tripped. Line Patrolled - Lines down. Repaired. Adverse Weather/Extreme Wind. Attended by John Tamarapu. | F4 | HOE-PATETONGA | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 17.3986 | 14.3986 | 4046 | 0.012358 | 0.00085829 | 2014-04-17 | C | 0.012358 | 0.00085829 | 2015 | 2014-04-17 | C | 281 | 0.012358 | 0.00085829
1 | 140260 | 2014-04-17 03:00 | 2014-04-17 06:24 | 204 | 536 | 92356 | 0.28209 | 0.0016372 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | No Power - CB9655/3 Tripped. Flags O/C, E/F, L/O. Line Patrolled - Cables Tested. Cable Fault Located between 9682/1 and 9630/3. Adverse Weather/Extreme Wind. Attended by Lubec Parata and Kim Lambert. | F3 | PAUANUI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 172.306 | 169.306 | 90748 | 0.27718 | 0.0016372 | 2014-04-17 | C | 0.27718 | 0.0016372 | 2015 | 2014-04-17 | C | 536 | 0.27718 | 0.0016372
1 | 140261 | 2014-04-17 18:10 | 2014-04-17 18:48 | 38 | 3 | 114 | 0.0003482 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Replace Transfomer C5372. Own AP Issued. Adverse Weather/Extreme Wind. | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 38 | 35 | 105 | 0.00032071 | 9.1633e-06 | 2014-04-17 | C | 0.00032071 | 9.163e-06 | 2015 | 2014-04-17 | C | 3 | 0.00032071 | 9.1633e-06
1 | 140262 | 2014-04-17 14:10 | 2014-04-17 15:20 | 70 | 37 | 2590 | 0.007911 | 0.00011301 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Recloser I07 Tripped - Circuit Breaker CB107 Auto Reclosed and Tripped. Line Patrolled and trees located through line. Temporary Line Break at Pole 785279 (TX 709). Adverse Weather/Extreme Wind. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 2479 | 0.0075719 | 0.00011301 | 2014-04-17 | C | 0.0075719 | 0.00011301 | 2015 | 2014-04-17 | C | 37 | 0.0075719 | 0.00011301
1 | 140264 | 2014-04-17 08:56 | 2014-04-18 13:50 | 1734 | 413 | 152457 | 0.46567 | 0.0012615 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Auto Recloser S6029 Tripped, L/O during severe storm event causing multiple feeder faults. 1/ Line patrol located lines down at pole 227563 Old Coach Rd. 2/ Recloser 9549 Tripped due to Tree thru lines Pukehina Parade Pole 385567 when Sub re-live | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 369.1453 | 366.1453 | 151218 | 0.46188 | 0.0012615 | 2014-04-17 | C | 0.46188 | 0.0012615 | 2015 | 2014-04-17 | C | 413 | 0.46188 | 0.0012615
1 | 140265 | 2014-04-17 11:13 | 2014-04-17 15:54 | 281 | 2602 | 726249 | 2.2183 | 0.0079476 | No Power | 33000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Te Matai 33kV CB 1102 (Te Puke B) & CB1122 (Te Puke C) tripped causing Loss of supply to Pongakawa & Atuaroa Substations. CB1102 restored successfully at 11:18 with no loss of supply to Te Puke Sub. Investigations reveal tree bark blown across 33 | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 279.1118 | 276.1118 | 718443 | 2.1944 | 0.0079476 | 2014-04-17 | C | 2.1944 | 0.0079476 | 2015 | 2014-04-17 | C | 2602 | 2.1944 | 0.0079476
1 | 140266 | 2014-04-17 07:54 | 2014-04-17 12:01 | 247 | 134 | 14942 | 0.045639 | 0.00040929 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | No Power - Recloser RP10 Tripped during severe wind storm event. Line patrols located Line Down past fuses SF5-013. Isolated at fuses, line repaired, supply restored. Dave Ngatai Attended. Note: Atuaroa Sub LOS from 11:13 to 11:52 due to subtrans faults | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 111.5075 | 108.5075 | 14540 | 0.044411 | 0.00040929 | 2014-04-17 | C | 0.044411 | 0.00040929 | 2015 | 2014-04-17 | C | 134 | 0.044411 | 0.00040929
1 | 140267 | 2014-04-17 11:13 | 2014-04-17 11:55 | 42 | 1083 | 42748 | 0.13057 | 0.0033079 | No Power | 33000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Te Matai 33kV CB 1102 (Te Puke B) & CB1122 (Te Puke C) tripped causing Loss of supply to Pongakawa & Atuaroa Substations. CB1102 restored successfully at 11:18 with no loss of supply to Te Puke Sub. Investigations reveal tree bark blown across 33 | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 39.4718 | 36.4718 | 39499 | 0.12065 | 0.0033079 | 2014-04-17 | C | 0.12065 | 0.0033079 | 2015 | 2014-04-17 | C | 1083 | 0.12065 | 0.0033079
1 | 140268 | 2014-04-17 21:54 | 2014-04-18 13:31 | 937 | 269 | 38083 | 0.11632 | 0.00082164 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - Recloser RS 10002/2 Tripped L/O during severe storm event. Isolated between ABS F53 & Recloser F48 & left off over night due to severe wind conditions. Update 18/4 - Line partrol located floating conductor at pole P13827, binder repl | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 141.5725 | 138.5725 | 37276 | 0.11386 | 0.00082164 | 2014-04-17 | C | 0.11386 | 0.00082164 | 2015 | 2014-04-17 | C | 269 | 0.11386 | 0.00082164
1 | 140269 | 2014-04-22 10:08 | 2014-04-22 11:25 | 77 | 2 | 154 | 0.00047038 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Found transformer TC3-065 badly leaking oil. Isolated at fuses and replaced. relivened Own SIS & AP | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 77 | 74 | 148 | 0.00045205 | 6.1088e-06 | 2014-04-22 | C | 0.00045205 | 6.109e-06 | 2015 | 2014-04-22 | C | 2 | 0.00045205 | 6.1088e-06
1 | 140271 | 2014-04-17 16:37 | 2014-04-18 10:22 | 1065 | 344 | 120790 | 0.36894 | 0.0010507 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - Turitea 33kV CB Z226, Keith St 33kV CB Z200, Kelvin Grove 33kV CB W40 & Tureatea 11kV Recloser RS10050/2 Tripped during severe storm event. 33kV CB's successfully re-energised, no fault found. Fault Investigations on Aokautere feeder | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 351.1337 | 348.1337 | 119758 | 0.36579 | 0.0010507 | 2014-04-17 | C | 0.36579 | 0.0010507 | 2015 | 2014-04-17 | C | 344 | 0.36579 | 0.0010507
1 | 140272 | 2014-04-17 10:57 | 2014-04-17 11:51 | 54 | 35 | 1890 | 0.0057729 | 0.0001069 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | Defective Component - Replace broken pole787878 that was caused by the storm on 17/04/14, line was isolated at ABS's 129 and 1080, broken pole was temporary held up as digging equipment was needed to dig the hole to replace the pole. Outage date adjusted | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 1785 | 0.0054521 | 0.0001069 | 2014-04-17 | C | 0.0054521 | 0.0001069 | 2015 | 2014-04-17 | C | 35 | 0.0054521 | 0.0001069
1 | 140273 | 2014-04-17 10:52 | 2014-04-18 13:09 | 1577 | 69 | 63384 | 0.1936 | 0.00021076 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Recloser Tripped L/O, A&B phase O/C. Investigations reveal large tree thru lines. Isolated from Fuses 920 & left off over night while tree cutters remove tree. Update 18/4 - Tree cleared, lines repaired, supply restored. Note: Invalid pole number | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 918.6087 | 915.6087 | 63177 | 0.19297 | 0.00021076 | 2014-04-17 | C | 0.19297 | 0.00021075 | 2015 | 2014-04-17 | C | 69 | 0.19297 | 0.00021076
1 | 140274 | 2014-04-22 10:54 | 2014-04-22 12:40 | 106 | 1 | 106 | 0.00032377 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component -Found transformer TE4-135 faulty, Isolated at fuses SE4-033. Replaced trany & relivened | F3/F4 | GREEN PARK | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 106 | 103 | 103 | 0.00031461 | 3.0544e-06 | 2014-04-22 | C | 0.00031461 | 3.054e-06 | 2015 | 2014-04-22 | C | 1 | 0.00031461 | 3.0544e-06
1 | 140275 | 2014-04-17 20:30 | 2014-04-18 09:54 | 804 | 289 | 106631 | 0.3257 | 0.00088273 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - CBC945 Tripped, L/O. Sectionalising proves fault past Sectionaliser 421 & left off over night due to severe wind conditions. Update 18/4 - Line patrols during daylight located HT lines twisted together by a fallen pine cone branch. Cleared branch | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 368.9654 | 365.9654 | 105764 | 0.32305 | 0.00088273 | 2014-04-17 | C | 0.32305 | 0.00088273 | 2015 | 2014-04-17 | C | 289 | 0.32305 | 0.00088273
1 | 140276 | 2014-04-17 15:52 | 2014-04-17 16:40 | 48 | 5 | 240 | 0.00073306 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Reports received of arcing at head of pole feeding Rimu production facility. Isolated at fuses 6745 to make repairs to jumper at head of pole after making arangements with Rimu. Jumper repaired, supply restored. | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 48 | 45 | 225 | 0.00068725 | 1.5272e-05 | 2014-04-17 | C | 0.00068724 | 1.5272e-05 | 2015 | 2014-04-17 | C | 5 | 0.00068725 | 1.5272e-05
1 | 140277 | 2014-04-19 02:07 | 2014-04-19 06:33 | 266 | 213 | 42910 | 0.13107 | 0.00065059 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - CB C638 tripped on E/F, A phase O/C. Conductor found down at pole 916562. Line rehung. Ben Taylor and James Matthews attended. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 201.4554 | 198.4554 | 42271 | 0.12911 | 0.00065059 | 2014-04-19 | C | 0.12911 | 0.00065059 | 2015 | 2014-04-19 | C | 213 | 0.12911 | 0.00065059
1 | 140278 | 2014-04-17 11:40 | 2014-04-17 14:30 | 170 | 38 | 6460 | 0.019732 | 0.00011607 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component - Line was isolated at Fuses V68 to replace a damaged transformer T9/214 that was hit by lightning on the 17/04/14, the transformer had a generator connected to it which was removed after the transformer was replaced. Shazil Khan atten | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 170 | 167 | 6346 | 0.019383 | 0.00011607 | 2014-04-17 | C | 0.019383 | 0.00011607 | 2015 | 2014-04-17 | C | 38 | 0.019383 | 0.00011607
1 | 140279 | 2014-04-17 14:28 | 2014-04-17 20:16 | 348 | 1090 | 336105 | 1.0266 | 0.0033293 | No Power | 33000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - Te Matai 33kV CB 1102 (Te Puke B) & CB1122 (Te Puke C) tripped causing Loss of supply to Pongakawa & Atuaroa Substations. CB1102 restored successfully at 11:18 with no loss of supply to Te Puke Sub. Investigations reveal tree bark blown across 33 | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 308.3532 | 305.3532 | 332835 | 1.0166 | 0.0033293 | 2014-04-17 | C | 1.0166 | 0.0033293 | 2015 | 2014-04-17 | C | 1090 | 1.0166 | 0.0033293
1 | 140280 | 2014-04-17 21:39 | 2014-04-18 10:02 | 743 | 35 | 26005 | 0.07943 | 0.0001069 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Reports received of no power at Otahome Road during severe storm event. Update 18/4 - Investigations reveal Sectionaliser C1019 Tripped. Line patrol located broken Xarm. Isolated from fuses 7889. No comms so faultman self issued perm | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 743 | 740 | 25900 | 0.07911 | 0.0001069 | 2014-04-17 | C | 0.07911 | 0.0001069 | 2015 | 2014-04-17 | C | 35 | 0.07911 | 0.0001069
1 | 140281 | 2014-04-17 15:51 | 2014-04-18 15:38 | 1427 | 673 | 886881 | 2.7089 | 0.0020556 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Recloser RS9513 Tripped during severe storm event following re-energising of Pongakawa Substation. Line patrols & sectionalising located Tree across lines at pole 218444 & blown jumper at pole 218414. Tree cleared, lines restored, jumper repaired, | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 1317.8024 | 1314.8024 | 884862 | 2.7027 | 0.0020556 | 2014-04-17 | C | 2.7027 | 0.0020556 | 2015 | 2014-04-17 | C | 673 | 2.7027 | 0.0020556
1 | 140282 | 2014-04-17 04:59 | 2014-04-17 07:42 | 163 | 147 | 7604 | 0.023226 | 0.000449 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Recloser RC 25 Tripped, O/C. Feeder sectionalised and outage isolated past ABS IC1099 to repair lines down. Lines repaired & relivened OK. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 51.7279 | 48.7279 | 7163 | 0.021879 | 0.000449 | 2014-04-17 | C | 0.021879 | 0.000449 | 2015 | 2014-04-17 | C | 147 | 0.021879 | 0.000449
1 | 140284 | 2014-04-17 12:20 | 2014-04-17 16:50 | 270 | 257 | 21872 | 0.066806 | 0.00078499 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - CB PU4 tripped, no flags. Feeder sectionalised and Mark Patterson patrolled lines. Outage required between ABS PU410 & PU413 to rebind in floating conductors. Backfeed from ABS PU203. Conductors repaired & relivened OK | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 85.1051 | 82.1051 | 21101 | 0.064451 | 0.00078499 | 2014-04-17 | C | 0.064451 | 0.00078499 | 2015 | 2014-04-17 | C | 257 | 0.064451 | 0.00078499
1 | 140285 | 2014-04-22 10:00 | 2014-04-22 14:30 | 270 | 31 | 8370 | 0.025566 | 9.4687e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/90986 - Replace 11kV Fused ABS 5295 for new Fuses 5295. 4478 Taranaki ABS renewal to remove old ABS 5295 and replace old 11kV fuses w/ new chance fuses on TX 3515T so we need to open ABS 5295 to do job safely and then take down old ABS and fuses a | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 270 | 267 | 8277 | 0.025281 | 9.4687e-05 | 2014-04-22 | B | 0.012641 | 4.7344e-05 | 2015 | 2014-04-22 | B | 31 | 0.025281 | 9.4687e-05
1 | 140286 | 2014-04-17 09:30 | 2014-04-17 11:59 | 149 | 9 | 1341 | 0.004096 | 2.749e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90749 - Install new double top off arm on existing11kV network pole 716312 fitted w/ new Fuses 8989 for supply to new 11kV spur line and new 100kVA 5614E to be livened same day. Isolation points: 11kV ABS 6685, ABS TA 823, ABS TA 803. Was the 17 | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 149 | 146 | 1314 | 0.0040135 | 2.749e-05 | 2014-04-17 | B | 0.0020068 | 1.3745e-05 | 2015 | 2014-04-17 | B | 9 | 0.0040135 | 2.749e-05
1 | 140287 | 2014-04-22 10:15 | 2014-04-22 14:47 | 272 | 3 | 816 | 0.0024924 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90044 - Replace 11kV pole, Xarms and hardware from pole E0270 to end of spur line pole E12653. Isolation points: 11kV Fuse FP1558 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 272 | 269 | 807 | 0.0024649 | 9.1633e-06 | 2014-04-22 | B | 0.0012325 | 4.582e-06 | 2015 | 2014-04-22 | B | 3 | 0.0024649 | 9.1633e-06
1 | 140289 | 2014-04-22 15:13 | 2014-04-22 15:30 | 17 | 55 | 935 | 0.0028559 | 0.00016799 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Emergency Isolation to replace x-arm center bolt at Pole EO906. Isolation at ABS 1083. No Backfeed available. Ian Smart & Iro Ezekiela Faultmen | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 770 | 0.0023519 | 0.00016799 | 2014-04-22 | C | 0.0023519 | 0.00016799 | 2015 | 2014-04-22 | C | 55 | 0.0023519 | 0.00016799
1 | 140293 | 2014-04-22 21:54 | 2014-04-23 00:10 | 136 | 227 | 18074 | 0.055206 | 0.00069335 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum at 21:54, Putaruru Sub, CB 5 Waotu Feeder, Recloser 9636 Tripped, PROT Trip, L/O. Faultman Dispatched & Investigation Began. Feeder Sectionalised. Found a Possum on the Lines at Pole M0800. Removed with Hot Stick. All Power Restored on C | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 79.6211 | 76.6211 | 17393 | 0.053126 | 0.00069335 | 2014-04-22 | C | 0.053126 | 0.00069335 | 2015 | 2014-04-22 | C | 227 | 0.053126 | 0.00069335
1 | 140295 | 2014-04-17 09:04 | 2014-04-17 21:59 | 775 | 5 | 3875 | 0.011836 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Fuses 2385 tripped due to a tree through the lines brought down in storm. Lines made safe to be repaired when resources available. Tree removed and lines repaired, relivened OK. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 775 | 772 | 3860 | 0.01179 | 1.5272e-05 | 2014-04-17 | C | 0.01179 | 1.5272e-05 | 2015 | 2014-04-17 | C | 5 | 0.01179 | 1.5272e-05
1 | 140296 | 2014-04-17 14:15 | 2014-04-17 18:09 | 234 | 294 | 34266 | 0.10466 | 0.000898 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT WIND (LINE CLASH) | CONDUCTOR | Unknown Cause - CB 17 tripped. Outage caused for all customers connected to TIR sub. Chris Brown performed sub check, OK. Service restored to sub by NOC except for Okoroire feeder. Okoroire feeder CB showed trip flag but did not trip. Feeder sectionalised | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 116.551 | 113.551 | 33384 | 0.10197 | 0.000898 | 2014-04-17 | C | 0.10197 | 0.000898 | 2015 | 2014-04-17 | C | 294 | 0.10197 | 0.000898
1 | 140297 | 2014-04-17 16:55 | 2014-04-18 12:44 | 1189 | 176 | 83715 | 0.2557 | 0.00053758 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Defective Component - Recloser 7417 tripped on E/F o/c. Feeder sectionalised and lines down found past Fuses 7993. Lines repaired, relivened OK. Trees on line. Pole 832173 replaced and crossarm on 832175. NDR 37685. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 475.6534 | 472.6534 | 83187 | 0.25409 | 0.00053758 | 2014-04-17 | C | 0.25409 | 0.00053758 | 2015 | 2014-04-17 | C | 176 | 0.25409 | 0.00053758
1 | 140298 | 2014-04-17 14:51 | 2014-04-17 15:55 | 64 | 22 | 1408 | 0.0043006 | 6.7197e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Outage between CB NG2, ABS NG245 & NG240 to replace jumper on ABS NG202 that is causing part power and low voltage faults. Jumper replaced, relivened OK. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 1342 | 0.004099 | 6.7197e-05 | 2014-04-17 | C | 0.004099 | 6.7197e-05 | 2015 | 2014-04-17 | C | 22 | 0.004099 | 6.7197e-05
1 | 140299 | 2014-04-18 17:56 | 2014-04-19 10:59 | 1023 | 492 | 103952 | 0.31751 | 0.0015028 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - CB C850 Tripped L/O. Feeder sectionalised and isolated between S225 and S152 to remove trees. Backfeed via TIN C935 and left off overnigth. Update 19/4 - Trees removed from line, lines repaired, supply restored. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 211.2846 | 208.2846 | 102476 | 0.31301 | 0.0015028 | 2014-04-18 | C | 0.31301 | 0.0015028 | 2015 | 2014-04-18 | C | 492 | 0.31301 | 0.0015028
1 | 140300 | 2014-04-17 09:00 | 2014-04-18 11:34 | 1594 | 182 | 104931 | 0.3205 | 0.00055591 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB D21 tripped, no flags. Feeder sectionalised and multiple faults found. Trees found through lines past Recloser 6413 & between ABS 5705 & ABS 4893, from storm. Past Recloser 6413 trees removed, lines repaired & relivened OK. Between ABS 5705 & A | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 576.544 | 573.544 | 104385 | 0.31884 | 0.00055591 | 2014-04-17 | C | 0.31884 | 0.0005559 | 2015 | 2014-04-17 | C | 182 | 0.31884 | 0.00055591
1 | 140302 | 2014-04-18 11:25 | 2014-04-18 13:05 | 100 | 10 | 1000 | 0.0030544 | 3.0544e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | Turitea CB4. H47 opened and tagged. Repairs made to floating conductor. 3 insulators and 1 H/T binder. Chris Naylor attended. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 970 | 0.0029628 | 3.0544e-05 | 2014-04-18 | C | 0.0029628 | 3.0544e-05 | 2015 | 2014-04-18 | C | 10 | 0.0029628 | 3.0544e-05
1 | 140303 | 2014-04-18 15:22 | 2014-04-18 17:42 | 140 | 25 | 3500 | 0.01069 | 7.6361e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | Isolation made to replace pole 785273 due to storm. Chris Winter attended. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 140 | 137 | 3425 | 0.010461 | 7.6361e-05 | 2014-04-18 | C | 0.010461 | 7.6361e-05 | 2015 | 2014-04-18 | C | 25 | 0.010461 | 7.6361e-05
1 | 140304 | 2014-04-18 10:52 | 2014-04-18 12:53 | 121 | 35 | 4235 | 0.012935 | 0.0001069 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | SWITCHGEAR - UG | No Power. Blown fuses at Switch Gear SA2-048. Adverse Weather/Extreme Wind. Cable Tested. Attended by: Brian Allison. | F3 | ATHENREE | WAIHI BEACH SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 121 | 118 | 4130 | 0.012615 | 0.0001069 | 2014-04-18 | C | 0.012615 | 0.0001069 | 2015 | 2014-04-18 | C | 35 | 0.012615 | 0.0001069
1 | 140305 | 2014-04-18 13:07 | 2014-04-18 15:07 | 120 | 625 | 59409 | 0.18146 | 0.001909 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Roberts Ave CB4 tripped. Investigation found cable fault. 11kV ABS 4210 opened and tagged. Recloser 083 opened. Backfeed put in at OKN4400/3. 11kV ABS 1054 and RC 4616/2 opened and tagged. WGE10 1487 closed and ABS 2627 opened. James Prime attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 95.0544 | 92.0544 | 57534 | 0.17573 | 0.001909 | 2014-04-18 | C | 0.17573 | 0.001909 | 2015 | 2014-04-18 | C | 625 | 0.17573 | 0.001909
1 | 140307 | 2014-04-18 16:54 | 2014-04-18 18:41 | 107 | 23 | 2461 | 0.0075169 | 7.0252e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Lines down beyond Fuse E29. Adverse Weather/Extreme Wind. | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107 | 104 | 2392 | 0.0073062 | 7.0252e-05 | 2014-04-18 | C | 0.0073062 | 7.0252e-05 | 2015 | 2014-04-18 | C | 23 | 0.0073062 | 7.0252e-05
1 | 140308 | 2014-04-18 14:36 | 2014-04-18 18:35 | 239 | 3 | 717 | 0.00219 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | No Power. Pole 810796 Down. (Materials used: 1 Pole & 1 H/T Crossarm). Isolated beyond Fuse 7352. Adverse Weather/Extreme Wind. Ben Taylor Attended. | F4 | OTARAIA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 239 | 236 | 708 | 0.0021625 | 9.1633e-06 | 2014-04-18 | C | 0.0021625 | 9.163e-06 | 2015 | 2014-04-18 | C | 3 | 0.0021625 | 9.1633e-06
1 | 140309 | 2014-04-18 16:56 | 2014-04-18 17:32 | 36 | 160 | 5760 | 0.017593 | 0.00048871 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Te Ore Ore C830 ABS S78 check open and tagged, S156 closed, S151 open and tagged. CB C830 opened (NOC) . Re bolt H/T Xarm back to pole. Line re-energised. Nev Pope attended. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 36 | 33 | 5280 | 0.016127 | 0.00048871 | 2014-04-18 | C | 0.016127 | 0.00048871 | 2015 | 2014-04-18 | C | 160 | 0.016127 | 0.00048871
1 | 140310 | 2014-04-18 13:57 | 2014-04-18 15:24 | 87 | 19 | 1653 | 0.005049 | 5.8034e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Down at pole number 796607. Isolated beyond Fuse 450. Materials used: 5m of conductor and 1 phase. Phil Osborne attended. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 87 | 84 | 1596 | 0.0048749 | 5.8034e-05 | 2014-04-18 | C | 0.0048749 | 5.8034e-05 | 2015 | 2014-04-18 | C | 19 | 0.0048749 | 5.8034e-05
1 | 140311 | 2014-04-17 00:17 | 2014-04-18 15:32 | 2355 | 53 | 80535 | 0.24599 | 0.00016188 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power. Line Patrolled. Backfeed supplied via TIN C935. Pole 839756/ TX T76 earths applied and tagged. Adverse Weather/Extreme Wind. NDR37683. | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1519.5283 | 1516.5283 | 80376 | 0.2455 | 0.00016188 | 2014-04-17 | C | 0.2455 | 0.00016188 | 2015 | 2014-04-17 | C | 53 | 0.2455 | 0.00016188
1 | 140312 | 2014-04-18 11:05 | 2014-04-18 16:41 | 336 | 66 | 21150 | 0.064601 | 0.00020159 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | No Power. Recloser 266 Tripped. Lines Down at Pole 787477. Isolated beyond Fuse 2555. Jeremy Hill attended. Materials Used: 2 metres of conductor. Adverse Weather/Extreme Wind. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 320.4545 | 317.4545 | 20952 | 0.063996 | 0.00020159 | 2014-04-18 | C | 0.063996 | 0.00020159 | 2015 | 2014-04-18 | C | 66 | 0.063996 | 0.00020159
1 | 140314 | 2014-04-17 10:02 | 2014-04-18 15:02 | 1740 | 385 | 205154 | 0.62663 | 0.001176 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - CB 8 tripped B & C Phase E/F. Feeder sectionalised and lines isolated past ABS 451, ABS 485 & Fuses 8459 with multiple faults. Feeder restored with isolated area to be restored as resources available. Lines in isolated areas repaired | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 532.8675 | 529.8675 | 203999 | 0.6231 | 0.001176 | 2014-04-17 | C | 0.6231 | 0.001176 | 2015 | 2014-04-17 | C | 385 | 0.6231 | 0.001176
1 | 140315 | 2014-04-18 12:47 | 2014-04-18 13:40 | 53 | 3 | 159 | 0.00048565 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | No Power. Line Patrolled. Cross Arm on Pole 709867 Replaced. Adverse Weather/Extreme Wind. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 150 | 0.00045816 | 9.1633e-06 | 2014-04-18 | C | 0.00045816 | 9.163e-06 | 2015 | 2014-04-18 | C | 3 | 0.00045816 | 9.1633e-06
1 | 140316 | 2014-04-18 16:10 | 2014-04-18 16:51 | 41 | 3 | 123 | 0.00037569 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | SURGE ARRESTOR | No Power. Line Patrolled. Repair of Surge Arrestor Jumper at Pole Number 712206. Isolated at Fuse NG290. Adverse Weather/Extreme Wind. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 41 | 38 | 114 | 0.0003482 | 9.1633e-06 | 2014-04-18 | C | 0.0003482 | 9.163e-06 | 2015 | 2014-04-18 | C | 3 | 0.0003482 | 9.1633e-06
1 | 140317 | 2014-04-17 16:30 | 2014-04-17 17:40 | 70 | 27 | 1293 | 0.0039494 | 8.2469e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Rata CB 1350. Fuses 757 blown. Line down found due to trees. Left isolated overnight. Trees removed. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 47.8889 | 44.8889 | 1212 | 0.003702 | 8.2469e-05 | 2014-04-17 | C | 0.003702 | 8.2469e-05 | 2015 | 2014-04-17 | C | 27 | 0.003702 | 8.2469e-05
1 | 140318 | 2014-04-18 13:59 | 2014-04-18 17:26 | 207 | 1 | 207 | 0.00063227 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Line patrolled. Lines down at pole number 221996. Adverse Weather/Extreme Wind. Isolated at Fuse SE6-238. Ted Glasglow attended. 2x Sleeves used. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 207 | 204 | 204 | 0.0006231 | 3.0544e-06 | 2014-04-18 | C | 0.0006231 | 3.054e-06 | 2015 | 2014-04-18 | C | 1 | 0.0006231 | 3.0544e-06
1 | 140320 | 2014-04-18 08:45 | 2014-04-18 09:52 | 67 | 1 | 67 | 0.00020465 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power. Blown Transformer TC6249. Transformer replaced. Adverse Weather/Extreme Wind. Dion Saunders attended. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 67 | 64 | 64 | 0.00019548 | 3.0544e-06 | 2014-04-18 | C | 0.00019548 | 3.054e-06 | 2015 | 2014-04-18 | C | 1 | 0.00019548 | 3.0544e-06
1 | 140321 | 2014-04-18 08:45 | 2014-04-18 09:02 | 17 | 7 | 119 | 0.00036348 | 2.1381e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Blown Transformer at TC1998. Transformer replaced. Adverse Weather/Extreme Wind. Dion Saunders attended. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 98 | 0.00029933 | 2.1381e-05 | 2014-04-18 | C | 0.00029933 | 2.1381e-05 | 2015 | 2014-04-18 | C | 7 | 0.00029933 | 2.1381e-05
1 | 140322 | 2014-04-18 11:10 | 2014-04-18 11:40 | 30 | 25 | 750 | 0.0022908 | 7.6361e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power. Line Patrolled. Rebolt Cross Arm at Pole 788157. Isolated at Fuse 175. Adverse Weather/Extreme Wind. Tony Sinclair Attended. | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 675 | 0.0020617 | 7.6361e-05 | 2014-04-18 | C | 0.0020617 | 7.6361e-05 | 2015 | 2014-04-18 | C | 25 | 0.0020617 | 7.6361e-05
1 | 140323 | 2014-04-18 09:32 | 2014-04-18 12:05 | 153 | 110 | 16830 | 0.051406 | 0.00033599 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | Line Isolated at ABS SE5-028 for Safety to Pull 33kV Lines. (Pole 230533). 33kV Lines Down - Adverse Weather/Extreme wind. Ted Glasgow Attended. | F1/F4 | TE PUKE QUARRY RD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 153 | 150 | 16500 | 0.050398 | 0.00033599 | 2014-04-18 | C | 0.050398 | 0.00033599 | 2015 | 2014-04-18 | C | 110 | 0.050398 | 0.00033599
1 | 140324 | 2014-04-17 10:44 | 2014-04-19 10:55 | 2891 | 96 | 174829 | 0.534 | 0.00029322 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | Defective Component - Taihape CB6. Recloser 4692/2 found open. Fuses 2954 open and tagged. Conductor repaired. Neville Ashton attended. No Power - Fuses 1063 open due to pole down. Replaced Pole 1 X Crossarm & 3 X H/T Insulators. Arvell Wallace Attende | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 1821.1354 | 1818.1354 | 174541 | 0.53312 | 0.00029322 | 2014-04-17 | C | 0.53312 | 0.00029322 | 2015 | 2014-04-17 | C | 96 | 0.53312 | 0.00029322
1 | 140325 | 2014-04-18 14:09 | 2014-04-18 14:54 | 45 | 39 | 1755 | 0.0053605 | 0.00011912 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE | No Power. Adverse Weather/Extreme wind. Line Patrolled. Isolated at Fuse 10068. 1 x DDO replaced at T4/178. Bruce Mehrtens attended. | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 1638 | 0.0050031 | 0.00011912 | 2014-04-18 | C | 0.0050031 | 0.00011912 | 2015 | 2014-04-18 | C | 39 | 0.0050031 | 0.00011912
1 | 140327 | 2014-04-17 18:21 | 2014-04-17 20:50 | 149 | 308 | 34628 | 0.10577 | 0.00094076 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT WIND (LINE CLASH) | CONDUCTOR | Unknown Cause - CB 8 tripped on E/F. Line patrolled, feeder sectionalised and restored with no fault found | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 112.4286 | 109.4286 | 33704 | 0.10295 | 0.00094076 | 2014-04-17 | C | 0.10295 | 0.00094076 | 2015 | 2014-04-17 | C | 308 | 0.10295 | 0.00094076
1 | 140328 | 2014-04-18 10:16 | 2014-04-18 11:50 | 94 | 295 | 26230 | 0.080118 | 0.00090105 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - CB 8 tripped on E/F. Brent Moratti attended & feeder sectionalised. Lines past Fuses 6462 isolated to repair lines. Lines repaired, relivened OK. | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 88.9153 | 85.9153 | 25345 | 0.077414 | 0.00090105 | 2014-04-18 | C | 0.077414 | 0.00090105 | 2015 | 2014-04-18 | C | 295 | 0.077414 | 0.00090105
1 | 140329 | 2014-04-23 09:47 | 2014-04-23 11:30 | 103 | 121 | 12463 | 0.038067 | 0.00036959 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | RECLOSER | Other/miscellaneous cause -Faultman found Recloser 2568 open, this recloser tripped on O/C while backfeeding a section of Pukepapa Sub CB 4 on outage 14/90867, ABS 709 was closed to restore the supply. Found out that this Recloser 2568 can only be used to | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 103 | 100 | 12100 | 0.036959 | 0.00036959 | 2014-04-23 | C | 0.036959 | 0.00036959 | 2015 | 2014-04-23 | C | 121 | 0.036959 | 0.00036959
1 | 140330 | 2014-04-16 13:40 | 2014-04-16 15:00 | 80 | 3 | 240 | 0.00073306 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | No Power -11kV transformer C5372 isolated for replacement after lightning damage (Attended by Brett Bensley) | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 231 | 0.00070557 | 9.1633e-06 | 2014-04-16 | C | 0.00070557 | 9.163e-06 | 2015 | 2014-04-16 | C | 3 | 0.00070557 | 9.1633e-06
1 | 140331 | 2014-04-23 09:01 | 2014-04-23 15:08 | 367 | 46 | 16882 | 0.051565 | 0.0001405 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90867 - Replace 37 double circuit Xarms from pole 800734 to pole 801733, part of the 33kV Xarm replacement job Pukepapa sub to Arahina sub. 33kV circuit above will be alive. Isolation points: CB3 Henderson, CB4 Turakina, ABS 1226, ABS 1368, ABS 26 | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 367 | 364 | 16744 | 0.051143 | 0.0001405 | 2014-04-23 | B | 0.025572 | 7.0252e-05 | 2015 | 2014-04-23 | B | 46 | 0.051143 | 0.0001405
1 | 140332 | 2014-04-23 11:35 | 2014-04-23 14:56 | 201 | 80 | 9414 | 0.028754 | 0.00024435 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Trees -Recloser C281/2 tripped on O/C B phase flags, received a call of a tree against the line, line was isolated at ABA S174, faultman found a tree contractorhad been cutting trees on Kaiwhata Road. Tree contractor informed faultman and showed him Close | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 117.675 | 114.675 | 9174 | 0.028021 | 0.00024435 | 2014-04-23 | C | 0.028021 | 0.00024435 | 2015 | 2014-04-23 | C | 80 | 0.028021 | 0.00024435
1 | 140334 | 2014-04-23 10:02 | 2014-04-23 12:38 | 156 | 5 | 780 | 0.0023825 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum Emergency switching to repair line down at pole N2250 & blown jumper at pole N1412. Isolation between ABS 547 & ABS 560 with back feed via ABS 1041. Line & jumper repaired, all service restored Don Watson attended. Materials 2 x H/V slee | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 156 | 153 | 765 | 0.0023366 | 1.5272e-05 | 2014-04-23 | C | 0.0023366 | 1.5272e-05 | 2015 | 2014-04-23 | C | 5 | 0.0023366 | 1.5272e-05
1 | 140335 | 2014-04-23 09:46 | 2014-04-23 14:12 | 266 | 546 | 62336 | 0.1904 | 0.0016677 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Accident - CB6 tripped O/C L/O. Report of tree cutters felling tree through 11kV lines at pole 13192 alos blowing jumper at pole WKP/WHI066. Isolations for lines down between ABS 252 & ABS 299 with back feed via ABS IC238. Isolations for blown jumper betw | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 114.1685 | 111.1685 | 60698 | 0.1854 | 0.0016677 | 2014-04-23 | C | 0.1854 | 0.0016677 | 2015 | 2014-04-23 | C | 546 | 0.1854 | 0.0016677
1 | 140336 | 2014-04-22 13:00 | 2014-04-22 13:47 | 47 | 19 | 893 | 0.0027276 | 5.8034e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | FUSE | SIN: 14/91446 - Upgrade 11kV fusing at fuses 5698 pole 740122, fuses 4979 pole 740148. Prior to new 11kV regulator installation (regulator 8996) East Rd Stratford. Isolation points:11kV fuses 5698, fuses 4979 | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 47 | 44 | 836 | 0.0025535 | 5.8034e-05 | 2014-04-22 | B | 0.0012767 | 2.9017e-05 | 2015 | 2014-04-22 | B | 19 | 0.0025535 | 5.8034e-05
1 | 140338 | 2014-04-23 09:16 | 2014-04-23 15:14 | 358 | 2 | 716 | 0.002187 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | RECLOSER | SIN: 14/89250 - 11kV Recloser maintenance and testing, Recloser 6943. Isolation points: 11kV ABS 6930. Opunaki Hydro CHEAL site. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 358 | 355 | 710 | 0.0021686 | 6.1088e-06 | 2014-04-23 | B | 0.0010843 | 3.054e-06 | 2015 | 2014-04-23 | B | 2 | 0.0021686 | 6.1088e-06
1 | 140339 | 2014-04-23 11:10 | 2014-04-23 11:48 | 38 | 1 | 38 | 0.00011607 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - Emergency Isolation to replace Stay Bolt No Pole Number on Pole. Lin e Feeds Transformer TC6278. Iro Ezekiela Faultman. Isolation at Fuses FC873 | F4 | OKOROIRE | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 38 | 35 | 35 | 0.0001069 | 3.0544e-06 | 2014-04-23 | C | 0.0001069 | 3.054e-06 | 2015 | 2014-04-23 | C | 1 | 0.0001069 | 3.0544e-06
1 | 140340 | 2014-04-17 09:39 | 2014-04-17 15:43 | 364 | 44 | 16016 | 0.04892 | 0.00013439 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Defective Component - Emergency Isolation to Clear Trees and re-connect fallen conductor. Isolation at Recloser 6413. Phil Webby - Faultman. Line was bought down in Easter Storm. Outage date adjusted to 'Cause and Effect' as a result of the MED storm on 1 | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 364 | 361 | 15884 | 0.048516 | 0.00013439 | 2014-04-17 | C | 0.048516 | 0.00013439 | 2015 | 2014-04-17 | C | 44 | 0.048516 | 0.00013439
1 | 140341 | 2014-04-23 17:18 | 2014-04-23 17:45 | 27 | 41 | 1107 | 0.0033812 | 0.00012523 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Trees - Unknown person fells tree, brushes 11kV line at pole V0496 blows 2 x fuses FC 4048 ( spur line ) Line patrolled checked Ok all service restored, Dean Brett attended Materials 2 x H/V fuses. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 984 | 0.0030056 | 0.00012523 | 2014-04-23 | C | 0.0030056 | 0.00012523 | 2015 | 2014-04-23 | C | 41 | 0.0030056 | 0.00012523
1 | 140342 | 2014-04-23 09:15 | 2014-04-23 15:00 | 345 | 8 | 2760 | 0.0084302 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91663 - Re-conductor. Isolation points: 11kV ABS 922 and Temp Links IP574 at pole M0315. New application due to work site reduced. Advertising 14/90457. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 2736 | 0.0083569 | 2.4435e-05 | 2014-04-23 | B | 0.0041785 | 1.2218e-05 | 2015 | 2014-04-23 | B | 8 | 0.0083569 | 2.4435e-05
1 | 140343 | 2014-04-23 09:15 | 2014-04-23 18:00 | 525 | 8 | 4200 | 0.012829 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/90457 - Re-conductor. Isolation points: ABS 922 and 908, Temp Links M1299 and M0315. This AP is now under SIN 91663 due to work site change. MR 22/04/2014 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 525 | 522 | 4176 | 0.012755 | 2.4435e-05 | 2014-04-23 | B | 0.0063776 | 1.2218e-05 | 2015 | 2014-04-23 | B | 8 | 0.012755 | 2.4435e-05
1 | 140346 | 2014-04-18 08:20 | 2014-04-18 08:25 | 5 | 123 | 615 | 0.0018785 | 0.00037569 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - CB I32 found tripped. No fault found. Closed. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 5 | 2 | 246 | 0.00075139 | 0.00037569 | 2014-04-18 | C | 0.00075139 | 0.00037569 | 2015 | 2014-04-18 | C | 123 | 0.00075139 | 0.00037569
1 | 140347 | 2014-04-17 11:10 | 2014-04-17 18:16 | 426 | 434 | 148135 | 0.45247 | 0.0013256 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Oakura CB8 tripped. Line patrolled and repairs made at pole 757753 and 757305. Neil Woodhead attended.During line patrol 11kV Crossarm on pole 758023 at 260 Denver road identified as broken to be replaced at a later date. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 341.3249 | 338.3249 | 146833 | 0.44849 | 0.0013256 | 2014-04-17 | C | 0.44849 | 0.0013256 | 2015 | 2014-04-17 | C | 434 | 0.44849 | 0.0013256
1 | 140348 | 2014-04-17 09:53 | 2014-04-17 10:44 | 51 | 24 | 3960 | 0.012096 | 7.3306e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91755 - Replace broken 11kV Xarms from the storm in emergency switching at pole 758023. Isolation points: 11kV ABS 407, ABS 252. Outage date adjusted to 'Cause and Effect' as a result of the MED storm on 17.04.14. (24.04.14). | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 165 | 162 | 3888 | 0.011876 | 7.3306e-05 | 2014-04-17 | B | 0.0059378 | 3.6653e-05 | 2015 | 2014-04-17 | B | 24 | 0.011876 | 7.3306e-05
1 | 140349 | 2014-04-18 05:44 | 2014-04-18 05:59 | 15 | 595 | 8925 | 0.027261 | 0.0018174 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - TP_Stratford CB 2762 Tripped on O/C and L/O causing LOS to Douglas Substation. Patrol found lines down at Douglas 33kV pole 737454. Line repaired and power restored. Huiroa and Stathmore backfed through Toko. | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 7140 | 0.021809 | 0.0018174 | 2014-04-18 | C | 0.021809 | 0.0018174 | 2015 | 2014-04-18 | C | 595 | 0.021809 | 0.0018174
1 | 140350 | 2014-04-24 10:00 | 2014-04-24 12:34 | 154 | 1 | 154 | 0.00047038 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90911 - To cut in LL gap at pole P30092 then replace TX structure and install new TX T9/144 at Glen Ora Rd. Isolation points: LL gap at pole P30092. Associated LLP 14/91449 & 14/91456 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 154 | 151 | 151 | 0.00046122 | 3.0544e-06 | 2014-04-24 | B | 0.00023061 | 1.527e-06 | 2015 | 2014-04-24 | B | 1 | 0.00046122 | 3.0544e-06
1 | 140351 | 2014-04-24 10:10 | 2014-04-24 12:50 | 160 | 4 | 640 | 0.0019548 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/91092 - Isolate 11kV Transformer TX 1838 to replace rotten LV Xarm on pole and connect LV cable on to o/h conductor. Isolation points: TC1838 NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP.Was on th | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 628 | 0.0019182 | 1.2218e-05 | 2014-04-24 | B | 0.00095909 | 6.109e-06 | 2015 | 2014-04-24 | B | 4 | 0.0019182 | 1.2218e-05
1 | 140353 | 2014-04-24 09:00 | 2014-04-24 14:55 | 355 | 25 | 8875 | 0.027108 | 7.6361e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89346 - AP to erect poles from 785333 through to 785239, change X arms. Isolation points: ABS 4620 Oneils Rd, 4621/2 Links, 4621/4, Links, 4621/1. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 355 | 352 | 8800 | 0.026879 | 7.6361e-05 | 2014-04-24 | B | 0.013439 | 3.818e-05 | 2015 | 2014-04-24 | B | 25 | 0.026879 | 7.6361e-05
1 | 140355 | 2014-04-24 13:10 | 2014-04-24 16:30 | 200 | 3 | 600 | 0.0018327 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Outage required on Transformer T2232 Fuses to enable a replacement to be fitted. (Faulty). | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 200 | 197 | 591 | 0.0018052 | 9.1633e-06 | 2014-04-24 | C | 0.0018052 | 9.163e-06 | 2015 | 2014-04-24 | C | 3 | 0.0018052 | 9.1633e-06
1 | 140356 | 2014-04-24 09:10 | 2014-04-24 15:27 | 377 | 13 | 4901 | 0.01497 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/90458 - Re-conductor. Isolation points: Temp Links IP0315 at pole M0315, Temp Links IP573 at pole M12839. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 377 | 374 | 4862 | 0.014851 | 3.9708e-05 | 2014-04-24 | B | 0.0074253 | 1.9854e-05 | 2015 | 2014-04-24 | B | 13 | 0.014851 | 3.9708e-05
1 | 140357 | 2014-04-24 19:15 | 2014-04-24 19:44 | 29 | 36 | 1044 | 0.0031888 | 0.00010996 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees - Found half broken branch hanging over lines. Asplundh called in to remove branch. Opened recloser RP 19 to de energise the line while branch removed. Relivened NDR 18384 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 29 | 26 | 936 | 0.0028589 | 0.00010996 | 2014-04-24 | C | 0.0028589 | 0.00010996 | 2015 | 2014-04-24 | C | 36 | 0.0028589 | 0.00010996
1 | 140358 | 2014-04-24 23:10 | 2014-04-25 00:36 | 86 | 1035 | 60392 | 0.18446 | 0.0031613 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - Reported pole on fire. Found insulator faulty at pole 219017. Found no SCADA CB 9139/4 Triped. Isolated between ABS IP158 fuse/Sw 9022/4 & ABS SD5-026. Backfeed rest of area & reclosed CB 9139/4. Replace faulty insulators and reliven | F2 | GRAVATT RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 58.3498 | 55.3498 | 57287 | 0.17498 | 0.0031613 | 2014-04-24 | C | 0.17498 | 0.0031613 | 2015 | 2014-04-24 | C | 1035 | 0.17498 | 0.0031613
1 | 140361 | 2014-04-25 10:00 | 2014-04-25 11:10 | 70 | 62 | 4340 | 0.013256 | 0.00018937 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Defective Component - Outage required between ABS E74 and H45 to repair a damaged conductor (Suspect caused by trees during last storm). One conductor rejointed, 2 sleeves and 20m conductor used. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 4154 | 0.012688 | 0.00018937 | 2014-04-25 | C | 0.012688 | 0.00018937 | 2015 | 2014-04-25 | C | 62 | 0.012688 | 0.00018937
1 | 140362 | 2014-04-25 11:45 | 2014-04-25 12:56 | 71 | 343 | 17832 | 0.054466 | 0.0010477 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees - Tripping on CB6 on O/C. Feeder patrolled / sectionalised with a broken branch found between ABS R51 and S19. Cut away and relivened OK. Tree branch was rotten and had broken off onto lines. NDR 19166. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 51.9883 | 48.9883 | 16803 | 0.051323 | 0.0010477 | 2014-04-25 | C | 0.051323 | 0.0010477 | 2015 | 2014-04-25 | C | 343 | 0.051323 | 0.0010477
1 | 140364 | 2014-04-25 16:17 | 2014-04-25 22:28 | 371 | 32 | 9288 | 0.028369 | 9.7742e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | BINDER | Defective Component - Faultman found Sectionaliser C633/2 open while attending a fault call. Line was sectionalised and patrolled and a floating wire was found at pole 811768, line was isolated at ABS S1203 to rebind the conductor. Adrian Marshall and Fra | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 290.25 | 287.25 | 9192 | 0.028076 | 9.7742e-05 | 2014-04-25 | C | 0.028076 | 9.7742e-05 | 2015 | 2014-04-25 | C | 32 | 0.028076 | 9.7742e-05
1 | 140365 | 2014-04-26 01:45 | 2014-04-26 10:00 | 495 | 182 | 39040 | 0.11924 | 0.00055591 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum. RS C216/2 found tripped as part of dispatch job - RS C216 tyripped on reclose - Fault found to be past ABS S162 during sectionlising - Broken DDO found at Pole 839007 - Isolated at ABS S162 and DDO replaced - On relivening found that | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 214.5055 | 211.5055 | 38494 | 0.11758 | 0.00055591 | 2014-04-26 | C | 0.11758 | 0.0005559 | 2015 | 2014-04-26 | C | 182 | 0.11758 | 0.00055591
1 | 140366 | 2014-04-17 09:45 | 2014-04-18 09:49 | 1444 | 95 | 73931 | 0.22582 | 0.00029017 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Walton CB4 RC25 Tripped on E/F. Patrolled and found line down. Steve Martin attended. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 778.2211 | 775.2211 | 73646 | 0.22495 | 0.00029017 | 2014-04-17 | C | 0.22495 | 0.00029017 | 2015 | 2014-04-17 | C | 95 | 0.22495 | 0.00029017
1 | 140367 | 2014-04-26 12:10 | 2014-04-26 18:27 | 377 | 88 | 14997 | 0.045807 | 0.00026879 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power - Walton CB 2 Trip A B O/C Car Verus Pole H1241. Isolation at ABS IC1217. No Back feeds available. Faultman Steve Martin. John Peters. NDR 32956. Materials:- 1 pole, 1 HV xarm, 1 HV take off xarm, 3 x 11kV insulators, 5 x DDO's, 3 x polymers. | F4 | CAMPBELL RD | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 170.4205 | 167.4205 | 14733 | 0.045001 | 0.00026879 | 2014-04-26 | C | 0.045001 | 0.00026879 | 2015 | 2014-04-26 | C | 88 | 0.045001 | 0.00026879
1 | 140369 | 2014-04-26 23:04 | 2014-04-27 01:46 | 162 | 223 | 19389 | 0.059222 | 0.00068114 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | OPOSSUM | CONDUCTOR | Animals - opossum Recloser RC24 tripped, L/O. Feeder sectionalised & fault located to beyond Fuses FP1290 at pole 04023 ( possum on line ) Possum removed all service restored, Don Watson & Colin Pepper attended. No materials | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 86.9462 | 83.9462 | 18720 | 0.057179 | 0.00068114 | 2014-04-26 | C | 0.057179 | 0.00068114 | 2015 | 2014-04-26 | C | 223 | 0.057179 | 0.00068114
1 | 140371 | 2014-04-27 13:10 | 2014-04-27 13:40 | 30 | 30 | 900 | 0.002749 | 9.1633e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - at 13:10, Kauri Point Sub, CB 1 Lindemann Rd Feeder. Found Connection from Jumper to Top of DDO Fuses at SA2-026 was faulty. Isolated Lines at Fuses SA2-031. Permit Issued & Repairs Carried out. All Power Restored On Completion. Nick | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 810 | 0.0024741 | 9.1633e-05 | 2014-04-27 | C | 0.0024741 | 9.1633e-05 | 2015 | 2014-04-27 | C | 30 | 0.0024741 | 9.1633e-05
1 | 140372 | 2014-04-27 23:00 | 2014-04-27 23:50 | 50 | 110 | 5500 | 0.016799 | 0.00033599 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/90485 - Make gap to replace 11kV crossarms. Isolation points: O62, O67 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 5170 | 0.015791 | 0.00033599 | 2014-04-27 | B | 0.0078957 | 0.00016799 | 2015 | 2014-04-27 | B | 110 | 0.015791 | 0.00033599
1 | 140373 | 2014-04-27 23:50 | 2014-04-28 02:00 | 130 | 4 | 520 | 0.0015883 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Outage required from fuses 5136 to repair a floating conductor which had tripped one of the fuses. Crossarm found to be burnt and required replacement along with 3 insulators. Relivened OK. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 130 | 127 | 508 | 0.0015516 | 1.2218e-05 | 2014-04-27 | C | 0.0015516 | 1.2218e-05 | 2015 | 2014-04-27 | C | 4 | 0.0015516 | 1.2218e-05
1 | 140374 | 2014-04-28 00:16 | 2014-04-28 01:26 | 70 | 259 | 11295 | 0.0345 | 0.0007911 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - Baird Rd CB 5 No Trip. Recloser 9198 Trip. No Flags. Line Sectionalized & Patrolled. Small branch removed from ABS 1110 Pole B12513 by hot stick. Faultman Dave Mckee | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 43.61 | 40.61 | 10518 | 0.032126 | 0.0007911 | 2014-04-28 | C | 0.032126 | 0.0007911 | 2015 | 2014-04-28 | C | 259 | 0.032126 | 0.0007911
1 | 140376 | 2014-04-28 04:00 | 2014-04-28 05:35 | 95 | 186 | 7509 | 0.022936 | 0.00056812 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | CAPITAL WORKS | CABLE TERMINATION | SIN: 14/91313 - Shut 2 of 2: Continuous from 28/04/14 to 27/06/14/ SIN No 14/14/91313 - Upgrade Maraetai sub T2 and 11kV LHS bus switchgear CBs and cables. Isolation points: Maraetai Sub AP1- 33kV ABS PC57, 11kV CB19. AP2- 11kV CB 19 , SW/Gear IC1937, c | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 40.371 | 37.371 | 6951 | 0.021231 | 0.00056812 | 2014-04-28 | B | 0.010616 | 0.00028406 | 2015 | 2014-04-28 | B | 186 | 0.021231 | 0.00056812
1 | 140378 | 2014-04-28 09:52 | 2014-04-28 12:48 | 176 | 75 | 13200 | 0.040318 | 0.00022908 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90870 - Replace 11kV xarms and 11kV fuses on Kaharoa Rd (in very poor condition and will fail soon). Also replace 11kV Transformer TX L4275 as has severe rust (holes in lid will allow water in) and will cause outage soon. Isolation points:11kV AB | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 176 | 173 | 12975 | 0.039631 | 0.00022908 | 2014-04-28 | B | 0.019816 | 0.00011454 | 2015 | 2014-04-28 | B | 75 | 0.039631 | 0.00022908
1 | 140379 | 2014-04-28 11:10 | 2014-04-28 11:55 | 45 | 4 | 180 | 0.0005498 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Emergency Isolation to replace HV crossarm. Isolation at Fuses FC1478. Iro Ezekiela Faultman. 1 x HV Crossarm, 3 x 11kV Pin Insulators, 2 x Stay Straps and bolts used. | F3 | MOWBRAY RD | WAHAROA SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 168 | 0.00051314 | 1.2218e-05 | 2014-04-28 | C | 0.00051314 | 1.2218e-05 | 2015 | 2014-04-28 | C | 4 | 0.00051314 | 1.2218e-05
1 | 140380 | 2014-04-28 09:04 | 2014-04-28 14:46 | 342 | 69 | 23598 | 0.072078 | 0.00021076 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90487 - Replace 11kV crossarms between O62 to O67 over 5 days. Isolation points: O67 to gap P34365 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 342 | 339 | 23391 | 0.071446 | 0.00021076 | 2014-04-28 | B | 0.035723 | 0.00010538 | 2015 | 2014-04-28 | B | 69 | 0.071446 | 0.00021076
1 | 140383 | 2014-04-28 15:44 | 2014-04-28 16:16 | 32 | 7 | 224 | 0.00068419 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Wind -RS F26 A/R, E/F. Later dispatch received call of a floating wire. Faultman found fault at Pole P11691 so work area isolated at Fuses F29 and wire rebound in. Materials used: 1 x Aluminium binder. Attended by Jeff Roberts. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 203 | 0.00062005 | 2.1381e-05 | 2014-04-28 | C | 0.00062005 | 2.1381e-05 | 2015 | 2014-04-28 | C | 7 | 0.00062005 | 2.1381e-05
1 | 140384 | 2014-04-28 09:15 | 2014-04-28 15:25 | 370 | 35 | 12950 | 0.039555 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90267 - Change 11kV poles, X-arms and reconductor. Isolation Points: 11kV ABS SE3-016 & TEMP19. Re-Advertise under SIN 14/91440. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 370 | 367 | 12845 | 0.039234 | 0.0001069 | 2014-04-28 | B | 0.019617 | 5.3452e-05 | 2015 | 2014-04-28 | B | 35 | 0.039234 | 0.0001069
1 | 140385 | 2014-04-28 09:15 | 2014-04-28 10:26 | 71 | 4 | 284 | 0.00086746 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - at 09:15 Kauri Point Sub, CB 2 Bowentown Feeder. Blown Transformer TA1-005 Needed replacing. Own Isolation & AP. Transformer Replaced & All Power Restored on Completion. Justin Middleton Attended. 1x Transformer Replaced. | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 272 | 0.0008308 | 1.2218e-05 | 2014-04-28 | C | 0.0008308 | 1.2218e-05 | 2015 | 2014-04-28 | C | 4 | 0.0008308 | 1.2218e-05
1 | 140388 | 2014-04-28 14:37 | 2014-04-28 21:33 | 416 | 57 | 16494 | 0.05038 | 0.0001741 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - Car V Pole Isolated At ABS's U12 & U13 with a backfeed installed via ABS S12 - Pole P16876 & Transformer T8/33 replaced, Feeder returned to Service - Attended by Trevor Pocock - Used 1 X Pole, 1 X 15kVA 3 ph Transformer, Hv & LV Cross arms and | F3 | EKETAHUNA | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 289.3684 | 286.3684 | 16323 | 0.049857 | 0.0001741 | 2014-04-28 | C | 0.049857 | 0.0001741 | 2015 | 2014-04-28 | C | 57 | 0.049857 | 0.0001741
1 | 140390 | 2014-04-28 13:55 | 2014-04-28 20:03 | 368 | 2246 | 395382 | 1.2077 | 0.0068602 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | No Power -33kV CB 1122 tripped at TeMatai on B phase O/C causing an outage to Pongakawa and Atuaroa subs . A report received from fire service advised of a line down on Rangiuru road . Atuaroa sub was backfed from Kaitimako and backfeeds put in place for | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 176.0383 | 173.0383 | 388644 | 1.1871 | 0.0068602 | 2014-04-28 | C | 1.1871 | 0.0068602 | 2015 | 2014-04-28 | C | 2246 | 1.1871 | 0.0068602
1 | 140391 | 2014-04-29 14:15 | 2014-04-29 14:40 | 25 | 27 | 675 | 0.0020617 | 8.2469e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component - Found fuse holder broken at transformer TC1472. Isolated at fuses FP1181. Replace fuse holder and re livened | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 25 | 22 | 594 | 0.0018143 | 8.2469e-05 | 2014-04-29 | C | 0.0018143 | 8.2469e-05 | 2015 | 2014-04-29 | C | 27 | 0.0018143 | 8.2469e-05
1 | 140393 | 2014-04-29 09:00 | 2014-04-29 13:40 | 280 | 19 | 5320 | 0.01625 | 5.8034e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/91300 - Replace rusty SDAF FMU for new Safelink cfcf. Isolation points 11kV FABS 2543, 400V incommers for X3159 open and tagged, LV incomers for X2279 open and tagged, 400V incomers for 4521W open and tagged.Applicant will connect generator to bac | F3 | CORNFOOT ST | CASTLECLIFF SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 280 | 277 | 5263 | 0.016075 | 5.8034e-05 | 2014-04-29 | B | 0.0080377 | 2.9017e-05 | 2015 | 2014-04-29 | B | 19 | 0.016075 | 5.8034e-05
1 | 140396 | 2014-04-11 09:41 | 2014-04-11 13:51 | 250 | 2 | 500 | 0.0015272 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90961 - New Date 29th April. KW to confirm new date. Due to weather. MR 11/04/2014We are replacing existing 11kV pole C14041 and installing new 11m pole with new 11kV Transformer TP2635. We will offload transformer TP2266 & TC517 before opening F | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 494 | 0.0015089 | 6.1088e-06 | 2014-04-11 | B | 0.00075444 | 3.054e-06 | 2015 | 2014-04-11 | B | 2 | 0.0015089 | 6.1088e-06
1 | 140398 | 2014-04-29 10:13 | 2014-04-29 14:28 | 255 | 46 | 11730 | 0.035828 | 0.0001405 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90868 - Advertising only ## RE_WRITTEN UNDER SIN 14/91870 ###Replace 37 double circuit Xarms from pole 800734 to pole 801733, part of the 33kV Xarm replacement job Pukepapa sub to Arahina sub. 33kV circuit above will be alive. Isolation points: CB | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 255 | 252 | 11592 | 0.035407 | 0.0001405 | 2014-04-29 | B | 0.017703 | 7.0252e-05 | 2015 | 2014-04-29 | B | 46 | 0.035407 | 0.0001405
1 | 140399 | 2014-04-29 09:45 | 2014-04-29 10:33 | 48 | 100 | 4800 | 0.014661 | 0.00030544 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CUSTOMER REQUEST | FUSE HOLDER | SIN: 14/90752 - Install new double tap off arm on existing 6.6kV network pole 369925 fitted w/ new 6.6kV Fuse 8991 for supply to new 6.6kV spur line and new 100kVA TX 5068T. Isolation points: 6.6kV Fused ABS 5534.Confirm Pre Commissioning & Inspection Cer | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 48 | 45 | 4500 | 0.013745 | 0.00030544 | 2014-04-29 | B | 0.0068725 | 0.00015272 | 2015 | 2014-04-29 | B | 100 | 0.013745 | 0.00030544
1 | 140400 | 2014-04-29 08:23 | 2014-04-29 10:30 | 127 | 4 | 508 | 0.0015516 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component -Emergency Isolation to Replace Broken LV arm on Pole H3314. Isolation at Fuses FC1452. Materials used. 1 x LV arm. 4 LV Pin Insulators. 2 Stays. Tamatu Pene Faultman | F4 | CAMPBELL RD | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 127 | 124 | 496 | 0.001515 | 1.2218e-05 | 2014-04-29 | C | 0.001515 | 1.2218e-05 | 2015 | 2014-04-29 | C | 4 | 0.001515 | 1.2218e-05
1 | 140401 | 2014-04-29 09:34 | 2014-04-29 15:15 | 341 | 65 | 22165 | 0.067701 | 0.00019854 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90892 - Replace existing poles P00715 and P19925 and restrain 11kV conductor. Isolation points: V7, V5, V6 | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 341 | 338 | 21970 | 0.067106 | 0.00019854 | 2014-04-29 | B | 0.033553 | 9.9269e-05 | 2015 | 2014-04-29 | B | 65 | 0.067106 | 0.00019854
1 | 140402 | 2014-04-29 09:00 | 2014-04-29 14:51 | 351 | 41 | 14391 | 0.043956 | 0.00012523 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90490 - Replace 11kV crossarms between O62 to O67 over 5 days. Isolation points: O62 to gap P34365 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 351 | 348 | 14268 | 0.043581 | 0.00012523 | 2014-04-29 | B | 0.02179 | 6.2616e-05 | 2015 | 2014-04-29 | B | 41 | 0.043581 | 0.00012523
1 | 140404 | 2014-04-29 13:11 | 2014-04-29 14:31 | 80 | 149 | 10136 | 0.03096 | 0.00045511 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause -CB A11 Trip. E/F. O/C. L/O. Feeder Sectionalised, no fault found. A/R Function was disabled at the time of the trip For Asplundh to do tree work. Asplundh were not near the lines at the time of the trip (Having Lunch). Jade Williams Faultma | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 68.0268 | 65.0268 | 9689 | 0.029594 | 0.00045511 | 2014-04-29 | C | 0.029594 | 0.00045511 | 2015 | 2014-04-29 | C | 149 | 0.029594 | 0.00045511
1 | 140405 | 2014-04-29 17:02 | 2014-04-29 18:41 | 99 | 7 | 693 | 0.0021167 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - 2 X Fuses at 8033 found blown due Branch found on the lines at pole 823988 as part of a Dispatch job - isolated at Fuses 8033 - Branch removed & circuit returned to Service - Attended by Lee Wilton | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 99 | 96 | 672 | 0.0020526 | 2.1381e-05 | 2014-04-29 | C | 0.0020526 | 2.1381e-05 | 2015 | 2014-04-29 | C | 7 | 0.0020526 | 2.1381e-05
1 | 140406 | 2014-04-29 22:11 | 2014-04-29 23:15 | 64 | 9 | 576 | 0.0017593 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - Floating wire found past pole 837162 as part of dispatch job - Isolated at Fuses 7768 - Line break made at Pole 837162, Isolating transformer T544 (Feededs Woolshed and Old Cottage) as unable to access pole that floater is on, faultm | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 549 | 0.0016769 | 2.749e-05 | 2014-04-29 | C | 0.0016769 | 2.749e-05 | 2015 | 2014-04-29 | C | 9 | 0.0016769 | 2.749e-05
1 | 140407 | 2014-04-29 18:49 | 2014-04-29 22:30 | 221 | 50 | 10698 | 0.032676 | 0.00015272 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Defective Component - at 18:49, Waihi Rd Sub, CB 5 Waihi Road Feeder. Faultman Dispatched to No Power Calls from Transformer TD4-527. Found blown fuse at Link Box SD4-425. Isolated at Fuse/Sw SD4-638 to replace fuse at Link Box. Fuse Replaced and tried re | F2 | WAIHI RD | WAIHI ROAD SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 213.96 | 210.96 | 10548 | 0.032218 | 0.00015272 | 2014-04-29 | C | 0.032218 | 0.00015272 | 2015 | 2014-04-29 | C | 50 | 0.032218 | 0.00015272
1 | 140409 | 2014-04-28 13:55 | 2014-04-28 15:50 | 115 | 1090 | 121871 | 0.37225 | 0.0033293 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power -33kV CB 1122 tripped at TeMatai on B phase O/C causing an outage to Pongakawa and Atuaroa subs . A report received from fire service advised of a line down on Rangiuru road . Atuaroa sub was backfed from Kaitimako and backfeeds put in place for | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 111.8083 | 108.8083 | 118601 | 0.36226 | 0.0033293 | 2014-04-28 | C | 0.36226 | 0.0033293 | 2015 | 2014-04-28 | C | 1090 | 0.36226 | 0.0033293
1 | 140410 | 2014-04-30 10:23 | 2014-04-30 11:07 | 44 | 985 | 43340 | 0.13238 | 0.0030086 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component -Emergency Shutdown of entire Sub. Loud crackling noise coming from somwhere on the 11kV Sub. Later found to be the Local Service transformer in the process of blowing up. Local Service Transformer Isolated and Power restored. Jason Ha | F1,F2,F3 | Not entered | Not entered | Not entered | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 44 | 41 | 40385 | 0.12335 | 0.0030086 | 2014-04-30 | C | 0.12335 | 0.0030086 | 2015 | 2014-04-30 | C | 985 | 0.12335 | 0.0030086
1 | 140411 | 2014-04-30 10:00 | 2014-04-30 11:40 | 100 | 2 | 200 | 0.00061088 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90048 - Replace 30kVA 11kV TX as lid is rusty plus also upgrade earths etc at pole 764685 . Isolation points: 11kV Fuses 5254 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 194 | 0.00059256 | 6.1088e-06 | 2014-04-30 | B | 0.00029628 | 3.054e-06 | 2015 | 2014-04-30 | B | 2 | 0.00059256 | 6.1088e-06
1 | 140412 | 2014-04-30 09:00 | 2014-04-30 14:25 | 325 | 52 | 16900 | 0.05162 | 0.00015883 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90461 - Upgrade TX TC2026 to 200kVA ground mount TX. Install 2 x 4c 185mm AI cables and streetlight cable from new TX and streetlight pillar up pole G0822. Upgrade links in DDOs FC1506. Install streetlight pilot break points at pole G12393 and G1 | F3 | ELIZABETH ST | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 325 | 322 | 16744 | 0.051143 | 0.00015883 | 2014-04-30 | B | 0.025572 | 7.9415e-05 | 2015 | 2014-04-30 | B | 52 | 0.051143 | 0.00015883
1 | 140417 | 2014-04-30 10:23 | 2014-04-30 14:59 | 276 | 46 | 12696 | 0.038779 | 0.0001405 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/90908 - Replace 11kV ABS CA422 and pole. Also have 110/220kV line crossing above work site. Isolation points: ABS CA433, ABS CA476. Requirement to have operator earthe as close as possible on both sides of ABS being worked on.MR AW. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 276 | 273 | 12558 | 0.038357 | 0.0001405 | 2014-04-30 | B | 0.019179 | 7.0252e-05 | 2015 | 2014-04-30 | B | 46 | 0.038357 | 0.0001405
1 | 140419 | 2014-04-30 09:00 | 2014-04-30 16:19 | 439 | 3 | 1317 | 0.0040227 | 9.1633e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90049 - Remove 11kV link-box SB2-068 and replace with automated Safelink CFCF Sw/gear 9765. Liven Sw/gear 9765/1 by LL at pole 248295 (201410). Isolation points: 11kV ABS SB2-009, 11kV Line break at pole 248295 (201410). | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 439 | 436 | 1308 | 0.0039952 | 9.1633e-06 | 2014-04-30 | B | 0.0019976 | 4.582e-06 | 2015 | 2014-04-30 | B | 3 | 0.0039952 | 9.1633e-06
1 | 140420 | 2014-04-29 10:33 | 2014-04-29 16:30 | 357 | 3 | 1071 | 0.0032713 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | POLE | No Power - Isolate Transformer 535 for Safety so can pull pole up Adam Whale Attended replaced a stay wire. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 357 | 354 | 1062 | 0.0032438 | 9.1633e-06 | 2014-04-29 | C | 0.0032438 | 9.163e-06 | 2015 | 2014-04-29 | C | 3 | 0.0032438 | 9.1633e-06
1 | 140423 | 2014-05-01 09:30 | 2014-05-01 13:00 | 210 | 12 | 2520 | 0.0076971 | 3.6653e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91398 - Replace 11kV pole 221917 and X-arms. Isolation points: 11kV ABS IP565 (new - LLP Refer14/91401) | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 210 | 207 | 2484 | 0.0075872 | 3.6653e-05 | 2014-05-01 | B | 0.0037936 | 1.8327e-05 | 2015 | 2014-05-01 | B | 12 | 0.0075872 | 3.6653e-05
1 | 140426 | 2014-05-01 09:00 | 2014-05-01 10:54 | 114 | 4 | 1680 | 0.0051314 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91642 - Rewritten from SIN 14/90900 to include 11kV isolation. Replace 33kV poles and X-arms as per work pack. Isolation points: 33kV ABS 1054, 1050, 3184 & 126; 11kV Fuses SD3-019. | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 420 | 417 | 1668 | 0.0050948 | 1.2218e-05 | 2014-05-01 | B | 0.0025474 | 6.109e-06 | 2015 | 2014-05-01 | B | 4 | 0.0050948 | 1.2218e-05
1 | 140427 | 2014-05-01 06:45 | 2014-05-01 07:00 | 15 | 21 | 315 | 0.00096214 | 6.4143e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Fused ABS 2674. Found open Transformer X799. Found L/V Cables Blown. L/V Backfeed in place from 07.00. L/VCables repaired. Garry Fisher Attended. | F2 | GUYTON | TAUPO QUAY SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 252 | 0.00076971 | 6.4143e-05 | 2014-05-01 | C | 0.00076972 | 6.4143e-05 | 2015 | 2014-05-01 | C | 21 | 0.00076971 | 6.4143e-05
1 | 140428 | 2014-05-01 09:40 | 2014-05-01 16:56 | 436 | 118 | 13309 | 0.040651 | 0.00036042 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Recloser 2754 Tripped E/F O/C A Phase. Patrolled found faulty Transformer X541. Isolated & relivened. Rest of Feeder Up OK. Karl Rogers Attended. Replaced Transformer X541. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 112.7881 | 109.7881 | 12955 | 0.03957 | 0.00036042 | 2014-05-01 | C | 0.03957 | 0.00036042 | 2015 | 2014-05-01 | C | 118 | 0.03957 | 0.00036042
1 | 140429 | 2014-05-02 00:02 | 2014-05-02 01:05 | 63 | 13 | 819 | 0.0025016 | 3.9708e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91031 - Isolate 11kV Transformer TD4-771 to fit MDIs to LV bus. Isolation points: 11kV Fuse/Sw SD4-793. | F2 | MALEME EXPRESS | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 780 | 0.0023825 | 3.9708e-05 | 2014-05-02 | B | 0.0011912 | 1.9854e-05 | 2015 | 2014-05-02 | B | 13 | 0.0023825 | 3.9708e-05
1 | 140430 | 2014-05-01 23:00 | 2014-05-02 03:25 | 265 | 114 | 30210 | 0.092274 | 0.0003482 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90747 - Replace 11kV G/M Transformer TC3812, leaking oil. Isolation point: 11kV Fuse/Sw 9233/2 | F2/F3 | PORT RD | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 265 | 262 | 29868 | 0.09123 | 0.0003482 | 2014-05-01 | B | 0.045615 | 0.0001741 | 2015 | 2014-05-01 | B | 114 | 0.09123 | 0.0003482
1 | 140433 | 2014-05-02 09:35 | 2014-05-02 11:15 | 100 | 3 | 300 | 0.00091633 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/90452 - Install 400V fuses on existing pole mounted TX. 11kV Transformer to be isolated via 11Kv Transformer fuses and new 400V disconnector to be fitted. Isolation points: 11kV Transformer Fuse TC2730.NOTE: Contact NOC prior to isolation and agai | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 291 | 0.00088884 | 9.1633e-06 | 2014-05-02 | B | 0.00044442 | 4.582e-06 | 2015 | 2014-05-02 | B | 3 | 0.00088884 | 9.1633e-06
1 | 140434 | 2014-05-02 09:47 | 2014-05-02 10:24 | 37 | 229 | 8473 | 0.02588 | 0.00069946 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - Tripping on recloser CB C638/2 on E/F, O/C. Patrolled / reclosed OK. Possibly bird strike. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 7786 | 0.023782 | 0.00069946 | 2014-05-02 | C | 0.023782 | 0.00069946 | 2015 | 2014-05-02 | C | 229 | 0.023782 | 0.00069946
1 | 140438 | 2014-05-02 09:15 | 2014-05-02 13:05 | 230 | 21 | 7245 | 0.022129 | 6.4143e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91332 - Connect new U/G cable to existing Transformer TP1749. Liven and commission new Transformer (TP2638). Isolation point: 11kV Fuse/Sw 9372/2. | F2 | MALEME EXPRESS | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 7182 | 0.021937 | 6.4143e-05 | 2014-05-02 | B | 0.010968 | 3.2071e-05 | 2015 | 2014-05-02 | B | 21 | 0.021937 | 6.4143e-05
1 | 140439 | 2014-05-02 12:03 | 2014-05-02 12:15 | 12 | 1993 | 20990 | 0.064112 | 0.0060875 | No Power | 33000 | Unplanned | Overhead Line | HUMAN ELEMENT | EQUIPMENT OPERATING ERROR | CONDUCTOR | Employee error - Tripping on MTN CB1132 causing loss of supply to both Arahina and Rata Subs. Trip caused by HiAb truck boom coming into contact with 33kV line while changing crossarms on Pukepapa Rd. Live Line procedures being used - Refer LLP 14/91623. | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 10.5319 | 7.5319 | 15011 | 0.04585 | 0.0060875 | 2014-05-02 | C | 0.04585 | 0.0060875 | 2015 | 2014-05-02 | C | 1993 | 0.04585 | 0.0060875
1 | 140440 | 2014-05-02 12:30 | 2014-05-02 14:10 | 100 | 7 | 700 | 0.0021381 | 2.1381e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/90862 - Install 400V fuses on existing pole mounted TX. TXs to be isolated via11kV Transformer Fuse and new 400V disconnector to be fitted/win the 1 hr HV shutdown. Followed w/ an 400V shutdown may be carried out after the HV is restored to comple | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 679 | 0.002074 | 2.1381e-05 | 2014-05-02 | B | 0.001037 | 1.069e-05 | 2015 | 2014-05-02 | B | 7 | 0.002074 | 2.1381e-05
1 | 140443 | 2014-05-03 09:30 | 2014-05-03 11:40 | 130 | 7 | 910 | 0.0027795 | 2.1381e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91368 - Replace set of 11kV termination Xarms on TX structure T7/130. Isolation points: Fuse links R45 | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 130 | 127 | 889 | 0.0027154 | 2.1381e-05 | 2014-05-03 | B | 0.0013577 | 1.069e-05 | 2015 | 2014-05-03 | B | 7 | 0.0027154 | 2.1381e-05
1 | 140445 | 2014-05-03 12:00 | 2014-05-03 12:30 | 30 | 4 | 120 | 0.00036653 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | STAY WIRE | Defective Component - Short outage required on Transformer 3761T to cut away a broken Stay wire (had come into contact with transformer jumper and blown the fuses). Relivened OK. | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 108 | 0.00032988 | 1.2218e-05 | 2014-05-03 | C | 0.00032988 | 1.2218e-05 | 2015 | 2014-05-03 | C | 4 | 0.00032988 | 1.2218e-05
1 | 140449 | 2014-05-03 23:33 | 2014-05-04 13:12 | 819 | 801 | 127406 | 0.38915 | 0.0024466 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | Defective Component - CB1 tripped O/C A & B Ph L/O. Feeder sectionalised & lines down found at pole Q0264. Isolation between CB1, Links 9719/6 & ABS IC201 with back feed via ABS IP523. Jumpers cut away only at pole Q12419 & rest of feeder returned to serv | F3 | BEACH RD WAIHI BEACH | WAIHI BEACH SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 159.0587 | 156.0587 | 125003 | 0.38181 | 0.0024466 | 2014-05-03 | C | 0.38181 | 0.0024466 | 2015 | 2014-05-03 | C | 801 | 0.38181 | 0.0024466
1 | 140451 | 2014-05-04 11:05 | 2014-05-04 13:20 | 135 | 412 | 25877 | 0.079039 | 0.0012584 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | No Power - Walton CB 4 trip B C O/C. Jumper broken at pole H0456 & fell across 2 phases. Line Patrolled & Sectionalized. Greg Whyte attended. Isolated at ABS IC732. No back feeds available. Materials 1 x 11kV Polymer, HD Connectors. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 62.8083 | 59.8083 | 24641 | 0.075264 | 0.0012584 | 2014-05-04 | C | 0.075264 | 0.0012584 | 2015 | 2014-05-04 | C | 412 | 0.075264 | 0.0012584
1 | 140454 | 2014-05-05 09:22 | 2014-05-05 14:23 | 301 | 41 | 12341 | 0.037695 | 0.00012523 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90494 - Replace 11kV crossarms between O62 to O67 over 5 days. Isolation points: O62 to gap P34365 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 301 | 298 | 12218 | 0.037319 | 0.00012523 | 2014-05-05 | B | 0.018659 | 6.2616e-05 | 2015 | 2014-05-05 | B | 41 | 0.037319 | 0.00012523
1 | 140455 | 2014-05-05 15:11 | 2014-05-05 15:45 | 34 | 1 | 34 | 0.00010385 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power - Livingston CB LI7 No Trip. Crossarm tipped over at pole 849752. Isolation at Fuses 6963 No Back Feeds available. Arm straightened up bolt pushed through & Double nuts applied. All works complete. Faultman Brett Bensley, Material 2 x Galv nuts | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 31 | 9.4687e-05 | 3.0544e-06 | 2014-05-05 | C | 9.4687e-05 | 3.054e-06 | 2015 | 2014-05-05 | C | 1 | 9.4687e-05 | 3.0544e-06
1 | 140456 | 2014-05-05 15:01 | 2014-05-05 17:25 | 144 | 210 | 19231 | 0.05874 | 0.00064143 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Tasman CB TA 1 Trip. E/F Line Patrolled & Sectionalized. Fault reported by member of public during this process. Line down at pole 715233. Isolation at Fuse TA121 No Back Feeds available. Faultman Bevan Hughes. Materials 2 sleeves / 5 m conduct | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 91.5762 | 88.5762 | 18601 | 0.056815 | 0.00064143 | 2014-05-05 | C | 0.056815 | 0.00064143 | 2015 | 2014-05-05 | C | 210 | 0.056815 | 0.00064143
1 | 140458 | 2014-05-05 10:06 | 2014-05-05 15:09 | 303 | 49 | 14847 | 0.045349 | 0.00014967 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90963 - Replace TX structure P1420 as it is in poor condition w/ new 11kV pole plus new earths etc. but TX is new and will use again. Isolation points: 11kV Fuse 6402. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 303 | 300 | 14700 | 0.0449 | 0.00014967 | 2014-05-05 | B | 0.02245 | 7.4833e-05 | 2015 | 2014-05-05 | B | 49 | 0.0449 | 0.00014967
1 | 140459 | 2014-05-05 09:20 | 2014-05-05 12:27 | 187 | 8 | 1560 | 0.0047649 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/91840 - Reinstate missing 11kV span between poles 380477 and P2256 old Waitekauri Rd. Isolation points:11kV ABS IC1223 & ABS 290.LLP 14/91803 | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 1536 | 0.0046916 | 2.4435e-05 | 2014-05-05 | B | 0.0023458 | 1.2218e-05 | 2015 | 2014-05-05 | B | 8 | 0.0046916 | 2.4435e-05
1 | 140464 | 2014-05-05 10:15 | 2014-05-05 12:52 | 157 | 2 | 314 | 0.00095909 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91690 - Replace 11kV poles 722743, 722737, 722738. Isolation points: 11kV Fuses WH864. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 157 | 154 | 308 | 0.00094076 | 6.1088e-06 | 2014-05-05 | B | 0.00047038 | 3.054e-06 | 2015 | 2014-05-05 | B | 2 | 0.00094076 | 6.1088e-06
1 | 140466 | 2014-05-05 10:19 | 2014-05-05 12:56 | 157 | 154 | 19619 | 0.059925 | 0.00047038 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | BINDER | Defective Component - Tripping on CB NG4 on B, C Phase. Fault caused by floating conductor. Isolation between ABS NG434 and NG402 with backfeeds at ABS NG326. Conductor rebound, relivened OK. (1 binder needed). High winds. | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 127.3961 | 124.3961 | 19157 | 0.058514 | 0.00047038 | 2014-05-05 | C | 0.058514 | 0.00047038 | 2015 | 2014-05-05 | C | 154 | 0.058514 | 0.00047038
1 | 140467 | 2014-05-05 07:40 | 2014-05-05 14:04 | 384 | 23 | 8832 | 0.026977 | 7.0252e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | Defective Component - Sectionaliser C213 tripped caused by broekn pole (High winds). Isolation from Sectionaliser C213 to end. Pole & associated hardware replaced. Relivened OK. NDR37954. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 384 | 381 | 8763 | 0.026766 | 7.0252e-05 | 2014-05-05 | C | 0.026766 | 7.0252e-05 | 2015 | 2014-05-05 | C | 23 | 0.026766 | 7.0252e-05
1 | 140468 | 2014-05-05 13:03 | 2014-05-05 17:00 | 237 | 207 | 31622 | 0.096587 | 0.00063227 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | BINDER | Defective Component - Reports of Part power / no power found fuses blown at Both 122 and 200. Fault caused by a floating conductor at pole 785518 with isolations at ABS 1298 and recloser CB107. (Backfeed at VS 4621/2). Conductor rebound with a new bider. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 152.7633 | 149.7633 | 31001 | 0.09469 | 0.00063227 | 2014-05-05 | C | 0.09469 | 0.00063227 | 2015 | 2014-05-05 | C | 207 | 0.09469 | 0.00063227
1 | 140469 | 2014-05-05 11:10 | 2014-05-05 12:02 | 52 | 1 | 52 | 0.00015883 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | Defective Component - Report of part power found a faulty Fuses carrier at FABS 2871. Isolation required from that switch to carry out repairs. Relivened OK. | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 49 | 0.00014967 | 3.0544e-06 | 2014-05-05 | C | 0.00014967 | 3.054e-06 | 2015 | 2014-05-05 | C | 1 | 0.00014967 | 3.0544e-06
1 | 140472 | 2014-05-05 17:30 | 2014-05-05 20:35 | 185 | 1 | 185 | 0.00056507 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92000 - Emergency shutdown for replacement of TX X561, TX is leaking oil. Isolation points: FABS 1036 | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 185 | 182 | 182 | 0.00055591 | 3.0544e-06 | 2014-05-05 | B | 0.00027795 | 1.527e-06 | 2015 | 2014-05-05 | B | 1 | 0.00055591 | 3.0544e-06
1 | 140473 | 2014-05-05 17:47 | 2014-05-05 19:52 | 125 | 1096 | 59161 | 0.1807 | 0.0033476 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Tripping on Feilding CB 22 on Phase B O/C. Feeder sectionalised/patrolled with a blown jumper found at Transformer T3/141. Isolation required between ABS O8, O11, O13 and Sw/Gear 227 with backfeeds at ABS O14 and M82. Jumper repair | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 53.979 | 50.979 | 55873 | 0.17066 | 0.0033476 | 2014-05-05 | C | 0.17066 | 0.0033476 | 2015 | 2014-05-05 | C | 1096 | 0.17066 | 0.0033476
1 | 140480 | 2014-05-06 08:32 | 2014-05-06 08:58 | 26 | 32 | 832 | 0.0025413 | 9.7742e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - at 08:32, Featherston Sub, CB C916 Revans St Feeder. Found Broken Jumper at ABS S582. Line was isolated at ABS S582 and Jumper was replaced using live line techniques under a live line permit. All Power Restored on Completion. 1x Jum | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 26 | 23 | 736 | 0.0022481 | 9.7742e-05 | 2014-05-06 | C | 0.0022481 | 9.7742e-05 | 2015 | 2014-05-06 | C | 32 | 0.0022481 | 9.7742e-05
1 | 140481 | 2014-05-06 09:30 | 2014-05-06 13:23 | 233 | 54 | 12582 | 0.038431 | 0.00016494 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91936 - Stage 7: Replace various 11kV poles and arms between pole 741961 and 741946. Isolation points: 11kV ABS 238. | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 233 | 230 | 12420 | 0.037936 | 0.00016494 | 2014-05-06 | B | 0.018968 | 8.2469e-05 | 2015 | 2014-05-06 | B | 54 | 0.037936 | 0.00016494
1 | 140482 | 2014-05-06 11:47 | 2014-05-06 12:55 | 68 | 18 | 1224 | 0.0037386 | 5.498e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component - Faultman found a blown transformer N3240 while attending a fault call, line was isolated at Fuses NG 384 to install the new transformer. Brett Bensley attended. | F4/F1 | SOUTH RD NGARIKI | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 1170 | 0.0035737 | 5.498e-05 | 2014-05-06 | C | 0.0035737 | 5.498e-05 | 2015 | 2014-05-06 | C | 18 | 0.0035737 | 5.498e-05
1 | 140483 | 2014-05-06 10:08 | 2014-05-06 14:26 | 258 | 80 | 20640 | 0.063043 | 0.00024435 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91334 - Replace 11kV pole 708510 East rd Stratford as is close to bank and in danger of falling over. Isolation points: 11kV ABS 6494, 5342, CB4915. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 258 | 255 | 20400 | 0.06231 | 0.00024435 | 2014-05-06 | B | 0.031155 | 0.00012218 | 2015 | 2014-05-06 | B | 80 | 0.06231 | 0.00024435
1 | 140484 | 2014-05-06 10:30 | 2014-05-06 14:37 | 247 | 6 | 1482 | 0.0045267 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90917 - LLP1: 14/91648 Create Live Line break between pole M1471 and M1477. AP1: Complete shutdown between pole M1477 and end of lines. LLP2: 14/91649. Close Line break between pole M1471 and M1477. Isolation points: 11kV Line Break Pole M1471 | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 247 | 244 | 1464 | 0.0044717 | 1.8327e-05 | 2014-05-06 | B | 0.0022358 | 9.163e-06 | 2015 | 2014-05-06 | B | 6 | 0.0044717 | 1.8327e-05
1 | 140485 | 2014-05-06 09:30 | 2014-05-06 12:10 | 160 | 8 | 1280 | 0.0039097 | 2.4435e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91712 - Upgrade 11kV Transformer TC1862. Isolation points: 11kV Transformer fuses TC1862. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP.NOTE: Applicant advises all works being undertaken is outside | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 1256 | 0.0038364 | 2.4435e-05 | 2014-05-06 | B | 0.0019182 | 1.2218e-05 | 2015 | 2014-05-06 | B | 8 | 0.0038364 | 2.4435e-05
1 | 140486 | 2014-05-06 14:40 | 2014-05-06 16:34 | 114 | 26 | 2964 | 0.0090533 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Faultman attending No Power calls found fuse blown at B20 - Line patrolled & floater located at pole P36067 - Isolation at fuses B20 to retie conductor - all supply restored after repairs completed - 1 x Al binder only material required - Jeff Roberts att | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 114 | 111 | 2886 | 0.0088151 | 7.9415e-05 | 2014-05-06 | C | 0.0088151 | 7.9415e-05 | 2015 | 2014-05-06 | C | 26 | 0.0088151 | 7.9415e-05
1 | 140487 | 2014-05-06 08:12 | 2014-05-06 14:49 | 397 | 12 | 4764 | 0.014551 | 3.6653e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91339 - Change Xarms and erect poles from pole no 785419-785359. Isolation points: R107, Links 2711, ABS 438, ABS 4620 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 397 | 394 | 4728 | 0.014441 | 3.6653e-05 | 2014-05-06 | B | 0.0072207 | 1.8327e-05 | 2015 | 2014-05-06 | B | 12 | 0.014441 | 3.6653e-05
1 | 140488 | 2014-05-06 10:20 | 2014-05-06 15:55 | 335 | 13 | 4355 | 0.013302 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91338 - Cut trees along Puke Rd and Ngatoto Rd North by poles 765150, 765122, 765092, badly need cutting. Isolation points:11kV Fuses 5153. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 335 | 332 | 4316 | 0.013183 | 3.9708e-05 | 2014-05-06 | B | 0.0065914 | 1.9854e-05 | 2015 | 2014-05-06 | B | 13 | 0.013183 | 3.9708e-05
1 | 140489 | 2014-05-06 18:38 | 2014-05-06 19:43 | 65 | 336 | 21840 | 0.066709 | 0.0010263 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | Defective Component - Faulty Joint found at Pole P26696 as part of dispatch job - Isolated at ABS's L9 & L12 - Joint replaced and feeder returned to service - attended by Anjay Prasad - Used 1X PG Clamp & 1m of Conductor (less than a Span) | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 20832 | 0.06363 | 0.0010263 | 2014-05-06 | C | 0.06363 | 0.0010263 | 2015 | 2014-05-06 | C | 336 | 0.06363 | 0.0010263
1 | 140490 | 2014-05-06 04:30 | 2014-05-06 07:58 | 208 | 128 | 15844 | 0.048394 | 0.00039097 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - RS 437/2 Tripped - Branch found on lines during Sectionalising - Isolated at ABS 7065 & branch removed using hot sticks - circuit returned to service - attended by Jason Hall and Lee Wilton. | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 123.7812 | 120.7812 | 15460 | 0.047221 | 0.00039097 | 2014-05-06 | C | 0.047221 | 0.00039097 | 2015 | 2014-05-06 | C | 128 | 0.047221 | 0.00039097
1 | 140491 | 2014-05-06 05:12 | 2014-05-06 10:08 | 296 | 65 | 19240 | 0.058767 | 0.00019854 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - RS V5 Tripped C ph O/C E/F L/O - Twisted crossarm found at Pole P31363 - Isolated at ABS V7 & Links V6 - Cross arm rebolted to Pole - Attended by Robin Smith and Trevor Pocock - Used 1X450mm Bolt | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 296 | 293 | 19045 | 0.058171 | 0.00019854 | 2014-05-06 | C | 0.058172 | 0.00019854 | 2015 | 2014-05-06 | C | 65 | 0.058171 | 0.00019854
1 | 140494 | 2014-05-06 09:12 | 2014-05-06 14:52 | 340 | 6 | 2040 | 0.006231 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Line Down Reported by Public - Isolated at Fuses 7318 - Line Repaired & returned to service - Attended by Ben Taylor & Gavin Pagett - Used 2x Sleeves and 10mt of Conductor (under a Span) | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 340 | 337 | 2022 | 0.006176 | 1.8327e-05 | 2014-05-06 | C | 0.006176 | 1.8327e-05 | 2015 | 2014-05-06 | C | 6 | 0.006176 | 1.8327e-05
1 | 140495 | 2014-05-06 21:00 | 2014-05-07 00:21 | 201 | 80 | 10668 | 0.032585 | 0.00024435 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT TREE CONTACT | UNKNOWN | Unknown Cause - RS C281 tripped L/O - No fault found while sectionalising - Attended by Adam Whale & Lucus Grant. Faultman to check line again in day light. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 133.35 | 130.35 | 10428 | 0.031852 | 0.00024435 | 2014-05-06 | C | 0.031852 | 0.00024435 | 2015 | 2014-05-06 | C | 80 | 0.031852 | 0.00024435
1 | 140496 | 2014-05-06 20:48 | 2014-05-06 22:32 | 104 | 287 | 29848 | 0.091168 | 0.00087662 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | Defective Component - Floating conductor found at Links I10 as part of Dispatch job - Isolated at ABS's XT45, XT56, I1 and Links I3 - floater repaired and circuit returned to service - Attended by Robin Smith - Used 1X connector & 1mt conductor. | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 104 | 101 | 28987 | 0.088539 | 0.00087662 | 2014-05-06 | C | 0.088539 | 0.00087662 | 2015 | 2014-05-06 | C | 287 | 0.088539 | 0.00087662
1 | 140499 | 2014-05-06 10:23 | 2014-05-06 11:17 | 54 | 783 | 42282 | 0.12915 | 0.0023916 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB23 Tripped O/C & HLT fast das treetrimmer working near lines - No Fault found - attended by Jeff Roberts & Anjay Prasad. See FR 140501 for outage on Rongotea feeder as CB23 was feeding part of this feeder at the time of the outage. Resto | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 39933 | 0.12197 | 0.0023916 | 2014-05-06 | C | 0.12197 | 0.0023916 | 2015 | 2014-05-06 | C | 783 | 0.12197 | 0.0023916
1 | 140500 | 2014-05-06 09:46 | 2014-05-06 17:10 | 444 | 250 | 21596 | 0.065963 | 0.00076361 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | Wind -SS C639 found tripped by faultman attending no power faults. SS C639 reclosed successfully and patrol carried out with a broken transformer pole found. Work area isolated at ABS S562 and pole was replaced. Work area relivened ok, but note that some | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 86.384 | 83.384 | 20846 | 0.063673 | 0.00076361 | 2014-05-06 | C | 0.063673 | 0.00076361 | 2015 | 2014-05-06 | C | 250 | 0.063673 | 0.00076361
1 | 140501 | 2014-05-06 10:23 | 2014-05-06 11:17 | 54 | 272 | 14688 | 0.044863 | 0.0008308 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause -Kairanga CB23 Tripped O/C & HLT fast due to treetrimmer working near lines - No Fault found - attended by Jeff Roberts & Anjay Prasad. Kairanga CB23 was supplying part of Sanson Sub - Rongotea feeder at the time. See 140499 for outage on Ta | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 13872 | 0.042371 | 0.0008308 | 2014-05-06 | C | 0.042371 | 0.0008308 | 2015 | 2014-05-06 | C | 272 | 0.042371 | 0.0008308
1 | 140503 | 2014-05-07 09:30 | 2014-05-07 09:50 | 20 | 3 | 60 | 0.00018327 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | Defective Component - Found jumper broken at ABS IC 1088. Open ABS IC 1088 and carried out repair with LLP 144344. | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 20 | 17 | 51 | 0.00015578 | 9.1633e-06 | 2014-05-07 | C | 0.00015578 | 9.163e-06 | 2015 | 2014-05-07 | C | 3 | 0.00015578 | 9.1633e-06
1 | 140504 | 2014-05-07 09:30 | 2014-05-07 10:38 | 68 | 163 | 11084 | 0.033855 | 0.00049787 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91640 - Replace 11kV pole S0511. Isolation points: 11kV ABS IC2628 & 392. Job was cancelled following initial shutdown when a complaint was received from Thames Timber as they had not realised the extent of the outage when they received shutdown n | F1/F4 | KOPU | MATATOKI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 10595 | 0.032362 | 0.00049787 | 2014-05-07 | B | 0.016181 | 0.00024894 | 2015 | 2014-05-07 | B | 163 | 0.032362 | 0.00049787
1 | 140507 | 2014-05-07 12:30 | 2014-05-07 14:49 | 139 | 2 | 278 | 0.00084913 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Found fuse blowen at fuses SF7-015 patrolled line & found line down. Isolated at fuses SF7-015 and repaired line & replaced cross arm. Relivened | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 139 | 136 | 272 | 0.0008308 | 6.1088e-06 | 2014-05-07 | C | 0.0008308 | 6.109e-06 | 2015 | 2014-05-07 | C | 2 | 0.0008308 | 6.1088e-06
1 | 140508 | 2014-05-07 09:00 | 2014-05-07 15:28 | 388 | 75 | 29100 | 0.088884 | 0.00022908 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90753 - Install & commission new11kV CCC Sw/Gear 9795 between existing Sw/Gear 9437/3 and 9438/1. Liven and commission new CFC RMU's 9796 and 9808 connected to Sw/gear 9795/2. Commission new Transformers (TP2618) and (TP2623). Isolation points: 1 | F2 | MALEME EXPRESS | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 388 | 385 | 28875 | 0.088196 | 0.00022908 | 2014-05-07 | B | 0.044098 | 0.00011454 | 2015 | 2014-05-07 | B | 75 | 0.088196 | 0.00022908
1 | 140511 | 2014-05-07 09:56 | 2014-05-07 14:45 | 289 | 77 | 22253 | 0.06797 | 0.00023519 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/89349 - Repair TX T2180 and replace/repair switchgear panels. Isolation points: 11kV Links 6696, Links 6717, Sw/Gear 6702/1, Sw/Gear 6702/3, fuse switch 6702/2 Note: Switchgear 6702 replaced due to severe corrosion. | F3 | OPUNAKE | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 289 | 286 | 22022 | 0.067265 | 0.00023519 | 2014-05-07 | B | 0.033632 | 0.0001176 | 2015 | 2014-05-07 | B | 77 | 0.067265 | 0.00023519
1 | 140513 | 2014-05-07 15:22 | 2014-05-07 17:44 | 142 | 783 | 38093 | 0.11635 | 0.0023916 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Trees - CB 23 A/R, L/O, E/F. Faultman dispatched to sectionalise and patrol. Fault determined to be between ABS B4 and B7 when comms went down to Taikorea Sub. It therefore became more prudent to patrol between these points, as opposed to sectionalising. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 48.6501 | 45.6501 | 35744 | 0.10918 | 0.0023916 | 2014-05-07 | C | 0.10918 | 0.0023916 | 2015 | 2014-05-07 | C | 783 | 0.10918 | 0.0023916
1 | 140514 | 2014-05-07 21:50 | 2014-05-08 01:01 | 191 | 27 | 5157 | 0.015752 | 8.2469e-05 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Report of car v pole on Horrell Rd - pole IO051 found damaged - 11kV line isolated at ABS 604, IC653 & 595 to replace pole - all supply restored following replacement - NDR number 18658 - Steve Martin attended. Material required. 2 x single crossarms. 3 x | F4 | HORRELLS RD | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 191 | 188 | 5076 | 0.015504 | 8.2469e-05 | 2014-05-07 | C | 0.015504 | 8.2469e-05 | 2015 | 2014-05-07 | C | 27 | 0.015504 | 8.2469e-05
1 | 140516 | 2014-05-08 09:42 | 2014-05-08 14:45 | 303 | 13 | 3939 | 0.012031 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | UNKNOWN | SIN: 14/90918 - To replace 11kV hardware beyond 11kV Fuse FP1347 , not able to be completed LL. Isolation points: 11kV Fuse FP1347. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 303 | 300 | 3900 | 0.011912 | 3.9708e-05 | 2014-05-08 | B | 0.0059561 | 1.9854e-05 | 2015 | 2014-05-08 | B | 13 | 0.011912 | 3.9708e-05
1 | 140519 | 2014-05-07 05:00 | 2014-05-08 01:01 | 1201 | 350 | 40640 | 0.12413 | 0.001069 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90914 - AP1: Disconnect 11kV cable from source B of TC3727, disconnect 11kV cable from source A of TC3711 and connect temp generator to LV from in TC3573. AP2: Replace Series 1 SD3 w/ Safelink CFC unit, switch IC1996 to be automated. TP1: Test eac | F3 | RAWHITI AVE | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 116.1143 | 113.1143 | 39590 | 0.12092 | 0.001069 | 2014-05-07 | B | 0.060462 | 0.00053452 | 2015 | 2014-05-07 | B | 350 | 0.12092 | 0.001069
1 | 140521 | 2014-05-09 02:42 | 2014-05-09 02:57 | 15 | 2176 | 27288 | 0.083349 | 0.0066464 | No Power | 33000 | Unplanned | Zone Sub Equip. | UNKNOWN | NO FAULT FOUND | CIRCUIT BREAKER | Lightning - at 02:42 Huirangi GXP CB 1342 and Motukawa CB 210 tripped on O/C time. Lightning in the area at the time. Loss of Supply to Waitara East Sub & McKee Sub. Waitara East Sub Restored from Pohokura 3180/5. at 02:54 CB U20 & U30 Restored. At 02:57 | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 12.5404 | 9.5404 | 20760 | 0.06341 | 0.0066464 | 2014-05-09 | C | 0.06341 | 0.0066464 | 2015 | 2014-05-09 | C | 2176 | 0.06341 | 0.0066464
1 | 140522 | 2014-05-09 02:42 | 2014-05-09 04:57 | 135 | 154 | 20790 | 0.063501 | 0.00047038 | No Power | 33000 | Unplanned | Zone Sub Equip. | UNKNOWN | NO FAULT FOUND | CIRCUIT BREAKER | Lightning - Huirangi GXP CB 1342 and Motukawa CB 210 tripped on O/C time. Lightning in the area at the time. | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 20328 | 0.06209 | 0.00047038 | 2014-05-09 | C | 0.06209 | 0.00047038 | 2015 | 2014-05-09 | C | 154 | 0.06209 | 0.00047038
1 | 140523 | 2014-05-09 10:35 | 2014-05-09 13:00 | 145 | 4 | 580 | 0.0017716 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90338 - Replace 11kV & 400V arms on pole M12563 (TC3492).Isolation points 11kV Fuse FC1579. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 145 | 142 | 568 | 0.0017349 | 1.2218e-05 | 2014-05-09 | B | 0.00086746 | 6.109e-06 | 2015 | 2014-05-09 | B | 4 | 0.0017349 | 1.2218e-05
1 | 140525 | 2014-05-09 13:50 | 2014-05-09 15:19 | 89 | 2 | 178 | 0.00054369 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component -Faultman found a loose jumper on the drop out fuses on transformer TE7062, line was isolated at Fuses FP 891 to repair the jumper to the fuse holder. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 89 | 86 | 172 | 0.00052536 | 6.1088e-06 | 2014-05-09 | C | 0.00052536 | 6.109e-06 | 2015 | 2014-05-09 | C | 2 | 0.00052536 | 6.1088e-06
1 | 140530 | 2014-05-08 09:40 | 2014-05-08 14:47 | 307 | 26 | 7982 | 0.02438 | 7.9415e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91427 - Replace hardwood TX pole P10330 T8/235 w/ new 11m busck pole and replace one span of 11kV conductor. Plus reinstall 10m busck pole 362080 which was washed out on the 17.12.2013. Isolation points: Fuses S11 | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 307 | 304 | 7904 | 0.024142 | 7.9415e-05 | 2014-05-08 | B | 0.012071 | 3.9708e-05 | 2015 | 2014-05-08 | B | 26 | 0.024142 | 7.9415e-05
1 | 140531 | 2014-05-08 10:18 | 2014-05-08 14:10 | 232 | 35 | 8120 | 0.024802 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91644 - Replace 11kV TX structure N3260 at pole 712722 . Isolation points: 11kV ABS NG341, ABS NG310, ABS NG343. | F4/F1 | SOUTH RD NGARIKI | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 232 | 229 | 8015 | 0.024481 | 0.0001069 | 2014-05-08 | B | 0.012241 | 5.3452e-05 | 2015 | 2014-05-08 | B | 35 | 0.024481 | 0.0001069
1 | 140534 | 2014-05-09 17:42 | 2014-05-09 18:09 | 27 | 122 | 3294 | 0.010061 | 0.00037264 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -CB 6722 A/R, L/O, No flags. With no calls received from public a successful close of CB 6722 was carried out. No fault found. Attended by Kaine MacKay | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 2928 | 0.0089434 | 0.00037264 | 2014-05-09 | C | 0.0089434 | 0.00037264 | 2015 | 2014-05-09 | C | 122 | 0.0089434 | 0.00037264
1 | 140535 | 2014-05-09 18:30 | 2014-05-09 22:02 | 212 | 3 | 636 | 0.0019426 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning -Faultman investigating No Power complaints found Transformer P1060 blown and requiring replacement. Work area isolated at Fuses PU250 and transformer replaced. Materials used: 50kVA 3 phase transformer. Attended by Craig Wellington. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 212 | 209 | 627 | 0.0019151 | 9.1633e-06 | 2014-05-09 | C | 0.0019151 | 9.163e-06 | 2015 | 2014-05-09 | C | 3 | 0.0019151 | 9.1633e-06
1 | 140536 | 2014-05-09 11:30 | 2014-05-09 13:15 | 105 | 1 | 105 | 0.00032071 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component -Urgent replacement of extremely corroded transformer T1345 required. Isolated at dedicated HV fuses and transformer replaced. Attended by Adam Whale. Materials used: 15kVA single phase transformer. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 102 | 0.00031155 | 3.0544e-06 | 2014-05-09 | C | 0.00031155 | 3.054e-06 | 2015 | 2014-05-09 | C | 1 | 0.00031155 | 3.0544e-06
1 | 140538 | 2014-05-10 00:42 | 2014-05-10 00:57 | 15 | 301 | 4515 | 0.013791 | 0.00091938 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | Unknown Cause - Recloser 9168 L/O O/C Reclosed Not Patrolled | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 3612 | 0.011033 | 0.00091938 | 2014-05-10 | C | 0.011033 | 0.00091938 | 2015 | 2014-05-10 | C | 301 | 0.011033 | 0.00091938
1 | 140539 | 2014-05-09 16:00 | 2014-05-09 20:10 | 250 | 6 | 1500 | 0.0045816 | 1.8327e-05 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning - Faultman investigating No Power complaints found Transformer 4245 faulty and requiring replacement. Transformer isolated at dedicated fuses and replaced. Materials used: 30kVA 3 phase transformer and 3x LV fuses complete. Attended by Craig Wel | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 1482 | 0.0045267 | 1.8327e-05 | 2014-05-09 | C | 0.0045267 | 1.8327e-05 | 2015 | 2014-05-09 | C | 6 | 0.0045267 | 1.8327e-05
1 | 140540 | 2014-05-07 17:07 | 2014-05-08 08:45 | 938 | 65 | 15713 | 0.047994 | 0.00019854 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Wind -RS V5 A/R, L/O, O/C, E/F. Faultmen dispatched to sectionalise and patrol found that the fault was beyond fuses V9. V9 left open overnight due to weather and rough terrain and faultman returned next morning to patrol. Floating conductor found at Pole | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 241.7385 | 238.7385 | 15518 | 0.047399 | 0.00019854 | 2014-05-07 | C | 0.047399 | 0.00019854 | 2015 | 2014-05-07 | C | 65 | 0.047399 | 0.00019854
1 | 140543 | 2014-05-10 12:15 | 2014-05-10 14:15 | 120 | 2 | 360 | 0.0010996 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92104 - 11kV TX TC6015 is leaking oil and there is no oil left in the site glass. TX is a dedicated supply but it is group fused w/ TC2880, which is also a dedicated supply. Isolation points: 11kV Sw/Gear Fuse FC5007. | F1/F3 | LOMOND AVE | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 354 | 0.0010813 | 6.1088e-06 | 2014-05-10 | B | 0.00054063 | 3.054e-06 | 2015 | 2014-05-10 | B | 2 | 0.0010813 | 6.1088e-06
1 | 140544 | 2014-05-10 14:17 | 2014-05-10 14:58 | 41 | 39 | 1599 | 0.004884 | 0.00011912 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Emergency switching to repair blown jumper at pole 228951. Isolation between ABS SF7 028 & ABS SF7 035 with back feed via Sectionaliser 9679. Jumper repaired, all service restored, Dave Ngatai & Paul Cooper attended. Materials 1 x H/ | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 41 | 38 | 1482 | 0.0045267 | 0.00011912 | 2014-05-10 | C | 0.0045267 | 0.00011912 | 2015 | 2014-05-10 | C | 39 | 0.0045267 | 0.00011912
1 | 140545 | 2014-05-10 10:31 | 2014-05-10 14:27 | 236 | 632 | 93582 | 0.28584 | 0.0019304 | No Power | 33000 | Unplanned | Zone Sub Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CIRCUIT BREAKER | Other/miscellaneous cause -TP_Mangamaire CB 1332 auto reclosed on on E/F flags and Pongaroa CB XT 30 tripped on E/F flags resulting in LOS to Pongaroa Substation. Faultman carried out inspection at substation and one fault was found, supply to transforme | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 148.0728 | 145.0728 | 91686 | 0.28005 | 0.0019304 | 2014-05-10 | C | 0.28005 | 0.0019304 | 2015 | 2014-05-10 | C | 632 | 0.28005 | 0.0019304
1 | 140546 | 2014-05-10 16:49 | 2014-05-10 19:00 | 131 | 3 | 393 | 0.0012004 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | Trees - Received a call from customer of lines down, faultman found tree through the line at pole 743438 after the customer had cut it down, line was Isolated at Fuses 8193 to repair the lines. Chris Viviers attended. NDR 38910. | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 131 | 128 | 384 | 0.0011729 | 9.1633e-06 | 2014-05-10 | C | 0.0011729 | 9.163e-06 | 2015 | 2014-05-10 | C | 3 | 0.0011729 | 9.1633e-06
1 | 140547 | 2014-05-10 16:45 | 2014-05-10 19:31 | 166 | 7 | 1162 | 0.0035492 | 2.1381e-05 | No Power | 11000 | Unplanned | Underground Cable | UNKNOWN | PATROLLED | CABLE | Unknown Cause - Found fuse blown at SE4-008. Found no cause on O/H line. Isolated at fuses SE4-016 replace fuse SE4-008. Tested cables & found no fault. Relivened. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 166 | 163 | 1141 | 0.0034851 | 2.1381e-05 | 2014-05-10 | C | 0.0034851 | 2.1381e-05 | 2015 | 2014-05-10 | C | 7 | 0.0034851 | 2.1381e-05
1 | 140552 | 2014-05-11 09:15 | 2014-05-11 12:30 | 195 | 8 | 1560 | 0.0047649 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | FUSE | SIN: 14/91692 - Replace LV rack on the back of 11kV transformer 1984N for a new 6 way rack. Isolation points: 11kV Fuse 6995 | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 1536 | 0.0046916 | 2.4435e-05 | 2014-05-11 | B | 0.0023458 | 1.2218e-05 | 2015 | 2014-05-11 | B | 8 | 0.0046916 | 2.4435e-05
1 | 140553 | 2014-05-11 16:00 | 2014-05-11 16:29 | 29 | 5 | 129 | 0.00039402 | 1.5272e-05 | No Power | 11000 | Unplanned | Distribution Equip. | UNKNOWN | PATROLLED | SWITCHGEAR - UG | Defective Component - Fuses on Sw/Gear found tripped at 233. (Supplies Helwan army camp at Waiouru). Unable to open Sw/Gear to access fuses. Discussed with S.Bullock to investigate during daylight hours. (Customer advised). 3 x 50 amp fuses repair place i | F3/F4 | RUAPEHU | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 25.8 | 22.8 | 114 | 0.0003482 | 1.5272e-05 | 2014-05-11 | C | 0.0003482 | 1.5272e-05 | 2015 | 2014-05-11 | C | 5 | 0.0003482 | 1.5272e-05
1 | 140554 | 2014-05-11 17:16 | 2014-05-11 17:58 | 42 | 26 | 1092 | 0.0033354 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Tripping on fuses 774 caused by a line down on Marahau Rd. Isolation from those fuses with the line jointed OK and relivened. (Conductor in deteriorated condition). | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 1014 | 0.0030972 | 7.9415e-05 | 2014-05-11 | C | 0.0030972 | 7.9415e-05 | 2015 | 2014-05-11 | C | 26 | 0.0030972 | 7.9415e-05
1 | 140557 | 2014-05-11 09:20 | 2014-05-11 10:04 | 44 | 1 | 44 | 0.00013439 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - OH | WA: 14/92135 - LTOS oil switches 6791/1, 6791/2, 6791/3, 6791/5. Isolation points: 11kV Links 4953 | F1 | BELL BLOCK 3 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 44 | 41 | 41 | 0.00012523 | 3.0544e-06 | 2014-05-11 | B | 6.2616e-05 | 1.527e-06 | 2015 | 2014-05-11 | B | 1 | 0.00012523 | 3.0544e-06
1 | 140561 | 2014-05-09 10:52 | 2014-05-09 13:04 | 132 | 15 | 1980 | 0.0060478 | 4.5816e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91992 - CANCELLED - Not picked up. Isolation required to enable cutting of trees near overhead lines. Isolation points:11kV ABS IC280 | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 132 | 129 | 1935 | 0.0059103 | 4.5816e-05 | 2014-05-09 | B | 0.0029552 | 2.2908e-05 | 2015 | 2014-05-09 | B | 15 | 0.0059103 | 4.5816e-05
1 | 140562 | 2014-05-02 12:03 | 2014-05-02 12:14 | 11 | 1183 | 13013 | 0.039747 | 0.0036134 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | Employee error - Tripping on MTN CB1132 causing loss of supply to both Arahina (See Out/Def 140439) and Rata Subs (Out/Def 140562)Trip caused by HiAb truck boom coming into contact with 33kV line while changing crossarms on Pukepapa Rd. Live Line procedur | F2 | MARTON | ARAHINA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 11 | 8 | 9464 | 0.028907 | 0.0036134 | 2014-05-02 | C | 0.028907 | 0.0036134 | 2015 | 2014-05-02 | C | 1183 | 0.028907 | 0.0036134
1 | 140564 | 2014-05-12 11:17 | 2014-05-12 14:53 | 216 | 105 | 8600 | 0.026268 | 0.00032071 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - Recloser 6610 tripped on E/F flags, received a call of a car vs pole. Faultman found car had hit pole 742544, line was isolated at ABS's 45 and 327 to replace the pole. Neal Woodhead attended. NDR:45854 | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 81.9048 | 78.9048 | 8285 | 0.025306 | 0.00032071 | 2014-05-12 | C | 0.025306 | 0.00032071 | 2015 | 2014-05-12 | C | 105 | 0.025306 | 0.00032071
1 | 140566 | 2014-05-12 12:33 | 2014-05-12 13:45 | 72 | 11 | 792 | 0.0024191 | 3.3599e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component - faultman found a broken fuse holders on transformer T5095, line was isolated at Fuses TA 805 to replace all 3 Fuses holders on transformer T5095 at pole 714869. Brett Bensley attended. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 759 | 0.0023183 | 3.3599e-05 | 2014-05-12 | C | 0.0023183 | 3.3599e-05 | 2015 | 2014-05-12 | C | 11 | 0.0023183 | 3.3599e-05
1 | 140567 | 2014-05-12 14:52 | 2014-05-12 18:02 | 190 | 553 | 105070 | 0.32093 | 0.0016891 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | REGULATOR | SIN: 14/91816 - Connect new regulator #2 HV cables to S714 and S769 (to complete this safely, disconnectors require isolating both sides of them). Isolation points: 11kV ABS S714, ABS S769, ABS S712, ABS S15, ABS S709, ABS S16, ABS S710, ABS S768, ABS S10 | F1,F2,F3 | Not entered | Not entered | Not entered | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 190 | 187 | 103411 | 0.31586 | 0.0016891 | 2014-05-12 | B | 0.15793 | 0.00084455 | 2015 | 2014-05-12 | B | 553 | 0.31586 | 0.0016891
1 | 140568 | 2014-05-13 03:29 | 2014-05-13 04:33 | 64 | 857 | 45405 | 0.13869 | 0.0026176 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - Tripping on CB7 on Phase A-B O/C. Feeder patrolled / sectionalised but nothing found. Relivened OK. | F2/F3 | WANGANUI EAST | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 52.9813 | 49.9813 | 42834 | 0.13083 | 0.0026176 | 2014-05-13 | C | 0.13083 | 0.0026176 | 2015 | 2014-05-13 | C | 857 | 0.13083 | 0.0026176
1 | 140569 | 2014-05-13 06:41 | 2014-05-13 12:58 | 377 | 118 | 13903 | 0.042466 | 0.00036042 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - at 06:27, Putaruru Sub, CB 3 Taumangi Rd Feeder, Recloser RC36 Tripped, Ph A & B O/C, Auto Reclosed. At 06:41, Recloser RC36 Tripped, E/F O/C, E/F, L/O. Investigation began and faultman dispatched. Faultman had a call from member of public that a | F4 | TAUMANGI RD | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 117.822 | 114.822 | 13549 | 0.041384 | 0.00036042 | 2014-05-13 | C | 0.041384 | 0.00036042 | 2015 | 2014-05-13 | C | 118 | 0.041384 | 0.00036042
1 | 140570 | 2014-05-12 10:08 | 2014-05-12 14:40 | 272 | 28 | 7616 | 0.023262 | 8.5524e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91683 - Offload TX T2/845, make gap P43527, replace 11kV ABS pole A91 and ABS P43523, replace P43522 and install new ABS 10200 for future work, close gap. Isolation points: gap at P43527, B14, B43, B3 Associated LLPs 14/91684, 14/91685 | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 272 | 269 | 7532 | 0.023006 | 8.5524e-05 | 2014-05-12 | B | 0.011503 | 4.2762e-05 | 2015 | 2014-05-12 | B | 28 | 0.023006 | 8.5524e-05
1 | 140572 | 2014-05-13 09:15 | 2014-05-13 10:52 | 97 | 1 | 97 | 0.00029628 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91693 - Replace 11kV pole. Isolation points: D8 fuses | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 97 | 94 | 94 | 0.00028712 | 3.0544e-06 | 2014-05-13 | B | 0.00014356 | 1.527e-06 | 2015 | 2014-05-13 | B | 1 | 0.00028712 | 3.0544e-06
1 | 140573 | 2014-05-13 10:02 | 2014-05-13 12:30 | 148 | 69 | 10212 | 0.031192 | 0.00021076 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90756 - Replace 11kV G/M Transformer TC4933. Isolation point: 11kV Fuses FP1591 | F3 | ACHILLES AVE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 148 | 145 | 10005 | 0.03056 | 0.00021076 | 2014-05-13 | B | 0.01528 | 0.00010538 | 2015 | 2014-05-13 | B | 69 | 0.03056 | 0.00021076
1 | 140574 | 2014-05-13 09:50 | 2014-05-13 13:30 | 220 | 5 | 1100 | 0.0033599 | 1.5272e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - at 09:50, Pongakawa Sub, CB 1 Tainui Feeder. Found Transformer TE7-048 needed LV Crossarms to be replaced. Faultman requested to Isolate at 11kV Fuses for work on LV crossarms. On isolating TE7-048 at it's associated fuses, 1x DDO be | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 220 | 217 | 1085 | 0.003314 | 1.5272e-05 | 2014-05-13 | C | 0.003314 | 1.5272e-05 | 2015 | 2014-05-13 | C | 5 | 0.003314 | 1.5272e-05
1 | 140575 | 2014-05-13 09:30 | 2014-05-13 14:20 | 290 | 35 | 10150 | 0.031002 | 0.0001069 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91694 - Install 3x new DDOs, move switch 6510 to pole 759044. Remove single span of LV. Install new 30kVA TX 2223N w/ new single LV termination and 3 mtr arms using existing DDOs. Isolation points: 11kV ABS 511, Oakura sub 8850/6 | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 290 | 287 | 10045 | 0.030682 | 0.0001069 | 2014-05-13 | B | 0.015341 | 5.3452e-05 | 2015 | 2014-05-13 | B | 35 | 0.030682 | 0.0001069
1 | 140576 | 2014-05-13 08:30 | 2014-05-13 14:57 | 387 | 23 | 8901 | 0.027187 | 7.0252e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91343 - Replacing HV/LV poles along Beamish Rd from Santoft Rd to the end. Isolation points: Fuse 887 | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 387 | 384 | 8832 | 0.026977 | 7.0252e-05 | 2014-05-13 | B | 0.013488 | 3.5126e-05 | 2015 | 2014-05-13 | B | 23 | 0.026977 | 7.0252e-05
1 | 140578 | 2014-05-13 09:41 | 2014-05-13 15:03 | 322 | 30 | 9660 | 0.029506 | 9.1633e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90037 - Replace 11kV pole, Xarms hardware at various sites in outage area. Install 11kV TEMP62 DOFs on pole E0328. Isolation points: 11kV ABS 1105 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 322 | 319 | 9570 | 0.029231 | 9.1633e-05 | 2014-05-13 | B | 0.014615 | 4.5816e-05 | 2015 | 2014-05-13 | B | 30 | 0.029231 | 9.1633e-05
1 | 140581 | 2014-05-13 17:33 | 2014-05-13 17:42 | 9 | 2 | 18 | 5.498e-05 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - UG | WA: 14/92136 - LTOS oil switches. Isolation points: 11kV fuse switch 230/1 | F3 | CITY 3 | CITY SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 12 | 3.6653e-05 | 6.1088e-06 | 2014-05-13 | B | 1.8327e-05 | 3.054e-06 | 2015 | 2014-05-13 | B | 2 | 3.6653e-05 | 6.1088e-06
1 | 140583 | 2014-05-13 18:48 | 2014-05-13 19:30 | 42 | 58 | 2436 | 0.0074406 | 0.00017716 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | No Power - Thames CB 1 No Trip. Broken Jumper feeding transformer TC5592. Isolation at Fuses FC4111 no back feeds available. Faultman Kim Lambert. Materials: to come | F3 | ROLLESTON ST | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 2262 | 0.0069091 | 0.00017716 | 2014-05-13 | C | 0.0069091 | 0.00017716 | 2015 | 2014-05-13 | C | 58 | 0.0069091 | 0.00017716
1 | 140586 | 2014-05-13 07:37 | 2014-05-13 09:24 | 107 | 822 | 87954 | 0.26865 | 0.0025107 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Stratford CB 2862 tripped on O/C and L/O. Line patrolled and LFI flashing. Line down found at pole 738721 and broken insulator at pole 738713 on Kaponga 33kV line. Phil Webby atttended. See outdef 140587 for outage affecting Cardiff Substation. | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 107 | 104 | 85488 | 0.26112 | 0.0025107 | 2014-05-13 | C | 0.26112 | 0.0025107 | 2015 | 2014-05-13 | C | 822 | 0.26112 | 0.0025107
1 | 140587 | 2014-05-13 07:37 | 2014-05-13 10:29 | 172 | 514 | 82440 | 0.25181 | 0.00157 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | No Power - Stratford CB 2862 tripped on O/C and L/O. Line patrolled and LFI's operated. Line down found at pole 738721 due to bird strike. Also a broken insulator at pole 738713 replaced. Kaponga back fed on alternate 33kV line. Cardiff back fed via 11kV | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 160.3891 | 157.3891 | 80898 | 0.2471 | 0.00157 | 2014-05-13 | C | 0.2471 | 0.00157 | 2015 | 2014-05-13 | C | 514 | 0.2471 | 0.00157
1 | 140588 | 2014-05-14 08:39 | 2014-05-14 10:11 | 92 | 1 | 92 | 0.00028101 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | LIGHTNING | LIGHTNING | INSULATOR | No Power - Fuses for Transformer 1319 found blown. (Lightning in area at time). Need new Fuses, Polymas & H/T Insulator. Isolation point ABS 419 & ABS 141. No Back feeds. Replaced 3X DDOs, 3x Polymas,1 x H/T Insulator. Brent Moreatti attended. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 92 | 89 | 89 | 0.00027184 | 3.0544e-06 | 2014-05-14 | C | 0.00027184 | 3.054e-06 | 2015 | 2014-05-14 | C | 1 | 0.00027184 | 3.0544e-06
1 | 140590 | 2014-05-13 09:00 | 2014-05-13 13:10 | 250 | 26 | 6500 | 0.019854 | 7.9415e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91324 - Replace red tagged larch pole and burnt of S/W pole P04542 and P22994. Isolation points: Fuses V66 Replaces SIS 14/90676 | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 6422 | 0.019616 | 7.9415e-05 | 2014-05-13 | B | 0.0098078 | 3.9708e-05 | 2015 | 2014-05-13 | B | 26 | 0.019616 | 7.9415e-05
1 | 140593 | 2014-05-14 14:15 | 2014-05-14 16:24 | 129 | 2 | 258 | 0.00078804 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component - at 14:15, Paeroa Sub, CB 5 Bennett. Found transformer TP1663 had blown. Isolated at Fuses FP940. Permit Issued & Repairs carried out. All power restored on completion. Brian Fisher Attended. 1x Transformer Replaced 1x Crossarm Replac | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 129 | 126 | 252 | 0.00076971 | 6.1088e-06 | 2014-05-14 | C | 0.00076972 | 6.109e-06 | 2015 | 2014-05-14 | C | 2 | 0.00076971 | 6.1088e-06
1 | 140594 | 2014-05-14 09:18 | 2014-05-14 15:45 | 387 | 80 | 30960 | 0.094565 | 0.00024435 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90757 - Replace 11kV G/M Transformer TC3938. Isolation point: 11kV Fuses FP1592 | F3 | ACHILLES AVE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 387 | 384 | 30720 | 0.093832 | 0.00024435 | 2014-05-14 | B | 0.046916 | 0.00012218 | 2015 | 2014-05-14 | B | 80 | 0.093832 | 0.00024435
1 | 140595 | 2014-05-14 09:12 | 2014-05-14 15:28 | 376 | 130 | 48880 | 0.1493 | 0.00039708 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | RECLOSER | SIN: 14/91716 - Install termination X-arm at pole 854121 and new Recloser 9787. Recloser left bypassed by ABS 9787/1. Isolation points: 11kV ABS IC328 | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 376 | 373 | 48490 | 0.14811 | 0.00039708 | 2014-05-14 | B | 0.074055 | 0.00019854 | 2015 | 2014-05-14 | B | 130 | 0.14811 | 0.00039708
1 | 140596 | 2014-05-14 09:00 | 2014-05-14 15:58 | 418 | 343 | 59638 | 0.18216 | 0.0010477 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/91128 - STAGED RESTORATION. (CB4 Pauanui and CB2 Pleasant Point). Replacing existing 11kV Safelink RMU IC1586/IC1552/IC1595 with new motorized Safelink with SCADA control. Isolation points: 11kV Sw/gear IC3244, 9682/4, 9057/3 and cables removed | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 173.8717 | 170.8717 | 58609 | 0.17902 | 0.0010477 | 2014-05-14 | B | 0.089508 | 0.00052383 | 2015 | 2014-05-14 | B | 343 | 0.17902 | 0.0010477
1 | 140597 | 2014-05-14 22:44 | 2014-05-14 23:50 | 66 | 96 | 6336 | 0.019353 | 0.00029322 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | SWITCHGEAR - UG | No Power - Tower Rd CB 4 No Trip. Transformer TC2752 isolated so that a LV Disconnector could be replaced due to Burn out. Isolation at Fuse/Sw FC2742 No Back feeds available. Repairs complete. Faultman Chris Brown & Jacob Joubert. Material 1 LV Disconnec | F2 | BURWOOD RD | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 66 | 63 | 6048 | 0.018473 | 0.00029322 | 2014-05-14 | C | 0.018473 | 0.00029322 | 2015 | 2014-05-14 | C | 96 | 0.018473 | 0.00029322
1 | 140599 | 2014-05-15 09:34 | 2014-05-15 12:30 | 176 | 2 | 390 | 0.0011912 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/92164 - Replace 11kV termination arm and install 11kV fuses FP1594 at pole F0940. 11kV TC3653 will need to be isolated at Transformer fuses prior to work starting on the arm replacement etc.Confirm Pre Commissioning & Inspection Certificate Comple | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 384 | 0.0011729 | 6.1088e-06 | 2014-05-15 | B | 0.00058645 | 3.054e-06 | 2015 | 2014-05-15 | B | 2 | 0.0011729 | 6.1088e-06
1 | 140601 | 2014-05-15 08:00 | 2014-05-15 11:50 | 230 | 2 | 460 | 0.001405 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Found transformer TC2651 fuses blowen. Retired and fuse blew. Isolated trany and replaced Relivened Own SIS & AP | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 230 | 227 | 454 | 0.0013867 | 6.1088e-06 | 2014-05-15 | C | 0.0013867 | 6.109e-06 | 2015 | 2014-05-15 | C | 2 | 0.0013867 | 6.1088e-06
1 | 140602 | 2014-05-15 09:30 | 2014-05-15 14:22 | 292 | 40 | 11680 | 0.035676 | 0.00012218 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/90944 - Replace 11kV TX 1257 w/ new 100kVA and all low voltage hanger arms. Isolation points:11kV Fuses 8377 | F3 | BROOKLANDS 8 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 292 | 289 | 11560 | 0.035309 | 0.00012218 | 2014-05-15 | B | 0.017655 | 6.1088e-05 | 2015 | 2014-05-15 | B | 40 | 0.035309 | 0.00012218
1 | 140603 | 2014-05-15 09:00 | 2014-05-15 14:51 | 351 | 4 | 1404 | 0.0042884 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90038 - Replace 11kV pole, Xarms hardware at various site in outage area. Isolation points: 11kV Fuses TEMP62. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 351 | 348 | 1392 | 0.0042518 | 1.2218e-05 | 2014-05-15 | B | 0.0021259 | 6.109e-06 | 2015 | 2014-05-15 | B | 4 | 0.0042518 | 1.2218e-05
1 | 140605 | 2014-05-14 16:27 | 2014-05-15 14:09 | 1302 | 106 | 96541 | 0.29488 | 0.00032377 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Recloser 2680 tripped O/C A B C Phase. Patrolled found nothing. After isolating all the transformers & putting back on 1 at a time found Transformer 1429W was faulty. Replaced transformer & livened on the 15-05-14. Pa Koro Attended on The 15th | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 910.7642 | 907.7642 | 96223 | 0.29391 | 0.00032377 | 2014-05-14 | C | 0.29391 | 0.00032377 | 2015 | 2014-05-14 | C | 106 | 0.29391 | 0.00032377
1 | 140606 | 2014-05-15 09:00 | 2014-05-15 16:50 | 470 | 61 | 28670 | 0.08757 | 0.00018632 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/92397 - Install new 11kV Safelink CFC Sw/gear 9770 between Sw/gear 9169/1 and IC2071. Connect existing Transformer TC3231 to Fuse/Sw 9770/2. Isolation points: 11kV Sw/gear 9169/1 & IC2071. Refer to 14/91129 for Advertising Only. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 470 | 467 | 28487 | 0.087011 | 0.00018632 | 2014-05-15 | B | 0.043506 | 9.316e-05 | 2015 | 2014-05-15 | B | 61 | 0.087011 | 0.00018632
1 | 140607 | 2014-05-15 15:42 | 2014-05-15 18:05 | 143 | 59 | 7271 | 0.022209 | 0.00018021 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | Accident - CB 6 L/O on O/C & E/F. Contractor Fulton Hogan working on CAC 35583 hit O/H lines breaking lines. Isolated between CB 6 & switch gear 9579/1. Backfeed rest of area. Repaired lines down on railway track & relivened. 2 spans of wire used. NDR343 | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 123.2373 | 120.2373 | 7094 | 0.021668 | 0.00018021 | 2014-05-15 | C | 0.021668 | 0.00018021 | 2015 | 2014-05-15 | C | 59 | 0.021668 | 0.00018021
1 | 140608 | 2014-05-16 00:57 | 2014-05-16 02:14 | 77 | 4 | 308 | 0.00094076 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Lines down found at Pole 726776 as part of dispatch job - Isolated at Fuses LI747. Lines repaired and returned to service - Attended by Kaine MacKay - Used 5 mtrs of conductor and 3 sleeves. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 77 | 74 | 296 | 0.00090411 | 1.2218e-05 | 2014-05-16 | C | 0.00090411 | 1.2218e-05 | 2015 | 2014-05-16 | C | 4 | 0.00090411 | 1.2218e-05
1 | 140609 | 2014-05-16 00:02 | 2014-05-16 04:18 | 256 | 139 | 27664 | 0.084498 | 0.00042456 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - RS 537 Tripped and Showed A/R due to Dispatch job. Later on it was found that RS 537 had not closed and power had been off since first Trip - Line found down between Poles 792948 & 792949 during sectionalising - Isolated at ABS 1066 | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 199.0216 | 196.0216 | 27247 | 0.083224 | 0.00042456 | 2014-05-16 | C | 0.083224 | 0.00042457 | 2015 | 2014-05-16 | C | 139 | 0.083224 | 0.00042456
1 | 140612 | 2014-05-16 11:23 | 2014-05-16 13:50 | 147 | 1 | 147 | 0.000449 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92261 - Replace TX T9/144, Glenora Rd. Isolation points: T9/144 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 147 | 144 | 144 | 0.00043984 | 3.0544e-06 | 2014-05-16 | B | 0.00021992 | 1.527e-06 | 2015 | 2014-05-16 | B | 1 | 0.00043984 | 3.0544e-06
1 | 140613 | 2014-05-15 08:51 | 2014-05-15 14:25 | 334 | 55 | 18370 | 0.05611 | 0.00016799 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91908 - Replace broken pole 825992 caused by MVA on 24.04.2014. Make LL break at pole 357008. At pole 830006 make LL break using GB technique. Replace pole 357008 under AP. Reconnect LL breaks at pole 357008. Reconnect LL break 830006 using GB tec | F3 | TOTARA ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 334 | 331 | 18205 | 0.055606 | 0.00016799 | 2014-05-15 | B | 0.027803 | 8.3997e-05 | 2015 | 2014-05-15 | B | 55 | 0.055606 | 0.00016799
1 | 140615 | 2014-05-09 09:38 | 2014-05-09 15:02 | 324 | 1 | 324 | 0.00098963 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91133 - Remove 6.6kV transformer and pad to replace ground/sawdust/sand w/ metal etc. This is due to TX and pad sinking in soft area. Contact person from Kaimata Sawmills is Rodney 027 271 7066. Isolation points: 6.6kV ABS 8654 | F3 | KAIMATA | INGLEWOOD SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 324 | 321 | 321 | 0.00098047 | 3.0544e-06 | 2014-05-09 | B | 0.00049023 | 1.527e-06 | 2015 | 2014-05-09 | B | 1 | 0.00098047 | 3.0544e-06
1 | 140616 | 2014-05-17 10:29 | 2014-05-17 10:58 | 29 | 1446 | 41934 | 0.12808 | 0.0044167 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | No Power - CB C838 Tripped O/C. Patrolled found 11kV wires twisted. (Third Party had been trying to cut branch and wires touched). Untwisted using hot stick. Reliven. OK. Brad Keating Attended. NDR 37915. Pole 817514. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 29 | 26 | 37596 | 0.11483 | 0.0044167 | 2014-05-17 | C | 0.11483 | 0.0044167 | 2015 | 2014-05-17 | C | 1446 | 0.11483 | 0.0044167
1 | 140617 | 2014-05-17 08:37 | 2014-05-17 14:00 | 323 | 999 | 84362 | 0.25768 | 0.0030514 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | SWITCHGEAR - UG | Defective Component - CB1 tripped A, B & C Ph O/C, E/F, L/O. Feeder sectionalised & faulty Sw/Gear 9531/1 found. Generator installed to supply transformer TP2111 while cables tested & Sw/Gear replaced. Sw/Gear replaced all service restored, Ted Glasgow, C | F3 | EVERSHAM RD | MATAPIHI SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 84.4464 | 81.4464 | 81365 | 0.24852 | 0.0030514 | 2014-05-17 | C | 0.24852 | 0.0030514 | 2015 | 2014-05-17 | C | 999 | 0.24852 | 0.0030514
1 | 140619 | 2014-05-17 18:11 | 2014-05-17 19:12 | 61 | 2 | 122 | 0.00037264 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | No Power - CB C947 Trip - Unknown Fault. Line Not patrolled. Neville Pope attended. | F4 | KOURARAU | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 61 | 58 | 116 | 0.00035431 | 6.1088e-06 | 2014-05-17 | C | 0.00035431 | 6.109e-06 | 2015 | 2014-05-17 | C | 2 | 0.00035431 | 6.1088e-06
1 | 140621 | 2014-05-18 05:39 | 2014-05-18 07:46 | 127 | 22 | 2794 | 0.0085341 | 6.7197e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91509 - Change oil on TX G55/2T (high moisture and acidity content). Isolation points: G55/T2 | F2 | MAIN ST 24 | MAIN ST SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 127 | 124 | 2728 | 0.0083325 | 6.7197e-05 | 2014-05-18 | B | 0.0041662 | 3.3599e-05 | 2015 | 2014-05-18 | B | 22 | 0.0083325 | 6.7197e-05
1 | 140624 | 2014-05-16 07:56 | 2014-05-16 09:42 | 106 | 427 | 39015 | 0.11917 | 0.0013042 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power - Tinui C937 tripped. No flags. No fault found. Feeder sectionalised and patrolled. During restoration CB937 tripped again and same sectionalising was undertaken. Jason Hall attended. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 91.37 | 88.37 | 37734 | 0.11526 | 0.0013042 | 2014-05-16 | C | 0.11526 | 0.0013042 | 2015 | 2014-05-16 | C | 427 | 0.11526 | 0.0013042
1 | 140625 | 2014-05-19 11:00 | 2014-05-19 11:30 | 30 | 9 | 270 | 0.00082469 | 2.749e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91861 - AP for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and HV fuses closed, relivening the TX up to the LV Disc-Connector. This is to be followed by a 400V shutdown to complete the 400V arm replacements. | F3/F4 | KAURI ST | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 243 | 0.00074222 | 2.749e-05 | 2014-05-19 | B | 0.00037111 | 1.3745e-05 | 2015 | 2014-05-19 | B | 9 | 0.00074222 | 2.749e-05
1 | 140626 | 2014-05-19 10:50 | 2014-05-19 12:50 | 120 | 6 | 720 | 0.0021992 | 1.8327e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91860 - AP is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the HV fuses closed. Relivening the TX up to the LV Disc-connector, to be followed by a 400V shutdown to completely the 400V arm replacements | F3/F4 | KAURI ST | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 702 | 0.0021442 | 1.8327e-05 | 2014-05-19 | B | 0.0010721 | 9.163e-06 | 2015 | 2014-05-19 | B | 6 | 0.0021442 | 1.8327e-05
1 | 140628 | 2014-05-19 10:50 | 2014-05-19 11:23 | 33 | 6249 | 206217 | 0.62987 | 0.019087 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB Z10 Trip, O/C B phase, Ground trip, Differential trip. This caused a complete outage to Kairanga Sub. Contractors were working in the sub at the time so sub equipment inspected and restoration attempted. This was unsuccessful due to the | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 33 | 30 | 187470 | 0.57261 | 0.019087 | 2014-05-19 | C | 0.57261 | 0.019087 | 2015 | 2014-05-19 | C | 6249 | 0.57261 | 0.019087
1 | 140629 | 2014-05-19 08:17 | 2014-05-19 14:20 | 363 | 1 | 363 | 0.0011088 | 3.0544e-06 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB W40, CB Z200 Trip at 08:17. Directional E/F, O/C A phase, Zone 1. This caused an outage to Tararua Wind Power North Wind Farm. The Windfarm was due to have a total outage for planned work beginning at 10:00am, so shutdown was started ea | F1,F2,F3 | TWP-KELVIN GROVE 33KV | TP_BUNNYTHORPE | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 363 | 360 | 360 | 0.0010996 | 3.0544e-06 | 2014-05-19 | C | 0.0010996 | 3.054e-06 | 2015 | 2014-05-19 | C | 1 | 0.0010996 | 3.0544e-06
1 | 140630 | 2014-05-19 14:44 | 2014-05-19 15:50 | 66 | 2193 | 44288 | 0.13527 | 0.0066984 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | BINDER | Accident - CB 12 Trip, E/F C Phase. Report came in of a truck having lost a tyre which came off truck hitting pole and causing binder to break and lines to clash. Work area was isolated at ABS 165 and the lines were rebound on to insulators. Relivened OK. | F3 | BROOKLANDS 12 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 20.1952 | 17.1952 | 37709 | 0.11518 | 0.0066984 | 2014-05-19 | C | 0.11518 | 0.0066984 | 2015 | 2014-05-19 | C | 2193 | 0.11518 | 0.0066984
1 | 140632 | 2014-05-19 10:25 | 2014-05-19 14:02 | 217 | 3 | 651 | 0.0019884 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91428 - Cut LL gap at pole P27250 and replace red tagged 11kV pole P11198, then close LL gap at pole P27250. Isolation points: LL gap at pole p27250 See LLP 14/91429 & 14/91993 | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 217 | 214 | 642 | 0.0019609 | 9.1633e-06 | 2014-05-19 | B | 0.00098047 | 4.582e-06 | 2015 | 2014-05-19 | B | 3 | 0.0019609 | 9.1633e-06
1 | 140634 | 2014-05-19 09:30 | 2014-05-19 15:42 | 372 | 1 | 372 | 0.0011362 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92335 - , Replacing 11kV pole 705174 and TX X1350. Isolation points: line break pole 705208 LLPs// | F3 | CARLTON | TAUPO QUAY SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 372 | 369 | 369 | 0.0011271 | 3.0544e-06 | 2014-05-19 | B | 0.00056354 | 1.527e-06 | 2015 | 2014-05-19 | B | 1 | 0.0011271 | 3.0544e-06
1 | 140635 | 2014-05-20 09:30 | 2014-05-20 11:00 | 90 | 5 | 450 | 0.0013745 | 1.5272e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91862 - AP is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be disconnected and the 11kV Transformer fuses closed, relivening the TX Up to the LV Disc-Connector. This is to be followed by a 400V shutdown to complete th | F3/F4 | KAURI ST | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 435 | 0.0013287 | 1.5272e-05 | 2014-05-20 | B | 0.00066434 | 7.636e-06 | 2015 | 2014-05-20 | B | 5 | 0.0013287 | 1.5272e-05
1 | 140637 | 2014-05-20 10:14 | 2014-05-20 11:45 | 91 | 7 | 637 | 0.0019457 | 2.1381e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91864 - AP is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the 11kV Transformer fuses closed, relivening the TX up to the LV Disc-Connector. This is to be followed by a 400V shutdown to complete the 4 | F3/F4 | KAURI ST | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 91 | 88 | 616 | 0.0018815 | 2.1381e-05 | 2014-05-20 | B | 0.00094076 | 1.069e-05 | 2015 | 2014-05-20 | B | 7 | 0.0018815 | 2.1381e-05
1 | 140638 | 2014-05-20 09:50 | 2014-05-20 10:05 | 15 | 7 | 105 | 0.00032071 | 2.1381e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91766 - Install LV fuses on existing pole mounted TX. TXs to be isoated via 11kV Transformer fuses and new LV disconnector to be fitted w/in the 1 hr HV shutdown. If required, an LV shutdown may be carried out after the HV is restored to complete | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 84 | 0.00025657 | 2.1381e-05 | 2014-05-20 | B | 0.00012829 | 1.069e-05 | 2015 | 2014-05-20 | B | 7 | 0.00025657 | 2.1381e-05
1 | 140639 | 2014-05-20 08:45 | 2014-05-20 12:12 | 207 | 2387 | 181347 | 0.55391 | 0.0072909 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | No Power - Trees - CB5 Tripped. E/F. O/C. L/O. Fault found to be a tree fallen through lines at Pole 750301. Fault isolated between ABS's 317 & 329. Rest of feeder backfed via VS 8760. VS8670 would not close via SCADA and had to be closed on site. 40mtrs | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 75.9728 | 72.9728 | 174186 | 0.53204 | 0.0072909 | 2014-05-20 | C | 0.53204 | 0.0072909 | 2015 | 2014-05-20 | C | 2387 | 0.53204 | 0.0072909
1 | 140640 | 2014-05-20 09:33 | 2014-05-20 10:17 | 44 | 632 | 12268 | 0.037472 | 0.0019304 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - CB 1332 at Mangamaire GXP Tripped. E/F. Losing Pongaroa Sub. Sub backfed by closing XT50. 33kV Line Patrolled and no fault found. Line re-energised OK. Trevor Pocock Faultman. | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 19.4114 | 16.4114 | 10372 | 0.03168 | 0.0019304 | 2014-05-20 | C | 0.03168 | 0.0019304 | 2015 | 2014-05-20 | C | 632 | 0.03168 | 0.0019304
1 | 140642 | 2014-05-20 15:55 | 2014-05-20 16:26 | 31 | 3 | 93 | 0.00028406 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Crossarm on pole 712799 found tipped over by Powerco staff doing line patrol - line isolated at fuses TA181 to replace nut on crossarm centre bolt - 1 x nut & washer only material used - Bruce Kerr attended. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 31 | 28 | 84 | 0.00025657 | 9.1633e-06 | 2014-05-20 | C | 0.00025657 | 9.163e-06 | 2015 | 2014-05-20 | C | 3 | 0.00025657 | 9.1633e-06
1 | 140644 | 2014-05-20 08:45 | 2014-05-20 13:16 | 271 | 114 | 30894 | 0.094363 | 0.0003482 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89342 - Replacing red tag TX pole T2110. Isolation points: 33kV S190, S122, pole 356967, Suband S765, 11kV C296, Links 8046 | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 271 | 268 | 30552 | 0.093319 | 0.0003482 | 2014-05-20 | B | 0.046659 | 0.0001741 | 2015 | 2014-05-20 | B | 114 | 0.093319 | 0.0003482
1 | 140645 | 2014-05-20 09:33 | 2014-05-20 13:10 | 217 | 5 | 1085 | 0.003314 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | ISOLATION FOR SAFETY | CONDUCTOR | SIN: 14/91735 - Isolate 11kV Transformer Fuses for P4375 to run new LV conductor and change LV Xarms. Isolation points: 11kV Transformer Fuses P4375. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 217 | 214 | 1070 | 0.0032682 | 1.5272e-05 | 2014-05-20 | B | 0.0016341 | 7.636e-06 | 2015 | 2014-05-20 | B | 5 | 0.0032682 | 1.5272e-05
1 | 140646 | 2014-05-20 10:32 | 2014-05-20 12:00 | 88 | 20 | 1760 | 0.0053758 | 6.1088e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92140 - Change wires on to new pole 785545 Owhakura Rd. Isolation points: ABS 1298, Fields Track R107, ABS 438, Links 2711. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 1700 | 0.0051925 | 6.1088e-05 | 2014-05-20 | B | 0.0025963 | 3.0544e-05 | 2015 | 2014-05-20 | B | 20 | 0.0051925 | 6.1088e-05
1 | 140647 | 2014-05-20 19:20 | 2014-05-20 21:13 | 113 | 93 | 6354 | 0.019408 | 0.00028406 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | No Power - Unknown Cause - Sectionaliser 9380 tripped, L/O. Feeder sectionalised but no fault found, Don Watson attended. Suspect Possum. | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 68.3226 | 65.3226 | 6075 | 0.018556 | 0.00028406 | 2014-05-20 | C | 0.018556 | 0.00028406 | 2015 | 2014-05-20 | C | 93 | 0.018556 | 0.00028406
1 | 140650 | 2014-05-20 14:19 | 2014-05-20 19:07 | 288 | 41 | 5758 | 0.017587 | 0.00012523 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | No Power - Mangatainoka Fuse R67 and R21 Open. Fuses R19 closed and tripped. Broken insulators and lines sitting on crossarms found at Pole P16632. 3 X 11kV Insulators replaced. Robin Smith attended. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 140.439 | 137.439 | 5635 | 0.017212 | 0.00012523 | 2014-05-20 | C | 0.017212 | 0.00012523 | 2015 | 2014-05-20 | C | 41 | 0.017212 | 0.00012523
1 | 140654 | 2014-04-30 22:25 | 2014-04-30 22:35 | 10 | 2 | 20 | 6.1088e-05 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component - at 18:49, Waihi Rd Sub, CB 5 Waihi Road Feeder. Faultman Dispatched to No Power Calls from Transformer TD4-527. Found blown fuse at Link Box SD4-425. Isolated at Fuse/Sw SD4-638 to replace fuse at Link Box. Fuse Replaced and tried re | F2 | WAIHI RD | WAIHI ROAD SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 14 | 4.2762e-05 | 6.1088e-06 | 2014-04-30 | C | 4.2762e-05 | 6.109e-06 | 2015 | 2014-04-30 | C | 2 | 4.2762e-05 | 6.1088e-06
1 | 140655 | 2014-05-21 08:30 | 2014-05-21 12:49 | 259 | 4 | 1036 | 0.0031644 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | No Power - Transformer X2264 Isolated for removal - all work done under Faultmans AP - Isolated at HV fuses on same pole as Transformer - Power off at 08:30 and back on at 12:49 - attended by D Cunningham (Connectics) (SIN14/91738). | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 259 | 256 | 1024 | 0.0031277 | 1.2218e-05 | 2014-05-21 | B | 0.0015639 | 6.109e-06 | 2015 | 2014-05-21 | B | 4 | 0.0031277 | 1.2218e-05
1 | 140656 | 2014-05-21 09:15 | 2014-05-21 14:45 | 330 | 199 | 65670 | 0.20058 | 0.00060783 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/91087 - Install new 4660 recloser at pole ABS 689, this replaces 689. Isolation points: ABS 402 | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 65073 | 0.19876 | 0.00060783 | 2014-05-21 | B | 0.09938 | 0.00030391 | 2015 | 2014-05-21 | B | 199 | 0.19876 | 0.00060783
1 | 140657 | 2014-05-21 09:32 | 2014-05-21 15:26 | 354 | 4 | 1416 | 0.0043251 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92091 - Replace 11kV pole E12384 and install a new 3 phase 30kVA TX on that pole, new TX NO TP2645. Isolation points: 11kV Fuse FC4113 | F4 | TOTMANS RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 354 | 351 | 1404 | 0.0042884 | 1.2218e-05 | 2014-05-21 | B | 0.0021442 | 6.109e-06 | 2015 | 2014-05-21 | B | 4 | 0.0042884 | 1.2218e-05
1 | 140659 | 2014-05-20 09:16 | 2014-05-20 14:51 | 335 | 31 | 10385 | 0.03172 | 9.4687e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91734 - Replace 11kV X-arms and Transformer TC3151 on twin feeder circuit. Isolation points: 11kV WGM CB3, ABS 211; 11kV WGM CB5, ABS 249 & 256. | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 335 | 332 | 10292 | 0.031436 | 9.4687e-05 | 2014-05-20 | B | 0.015718 | 4.7344e-05 | 2015 | 2014-05-20 | B | 31 | 0.031436 | 9.4687e-05
1 | 140662 | 2014-05-21 08:30 | 2014-05-21 13:50 | 320 | 1 | 320 | 0.00097742 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92503 - Maintenance of 11kV Sw/gear SD5-258, SD5-256 & Fuse/Sw SD5-266, SD5-260, SD5-262. Maintenance of Transformers SD5-262, SD5-260. Isolation Points: 11kV U/G cables removed from poles 215116 & 215114. | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 320 | 317 | 317 | 0.00096825 | 3.0544e-06 | 2014-05-21 | B | 0.00048413 | 1.527e-06 | 2015 | 2014-05-21 | B | 1 | 0.00096825 | 3.0544e-06
1 | 140664 | 2014-05-21 15:07 | 2014-05-21 17:18 | 131 | 109 | 8913 | 0.027224 | 0.00033293 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | No Power - Ohakune CB 2 No trip. Recloser RS1022 Tripped Flags E/F. Line sectionalised & patrolled. Faulty transformer Y4404 isolated. Customer advised that transformer will need to be upgraded as it is undersized for his current operation. Transformer Y | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 81.7706 | 78.7706 | 8586 | 0.026225 | 0.00033293 | 2014-05-21 | C | 0.026225 | 0.00033293 | 2015 | 2014-05-21 | C | 109 | 0.026225 | 0.00033293
1 | 140665 | 2014-05-21 19:09 | 2014-05-21 21:48 | 159 | 52 | 5086 | 0.015535 | 0.00015883 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power - Kimbolton CB 7 No Trip. Recloser 4443/2 Trip. Flags A,B,C E/F. Line patrolled & Sectionalised. No fault Found. Faultman Bruce Mehens, Jeff Roberts. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 97.8077 | 94.8077 | 4930 | 0.015058 | 0.00015883 | 2014-05-21 | C | 0.015058 | 0.00015883 | 2015 | 2014-05-21 | C | 52 | 0.015058 | 0.00015883
1 | 140672 | 2014-04-09 10:07 | 2014-04-09 15:12 | 305 | 69 | 21045 | 0.06428 | 0.00021076 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90046 - Replace hardware, poles etc and install temporary line break linkls for future shuts. Isolation points:11kV IC860, IC876, 9636/1, 9636/4, IC908, IC1378, 9308/1, 9308/4.. Temporary Links IP573 at pole M12839; Links IP574 at pole M0315; Lin | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 305 | 302 | 20838 | 0.063648 | 0.00021076 | 2014-04-09 | B | 0.031824 | 0.00010538 | 2015 | 2014-04-09 | B | 69 | 0.063648 | 0.00021076
1 | 140674 | 2014-05-22 09:30 | 2014-05-22 10:28 | 58 | 35 | 2030 | 0.0062005 | 0.0001069 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/92294 - NETWORK CRITICAL WORK. Install hardware over river spans & remove temporary ABS TEMP19. Isolation points: 11kV ABS SE3-016 & TEMP19. Refer to LLP 14/92295. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 58 | 55 | 1925 | 0.0058798 | 0.0001069 | 2014-05-22 | B | 0.0029399 | 5.3452e-05 | 2015 | 2014-05-22 | B | 35 | 0.0058798 | 0.0001069
1 | 140676 | 2014-05-22 16:10 | 2014-05-23 04:38 | 748 | 259 | 15083 | 0.04607 | 0.0007911 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | Defective Component - Recloser 9198 Trip. No Flags. L/O. Feeder sectionalised. Fault found to be a Transformer pole had fallen over. Pole # B12563. Pole isolated, feeder restored and pole replaced. Bob Whitehead Faultman. | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 58.2355 | 55.2355 | 14306 | 0.043697 | 0.0007911 | 2014-05-22 | C | 0.043697 | 0.0007911 | 2015 | 2014-05-22 | C | 259 | 0.043697 | 0.0007911
1 | 140680 | 2014-05-22 13:01 | 2014-05-22 15:02 | 121 | 553 | 66913 | 0.20438 | 0.0016891 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | REGULATOR | SIN: 14/91963 - Regulator NO 1 to be removed permanently from system. Bypass cables will be installed between S713 and S768 permanently. Remove regulator No 1 and foundation to allow new cable install. Isolation points: S713, S768, S711, S11, S707, S16, S | F1,F2,F3 | Not entered | Not entered | Not entered | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 121 | 118 | 65254 | 0.19931 | 0.0016891 | 2014-05-22 | B | 0.099657 | 0.00084455 | 2015 | 2014-05-22 | B | 553 | 0.19931 | 0.0016891
1 | 140681 | 2014-05-22 09:00 | 2014-05-22 13:51 | 291 | 25 | 7275 | 0.022221 | 7.6361e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91739 - Replace 11kV Xarms and run new al wire between poles 702281 and 702294 as old wire has been falling down due to high fault current. Isolation points: 11kV ABS 221, ABS 61, ABS 4882 | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 291 | 288 | 7200 | 0.021992 | 7.6361e-05 | 2014-05-22 | B | 0.010996 | 3.818e-05 | 2015 | 2014-05-22 | B | 25 | 0.021992 | 7.6361e-05
1 | 140683 | 2014-05-22 09:53 | 2014-05-22 13:31 | 218 | 25 | 5450 | 0.016647 | 7.6361e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92404 - Erect pole w/ digger to lift up 1kV wires as ground clearance is borderline. Line feeds TX 4546W. Isolation points: 4621/1, 4621/6, ABS 4620 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 218 | 215 | 5375 | 0.016418 | 7.6361e-05 | 2014-05-22 | B | 0.0082088 | 3.818e-05 | 2015 | 2014-05-22 | B | 25 | 0.016418 | 7.6361e-05
1 | 140684 | 2014-05-23 09:07 | 2014-05-23 12:29 | 202 | 2 | 404 | 0.001234 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | No Power - Lake Road CB 3 No trip. Replace Broken Crossarm at Pole E12829. Isolation at Fuses FC825. Fautlman Dave McKee. Materials Double 11kV termination Arm. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 202 | 199 | 398 | 0.0012157 | 6.1088e-06 | 2014-05-23 | C | 0.0012157 | 6.109e-06 | 2015 | 2014-05-23 | C | 2 | 0.0012157 | 6.1088e-06
1 | 140686 | 2014-05-23 10:31 | 2014-05-23 13:44 | 193 | 187 | 36091 | 0.11024 | 0.00057118 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/92122 - Re-sag 11kV / 400V conductors at pole T12655. Isolation points: 11kV CB 3 & ABS IC2708. | F2/F3 | QUEEN ST | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 193 | 190 | 35530 | 0.10852 | 0.00057118 | 2014-05-23 | B | 0.054262 | 0.00028559 | 2015 | 2014-05-23 | B | 187 | 0.10852 | 0.00057118
1 | 140687 | 2014-05-23 10:13 | 2014-05-23 10:27 | 14 | 1091 | 15274 | 0.046653 | 0.0033324 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | No Power - Te Matai CB 1122 Trip A,B,C O/C. Total loss of supply to Atuaroa Sub Station. Report from public of digger working near lines at Rangiuru Rd & heard a bang. Faultmen dispatched to area ascertain the status of the network & digger operator. Digg | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 12001 | 0.036656 | 0.0033324 | 2014-05-23 | C | 0.036656 | 0.0033324 | 2015 | 2014-05-23 | C | 1091 | 0.036656 | 0.0033324
1 | 140688 | 2014-05-23 10:13 | 2014-05-23 11:18 | 65 | 2606 | 169390 | 0.51739 | 0.0079598 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | No Power - Te Matai CB 1122 Trip A,B,C O/C. Total loss of supply to Pongakawa Sub Station. This out Def for PKW CB 2 & 3 Report from public of digger working near lines at Rangiuru Rd & heard a bang. Faultmen dispatched to area ascertain the status of the | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 161572 | 0.49351 | 0.0079598 | 2014-05-23 | C | 0.49351 | 0.0079598 | 2015 | 2014-05-23 | C | 2606 | 0.49351 | 0.0079598
1 | 140689 | 2014-05-23 10:13 | 2014-05-23 11:18 | 65 | 815 | 25259 | 0.077152 | 0.0024894 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | No Power - Te Matai CB 1122 Trip A,B,C O/C. Total loss of supply to Pongakawa Sub Station. This out Def for PKW CB 1 Report from public of digger working near lines at Rangiuru Rd & heard a bang. Faultmen dispatched to area ascertain the status of the net | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 30.9926 | 27.9926 | 22814 | 0.069684 | 0.0024894 | 2014-05-23 | C | 0.069684 | 0.0024894 | 2015 | 2014-05-23 | C | 815 | 0.069684 | 0.0024894
1 | 140690 | 2014-05-23 10:13 | 2014-05-23 11:17 | 64 | 339 | 15461 | 0.047224 | 0.0010354 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | No Power - Te Matai CB 1122 Trip A,B,C O/C. Total loss of supply to Pongakawa Sub Station. This out Def for PKW CB 4 Report from public of digger working near lines at Rangiuru Rd & heard a bang. Faultmen dispatched to area ascertain the status of the net | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 45.6077 | 42.6077 | 14444 | 0.044118 | 0.0010354 | 2014-05-23 | C | 0.044118 | 0.0010355 | 2015 | 2014-05-23 | C | 339 | 0.044118 | 0.0010354
1 | 140691 | 2014-05-23 10:13 | 2014-05-23 11:19 | 66 | 20 | 1320 | 0.0040318 | 6.1088e-05 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE - TREES | CONDUCTOR | No Power - Te Matai CB 1122 Trip A,B,C O/C. Total loss of supply to Pongakawa Sub Station. This out Def for Te Puke CB 6 Report from public of digger working near lines at Rangiuru Rd & heard a bang. Faultmen dispatched to area ascertain the status of the | F1,F2,F3 | RANGIRURU | Not entered | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 66 | 63 | 1260 | 0.0038486 | 6.1088e-05 | 2014-05-23 | C | 0.0038486 | 6.1088e-05 | 2015 | 2014-05-23 | C | 20 | 0.0038486 | 6.1088e-05
1 | 140693 | 2014-05-23 09:30 | 2014-05-23 10:30 | 60 | 1 | 60 | 0.00018327 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92250 - AP Is for 1 hr to install a 400V Disconnector to the LV of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disconnector. This is to be followed by a 400V shutdown to complete the 400V arm replacemen | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 57 | 0.0001741 | 3.0544e-06 | 2014-05-23 | B | 8.7051e-05 | 1.527e-06 | 2015 | 2014-05-23 | B | 1 | 0.0001741 | 3.0544e-06
1 | 140695 | 2014-05-23 11:00 | 2014-05-23 11:40 | 40 | 8 | 320 | 0.00097742 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92251 - AP Is for 1 hr to install a 400V Disconnector to the LV of the TX. AP can then be cancelled and the 11kV Transformer fuses closed, relivening the TX up to the LV disconnector. This is to be followed by a 400V shutdown to complete the 400V | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 296 | 0.00090411 | 2.4435e-05 | 2014-05-23 | B | 0.00045205 | 1.2218e-05 | 2015 | 2014-05-23 | B | 8 | 0.00090411 | 2.4435e-05
1 | 140697 | 2014-05-23 14:00 | 2014-05-23 14:30 | 30 | 3 | 90 | 0.0002749 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE HOLDER | SIN: 14/92252 - AP Is for 1 hr to install a 400V Disconnector to the LV of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disconnector. This is to be followed by a 400V shutdown to complete the 400V arm replacemen | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 81 | 0.00024741 | 9.1633e-06 | 2014-05-23 | B | 0.0001237 | 4.582e-06 | 2015 | 2014-05-23 | B | 3 | 0.00024741 | 9.1633e-06
1 | 140699 | 2014-05-23 12:00 | 2014-05-23 12:30 | 30 | 3 | 90 | 0.0002749 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE HOLDER | SIN: 14/92255 - AP Is for 1 hr to install a 400V Disconnector to the LV of the Transformer TC2424. AP can then be cancelled and the 11kV Transformer fuses closed, relivening the TX up to the LV disconnector. This is to be followed by a 400V shutdown to co | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 81 | 0.00024741 | 9.1633e-06 | 2014-05-23 | B | 0.0001237 | 4.582e-06 | 2015 | 2014-05-23 | B | 3 | 0.00024741 | 9.1633e-06
1 | 140702 | 2014-05-21 09:25 | 2014-05-21 10:35 | 70 | 8 | 560 | 0.0017105 | 2.4435e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92253 - AP Is for 1 hr to install a 400V Disc-Connector to the 400V of the Transformer. AP can then be cancelled and the 11kV fuses closed, relivening the Transformer up to the 400V disc-connector. This is to be followed by a 400V shutdown to com | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 536 | 0.0016372 | 2.4435e-05 | 2014-05-21 | B | 0.00081859 | 1.2218e-05 | 2015 | 2014-05-21 | B | 8 | 0.0016372 | 2.4435e-05
1 | 140703 | 2014-05-22 09:20 | 2014-05-22 10:50 | 90 | 7 | 630 | 0.0019243 | 2.1381e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92254 - AP Is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the 11kV Transformer Fuses closed, relivening the Transformer up to the LV disc-connector. This is to be followed by a 400V shutdown to compl | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 609 | 0.0018601 | 2.1381e-05 | 2014-05-22 | B | 0.00093007 | 1.069e-05 | 2015 | 2014-05-22 | B | 7 | 0.0018601 | 2.1381e-05
1 | 140704 | 2014-05-22 09:24 | 2014-05-22 15:38 | 374 | 196 | 73304 | 0.2239 | 0.00059867 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91740 - Replace 11kV X-arms and conductor at various places within the isolated area. Isolation points: 11kV Links IP161 & ABS 2122. | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 374 | 371 | 72716 | 0.22211 | 0.00059867 | 2014-05-22 | B | 0.11105 | 0.00029933 | 2015 | 2014-05-22 | B | 196 | 0.22211 | 0.00059867
1 | 140707 | 2014-05-23 20:37 | 2014-05-23 23:40 | 183 | 165 | 15128 | 0.046207 | 0.00050398 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB C946 Found Tripped as part of dispatch jobs - Feeder Sectionlised with no fault found - Attended by Adrian Marshell & Gavin Paget. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 91.6848 | 88.6848 | 14633 | 0.044695 | 0.00050398 | 2014-05-23 | C | 0.044695 | 0.00050398 | 2015 | 2014-05-23 | C | 165 | 0.044695 | 0.00050398
1 | 140708 | 2014-05-23 20:06 | 2014-05-23 23:57 | 231 | 207 | 31131 | 0.095087 | 0.00063227 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees - CB C881 Tripped Lines Found Down Between Poles 826659 & 826657 - Isolated at ABS's S321 & S114 - Lines Repaired and feeder returned to service - Damaged caused by tree in notice zone - attended by Frank Martin & Ben Taylor - Used 2 mtrs of Conduct | F4 | HOLDSWORTH | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 150.3913 | 147.3913 | 30510 | 0.09319 | 0.00063227 | 2014-05-23 | C | 0.09319 | 0.00063227 | 2015 | 2014-05-23 | C | 207 | 0.09319 | 0.00063227
1 | 140709 | 2014-05-23 21:14 | 2014-05-24 03:30 | 376 | 267 | 32141 | 0.098172 | 0.00081553 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | Defective Component - OYT C1024 Found Tripped as part of Dispatch Job - Line down found during sectionlising at Pole 834074 - Isolated at ABS C223/1 & Links C223/6 - Line repaired & feeder returned to Service - Attended by Adam Whale, Ben Taylor & Gavin P | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 120.3783 | 117.3783 | 31340 | 0.095726 | 0.00081553 | 2014-05-23 | C | 0.095726 | 0.00081553 | 2015 | 2014-05-23 | C | 267 | 0.095726 | 0.00081553
1 | 140710 | 2014-05-24 06:04 | 2014-05-24 08:30 | 146 | 134 | 19564 | 0.059757 | 0.00040929 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Fuse/sw SC4-514 found open (1 blown fuse) by f/man attending N/P call - cable test carried out on cable and found to be faulty - generator connected at transformers TC4-200 & TC4-230 for duration of outage - cable isolated at fuse/sw SC4-514 for repairs - | F3 | TOTARA ST NORTH | TRITON SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 146 | 143 | 19162 | 0.058529 | 0.00040929 | 2014-05-24 | C | 0.058529 | 0.00040929 | 2015 | 2014-05-24 | C | 134 | 0.058529 | 0.00040929
1 | 140711 | 2014-05-24 17:06 | 2014-05-24 20:56 | 230 | 188 | 15548 | 0.04749 | 0.00057423 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | No Power - Recloser 449 tripped - no flags. Adverse Weather/Extreme Wind. Section of line from ABS 56 to ABS 266 isolated to repair conductor and replace insulator on pole 746696 (attended by Mark Patterson). Materials used: 1 x Pin Insulator, 10 metres o | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 82.7021 | 79.7021 | 14984 | 0.045767 | 0.00057423 | 2014-05-24 | C | 0.045767 | 0.00057423 | 2015 | 2014-05-24 | C | 188 | 0.045767 | 0.00057423
1 | 140712 | 2014-05-24 15:02 | 2014-05-25 11:42 | 1240 | 478 | 314072 | 0.95931 | 0.00146 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power - CB C281, C850 & 8097 tripped line sectionalised and patrolled and supply restored to Section beyond CB 8097 with tree removed from lines at pole 835519. Section beyond CB C281 left off as lines still to be repaired in daylight. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 657.0544 | 654.0544 | 312638 | 0.95493 | 0.00146 | 2014-05-24 | C | 0.95493 | 0.00146 | 2015 | 2014-05-24 | C | 478 | 0.95493 | 0.00146
1 | 140713 | 2014-05-24 20:30 | 2014-05-24 21:48 | 78 | 23 | 1794 | 0.0054796 | 7.0252e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | No Power - Adverse Weather/Extreme Wind. Section of line from Fuses 4937 isolated to replace 1 x insulator and rebind conductors on pole 733482 (attended by Henry Hood). | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 78 | 75 | 1725 | 0.0052689 | 7.0252e-05 | 2014-05-24 | C | 0.0052689 | 7.0252e-05 | 2015 | 2014-05-24 | C | 23 | 0.0052689 | 7.0252e-05
1 | 140714 | 2014-05-24 15:28 | 2014-05-24 16:10 | 42 | 86 | 3428 | 0.010471 | 0.00026268 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power. Adverse weather/extreme wind. Broken Pole (Unable to supply power from either backfeed). Truck holding pole overnight. Dave Thomson attended. Pole number required. | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39.8605 | 36.8605 | 3170 | 0.0096825 | 0.00026268 | 2014-05-24 | C | 0.0096825 | 0.00026268 | 2015 | 2014-05-24 | C | 86 | 0.0096825 | 0.00026268
1 | 140715 | 2014-05-24 11:57 | 2014-05-24 13:50 | 113 | 108 | 8074 | 0.024661 | 0.00032988 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Recloser T42 tripped. Line Patrolled - No Fault Found. Adverse weather/extreme wind. Dave Whale attended. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 74.7593 | 71.7593 | 7750 | 0.023672 | 0.00032988 | 2014-05-24 | C | 0.023672 | 0.00032988 | 2015 | 2014-05-24 | C | 108 | 0.023672 | 0.00032988
1 | 140716 | 2014-05-24 17:08 | 2014-05-25 08:21 | 913 | 297 | 269499 | 0.82316 | 0.00090716 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Recloser C225 Tripped. Line Patrolled - No Fault Found. Adverse Weather/Extreme Wind. Isolated at ABS S167 - left off overnight as it was deemed unsafe for field staff to restore. Restoration of power completed the following morning. Adam Wha | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 907.404 | 904.404 | 268608 | 0.82044 | 0.00090716 | 2014-05-24 | C | 0.82044 | 0.00090716 | 2015 | 2014-05-24 | C | 297 | 0.82044 | 0.00090716
1 | 140717 | 2014-05-24 11:51 | 2014-05-24 16:25 | 274 | 1446 | 303750 | 0.92778 | 0.0044167 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C838 tripped on O/C. Adverse Weather/Extreme Wind. Line patrolled - No Fault Found. CB 838 Tripped - affecting the whole feeder. Line patrolled and branch located on line. Branch removed with Hot Line Stick and power restored. The branch | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 210.0622 | 207.0622 | 299412 | 0.91453 | 0.0044167 | 2014-05-24 | C | 0.91453 | 0.0044167 | 2015 | 2014-05-24 | C | 1446 | 0.91453 | 0.0044167
1 | 140718 | 2014-05-24 08:15 | 2014-05-24 10:48 | 153 | 291 | 12275 | 0.037493 | 0.00088884 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. CB C945 found open. Line patrolled - nothing found. Adverse Weather/Extreme Wind. (Joe Attended). | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 42.1821 | 39.1821 | 11402 | 0.034827 | 0.00088884 | 2014-05-24 | C | 0.034827 | 0.00088884 | 2015 | 2014-05-24 | C | 291 | 0.034827 | 0.00088884
1 | 140719 | 2014-05-24 18:26 | 2014-05-25 13:41 | 1155 | 1120 | 205087 | 0.62642 | 0.003421 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C916 Tripped. No Flags. Adverse Weather/Extreme Wind. Reports of tree through line at pole 814168. Temporary Line Break made at Pole 814172. NDR 37688. Bread Keating attended. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 183.1134 | 180.1134 | 201727 | 0.61616 | 0.003421 | 2014-05-24 | C | 0.61616 | 0.003421 | 2015 | 2014-05-24 | C | 1120 | 0.61616 | 0.003421
1 | 140720 | 2014-05-24 11:56 | 2014-05-24 15:38 | 222 | 65 | 12891 | 0.039375 | 0.00019854 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Recloser V5 Tripped. Adverse Weather/Extreme Wind. Line patrolled and trees located after 11kV Fuses V9. Neville Morris attended. No NDR number noted on Fault Record. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 198.3231 | 195.3231 | 12696 | 0.038779 | 0.00019854 | 2014-05-24 | C | 0.038779 | 0.00019854 | 2015 | 2014-05-24 | C | 65 | 0.038779 | 0.00019854
1 | 140721 | 2014-05-24 14:16 | 2014-05-24 15:52 | 96 | 769 | 73498 | 0.22449 | 0.0023489 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Recloser C953 Tripped. No Flags. Adverse Weather/Extreme Wind. Line Patrolled. Found conductor down due to tree in lines. (Less than 1 span of conductor). Adam Whale attended. | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 95.5761 | 92.5761 | 71191 | 0.21745 | 0.0023489 | 2014-05-24 | C | 0.21745 | 0.0023489 | 2015 | 2014-05-24 | C | 769 | 0.21745 | 0.0023489
1 | 140722 | 2014-05-24 10:50 | 2014-05-24 11:53 | 63 | 10 | 630 | 0.0019243 | 3.0544e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | No Power. Line Patrolled. Insulator replaced at pole 741390. Beyond 11kV Fuses 5553. Adverse Weather/ Extreme Wind. Bruce Kerr attended. | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 600 | 0.0018327 | 3.0544e-05 | 2014-05-24 | C | 0.0018327 | 3.0544e-05 | 2015 | 2014-05-24 | C | 10 | 0.0018327 | 3.0544e-05
1 | 140723 | 2014-05-24 10:31 | 2014-05-24 12:17 | 106 | 13 | 1378 | 0.004209 | 3.9708e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power. Line Patrolled and twisted cross arm located at pole 842045. Isolated beyond 11kV Fuses 7855. Nev Pope attended. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106 | 103 | 1339 | 0.0040899 | 3.9708e-05 | 2014-05-24 | C | 0.0040899 | 3.9708e-05 | 2015 | 2014-05-24 | C | 13 | 0.0040899 | 3.9708e-05
1 | 140724 | 2014-05-24 07:06 | 2014-05-24 13:07 | 361 | 37 | 13357 | 0.040798 | 0.00011301 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power. Car vs Pole #38178. Isolated beyond 11kV Earth Switch 8555/3. Backfeed supplied though CKL10 6406/3. NDR to come.Blair attended. | F2 | KATERE 6 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 361 | 358 | 13246 | 0.040459 | 0.00011301 | 2014-05-24 | C | 0.040459 | 0.00011301 | 2015 | 2014-05-24 | C | 37 | 0.040459 | 0.00011301
1 | 140725 | 2014-05-23 17:35 | 2014-05-24 13:40 | 1205 | 195 | 27103 | 0.082784 | 0.00059561 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Recloser Q61 Tripped. E/F B & C O/C. Public reported tree on lines. Temporary Line Break at Pole P45985. Power restored beyond Temporary Line Break the following day.Trevor Pocock attended. NDR to come. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 138.9897 | 135.9897 | 26518 | 0.080997 | 0.00059561 | 2014-05-23 | C | 0.080997 | 0.00059561 | 2015 | 2014-05-23 | C | 195 | 0.080997 | 0.00059561
1 | 140726 | 2014-05-25 09:00 | 2014-05-25 15:06 | 366 | 4 | 1464 | 0.0044717 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90924 - Install new 11kV CFC RMU 9816 between existing Sw/gear 9481/1 & 9482/3. Liven and commission new RMU 9816 and new Transformer (TP2633) connected to Fuse/Sw 9816/2. Isolation points: 11kV Sw/gear 9481/1, 9482/3, 9816/1,2,3. | F2 | MALEME EXPRESS | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 366 | 363 | 1452 | 0.004435 | 1.2218e-05 | 2014-05-25 | B | 0.0022175 | 6.109e-06 | 2015 | 2014-05-25 | B | 4 | 0.004435 | 1.2218e-05
1 | 140727 | 2014-05-25 15:37 | 2014-05-25 16:12 | 35 | 62 | 2170 | 0.0066281 | 0.00018937 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | Defective Component - Emergency switching to repair blown jumper at pole U12722 (top of fuse at transformer TC5644). Isolation at ABS IC314 (no back feeds) jumper repaired, all service restored, Don Watson attended. Materials 1 x bi metal lug. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 1984 | 0.00606 | 0.00018937 | 2014-05-25 | C | 0.00606 | 0.00018937 | 2015 | 2014-05-25 | C | 62 | 0.00606 | 0.00018937
1 | 140728 | 2014-05-23 13:50 | 2014-05-23 16:20 | 150 | 291 | 17154 | 0.052396 | 0.00088884 | No Power | 11000 | Unplanned | Zone Sub Equip. | UNKNOWN | NO FAULT FOUND | CIRCUIT BREAKER | Unknown Cause - at 13:50, Gladstone Sub, CB C945 Longbush Feeder, Tripped, No Flags, L/O. Faultman dispatched and investigation began. Feeder Sectionalised. No Fault Found. Found. Brad Keating Attended. | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 58.9485 | 55.9485 | 16281 | 0.049729 | 0.00088884 | 2014-05-23 | C | 0.049729 | 0.00088884 | 2015 | 2014-05-23 | C | 291 | 0.049729 | 0.00088884
1 | 140729 | 2014-05-23 15:43 | 2014-05-23 17:06 | 83 | 893 | 66053 | 0.20175 | 0.0027276 | No Power | 11000 | Unplanned | Zone Sub Equip. | UNKNOWN | NOT PATROLLED | CIRCUIT BREAKER | Unknown Cause - at 15:43 Kelvin Grove Sub, CB 8 Pohangina Feeder, Tripped, No Flags, L/O. at 15:43 KIM 5 KEG 8 Auto Backfeed Scheme Initiated, Recloser F26 Opened, Recloser F48 Closed. Faultman dispatched & investigation began. Feeder was sectionalised. N | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 73.9675 | 70.9675 | 63374 | 0.19357 | 0.0027276 | 2014-05-23 | C | 0.19357 | 0.0027276 | 2015 | 2014-05-23 | C | 893 | 0.19357 | 0.0027276
1 | 140730 | 2014-05-23 09:19 | 2014-05-23 11:37 | 138 | 436 | 43387 | 0.13252 | 0.0013317 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 09:19, Featherston Sub, CB C911 Waite St Feeder, Tripped, E/F, L/O. Call came in of lines down at Pole 814562. Faultman dispatched & lines isolated at ABS S549, S563, S589 & S587. CB 911 Closed at 09:50. Backfeed supplied from FEA Sub CB C917 | F3/F4 | WAITE ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 99.5115 | 96.5115 | 42079 | 0.12853 | 0.0013317 | 2014-05-23 | C | 0.12853 | 0.0013317 | 2015 | 2014-05-23 | C | 436 | 0.12853 | 0.0013317
1 | 140732 | 2014-05-24 16:27 | 2014-05-24 19:46 | 199 | 705 | 76023 | 0.23221 | 0.0021534 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | No Power. CB9 Tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled. Located lines down at pole P42252. Materials used: Conductor & 4 Sleeves. Mike Thompson attended. | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107.834 | 104.834 | 73908 | 0.22575 | 0.0021534 | 2014-05-24 | C | 0.22575 | 0.0021534 | 2015 | 2014-05-24 | C | 705 | 0.22575 | 0.0021534
1 | 140733 | 2014-05-24 16:45 | 2014-05-24 19:24 | 159 | 65 | 10335 | 0.031567 | 0.00019854 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. Recloser V5 Tripped. No Flags. Adverese Weather/Extreme Wind. Suspected clash of overhead lines due to high winds. Line not patrolled. Nev Morris attended. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 159 | 156 | 10140 | 0.030972 | 0.00019854 | 2014-05-24 | C | 0.030972 | 0.00019854 | 2015 | 2014-05-24 | C | 65 | 0.030972 | 0.00019854
1 | 140734 | 2014-05-24 17:03 | 2014-05-24 20:43 | 220 | 1019 | 64088 | 0.19575 | 0.0031125 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. CB8 Tripped. No Flags. Adverse Weather/Extreme Wind. Line patrolled. Floating Conductor found and repaired at Pole P17000. A Parsad attended. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 62.893 | 59.893 | 61031 | 0.18641 | 0.0031125 | 2014-05-24 | C | 0.18641 | 0.0031125 | 2015 | 2014-05-24 | C | 1019 | 0.18641 | 0.0031125
1 | 140735 | 2014-05-24 16:13 | 2014-05-24 17:16 | 63 | 1064 | 61782 | 0.18871 | 0.0032499 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. CB5 tripped. No Flags. Adverse Weather/Extreme Wind. Line Patrolled. Line down at 60 Burns Street, Hawera. Line down not mentioned on fault sheet, nor any permit issued to repair? Not sure how line down and address has come about (ASW) | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 58.0658 | 55.0658 | 58590 | 0.17896 | 0.0032499 | 2014-05-24 | C | 0.17896 | 0.0032499 | 2015 | 2014-05-24 | C | 1064 | 0.17896 | 0.0032499
1 | 140736 | 2014-05-24 18:40 | 2014-05-25 10:15 | 935 | 59 | 55165 | 0.1685 | 0.00018021 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power. Adverse Weather/Extreme Wind. Line Patrolled - Pole 825068 on fire. Isolated beyond ABS S320. | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 935 | 932 | 54988 | 0.16796 | 0.00018021 | 2014-05-24 | C | 0.16796 | 0.00018021 | 2015 | 2014-05-24 | C | 59 | 0.16796 | 0.00018021
1 | 140737 | 2014-05-24 09:50 | 2014-05-25 10:08 | 1458 | 232 | 324450 | 0.99101 | 0.00070863 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Patrolled. Floating Conductor loacted at pole P55742. Isolated beyond ABS S5. Materials used: 3 x Clamp Top Insulators. Phil Barnes attended. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1398.4914 | 1395.4914 | 323754 | 0.98888 | 0.00070863 | 2014-05-24 | C | 0.98888 | 0.00070863 | 2015 | 2014-05-24 | C | 232 | 0.98888 | 0.00070863
1 | 140738 | 2014-05-25 09:13 | 2014-05-25 11:30 | 137 | 24 | 3288 | 0.010043 | 7.3306e-05 | No Power | 6600 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | UNKNOWN | No Power. Adverse Weather/Extreme Wind. Line Patrolled. Isolated beyond 6.6kV Fuses 952. NDR to follow. | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 137 | 134 | 3216 | 0.009823 | 7.3306e-05 | 2014-05-25 | C | 0.009823 | 7.3306e-05 | 2015 | 2014-05-25 | C | 24 | 0.009823 | 7.3306e-05
1 | 140739 | 2014-05-24 14:05 | 2014-05-25 12:56 | 1371 | 89 | 68553 | 0.20939 | 0.00027184 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power. Adverse Weather/Extreme Wind. Pole on Fire at pole 817647. Isolated beyond Fuses 7570 overnight. Gavin Gray attended. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 770.2584 | 767.2584 | 68286 | 0.20857 | 0.00027184 | 2014-05-24 | C | 0.20857 | 0.00027184 | 2015 | 2014-05-24 | C | 89 | 0.20857 | 0.00027184
1 | 140740 | 2014-05-24 20:03 | 2014-05-25 12:49 | 1006 | 6 | 6036 | 0.018437 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line patrolled and broken lines located at pole 737927. (Transformer 2704T Mountain House had generator - no loss of supply experienced). Lines repaired. Bruce Kerr attended. | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 1006 | 1003 | 6018 | 0.018382 | 1.8327e-05 | 2014-05-24 | C | 0.018382 | 1.8327e-05 | 2015 | 2014-05-24 | C | 6 | 0.018382 | 1.8327e-05
1 | 140741 | 2014-05-24 19:45 | 2014-05-25 11:58 | 973 | 50 | 43097 | 0.13164 | 0.00015272 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Sectionaliser C218/2 found open (24/05/2014) Closed & tripped at 19.45. Tree found across line - no damage. Denis Rose Attended. No NDR supplied. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 861.94 | 858.94 | 42947 | 0.13118 | 0.00015272 | 2014-05-24 | C | 0.13118 | 0.00015272 | 2015 | 2014-05-24 | C | 50 | 0.13118 | 0.00015272
1 | 140742 | 2014-05-26 10:43 | 2014-05-26 11:36 | 53 | 61 | 3233 | 0.009875 | 0.00018632 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | No Power - Whareroa CB WH1 No Trip Broken Jumper at Fuses WH184 Pole 728085. Isolation at ABS WH101 & WH 130 Back feed from Livingston LI 7 vai ABS LI734. Faultman Phil Webby Materials 16mm Sleeve | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 3050 | 0.009316 | 0.00018632 | 2014-05-26 | C | 0.009316 | 0.00018632 | 2015 | 2014-05-26 | C | 61 | 0.009316 | 0.00018632
1 | 140743 | 2014-05-25 03:32 | 2014-05-25 11:08 | 456 | 353 | 138390 | 0.4227 | 0.0010782 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Recloser 8097 Tripped A, O/C & E/F. Adverse Weather/Extreme Wind. Line patrolled - nothing found. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 392.0397 | 389.0397 | 137331 | 0.41947 | 0.0010782 | 2014-05-25 | C | 0.41947 | 0.0010782 | 2015 | 2014-05-25 | C | 353 | 0.41947 | 0.0010782
1 | 140744 | 2014-05-24 09:45 | 2014-05-25 14:20 | 1715 | 45 | 70595 | 0.21563 | 0.00013745 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Recloser I25 Tripped. Adverse Weather/Extreme Wind. Line patrolled. Located conductor down. Rehung conductor and restored power. Peter Marshall attended. | F4 | BROOKLANDS | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1568.7778 | 1565.7778 | 70460 | 0.21521 | 0.00013745 | 2014-05-24 | C | 0.21521 | 0.00013745 | 2015 | 2014-05-24 | C | 45 | 0.21521 | 0.00013745
1 | 140745 | 2014-05-26 09:56 | 2014-05-26 10:04 | 8 | 1394 | 10169 | 0.03106 | 0.0042579 | No Power | 11000 | Unplanned | Zone Sub Equip. | UNKNOWN | PATROLLED | UNKNOWN | No Power - Total loss of supply to Tirau Sub station. CB 17 Tripped No Flags. CB22 flags showed E/F. Switch board checked visually on site. Graeme Ward on site. Feeder CB's offloaded & CB 17 closed. No Fault Found all supply restored. | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 7.2948 | 4.2948 | 5987 | 0.018287 | 0.0042579 | 2014-05-26 | C | 0.018287 | 0.0042579 | 2015 | 2014-05-26 | C | 1394 | 0.018287 | 0.0042579
1 | 140746 | 2014-05-25 14:40 | 2014-05-25 15:45 | 65 | 6 | 390 | 0.0011912 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line patrolled & floating conductor located at pole 359619. Isolated beyond 11kV Fuses 7888. Ben Taylor attended. | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 372 | 0.0011362 | 1.8327e-05 | 2014-05-25 | C | 0.0011362 | 1.8327e-05 | 2015 | 2014-05-25 | C | 6 | 0.0011362 | 1.8327e-05
1 | 140747 | 2014-05-25 14:30 | 2014-05-25 16:07 | 97 | 26 | 2446 | 0.0074711 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Temporary Line Break required at Pole P06844. Isolated at 11kV Fuses V16. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 94.0769 | 91.0769 | 2368 | 0.0072329 | 7.9415e-05 | 2014-05-25 | C | 0.0072329 | 7.9415e-05 | 2015 | 2014-05-25 | C | 26 | 0.0072329 | 7.9415e-05
1 | 140748 | 2014-05-24 21:15 | 2014-05-25 16:24 | 1149 | 9 | 10341 | 0.031586 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power. Adverse Weather/Extreme Wind. Line Patrolled & 11kV pole 827755 replaced. Isolated beyond Fuses 7109. Joe Matthews attended. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1149 | 1146 | 10314 | 0.031503 | 2.749e-05 | 2014-05-24 | C | 0.031503 | 2.749e-05 | 2015 | 2014-05-24 | C | 9 | 0.031503 | 2.749e-05
1 | 140749 | 2014-05-26 04:33 | 2014-05-26 08:05 | 212 | 299 | 45962 | 0.14039 | 0.00091327 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power - Cambria CB 5 No Trip Recloser 6561 Trip A & B O/C. 4 A/R before finally tripping at 04:33. Line Patrolled & Sectionalized No Fault Found. Faultman Bruce Kerr. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 153.7191 | 150.7191 | 45065 | 0.13765 | 0.00091327 | 2014-05-26 | C | 0.13765 | 0.00091327 | 2015 | 2014-05-26 | C | 299 | 0.13765 | 0.00091327
1 | 140750 | 2014-05-25 13:58 | 2014-05-25 14:23 | 25 | 222 | 5550 | 0.016952 | 0.00067808 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | RECLOSER | No Power. Adverse Weather/Extreme Wind. Recloser T21 tripped. E/F. Tripped due to backfeed at PON1 (ABS V19). ABS V19 Open & Tagged. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 25 | 22 | 4884 | 0.014918 | 0.00067808 | 2014-05-25 | C | 0.014918 | 0.00067808 | 2015 | 2014-05-25 | C | 222 | 0.014918 | 0.00067808
1 | 140751 | 2014-05-25 13:17 | 2014-05-25 15:27 | 130 | 40 | 5200 | 0.015883 | 0.00012218 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Patrolled. Tree found in lines and cut away. Isolated beyond Links U41. No NDR Number supplied. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 130 | 127 | 5080 | 0.015516 | 0.00012218 | 2014-05-25 | C | 0.015516 | 0.00012218 | 2015 | 2014-05-25 | C | 40 | 0.015516 | 0.00012218
1 | 140752 | 2014-05-24 12:33 | 2014-05-25 15:45 | 1632 | 66 | 44530 | 0.13601 | 0.00020159 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Adverse Weather/Extreme Wind. Isolation for Safety undertaken beyond 11kV Fuses 7029 and 7702 and 7699 and 8153. Separate sites unable to have power restored until following day. Gavin Gray attended. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 674.697 | 671.697 | 44332 | 0.13541 | 0.00020159 | 2014-05-24 | C | 0.13541 | 0.00020159 | 2015 | 2014-05-24 | C | 66 | 0.13541 | 0.00020159
1 | 140753 | 2014-05-24 23:30 | 2014-05-25 14:51 | 921 | 230 | 211830 | 0.64702 | 0.00070252 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Auto Reclose CB3 tripped at 23.30 - Line Patrolled and A/R CB3 found open at 2.10am. Closed & tripped 02.13am. Floating conductor located beyond ABS U22. Due to poor communcations A/P was self issued. Mike Mabey a | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 921 | 918 | 211140 | 0.64491 | 0.00070252 | 2014-05-24 | C | 0.64491 | 0.00070252 | 2015 | 2014-05-24 | C | 230 | 0.64491 | 0.00070252
1 | 140755 | 2014-05-26 09:10 | 2014-05-26 10:00 | 50 | 9 | 450 | 0.0013745 | 2.749e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE HOLDER | SIN: 14/92407 - AP is for 1 hr to install a 400V Disc-Connector to the LV Of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV Disc-Connector. This is to be followed by a 400V shutdown to complete the 400V arm replac | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 423 | 0.001292 | 2.749e-05 | 2014-05-26 | B | 0.00064601 | 1.3745e-05 | 2015 | 2014-05-26 | B | 9 | 0.001292 | 2.749e-05
1 | 140756 | 2014-05-25 11:56 | 2014-05-25 14:25 | 149 | 9 | 1341 | 0.004096 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE | No Power. Adverse Weather/Extreme Wind. Line Patrolled. 3 x broken DDO's located. Isolated beyond PU474 . Pole 704220. Blair Gregg attended. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 149 | 146 | 1314 | 0.0040135 | 2.749e-05 | 2014-05-25 | C | 0.0040135 | 2.749e-05 | 2015 | 2014-05-25 | C | 9 | 0.0040135 | 2.749e-05
1 | 140758 | 2014-05-24 21:26 | 2014-05-25 14:40 | 1034 | 86 | 19084 | 0.058291 | 0.00026268 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | No Power. Adverse Weather/ Extreme Wind. Emergency Isolation required for broken Pole. Pole number not noted on Fault Record. Frank Edwards attended. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 221.907 | 218.907 | 18826 | 0.057503 | 0.00026268 | 2014-05-24 | C | 0.057503 | 0.00026268 | 2015 | 2014-05-24 | C | 86 | 0.057503 | 0.00026268
1 | 140759 | 2014-05-26 12:49 | 2014-05-26 14:22 | 93 | 32 | 2976 | 0.00909 | 9.7742e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE | No Power - Eltham CB R61 No Trip. Isolation to Change broken transformer Fuses 4486T. Isolation at Fuses 6051 No Back feeds available. Faultman Brett Bensley. Materials 3 11kV Fuses assemblies, 3 x 16mm sleeves 3x 130 M12 Bolts, 32 x 2Amp fuse links Pole | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 93 | 90 | 2880 | 0.0087967 | 9.7742e-05 | 2014-05-26 | C | 0.0087967 | 9.7742e-05 | 2015 | 2014-05-26 | C | 32 | 0.0087967 | 9.7742e-05
1 | 140760 | 2014-05-26 08:50 | 2014-05-26 14:27 | 337 | 10 | 3370 | 0.010293 | 3.0544e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92296 - Site 1: Change 33/11kV pole 205363. Site 2: Change 33kV "H" pole 209771 apply cover up gear to 11kV. Isolation points: 33kV ABS 3184 & 96; Site 1, 11kV LL break at pole 205352, Site 2: 11kV LL cover up gear at 209238. Refer LLP's 14/9 | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 337 | 334 | 3340 | 0.010202 | 3.0544e-05 | 2014-05-26 | B | 0.0051009 | 1.5272e-05 | 2015 | 2014-05-26 | B | 10 | 0.010202 | 3.0544e-05
1 | 140761 | 2014-05-24 19:15 | 2014-05-25 11:37 | 982 | 108 | 106056 | 0.32394 | 0.00032988 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Adverse Weather/Extreme Wind. Recloser T42 Tripped - No Flags. Line Patrolled. No Fault Located. Shazil Khan attended. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 982 | 979 | 105732 | 0.32295 | 0.00032988 | 2014-05-24 | C | 0.32295 | 0.00032988 | 2015 | 2014-05-24 | C | 108 | 0.32295 | 0.00032988
1 | 140762 | 2014-05-25 15:58 | 2014-05-25 17:00 | 62 | 24 | 1488 | 0.004545 | 7.3306e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Patrolled and tree located in lines at pole 27148. Materials Used = 40metres of wire. NDR #37461. Les Robinson attended. | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 1416 | 0.0043251 | 7.3306e-05 | 2014-05-25 | C | 0.0043251 | 7.3306e-05 | 2015 | 2014-05-25 | C | 24 | 0.0043251 | 7.3306e-05
1 | 140764 | 2014-05-26 09:25 | 2014-05-26 15:05 | 340 | 30 | 10200 | 0.031155 | 9.1633e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91790 - Replace 11kV conductor between ABS 658 and pole I878. Replace 11kV Xarms on poles I12495, I12496, I1870. Capacitor bank CC42 will have to be isolated and discharged as part of the isolation. Isolation points: 11kV Line break on pole 264586 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 340 | 337 | 10110 | 0.03088 | 9.1633e-05 | 2014-05-26 | B | 0.01544 | 4.5816e-05 | 2015 | 2014-05-26 | B | 30 | 0.03088 | 9.1633e-05
1 | 140767 | 2014-05-24 14:30 | 2014-05-25 10:30 | 1200 | 128 | 46350 | 0.14157 | 0.00039097 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power. Adverse Weather/Extreme Wind. Line Patrolled and Recloser 437 found open. Transformer T3783 found to have blown transformer fuses. Line isolated beyond ABS 7064 and repairs undertaken the following day. A Marshall attended. | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 362.1094 | 359.1094 | 45966 | 0.1404 | 0.00039097 | 2014-05-24 | C | 0.1404 | 0.00039097 | 2015 | 2014-05-24 | C | 128 | 0.1404 | 0.00039097
1 | 140768 | 2014-05-25 10:54 | 2014-05-25 17:00 | 366 | 23 | 8418 | 0.025712 | 7.0252e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Patrolled - Rusty No.8 Wire located. Temporary Line Break made at pole P11372. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 366 | 363 | 8349 | 0.025501 | 7.0252e-05 | 2014-05-25 | C | 0.025501 | 7.0252e-05 | 2015 | 2014-05-25 | C | 23 | 0.025501 | 7.0252e-05
1 | 140769 | 2014-05-24 17:08 | 2014-05-25 17:12 | 1444 | 113 | 152488 | 0.46576 | 0.00034515 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Recloser C224 tripped. No Flags. Adverse Weather/Extreme Wind. Line Patrolled. Cause of Fault not recorded. Dennis Rose attended. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1349.4513 | 1346.4513 | 152149 | 0.46473 | 0.00034515 | 2014-05-24 | C | 0.46473 | 0.00034515 | 2015 | 2014-05-24 | C | 113 | 0.46473 | 0.00034515
1 | 140770 | 2014-05-25 15:30 | 2014-05-25 16:53 | 83 | 1 | 83 | 0.00025352 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | No Power. Adverse Weather/Extreme Wind. Isolated beyond Fuses O1 and Transformer T3/3/88 replaced. | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 83 | 80 | 80 | 0.00024435 | 3.0544e-06 | 2014-05-25 | C | 0.00024435 | 3.054e-06 | 2015 | 2014-05-25 | C | 1 | 0.00024435 | 3.0544e-06
1 | 140771 | 2014-05-24 16:33 | 2014-05-25 16:35 | 1442 | 462 | 193602 | 0.59134 | 0.0014111 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Adverse Weather/Extreme Wind. Recloser 4242 Tripped - No Flags. Power restored. Additional fault located beyond Fuses 859. Note: This section of line was left off overnight and restored the following day. Allen Cox Attended. Notification 23.06 | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 419.0519 | 416.0519 | 192216 | 0.58711 | 0.0014111 | 2014-05-24 | C | 0.58711 | 0.0014111 | 2015 | 2014-05-24 | C | 462 | 0.58711 | 0.0014111
1 | 140772 | 2014-05-25 17:09 | 2014-05-25 17:37 | 28 | 9 | 252 | 0.00076971 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line Patrolled. Floating Conductor Located Beyond Fuses WH201. HV Binder changed. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 225 | 0.00068725 | 2.749e-05 | 2014-05-25 | C | 0.00068724 | 2.749e-05 | 2015 | 2014-05-25 | C | 9 | 0.00068725 | 2.749e-05
1 | 140773 | 2014-05-25 17:30 | 2014-05-25 17:39 | 9 | 251 | 2259 | 0.0068999 | 0.00076666 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Adverse Weather/Extreme Wind. Line Patrolled - Sectionaliser C639/2 found open. Closed and power restored. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 1506 | 0.0046 | 0.00076666 | 2014-05-25 | C | 0.0046 | 0.00076666 | 2015 | 2014-05-25 | C | 251 | 0.0046 | 0.00076666
1 | 140775 | 2014-05-24 15:13 | 2014-05-25 18:21 | 1628 | 62 | 86312 | 0.26363 | 0.00018937 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | SECTIONALISER | No Power. Sectionaliser C1050 Tripped - No Flags. Adverse Weather/Extreme Wind. Line Patrolled No Fault Loctaed. Dennis Rose Attended. | F5 | ANNEDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1392.129 | 1389.129 | 86126 | 0.26307 | 0.00018937 | 2014-05-24 | C | 0.26307 | 0.00018937 | 2015 | 2014-05-24 | C | 62 | 0.26307 | 0.00018937
1 | 140776 | 2014-05-25 14:25 | 2014-05-25 18:50 | 265 | 353 | 93545 | 0.28573 | 0.0010782 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | RECLOSER | No Power. Recloser 8097 tripped. E/F O/C AB Phase. Adverse Weather/Extreme Wind. Line patrolled - no fault located. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 265 | 262 | 92486 | 0.28249 | 0.0010782 | 2014-05-25 | C | 0.28249 | 0.0010782 | 2015 | 2014-05-25 | C | 353 | 0.28249 | 0.0010782
1 | 140777 | 2014-05-25 18:36 | 2014-05-25 22:24 | 228 | 95 | 11415 | 0.034866 | 0.00029017 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | No Power. CB 4 Tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled. 1 fuse found blown at Fuses S38 . Binder repaired. Trevor Pocock attended. | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 120.1579 | 117.1579 | 11130 | 0.033996 | 0.00029017 | 2014-05-25 | C | 0.033996 | 0.00029017 | 2015 | 2014-05-25 | C | 95 | 0.033996 | 0.00029017
1 | 140780 | 2014-05-25 18:14 | 2014-05-25 20:32 | 138 | 678 | 44174 | 0.13493 | 0.0020709 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C954 tripped. Adverse Weather/Extreme Wind. Line patrolled and trees located at Pole 818045. NDR number not supplied. | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 65.1534 | 62.1534 | 42140 | 0.12871 | 0.0020709 | 2014-05-25 | C | 0.12871 | 0.0020709 | 2015 | 2014-05-25 | C | 678 | 0.12871 | 0.0020709
1 | 140781 | 2014-05-26 04:32 | 2014-05-26 06:01 | 89 | 2 | 178 | 0.00054369 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line patrolled and located lines down at Pole 759044. Transformer 1577 isolated due to 11kV/400V contact. Nick Paton attended. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 89 | 86 | 172 | 0.00052536 | 6.1088e-06 | 2014-05-26 | C | 0.00052536 | 6.109e-06 | 2015 | 2014-05-26 | C | 2 | 0.00052536 | 6.1088e-06
1 | 140782 | 2014-05-25 10:00 | 2014-05-25 15:19 | 319 | 92 | 29348 | 0.089641 | 0.00028101 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Sectionaliser C632 found open. Lines Down? Material used: 150 metres conductor. Self issue of Access Pemit due to poor comms. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 319 | 316 | 29072 | 0.088798 | 0.00028101 | 2014-05-25 | C | 0.088798 | 0.00028101 | 2015 | 2014-05-25 | C | 92 | 0.088798 | 0.00028101
1 | 140783 | 2014-05-27 09:49 | 2014-05-27 09:54 | 5 | 1 | 5 | 1.5272e-05 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | No Power - Mangorei CB 6 No trip. Isolation of Transformer 405:N for Live Tank Oil Sampling. Chris Viviers | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 5 | 2 | 2 | 6.1088e-06 | 3.0544e-06 | 2014-05-27 | B | 3.054e-06 | 1.527e-06 | 2015 | 2014-05-27 | B | 1 | 6.1088e-06 | 3.0544e-06
1 | 140784 | 2014-05-26 06:00 | 2014-05-26 12:10 | 370 | 9 | 3330 | 0.010171 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Patrolled. Tree found through lines at Railway Road. Branch removed - no damage. Shane Walker attended. No NDR noted on Fault Record. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 370 | 367 | 3303 | 0.010089 | 2.749e-05 | 2014-05-26 | C | 0.010089 | 2.749e-05 | 2015 | 2014-05-26 | C | 9 | 0.010089 | 2.749e-05
1 | 140785 | 2014-05-25 21:00 | 2014-05-26 10:37 | 817 | 261 | 211221 | 0.64516 | 0.0007972 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | INSULATOR | No Power. CB C Tripped - No flags. Adverse Weather/Extreme Wind. Line patrolled - Isolation for trees through line at pole. 1 x broken HT cross arm, 1 x broken DDO crossarm and 3 x 11kV insulators also replaced during this outage. No NDR number supplied. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 809.2759 | 806.2759 | 210438 | 0.64277 | 0.0007972 | 2014-05-25 | C | 0.64277 | 0.00079721 | 2015 | 2014-05-25 | C | 261 | 0.64277 | 0.0007972
1 | 140786 | 2014-05-25 23:11 | 2014-05-26 08:33 | 562 | 256 | 135222 | 0.41303 | 0.00078193 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C955 tripped. ARC. Adverse Weather/Extreme Wind. Line patrolled - located tree branch across all 3 phases. No damage to conductor. Pole #819355. Not NDR number noted. | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 528.2109 | 525.2109 | 134454 | 0.41068 | 0.00078193 | 2014-05-25 | C | 0.41068 | 0.00078193 | 2015 | 2014-05-25 | C | 256 | 0.41068 | 0.00078193
1 | 140787 | 2014-05-25 20:16 | 2014-05-25 22:09 | 113 | 1445 | 157225 | 0.48023 | 0.0044136 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE | No Power. Adverse Weather/Extreme Wind. Emergency Offload due to Temp Links Burning. Temporary Links Open at Pole 822090 (Temporary Links between Poles 822090 & 847362). Burnt Up Links Removed and Conductors Joined. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 108.8062 | 105.8062 | 152890 | 0.46699 | 0.0044136 | 2014-05-25 | C | 0.46699 | 0.0044136 | 2015 | 2014-05-25 | C | 1445 | 0.46699 | 0.0044136
1 | 140788 | 2014-05-24 13:37 | 2014-05-26 12:16 | 2799 | 77 | 67911 | 0.20743 | 0.00023519 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Recloser 7417 tripped. Adverse Weather/Extreme Wind. Line patrolled and 3 separate faults located due to trees. Broken Conductors. Poles 365120, 367737 and 832155. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 881.961 | 878.961 | 67680 | 0.20672 | 0.00023519 | 2014-05-24 | C | 0.20672 | 0.00023519 | 2015 | 2014-05-24 | C | 77 | 0.20672 | 0.00023519
1 | 140791 | 2014-05-25 19:03 | 2014-05-26 12:40 | 1057 | 104 | 101428 | 0.3098 | 0.00031766 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C881 tripped - no flags. Adverse Weather/Extreme Wind. Line Patrolled. Tree located through line and conductor broken at pole 826647. Conductor rejoined. Adam Whale attended. No NDR number supplied. | F4 | HOLDSWORTH | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 975.2692 | 972.2692 | 101116 | 0.30885 | 0.00031766 | 2014-05-25 | C | 0.30885 | 0.00031766 | 2015 | 2014-05-25 | C | 104 | 0.30885 | 0.00031766
1 | 140792 | 2014-05-25 16:52 | 2014-05-26 14:26 | 1294 | 4 | 5176 | 0.01581 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line patrolled. 1x HV line down beyond Fuses 7100. Line rejointed. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1294 | 1291 | 5164 | 0.015773 | 1.2218e-05 | 2014-05-25 | C | 0.015773 | 1.2218e-05 | 2015 | 2014-05-25 | C | 4 | 0.015773 | 1.2218e-05
1 | 140793 | 2014-05-26 14:10 | 2014-05-26 14:35 | 25 | 152 | 3800 | 0.011607 | 0.00046427 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power. Adverse Weather/Extreme Wind. Line patrolled and broken HT lead to Transformer T2862 located and repaired. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 25 | 22 | 3344 | 0.010214 | 0.00046427 | 2014-05-26 | C | 0.010214 | 0.00046427 | 2015 | 2014-05-26 | C | 152 | 0.010214 | 0.00046427
1 | 140795 | 2014-05-27 13:30 | 2014-05-27 13:37 | 7 | 210 | 1470 | 0.00449 | 0.00064143 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - UG | No Power - Brooklands CB 12 No Trip. Live Tank Oil Testing of Switch Gear 416/2 required Opening of this Switch. Faultman Chris Viviers | F3 | BROOKLANDS 12 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 7 | 4 | 840 | 0.0025657 | 0.00064143 | 2014-05-27 | B | 0.0012829 | 0.00032071 | 2015 | 2014-05-27 | B | 210 | 0.0025657 | 0.00064143
1 | 140797 | 2014-05-27 09:10 | 2014-05-27 14:18 | 308 | 30 | 9240 | 0.028223 | 9.1633e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90041 - Replace 11kV pole, Xarms hardware at various sites in outage area. Remove TEMP62 DOFs on pole E0328 which are being installed on the 13th May 2014. Isolation points: 11kV ABS 1105 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 308 | 305 | 9150 | 0.027948 | 9.1633e-05 | 2014-05-27 | B | 0.013974 | 4.5816e-05 | 2015 | 2014-05-27 | B | 30 | 0.027948 | 9.1633e-05
1 | 140803 | 2014-05-27 10:00 | 2014-05-27 12:31 | 151 | 101 | 15251 | 0.046583 | 0.0003085 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91865 - Replace 11kV Transformer TC4445 (leaking oil). Isolation points: 11kV Fuse/Sw 9183/2. | F3 | PLEASANT POINT | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 151 | 148 | 14948 | 0.045658 | 0.0003085 | 2014-05-27 | B | 0.022829 | 0.00015425 | 2015 | 2014-05-27 | B | 101 | 0.045658 | 0.0003085
1 | 140808 | 2014-05-26 09:45 | 2014-05-26 11:27 | 102 | 43 | 4386 | 0.013397 | 0.00013134 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92376 - Change two 11kV Xarms at pole 356735/779831. Isolation points: R142, ABS 147, Links 155, Temp fuses 02 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 102 | 99 | 4257 | 0.013003 | 0.00013134 | 2014-05-26 | B | 0.0065013 | 6.567e-05 | 2015 | 2014-05-26 | B | 43 | 0.013003 | 0.00013134
1 | 140809 | 2014-05-27 14:30 | 2014-05-27 14:40 | 10 | 1 | 10 | 3.0544e-05 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | UNKNOWN | PATROLLED | DISTRIBUTION TRANSFORMER | LT Transformer Fuse - Short outage required at Transformer 4657W to safely replace HRC fuses. Relivened OK. | F2 | TAIHAPE TOWN NORTH | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 7 | 2.1381e-05 | 3.0544e-06 | 2014-05-27 | C | 2.1381e-05 | 3.054e-06 | 2015 | 2014-05-27 | C | 1 | 2.1381e-05 | 3.0544e-06
1 | 140811 | 2014-05-14 10:38 | 2014-05-14 12:50 | 132 | 38 | 5016 | 0.015321 | 0.00011607 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91426 - Install new 11m busck pole and replace damaged 11kV conductor. Isolation points: ABS U18, ABS U21 | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 132 | 129 | 4902 | 0.014973 | 0.00011607 | 2014-05-14 | B | 0.0074864 | 5.8034e-05 | 2015 | 2014-05-14 | B | 38 | 0.014973 | 0.00011607
1 | 140812 | 2014-05-21 08:45 | 2014-05-22 11:46 | 1621 | 257 | 52282 | 0.15969 | 0.00078499 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92582 - Replace defective TX T3219 and switch gear C1012/C 1014/C 1013 which is built into TX cubicle. C1013, C1014 and C284 will be closed after AP is returned w/ C1012 and C298 staying open so that C1012 cable can be terminated the day after. Is | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 203.4319 | 200.4319 | 51511 | 0.15734 | 0.00078499 | 2014-05-21 | B | 0.078668 | 0.00039249 | 2015 | 2014-05-21 | B | 257 | 0.15734 | 0.00078499
1 | 140814 | 2014-05-24 19:35 | 2014-05-24 20:20 | 45 | 134 | 6030 | 0.018418 | 0.00040929 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Fuse/sw SC4-514 found open (1 blown fuse) by f/man attending N/P call - cable test carried out on cable and found to be faulty - generator connected at transformers TC4-200 & TC4-230 for duration of outage - cable isolated at fuse/sw SC4-514 for repairs - | F3 | TOTARA ST NORTH | TRITON SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 5628 | 0.01719 | 0.00040929 | 2014-05-24 | C | 0.01719 | 0.00040929 | 2015 | 2014-05-24 | C | 134 | 0.01719 | 0.00040929
1 | 140815 | 2014-05-25 12:00 | 2014-05-25 16:21 | 261 | 1 | 261 | 0.0007972 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power - Blairlogie fuses 7139 opened and tagged. Self issue permit as no comms. Two broken conductors rejointed. Brad Keating attended. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 261 | 258 | 258 | 0.00078804 | 3.0544e-06 | 2014-05-25 | C | 0.00078804 | 3.054e-06 | 2015 | 2014-05-25 | C | 1 | 0.00078804 | 3.0544e-06
1 | 140816 | 2014-05-26 15:47 | 2014-05-26 16:35 | 48 | 20 | 960 | 0.0029322 | 6.1088e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | No Power. Adverse Weather/Extreme Wind. Line patrolled and insulator replaced beyond Fuse Q51. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 48 | 45 | 900 | 0.002749 | 6.1088e-05 | 2014-05-26 | C | 0.002749 | 6.1088e-05 | 2015 | 2014-05-26 | C | 20 | 0.002749 | 6.1088e-05
1 | 140819 | 2014-05-26 13:29 | 2014-05-26 18:34 | 305 | 175 | 30449 | 0.093004 | 0.00053452 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB Tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled and lines found down at Fuses V53. Line also located down past Fuse V56 at pole P22915. Tree located on line past ABS V55. Trees removed by hotstick at pole. Shazil Khan atte | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 173.9943 | 170.9943 | 29924 | 0.091401 | 0.00053452 | 2014-05-26 | C | 0.091401 | 0.00053452 | 2015 | 2014-05-26 | C | 175 | 0.091401 | 0.00053452
1 | 140820 | 2014-05-25 18:28 | 2014-05-26 16:40 | 1332 | 113 | 147223 | 0.44968 | 0.00034515 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. CB C224 tripped B & C and O/C. Adverse Weather/Extreme Wind. Line patrolled and 11kV line found to be hung up in tree. Earths applied at pole 837936. Brian Butler attended. No NDR number noted on fault record. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1302.8584 | 1299.8584 | 146884 | 0.44865 | 0.00034515 | 2014-05-25 | C | 0.44865 | 0.00034515 | 2015 | 2014-05-25 | C | 113 | 0.44865 | 0.00034515
1 | 140822 | 2014-05-28 08:56 | 2014-05-28 09:36 | 40 | 949 | 36607 | 0.11181 | 0.0028986 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | Other/miscellaneous cause - CB 7 Tripped O/C E/F - While Sectionalising received report of digger touching lines - Faultman checked over site and feeder returned to service - Attended by Neal Woodhead, Jade Williams and Brian Leithley NDR 45855 | F3 | BELL BLOCK 7 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 38.5743 | 35.5743 | 33760 | 0.10312 | 0.0028986 | 2014-05-28 | C | 0.10312 | 0.0028986 | 2015 | 2014-05-28 | C | 949 | 0.10312 | 0.0028986
1 | 140823 | 2014-05-25 21:18 | 2014-05-26 15:46 | 1108 | 17 | 2966 | 0.0090594 | 5.1925e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | No Power. Adverse Weather/Extreme Wind. Line patrolled. Break jumpers at Pole 831965 to isolate pole 831968 which had burnt down. Adrian Marshal attended. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 174.4706 | 171.4706 | 2915 | 0.0089036 | 5.1925e-05 | 2014-05-25 | C | 0.0089036 | 5.1925e-05 | 2015 | 2014-05-25 | C | 17 | 0.0089036 | 5.1925e-05
1 | 140824 | 2014-05-26 15:00 | 2014-05-26 18:00 | 180 | 50 | 4680 | 0.014295 | 0.00015272 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. CB C218/2 Tripped - No Flags. Adverse Weather/Extreme Wind. Feeder patrolled and sectionalised but nothing found. Suspect Line Clash. Power restored without further issues. Steve Johnson attended. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 93.6 | 90.6 | 4530 | 0.013837 | 0.00015272 | 2014-05-26 | C | 0.013837 | 0.00015272 | 2015 | 2014-05-26 | C | 50 | 0.013837 | 0.00015272
1 | 140825 | 2014-05-28 09:00 | 2014-05-28 12:00 | 180 | 1 | 180 | 0.0005498 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92183 - Replace 11kV Transformer and LV fuses on 11kV Transformer TC5087. Isolation points: 11kV Transformer fuses TC5087.NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Confirm Pre Commissioning | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 177 | 0.00054063 | 3.0544e-06 | 2014-05-28 | B | 0.00027032 | 1.527e-06 | 2015 | 2014-05-28 | B | 1 | 0.00054063 | 3.0544e-06
1 | 140826 | 2014-05-26 12:06 | 2014-05-26 13:06 | 60 | 47 | 2820 | 0.0086135 | 0.00014356 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power. Adverse Weather/Extreme Wind. Line patrolled. Twisted cross arm located and re-tightened with a new king bolt. Pa Koro attended. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 2679 | 0.0081828 | 0.00014356 | 2014-05-26 | C | 0.0081828 | 0.00014356 | 2015 | 2014-05-26 | C | 47 | 0.0081828 | 0.00014356
1 | 140827 | 2014-05-26 14:45 | 2014-05-26 16:15 | 90 | 172 | 15480 | 0.047282 | 0.00052536 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | No Power. Adverse Weather/Extreme Wind. Line patrolled and 824893 found broken at base. Kourarau A 33kV Line - Assurance of isolation received by NOC. Temporary repair undertaken and pole secured safely. Ben Taylor attended. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 14964 | 0.045706 | 0.00052536 | 2014-05-26 | C | 0.045706 | 0.00052536 | 2015 | 2014-05-26 | C | 172 | 0.045706 | 0.00052536
1 | 140828 | 2014-05-26 16:00 | 2014-05-26 16:59 | 59 | 251 | 14809 | 0.045233 | 0.00076666 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. CB C639 Tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled - nothing located. Suspect Line Clash as the cause. Adam Whale attended. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 59 | 56 | 14056 | 0.042933 | 0.00076666 | 2014-05-26 | C | 0.042933 | 0.00076666 | 2015 | 2014-05-26 | C | 251 | 0.042933 | 0.00076666
1 | 140829 | 2014-05-25 21:21 | 2014-05-26 16:34 | 1153 | 7 | 8071 | 0.024652 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Line patrolled. Trees cut away at pole 797598 - no damage to conductor. No NDR supplied with fault record. Dave Ngatai attended. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1153 | 1150 | 8050 | 0.024588 | 2.1381e-05 | 2014-05-25 | C | 0.024588 | 2.1381e-05 | 2015 | 2014-05-25 | C | 7 | 0.024588 | 2.1381e-05
1 | 140830 | 2014-05-25 17:50 | 2014-05-26 13:09 | 1159 | 632 | 727602 | 2.2224 | 0.0019304 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | UNKNOWN | No Power. TP Mangamaiere CB1272 Tripped E/F. TP Mangamaire CB 1332 Tripped E/F. Pongaroa CB XT 30 opened to isolatte Pongaroa Sub for fault finding. Adverse Weather/Extreme Wind. Patrolled. Found 1 phase missing on 33kV at CB XT30. Broken Jumper also loca | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1151.269 | 1148.269 | 725706 | 2.2166 | 0.0019304 | 2014-05-25 | C | 2.2166 | 0.0019304 | 2015 | 2014-05-25 | C | 632 | 2.2166 | 0.0019304
1 | 140833 | 2014-05-26 06:00 | 2014-05-26 17:00 | 660 | 3 | 1980 | 0.0060478 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | No Power. Fuses L63 tripped. Adverse Weather/Extreme Wind. Line patrolled. Broke pole (P23108). Broken pole replaced including cross arms & 3 x insulators. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 660 | 657 | 1971 | 0.0060203 | 9.1633e-06 | 2014-05-26 | C | 0.0060203 | 9.163e-06 | 2015 | 2014-05-26 | C | 3 | 0.0060203 | 9.1633e-06
1 | 140834 | 2014-05-28 07:43 | 2014-05-28 09:13 | 90 | 1732 | 10233 | 0.031256 | 0.0052903 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Faultman found a blown jumper at ABS Q1 after receiving fault calls of part power line was isolated at CB 5, ABS"s Q2 and Q4 to replace the blown jumper at pole P00065, Attended by Robin Smith. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 5.9082 | 2.9082 | 5037 | 0.015385 | 0.0052903 | 2014-05-28 | C | 0.015385 | 0.0052903 | 2015 | 2014-05-28 | C | 1732 | 0.015385 | 0.0052903
1 | 140835 | 2014-05-26 09:36 | 2014-05-26 15:13 | 337 | 353 | 112407 | 0.34334 | 0.0010782 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. CB8097 tripped pH A & B O/C. Adverse Weather/Extreme Wind. Line patrolled. Floating conductor located at pole 835679. Joe Matthews attended. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 318.4334 | 315.4334 | 111348 | 0.3401 | 0.0010782 | 2014-05-26 | C | 0.3401 | 0.0010782 | 2015 | 2014-05-26 | C | 353 | 0.3401 | 0.0010782
1 | 140836 | 2014-05-25 19:03 | 2014-05-26 16:40 | 1297 | 80 | 101474 | 0.30994 | 0.00024435 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | No Power. CB C281 tripped AR & O/C. Adverse Weather/Extreme Wind. Line patrolled and twisted cross arm located and straightened at pole 835995. Joe Matthews attended. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1268.425 | 1265.425 | 101234 | 0.30921 | 0.00024435 | 2014-05-25 | C | 0.30921 | 0.00024435 | 2015 | 2014-05-25 | C | 80 | 0.30921 | 0.00024435
1 | 140837 | 2014-05-25 22:26 | 2014-05-26 17:35 | 1149 | 181 | 20620 | 0.062982 | 0.00055285 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | POLE | No Power. Recloser C216 tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled. Trees found on lines. Broken pole 843715 located and broken conductor. Also located broken pole 834808. No NDR noted on Fault Record. Gavin Paget attended. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 113.9227 | 110.9227 | 20077 | 0.061324 | 0.00055285 | 2014-05-25 | C | 0.061324 | 0.00055285 | 2015 | 2014-05-25 | C | 181 | 0.061324 | 0.00055285
1 | 140838 | 2014-05-26 12:00 | 2014-05-27 15:30 | 1650 | 14 | 2300 | 0.0070252 | 4.2762e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Outage required from ABS S174 to replace broken crossarm. Crossarm replaced, relivened OK | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 164.2857 | 161.2857 | 2258 | 0.0068969 | 4.2762e-05 | 2014-05-26 | C | 0.0068969 | 4.2762e-05 | 2015 | 2014-05-26 | C | 14 | 0.0068969 | 4.2762e-05
1 | 140839 | 2014-05-25 16:00 | 2014-05-27 12:20 | 2660 | 4 | 10640 | 0.032499 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Fuses 7745 tripped. No Flags - Adverse Weather/Extreme Wind. Line patrolled. Broken conductor located and rejointed at pole 834421. Shane Walker attended. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 2660 | 2657 | 10628 | 0.032462 | 1.2218e-05 | 2014-05-25 | C | 0.032462 | 1.2218e-05 | 2015 | 2014-05-25 | C | 4 | 0.032462 | 1.2218e-05
1 | 140840 | 2014-05-24 17:41 | 2014-05-24 19:15 | 94 | 26 | 2276 | 0.0069519 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Trees - Outage required between Fuses V16 & ABS V19 to repair lines bought down in storm event. Downed line disconnected and made safe until resources available for repairs. Lines repaired, restored OK. No NDR noted on fault record. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.5385 | 84.5385 | 2198 | 0.0067136 | 7.9415e-05 | 2014-05-24 | C | 0.0067136 | 7.9415e-05 | 2015 | 2014-05-24 | C | 26 | 0.0067136 | 7.9415e-05
1 | 140841 | 2014-05-27 10:26 | 2014-05-27 12:40 | 134 | 21 | 2814 | 0.0085951 | 6.4143e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | No Power. Adverse Weather/Extreme Wind. Line patrolled and broken pole located (to be replaced after storm - undertaken in FR140839). Broken pole replaced/cross arm & 3 x insulators. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 134 | 131 | 2751 | 0.0084027 | 6.4143e-05 | 2014-05-27 | C | 0.0084027 | 6.4143e-05 | 2015 | 2014-05-27 | C | 21 | 0.0084027 | 6.4143e-05
1 | 140842 | 2014-05-25 16:00 | 2014-05-27 14:25 | 2785 | 55 | 58690 | 0.17926 | 0.00016799 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Transpower - Recloser C269/2 Tripped, no flags (trip time estimated, no SCADA). Lines past Links 7113 isolated for safety because of multiple cases of trees through lines. Lines to be repaired when resources available. Repaired 2 broken conductors and rem | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1067.0909 | 1064.0909 | 58525 | 0.17876 | 0.00016799 | 2014-05-25 | C | 0.17876 | 0.00016799 | 2015 | 2014-05-25 | C | 55 | 0.17876 | 0.00016799
1 | 140843 | 2014-05-25 22:16 | 2014-05-25 23:30 | 74 | 133 | 9842 | 0.030062 | 0.00040624 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | No Power. No Power. Adverse Weather/Extreme Wind. Line patrolled and 2x blown jumpers located at ABS S588. Outage occurred whilst backfeed was being undertaken. Later repaired Live Line. Neville Pope attended. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 74 | 71 | 9443 | 0.028843 | 0.00040624 | 2014-05-25 | C | 0.028843 | 0.00040624 | 2015 | 2014-05-25 | C | 133 | 0.028843 | 0.00040624
1 | 140844 | 2014-05-26 22:00 | 2014-05-27 12:10 | 850 | 92 | 78200 | 0.23886 | 0.00028101 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. CB C632/2 tripped - no flags. Adverse Weather/Extreme Wind. Tripped during night, patrolled and reclosed okay. Suspect line clash due to high winds. C Naylor attended. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 850 | 847 | 77924 | 0.23801 | 0.00028101 | 2014-05-26 | C | 0.23801 | 0.00028101 | 2015 | 2014-05-26 | C | 92 | 0.23801 | 0.00028101
1 | 140845 | 2014-05-27 11:00 | 2014-05-27 13:04 | 124 | 9 | 1116 | 0.0034087 | 2.749e-05 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT BIRD | CONDUCTOR | No Power. Line patrolled and floating conductor found at pole P01499. Not storm related - suspect bird strike.T Pocock attended. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 124 | 121 | 1089 | 0.0033263 | 2.749e-05 | 2014-05-27 | C | 0.0033263 | 2.749e-05 | 2015 | 2014-05-27 | C | 9 | 0.0033263 | 2.749e-05
1 | 140846 | 2014-05-26 21:00 | 2014-05-27 12:30 | 930 | 4 | 3720 | 0.011362 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Fuses 7771 Tripped - No Flags. Adverse Weather/Extreme Wind. Line patrolled and trees found through line. 2 x broken conductors rejointed. Ben Edwards attended. No NDR noted on Fault Record. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 930 | 927 | 3708 | 0.011326 | 1.2218e-05 | 2014-05-26 | C | 0.011326 | 1.2218e-05 | 2015 | 2014-05-26 | C | 4 | 0.011326 | 1.2218e-05
1 | 140847 | 2014-05-25 17:29 | 2014-05-26 13:05 | 1176 | 226 | 74470 | 0.22746 | 0.0006903 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB 3 tripped, no flags. Line patrolled & feeder sectionalised. Fault located and an outage required between Recloser U39 & ABS 10169 to repair conductors bought down by trees in storm event. Lines repaired, restored OK. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 329.5133 | 326.5133 | 73792 | 0.22539 | 0.0006903 | 2014-05-25 | C | 0.22539 | 0.0006903 | 2015 | 2014-05-25 | C | 226 | 0.22539 | 0.0006903
1 | 140848 | 2014-05-26 22:00 | 2014-05-27 13:45 | 945 | 32 | 29292 | 0.08947 | 9.7742e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. CB C633/2 tripped - no flags. Adverse Weather/Extreme Wind. Line patrolled and floating conductor located at pole 811768. Conductor rebound and power restored. C Naylor attended. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 915.375 | 912.375 | 29196 | 0.089177 | 9.7742e-05 | 2014-05-26 | C | 0.089177 | 9.7742e-05 | 2015 | 2014-05-26 | C | 32 | 0.089177 | 9.7742e-05
1 | 140849 | 2014-05-26 12:32 | 2014-05-26 14:56 | 144 | 121 | 11376 | 0.034747 | 0.00036959 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - CB 2 Tripped, no flags. Line patrolled and broken binder found, damaged by storm event. Outage required from Recloser V27 to repair. Repaired and relivened. Sectionaliser V41 found tripped as a result of earlier fault and closed OK. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 94.0165 | 91.0165 | 11013 | 0.033638 | 0.00036959 | 2014-05-26 | C | 0.033638 | 0.00036959 | 2015 | 2014-05-26 | C | 121 | 0.033638 | 0.00036959
1 | 140850 | 2014-05-25 13:00 | 2014-05-27 13:57 | 2937 | 55 | 73647 | 0.22495 | 0.00016799 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Recloser V5 tripped A/B & O/C & E/F. Adverse Weather/Extreme Wind. Line patrolled and 2 damaged (floating conductors) located either side of pole P06647. Repaired/rejointed. Bruce Mehrtens attended. This fault record only covers the restoration | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1339.0364 | 1336.0364 | 73482 | 0.22445 | 0.00016799 | 2014-05-25 | C | 0.22445 | 0.00016799 | 2015 | 2014-05-25 | C | 55 | 0.22445 | 0.00016799
1 | 140851 | 2014-05-24 22:01 | 2014-05-24 22:39 | 38 | 124 | 4712 | 0.014392 | 0.00037875 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Outage required Between Reslocer 6616/2 & ABS 5536 with back feed from Sectionaliser 6283, to repair broken jumper. Jumper repaired, relivened OK. | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 38 | 35 | 4340 | 0.013256 | 0.00037875 | 2014-05-24 | C | 0.013256 | 0.00037875 | 2015 | 2014-05-24 | C | 124 | 0.013256 | 0.00037875
1 | 140852 | 2014-05-28 09:25 | 2014-05-28 15:05 | 340 | 81 | 27540 | 0.084119 | 0.00024741 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92081 - Replace 11kV pole P30352 and 9 11kV Xarms. Isolation points: O52, O49 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 340 | 337 | 27297 | 0.083377 | 0.00024741 | 2014-05-28 | B | 0.041688 | 0.0001237 | 2015 | 2014-05-28 | B | 81 | 0.083377 | 0.00024741
1 | 140853 | 2014-05-23 14:49 | 2014-05-23 16:29 | 100 | 148 | 8310 | 0.025382 | 0.00045205 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. CB M81 tripped A + B O/C. Adverse Weather/Extreme Wind. Patrolled and 1 line found down. S Khan attended. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56.1486 | 53.1486 | 7866 | 0.024026 | 0.00045205 | 2014-05-23 | C | 0.024026 | 0.00045205 | 2015 | 2014-05-23 | C | 148 | 0.024026 | 0.00045205
1 | 140854 | 2014-05-28 09:45 | 2014-05-28 13:45 | 240 | 3 | 720 | 0.0021992 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | LV FAULT - OTHER | SIN: 14/92499 - Replace low voltage TX Xarms on TX pole X978. Isolation points: X978 | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 711 | 0.0021717 | 9.1633e-06 | 2014-05-28 | B | 0.0010858 | 4.582e-06 | 2015 | 2014-05-28 | B | 3 | 0.0021717 | 9.1633e-06
1 | 140855 | 2014-05-26 12:00 | 2014-05-28 13:23 | 2963 | 1 | 2963 | 0.0090503 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | Wind - Faultman found Fuses 7105 open on investigation found at pole 359758 broken and transformer T2013 on the ground after storm past through, line was isolated at Fuses 7105 to replace the transformer and pole. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 2963 | 2960 | 2960 | 0.0090411 | 3.0544e-06 | 2014-05-26 | C | 0.0090411 | 3.054e-06 | 2015 | 2014-05-26 | C | 1 | 0.0090411 | 3.0544e-06
1 | 140856 | 2014-05-24 09:16 | 2014-05-26 15:12 | 3236 | 256 | 115742 | 0.35353 | 0.00078193 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme Wind. Patrolled and lines found down. Dave Whale attended. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 452.1172 | 449.1172 | 114974 | 0.35118 | 0.00078193 | 2014-05-24 | C | 0.35118 | 0.00078193 | 2015 | 2014-05-24 | C | 256 | 0.35118 | 0.00078193
1 | 140857 | 2014-05-28 06:51 | 2014-05-28 10:11 | 200 | 53 | 6088 | 0.018595 | 0.00016188 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | CONDUCTOR | Defective Component - CB C844 tripped, received a call from customer of a line down, after investigation Faultman found line down at pole 839708, line was isolated at ABS S158 and at CB C844 to repair the line down. | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 114.8679 | 111.8679 | 5929 | 0.01811 | 0.00016188 | 2014-05-28 | C | 0.01811 | 0.00016188 | 2015 | 2014-05-28 | C | 53 | 0.01811 | 0.00016188
1 | 140859 | 2014-05-28 11:50 | 2014-05-28 15:45 | 235 | 251 | 24598 | 0.075133 | 0.00076666 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component -Faultan found a broken jumper and broken Fuse holders to transformer T1684, line was isolated at Links C639/6 and ABS C639/1 to make the repair to jumper and replace 2 Fuse holders, this line was isolated twice due to after the first | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98 | 95 | 23845 | 0.072833 | 0.00076666 | 2014-05-28 | C | 0.072833 | 0.00076666 | 2015 | 2014-05-28 | C | 251 | 0.072833 | 0.00076666
1 | 140860 | 2014-05-27 11:17 | 2014-05-28 15:13 | 1676 | 2 | 3352 | 0.010238 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component -Isolation to repair downed line to Pumpshed at Pole 228423. Farmer ok with leaving power off until next day. Isolation at Fuses SF7-015. Mike Strange and Andy Wreaks Faultmen. Materials used: 1 X HV Crossarm, 3 11kV Insulators and 15 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 1676 | 1673 | 3346 | 0.01022 | 6.1088e-06 | 2014-05-27 | C | 0.01022 | 6.109e-06 | 2015 | 2014-05-27 | C | 2 | 0.01022 | 6.1088e-06
1 | 140861 | 2014-05-28 09:25 | 2014-05-28 14:25 | 300 | 6 | 1800 | 0.005498 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92229 - Replacing 400V Xarms. At 11kV Transformer TC3451 from transformer fuses. Isolation points: 11kV Transformer Fuse TC3451.NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 300 | 297 | 1782 | 0.005443 | 1.8327e-05 | 2014-05-28 | B | 0.0027215 | 9.163e-06 | 2015 | 2014-05-28 | B | 6 | 0.005443 | 1.8327e-05
1 | 140862 | 2014-05-28 10:50 | 2014-05-28 12:15 | 85 | 1 | 85 | 0.00025963 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/92182 - Replace 11kV Transformer and LV fuses on TC2179. Isolation points: HV TX fuses TC2179. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP.Confirm Pre Commissioning & Inspection Certificate Comple | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 85 | 82 | 82 | 0.00025046 | 3.0544e-06 | 2014-05-28 | B | 0.00012523 | 1.527e-06 | 2015 | 2014-05-28 | B | 1 | 0.00025046 | 3.0544e-06
1 | 140864 | 2014-05-28 09:00 | 2014-05-28 10:00 | 60 | 1 | 60 | 0.00018327 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92183 - Replace 11kV Transformer and LV fuses on 11kV Transformer TC5087. Isolation points: 11kV Transformer fuses TC5087.NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Confirm Pre Commissioning | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 57 | 0.0001741 | 3.0544e-06 | 2014-05-28 | B | 8.7051e-05 | 1.527e-06 | 2015 | 2014-05-28 | B | 1 | 0.0001741 | 3.0544e-06
1 | 140867 | 2014-05-28 08:45 | 2014-05-28 17:31 | 526 | 6 | 3156 | 0.0096398 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92289 - Replace 33kV /11kV H pole 200203, 200204. Join 11kV cable to extend to O/H on new pole and phase check feeder cable at pole 855578. Isolation points: 33kV ABS 126,1053, 1054, 33kV ABS 146, 1055, 1041; 11kV Sw/gear S5790 & Line Break at p | F3 | BETHLEHEM | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 526 | 523 | 3138 | 0.0095848 | 1.8327e-05 | 2014-05-28 | B | 0.0047924 | 9.163e-06 | 2015 | 2014-05-28 | B | 6 | 0.0095848 | 1.8327e-05
1 | 140870 | 2014-05-28 09:15 | 2014-05-28 15:04 | 349 | 202 | 70498 | 0.21533 | 0.00061699 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/89347 - Replace 6.6kV pole 707933 and pole 707880. Isolation points:6.6kV Sw/gear 6651/3, ABS 5506, ABS 5531. | F3 | BROOKES ST | INGLEWOOD SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 349 | 346 | 69892 | 0.21348 | 0.00061699 | 2014-05-28 | B | 0.10674 | 0.0003085 | 2015 | 2014-05-28 | B | 202 | 0.21348 | 0.00061699
1 | 140872 | 2014-05-28 18:00 | 2014-05-28 19:10 | 70 | 51 | 3570 | 0.010904 | 0.00015578 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Other/miscellaneous cause - Short outage required on Transformer T1982 to safely repair LV leads at back of transformmer. Relivened OK. | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 3417 | 0.010437 | 0.00015578 | 2014-05-28 | C | 0.010437 | 0.00015578 | 2015 | 2014-05-28 | C | 51 | 0.010437 | 0.00015578
1 | 140873 | 2014-05-28 23:00 | 2014-05-29 01:23 | 143 | 4 | 572 | 0.0017471 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component - Fuses found tripped on Transformer T1364. Faulty transformer needed replacement. Isolation required from Fuses 8288 to safely replace all 3 DDO Fuse holders which were also in poor condition. Relivened OK. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 143 | 140 | 560 | 0.0017105 | 1.2218e-05 | 2014-05-28 | C | 0.0017105 | 1.2218e-05 | 2015 | 2014-05-28 | C | 4 | 0.0017105 | 1.2218e-05
1 | 140874 | 2014-05-25 17:14 | 2014-05-28 16:15 | 4261 | 3 | 12783 | 0.039045 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | TREE CONTACTS | OTHER VEGETATION | DISTRIBUTION TRANSFORMER | Trees - faultman found Fuses 7120 open after investigation found a tree had gone through the line and broken pole 827549 and transformer T1733 was on the ground, line was isolated at Fuses 7120 to replace the pole 827549 and transformer T1733. Brad Keatin | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 4261 | 4258 | 12774 | 0.039017 | 9.1633e-06 | 2014-05-25 | C | 0.039017 | 9.163e-06 | 2015 | 2014-05-25 | C | 3 | 0.039017 | 9.1633e-06
1 | 140875 | 2014-05-26 10:30 | 2014-05-26 18:27 | 477 | 1 | 477 | 0.001457 | 3.0544e-06 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Defective Component - Fuses 10172/4 tripped. Cable fault found. Cable was rebolted. Nick Brown attended. | F3 | PIONEER | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 477 | 474 | 474 | 0.0014478 | 3.0544e-06 | 2014-05-26 | C | 0.0014478 | 3.054e-06 | 2015 | 2014-05-26 | C | 1 | 0.0014478 | 3.0544e-06
1 | 140876 | 2014-04-10 09:16 | 2014-04-10 14:52 | 336 | 1 | 336 | 0.0010263 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91352 - Replace 11kV poles & cross arms.Urgent changes to switching AP14/90270 Links not installed So 922 check open & tag only. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 336 | 333 | 333 | 0.0010171 | 3.0544e-06 | 2014-04-10 | B | 0.00050856 | 1.527e-06 | 2015 | 2014-04-10 | B | 1 | 0.0010171 | 3.0544e-06
1 | 140878 | 2014-05-29 09:00 | 2014-05-29 10:33 | 93 | 6 | 558 | 0.0017044 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/92280 - Trim trees on spur line to T3362 (dangerous condition). No 11kV fuses at T/O and proactive treemaintenance at front of property (trees encroaching). Isolation points: S388, 7178, S564 | F4 | OTARAIA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 93 | 90 | 540 | 0.0016494 | 1.8327e-05 | 2014-05-29 | B | 0.00082469 | 9.163e-06 | 2015 | 2014-05-29 | B | 6 | 0.0016494 | 1.8327e-05
1 | 140882 | 2014-05-29 13:30 | 2014-05-29 14:15 | 45 | 25 | 1125 | 0.0034362 | 7.6361e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92353 - Connect onto 11kV new DO fuses to 100kVA 3 phase pole TX. Isolation points: 7523 | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 1050 | 0.0032071 | 7.6361e-05 | 2014-05-29 | B | 0.0016036 | 3.818e-05 | 2015 | 2014-05-29 | B | 25 | 0.0032071 | 7.6361e-05
1 | 140883 | 2014-04-10 08:58 | 2014-04-10 11:27 | 149 | 54 | 8046 | 0.024576 | 0.00016494 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90626 - AP1: Replace defective 11kV safelink CFC 9598. AP2: Start testing 11kV cable between 9598/3 and TC4310. Prior testing has indicated a fault on this cable but testing was abandoned b/c a fault developed on the earth switch on 9598/3. Isolat | F3 | MOSSOPS RD | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 149 | 146 | 7884 | 0.024081 | 0.00016494 | 2014-04-10 | B | 0.012041 | 8.2469e-05 | 2015 | 2014-04-10 | B | 54 | 0.024081 | 0.00016494
1 | 140884 | 2014-04-11 09:00 | 2014-04-11 14:49 | 349 | 24 | 840 | 0.0025657 | 7.3306e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/90448 - AP1: connect temp generator to TX TC3672 and restore supply to customers by 1000. Replace existing series one SD3 unit w/ Safelink CFC unit 9817/1 /2 /3. TP1: Test 11kV cables that will be connected to the new switch unit. AP2: Connect 11k | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 768 | 0.0023458 | 7.3306e-05 | 2014-04-11 | B | 0.0011729 | 3.6653e-05 | 2015 | 2014-04-11 | B | 24 | 0.0023458 | 7.3306e-05
1 | 140885 | 2014-04-10 09:40 | 2014-04-10 15:00 | 320 | 91 | 29120 | 0.088945 | 0.00027795 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/89176 - Replace 11kV Transformer 3506T. Isolation points: 11kV Fuse 5392. Confirm Pre Commissioning & Inspection Certificate Completed & Equipment Ready for Livening. Changed to Alt date due to weather. MR | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 320 | 317 | 28847 | 0.088111 | 0.00027795 | 2014-04-10 | B | 0.044055 | 0.00013898 | 2015 | 2014-04-10 | B | 91 | 0.088111 | 0.00027795
1 | 140886 | 2014-05-29 11:47 | 2014-05-29 12:42 | 55 | 175 | 9625 | 0.029399 | 0.00053452 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CROSSARM | Accident - CB 10 tripped on b phase O/C flags, received a call from customer that a tractor had brought down lines at transformer X4233, after investigation line was isolated at ABS's 702, 452, 2685 and 889, to cut a line break at pole 792345. CB 10 was r | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 9100 | 0.027795 | 0.00053452 | 2014-05-29 | C | 0.027795 | 0.00053452 | 2015 | 2014-05-29 | C | 175 | 0.027795 | 0.00053452
1 | 140887 | 2014-04-16 09:45 | 2014-04-16 10:00 | 15 | 28 | 420 | 0.0012829 | 8.5524e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/91005 - Off load TX T2/845, make gap P43527, replace 11kV ABS pole A91 and close gap. Isolation points: gap at P43527, B14, B43, B3. Associated LLP 14/91006 & 14/91007 | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 336 | 0.0010263 | 8.5524e-05 | 2014-04-16 | B | 0.00051314 | 4.2762e-05 | 2015 | 2014-04-16 | B | 28 | 0.0010263 | 8.5524e-05
1 | 140889 | 2014-04-30 09:05 | 2014-04-30 14:54 | 349 | 69 | 24081 | 0.073554 | 0.00021076 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90491 - Replace 11kV crossarms between O62 to O67 over 5 days. Isolation points: O67 to gap P34365 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 349 | 346 | 23874 | 0.072921 | 0.00021076 | 2014-04-30 | B | 0.036461 | 0.00010538 | 2015 | 2014-04-30 | B | 69 | 0.072921 | 0.00021076
1 | 140890 | 2014-05-29 11:47 | 2014-05-29 13:58 | 131 | 205 | 26855 | 0.082027 | 0.00062616 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | Accident - CB 10 tripped on b phase O/C flags, received a call from customer that a tractor had brought down lines at transformer X4233, after investigation line was isolated at ABS's 702, 452, 2685 and 889, to cut a line break at pole 792345. CB 10 was r | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 131 | 128 | 26240 | 0.080148 | 0.00062616 | 2014-05-29 | C | 0.080148 | 0.00062616 | 2015 | 2014-05-29 | C | 205 | 0.080148 | 0.00062616
1 | 140891 | 2014-05-29 11:47 | 2014-05-29 13:57 | 130 | 607 | 61220 | 0.18699 | 0.001854 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | CONDUCTOR | Accident - CB 10 tripped on b phase O/C flags, received a call from customer that a tractor had brought down lines at transformer X4233, after investigation line was isolated at ABS's 702, 452, 2685 and 889, to cut a line break at pole 792345. CB 10 was r | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 100.8567 | 97.8567 | 59399 | 0.18143 | 0.001854 | 2014-05-29 | C | 0.18143 | 0.001854 | 2015 | 2014-05-29 | C | 607 | 0.18143 | 0.001854
1 | 140892 | 2014-04-30 08:33 | 2014-04-30 15:17 | 404 | 183 | 73932 | 0.22582 | 0.00055896 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | RECLOSER | SIN: 14/90745 - Isolate T2250 and open C267 and C217 to make a LL cut at pole 836506. Replace 11kV circuit breakers and poles at site C267 and C217. Both C267 and C217 will be operational but have no SCADA at completion of this switching and the techs wil | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 404 | 401 | 73383 | 0.22414 | 0.00055896 | 2014-04-30 | B | 0.11207 | 0.00027948 | 2015 | 2014-04-30 | B | 183 | 0.22414 | 0.00055896
1 | 140893 | 2014-04-30 10:30 | 2014-04-30 14:02 | 212 | 1 | 212 | 0.00064754 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91350 - Downgrade TX 4657W from 500kVA to 100kVA at Taihape school. No 400V backfeed available for school. Isolation points: FABS 4495 | F2 | TAIHAPE TOWN NORTH | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 212 | 209 | 209 | 0.00063837 | 3.0544e-06 | 2014-04-30 | B | 0.00031919 | 1.527e-06 | 2015 | 2014-04-30 | B | 1 | 0.00063837 | 3.0544e-06
1 | 140894 | 2014-05-01 08:45 | 2014-05-01 14:28 | 343 | 17 | 5831 | 0.01781 | 5.1925e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91307 - Remove temporary fuse TEMP56, Alfredton Road - Reconductor between poles P2543, P10615. 11kV. Isolation points links I5, I6, ABS I7. | F4 | IHURAUA | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 343 | 340 | 5780 | 0.017655 | 5.1925e-05 | 2014-05-01 | B | 0.0088273 | 2.5963e-05 | 2015 | 2014-05-01 | B | 17 | 0.017655 | 5.1925e-05
1 | 140895 | 2014-05-29 09:06 | 2014-05-29 11:10 | 124 | 195 | 16954 | 0.051785 | 0.00059561 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -Faultman found Recloser C279/2 open after receiving fault calls, line was sectionalised and patrolled and no fault was found, Tony Sinclair attened. | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 86.9436 | 83.9436 | 16369 | 0.049998 | 0.00059561 | 2014-05-29 | C | 0.049998 | 0.00059561 | 2015 | 2014-05-29 | C | 195 | 0.049998 | 0.00059561
1 | 140896 | 2014-05-01 09:00 | 2014-05-01 14:44 | 344 | 41 | 14104 | 0.04308 | 0.00012523 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90493 - Replace 11kV crossarms between O62 to O67 over 5 days. Isolation points: O62 to gap P34365 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 13981 | 0.042704 | 0.00012523 | 2014-05-01 | B | 0.021352 | 6.2616e-05 | 2015 | 2014-05-01 | B | 41 | 0.042704 | 0.00012523
1 | 140897 | 2014-05-24 09:50 | 2014-05-24 21:39 | 709 | 963 | 636297 | 1.9435 | 0.0029414 | No Power | 33000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Defective Component - at 09:50, Mangamaire GXP, 33kV CB 1352 Tripped, E/F, L/O. This caused an outage to Parkville Sub. At 09:59 Pongaroa Sub, 33kV CB XT50 closed & tripped, L/O in attempt to backfeed Alfredton Sub. Investigations began. Multiple Faults f | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 660.7445 | 657.7445 | 633408 | 1.9347 | 0.0029414 | 2014-05-24 | C | 1.9347 | 0.0029414 | 2015 | 2014-05-24 | C | 963 | 1.9347 | 0.0029414
1 | 140898 | 2014-05-29 08:30 | 2014-05-29 15:36 | 426 | 23 | 9798 | 0.029927 | 7.0252e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91348 - Replacing conductor between poles 803097 to 803117 and 803117 to 847176. Isolation points: Fuse 887 | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 426 | 423 | 9729 | 0.029716 | 7.0252e-05 | 2014-05-29 | B | 0.014858 | 3.5126e-05 | 2015 | 2014-05-29 | B | 23 | 0.029716 | 7.0252e-05
1 | 140899 | 2014-05-29 10:33 | 2014-05-29 12:24 | 111 | 23 | 2553 | 0.0077979 | 7.0252e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | POLE | Wind -Line was isolated between ABS's T8, T9 and S44 to replace a damaged pole P37778 that was damaged in the storm on the 24/05/14, pole was been held up with a line truck until replacement could be replaced. Phil Barnes attened. | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 111 | 108 | 2484 | 0.0075872 | 7.0252e-05 | 2014-05-29 | C | 0.0075872 | 7.0252e-05 | 2015 | 2014-05-29 | C | 23 | 0.0075872 | 7.0252e-05
1 | 140900 | 2014-05-28 18:30 | 2014-05-29 12:58 | 1108 | 108 | 28168 | 0.086037 | 0.00032988 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -faultman found Recloser c217/2 and Sectionaliser C218/2, open after receiving calls of lines down, faultman found multiple lines down past pole 848955 caused by trees, line was isolated at ABS S150 to repair all the lines down,supply was restored u | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 260.8148 | 257.8148 | 27844 | 0.085047 | 0.00032988 | 2014-05-28 | C | 0.085047 | 0.00032988 | 2015 | 2014-05-28 | C | 108 | 0.085047 | 0.00032988
1 | 140901 | 2014-05-29 10:36 | 2014-05-29 11:08 | 32 | 51 | 1632 | 0.0049848 | 0.00015578 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | JUMPER | Defective Component - Faultman found a broken jumper to spur line that feeds transformer T3086 at pole 798045, line was isolated at ABS s571 to replace the broken jumper, Lee Wilton attended. | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 1479 | 0.0045175 | 0.00015578 | 2014-05-29 | C | 0.0045175 | 0.00015578 | 2015 | 2014-05-29 | C | 51 | 0.0045175 | 0.00015578
1 | 140904 | 2014-05-29 09:15 | 2014-05-29 14:57 | 342 | 30 | 10260 | 0.031338 | 9.1633e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91794 - Replace 11kV conductor between pole I1878 and pole 856901. Capacitor bank CC42 will have to be isolated and discharged as part of the isolation. Temp ABS 28 on pole 856901 to be checked open before new conductor is livened. Isolation point | F4 | KEREONE | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 342 | 339 | 10170 | 0.031063 | 9.1633e-05 | 2014-05-29 | B | 0.015532 | 4.5816e-05 | 2015 | 2014-05-29 | B | 30 | 0.031063 | 9.1633e-05
1 | 140905 | 2014-05-29 09:52 | 2014-05-29 15:07 | 315 | 54 | 17010 | 0.051956 | 0.00016494 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91985 - Stage 5: LLP cut jumpers at 11kV pole 742028. AP change ABS 238 and pole. Replace various arms and poles between pole 742028 and 741970 on Airport Drive. LLP Reconnect jumpers. Isolation points: Line break at pole 742028 See LLPs 1 | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 315 | 312 | 16848 | 0.051461 | 0.00016494 | 2014-05-29 | B | 0.02573 | 8.2469e-05 | 2015 | 2014-05-29 | B | 54 | 0.051461 | 0.00016494
1 | 140906 | 2014-05-29 09:13 | 2014-05-29 14:56 | 343 | 7 | 2401 | 0.0073337 | 2.1381e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/90755 - Replace 11kV pole, Xarms and hardware at various sites in outage area. Isolation points: 11kV Fuse FP1346. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 343 | 340 | 2380 | 0.0072695 | 2.1381e-05 | 2014-05-29 | B | 0.0036348 | 1.069e-05 | 2015 | 2014-05-29 | B | 7 | 0.0072695 | 2.1381e-05
1 | 140907 | 2014-05-29 16:58 | 2014-05-29 17:56 | 58 | 113 | 6334 | 0.019347 | 0.00034515 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component -Faultman found a blown jumper at Links 504 on pole 781208, line was isolated at ABS's 029, 4606/1 and 4606/6 to replace the jumper, section of feeder was back fed from VS 516. Paul Webster attended. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 56.0531 | 53.0531 | 5995 | 0.018311 | 0.00034515 | 2014-05-29 | C | 0.018311 | 0.00034515 | 2015 | 2014-05-29 | C | 113 | 0.018311 | 0.00034515
1 | 140909 | 2014-05-29 18:19 | 2014-05-29 19:58 | 99 | 231 | 16558 | 0.050575 | 0.00070557 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - CB5 tripped on E/F. Feeder patrolled / sectionalised but nothing found. All restored OK. (NOTE: Auto-backfeed operated as designed). | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.6797 | 68.6797 | 15865 | 0.048458 | 0.00070557 | 2014-05-29 | C | 0.048458 | 0.00070557 | 2015 | 2014-05-29 | C | 231 | 0.048458 | 0.00070557
1 | 140911 | 2014-05-29 23:30 | 2014-05-30 01:30 | 120 | 34 | 4080 | 0.012462 | 0.00010385 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/93262 - URGENT REPAIR. Isloate 11kV Transformer TC 3770 to repair LV bus. | F1/F3 | LORNE ST | MORRINSVILLE SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 3978 | 0.01215 | 0.00010385 | 2014-05-29 | B | 0.0060752 | 5.1925e-05 | 2015 | 2014-05-29 | B | 34 | 0.01215 | 0.00010385
1 | 140912 | 2014-05-29 22:05 | 2014-05-29 22:48 | 43 | 23 | 989 | 0.0030208 | 7.0252e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91036 - Isolate 11kV Transformer TD4-636 to fit MDIs to LV bus. Isolation points: 11kV Fuse/Sw 9230/2. | F2 | MALEME EXPRESS | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 920 | 0.0028101 | 7.0252e-05 | 2014-05-29 | B | 0.001405 | 3.5126e-05 | 2015 | 2014-05-29 | B | 23 | 0.0028101 | 7.0252e-05
1 | 140913 | 2014-05-30 03:28 | 2014-05-30 04:30 | 62 | 795 | 49290 | 0.15055 | 0.0024283 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB 2 Trip. E/F. O/C. L/O. Report of loud bang at 180 No 3 Line from member of Public. Found to be a tree branch fallen across lines at Pole 223081. Branch knocked off with Fuse stick and feeder restored. Sam Jones Faultman. | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 46905 | 0.14327 | 0.0024283 | 2014-05-30 | C | 0.14327 | 0.0024283 | 2015 | 2014-05-30 | C | 795 | 0.14327 | 0.0024283
1 | 140914 | 2014-05-30 09:13 | 2014-05-30 10:38 | 85 | 92 | 7820 | 0.023886 | 0.00028101 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - CB C642/2 A/R. Also A/R at 09:13. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 85 | 82 | 7544 | 0.023043 | 0.00028101 | 2014-05-30 | C | 0.023043 | 0.00028101 | 2015 | 2014-05-30 | C | 92 | 0.023043 | 0.00028101
1 | 140915 | 2014-05-05 09:42 | 2014-05-05 15:13 | 331 | 2 | 662 | 0.002022 | 6.1088e-06 | No Power | 11000 | Planned | Zone Sub Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | BUSWORK | SIN: 14/91802 - Replace CT off the end of the 11kV bus towards T2, replace CT and jumpers to cables towards T2. Entire sub requires isolation including CB1327 factory feeder. Isolate this part of the bus via BS 2656, ABS 2583 (treat this section as alive | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 331 | 328 | 656 | 0.0020037 | 6.1088e-06 | 2014-05-05 | B | 0.0010019 | 3.054e-06 | 2015 | 2014-05-05 | B | 2 | 0.0020037 | 6.1088e-06
1 | 140916 | 2014-05-06 23:04 | 2014-05-07 00:07 | 63 | 110 | 6930 | 0.021167 | 0.00033599 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/90486 - Close gap after replacing 11kV crossarms. Isolation points: O62, O67 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 6600 | 0.020159 | 0.00033599 | 2014-05-06 | B | 0.01008 | 0.00016799 | 2015 | 2014-05-06 | B | 110 | 0.020159 | 0.00033599
1 | 140917 | 2014-04-17 10:07 | 2014-04-17 14:20 | 253 | 91 | 23023 | 0.070322 | 0.00027795 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/91146 - Replace padmount TX 2186 Liverpool St, TX is in bad condition and requires replacement. Isolation points: X2186 | F3 | PITT ST | PEAT ST SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 253 | 250 | 22750 | 0.069488 | 0.00027795 | 2014-04-17 | B | 0.034744 | 0.00013898 | 2015 | 2014-04-17 | B | 91 | 0.069488 | 0.00027795
1 | 140918 | 2014-05-13 09:15 | 2014-05-13 17:26 | 491 | 23 | 11293 | 0.034494 | 7.0252e-05 | No Power | 33000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/87376 - To replace 33kV and 11kV cross arms on section of line along Kereone Rd. Poles KERWLN035 and KERPKO001. Isolation points: 33kV at PC21, PC184, PC221, 11kV at IC681, IC1030, IC1285, IC2668, IC999. PD 19.03.14 DEFERRED FROM MARCH | F4 | CAMPBELL RD | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 491 | 488 | 11224 | 0.034283 | 7.0252e-05 | 2014-05-13 | B | 0.017141 | 3.5126e-05 | 2015 | 2014-05-13 | B | 23 | 0.034283 | 7.0252e-05
1 | 140919 | 2014-05-15 09:15 | 2014-05-15 13:00 | 225 | 17 | 3825 | 0.011683 | 5.1925e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/91255 - Tree work near 11kV lines. S565 | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 225 | 222 | 3774 | 0.011527 | 5.1925e-05 | 2014-05-15 | B | 0.0057637 | 2.5963e-05 | 2015 | 2014-05-15 | B | 17 | 0.011527 | 5.1925e-05
1 | 140921 | 2014-05-15 10:30 | 2014-05-15 16:00 | 330 | 5 | 1650 | 0.0050398 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92114 - Change LV TX arms on pole 779881 TX 1155. Isolation points: TX fuses X1155 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 1635 | 0.004994 | 1.5272e-05 | 2014-05-15 | B | 0.002497 | 7.636e-06 | 2015 | 2014-05-15 | B | 5 | 0.004994 | 1.5272e-05
1 | 140922 | 2014-05-15 08:45 | 2014-05-15 15:20 | 395 | 78 | 30810 | 0.094107 | 0.00023825 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/90274 - Replace damaged, leaking 11kV Transformer. 11kV. Isolation points 11kV fuse 6587, 400V fuse at 17 St Ives. | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 395 | 392 | 30576 | 0.093392 | 0.00023825 | 2014-05-15 | B | 0.046696 | 0.00011912 | 2015 | 2014-05-15 | B | 78 | 0.093392 | 0.00023825
1 | 140923 | 2014-05-30 13:58 | 2014-05-30 14:11 | 13 | 6 | 78 | 0.00023825 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - Outage required from Fuses 7318 to repair floating conductor. Conductor rebound, relivened OK. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 13 | 10 | 60 | 0.00018327 | 1.8327e-05 | 2014-05-30 | C | 0.00018327 | 1.8327e-05 | 2015 | 2014-05-30 | C | 6 | 0.00018327 | 1.8327e-05
1 | 140924 | 2014-05-30 08:45 | 2014-05-30 13:30 | 285 | 88 | 25080 | 0.076605 | 0.00026879 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/92116 - Tree work near overhead lines between pole NO 8129890 and 812991. Isolation points: S8138 | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 285 | 282 | 24816 | 0.075799 | 0.00026879 | 2014-05-30 | B | 0.037899 | 0.00013439 | 2015 | 2014-05-30 | B | 88 | 0.075799 | 0.00026879
1 | 140925 | 2014-05-29 16:52 | 2014-05-30 15:20 | 1348 | 1 | 1348 | 0.0041174 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | CONDUCTOR | Accident - Follow on from FRN 140886 & line break at pole 792345. Lines repaired and relivend via Live Line. Relivened OK. NDR 792382. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 1348 | 1345 | 1345 | 0.0041082 | 3.0544e-06 | 2014-05-29 | C | 0.0041082 | 3.054e-06 | 2015 | 2014-05-29 | C | 1 | 0.0041082 | 3.0544e-06
1 | 140928 | 2014-05-28 15:46 | 2014-05-28 16:30 | 44 | 287 | 12628 | 0.038571 | 0.00087662 | No Power | 33000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB XT40 tripped, no flags. Trees found through lines, bought down in storm event. Lines isolated and service restored. Daily permits issued to repiar lines. Relivened OK | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 44 | 41 | 11767 | 0.035941 | 0.00087662 | 2014-05-28 | C | 0.035941 | 0.00087662 | 2015 | 2014-05-28 | C | 287 | 0.035941 | 0.00087662
1 | 140929 | 2014-05-30 10:00 | 2014-05-30 11:52 | 112 | 59 | 6608 | 0.020184 | 0.00018021 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92301 - Replace 11kV Xarm 747210. Has a broken insulator, risk is too high to do LL. Isolation points: 11kV ABS 179, ABS 365 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 112 | 109 | 6431 | 0.019643 | 0.00018021 | 2014-05-30 | B | 0.0098215 | 9.0105e-05 | 2015 | 2014-05-30 | B | 59 | 0.019643 | 0.00018021
1 | 140934 | 2014-05-31 22:35 | 2014-06-01 00:50 | 135 | 5 | 675 | 0.0020617 | 1.5272e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component -Faultman found transformer X778 to be damaged after attending a fault call, transformer was isolated and replaced. Neil Woodhead and Paul Sullivan attended. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 660 | 0.0020159 | 1.5272e-05 | 2014-05-31 | C | 0.0020159 | 1.5272e-05 | 2015 | 2014-05-31 | C | 5 | 0.0020159 | 1.5272e-05
1 | 140935 | 2014-05-31 22:37 | 2014-06-01 04:15 | 338 | 395 | 44931 | 0.13724 | 0.0012065 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | POLE | Accident - Received a call from the fire Services at 22:36 of a car vs pole and the person was still inside the vehicle, CB 2 was opened at 22:37 and the the Fire Services were informed that the line is de-energised but must still treat it as live and wai | F3 | EKETAHUNA | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 113.7494 | 110.7494 | 43746 | 0.13362 | 0.0012065 | 2014-05-31 | C | 0.13362 | 0.0012065 | 2015 | 2014-05-31 | C | 395 | 0.13362 | 0.0012065
1 | 140939 | 2014-06-02 04:15 | 2014-06-02 06:55 | 160 | 1 | 160 | 0.00048871 | 3.0544e-06 | No Power | 66000 | Unplanned | Zone Sub Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | SURGE ARRESTOR | Defective Component - at 04:15 Thames Sub, CB 15 Tripped, No Flags. CB QC24 Tripped, No Flags. This caused an outage on T3 Transformer. Also caused an outage to A & G Price. Faultman dispatched and investigation began. Subs and electricial team were also | F1 | A & G PRICE | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 157 | 0.00047954 | 3.0544e-06 | 2014-06-02 | C | 0.00047955 | 3.054e-06 | 2015 | 2014-06-02 | C | 1 | 0.00047954 | 3.0544e-06
1 | 140940 | 2014-06-03 10:14 | 2014-06-03 14:58 | 284 | 49 | 13916 | 0.042505 | 0.00014967 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92375 - Replace poles and Xarms on Pungarehu 33kV line. Isolation points: 33kV: ABS 31:36, ABS 31:26, ABS 32:87, 11kV: ABS NG248, AGS NG237. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 284 | 281 | 13769 | 0.042056 | 0.00014967 | 2014-06-03 | B | 0.021028 | 7.4833e-05 | 2015 | 2014-06-03 | B | 49 | 0.042056 | 0.00014967
1 | 140941 | 2014-06-03 09:20 | 2014-06-03 14:05 | 285 | 5 | 1425 | 0.0043526 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/91777 - Replace Xarms between M0033 and temp ABS pole M0043. Isolation points: Temp ABS on pole M0043, broken jumpers on M0033 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 285 | 282 | 1410 | 0.0043067 | 1.5272e-05 | 2014-06-03 | B | 0.0021534 | 7.636e-06 | 2015 | 2014-06-03 | B | 5 | 0.0043067 | 1.5272e-05
1 | 140943 | 2014-06-03 11:15 | 2014-06-03 11:26 | 11 | 1 | 11 | 3.3599e-05 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | WA: 14/92441 - LTOS oil switches. Isolation points: 8700. Obtain live tank oil sample in accordance with standard 393S084 at 11kV Sw/gear 8700. Isolation points: 11kV Sw/gear 8700. | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 11 | 8 | 8 | 2.4435e-05 | 3.0544e-06 | 2014-06-03 | B | 1.2218e-05 | 1.527e-06 | 2015 | 2014-06-03 | B | 1 | 2.4435e-05 | 3.0544e-06
1 | 140945 | 2014-06-04 08:45 | 2014-06-04 11:20 | 155 | 13 | 2015 | 0.0061547 | 3.9708e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CROSSARM | SIN: 14/92125 - Replace broken 11kV arm on pole 829259 (temp repairs done 02.03.2014). Isolation points: Links 7651 | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 155 | 152 | 1976 | 0.0060355 | 3.9708e-05 | 2014-06-04 | B | 0.0030178 | 1.9854e-05 | 2015 | 2014-06-04 | B | 13 | 0.0060355 | 3.9708e-05
1 | 140948 | 2014-06-04 10:00 | 2014-06-04 12:50 | 170 | 40 | 6800 | 0.02077 | 0.00012218 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - OH | SIN: 14/92300 - Replace ABS 2682, damage caused by trees. NDR 22318. Isolation points: Links 248 | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 170 | 167 | 6680 | 0.020404 | 0.00012218 | 2014-06-04 | B | 0.010202 | 6.1088e-05 | 2015 | 2014-06-04 | B | 40 | 0.020404 | 0.00012218
1 | 140950 | 2014-06-04 09:00 | 2014-06-04 14:00 | 300 | 56 | 16800 | 0.051314 | 0.00017105 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92279 - Replace X3043 Aiken Rd Wanganui. TX 400V circuits cannot be backfed for this job. Isolation points: FABS 1123 | F3 | ST JOHNS | PEAT ST SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 300 | 297 | 16632 | 0.050801 | 0.00017105 | 2014-06-04 | B | 0.025401 | 8.5524e-05 | 2015 | 2014-06-04 | B | 56 | 0.050801 | 0.00017105
1 | 140951 | 2014-06-04 09:15 | 2014-06-04 15:00 | 345 | 6 | 2070 | 0.0063227 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/92452 - Felling approximately 20 pine trees between pole 850094 and pole 807805 Watershed Rd Hunterville. Isolation points: ABS 694 Steve Edwards on site. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 2052 | 0.0062677 | 1.8327e-05 | 2014-06-04 | B | 0.0031338 | 9.163e-06 | 2015 | 2014-06-04 | B | 6 | 0.0062677 | 1.8327e-05
1 | 140953 | 2014-06-04 08:55 | 2014-06-04 14:40 | 345 | 14 | 4830 | 0.014753 | 4.2762e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92354 - Replace 11kV poles and X-arms to repair defects. Isolation points: 11kV Fuse/Sw SE6-133 | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 4788 | 0.014625 | 4.2762e-05 | 2014-06-04 | B | 0.0073123 | 2.1381e-05 | 2015 | 2014-06-04 | B | 14 | 0.014625 | 4.2762e-05
1 | 140954 | 2014-06-04 11:00 | 2014-06-04 15:51 | 291 | 18 | 5238 | 0.015999 | 5.498e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92097 - Replace poles and Xarms on Pungarehu 33kV line. Isolation points: 33kV: ABS 31:36, ABS 31:26, ABS 32:87, 11kV: ABS 6453, ABS PU495, ABS PU422. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 291 | 288 | 5184 | 0.015834 | 5.498e-05 | 2014-06-04 | B | 0.0079171 | 2.749e-05 | 2015 | 2014-06-04 | B | 18 | 0.015834 | 5.498e-05
1 | 140955 | 2014-06-04 15:32 | 2014-06-04 16:53 | 81 | 510 | 18870 | 0.057637 | 0.0015578 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | Unknown Cause - CB 6 Trip. E/F. L/O. Feeder sectionalised but no fault found. Deon Sanders and Jayden Te Aho Faultmen. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 17340 | 0.052964 | 0.0015578 | 2014-06-04 | C | 0.052964 | 0.0015578 | 2015 | 2014-06-04 | C | 510 | 0.052964 | 0.0015578
1 | 140957 | 2014-06-05 00:13 | 2014-06-05 01:53 | 100 | 2573 | 254676 | 0.77789 | 0.007859 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power -33kV CB 1182 CB Y40 CB Y10 All Tripped on A | F1,F2,F3 | Not entered | Not entered | Not entered | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 98.9802 | 95.9802 | 246957 | 0.75431 | 0.007859 | 2014-06-05 | C | 0.75431 | 0.007859 | 2015 | 2014-06-05 | C | 2573 | 0.75431 | 0.007859
1 | 140958 | 2014-06-04 09:05 | 2014-06-04 16:08 | 423 | 64 | 4544 | 0.013879 | 0.00019548 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/91388 - Replace existing 11kV SDAF3 unit, 9083, w/ a new Safelink CFC w/ motor drive on Sw/Gear 9083/3. Isolation points: AP1: 11kV Sw/Gear IC1828, 3039, AP2:11kV Sw/Gear IC1828, 3039, AP3:11kV Sw/Gear 9083/2, AP4: 11kV Sw/Gear 9083/3, 3039, AP5: | F3 | THOMPSON DR | MARAETAI ROAD SUB | TP_KINLEITH | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 4352 | 0.013293 | 0.00019548 | 2014-06-04 | B | 0.0066464 | 9.7742e-05 | 2015 | 2014-06-04 | B | 64 | 0.013293 | 0.00019548
1 | 140960 | 2014-06-05 09:15 | 2014-06-05 10:00 | 45 | 5 | 225 | 0.00068725 | 1.5272e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92247 - AP Is for 1 hr to install a 400V Disc-Connector to the LV of the Transformer. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disc-connector. This is to be followed by a 400V shutdown to complete the 400V a | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 210 | 0.00064143 | 1.5272e-05 | 2014-06-05 | B | 0.00032071 | 7.636e-06 | 2015 | 2014-06-05 | B | 5 | 0.00064143 | 1.5272e-05
1 | 140961 | 2014-06-05 10:40 | 2014-06-05 14:40 | 240 | 3 | 720 | 0.0021992 | 9.1633e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92961 - Upgrade TX X2056 from a 15/11/3 to a 30/11/3 and change all LV Xarms. Isolation points: X2056 | F4 | CROFTON | ARAHINA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 711 | 0.0021717 | 9.1633e-06 | 2014-06-05 | B | 0.0010858 | 4.582e-06 | 2015 | 2014-06-05 | B | 3 | 0.0021717 | 9.1633e-06
1 | 140962 | 2014-06-05 13:00 | 2014-06-05 13:45 | 45 | 5 | 225 | 0.00068725 | 1.5272e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CUSTOMER REQUEST | DISTRIBUTION TRANSFORMER | SIN: 14/92839 - Replace leaking TX T3/275. Isolation points: T3/275 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 210 | 0.00064143 | 1.5272e-05 | 2014-06-05 | B | 0.00032071 | 7.636e-06 | 2015 | 2014-06-05 | B | 5 | 0.00064143 | 1.5272e-05
1 | 140963 | 2014-06-05 10:15 | 2014-06-05 11:55 | 100 | 18 | 1800 | 0.005498 | 5.498e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92926 - Replace rotten 11kV Xarm. Isolation points: Fuses S23 | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 1746 | 0.005333 | 5.498e-05 | 2014-06-05 | B | 0.0026665 | 2.749e-05 | 2015 | 2014-06-05 | B | 18 | 0.005333 | 5.498e-05
1 | 140964 | 2014-06-05 09:15 | 2014-06-05 10:30 | 75 | 2 | 150 | 0.00045816 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CUSTOMER REQUEST | DISTRIBUTION TRANSFORMER | SIN: 14/92838 - Replace leaking TXs T3/369. Isolation points: T3/369 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 75 | 72 | 144 | 0.00043984 | 6.1088e-06 | 2014-06-05 | B | 0.00021992 | 3.054e-06 | 2015 | 2014-06-05 | B | 2 | 0.00043984 | 6.1088e-06
1 | 140966 | 2014-06-05 09:05 | 2014-06-05 10:00 | 55 | 4 | 220 | 0.00067197 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91931 - Replace pole 816731. Isolation points: 7374 Pole was not replaced customers were not advertised. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 208 | 0.00063532 | 1.2218e-05 | 2014-06-05 | B | 0.00031766 | 6.109e-06 | 2015 | 2014-06-05 | B | 4 | 0.00063532 | 1.2218e-05
1 | 140967 | 2014-06-05 11:27 | 2014-06-05 12:21 | 54 | 43 | 2322 | 0.0070924 | 0.00013134 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - Faultman found the king pin on pole 358175 was broken, line was isolated at Links 147, 155 and at Temp 02 Fuses to replace the king pin bolt. Glen Most attended. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 2193 | 0.0066984 | 0.00013134 | 2014-06-05 | C | 0.0066984 | 0.00013134 | 2015 | 2014-06-05 | C | 43 | 0.0066984 | 0.00013134
1 | 140968 | 2014-06-05 09:45 | 2014-06-05 15:09 | 324 | 54 | 17496 | 0.05344 | 0.00016494 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91753 - Reconductor Airport Dr from pole 741979 to 741961. Isolation points:11kV ABS 238. | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 324 | 321 | 17334 | 0.052945 | 0.00016494 | 2014-06-05 | B | 0.026473 | 8.2469e-05 | 2015 | 2014-06-05 | B | 54 | 0.052945 | 0.00016494
1 | 140969 | 2014-06-05 09:00 | 2014-06-05 14:50 | 350 | 99 | 34650 | 0.10584 | 0.00030239 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92235 - Isolation required to change11kV stud poles. Isolation points: 11kV ABS SC2-003 | F3/F4 | WILLS RD | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 350 | 347 | 34353 | 0.10493 | 0.00030239 | 2014-06-05 | B | 0.052464 | 0.00015119 | 2015 | 2014-06-05 | B | 99 | 0.10493 | 0.00030239
1 | 140972 | 2014-06-06 09:00 | 2014-06-06 12:00 | 180 | 4 | 720 | 0.0021992 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/92245 - AP Is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disc-connector. This is to be followed by a 400V shutdown to complete the 400V arm replac | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 708 | 0.0021625 | 1.2218e-05 | 2014-06-06 | B | 0.0010813 | 6.109e-06 | 2015 | 2014-06-06 | B | 4 | 0.0021625 | 1.2218e-05
1 | 140973 | 2014-06-06 08:51 | 2014-06-06 11:18 | 147 | 265 | 15759 | 0.048135 | 0.00080942 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | No Power -Brooklands Cb 2 Recloser 6610 Trip E/F. Found line down at pole 745023. Isolated At ABS 118 and 355 Backfeed applied at ABS 347. Materials Used 9 sleeves # binders | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 59.4679 | 56.4679 | 14964 | 0.045706 | 0.00080942 | 2014-06-06 | C | 0.045706 | 0.00080942 | 2015 | 2014-06-06 | C | 265 | 0.045706 | 0.00080942
1 | 140975 | 2014-06-06 09:46 | 2014-06-06 13:13 | 207 | 23 | 4761 | 0.014542 | 7.0252e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92968 - Replace burnt off 11kV pole. Isolation points: Fuses S8 | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 207 | 204 | 4692 | 0.014331 | 7.0252e-05 | 2014-06-06 | B | 0.0071657 | 3.5126e-05 | 2015 | 2014-06-06 | B | 23 | 0.014331 | 7.0252e-05
1 | 140976 | 2014-06-06 10:00 | 2014-06-06 14:30 | 270 | 20 | 5400 | 0.016494 | 6.1088e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92080 - Replace 11kV pole 756388 that is in bad condition and remove trees around TX 1737N. Isolation points: 11kV Fuses 8406. | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 270 | 267 | 5340 | 0.016311 | 6.1088e-05 | 2014-06-06 | B | 0.0081553 | 3.0544e-05 | 2015 | 2014-06-06 | B | 20 | 0.016311 | 6.1088e-05
1 | 140977 | 2014-06-06 09:30 | 2014-06-06 13:40 | 250 | 23 | 5750 | 0.017563 | 7.0252e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92714 - Replace 11kV pole P14873 hit by tractor. Isolation points: E29 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 5681 | 0.017352 | 7.0252e-05 | 2014-06-06 | B | 0.0086761 | 3.5126e-05 | 2015 | 2014-06-06 | B | 23 | 0.017352 | 7.0252e-05
1 | 140978 | 2014-06-06 10:43 | 2014-06-06 13:18 | 155 | 44 | 6820 | 0.020831 | 0.00013439 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - OH | SIN: 14/93212 - Replace ABS M72 DNO. Associated 14/92379 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 155 | 152 | 6688 | 0.020428 | 0.00013439 | 2014-06-06 | B | 0.010214 | 6.7197e-05 | 2015 | 2014-06-06 | B | 44 | 0.020428 | 0.00013439
1 | 140980 | 2014-06-06 14:42 | 2014-06-06 15:57 | 75 | 242 | 14364 | 0.043874 | 0.00073917 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -Recloser 1011 tripped on B and C phase O/C flags, line was patrolled and sectionalised and no fault was found. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 59.3554 | 56.3554 | 13638 | 0.041656 | 0.00073917 | 2014-06-06 | C | 0.041656 | 0.00073917 | 2015 | 2014-06-06 | C | 242 | 0.041656 | 0.00073917
1 | 140981 | 2014-06-06 08:33 | 2014-06-06 15:08 | 395 | 17 | 6715 | 0.02051 | 5.1925e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/92610 - Reconductor between poles P26543 and P10615. Isolation points: Links I5, I6, ABS I7 | F4 | IHURAUA | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 395 | 392 | 6664 | 0.020355 | 5.1925e-05 | 2014-06-06 | B | 0.010177 | 2.5963e-05 | 2015 | 2014-06-06 | B | 17 | 0.020355 | 5.1925e-05
1 | 140983 | 2014-06-06 13:00 | 2014-06-06 15:00 | 120 | 5 | 600 | 0.0018327 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/92246 - AP Is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disc-connector. This is to be followed by a 400V shutdown to complete the 400V arm replac | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 585 | 0.0017868 | 1.5272e-05 | 2014-06-06 | B | 0.00089342 | 7.636e-06 | 2015 | 2014-06-06 | B | 5 | 0.0017868 | 1.5272e-05
1 | 140985 | 2014-06-06 09:34 | 2014-06-06 13:45 | 251 | 1 | 251 | 0.00076666 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92757 - Replace broken 11kV X-arms at pole 229235 (Transformer TF7-078). Isolation points: 11kV Fuses SF7-043 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 251 | 248 | 248 | 0.0007575 | 3.0544e-06 | 2014-06-06 | B | 0.00037875 | 1.527e-06 | 2015 | 2014-06-06 | B | 1 | 0.0007575 | 3.0544e-06
1 | 140986 | 2014-06-06 09:05 | 2014-06-06 12:07 | 182 | 52 | 9464 | 0.028907 | 0.00015883 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | ISOLATION FOR SAFETY | POLE | SIN: 14/91681 - Replace 33kV X-arms on TP WG3 line on same pole as 11kV O/H on pole 211739 (insufficient clearance for EWP for LL). Isolation points: 11kV Links 9566/4, ABS 9566/1 and ABS SE3-005 | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 9308 | 0.028431 | 0.00015883 | 2014-06-06 | B | 0.014215 | 7.9415e-05 | 2015 | 2014-06-06 | B | 52 | 0.028431 | 0.00015883
1 | 140987 | 2014-06-06 13:00 | 2014-06-06 14:55 | 115 | 34 | 3910 | 0.011943 | 0.00010385 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | ISOLATION FOR SAFETY | CONDUCTOR | SIN: 14/91680 - Replace 33kV X-arms on TP WG3 line on same pole as 11kV O/H on pole 211343 (insufficient clearance for EWP for LL). Isolation points: 11kV ABS SD3-029, Sw/gear 9243/1 & 9186/1. | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 115 | 112 | 3808 | 0.011631 | 0.00010385 | 2014-06-06 | B | 0.0058156 | 5.1925e-05 | 2015 | 2014-06-06 | B | 34 | 0.011631 | 0.00010385
1 | 140988 | 2014-06-06 17:08 | 2014-06-06 17:40 | 32 | 39 | 1248 | 0.0038119 | 0.00011912 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component -Faultman found a loose jumper going to a take off line that fed transformer T9/252 at pole P04648, line was isolated at ABS's V76 and V81 to reconnect the jumper. Trevor Pocock attended. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 1131 | 0.0034546 | 0.00011912 | 2014-06-06 | C | 0.0034546 | 0.00011912 | 2015 | 2014-06-06 | C | 39 | 0.0034546 | 0.00011912
1 | 140989 | 2014-06-06 17:05 | 2014-06-06 19:49 | 164 | 308 | 17251 | 0.052692 | 0.00094076 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | HT Line - at 17:05, Peat St Sub, CB 5 Westmere Feeder, Tripped, O/C, E/F, L/O. Faultman Dispatched and investigation began. Found lines down at Pole 769446. Unsure of exact cause, faultman believes possible bird strike may have occurred but no evidence of | F3 | WESTMERE PEAT ST | PEAT ST SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 56.0097 | 53.0097 | 16327 | 0.04987 | 0.00094076 | 2014-06-06 | C | 0.04987 | 0.00094076 | 2015 | 2014-06-06 | C | 308 | 0.04987 | 0.00094076
1 | 140990 | 2014-06-07 09:15 | 2014-06-07 13:55 | 280 | 2 | 560 | 0.0017105 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/91820 - Replace 11kV Transformer TC4212. Isolation points:11 kV Fuse FC2296 | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 280 | 277 | 554 | 0.0016922 | 6.1088e-06 | 2014-06-07 | B | 0.00084607 | 3.054e-06 | 2015 | 2014-06-07 | B | 2 | 0.0016922 | 6.1088e-06
1 | 140992 | 2014-06-06 19:36 | 2014-06-07 09:00 | 804 | 1 | 804 | 0.0024558 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | No Power -Section of line from fuses 8164 isolated to repair fuse Holder on pole 365989 .. Repaired using live line (Attended by Adam Whale & Gavin Grey) | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 804 | 801 | 801 | 0.0024466 | 3.0544e-06 | 2014-06-06 | C | 0.0024466 | 3.054e-06 | 2015 | 2014-06-06 | C | 1 | 0.0024466 | 3.0544e-06
1 | 140993 | 2014-06-07 09:09 | 2014-06-07 15:06 | 357 | 31 | 11067 | 0.033803 | 9.4687e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | RECLOSER | SIN: 14/92084 - Change pole P31461 and install 1 x set of new isolators and new nova recloser ready for commissioning on same pole. ABS will also be reinstalled on pole. Isolation points: C14, C20, C10, C11, C9 | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 357 | 354 | 10974 | 0.033519 | 9.4687e-05 | 2014-06-07 | B | 0.01676 | 4.7344e-05 | 2015 | 2014-06-07 | B | 31 | 0.033519 | 9.4687e-05
1 | 140996 | 2014-06-08 08:57 | 2014-06-08 13:23 | 266 | 262 | 69692 | 0.21287 | 0.00080026 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - Car hit pole 212658. Isolated between ABS SE4-014. ABS 9209/1 & Links 9209/4. Backfeed rest of area. Replaced pole that had ABS SE4-012 on it. Relivened. Car did a runner NDR 048405. 1 pole, 3 ducts 1 30kvA transformer 1 switch handle rest of g | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 266 | 263 | 68906 | 0.21047 | 0.00080026 | 2014-06-08 | C | 0.21047 | 0.00080026 | 2015 | 2014-06-08 | C | 262 | 0.21047 | 0.00080026
1 | 140997 | 2014-06-08 08:45 | 2014-06-08 12:37 | 232 | 1 | 232 | 0.00070863 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | PROTECTION | SIN: 14/93276 - Replace HV VT fuses on 11kV metering unit for Waverly Sawmills which is fed from FABS 1036. Isolation points: New HV links 4693. Associated LLP 14/93337 | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 232 | 229 | 229 | 0.00069946 | 3.0544e-06 | 2014-06-08 | B | 0.00034973 | 1.527e-06 | 2015 | 2014-06-08 | B | 1 | 0.00069946 | 3.0544e-06
1 | 140998 | 2014-06-08 08:19 | 2014-06-08 14:46 | 387 | 28 | 10836 | 0.033098 | 8.5524e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92085 - Replace TX T3/254 and associated LV equipment. Isolation points: FS59 | F2 | WORKS | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 387 | 384 | 10752 | 0.032841 | 8.5524e-05 | 2014-06-08 | B | 0.016421 | 4.2762e-05 | 2015 | 2014-06-08 | B | 28 | 0.032841 | 8.5524e-05
1 | 140999 | 2014-06-08 08:15 | 2014-06-08 11:52 | 217 | 16 | 3472 | 0.010605 | 4.8871e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92287 - Replacing TX red tag pole 833564 w/ new 2xbusck poles. Isolation points: C1007, S139, C288 | F2 | HEAD OFFICE | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 217 | 214 | 3424 | 0.010458 | 4.8871e-05 | 2014-06-08 | B | 0.0052292 | 2.4435e-05 | 2015 | 2014-06-08 | B | 16 | 0.010458 | 4.8871e-05
1 | 141001 | 2014-06-08 16:19 | 2014-06-08 18:20 | 121 | 1 | 121 | 0.00036959 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92812 - T6/617T (high moisture and acidity content). Isolation points: FS31 (Switching delayed due to customer generator arived late) | F2 | MALDEN ST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 121 | 118 | 118 | 0.00036042 | 3.0544e-06 | 2014-06-08 | B | 0.00018021 | 1.527e-06 | 2015 | 2014-06-08 | B | 1 | 0.00036042 | 3.0544e-06
1 | 141002 | 2014-06-08 15:54 | 2014-06-08 20:12 | 258 | 153 | 15056 | 0.045987 | 0.00046733 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Recloser 9604/2 tripped to L/O - E/F flag - line sectionalised & patrolled - floater located at pole P1567 - Isolation points to retie floater were ABS IC278, IC243, 9712/1, & Links 9712/4 - backfeed established from ABS IC213 to ABS IC243 for duration of | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 98.4052 | 95.4052 | 14597 | 0.044585 | 0.00046733 | 2014-06-08 | C | 0.044585 | 0.00046733 | 2015 | 2014-06-08 | C | 153 | 0.044585 | 0.00046733
1 | 141003 | 2014-06-09 16:25 | 2014-06-09 16:53 | 28 | 216 | 6048 | 0.018473 | 0.00065976 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | UNKNOWN | Defective Component - Found broken dead end on pole 209163. Isolated whole of CB 6 as no backeeds available, replaced 1 dead end & 1 polymar. Relivened. To wet for live line to repair | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 5400 | 0.016494 | 0.00065976 | 2014-06-09 | C | 0.016494 | 0.00065976 | 2015 | 2014-06-09 | C | 216 | 0.016494 | 0.00065976
1 | 141004 | 2014-06-09 09:31 | 2014-06-09 09:58 | 27 | 10 | 270 | 0.00082469 | 3.0544e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - UG | WA: 14/92618 - LTOS oil switch 6651/1. Isolation points: 6.6kV CB I61, Fuse switch 6651/1, ABS 8543. Obtain live tank oil sample in accordance with standard 393S084 at 6.6kV Sw/gear 6651/1 . Isolation points: 11kV Sw/gear 6651/1. 6.6kV CBI61, 6.6kV ABS 85 | F3 | BROOKES ST | INGLEWOOD SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 240 | 0.00073306 | 3.0544e-05 | 2014-06-09 | B | 0.00036653 | 1.5272e-05 | 2015 | 2014-06-09 | B | 10 | 0.00073306 | 3.0544e-05
1 | 141007 | 2014-06-09 09:15 | 2014-06-09 10:00 | 45 | 5 | 225 | 0.00068725 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | LV FAULT - OTHER | SIN: 14/92249 - AP Is for 1 hr to install a 400V Disc-Connector to the LV of the TX. AP can then be cancelled and the HV fuses closed, relivening the TX up to the LV disc-connector. This is to be followed by a 400V shutdown to complete the 400V arm replac | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 210 | 0.00064143 | 1.5272e-05 | 2014-06-09 | B | 0.00032071 | 7.636e-06 | 2015 | 2014-06-09 | B | 5 | 0.00064143 | 1.5272e-05
1 | 141010 | 2014-06-09 14:14 | 2014-06-09 14:23 | 9 | 1 | 9 | 2.749e-05 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - UG | WA: 14/92621 - LTOS oil switch 8723. Isolation points: Fuse switch 8723 | F4 | CLOTON RD NORTH EAST | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 6 | 1.8327e-05 | 3.0544e-06 | 2014-06-09 | B | 9.163e-06 | 1.527e-06 | 2015 | 2014-06-09 | B | 1 | 1.8327e-05 | 3.0544e-06
1 | 141012 | 2014-06-09 12:48 | 2014-06-09 14:46 | 118 | 93 | 10974 | 0.033519 | 0.00028406 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power -Shut down required to change pole after Car hit it Isolation Points ABS 678 & ABS 1300 No backfeeds Pole Number 840067 NDR Number 30355 Used 1 X Pole 1 X Crossarm H/T 3X H/T Insulators 2 X L/V Crossarms 4 X L/V Insulators | F3 | WESTMERE PEAT ST | PEAT ST SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 118 | 115 | 10695 | 0.032667 | 0.00028406 | 2014-06-09 | C | 0.032667 | 0.00028406 | 2015 | 2014-06-09 | C | 93 | 0.032667 | 0.00028406
1 | 141014 | 2014-06-09 16:55 | 2014-06-09 19:30 | 155 | 231 | 20630 | 0.063013 | 0.00070557 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - Tripping on CB5 on E/F. Feeder sectionalised / patrolled with a broken insulator found between ABS P42 and P44 (Backfeed at CB 1000/2). Insulator replaced / rebound and feeder restored to normal. (NOTE: Auto backfeed operated OK). | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 89.3074 | 86.3074 | 19937 | 0.060896 | 0.00070557 | 2014-06-09 | C | 0.060896 | 0.00070557 | 2015 | 2014-06-09 | C | 231 | 0.060896 | 0.00070557
1 | 141015 | 2014-06-10 10:36 | 2014-06-10 11:15 | 39 | 7 | 273 | 0.00083386 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | No Power -Shutdown required to close Temp Line Break at Pole 807925 isolation point Fuses 4015 No back feeds Nev Ashton attended | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 39 | 36 | 252 | 0.00076971 | 2.1381e-05 | 2014-06-10 | C | 0.00076972 | 2.1381e-05 | 2015 | 2014-06-10 | C | 7 | 0.00076971 | 2.1381e-05
1 | 141016 | 2014-06-10 04:28 | 2014-06-10 07:05 | 157 | 368 | 51374 | 0.15692 | 0.001124 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | No Power -Shutdown required to Replace Insulator at pole 801463 Isolation point ABS 1409 & ABS4086 Back feed in at ABS 738 Ben pittams Tony Sinclair Attended | F3 | NGATAWA | ARAHINA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 139.6033 | 136.6033 | 50270 | 0.15355 | 0.001124 | 2014-06-10 | C | 0.15355 | 0.001124 | 2015 | 2014-06-10 | C | 368 | 0.15355 | 0.001124
1 | 141018 | 2014-06-10 09:00 | 2014-06-10 11:08 | 128 | 105 | 13440 | 0.041051 | 0.00032071 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92447 - Change 11kV X-arms at various sites within the isolated area. Isolation point: 11kV ABS SC2-012 | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 128 | 125 | 13125 | 0.040089 | 0.00032071 | 2014-06-10 | B | 0.020045 | 0.00016036 | 2015 | 2014-06-10 | B | 105 | 0.040089 | 0.00032071
1 | 141019 | 2014-06-09 10:08 | 2014-06-09 12:40 | 152 | 16 | 2432 | 0.0074284 | 4.8871e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92158 - Move 11kV pole 374074 to other side of driveway as it is a visibility hazard. Isolation points: 11kV ABS 316, ABS 480 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 152 | 149 | 2384 | 0.0072817 | 4.8871e-05 | 2014-06-09 | B | 0.0036409 | 2.4435e-05 | 2015 | 2014-06-09 | B | 16 | 0.0072817 | 4.8871e-05
1 | 141020 | 2014-06-09 01:30 | 2014-06-10 12:33 | 2103 | 19 | 29298 | 0.089489 | 5.8034e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Unknown fault beyond fuses 4973, unable to access at night , so temp line break made at pole 739432 ( tee off spur ). Burnt cross arm found next day with isolation being temp line break at pole 739432. Arm replaced further isolation | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 1542 | 1539 | 29241 | 0.089314 | 5.8034e-05 | 2014-06-09 | C | 0.089314 | 5.8034e-05 | 2015 | 2014-06-09 | C | 19 | 0.089314 | 5.8034e-05
1 | 141022 | 2014-06-10 13:00 | 2014-06-10 14:00 | 60 | 3 | 180 | 0.0005498 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power -Shutdown required to fix Floating conductor at Pole 809503 isolation point Links 563 Wayne E Attended | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 171 | 0.00052231 | 9.1633e-06 | 2014-06-10 | C | 0.00052231 | 9.163e-06 | 2015 | 2014-06-10 | C | 3 | 0.00052231 | 9.1633e-06
1 | 141023 | 2014-06-10 09:05 | 2014-06-10 13:30 | 265 | 33 | 924 | 0.0028223 | 0.0001008 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power -Shutdown required after car V Pole NDR Number 37690 Isolation Points ABSS106 Fuses 7798 & Temp Line break at Pole 828582 Back feed in at Switch gear C203 Replaced Pole ABS Crossarms etc Brad Keating Attended | F3 | HIGH ST | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 825 | 0.0025199 | 0.0001008 | 2014-06-10 | C | 0.0025199 | 0.0001008 | 2015 | 2014-06-10 | C | 33 | 0.0025199 | 0.0001008
1 | 141024 | 2014-06-10 13:33 | 2014-06-10 14:53 | 80 | 888 | 23655 | 0.072252 | 0.0027123 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CIRCUIT BREAKER | No Power -CB 3035 & CB 1488 Tripped O/C A& B Phase. Found CB 1488 fauly and requires looking at.Back Feed Hunterville from MABS 539. Feed Putorino from CB 1350. Jason Pram to look at. James Prime & Karl Rogers attended | F1,F2,F3 | Not entered | Not entered | Not entered | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 26.6385 | 23.6385 | 20991 | 0.064115 | 0.0027123 | 2014-06-10 | C | 0.064115 | 0.0027123 | 2015 | 2014-06-10 | C | 888 | 0.064115 | 0.0027123
1 | 141025 | 2014-06-10 09:50 | 2014-06-10 14:46 | 296 | 149 | 44104 | 0.13471 | 0.00045511 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92862 - Replace leaking11kV TX TC3727. Like for like replacement. Isolation points:11kV Sw/Gear IC1906 , IC1996 Note - late restoration due to weather | F3 | RAWHITI AVE | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 296 | 293 | 43657 | 0.13335 | 0.00045511 | 2014-06-10 | B | 0.066673 | 0.00022755 | 2015 | 2014-06-10 | B | 149 | 0.13335 | 0.00045511
1 | 141026 | 2014-06-10 13:59 | 2014-06-10 14:13 | 14 | 78 | 1092 | 0.0033354 | 0.00023825 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Emergency switching to re position jumper burning on cross arm at Fuses FC2500 ( no pole No ) Isolations between ABS's IC1301, 787, IC1050 & IC1058 with back feeds via ABS's 1274 & 1356. Jumper repositioned, arm & conductor ok all se | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 858 | 0.0026207 | 0.00023825 | 2014-06-10 | C | 0.0026207 | 0.00023824 | 2015 | 2014-06-10 | C | 78 | 0.0026207 | 0.00023825
1 | 141027 | 2014-06-10 15:32 | 2014-06-10 17:46 | 134 | 21 | 2814 | 0.0085951 | 6.4143e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Emergency switching to replace burnt cross arm at pole 718383. Isolation at fuses MA574 ( no back feeds ) . Arm replaced all service restored, Chris Katene attended. Materials 2 x Arms, 3 x Polymers, 3 x Fuse Holders, 1 x H/V insulat | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 134 | 131 | 2751 | 0.0084027 | 6.4143e-05 | 2014-06-10 | C | 0.0084027 | 6.4143e-05 | 2015 | 2014-06-10 | C | 21 | 0.0084027 | 6.4143e-05
1 | 141036 | 2014-06-10 20:51 | 2014-06-10 22:35 | 104 | 95 | 6843 | 0.020901 | 0.00029017 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Recloser RC25 L/O. Sectionalised and isolated old 33kv line now used for 11kV. Suspect insulator on that line broken Links IP576 to Recloser 9705 left de enigised | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 72.0316 | 69.0316 | 6558 | 0.020031 | 0.00029017 | 2014-06-10 | C | 0.020031 | 0.00029017 | 2015 | 2014-06-10 | C | 95 | 0.020031 | 0.00029017
1 | 141041 | 2014-06-09 10:55 | 2014-06-09 13:05 | 130 | 19 | 2470 | 0.0075444 | 5.8034e-05 | No Power | 33000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92111 - Replace 33kV Xarms on each of the specified poles. Isolation points: 33kV ABS PC139, ABS PC113, ABS 48 at FRM, ABS 24 at TTU | F4 | CAMPBELL RD | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 130 | 127 | 2413 | 0.0073703 | 5.8034e-05 | 2014-06-09 | B | 0.0036852 | 2.9017e-05 | 2015 | 2014-06-09 | B | 19 | 0.0073703 | 5.8034e-05
1 | 141043 | 2014-06-10 16:45 | 2014-06-10 21:55 | 310 | 2 | 620 | 0.0018937 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | HV LINK BOX | No Power -Section of line from Fuses 7301 Isolated to repair link box on transformer T2634 (Attended by Brad Keating and Brian Buttler) | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 310 | 307 | 614 | 0.0018754 | 6.1088e-06 | 2014-06-10 | C | 0.0018754 | 6.109e-06 | 2015 | 2014-06-10 | C | 2 | 0.0018754 | 6.1088e-06
1 | 141044 | 2014-06-10 09:28 | 2014-06-10 13:05 | 217 | 44 | 9548 | 0.029164 | 0.00013439 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power -Shutdown required after car V Pole NDR Number 37690 Isolation Points ABSS106 Fuses 7798 & Temp Line break at Pole 828582 Back feed in at Switch gear C203 Replaced Pole ABS Crossarms etc Brad Keating Attended .See FR 141044 for Ngamutawa Rd O | F2 | NGAUMUTAWA RD | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 217 | 214 | 9416 | 0.02876 | 0.00013439 | 2014-06-10 | C | 0.02876 | 0.00013439 | 2015 | 2014-06-10 | C | 44 | 0.02876 | 0.00013439
1 | 141045 | 2014-06-11 10:33 | 2014-06-11 11:19 | 46 | 73 | 3358 | 0.010257 | 0.00022297 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Reports received of No Power, investigations reveal fuses SC3-009 blown & Tree thru lines at poles 268168 & 200757. Isolated at Fuses SC3-009, trees cleared, repairs made & supply restored. Steve Doran attended. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 46 | 43 | 3139 | 0.0095878 | 0.00022297 | 2014-06-11 | C | 0.0095878 | 0.00022297 | 2015 | 2014-06-11 | C | 73 | 0.0095878 | 0.00022297
1 | 141046 | 2014-06-11 05:10 | 2014-06-11 11:03 | 353 | 306 | 108018 | 0.32993 | 0.00093465 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - CB2 & Recloser 9560 Tripped L/O during severe wind storm. Recloser isolated & CB2 successfully relivened at 11:03 following line patrol. Line patrol past recloser under way.Also refer FR 141050 for later tripping event. | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 353 | 350 | 107100 | 0.32713 | 0.00093465 | 2014-06-11 | C | 0.32713 | 0.00093465 | 2015 | 2014-06-11 | C | 306 | 0.32713 | 0.00093465
1 | 141047 | 2014-06-11 03:42 | 2014-06-11 12:00 | 498 | 261 | 86506 | 0.26423 | 0.0007972 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Recloser 9147 Triped L/O during severe wind storm. Line patrol located lines down at pole 228019. Isolated at ABS SE6-079, lines repaired supply restored. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 331.4406 | 328.4406 | 85723 | 0.26183 | 0.0007972 | 2014-06-11 | C | 0.26183 | 0.00079721 | 2015 | 2014-06-11 | C | 261 | 0.26183 | 0.0007972
1 | 141048 | 2014-06-11 12:02 | 2014-06-11 12:47 | 45 | 79 | 3555 | 0.010858 | 0.0002413 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Reports received of Tree thru lines near pole 222162. Isolated at ABS SE4-022, tree cleared, repairs made, supply restored. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 3318 | 0.010135 | 0.0002413 | 2014-06-11 | C | 0.010135 | 0.0002413 | 2015 | 2014-06-11 | C | 79 | 0.010135 | 0.0002413
1 | 141049 | 2014-06-11 05:26 | 2014-06-11 11:38 | 372 | 653 | 241816 | 0.73861 | 0.0019945 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - CB1 Tripped, L/O, during severe storm conditions. Feeder patroled, sectionalised & supply restored with out finding the cause of tripping. Suspect conductor clash during severe winds. | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 370.3155 | 367.3155 | 239857 | 0.73262 | 0.0019945 | 2014-06-11 | C | 0.73262 | 0.0019945 | 2015 | 2014-06-11 | C | 653 | 0.73262 | 0.0019945
1 | 141050 | 2014-06-11 11:56 | 2014-06-11 13:37 | 101 | 543 | 44509 | 0.13595 | 0.0016586 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Wind - CB2 Tripped L/O, during severe storm conditions. Feeder patrolled sectionalised & supply restored with out finding the cause of the tripping. Suspect line clash during severe winds. Also refer FR 141046 for earlier tripping. | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 81.9687 | 78.9687 | 42880 | 0.13097 | 0.0016586 | 2014-06-11 | C | 0.13097 | 0.0016586 | 2015 | 2014-06-11 | C | 543 | 0.13097 | 0.0016586
1 | 141051 | 2014-06-11 04:55 | 2014-06-11 11:45 | 410 | 807 | 191126 | 0.58378 | 0.0024649 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - CB1 Tripped L/O during severe storm event. Reports received of lines down in Furgus Rd. Isolated at ABS IC292. Broken insulators replaced (x3) and supply restored. | F3 | BEACH RD WAIHI BEACH | WAIHI BEACH SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 236.8352 | 233.8352 | 188705 | 0.57639 | 0.0024649 | 2014-06-11 | C | 0.57639 | 0.0024649 | 2015 | 2014-06-11 | C | 807 | 0.57639 | 0.0024649
1 | 141052 | 2014-06-11 10:30 | 2014-06-11 11:34 | 64 | 33 | 2112 | 0.0064509 | 0.0001008 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | Defective Component - Reports received of lines sagging during severe storm event. Investigations reveal broken eyebolt on ABS IC845. Isolated at ABS IC845, ABS repairs made, supply restored. | F3 | FIRTH ST | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 2013 | 0.0061486 | 0.0001008 | 2014-06-11 | C | 0.0061486 | 0.0001008 | 2015 | 2014-06-11 | C | 33 | 0.0061486 | 0.0001008
1 | 141053 | 2014-06-11 07:05 | 2014-06-11 11:51 | 286 | 377 | 43717 | 0.13353 | 0.0011515 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Recloser 4196 Tripped, L/O. While sectionalising CB6 Tripped during severe storm conditions. Extensive sectionalising traced fault to a blown jumper at pole 788710. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 115.9602 | 112.9602 | 42586 | 0.13008 | 0.0011515 | 2014-06-11 | C | 0.13008 | 0.0011515 | 2015 | 2014-06-11 | C | 377 | 0.13008 | 0.0011515
1 | 141058 | 2014-06-11 12:15 | 2014-06-11 14:10 | 115 | 47 | 5405 | 0.016509 | 0.00014356 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CROSSARM | No Power - Tinui C937 Castlepoint tripped. Fallen tree outside notice zone. NDR. Isolated at links 7366. Replace broken HV and LV crossarms. No backfeed available. Tree(s) outside Notice Zone - No NDR. Brad Keating attended. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 115 | 112 | 5264 | 0.016078 | 0.00014356 | 2014-06-11 | C | 0.016078 | 0.00014356 | 2015 | 2014-06-11 | C | 47 | 0.016078 | 0.00014356
1 | 141060 | 2014-06-12 09:27 | 2014-06-12 10:20 | 53 | 8 | 424 | 0.0012951 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92957 - Replace 11kV defected Xarm (defect ID 174-10472) McKenna Rd pole no 726831. Isolation points: 11kV Fuses L1784 | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 400 | 0.0012218 | 2.4435e-05 | 2014-06-12 | B | 0.00061089 | 1.2218e-05 | 2015 | 2014-06-12 | B | 8 | 0.0012218 | 2.4435e-05
1 | 141061 | 2014-06-12 00:03 | 2014-06-12 11:12 | 669 | 446 | 277492 | 0.84758 | 0.0013623 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | INSULATOR | 1/ No Power 2/ CB 2 Opened after repeated A/R attempts 3/ - 4/ Tree in Fuses, Faulty Insulator and surge arrestors. 5/ Fuses FP203, FP302, FP317 Pole 209598, and Fuses SD2-025 6/ SD2-007 7/ OMO3 at SC2-024 back to SD2-004 8/ 11kV Insula | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 622.1794 | 619.1794 | 276154 | 0.84349 | 0.0013623 | 2014-06-12 | C | 0.84349 | 0.0013623 | 2015 | 2014-06-12 | C | 446 | 0.84349 | 0.0013623
1 | 141062 | 2014-06-11 23:59 | 2014-06-12 11:11 | 672 | 31 | 20832 | 0.06363 | 9.4687e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | JUMPER | 1/ No Power 2/ 3/ 4/ Mechanical Damage 5/ Transformer TE3-114 6/ Fuses SF3-001 7/ 8/ Jumpers repaired 9/ Yes 10/no 11/Shane Pepperell 12/ 13/ 14/ | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 672 | 669 | 20739 | 0.063346 | 9.4687e-05 | 2014-06-11 | C | 0.063346 | 9.4687e-05 | 2015 | 2014-06-11 | C | 31 | 0.063346 | 9.4687e-05
1 | 141063 | 2014-06-11 21:16 | 2014-06-12 12:06 | 890 | 298 | 59600 | 0.18204 | 0.00091022 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | 1/No Power Beyond ABS SD4-163 After isolation due to Car v Pole. Paul Cooper was Attending and replaced pole and Associated Hardware.Works are completed and are NDR. | F3 | BROOKFIELD TCE | OTUMOETAI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 200 | 197 | 58706 | 0.17931 | 0.00091022 | 2014-06-11 | C | 0.17931 | 0.00091022 | 2015 | 2014-06-11 | C | 298 | 0.17931 | 0.00091022
1 | 141066 | 2014-06-12 10:05 | 2014-06-12 12:32 | 147 | 80 | 11760 | 0.03592 | 0.00024435 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - OH | SIN: 14/92967 - Replace ABS V41/1 install new handle and earthing and remove DNO number 140307. Isolation points: ABS V35 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 147 | 144 | 11520 | 0.035187 | 0.00024435 | 2014-06-12 | B | 0.017593 | 0.00012218 | 2015 | 2014-06-12 | B | 80 | 0.035187 | 0.00024435
1 | 141067 | 2014-06-12 08:45 | 2014-06-12 11:50 | 185 | 16 | 2960 | 0.0090411 | 4.8871e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CONDUCTOR | SIN: 14/92958 - Straighten 11kV pole 793496 and resag conductor, repair 11kV conductor at pole 794696 broken strand. Isolation points: ABS 1125, Fuses 859 | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 185 | 182 | 2912 | 0.0088945 | 4.8871e-05 | 2014-06-12 | B | 0.0044472 | 2.4435e-05 | 2015 | 2014-06-12 | B | 16 | 0.0088945 | 4.8871e-05
1 | 141069 | 2014-06-11 05:26 | 2014-06-11 10:30 | 304 | 421 | 127984 | 0.39092 | 0.0012859 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power - Tahuna CB2 tripped and L/O. Process book used to get close time. | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 304 | 301 | 126721 | 0.38706 | 0.0012859 | 2014-06-11 | C | 0.38706 | 0.0012859 | 2015 | 2014-06-11 | C | 421 | 0.38706 | 0.0012859
1 | 141070 | 2014-06-12 09:10 | 2014-06-12 10:04 | 54 | 35 | 1890 | 0.0057729 | 0.0001069 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | No Power - Browne St CB5 - Station Rd. Emergency isolation to replace broken DDO holders at transformer TC2300. ABS IC710 check open and tag. ABS IC1346 open and tag. Do repairs. Iro Ezekiela. | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 1785 | 0.0054521 | 0.0001069 | 2014-06-12 | C | 0.0054521 | 0.0001069 | 2015 | 2014-06-12 | C | 35 | 0.0054521 | 0.0001069
1 | 141072 | 2014-06-12 09:15 | 2014-06-12 11:45 | 150 | 12 | 1800 | 0.005498 | 3.6653e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92823 - Replace two defect 11kV poles no 772966, 772967. Isolation points: Fuses 070 | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 150 | 147 | 1764 | 0.005388 | 3.6653e-05 | 2014-06-12 | B | 0.002694 | 1.8327e-05 | 2015 | 2014-06-12 | B | 12 | 0.005388 | 3.6653e-05
1 | 141076 | 2014-06-11 00:28 | 2014-06-11 04:44 | 256 | 255 | 65280 | 0.19939 | 0.00077888 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB 4 tripped, no flags. Trees removed using hot sticks. Relivened OK | F4 | TOWNSHIP & LS | FARMER ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 256 | 253 | 64515 | 0.19706 | 0.00077888 | 2014-06-11 | C | 0.19706 | 0.00077888 | 2015 | 2014-06-11 | C | 255 | 0.19706 | 0.00077888
1 | 141078 | 2014-06-12 10:37 | 2014-06-12 11:50 | 73 | 8 | 584 | 0.0017838 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92965 - Replace defective crossarms at 11kV Pole 726882. Isolation Point: 11kV Fuse LI701. Note: Work started early in agreement with customer. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 73 | 70 | 560 | 0.0017105 | 2.4435e-05 | 2014-06-12 | B | 0.00085524 | 1.2218e-05 | 2015 | 2014-06-12 | B | 8 | 0.0017105 | 2.4435e-05
1 | 141079 | 2014-06-11 05:10 | 2014-06-11 12:59 | 469 | 3717 | 838104 | 2.5599 | 0.011353 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | Defective Component - GRE CB 122 & 142, BLM 82 & AON CB 82 tripped causing loss of supply to AON, KTK, & KPT Subs. Sub-trans sectionalised and subs restoreded. Fault isolated to broken pole. Pole replaced, relivened OK | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 225.4786 | 222.4786 | 826953 | 2.5259 | 0.011353 | 2014-06-11 | C | 2.5259 | 0.011353 | 2015 | 2014-06-11 | C | 3717 | 2.5259 | 0.011353
1 | 141080 | 2014-06-10 09:15 | 2014-06-10 14:10 | 295 | 64 | 18880 | 0.057668 | 0.00019548 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92293 - Replace pole 814786. Isolation poitns: Temp Links number 1, S563 | F3/F4 | WAITE ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 295 | 292 | 18688 | 0.057081 | 0.00019548 | 2014-06-10 | B | 0.028541 | 9.7742e-05 | 2015 | 2014-06-10 | B | 64 | 0.057081 | 0.00019548
1 | 141081 | 2014-06-11 16:45 | 2014-06-12 11:45 | 1140 | 2 | 2280 | 0.0069641 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | LIGHTNING | LIGHTNING | DISTRIBUTION TRANSFORMER | Lightning -Faultman dispatched to investigate No Powers found that Transformer 4085W was blown and required replacement. Line crew attended next morning and replaced transformer. Materials used: 1x 15kVA single phase transformer. Attended by Karl Rodgers/ | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 1140 | 1137 | 2274 | 0.0069458 | 6.1088e-06 | 2014-06-11 | C | 0.0069458 | 6.109e-06 | 2015 | 2014-06-11 | C | 2 | 0.0069458 | 6.1088e-06
1 | 141082 | 2014-06-12 17:45 | 2014-06-12 22:28 | 283 | 24 | 6792 | 0.020746 | 7.3306e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | No Power -A shutdown required to Change cross arm at pole 810043 Isolation point Fuses 997 Used 1 X Crossarm 3 X H/T Insulators karl rogers Attended | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 283 | 280 | 6720 | 0.020526 | 7.3306e-05 | 2014-06-12 | C | 0.020526 | 7.3306e-05 | 2015 | 2014-06-12 | C | 24 | 0.020526 | 7.3306e-05
1 | 141083 | 2014-06-12 19:41 | 2014-06-12 22:04 | 143 | 848 | 54811 | 0.16742 | 0.0025902 | No Power | 11000 | Unplanned | Distribution Equip. | FOREIGN INTERFERENCE | OPOSSUM | RECLOSER | Animals - opossum - at 19:41 Coromandel Sub, CB 5 Manaia Feeder, Tripped, O/C, L/O. Faultman Dispatched & Investigation Began. Recloser RC12 was bypassed due to issues with protection on Recloser. Opened RC 12 Bypass ABS 321. Reclosed CB 5 and Held In. Fe | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 64.6356 | 61.6356 | 52267 | 0.15965 | 0.0025902 | 2014-06-12 | C | 0.15965 | 0.0025902 | 2015 | 2014-06-12 | C | 848 | 0.15965 | 0.0025902
1 | 141084 | 2014-06-11 13:54 | 2014-06-12 19:56 | 1802 | 154 | 80748 | 0.24664 | 0.00047038 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | RECLOSER | Defective Component - at 13:54, Atuaroa Sub, CB 6 Te Puke Quarry Rd Feeder, Recloser 9274 Tripped, L/O. Faultman Dispatched & Investigation Began. Multiple Issues on this feeder. Concluded with Lightning arrestors being disconnected at Fuses SE5-158 as be | F1/F4 | TE PUKE QUARRY RD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 524.3377 | 521.3377 | 80286 | 0.24523 | 0.00047038 | 2014-06-11 | C | 0.24523 | 0.00047038 | 2015 | 2014-06-11 | C | 154 | 0.24523 | 0.00047038
1 | 141085 | 2014-06-12 22:15 | 2014-06-13 23:18 | 1503 | 16 | 24048 | 0.073453 | 4.8871e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | WA: 14/92963 - LTOS 11kV oil switches 530/6 after isolation. Obtain live tank oil sample in accordance with standard 393S084 at 11kV Sw/gear 530/6 . Isolation points: 11kV Sw/gear 530/6. Transformer could not be changes as could not earth F/S 530/6. Tank | F2 | CITY 5 | CITY SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 1503 | 1500 | 24000 | 0.073306 | 4.8871e-05 | 2014-06-12 | B | 0.036653 | 2.4435e-05 | 2015 | 2014-06-12 | B | 16 | 0.073306 | 4.8871e-05
1 | 141086 | 2014-06-12 15:00 | 2014-06-12 17:15 | 135 | 1 | 135 | 0.00041235 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | ADVERSE WEATHER | WIND | DISTRIBUTION TRANSFORMER | 1/ No Power 2/- 3/- 4/ Lightning Struck Transformer 5/ Transformer TE5-024 6/- Transformer TE5-024 Fuses 7/- 8/11kV Transformer 9/ Yes Complete 10/ No NDR 11/ Robin McClean Attended 12/- 13/- 14/- | F1/F4 | TE PUKE QUARRY RD | ATUAROA AVE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 132 | 0.00040318 | 3.0544e-06 | 2014-06-12 | C | 0.00040318 | 3.054e-06 | 2015 | 2014-06-12 | C | 1 | 0.00040318 | 3.0544e-06
1 | 141087 | 2014-06-11 04:23 | 2014-06-11 16:30 | 727 | 338 | 92755 | 0.28331 | 0.0010324 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | 1/No Power 2/ AON3 Tripped 3/ Locked Out 4/ Trees on Lines and Lines Down 5/Pole 205243 6/ AON3 , ABS SC2-081, Sw/gear SC2-072, SC2-043 7/ Backfeed from OMO3 via Sectionaliser 9702/2 back to Recloser RS9489/2 8/ Line Crimps 9/ Yes | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 274.4231 | 271.4231 | 91741 | 0.28022 | 0.0010324 | 2014-06-11 | C | 0.28022 | 0.0010324 | 2015 | 2014-06-11 | C | 338 | 0.28022 | 0.0010324
1 | 141091 | 2014-06-11 16:40 | 2014-06-11 21:00 | 260 | 406 | 63539 | 0.19408 | 0.0012401 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - CB 2 tripped, no flags. Feeder patrolled & sectionalised. Lines down found past ABS SD3-014. Lines repaired, relivened OK | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 156.5 | 153.5 | 62321 | 0.19035 | 0.0012401 | 2014-06-11 | C | 0.19035 | 0.0012401 | 2015 | 2014-06-11 | C | 406 | 0.19035 | 0.0012401
1 | 141092 | 2014-06-10 22:33 | 2014-06-11 17:39 | 1146 | 529 | 213754 | 0.6529 | 0.0016158 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS | CONDUCTOR | 1/No Power 2/RecloserRC12 3/ Locked Open 4/ Unknown 5/Pole T1582 6/ ABS IP428, ABS IC311, ABS IC368, ABS IC380, ABS IP448. 7/ Backfeed from THS4 Via Sectionaliser9235/2 to ABS IC368 8/ Unknown 9/ All Work Complete 10/ No N | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 404.0718 | 401.0718 | 212167 | 0.64805 | 0.0016158 | 2014-06-10 | C | 0.64805 | 0.0016158 | 2015 | 2014-06-10 | C | 529 | 0.64805 | 0.0016158
1 | 141097 | 2014-06-12 00:22 | 2014-06-12 12:33 | 731 | 786 | 293535 | 0.89658 | 0.0024008 | No Power | 11000 | Unplanned | Distribution Equip. | ADVERSE WEATHER | WIND BLOW DEBRIS | DISTRIBUTION TRANSFORMER | 1/ No Power 2/ CB COR5 3/ Locked Out 4/Reported Flashes 5/at Transformer TC1343 6/ABS IP428, ABS 349, Fuses FP1238 7/ Sectionaliser 9235/2 8/ Unknown Equipment 9/ All Complete 10/ No NDR 11/ Shane Walker 12/ See related report 1 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 373.4542 | 370.4542 | 291177 | 0.88938 | 0.0024008 | 2014-06-12 | C | 0.88938 | 0.0024008 | 2015 | 2014-06-12 | C | 786 | 0.88938 | 0.0024008
1 | 141098 | 2014-06-11 06:35 | 2014-06-11 08:15 | 100 | 249 | 7658 | 0.023391 | 0.00076055 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - CB 4 tripped, no flags. Feeder sectionalised and line found off insulator past ABS IC711. Line repaired, relivened OK. | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 30.755 | 27.755 | 6911 | 0.021109 | 0.00076055 | 2014-06-11 | C | 0.021109 | 0.00076055 | 2015 | 2014-06-11 | C | 249 | 0.021109 | 0.00076055
1 | 141100 | 2014-06-11 10:32 | 2014-06-11 13:28 | 176 | 35 | 6160 | 0.018815 | 0.0001069 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Outage required from KPE CB 6 to ABS 471 to repair lines down. Backfeed from KPE5 via ABS IC447. Lines repaired, relivened OK. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 176 | 173 | 6055 | 0.018495 | 0.0001069 | 2014-06-11 | C | 0.018495 | 0.0001069 | 2015 | 2014-06-11 | C | 35 | 0.018495 | 0.0001069
1 | 141102 | 2014-06-13 09:26 | 2014-06-13 10:18 | 52 | 44 | 2288 | 0.0069885 | 0.00013439 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | CROSSARM | SIN: 14/92872 - 503 East Rd Stratford (Cloton Rd Industrial) ( HV Xarm very loose on pole 735991 King bolt bent will need to be cut off and replaced w/ new bolt. Isolation points:11kV ABS 5755, Links 6287 | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 2156 | 0.0065853 | 0.00013439 | 2014-06-13 | B | 0.0032927 | 6.7197e-05 | 2015 | 2014-06-13 | B | 44 | 0.0065853 | 0.00013439
1 | 141103 | 2014-06-11 03:40 | 2014-06-11 14:00 | 620 | 10097 | 5822458 | 17.7843 | 0.030841 | No Power | 66000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CROSSARM | Trees - CB 1092 tripped. Trees found through lines which damaged 5 crossarms. Service restored from TAI CB 60. Trees removed and cross arms replaced. Relivened OK. Tree(s) outside Notice Zone - No NDR. Outage followed on in FRN 141322, because of outdef f | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 576.6523 | 573.6523 | 5792167 | 17.6917 | 0.030841 | 2014-06-11 | C | 17.6917 | 0.030841 | 2015 | 2014-06-11 | C | 10097 | 17.6917 | 0.030841
1 | 141104 | 2014-06-11 13:00 | 2014-06-11 15:26 | 146 | 232 | 11969 | 0.036558 | 0.00070863 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/No Power 2/ Recloser RC12 3/ RC12 Tripped 4/ No Fault Found 5/ Mania Road Coromandel 6/ Isolation Points ABS IC353, ABS IP428, ABS IC311 7/ No Backfeeds 8/ No Equipment 9/ All complete 10/ No NDR 11/ Andrew King Attended | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 51.5905 | 48.5905 | 11273 | 0.034433 | 0.00070863 | 2014-06-11 | C | 0.034433 | 0.00070863 | 2015 | 2014-06-11 | C | 232 | 0.034433 | 0.00070863
1 | 141106 | 2014-06-12 18:53 | 2014-06-13 12:30 | 1057 | 3 | 3171 | 0.0096856 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | POLE | Defective Component -Faultman found Fuses 7480 open after a fault call, line was only patrolled at day light due to the terran and they found that the top of the pole had burnt off, Faultman isolated the line at Fuses 7480 to fit a new cross arm on pole 8 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1057 | 1054 | 3162 | 0.0096581 | 9.1633e-06 | 2014-06-12 | C | 0.0096581 | 9.163e-06 | 2015 | 2014-06-12 | C | 3 | 0.0096581 | 9.1633e-06
1 | 141107 | 2014-06-13 09:20 | 2014-06-13 10:40 | 80 | 5 | 400 | 0.0012218 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92971 - Replace defected Xarm (defect ID 146-11050) pole no 729147 Wilford Rd. Isolation points: HV Fuses L1799 | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 385 | 0.001176 | 1.5272e-05 | 2014-06-13 | B | 0.00058798 | 7.636e-06 | 2015 | 2014-06-13 | B | 5 | 0.001176 | 1.5272e-05
1 | 141109 | 2014-06-13 10:20 | 2014-06-13 10:52 | 32 | 4 | 128 | 0.00039097 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | JOINT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Outage required at Transformer TC3288 Fuses to repair a broken jumper. Repaired / relivened OK. | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 116 | 0.00035431 | 1.2218e-05 | 2014-06-13 | C | 0.00035431 | 1.2218e-05 | 2015 | 2014-06-13 | C | 4 | 0.00035431 | 1.2218e-05
1 | 141110 | 2014-06-13 11:12 | 2014-06-13 12:30 | 78 | 3 | 234 | 0.00071474 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92970 - Replace defected Xarm (defect ID 146-11055) pole no 728907 Clifford Rd. Isolation points: HV fuses L1706 | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 78 | 75 | 225 | 0.00068725 | 9.1633e-06 | 2014-06-13 | B | 0.00034362 | 4.582e-06 | 2015 | 2014-06-13 | B | 3 | 0.00068725 | 9.1633e-06
1 | 141111 | 2014-06-13 11:23 | 2014-06-13 15:23 | 240 | 13 | 3120 | 0.0095298 | 3.9708e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | LAND SLIPPAGE | POLE | Wind - Outage required between ABS 720, 748 and 752 to replace a pole. Original pole on a a lean after stormy conditions with soggy ground conditions underneath. New Pole and associated hardware moved to more stable location. Relivened OK. | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 240 | 237 | 3081 | 0.0094107 | 3.9708e-05 | 2014-06-13 | C | 0.0094107 | 3.9708e-05 | 2015 | 2014-06-13 | C | 13 | 0.0094107 | 3.9708e-05
1 | 141112 | 2014-06-13 12:40 | 2014-06-13 14:57 | 137 | 139 | 5987 | 0.018287 | 0.00042456 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | CONDUCTOR | Other/miscellaneous cause - Initial tripping on Tower Rd CB3 causing some loss of Supply in Matamata. Contractors were working on LiveLine Permit 14/90974 at the time removing temp links No. FP1581 and FP1582. It appears one of the sleeves "let go" causin | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 43.0719 | 40.0719 | 5570 | 0.017013 | 0.00042456 | 2014-06-13 | C | 0.017013 | 0.00042457 | 2015 | 2014-06-13 | C | 139 | 0.017013 | 0.00042456
1 | 141113 | 2014-06-13 17:52 | 2014-06-13 18:00 | 8 | 13 | 104 | 0.00031766 | 3.9708e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Reports of part power found ABS 752 has a blown jumper, centre phase, incoming side. ABS open and tagged with backfeed at ABS 720. Red Pin 140609. | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 8 | 5 | 65 | 0.00019854 | 3.9708e-05 | 2014-06-13 | C | 0.00019854 | 3.9708e-05 | 2015 | 2014-06-13 | C | 13 | 0.00019854 | 3.9708e-05
1 | 141114 | 2014-06-13 11:30 | 2014-06-13 15:05 | 215 | 166 | 35690 | 0.10901 | 0.00050703 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92873 - Replace 11kV pole S0511. Isolation points: 11kV ABS IC2628 & 392. | F1/F4 | KOPU | MATATOKI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 215 | 212 | 35192 | 0.10749 | 0.00050703 | 2014-06-13 | B | 0.053746 | 0.00025352 | 2015 | 2014-06-13 | B | 166 | 0.10749 | 0.00050703
1 | 141115 | 2014-06-13 20:58 | 2014-06-13 22:23 | 85 | 1024 | 40032 | 0.12227 | 0.0031277 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -CB 22 Trip, O/C A-B-C Phase, Faultmen dispatched to sectionalise and patrol. No fault found. Attended by Chris Naylor/Dave Whale/Shane Robinson | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39.0938 | 36.0938 | 36960 | 0.11289 | 0.0031277 | 2014-06-13 | C | 0.11289 | 0.0031277 | 2015 | 2014-06-13 | C | 1024 | 0.11289 | 0.0031277
1 | 141118 | 2014-06-14 13:04 | 2014-06-14 13:28 | 24 | 3 | 72 | 0.00021992 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -Faultman found a branch on the line at pole 702237 while attending a fault call, line was isolated at Fuses 8485 and branch was knocked off with hot line sticks. Brent Moratti attended | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 24 | 21 | 63 | 0.00019243 | 9.1633e-06 | 2014-06-14 | C | 0.00019243 | 9.163e-06 | 2015 | 2014-06-14 | C | 3 | 0.00019243 | 9.1633e-06
1 | 141119 | 2014-06-14 11:33 | 2014-06-14 13:35 | 122 | 235 | 11281 | 0.034457 | 0.00071779 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component -CB 6 tripped on B phase O/C flags, line was sectionalised at and a floating wire was found at pole P02073, line was isolated at ABS's N7 and N58 to rebind the floating wire, back feeds were put in place at MABs N34 and N16. Bruce Mehr | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 48.0043 | 45.0043 | 10576 | 0.032304 | 0.00071779 | 2014-06-14 | C | 0.032304 | 0.00071779 | 2015 | 2014-06-14 | C | 235 | 0.032304 | 0.00071779
1 | 141120 | 2014-06-14 15:28 | 2014-06-14 15:48 | 20 | 14 | 280 | 0.00085524 | 4.2762e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | BINDER | Floater located by faultman on pole V0454 - result of recent storm - line isolated between ABS IP448 & IC311 to repair - backfeed establised from recloser 9235/2 to ABS IP448 for duration of outage - 1 x AL binder only material required - Shane Walker att | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 20 | 17 | 238 | 0.00072695 | 4.2762e-05 | 2014-06-14 | C | 0.00072695 | 4.2762e-05 | 2015 | 2014-06-14 | C | 14 | 0.00072695 | 4.2762e-05
1 | 141121 | 2014-06-14 07:24 | 2014-06-14 13:42 | 378 | 2439 | 379974 | 1.1606 | 0.0074497 | No Power | 33000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | POLE | Report from fire service of truck v pole on cnr of SH 2 & Thompsons track Katikati - Andy Wreaks arrived on site shorty after (in area as coincidence) and reported pole with 11kV & 33kV broken and in dangerous condition - no trippings at time of impact bu | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 155.7909 | 152.7909 | 372657 | 1.1383 | 0.0074497 | 2014-06-14 | C | 1.1383 | 0.0074497 | 2015 | 2014-06-14 | C | 2439 | 1.1383 | 0.0074497
1 | 141122 | 2014-06-14 07:24 | 2014-06-14 13:27 | 363 | 254 | 91932 | 0.2808 | 0.00077582 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | THIRD PARTY DAMAGE | POLE | Report from fire service of truck v pole on cnr of SH 2 & Thompsons track Katikati - Andy Wreaks arrived on site shorty after (in area as coincidence) and reported pole with 11kV & 33kV broken and in dangerous condition - no trippings at time of impact bu | F4 | KATIKATI | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 361.937 | 358.937 | 91170 | 0.27847 | 0.00077582 | 2014-06-14 | C | 0.27847 | 0.00077582 | 2015 | 2014-06-14 | C | 254 | 0.27847 | 0.00077582
1 | 141124 | 2014-06-14 21:45 | 2014-06-14 22:56 | 71 | 51 | 3621 | 0.01106 | 0.00015578 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component -Faultman investigating part power complaints found a line down at Pole 778391. Isolated at ABS 596 and ABS 965, and backfeed installed via VS4621. Line repaired and feeder restored to normal configuration. Materials used: 4 mtrs of sq | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 3468 | 0.010593 | 0.00015578 | 2014-06-14 | C | 0.010593 | 0.00015578 | 2015 | 2014-06-14 | C | 51 | 0.010593 | 0.00015578
1 | 141127 | 2014-06-15 10:00 | 2014-06-15 11:00 | 60 | 16 | 960 | 0.0029322 | 4.8871e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/92981 - Put 11kV cuts into network for Treescape to clear trees causing feeder tripping. Cuts at poles 835256 and 835280 15.06.14. Reconnection back to normal on 22.06.2014. Isolation points: C850, S152 | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 912 | 0.0027856 | 4.8871e-05 | 2014-06-15 | B | 0.0013928 | 2.4435e-05 | 2015 | 2014-06-15 | B | 16 | 0.0027856 | 4.8871e-05
1 | 141128 | 2014-06-15 09:00 | 2014-06-15 10:50 | 110 | 19 | 2090 | 0.0063837 | 5.8034e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92875 - Change oil on TX T6/563T (high moisture and acidity content). Isolation points: SG 10181/3, 314 | F2 | ARMSTRONG ST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 110 | 107 | 2033 | 0.0062096 | 5.8034e-05 | 2014-06-15 | B | 0.0031048 | 2.9017e-05 | 2015 | 2014-06-15 | B | 19 | 0.0062096 | 5.8034e-05
1 | 141129 | 2014-06-15 08:00 | 2014-06-15 09:12 | 72 | 2 | 144 | 0.00043984 | 6.1088e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Transformer TC2579 found to be faulty by f/man attending N/P call - isolated at transformer fuses for replacement - new transformer only materials required - Shane Walker attended | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 138 | 0.00042151 | 6.1088e-06 | 2014-06-15 | C | 0.00042151 | 6.109e-06 | 2015 | 2014-06-15 | C | 2 | 0.00042151 | 6.1088e-06
1 | 141130 | 2014-06-15 00:23 | 2014-06-15 14:25 | 842 | 175 | 23065 | 0.07045 | 0.00053452 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | CB 2 tripped to L/O - E/F & O/C flags - car v pole on Stanley Rd South - pole demolished at number 384174 - line isolated at ABS IC609, IC629 & Links 9343/6 - back feed established from recloser 9715 for duration of outage - all supply restored after repa | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 131.8 | 128.8 | 22540 | 0.068847 | 0.00053452 | 2014-06-15 | C | 0.068847 | 0.00053452 | 2015 | 2014-06-15 | C | 175 | 0.068847 | 0.00053452
1 | 141132 | 2014-06-15 19:42 | 2014-06-15 20:32 | 50 | 727 | 35572 | 0.10865 | 0.0022206 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Trip. O/C. L/O. Initially no fault found and feeder went back in But later found to have part power to most of the feeder. Jumper found off at Pole 200653. See Outdef 141133. Andy Wreaks Faultman. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 48.9298 | 45.9298 | 33391 | 0.10199 | 0.0022206 | 2014-06-15 | C | 0.10199 | 0.0022206 | 2015 | 2014-06-15 | C | 727 | 0.10199 | 0.0022206
1 | 141133 | 2014-06-15 22:04 | 2014-06-15 23:09 | 65 | 295 | 19027 | 0.058117 | 0.00090105 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component - Emergency Isolation to repair Broken Jumper at Pole 200653. Andy Wreaks Faultman. Isolation Between ABS's SD3-009, SD#-010 & SD3-112. Backfeed via RS 9805. Jumper Repaired. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 64.4983 | 61.4983 | 18142 | 0.055413 | 0.00090105 | 2014-06-15 | C | 0.055413 | 0.00090105 | 2015 | 2014-06-15 | C | 295 | 0.055413 | 0.00090105
1 | 141135 | 2014-06-16 05:28 | 2014-06-16 06:11 | 43 | 46 | 1978 | 0.0060417 | 0.0001405 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees - Emergency Isolation to remove trees from Lines and repair downed line. Trees removed and line rejoined. Ted Glasgow Faultman. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 1840 | 0.0056201 | 0.0001405 | 2014-06-16 | C | 0.0056201 | 0.0001405 | 2015 | 2014-06-16 | C | 46 | 0.0056201 | 0.0001405
1 | 141136 | 2014-06-11 04:43 | 2014-06-12 16:00 | 2117 | 273 | 261987 | 0.80022 | 0.00083386 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/No Power 2/ Sectionaliser 9222 Tripped 3/ Locked out 4/ Lines Down 5/ Pole 212180 6/ Isolations at ABS SE3-014, ABS IP183, ABS SF3-010 7/ Backfeed from ABS SF3-010 8/ Unknown 9/ Work not Complete- Transformer TE3132 requires | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 959.6593 | 956.6593 | 261168 | 0.79772 | 0.00083386 | 2014-06-11 | C | 0.79772 | 0.00083386 | 2015 | 2014-06-11 | C | 273 | 0.79772 | 0.00083386
1 | 141137 | 2014-06-13 12:04 | 2014-06-13 18:34 | 390 | 746 | 125177 | 0.38234 | 0.0022786 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | 1/ No Power 2/COR CB 5 Tripped 3/ E/F O/C L/O 4/ Trees in Lines 5/ Pole 854055 6/IP428, ABS321, IC491, IC353, IC491, IC311, IC368, IP488, IP448, IP380, IC368, 7/Sectionaliser 9235 8/Tree cutters 9/ Works Complete 10/ No NDR 11 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 167.7976 | 164.7976 | 122939 | 0.37551 | 0.0022786 | 2014-06-13 | C | 0.37551 | 0.0022786 | 2015 | 2014-06-13 | C | 746 | 0.37551 | 0.0022786
1 | 141138 | 2014-06-12 15:45 | 2014-06-12 16:36 | 51 | 529 | 26979 | 0.082405 | 0.0016158 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | RECLOSER | 1/No Power 2/Recloser RC12 Tripped 3/- 4/Damaged Recloser 5/ RC12 6/- 7/Sectionaliser 9235 opened 8/- 9/RC12 DNO Tagged 10/No NDR 11/- 12/- 13/- 14/ Note RC12 bypassed with DNO Tag 140608 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 51 | 48 | 25392 | 0.077558 | 0.0016158 | 2014-06-12 | C | 0.077558 | 0.0016158 | 2015 | 2014-06-12 | C | 529 | 0.077558 | 0.0016158
1 | 141139 | 2014-06-13 09:32 | 2014-06-13 12:58 | 206 | 209 | 43054 | 0.13151 | 0.00063837 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | 1/No Power 2/AON CB 4 4/Lines Down 5/Pole 201141 6/ABS IP537, ABS SB!-045, Links 9515/4 7/ No Backfeeds 8/ Unknown Equipment used 9/ Works Complete 10/No NDR 11/ Clint Johnston Attended | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 206 | 203 | 42427 | 0.12959 | 0.00063837 | 2014-06-13 | C | 0.12959 | 0.00063838 | 2015 | 2014-06-13 | C | 209 | 0.12959 | 0.00063837
1 | 141140 | 2014-06-13 10:54 | 2014-06-13 12:03 | 69 | 261 | 15710 | 0.047985 | 0.0007972 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | 1/Isolate to Correct Phasing 2/- 3/- 4/ Incorrect Phasing at ABS IC936 5/- 6/ABS IC936, ABS 358, Recloser 9281 7/Backfeed Sectionaliser 9717/2 8/- 9/Work Complete 10/ No NDR 11/ Kim Lambert Attended 12/- 13/- 14/- | F3 | TOTARA | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 60.1916 | 57.1916 | 14927 | 0.045593 | 0.0007972 | 2014-06-13 | C | 0.045593 | 0.00079721 | 2015 | 2014-06-13 | C | 261 | 0.045593 | 0.0007972
1 | 141141 | 2014-06-13 11:37 | 2014-06-13 13:38 | 121 | 1 | 121 | 0.00036959 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | 1/No Power 2/- 3/- 4/ Lines Down 5/ Pole 264518 6/Fuses FC2416 7/ No Feedbacks 8/ Line Links 9/ All Work Complete 10/ No NDR 11/ Brian Fisher Attended 12/- 13/- 14/- | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 121 | 118 | 118 | 0.00036042 | 3.0544e-06 | 2014-06-13 | C | 0.00036042 | 3.054e-06 | 2015 | 2014-06-13 | C | 1 | 0.00036042 | 3.0544e-06
1 | 141142 | 2014-06-11 | 2014-06-11 12:25 | 745 | 157 | 45250 | 0.13821 | 0.00047954 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS | CONDUCTOR | 1/No Power 2/ MIK CB 5 Tripped 3/ Locked Out 4/ Roof of Bran in Lines 5/ Pole C321 6/ Feeder Isolated at ABS 675 7/ Backfeeds From ABS IC1270 8/ Line Links 9/ Works Complete 10/ No NDR 11/ Steve Martin, Warren & Adrian Sock 12/- | F4 | NGARUA | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 288.2166 | 285.2166 | 44779 | 0.13677 | 0.00047954 | 2014-06-11 | C | 0.13677 | 0.00047955 | 2015 | 2014-06-11 | C | 157 | 0.13677 | 0.00047954
1 | 141147 | 2014-06-11 03:47 | 2014-06-11 12:16 | 509 | 696 | 354264 | 1.0821 | 0.0021259 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | 1/ No Power 2/Recloser 9516 Tripped 3/ O/C 4/ Line Clash Due to Storm 5/- 6/- 7/ Sw/ Gear 9765/3 Backfeed 8/- 9/ Works Complete 10/No NDR 11/ Shane Pepperell attended 12/ 13/ 14/ | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 509 | 506 | 352176 | 1.0757 | 0.0021259 | 2014-06-11 | C | 1.0757 | 0.0021259 | 2015 | 2014-06-11 | C | 696 | 1.0757 | 0.0021259
1 | 141148 | 2014-06-11 04:37 | 2014-06-11 12:35 | 478 | 476 | 227528 | 0.69497 | 0.0014539 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | 1/No Power 2/ KPT CB1 Tripped 3/- 4/ Trees on Lines 5/ Pole 388120 6; ABS IP{534, ABS SA2-004 7 No Backfeed 8/ Tree Cutters 9/Works Complete 10/ No NDR 11/ Nick Hayward & Dion Sanders attended 12/ 13/ 14/ | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 478 | 475 | 226100 | 0.69061 | 0.0014539 | 2014-06-11 | C | 0.69061 | 0.0014539 | 2015 | 2014-06-11 | C | 476 | 0.69061 | 0.0014539
1 | 141151 | 2014-06-11 05:00 | 2014-06-12 12:56 | 1916 | 175 | 128190 | 0.39155 | 0.00053452 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/ No Power 2/ KPE CB1 Tripped 3/- 4/ Lines Down at Pole 381701 5/ 6//Isolated at ABS 522, Fuses FP1280 ABS 512 7/ No Backfeeds 8/ Line Links 9/ Works Complete 10/ No NDR 11/ Stu Simpson & James Kennedy Attended 12/ 13/ 14/ | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 732.5143 | 729.5143 | 127665 | 0.38994 | 0.00053452 | 2014-06-11 | C | 0.38994 | 0.00053452 | 2015 | 2014-06-11 | C | 175 | 0.38994 | 0.00053452
1 | 141152 | 2014-06-16 09:22 | 2014-06-16 15:00 | 338 | 2 | 676 | 0.0020648 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92099 - Replace 11kV Xarms beyond pole C13126 and replace pole mount TX TC2856 to improve ground clearances at 11kV bushings. Isolation points: Span break at pole C237. LLP's 14/92098 , 14/93260 & 14/93261 . | F4 | TOWNSHIP & LS | FARMER ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 338 | 335 | 670 | 0.0020465 | 6.1088e-06 | 2014-06-16 | B | 0.0010232 | 3.054e-06 | 2015 | 2014-06-16 | B | 2 | 0.0020465 | 6.1088e-06
1 | 141156 | 2014-06-11 04:36 | 2014-06-11 15:00 | 624 | 753 | 384983 | 1.1759 | 0.0023 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS | CONDUCTOR | 1/No Power 2/ KPE CB 3 Tripped 3/- 4/ Roof in Lines 5/ Pole O1183 6/ Isolations at ABS IC432, ABS IC459, ABS IC461 7/ Backfeed Sectionaliser 9724 8/Remove roof from Lines 9/ Works Complete 10/ No NDR 11/ Stu Simpson Attended ?. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 511.2656 | 508.2656 | 382724 | 1.169 | 0.0023 | 2014-06-11 | C | 1.169 | 0.0023 | 2015 | 2014-06-11 | C | 753 | 1.169 | 0.0023
1 | 141157 | 2014-06-12 14:30 | 2014-06-12 15:41 | 71 | 7 | 497 | 0.001518 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | 1/ No Power 2/ Fuses FP1346 Opened 3/ 4/ Broken Crossarm 5/ Pole E0343 6/ Fuses FP1346 7/ No Backfeeds 8/ Crossarm etc 9/ Works Complete 10/ No NDR 11/ Iro Ezekiel Attended | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 476 | 0.0014539 | 2.1381e-05 | 2014-06-12 | C | 0.0014539 | 2.1381e-05 | 2015 | 2014-06-12 | C | 7 | 0.0014539 | 2.1381e-05
1 | 141158 | 2014-06-16 10:39 | 2014-06-16 15:59 | 320 | 6 | 1920 | 0.0058645 | 1.8327e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92975 - Replace 11kV pole 727266 Matuku Rd also change rusty TX L460. Isolation points: LI139 | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 320 | 317 | 1902 | 0.0058095 | 1.8327e-05 | 2014-06-16 | B | 0.0029048 | 9.163e-06 | 2015 | 2014-06-16 | B | 6 | 0.0058095 | 1.8327e-05
1 | 141159 | 2014-06-16 16:18 | 2014-06-16 16:33 | 15 | 1 | 15 | 4.5816e-05 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - Emergency switching to repair floating conductor at pole 1726. Isolation at Fuses FC4058 ( no back feeds ) conductor re bound all service restored, Justin Middleton attended. Advised that 1 x binder was rep[laced. | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 12 | 3.6653e-05 | 3.0544e-06 | 2014-06-16 | C | 3.6653e-05 | 3.054e-06 | 2015 | 2014-06-16 | C | 1 | 3.6653e-05 | 3.0544e-06
1 | 141160 | 2014-06-16 11:33 | 2014-06-16 13:45 | 132 | 1 | 132 | 0.00040318 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - Emergency switching to replace blown transformer TB1 131. Nick Hyland issues own AP & isolation. Transformer replaced all service restored. Materials 1 x transformer | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 132 | 129 | 129 | 0.00039402 | 3.0544e-06 | 2014-06-16 | C | 0.00039402 | 3.054e-06 | 2015 | 2014-06-16 | C | 1 | 0.00039402 | 3.0544e-06
1 | 141162 | 2014-06-16 09:40 | 2014-06-16 12:26 | 166 | 39 | 6474 | 0.019774 | 0.00011912 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92767 - Replace 11kV pole P05962 hit by ute. Isolation points: P64 NDR number not requried. Refer to original fault record FR**** | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 166 | 163 | 6357 | 0.019417 | 0.00011912 | 2014-06-16 | B | 0.0097085 | 5.9561e-05 | 2015 | 2014-06-16 | B | 39 | 0.019417 | 0.00011912
1 | 141164 | 2014-06-16 21:38 | 2014-06-16 22:21 | 43 | 20 | 860 | 0.0026268 | 6.1088e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Broken Line found as part of Dispatch Jopb at Pole 727046 - Isolated at Fuses LI182 - Conductor repaired and Feeder returned to service - Attended by Dennis Embling - Used .5 mtr of conductor, 1X sleeve & 1 X Binder | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 800 | 0.0024435 | 6.1088e-05 | 2014-06-16 | C | 0.0024435 | 6.1088e-05 | 2015 | 2014-06-16 | C | 20 | 0.0024435 | 6.1088e-05
1 | 141165 | 2014-06-14 15:42 | 2014-06-14 17:10 | 88 | 3 | 264 | 0.00080637 | 9.1633e-06 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | 1 x blown fuse found at fuses SB1-085 - blew again on reload - cable isolated at ABS SB1-063 for testing & found faulty - repairs completed on 15/06/14 - all supply restored - David Joynt attended - Materials required, 1 x HV cable repair kit | F3/F4 | WILLS RD | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 255 | 0.00077888 | 9.1633e-06 | 2014-06-14 | C | 0.00077888 | 9.163e-06 | 2015 | 2014-06-14 | C | 3 | 0.00077888 | 9.1633e-06
1 | 141167 | 2014-06-11 05:31 | 2014-06-11 11:15 | 344 | 548 | 147514 | 0.45057 | 0.0016738 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | 1/No Power 2/ LAK CB5 Tripped 3/- 4/ Cause of Outage Unknown 5/- 6/ ABS 847, ABS 811, ABS2526, ABS 820 7/ Backfeed from Sectionaliser 9790 8/ 9/ Work Complete 10/ No Ndr 11/ Kevin Cole Attended | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 269.1861 | 266.1861 | 145870 | 0.44555 | 0.0016738 | 2014-06-11 | C | 0.44555 | 0.0016738 | 2015 | 2014-06-11 | C | 548 | 0.44555 | 0.0016738
1 | 141169 | 2014-06-11 06:47 | 2014-06-11 14:11 | 444 | 415 | 40719 | 0.12437 | 0.0012676 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CROSSARM | 1/No Power 2/ MIK CB 1 3/ Locked out 4/ Burning Cross Arm 5/ Past ABS 659 6/ ABS 659 IC704, & IC672 7/ no backfeeds 8/ Crossarm and Bolt 9/ Work Complete 10 No NDR 11/ Adrian Jake attended | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 98.1181 | 95.1181 | 39474 | 0.12057 | 0.0012676 | 2014-06-11 | C | 0.12057 | 0.0012676 | 2015 | 2014-06-11 | C | 415 | 0.12057 | 0.0012676
1 | 141170 | 2014-06-11 14:02 | 2014-06-11 18:57 | 295 | 118 | 32730 | 0.099971 | 0.00036042 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | RAIN | SURGE ARRESTOR | 1/No Power 2/ Recloser RS9480 Tripped 3/ O/C L/O 4/ Storm Weather 5/ Lightning Arrestor on pole C14208 6/ ABS IC1241 & ABS IC676 7/No Backfeeds 8/ Lightning Arrestor 9/ Work Complete 10 No NDR 11/ Ken Langman Attended | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 277.3729 | 274.3729 | 32376 | 0.09889 | 0.00036042 | 2014-06-11 | C | 0.09889 | 0.00036042 | 2015 | 2014-06-11 | C | 118 | 0.09889 | 0.00036042
1 | 141171 | 2014-06-12 12:20 | 2014-06-12 16:30 | 250 | 1 | 250 | 0.00076361 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | No Power. Line Patrolled and Blown Transformer (TP1242) located. Adverse Weather/Extreme Wind with Lightning. Isolated beyond Fuses FP114. Kevin Cole & Marty Keenan attended. | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 247 | 0.00075444 | 3.0544e-06 | 2014-06-12 | C | 0.00075444 | 3.054e-06 | 2015 | 2014-06-12 | C | 1 | 0.00075444 | 3.0544e-06
1 | 141172 | 2014-06-12 11:40 | 2014-06-12 14:07 | 147 | 3 | 441 | 0.001347 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Adverse Weather/Extreme wind. Line patrolled and floating conductor located at Pole C42400. Conductor rebound. Kawhia Ingley attended. | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 147 | 144 | 432 | 0.0013195 | 9.1633e-06 | 2014-06-12 | C | 0.0013195 | 9.163e-06 | 2015 | 2014-06-12 | C | 3 | 0.0013195 | 9.1633e-06
1 | 141173 | 2014-06-12 06:21 | 2014-06-12 10:14 | 233 | 415 | 75704 | 0.23123 | 0.0012676 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. CB 1 Tripped. L/O. Fault sectionalised. Line patrolled - no fault found. Adverse Weather/Extreme Wind. Suspect tree branch on line. Marty Keenan attended. | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 182.4193 | 179.4193 | 74459 | 0.22743 | 0.0012676 | 2014-06-12 | C | 0.22743 | 0.0012676 | 2015 | 2014-06-12 | C | 415 | 0.22743 | 0.0012676
1 | 141174 | 2014-06-11 03:49 | 2014-06-11 22:09 | 1100 | 216 | 237600 | 0.72573 | 0.00065976 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. Mikkelsen CB10. Recloser RP04 tripped. E/F. Adverse Weather/Extreme Wind. Possible Line Clash. Line not patrolled - fault unknown. Steve Martin attended. | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 1100 | 1097 | 236952 | 0.72375 | 0.00065976 | 2014-06-11 | C | 0.72375 | 0.00065976 | 2015 | 2014-06-11 | C | 216 | 0.72375 | 0.00065976
1 | 141175 | 2014-06-17 09:10 | 2014-06-17 11:35 | 145 | 2 | 290 | 0.00088578 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - Emergency switching to replace broken cross arm at pole 220657. Isolation at Fuses SD6 007 ( no back feeds ) arm replaced all service restored, T J Tanoa attended. Materials 1 x arm & 2 x 11kV insulators. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 145 | 142 | 284 | 0.00086746 | 6.1088e-06 | 2014-06-17 | C | 0.00086746 | 6.109e-06 | 2015 | 2014-06-17 | C | 2 | 0.00086746 | 6.1088e-06
1 | 141176 | 2014-06-11 17:05 | 2014-06-11 17:49 | 44 | 36 | 1584 | 0.0048382 | 0.00010996 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Line patrolled and trees located in lines at pole C388. Adverse Weather/Extreme Wind. Trees outside Notice Zone - No NDR. Kevin Cole attended. | F4 | NGARUA | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 44 | 41 | 1476 | 0.0045083 | 0.00010996 | 2014-06-11 | C | 0.0045083 | 0.00010996 | 2015 | 2014-06-11 | C | 36 | 0.0045083 | 0.00010996
1 | 141177 | 2014-06-13 10:00 | 2014-06-13 11:29 | 89 | 3 | 267 | 0.00081553 | 9.1633e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93465 - Repair rotten 11kV arm at TC3380. Pole F12556. In danger of failure. 11kv. Isolation points FC 2150. | F3 | MOWBRAY RD | WAHAROA SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 89 | 86 | 258 | 0.00078804 | 9.1633e-06 | 2014-06-13 | B | 0.00039402 | 4.582e-06 | 2015 | 2014-06-13 | B | 3 | 0.00078804 | 9.1633e-06
1 | 141179 | 2014-06-11 04:34 | 2014-06-11 12:20 | 466 | 458 | 213428 | 0.6519 | 0.0013989 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Pwer. Omokoroa CB4. Recloser 9674 Tripped. L/O. Fedder patrolled - no fault loctaed. Adverse Weather/Extrteme Wind. Suspect Line Clash. Andy Wreaks attended. | F3 | OMOKOROA RD | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 466 | 463 | 212054 | 0.6477 | 0.0013989 | 2014-06-11 | C | 0.6477 | 0.0013989 | 2015 | 2014-06-11 | C | 458 | 0.6477 | 0.0013989
1 | 141180 | 2014-06-12 15:30 | 2014-06-12 16:10 | 40 | 3 | 120 | 0.00036653 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | SURGE ARRESTOR | No Power. Adverse Weather/Extreme Wind. Emergency Isolation required to cut away blown lightning arrestors. Isolated beyond Fuses FC4132.(Kim Lambert contacted at 1544 to put fuses back in). | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 111 | 0.00033904 | 9.1633e-06 | 2014-06-12 | C | 0.00033904 | 9.163e-06 | 2015 | 2014-06-12 | C | 3 | 0.00033904 | 9.1633e-06
1 | 141181 | 2014-06-11 02:23 | 2014-06-11 03:03 | 40 | 326 | 13040 | 0.03983 | 0.00099574 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. PMA CB8. Recloser RP09 reclosed. L/O. Adverse Wether/Extreme Wind. Line not patrolled - fault unknown. | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 12062 | 0.036842 | 0.00099574 | 2014-06-11 | C | 0.036842 | 0.00099574 | 2015 | 2014-06-11 | C | 326 | 0.036842 | 0.00099574
1 | 141182 | 2014-06-17 09:21 | 2014-06-17 12:00 | 159 | 5 | 795 | 0.0024283 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/92764 - Offload T3/165 T3/367, make gap P49073 LL, then replace 11kV pole P30523 under AP, then close gap LL, restore load to TX T3/165, T3/367. Isolation points: M76 LLP, Gap P49073 AP LLPs 14/92765, 14/92766 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 159 | 156 | 780 | 0.0023825 | 1.5272e-05 | 2014-06-17 | B | 0.0011912 | 7.636e-06 | 2015 | 2014-06-17 | B | 5 | 0.0023825 | 1.5272e-05
1 | 141183 | 2014-06-17 11:10 | 2014-06-17 11:28 | 18 | 211 | 3798 | 0.011601 | 0.00064448 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | Unknown Cause - Recloser RP04 L/O No flags Not patrolled Reclosed | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 18 | 15 | 3165 | 0.0096673 | 0.00064448 | 2014-06-17 | C | 0.0096673 | 0.00064448 | 2015 | 2014-06-17 | C | 211 | 0.0096673 | 0.00064448
1 | 141184 | 2014-06-17 09:45 | 2014-06-17 12:36 | 171 | 28 | 4788 | 0.014625 | 8.5524e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/93397 - Run in 500m of new conductor and remove temp line breaks at pole P28521 and P06379, poles P06847 and P06844 due to severe wind damage. Isolation points: V16, aBS V19 | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 171 | 168 | 4704 | 0.014368 | 8.5524e-05 | 2014-06-17 | B | 0.007184 | 4.2762e-05 | 2015 | 2014-06-17 | B | 28 | 0.014368 | 8.5524e-05
1 | 141187 | 2014-06-17 09:00 | 2014-06-17 10:14 | 74 | 76 | 5624 | 0.017178 | 0.00023214 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | RECLOSER | SIN: 14/92992 - Erect new 11m pole and terminate line, liven new entec sectionaliser 4706 also liven new TX 4841W and complete SCADA checks. Isolation points: ABS 1320, Links 143 | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 74 | 71 | 5396 | 0.016482 | 0.00023214 | 2014-06-17 | B | 0.0082408 | 0.00011607 | 2015 | 2014-06-17 | B | 76 | 0.016482 | 0.00023214
1 | 141188 | 2014-06-12 05:59 | 2014-06-12 06:15 | 16 | 891 | 14256 | 0.043544 | 0.0027215 | No Power | 11000 | Unplanned | Distribution Equip. | ADVERSE WEATHER | RAIN | CIRCUIT BREAKER | 1/No Power 2/ Mik CB 2, CB 4 & CB 6 Tripped 3/ CB 2 Autoreclosed CB 4 Locked Out CB 6 Autoreclosed 4/ Caused by Lightning 5 CB 2,4 ,6 No isolations 7/ no Backfeeds 9/ Work Complete 10/No NDR | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 16 | 13 | 11583 | 0.035379 | 0.0027215 | 2014-06-12 | C | 0.035379 | 0.0027215 | 2015 | 2014-06-12 | C | 891 | 0.035379 | 0.0027215
1 | 141189 | 2014-06-11 03:13 | 2014-06-11 10:25 | 432 | 326 | 120383 | 0.3677 | 0.00099574 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/No Power 2/ Sectionaliser RP09 3/ Locked Out 4/ Lines Down 5/ Pole 220104 6/Isolated at ABS SD5-002 7/No Backfeeds 8/ 9/ Works Complete 10/No NDR 11/Clint Johnston Attended | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 369.273 | 366.273 | 119405 | 0.36471 | 0.00099574 | 2014-06-11 | C | 0.36471 | 0.00099574 | 2015 | 2014-06-11 | C | 326 | 0.36471 | 0.00099574
1 | 141190 | 2014-06-11 00:31 | 2014-06-11 04:19 | 228 | 325 | 74100 | 0.22633 | 0.00099269 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | 1/No Power 2/Recloser 9121 3/ L/O 4/Storm Line Clash 5/ 6/ 7/No Backfeeds 8/ 9/ Works Complete 10/No NDR | F4 | KEREONE | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 228 | 225 | 73125 | 0.22335 | 0.00099269 | 2014-06-11 | C | 0.22335 | 0.00099269 | 2015 | 2014-06-11 | C | 325 | 0.22335 | 0.00099269
1 | 141191 | 2014-06-10 23:27 | 2014-06-11 03:29 | 242 | 1133 | 195768 | 0.59796 | 0.0034607 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | 1/No Power 2/PKO CB 2 3/ L/O 4/ Break in Lines 5/Pole I13625 6/ABS972, ABS1189, S/G IC3163, ABS972 7/Backfeed ABS 362 8/ Removed branch from lines at Pole I13625. 9/Work Complete 10/ No NDR 11/ Marty Keenan, Tomatu Pene Attended | F3 | MVILLE SOUTH | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 172.7873 | 169.7873 | 192369 | 0.58758 | 0.0034607 | 2014-06-10 | C | 0.58758 | 0.0034607 | 2015 | 2014-06-10 | C | 1133 | 0.58758 | 0.0034607
1 | 141192 | 2014-06-16 09:40 | 2014-06-16 13:10 | 210 | 1 | 210 | 0.00064143 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92029 - NOTE:Move to alternate date 17/06/14. Replace defective TX T1808. Isolation points: Links 7290 | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 210 | 207 | 207 | 0.00063227 | 3.0544e-06 | 2014-06-16 | B | 0.00031613 | 1.527e-06 | 2015 | 2014-06-16 | B | 1 | 0.00063227 | 3.0544e-06
1 | 141193 | 2014-06-17 13:10 | 2014-06-17 13:47 | 37 | 121 | 4477 | 0.013675 | 0.00036959 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | No Power -Shutdown required to replace 1 X Insulator at pole P00410 Isolation Point ABS V27 & Links V28 Trevor pocock Attended | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 4114 | 0.012566 | 0.00036959 | 2014-06-17 | C | 0.012566 | 0.00036959 | 2015 | 2014-06-17 | C | 121 | 0.012566 | 0.00036959
1 | 141194 | 2014-06-17 13:40 | 2014-06-17 14:48 | 68 | 44 | 2992 | 0.0091388 | 0.00013439 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | No Power -Shutdown required to change 2X H/T Crossarms & 6 X H/T Insulators at Pole 797426 Isolation point ABS S562 no Back feed Adam whale Attended | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 2860 | 0.0087357 | 0.00013439 | 2014-06-17 | C | 0.0087357 | 0.00013439 | 2015 | 2014-06-17 | C | 44 | 0.0087357 | 0.00013439
1 | 141195 | 2014-06-17 09:10 | 2014-06-17 13:47 | 277 | 5 | 1385 | 0.0042304 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | UNKNOWN | SIN: 14/92990 - Asplundh requires the setion of line beyond fuses FP1327 isolated to allow removal of trees. Northpower staff member on site as AP holder. Isolation points: 11kV FP1327. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 277 | 274 | 1370 | 0.0041846 | 1.5272e-05 | 2014-06-17 | B | 0.0020923 | 7.636e-06 | 2015 | 2014-06-17 | B | 5 | 0.0041846 | 1.5272e-05
1 | 141196 | 2014-06-11 12:27 | 2014-06-11 15:56 | 209 | 69 | 14421 | 0.044048 | 0.00021076 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | 1/No Power 2/PKO CB 4 Tripped 3/ 4/ Trees in Lines Causing Damage to Pole And Crossarm 5/ Pole I12457 PKO6 and Pole I0707 PKO4 6/ PKO CB6, ABS IC695, ABS IC603, ABS IC735, Sw/Gear 9644/2(MOV4) 7/ ? 8/ Cross arm etc 9/ Work Complete 1 | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 209 | 206 | 14214 | 0.043416 | 0.00021076 | 2014-06-11 | C | 0.043416 | 0.00021075 | 2015 | 2014-06-11 | C | 69 | 0.043416 | 0.00021076
1 | 141198 | 2014-06-11 05:56 | 2014-06-11 22:22 | 986 | 142 | 140012 | 0.42766 | 0.00043373 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | POLE | 1/No Power 2/Recloser 9561/2 3/L/O 4/Broken Pole & Lines Down 5/ Pole I13488 6/Links9561/6 7/No Feedbacks 8/Pole & Conductor 9/Works Complete 10/No NDR 11/John Goodyear & Chris Browne Attended | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 986 | 983 | 139586 | 0.42635 | 0.00043373 | 2014-06-11 | C | 0.42635 | 0.00043373 | 2015 | 2014-06-11 | C | 142 | 0.42635 | 0.00043373
1 | 141199 | 2014-06-12 13:09 | 2014-06-12 14:57 | 108 | 7 | 756 | 0.0023091 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Emergency Isoaltion required beyond Fuses FP1511 to reapir floating coinductor and lines in trees. Adverse Weather/Extreme Wind. No NDR - Trees Outside Notice Zone. Ken Langman attended. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 108 | 105 | 735 | 0.002245 | 2.1381e-05 | 2014-06-12 | C | 0.002245 | 2.1381e-05 | 2015 | 2014-06-12 | C | 7 | 0.002245 | 2.1381e-05
1 | 141200 | 2014-06-11 08:34 | 2014-06-11 09:10 | 36 | 47 | 1692 | 0.0051681 | 0.00014356 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/No Power 2/ No Trip 3/ 4/ Mechanical Damage 5/Pole F12851 6/ABS IC784 7/No Backfeed 8/Cable Crimp 9/Work Complete 10/No NDR 11/Jim Cameron Attended | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 36 | 33 | 1551 | 0.0047374 | 0.00014356 | 2014-06-11 | C | 0.0047374 | 0.00014356 | 2015 | 2014-06-11 | C | 47 | 0.0047374 | 0.00014356
1 | 141201 | 2014-06-11 04:43 | 2014-06-13 12:35 | 3352 | 141 | 94706 | 0.28927 | 0.00043067 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. PONGAKAWA CB2. Recloser S6029 tripped. L/O. Adverse Weather/Extreme Wind. Lines patrolled and line found down due to high winds. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 671.6738 | 668.6738 | 94283 | 0.28798 | 0.00043067 | 2014-06-11 | C | 0.28798 | 0.00043067 | 2015 | 2014-06-11 | C | 141 | 0.28798 | 0.00043067
1 | 141203 | 2014-06-10 21:52 | 2014-06-11 00:16 | 144 | 282 | 28967 | 0.088477 | 0.00086135 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | 1/No Power 2/Recloser RC01 3/L/O 4/Trees in Lines 5/PoleF0920 6/ABS IC1296, ABS IC754 7/ No Backfeed 8/ 9/Work Complete 10/No NDR 11/Iro Ezekhiel & Chris Browne Attended | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 102.7199 | 99.7199 | 28121 | 0.085893 | 0.00086135 | 2014-06-10 | C | 0.085893 | 0.00086135 | 2015 | 2014-06-10 | C | 282 | 0.085893 | 0.00086135
1 | 141204 | 2014-06-11 03:11 | 2014-06-11 14:40 | 689 | 245 | 157981 | 0.48254 | 0.00074833 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS | CONDUCTOR | 1/No Power Branch Across Lines At Pole U12690 Caused Recloser 9643 to Trip.Isolated at ABS314 then ABS IC328 & Sectionaliser 9787. No Backfeed No NDR Don Watson Attended | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 644.8204 | 641.8204 | 157246 | 0.4803 | 0.00074833 | 2014-06-11 | C | 0.4803 | 0.00074833 | 2015 | 2014-06-11 | C | 245 | 0.4803 | 0.00074833
1 | 141206 | 2014-06-11 16:12 | 2014-06-11 16:29 | 17 | 3 | 51 | 0.00015578 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Defective Component - Tauranga CB17. Trees through line at Transformer TF3-024. TLB at Pole 217021. Fuses SF3-003 opened and tagged. Repairs made and fuses closed. Steve Doran attended. | F2/F4 | MALEME ST | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 42 | 0.00012829 | 9.1633e-06 | 2014-06-11 | C | 0.00012829 | 9.163e-06 | 2015 | 2014-06-11 | C | 3 | 0.00012829 | 9.1633e-06
1 | 141207 | 2014-06-11 14:47 | 2014-06-11 18:00 | 193 | 594 | 101886 | 0.3112 | 0.0018143 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | No Power. Omorkoroa CB2 tripped E/F. Adverse Weather/Extreme Wind. Line Patrolled and no fault found. Andy Wreaks Attended. | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 171.5253 | 168.5253 | 100104 | 0.30576 | 0.0018143 | 2014-06-11 | C | 0.30576 | 0.0018143 | 2015 | 2014-06-11 | C | 594 | 0.30576 | 0.0018143
1 | 141208 | 2014-06-17 09:35 | 2014-06-17 15:58 | 383 | 1 | 383 | 0.0011698 | 3.0544e-06 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Trees in lines beyond Fuses FC4194. Isolation at Fuses FC4194 ( spur no back feeds ). Asplundh remove trees, Tenex repair conductor at pole 13668 all service restored, Dion Saunders attended. Materials - 2 x h/v sleeves, 2 x bi metals, 2 x dead en | F3 | BEACH RD WAIHI BEACH | WAIHI BEACH SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 383 | 380 | 380 | 0.0011607 | 3.0544e-06 | 2014-06-17 | C | 0.0011607 | 3.054e-06 | 2015 | 2014-06-17 | C | 1 | 0.0011607 | 3.0544e-06
1 | 141209 | 2014-06-17 09:15 | 2014-06-17 16:30 | 435 | 22 | 9570 | 0.029231 | 6.7197e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/92991 - Install new poles and conductor. Remove TEMP FUSE 38. Isolation points: F892, S581 AP Handed back at 15:19 Waited until 16:24 For Tenix to be on site to do Switching | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 435 | 432 | 9504 | 0.029029 | 6.7197e-05 | 2014-06-17 | B | 0.014515 | 3.3599e-05 | 2015 | 2014-06-17 | B | 22 | 0.029029 | 6.7197e-05
1 | 141210 | 2014-06-17 16:45 | 2014-06-17 17:07 | 22 | 3 | 66 | 0.00020159 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | BINDER | Defective Component - Found binder broken at pole 702236. Isolated at fuses 8485. Replaced binder & re livened | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 57 | 0.0001741 | 9.1633e-06 | 2014-06-17 | C | 0.0001741 | 9.163e-06 | 2015 | 2014-06-17 | C | 3 | 0.0001741 | 9.1633e-06
1 | 141211 | 2014-06-11 05:26 | 2014-06-11 10:37 | 311 | 420 | 130620 | 0.39897 | 0.0012829 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | 1/No Power 2/ CB 2 Tripped 3/ L/O 4/ Trees in Lines 5/Transformer TC1446 6/Isolation ABS 541 7/TAH CB3 being backfeed via ABS 541 for Sub Upgrade. 8/ 9/Works Complete 10/No NDR 11/Marty Keenan & Dave McKee Attended | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 311 | 308 | 129360 | 0.39512 | 0.0012829 | 2014-06-11 | C | 0.39512 | 0.0012829 | 2015 | 2014-06-11 | C | 420 | 0.39512 | 0.0012829
1 | 141212 | 2014-06-12 11:20 | 2014-06-12 12:05 | 45 | 2 | 90 | 0.0002749 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | 1/No Power 2/No Tripping 3/ 4/Floating Conductor 5/ Pole K2416 6/isolated at Fuses FC2260 7/No Backfeed 8/Binders 9/ Work Complete 10/ No NDR 11/Dave McKee Attended | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 84 | 0.00025657 | 6.1088e-06 | 2014-06-12 | C | 0.00025657 | 6.109e-06 | 2015 | 2014-06-12 | C | 2 | 0.00025657 | 6.1088e-06
1 | 141214 | 2014-06-11 00:21 | 2014-06-11 14:29 | 848 | 157 | 132729 | 0.40541 | 0.00047954 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | POLE | 1/No Power 2/TAH CB 2 3/L/O 4/Floating Pole 5/Pole K2142 6/Isolated at ABS IC1222, Fuses FP643, ABS 9122, ABS 837. 7/TAH CB3 back Feed from TAH CB1 via ABS IC122. Fault In TAH CB3 Feeder. 8/ 9/Work Complete 10/No NDR 11/Marty Keenan | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 845.4076 | 842.4076 | 132258 | 0.40397 | 0.00047954 | 2014-06-11 | C | 0.40397 | 0.00047955 | 2015 | 2014-06-11 | C | 157 | 0.40397 | 0.00047954
1 | 141216 | 2014-06-11 12:22 | 2014-06-11 12:40 | 18 | 7 | 126 | 0.00038486 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Remove Branches From Lines Near Transformer TC6152. Transformer isolated use Transformer Fuses. No Backfeeds. No NDR. Dave McKee attended | F4 | HOE-PATETONGA | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 18 | 15 | 105 | 0.00032071 | 2.1381e-05 | 2014-06-11 | C | 0.00032071 | 2.1381e-05 | 2015 | 2014-06-11 | C | 7 | 0.00032071 | 2.1381e-05
1 | 141217 | 2014-06-11 12:00 | 2014-06-11 16:33 | 273 | 275 | 29171 | 0.089101 | 0.00083997 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | / No Power Sectionaliser 9208 Tripped.Isolations used Fuses FP1534, ABS Ip558 ABS SF3-005. Works Completed. No Back Feeds. No NDR. No Fault Found.Suspect tree Contact. Wayne Neutroski Attended | F2/F4 | MALEME ST | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 106.0764 | 103.0764 | 28346 | 0.086581 | 0.00083997 | 2014-06-11 | C | 0.086581 | 0.00083997 | 2015 | 2014-06-11 | C | 275 | 0.086581 | 0.00083997
1 | 141219 | 2014-06-11 07:11 | 2014-06-11 10:23 | 192 | 50 | 7686 | 0.023476 | 0.00015272 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | Initially Recloser C217 Auto Reclosed, Then Sectionaliser C218/2 Tripped. Isolations at ABS S149. Line Patrolled. No Fault Found. No Backfeed. No NDR.Work Complete. No Record of Attending Fault Man | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 153.72 | 150.72 | 7536 | 0.023018 | 0.00015272 | 2014-06-11 | C | 0.023018 | 0.00015272 | 2015 | 2014-06-11 | C | 50 | 0.023018 | 0.00015272
1 | 141223 | 2014-06-12 08:00 | 2014-06-12 15:13 | 433 | 4 | 1732 | 0.0052903 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Tripping. Tree Through Lines Causing Damage to O/H Lines ap Pole 229377. Binders Uses. No NDR. No Backfeed. Works Complete. Hayden Bedgood Attended | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 433 | 430 | 1720 | 0.0052536 | 1.2218e-05 | 2014-06-12 | C | 0.0052536 | 1.2218e-05 | 2015 | 2014-06-12 | C | 4 | 0.0052536 | 1.2218e-05
1 | 141236 | 2014-06-18 10:04 | 2014-06-18 11:02 | 58 | 1 | 58 | 0.00017716 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | MAINTENANCE | STAY WIRE | SIN: 14/93363 - Replace 11kV HV stay wire as its flapping around in the breeze at pole 726942. Isolation points: Fuse links LI721 | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 58 | 55 | 55 | 0.00016799 | 3.0544e-06 | 2014-06-18 | B | 8.3997e-05 | 1.527e-06 | 2015 | 2014-06-18 | B | 1 | 0.00016799 | 3.0544e-06
1 | 141237 | 2014-06-18 05:01 | 2014-06-18 06:48 | 107 | 927 | 96003 | 0.29323 | 0.0028315 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | CB 4 Tripped. Feeder was sectionalised but no Fault found. Isolation points include ABS SE6-111, Sectionaliser 9689 and Recloser S6031. No Backfeeds. No NDR. Denis Ngatai Attended | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 103.5631 | 100.5631 | 93222 | 0.28474 | 0.0028315 | 2014-06-18 | C | 0.28474 | 0.0028315 | 2015 | 2014-06-18 | C | 927 | 0.28474 | 0.0028315
1 | 141239 | 2014-06-11 03:33 | 2014-06-11 05:37 | 124 | 803 | 99572 | 0.30414 | 0.0024527 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Waihi Rd CB2. Auto reclosed - L/O. Adverse Weather/Extreme Wind. Line patrolled - branch on line knocked off. Ted Glasgow attended. Tree oustide notice zone - no NDR. Pole number not recorded on fault record. | F2 | KOROMIKO ST | WAIHI ROAD SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 124 | 121 | 97163 | 0.29678 | 0.0024527 | 2014-06-11 | C | 0.29678 | 0.0024527 | 2015 | 2014-06-11 | C | 803 | 0.29678 | 0.0024527
1 | 141240 | 2014-06-12 14:54 | 2014-06-12 16:20 | 86 | 1151 | 67009 | 0.20467 | 0.0035156 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | No Power. ThamesCB4. Adverse Weather/Extreme Wind. Line patrolled - jumpers found off on poles T12857 and T12834. | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 58.2181 | 55.2181 | 63556 | 0.19413 | 0.0035156 | 2014-06-12 | C | 0.19413 | 0.0035156 | 2015 | 2014-06-12 | C | 1151 | 0.19413 | 0.0035156
1 | 141241 | 2014-06-11 15:16 | 2014-06-11 17:12 | 116 | 63 | 5608 | 0.017129 | 0.00019243 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | FUSE | No Power. CB8 Linton. Adverse Weather/Extreme Wind. Line patrolled and broken dropout fuse located. Replace 3 sets of dropouts (materials = 3 x dropout fuses complete with 10Amp links). W Kaipuke attended. NOTE: It was noticed that fuse at H128 was arci | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 89.0159 | 86.0159 | 5419 | 0.016552 | 0.00019243 | 2014-06-11 | C | 0.016552 | 0.00019243 | 2015 | 2014-06-11 | C | 63 | 0.016552 | 0.00019243
1 | 141242 | 2014-06-11 05:01 | 2014-06-11 17:50 | 769 | 19 | 3833 | 0.011708 | 5.8034e-05 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | POLE | TPV CB 6 Tripped. Pole 220969 Damaged and Jumpers at ABS SE6-112 Blown. Isolations include TPV CB 6, ABS SE5-193, ABS SE6-1134, and SE6-2631. Feeder backfeed from TPV8 via ABS SE6-231. Works completed by T J Tanoa, Denis Ngatai, Mike Strange, and John Dee | F1 | RANGIURU | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 201.7368 | 198.7368 | 3776 | 0.011534 | 5.8034e-05 | 2014-06-11 | C | 0.011534 | 5.8034e-05 | 2015 | 2014-06-11 | C | 19 | 0.011534 | 5.8034e-05
1 | 141243 | 2014-06-10 20:32 | 2014-06-10 22:07 | 95 | 301 | 25213 | 0.077011 | 0.00091938 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Waharoa CB1. Adverse Weather/Extreme Wind. Line patrolled. Comms lost during patrol - lines locate down at pole 264218 (156 Maiseys Road). Jason Deans/Chris Brown attended. | F3 | MOWBRAY RD | WAHAROA SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 83.7641 | 80.7641 | 24310 | 0.074253 | 0.00091938 | 2014-06-10 | C | 0.074253 | 0.00091938 | 2015 | 2014-06-10 | C | 301 | 0.074253 | 0.00091938
1 | 141245 | 2014-06-17 15:40 | 2014-06-19 14:00 | 2780 | 1 | 475 | 0.0014509 | 3.0544e-06 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE TERMINATION | Defective Component - Found all fuses blown at FC2193. Isolated & tested cable. Found cable needs replacing. Customer advised. Affects a shed which is not used. On investigation it was found that this was a faulty pothead which was replaced on the 19.06.1 | F4/F5 | MOUNTAIN | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 475 | 472 | 472 | 0.0014417 | 3.0544e-06 | 2014-06-17 | C | 0.0014417 | 3.054e-06 | 2015 | 2014-06-17 | C | 1 | 0.0014417 | 3.0544e-06
1 | 141246 | 2014-06-18 09:00 | 2014-06-18 13:35 | 275 | 2 | 550 | 0.0016799 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93123 - Replace TX T3/55, remove 1 pole of 2 pole TX structure, install new TX on remaining pole. Isolation points: M58 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 275 | 272 | 544 | 0.0016616 | 6.1088e-06 | 2014-06-18 | B | 0.0008308 | 3.054e-06 | 2015 | 2014-06-18 | B | 2 | 0.0016616 | 6.1088e-06
1 | 141247 | 2014-06-11 15:20 | 2014-06-13 15:20 | 2880 | 224 | 9077 | 0.027725 | 0.00068419 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE HOLDER | No Power at Transformer TC5095. One fuse and DDO Replaced by Nick Hayland. Isolated at ABS IC277, ABS 221, abd ABS IC202. Backfeeds from WHI 3 via Switch 9714 and from WHI 6 Via ABS 271. No NDR. Work Complete. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 40.5223 | 37.5223 | 8405 | 0.025672 | 0.00068419 | 2014-06-11 | C | 0.025672 | 0.00068419 | 2015 | 2014-06-11 | C | 224 | 0.025672 | 0.00068419
1 | 141248 | 2014-06-18 10:14 | 2014-06-18 13:10 | 176 | 24 | 4224 | 0.012902 | 7.3306e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93210 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Replace 11kV Transformer TC1483 and LV X-arm. Isolation points: 11kV transformer fuses TC1483 | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 176 | 173 | 4152 | 0.012682 | 7.3306e-05 | 2014-06-18 | B | 0.006341 | 3.6653e-05 | 2015 | 2014-06-18 | B | 24 | 0.012682 | 7.3306e-05
1 | 141249 | 2014-06-18 13:00 | 2014-06-18 13:37 | 37 | 291 | 10767 | 0.032887 | 0.00088884 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | SWITCHGEAR - OH | WA: 14/92694 - LTOS 11kV oil switches 8666/1, 8666/2, 8666/3. Isolation points: 11kV ABS 341, ABS 531, Fuse 6602. Obtain live tank oil sample in accordance with standard 393S084 at 11kV Sw/gear 8666/1, 8666/2.8666/3. | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 9894 | 0.03022 | 0.00088884 | 2014-06-18 | B | 0.01511 | 0.00044442 | 2015 | 2014-06-18 | B | 291 | 0.03022 | 0.00088884
1 | 141250 | 2014-06-18 09:30 | 2014-06-18 13:25 | 235 | 2 | 470 | 0.0014356 | 6.1088e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | MAINTENANCE | DISTRIBUTION TRANSFORMER | SIN: 14/92994 - Isolate 11kV Transformer TE6-178 to clean out and close rabbit burrow. Isolation points: 11kV Fuses SE6-097 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 235 | 232 | 464 | 0.0014173 | 6.1088e-06 | 2014-06-18 | B | 0.00070863 | 3.054e-06 | 2015 | 2014-06-18 | B | 2 | 0.0014173 | 6.1088e-06
1 | 141252 | 2014-06-11 16:57 | 2014-06-11 19:46 | 169 | 272 | 45968 | 0.14041 | 0.0008308 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | No Power. Whitianga CB3. Recloser 9632 auto reclosed - No flags. Adverse Weather/Extreme Wind. Line patrolled and located lines down at pole W13817. Shane Walker attended. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 169 | 166 | 45152 | 0.13791 | 0.0008308 | 2014-06-11 | C | 0.13791 | 0.0008308 | 2015 | 2014-06-11 | C | 272 | 0.13791 | 0.0008308
1 | 141253 | 2014-06-11 17:14 | 2014-06-11 18:41 | 87 | 1303 | 113361 | 0.34625 | 0.0039799 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | No Power. Whitianga CB5. Adverse Weather/Extreme Wind. Line patrolled and floater repaired ar pole W12926. Ben Edwards attended. | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 87 | 84 | 109452 | 0.33431 | 0.0039799 | 2014-06-11 | C | 0.33431 | 0.0039799 | 2015 | 2014-06-11 | C | 1303 | 0.33431 | 0.0039799
1 | 141254 | 2014-06-11 03:34 | 2014-06-11 09:20 | 346 | 1311 | 452754 | 1.3829 | 0.0040043 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | WBH CB 5 and Recloser 9225/2 tripped during Storm. No Fault Found. Suspect line Clash During Storm. No NDR. Ne Gear used. No Liney.Works Complete. | F3 | ATHENREE | WAIHI BEACH SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 345.3501 | 342.3501 | 448821 | 1.3709 | 0.0040043 | 2014-06-11 | C | 1.3709 | 0.0040043 | 2015 | 2014-06-11 | C | 1311 | 1.3709 | 0.0040043
1 | 141255 | 2014-06-11 03:43 | 2014-06-11 06:36 | 173 | 607 | 104927 | 0.32049 | 0.001854 | No Power | 33000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | /No Power 2/33kV CB 402, CB 60 3/ L/O 4/33kV Line Down 5/WHU GXP CB 402 33kV Lines Down 6/33kV Isolated at ABS3253, ABS 3118 and CB 402. 11kV isolations at TTU CB 17, FRM CB 17 & 19. 7/ Back feed to TTU from PKO3 via ABS IC2116. 8/ 33kV Li | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 172.8616 | 169.8616 | 103106 | 0.31493 | 0.001854 | 2014-06-11 | C | 0.31493 | 0.001854 | 2015 | 2014-06-11 | C | 607 | 0.31493 | 0.001854
1 | 141257 | 2014-06-11 03:59 | 2014-06-12 10:45 | 1846 | 153 | 143549 | 0.43846 | 0.00046733 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Waihi CB1. Adverse Weather/Extreme Wind. Line aptrolled and tree located on lines at ABS IC243. No NDR tree outside notice zone. Dion Saunders and Morgan Wells attended. | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 938.2288 | 935.2288 | 143090 | 0.43706 | 0.00046733 | 2014-06-11 | C | 0.43706 | 0.00046733 | 2015 | 2014-06-11 | C | 153 | 0.43706 | 0.00046733
1 | 141258 | 2014-06-18 13:13 | 2014-06-18 13:56 | 43 | 260 | 11180 | 0.034148 | 0.00079415 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - at 13:03, Tauranga GXP, CB 11 Kaimai Drive Feeder, Recloser 9566, Tripped, E/F, Auto Reclosed. At 13:30 Recloser 9566 Tripped, E/F, L/O. Faultman Dispatched & Investigation Began. Feeder Sectionalised. Found Small Tree branch on line at Pole 21220 | F4 | KAIMAI DRIVE | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 10400 | 0.031766 | 0.00079415 | 2014-06-18 | C | 0.031766 | 0.00079415 | 2015 | 2014-06-18 | C | 260 | 0.031766 | 0.00079415
1 | 141260 | 2014-06-11 03:56 | 2014-06-11 12:24 | 508 | 614 | 306749 | 0.93694 | 0.0018754 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | SURGE ARRESTOR | 1/No Power 2/ WGM CB1 Tripped 3/ E/F 4/Trees in line 5/ 6/Isolations ABS IC251, ABS IC424, Sectionaliser 9712/2, Sw/Gear IC2070 7/ Back feed from WHI 1 via 9712/2 8/- 9/Works Complete 10/No NDR 11/ Wayne Seath | F4 | WHIRITOA | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 499.5912 | 496.5912 | 304907 | 0.93132 | 0.0018754 | 2014-06-11 | C | 0.93132 | 0.0018754 | 2015 | 2014-06-11 | C | 614 | 0.93132 | 0.0018754
1 | 141261 | 2014-06-18 10:01 | 2014-06-18 15:48 | 347 | 5 | 1735 | 0.0052994 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91779 - Replace conductor between 11kV Pole M0044 TEMP ABS TEMP73 and 11kV ABS 957. Isolation points: 11KV ABS 957 & TEMP ABS73. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 347 | 344 | 1720 | 0.0052536 | 1.5272e-05 | 2014-06-18 | B | 0.0026268 | 7.636e-06 | 2015 | 2014-06-18 | B | 5 | 0.0052536 | 1.5272e-05
1 | 141263 | 2014-06-11 02:31 | 2014-06-11 21:25 | 1134 | 1208 | 1019649 | 3.1144 | 0.0036897 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | / No Power 2/ Recloser RC28 Then WGM CB 3 3/ 4 Trees in Lines Damaging Conductors 5/ Pole R0847 6/Isolations atABS 287, RC28, Sw/gear 9637/2, ABS IP487, Sw/Gear IC1488, And CB 3 7/Back feeds from WGM 11 Via Recloser 9514/2 8/ Cable Crimp | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 844.0803 | 841.0803 | 1016025 | 3.1034 | 0.0036897 | 2014-06-11 | C | 3.1034 | 0.0036897 | 2015 | 2014-06-11 | C | 1208 | 3.1034 | 0.0036897
1 | 141266 | 2014-06-13 14:37 | 2014-06-13 15:44 | 67 | 234 | 3846 | 0.011747 | 0.00071474 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | POLE | 1/No Power 2/No Tripping 3/ No Flags 4/ Damaged pole 5/ but no pole I.D 6/Isolations at Line Breaks at Pole W1829 and Pole W13359, ABS IC2589, ABS IC216, Sectionaliser 9721/1and ABS 9721/2 7/Backfeed from WHT5 via Recloser 9278 8/ Pole? | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 16.4359 | 13.4359 | 3144 | 0.0096031 | 0.00071474 | 2014-06-13 | C | 0.0096031 | 0.00071473 | 2015 | 2014-06-13 | C | 234 | 0.0096031 | 0.00071474
1 | 141267 | 2014-06-13 08:26 | 2014-06-13 09:00 | 34 | 267 | 9078 | 0.027728 | 0.00081553 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | 1/No Power 2/no trip 3/no Flags 4/Broken Jumper to Transformer 5/Transformer TC3907 6/Isolated at ABS 476 and Line Break 7/No Backfeeds 8/Cable joiner 9/Works Complete 10/No NDR 11/Steve Johnson Attended | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 8277 | 0.025281 | 0.00081553 | 2014-06-13 | C | 0.025281 | 0.00081553 | 2015 | 2014-06-13 | C | 267 | 0.025281 | 0.00081553
1 | 141270 | 2014-06-11 02:52 | 2014-06-11 18:28 | 936 | 432 | 399557 | 1.2204 | 0.0013195 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/ No Power 2/AutorecloserRC15 Tripped Isolations at ABS326 abs 344. No Backfeeds. No NDR. No Fault Found. Andrew King Attended | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 924.9005 | 921.9005 | 398261 | 1.2165 | 0.0013195 | 2014-06-11 | C | 1.2165 | 0.0013195 | 2015 | 2014-06-11 | C | 432 | 1.2165 | 0.0013195
1 | 141271 | 2014-06-11 03:16 | 2014-06-11 03:40 | 24 | 1039 | 24936 | 0.076165 | 0.0031735 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | CONDUCTOR | 1/ No Power WHT CB 3 Tripped. This CB did not close before the main Coromandel outage of 141322 and 141103 commenced at 0340. This outage is only for the time between. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 24 | 21 | 21819 | 0.066644 | 0.0031735 | 2014-06-11 | C | 0.066644 | 0.0031735 | 2015 | 2014-06-11 | C | 1039 | 0.066644 | 0.0031735
1 | 141272 | 2014-06-11 23:52 | 2014-06-12 01:07 | 75 | 272 | 20400 | 0.06231 | 0.0008308 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | RAIN | JUMPER | No Power Blown Jumper on Regulator TC6232 Repaired by Andrew King. Isolations at Sectionaliser 9632/2. No Backfeed. No NDR. Work Complete. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 75 | 72 | 19584 | 0.059818 | 0.0008308 | 2014-06-11 | C | 0.059818 | 0.0008308 | 2015 | 2014-06-11 | C | 272 | 0.059818 | 0.0008308
1 | 141274 | 2014-06-19 11:00 | 2014-06-19 13:05 | 125 | 4 | 500 | 0.0015272 | 1.2218e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CUSTOMER REQUEST | DISTRIBUTION TRANSFORMER | SIN: 14/93303 - Upgrade the existing 11kV 30kVA TX to a 50kVA TX. Isolation points: 11kV Transformer Fuses TC2703. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. | F4 | MAUNGAKAWA RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 125 | 122 | 488 | 0.0014906 | 1.2218e-05 | 2014-06-19 | B | 0.00074528 | 6.109e-06 | 2015 | 2014-06-19 | B | 4 | 0.0014906 | 1.2218e-05
1 | 141275 | 2014-06-13 09:15 | 2014-06-13 13:30 | 255 | 4 | 1020 | 0.0031155 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93510 - To replace LV termination arm under shut down conditions. Isolation point: 11kV Fuses at Transformer TC245. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. (old switching number 14/93455) | F4 | KEREONE | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 255 | 252 | 1008 | 0.0030789 | 1.2218e-05 | 2014-06-13 | B | 0.0015394 | 6.109e-06 | 2015 | 2014-06-13 | B | 4 | 0.0030789 | 1.2218e-05
1 | 141276 | 2014-06-19 10:06 | 2014-06-19 14:20 | 254 | 8 | 2032 | 0.0062066 | 2.4435e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93314 - Change 11kV X-arms at various sites past Fuses FP1354. Isolation points: 11kV Fuses FP1354. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 254 | 251 | 2008 | 0.0061333 | 2.4435e-05 | 2014-06-19 | B | 0.0030666 | 1.2218e-05 | 2015 | 2014-06-19 | B | 8 | 0.0061333 | 2.4435e-05
1 | 141277 | 2014-06-17 09:20 | 2014-06-17 15:04 | 344 | 5 | 1720 | 0.0052536 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/93526 - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Lift 11kV Transformer TC3406 and replace 400V pole P1517. Isolation points: 11kV transformer fuses TC3406 | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 1705 | 0.0052078 | 1.5272e-05 | 2014-06-17 | B | 0.0026039 | 7.636e-06 | 2015 | 2014-06-17 | B | 5 | 0.0052078 | 1.5272e-05
1 | 141278 | 2014-06-19 09:40 | 2014-06-19 14:30 | 290 | 7 | 2030 | 0.0062005 | 2.1381e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/92455 - Change existing 11kV Transformer plus replace LV Xarms plus upgrade earths on 11kV Transformer 1081. Isolation points: 11kV Transformer Fuse 1081. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 290 | 287 | 2009 | 0.0061363 | 2.1381e-05 | 2014-06-19 | B | 0.0030682 | 1.069e-05 | 2015 | 2014-06-19 | B | 7 | 0.0061363 | 2.1381e-05
1 | 141279 | 2014-06-19 08:15 | 2014-06-19 11:59 | 224 | 257 | 7144 | 0.021821 | 0.00078499 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93376 - Replace defective TX T2762. Isolation points: C1005 | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 27.7977 | 24.7977 | 6373 | 0.019466 | 0.00078499 | 2014-06-19 | B | 0.0097329 | 0.00039249 | 2015 | 2014-06-19 | B | 257 | 0.019466 | 0.00078499
1 | 141280 | 2014-06-19 09:05 | 2014-06-19 12:20 | 195 | 26 | 5070 | 0.015486 | 7.9415e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | RECLOSER | SIN: 14/92995 - Erect new pole and terminate line, install and liven new links on the 787642 side of the new pole for new entec sectionalizer 4705 also VT 4840W, do SCADA checks and liven. Isolation points: ABS 137, ABS 008, ABS 655 | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 4992 | 0.015248 | 7.9415e-05 | 2014-06-19 | B | 0.0076238 | 3.9708e-05 | 2015 | 2014-06-19 | B | 26 | 0.015248 | 7.9415e-05
1 | 141281 | 2014-06-19 11:35 | 2014-06-19 12:45 | 70 | 2 | 140 | 0.00042762 | 6.1088e-06 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component -Faultman investigating fault found crossarm had come detached from pole causing it to twist around. Work area isolated via Fuses F34 and crossarm repaired. Relivened ok. Materials used: 2x 16mm nuts and a 16mm washer. Attended by Jeff | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 134 | 0.00040929 | 6.1088e-06 | 2014-06-19 | C | 0.00040929 | 6.109e-06 | 2015 | 2014-06-19 | C | 2 | 0.00040929 | 6.1088e-06
1 | 141282 | 2014-06-19 16:53 | 2014-06-19 18:41 | 108 | 179 | 16244 | 0.049616 | 0.00054674 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power -Recloser C279/2 Found open Patrolled Nothing Found No rain or wind Suspect bird Strike Ben Taylor Attended | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 90.7486 | 87.7486 | 15707 | 0.047976 | 0.00054674 | 2014-06-19 | C | 0.047976 | 0.00054674 | 2015 | 2014-06-19 | C | 179 | 0.047976 | 0.00054674
1 | 141283 | 2014-06-19 19:22 | 2014-06-19 19:45 | 23 | 1831 | 42113 | 0.12863 | 0.0055926 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | CONDUCTOR | No Power -CB 14 Tripped E/F IDMT Patrolled Found High load Had hit L/V which had gone up and hit H/T removed L/V Line and reliven Les Robinson Attended NDR 37463 189 Pioneer Highway transformer T6/250 | F3 | PIONEER | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 23 | 20 | 36620 | 0.11185 | 0.0055926 | 2014-06-19 | C | 0.11185 | 0.0055927 | 2015 | 2014-06-19 | C | 1831 | 0.11185 | 0.0055926
1 | 141284 | 2014-06-19 23:43 | 2014-06-20 00:40 | 57 | 76 | 4332 | 0.013232 | 0.00023214 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - Emergency switching to repair blown jumper at pole 214516 fuses supplying transformer TC5 008. Jumper repaired all service restored, Wayne Neustroski attended. Materials Nil | F2 | BAYFAIR | OMANU SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 57 | 54 | 4104 | 0.012535 | 0.00023214 | 2014-06-19 | C | 0.012535 | 0.00023214 | 2015 | 2014-06-19 | C | 76 | 0.012535 | 0.00023214
1 | 141285 | 2014-06-19 22:03 | 2014-06-20 00:31 | 148 | 289 | 25941 | 0.079235 | 0.00088273 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT TREE CONTACT | UNKNOWN | Unknown Cause - possibly trees. Recloser 9606 tripped E/F L/O. ( strong winds ) Feeder sectionalised & fault narrowed down to beyond ABS SB1 041 with back feed via Sectionaliser 9223. Feeder patrolled beyond ABS SB1 041 with no fault found ( wind had died | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 89.7612 | 86.7612 | 25074 | 0.076587 | 0.00088273 | 2014-06-19 | C | 0.076587 | 0.00088273 | 2015 | 2014-06-19 | C | 289 | 0.076587 | 0.00088273
1 | 141286 | 2014-06-20 03:09 | 2014-06-20 08:51 | 342 | 171 | 37124 | 0.11339 | 0.00052231 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - Tripping on Recloser CB 9320. Patrol found broken Cross arm on Mataku Rd.with Isolation from ABS IC2565 to end. Repaired, relivened OK. Required new crossarm and insulators. It appears a faulty insulator had initially failed causing | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 217.0994 | 214.0994 | 36611 | 0.11183 | 0.00052231 | 2014-06-20 | C | 0.11183 | 0.00052231 | 2015 | 2014-06-20 | C | 171 | 0.11183 | 0.00052231
1 | 141287 | 2014-06-19 17:58 | 2014-06-20 14:50 | 1252 | 6 | 6318 | 0.019298 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Pongakawa CB3. Open and tag fuses SF7-024. Line break created at Pole 229154.Three transformers left off overnight but customers happy as they only feed pumps. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 1053 | 1050 | 6300 | 0.019243 | 1.8327e-05 | 2014-06-19 | C | 0.019243 | 1.8327e-05 | 2015 | 2014-06-19 | C | 6 | 0.019243 | 1.8327e-05
1 | 141288 | 2014-06-16 10:24 | 2014-06-16 12:00 | 96 | 4 | 384 | 0.0011729 | 1.2218e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Hau Nui C642. Fuses 7322 opened. Broken 11kV crossarm (2nd xarm rotten) on pole 811817. Materials 2 x 2.9m 11kV strain xarms, 4 x 11kV insulators. Attended by Adam Whale, Jason Hall | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 96 | 93 | 372 | 0.0011362 | 1.2218e-05 | 2014-06-16 | C | 0.0011362 | 1.2218e-05 | 2015 | 2014-06-16 | C | 4 | 0.0011362 | 1.2218e-05
1 | 141290 | 2014-06-13 14:19 | 2014-06-13 15:37 | 78 | 31 | 2418 | 0.0073856 | 9.4687e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | UNKNOWN | Defective Component - Bethlehem CB1. NOC closed Recloser 9805 and opened SD3-012 and SD3-112 to backfeed. Permit AP144518. David Joynt, Clint Johnston and Josh Reid attended. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 78 | 75 | 2325 | 0.0071015 | 9.4687e-05 | 2014-06-13 | C | 0.0071015 | 9.4687e-05 | 2015 | 2014-06-13 | C | 31 | 0.0071015 | 9.4687e-05
1 | 141291 | 2014-06-20 10:20 | 2014-06-20 14:30 | 250 | 6 | 1500 | 0.0045816 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/93200 - AP for Asplunch to climb and prune trees clear of lines, then fell. Isolation points: 11kV Fuses 12006 (pole 709456) | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 1482 | 0.0045267 | 1.8327e-05 | 2014-06-20 | B | 0.0022633 | 9.163e-06 | 2015 | 2014-06-20 | B | 6 | 0.0045267 | 1.8327e-05
1 | 141293 | 2014-06-20 09:55 | 2014-06-20 13:20 | 205 | 108 | 13762 | 0.042035 | 0.00032988 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | CONDUCTOR | Accident -RS M79 Trip, No flags (Non Scadarised). Call came in from a truck driver who had been unloading a digger which had contacted and brought down lines. Faultman dispatched to investigate who isolated work area at Fuses M71 and then reclosed RS M79. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 127.4259 | 124.4259 | 13438 | 0.041045 | 0.00032988 | 2014-06-20 | C | 0.041045 | 0.00032988 | 2015 | 2014-06-20 | C | 108 | 0.041045 | 0.00032988
1 | 141295 | 2014-06-20 09:05 | 2014-06-20 11:20 | 135 | 2 | 270 | 0.00082469 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93482 - NOT: Contact NOC prior to isolation and again on restoration of the HV own isoaltion and AP. Replace Transformer crossarms T1/124. Isolation Point: Transformer Fuses T1/124. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 264 | 0.00080637 | 6.1088e-06 | 2014-06-20 | B | 0.00040318 | 3.054e-06 | 2015 | 2014-06-20 | B | 2 | 0.00080637 | 6.1088e-06
1 | 141296 | 2014-06-20 17:05 | 2014-06-20 17:38 | 33 | 43 | 1419 | 0.0043342 | 0.00013134 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component -Faultman investigating fault found a burnt up jumper. Work area isolated at Fuses L43 and jumper was replaced. Materials used: 1 mtr of squirrel conductor and 1x Ampac sleeve. Attended by Bruce Mehrtens | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 33 | 30 | 1290 | 0.0039402 | 0.00013134 | 2014-06-20 | C | 0.0039402 | 0.00013134 | 2015 | 2014-06-20 | C | 43 | 0.0039402 | 0.00013134
1 | 141298 | 2014-06-20 09:30 | 2014-06-20 12:49 | 199 | 58 | 11542 | 0.035254 | 0.00017716 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93729 - URGENT Network Reliability. Replace 11kV X-arm and install new fuses at 11kV pole 205088 (TC1-022). Isolation points: 11kV Fuses SC2-134. | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 199 | 196 | 11368 | 0.034723 | 0.00017716 | 2014-06-20 | B | 0.017361 | 8.8578e-05 | 2015 | 2014-06-20 | B | 58 | 0.034723 | 0.00017716
1 | 141300 | 2014-06-20 18:09 | 2014-06-20 19:14 | 65 | 1083 | 37683 | 0.1151 | 0.0033079 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power -CB 22 tripped O/C A& C Phase. Patrolled Nothing Found. Shazil Khan & Bruce Merthens Attended | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 34.795 | 31.795 | 34434 | 0.10518 | 0.0033079 | 2014-06-20 | C | 0.10518 | 0.0033079 | 2015 | 2014-06-20 | C | 1083 | 0.10518 | 0.0033079
1 | 141301 | 2014-06-21 10:02 | 2014-06-21 11:07 | 65 | 3 | 195 | 0.00059561 | 9.1633e-06 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - Isolation to allow a tree that had blown over lines in the last storm event and had only just been found by customer when he shifted stock and needed water from his pump. Lines down at Pole 381351. Tree removed and Lines re hung. Hilton Gardener F | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 186 | 0.00056812 | 9.1633e-06 | 2014-06-21 | C | 0.00056812 | 9.163e-06 | 2015 | 2014-06-21 | C | 3 | 0.00056812 | 9.1633e-06
1 | 141302 | 2014-06-21 09:50 | 2014-06-21 11:44 | 114 | 95 | 6485 | 0.019808 | 0.00029017 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | BINDER | Defective Component -CB 4 tripped on no flags, line was sectionalised and patrolled and a floating wire was found at pole P28663, line was isolated at Fuses S38 to rebind the wire, Robin Smith attended. | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 68.2632 | 65.2632 | 6200 | 0.018937 | 0.00029017 | 2014-06-21 | C | 0.018937 | 0.00029017 | 2015 | 2014-06-21 | C | 95 | 0.018937 | 0.00029017
1 | 141303 | 2014-06-21 13:27 | 2014-06-21 19:19 | 352 | 111 | 39072 | 0.11934 | 0.00033904 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident -Car V Pole. Pole # 267370 Hit. Isolation Between Sw/gear IC3183, Sw/gear 2073 and ABS IC205. Back Feeds via RS 9714 and Sw/gear IC3178. Faultman Nick Hyland. NDR #17371. 1x Pole Replaced | F3 | GILMOUR ST | WAIHI SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 352 | 349 | 38739 | 0.11833 | 0.00033904 | 2014-06-21 | C | 0.11833 | 0.00033904 | 2015 | 2014-06-21 | C | 111 | 0.11833 | 0.00033904
1 | 141304 | 2014-06-21 15:47 | 2014-06-21 18:00 | 133 | 49 | 3039 | 0.0092824 | 0.00014967 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -CB C843 tripped, line was patrolled and faultman found a line down at pole 833961 due to a branch that had broken off in the wind and fell on the line, tree was out of notice zone. Ben Taylor attended. | F5 | ROROKOKO | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 62.0204 | 59.0204 | 2892 | 0.0088334 | 0.00014967 | 2014-06-21 | C | 0.0088334 | 0.00014967 | 2015 | 2014-06-21 | C | 49 | 0.0088334 | 0.00014967
1 | 141305 | 2014-06-22 08:22 | 2014-06-22 10:20 | 118 | 527 | 62186 | 0.18994 | 0.0016097 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird Recloser L34 tripped on B phase O/C and E/F flags, received a call from customer of line down, line was isolated at ABS's L33 and L36 to repair the line down between poles P33441 and P33450 due to duck strike. Anjay Prasad and Les Robinson | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 118 | 115 | 60605 | 0.18511 | 0.0016097 | 2014-06-22 | C | 0.18511 | 0.0016097 | 2015 | 2014-06-22 | C | 527 | 0.18511 | 0.0016097
1 | 141307 | 2014-06-21 21:44 | 2014-06-22 10:16 | 752 | 221 | 32015 | 0.097787 | 0.00067503 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees - Recloser R12 tripped on no flags, line was sectionalised and patrolled up to Fuses R19, patrol was stopped due to bad weather and feeder went cross country, faultman returned in morning and found lines down at pole P27544 due to trees that had com | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 144.8643 | 141.8643 | 31352 | 0.095762 | 0.00067503 | 2014-06-21 | C | 0.095762 | 0.00067503 | 2015 | 2014-06-21 | C | 221 | 0.095762 | 0.00067503
1 | 141309 | 2014-06-22 15:44 | 2014-06-22 17:06 | 82 | 144 | 11808 | 0.036067 | 0.00043984 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident - Initial Auto-reclose on CB1 on Phase B, C O/C and E/F. Cause due to Car accident on Corner Minden Rd/ SH2 with the LV flicking up into 11kV. Pole badly damaged with isolation between ABS SD3-002, SD3-003 and SD3-009 (backfeed at CB 9805). Pole | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 82 | 79 | 11376 | 0.034747 | 0.00043984 | 2014-06-22 | C | 0.034747 | 0.00043984 | 2015 | 2014-06-22 | C | 144 | 0.034747 | 0.00043984
1 | 141310 | 2014-06-23 00:15 | 2014-06-23 01:15 | 60 | 83 | 4980 | 0.015211 | 0.00025352 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | ISOLATION FOR SAFETY | SWITCHGEAR - UG | SIN: 14/93495 - STAGE 1:1- Switching to isolate Magnefix 568/1. 2-Replace canopy 879 (1hr). 3- after completion on 2, put isolation (magnefix 879/1) in place for Stage 2 work. Isolation points Switch 891/3, Magnefix 568/1. | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 4731 | 0.01445 | 0.00025352 | 2014-06-23 | B | 0.0072252 | 0.00012676 | 2015 | 2014-06-23 | B | 83 | 0.01445 | 0.00025352
1 | 141311 | 2014-06-22 20:19 | 2014-06-22 23:37 | 198 | 19 | 3762 | 0.011491 | 5.8034e-05 | No Power | 11000 | Unplanned | Underground Cable | DEFECTIVE EQUIPMENT | UG EQUIPMENT FAILURE | CABLE | Defective Component - Isolation of Transformer at HV Fuses on Pole H1380 to Test for suspected Cable Fault. Cable found to be faulty. Generator Fitted to LV to supply Customers. Faultman TJ Tanoa and John Goodyear. | F4 | PIAKOITI RD | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 198 | 195 | 3705 | 0.011317 | 5.8034e-05 | 2014-06-22 | C | 0.011317 | 5.8034e-05 | 2015 | 2014-06-22 | C | 19 | 0.011317 | 5.8034e-05
1 | 141312 | 2014-06-21 14:50 | 2014-06-21 16:20 | 90 | 6 | 540 | 0.0016494 | 1.8327e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component -. Isolation to repair broken Jumper left over from previous storm damage. Isolation at Fuses SF7-024. T J Tanoa Faultman. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 522 | 0.0015944 | 1.8327e-05 | 2014-06-21 | C | 0.0015944 | 1.8327e-05 | 2015 | 2014-06-21 | C | 6 | 0.0015944 | 1.8327e-05
1 | 141316 | 2014-06-12 09:15 | 2014-06-12 14:35 | 320 | 2 | 640 | 0.0019548 | 6.1088e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92996 - Rescheduled due to weather. Install new termination arms at poles F1990 and F1991 in preparation for new feeder extension. The 11kV line to Transformer TC2934 will need to be isolated while new arms are being installed. Also, works will b | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 320 | 317 | 634 | 0.0019365 | 6.1088e-06 | 2014-06-12 | B | 0.00096825 | 3.054e-06 | 2015 | 2014-06-12 | B | 2 | 0.0019365 | 6.1088e-06
1 | 141318 | 2014-06-23 19:04 | 2014-06-23 21:39 | 155 | 291 | 26181 | 0.079968 | 0.00088884 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | Unknown Cause -Recloser 6224/2 tripped on A phase O/C, faultman found line down between poles 764150 and 764151 after a call from a customer, line was isolated at ABS's 5128, 5192 and 5207 to repair the line. Mark Patterson and Blair Gregg attended.50 met | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 89.9691 | 86.9691 | 25308 | 0.077301 | 0.00088884 | 2014-06-23 | C | 0.077301 | 0.00088884 | 2015 | 2014-06-23 | C | 291 | 0.077301 | 0.00088884
1 | 141319 | 2014-06-23 20:09 | 2014-06-23 20:20 | 11 | 2049 | 21504 | 0.065682 | 0.0062585 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -33KV CB 1342 tripped on O/C flags, line was patrolled and sectionalised and no fault was found. Mark Patterson and Nick Patton attended.REF FR 141320 | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 10.4949 | 7.4949 | 15357 | 0.046907 | 0.0062585 | 2014-06-23 | C | 0.046907 | 0.0062585 | 2015 | 2014-06-23 | C | 2049 | 0.046907 | 0.0062585
1 | 141320 | 2014-06-23 20:09 | 2014-06-24 00:34 | 265 | 154 | 5410 | 0.016524 | 0.00047038 | No Power | 33000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -33KV CB 1342 tripped on O/C flags, line was patrolled and sectionalised and no fault was found. Mark Patterson and Nick Patton attended. REF FR 141319. | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 35.1299 | 32.1299 | 4948 | 0.015113 | 0.00047038 | 2014-06-23 | C | 0.015113 | 0.00047038 | 2015 | 2014-06-23 | C | 154 | 0.015113 | 0.00047038
1 | 141321 | 2014-06-23 19:36 | 2014-06-23 20:49 | 73 | 632 | 46136 | 0.14092 | 0.0019304 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component - Emergency isolation to replace a HV Fuse Holder to Transformer TC908 at Pole R12936. Wayne Seath Faultman. Isolation at ABS 2576. No Backfeeds available. | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 73 | 70 | 44240 | 0.13513 | 0.0019304 | 2014-06-23 | C | 0.13513 | 0.0019304 | 2015 | 2014-06-23 | C | 632 | 0.13513 | 0.0019304
1 | 141322 | 2014-06-11 03:40 | 2014-06-11 14:01 | 621 | 584 | 362664 | 1.1077 | 0.0017838 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees - CB 1092 tripped. Trees found through lines which damaged 5 crossarms. Service restored from TAI CB 60. Trees removed and cross arms replaced. Relivened OK. Tree(s) outside Notice Zone - No NDR. Outage followed on from FRN 141103, because of outdef | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 621 | 618 | 360912 | 1.1024 | 0.0017838 | 2014-06-11 | C | 1.1024 | 0.0017838 | 2015 | 2014-06-11 | C | 584 | 1.1024 | 0.0017838
1 | 141325 | 2014-06-24 09:55 | 2014-06-24 14:50 | 295 | 26 | 7670 | 0.023427 | 7.9415e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93108 - Replace existing 100kVA TX, with 100kVA refurbished unitised TX, at pole 221979. Replace existing (LV) isolating fuses w/ 3x 160A fuse holders and links. Isolation points: 11kV fuses FP1605 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 295 | 292 | 7592 | 0.023189 | 7.9415e-05 | 2014-06-24 | B | 0.011595 | 3.9708e-05 | 2015 | 2014-06-24 | B | 26 | 0.023189 | 7.9415e-05
1 | 141326 | 2014-06-24 10:30 | 2014-06-24 13:56 | 206 | 152 | 22672 | 0.06925 | 0.00046427 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/92358 - Replace poles and Xarms on Pungarehu 33kV line. Group A: Replace Pole 710661. Group B: Replace crossarm on Pole 710626. Isolation points: 33kV: ABS 31:36, ABS 31:26, ABS 32:87, Group A: 11kV: ABS TA720, ABS TA119. Group B: 11kV: ABS NG310, | F1,F2,F3 | Not entered | Not entered | Not entered | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 149.1579 | 146.1579 | 22216 | 0.067857 | 0.00046427 | 2014-06-24 | B | 0.033929 | 0.00023214 | 2015 | 2014-06-24 | B | 152 | 0.067857 | 0.00046427
1 | 141328 | 2014-06-10 09:00 | 2014-06-10 15:00 | 360 | 5 | 1800 | 0.005498 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CONDUCTOR | SIN: 14/91778 - CANCELLED DUE TO WEATHER - Replace conductor between M0034 and pole M0043. Isolation points:11kV Line Break at poole M0033 and Temp ABS TEMP73 on pole M0043. LLP 14/93412 and LLP 14/93413. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 1785 | 0.0054521 | 1.5272e-05 | 2014-06-10 | B | 0.0027261 | 7.636e-06 | 2015 | 2014-06-10 | B | 5 | 0.0054521 | 1.5272e-05
1 | 141329 | 2014-06-24 09:15 | 2014-06-24 17:20 | 485 | 92 | 5669 | 0.017316 | 0.00028101 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/93310 - STAGED RESTORATION. Replace pole and X-arms on 66kV / 11kV pole T0815. Isolation points: 66kV ABS QC66 & QC163; 11kV Fuses FP1006 | F3 | TOTARA | THAMES SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 61.6196 | 58.6196 | 5393 | 0.016473 | 0.00028101 | 2014-06-24 | B | 0.0082363 | 0.0001405 | 2015 | 2014-06-24 | B | 92 | 0.016473 | 0.00028101
1 | 141330 | 2014-06-24 17:58 | 2014-06-24 19:34 | 96 | 41 | 3936 | 0.012022 | 0.00012523 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Unknown Cause - Reported cross arm broken on pole M0761. Back feed and isolated between ABS 1187 & ABS 1271. Fault caused by faulty insulator burning through. Crossarm and 3 insulators replaced. Relivened OK. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 96 | 93 | 3813 | 0.011647 | 0.00012523 | 2014-06-24 | C | 0.011647 | 0.00012523 | 2015 | 2014-06-24 | C | 41 | 0.011647 | 0.00012523
1 | 141331 | 2014-06-24 09:07 | 2014-06-24 14:23 | 316 | 43 | 13588 | 0.041504 | 0.00013134 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93119 - Replace TX T1/329 and pole P34460. Isolation points: gap at poole P32998 LLPs 14/93120, 14/93122 | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 316 | 313 | 13459 | 0.041109 | 0.00013134 | 2014-06-24 | B | 0.020555 | 6.567e-05 | 2015 | 2014-06-24 | B | 43 | 0.041109 | 0.00013134
1 | 141339 | 2014-06-24 11:40 | 2014-06-24 11:55 | 15 | 6 | 90 | 0.0002749 | 1.8327e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/93322 - Install LV fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer fuses and new LV disconnector to be fitted w/in the 1hr HV shutdown. If required, an LV shutdown may be carried out after the HV is restored to complete | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 72 | 0.00021992 | 1.8327e-05 | 2014-06-24 | B | 0.00010996 | 9.163e-06 | 2015 | 2014-06-24 | B | 6 | 0.00021992 | 1.8327e-05
1 | 141340 | 2014-06-25 07:57 | 2014-06-25 14:40 | 403 | 154 | 18989 | 0.058 | 0.00047038 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - CB NG4 L/O on E/F, Sectionalised & found transformer N1010 with 1 fuse blown, Isolated transformer and relivened. 50kvA Transformer replaced. | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 123.3052 | 120.3052 | 18527 | 0.056589 | 0.00047038 | 2014-06-25 | C | 0.056589 | 0.00047038 | 2015 | 2014-06-25 | C | 154 | 0.056589 | 0.00047038
1 | 141341 | 2014-06-25 10:37 | 2014-06-25 11:28 | 51 | 34 | 1734 | 0.0052964 | 0.00010385 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | CABLE | SIN: 14/93542 - Isolate Transformer X1264 due to discharging cable on RMU 2008/2. Isolation Point: 11kV Fuse 2008/2. Note: Tenix will back feed all 400V lines that are fed from X1264. | F2 | BROADWAY | ARAHINA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 51 | 48 | 1632 | 0.0049848 | 0.00010385 | 2014-06-25 | B | 0.0024924 | 5.1925e-05 | 2015 | 2014-06-25 | B | 34 | 0.0049848 | 0.00010385
1 | 141342 | 2014-06-25 09:30 | 2014-06-25 11:25 | 115 | 5 | 1875 | 0.005727 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93764 - ADVERTISING ONLY - NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Replace 400V X-arm at Transformer TC5309. Isolation Point:11kV transformer fuses TC5309. | F4 | WHIRITOA | WHANGAMATA SUB | TP_WAIKINO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 375 | 372 | 1860 | 0.0056812 | 1.5272e-05 | 2014-06-25 | B | 0.0028406 | 7.636e-06 | 2015 | 2014-06-25 | B | 5 | 0.0056812 | 1.5272e-05
1 | 141344 | 2014-06-24 12:31 | 2014-06-24 12:55 | 24 | 5 | 120 | 0.00036653 | 1.5272e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/93318 - Install LV fuses on existing pole mounted TX. TXs to be isolated via 11kV Transformer Fuses and new LV disconnector to be fitted w/in the 1 hr HV shutdown. IF required an LV shutdown may be carried out after the HV is restored to complete | F3 | MOWBRAY RD | WAHAROA SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 24 | 21 | 105 | 0.00032071 | 1.5272e-05 | 2014-06-24 | B | 0.00016036 | 7.636e-06 | 2015 | 2014-06-24 | B | 5 | 0.00032071 | 1.5272e-05
1 | 141345 | 2014-06-25 09:06 | 2014-06-25 13:00 | 234 | 1 | 234 | 0.00071474 | 3.0544e-06 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | CROSSARM | SIN: 14/93336 - Replacing 400V Xarms at TC3304 open 11kV Transformer fuse. Isolation points: 11kV Transformer Fuse TC3304. NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. ADVERTISING ONLY FOR 14/933 | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 234 | 231 | 231 | 0.00070557 | 3.0544e-06 | 2014-06-25 | B | 0.00035279 | 1.527e-06 | 2015 | 2014-06-25 | B | 1 | 0.00070557 | 3.0544e-06
1 | 141346 | 2014-06-25 12:25 | 2014-06-25 14:17 | 112 | 580 | 31722 | 0.096892 | 0.0017716 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | JUMPER | Trees - CB 9 L/O reported flash in Dawson Rd & Tree in lines in Frankley Rd, Isolated 2 faults. 1 between Sw/Gear 254/3 & ABS 493 which had a blown jumper at links 506 caused by tree in Frankley Rd. Isolate tree in line betweeb ABS 107 & ABS 392 & Sw/gear | F3 | CITY 9 | CITY SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 54.6931 | 51.6931 | 29982 | 0.091578 | 0.0017716 | 2014-06-25 | C | 0.091578 | 0.0017716 | 2015 | 2014-06-25 | C | 580 | 0.091578 | 0.0017716
1 | 141348 | 2014-06-25 10:06 | 2014-06-25 17:01 | 415 | 197 | 37205 | 0.11364 | 0.00060172 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CROSSARM | Defective Component - CB TA7 L/O Reported lines down in Feaver Rd Isolated between ABS TA720 & TA119 Restored rest of power. Replaced cross arm & re-livened 2 HV cross arms, 6 polymers, 20 meters of wire used | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 188.8579 | 185.8579 | 36614 | 0.11183 | 0.00060172 | 2014-06-25 | C | 0.11183 | 0.00060172 | 2015 | 2014-06-25 | C | 197 | 0.11183 | 0.00060172
1 | 141349 | 2014-06-25 09:35 | 2014-06-25 12:39 | 184 | 37 | 6808 | 0.020795 | 0.00011301 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CUSTOMER REQUEST | CONDUCTOR | SIN: 14/93386 - Replace 11kV pole for the running of fibre optic cable. Isolation points: Line break at pole 768552. Associated 14/92048 | F2/F3 | EASTOWN RD | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 184 | 181 | 6697 | 0.020455 | 0.00011301 | 2014-06-25 | B | 0.010228 | 5.6507e-05 | 2015 | 2014-06-25 | B | 37 | 0.020455 | 0.00011301
1 | 141351 | 2014-06-25 08:30 | 2014-06-25 15:41 | 431 | 66 | 6226 | 0.019017 | 0.00020159 | No Power | 11000 | Planned | Underground Cable | PLANNED SHUTDOWN | CAPITAL WORKS | CABLE | SIN: 14/93201 - Network changes to TePuke feeders CB 2 & CB5. Connect new 11kV CFCC Sw/gear 9818. Shift connection of Transformer TE5-019 to PMA CB5 (from CB 2). Isolation points: 11kV CB5, ABS SE5-059, cable break at pole 222619, Sw/Gear 9818/4; 11kV (CB | F1,F2,F3 | Not entered | Not entered | Not entered | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 94.3333 | 91.3333 | 6028 | 0.018412 | 0.00020159 | 2014-06-25 | B | 0.009206 | 0.0001008 | 2015 | 2014-06-25 | B | 66 | 0.018412 | 0.00020159
1 | 141352 | 2014-06-25 16:10 | 2014-06-25 17:40 | 90 | 26 | 2340 | 0.0071474 | 7.9415e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Found lines down.Isolated at fuses NG404. Repaired line & re-livened | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 2262 | 0.0069091 | 7.9415e-05 | 2014-06-25 | C | 0.0069091 | 7.9415e-05 | 2015 | 2014-06-25 | C | 26 | 0.0069091 | 7.9415e-05
1 | 141354 | 2014-06-26 01:30 | 2014-06-26 04:40 | 190 | 40 | 7600 | 0.023214 | 0.00012218 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93497 - STAGE 4: Remove existing 11kV cable from Magnefix 568/4 reterminate and connect cable into new CFCF Safelink TEMP 78/2.11kV. Isolation points 11kV Fuse Switch TEMP 78/2, Switch 8942/1. | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 190 | 187 | 7480 | 0.022847 | 0.00012218 | 2014-06-26 | B | 0.011424 | 6.1088e-05 | 2015 | 2014-06-26 | B | 40 | 0.022847 | 0.00012218
1 | 141355 | 2014-06-26 00:33 | 2014-06-26 01:15 | 42 | 34 | 1020 | 0.0031155 | 0.00010385 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93496 - STAGE 3: Remove existing cable from Magnefix 568/4 at TX 2045N and connect new cable from new CFCF Safelink TEMP 78/4 to HV side TX 2045N and liven. Isolation points Fuse Switch TEMP 78/4, Switch 8942/1. | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 918 | 0.002804 | 0.00010385 | 2014-06-26 | B | 0.001402 | 5.1925e-05 | 2015 | 2014-06-26 | B | 34 | 0.002804 | 0.00010385
1 | 141356 | 2014-06-11 03:45 | 2014-06-11 11:16 | 451 | 666 | 298398 | 0.91143 | 0.0020342 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component - Katikati CB2 (Tetley Rd) L/O. Isolations made and lines down found at pole 201283. Repairs made and power restored. Shane Pepperel attended. | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 448.045 | 445.045 | 296400 | 0.90533 | 0.0020342 | 2014-06-11 | C | 0.90533 | 0.0020342 | 2015 | 2014-06-11 | C | 666 | 0.90533 | 0.0020342
1 | 141358 | 2014-06-26 09:44 | 2014-06-26 10:42 | 58 | 308 | 17864 | 0.054564 | 0.00094076 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | JUMPER | Defective Component - at 09:35, Pongakawa Sub, CB 2 Otamarakau Feeder. Found Blown Jumper at Fuses SE7-067. Isolated Lines at 11kV ABS 9760/1, SE7-020 & Links 9760/4. Permit Issued & Repairs Carried out. All Power Restored on Completion. Dave Ngatai Atten | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 58 | 55 | 16940 | 0.051742 | 0.00094076 | 2014-06-26 | C | 0.051742 | 0.00094076 | 2015 | 2014-06-26 | C | 308 | 0.051742 | 0.00094076
1 | 141359 | 2014-06-11 01:03 | 2014-06-11 02:35 | 92 | 2242 | 198255 | 0.60555 | 0.006848 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Whitianga CB1 tripped and L/O. ABS 318 was opened and CB1 closed. Recloser 9457/1 opened and 318 closed. 9457/1 closed and power restored. Patrolled by Ben Edwards but no fault found. | F1,F2,F3 | Not entered | Not entered | Not entered | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 88.4277 | 85.4277 | 191529 | 0.58501 | 0.006848 | 2014-06-11 | C | 0.58501 | 0.006848 | 2015 | 2014-06-11 | C | 2242 | 0.58501 | 0.006848
1 | 141360 | 2014-06-11 05:31 | 2014-06-11 13:50 | 499 | 698 | 300144 | 0.91677 | 0.002132 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Tirau CB 5. (Cambridge Rd) tripped when backfeeding Lake 5. Line was patrolled and no fault was found. Kevin Cole attended. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 430.0057 | 427.0057 | 298050 | 0.91037 | 0.002132 | 2014-06-11 | C | 0.91037 | 0.002132 | 2015 | 2014-06-11 | C | 698 | 0.91037 | 0.002132
1 | 141361 | 2014-06-11 13:53 | 2014-06-11 20:53 | 420 | 152 | 59150 | 0.18067 | 0.00046427 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND | UNKNOWN | Unknown Cause - Te Puke CB 8. Recloser 9502 tripped. Storm in region. Line patrolled and no fault found. David Joynt, Ted Glasgow, Denis Ngatai attended. | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 389.1447 | 386.1447 | 58694 | 0.17928 | 0.00046427 | 2014-06-11 | C | 0.17928 | 0.00046427 | 2015 | 2014-06-11 | C | 152 | 0.17928 | 0.00046427
1 | 141363 | 2014-05-31 08:45 | 2014-05-31 12:00 | 195 | 4 | 780 | 0.0023825 | 1.2218e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/91984 - Rescheduled 26th June 2014 . Replace defect pole 834482 Opaki Race Course Rd. Isolation points: Links 7462. Joe advises he has spoken to the 4 effected ICPs and they are ok with outage today. DC confirms ok to process today. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 768 | 0.0023458 | 1.2218e-05 | 2014-05-31 | B | 0.0011729 | 6.109e-06 | 2015 | 2014-05-31 | B | 4 | 0.0023458 | 1.2218e-05
1 | 141364 | 2014-06-26 12:15 | 2014-06-26 14:00 | 105 | 4 | 420 | 0.0012829 | 1.2218e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - at 12:15, Kerepehi Sub, CB 6 Ngatea Feeder. Found Transformer TC1419 had blown. Own Isolation & Access Permit Issued & Repairs Carried out. All Power Restored on Completion. Brian Fisher Attended. 1x Transformer Replaced & 3x HV Fuse | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 408 | 0.0012462 | 1.2218e-05 | 2014-06-26 | C | 0.0012462 | 1.2218e-05 | 2015 | 2014-06-26 | C | 4 | 0.0012462 | 1.2218e-05
1 | 141366 | 2014-06-27 04:34 | 2014-06-27 05:30 | 56 | 142 | 5068 | 0.01548 | 0.00043373 | No Power | 11000 | Unplanned | Distribution Equip. | UNKNOWN | NOT PATROLLED | SWITCHGEAR - OH | No Power -11kV CB 4 ARC (1adv) Recloser CB 575 ARC & Trip C phase E/f line sectionalised and supply restored (Attended by Jeremy Hill) Motorised ABS 2995 went to an invalid state when trying to ooperate it and Faultman had to go to site to ooperate local | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 35.6901 | 32.6901 | 4642 | 0.014179 | 0.00043373 | 2014-06-27 | C | 0.014179 | 0.00043373 | 2015 | 2014-06-27 | C | 142 | 0.014179 | 0.00043373
1 | 141368 | 2014-06-26 17:16 | 2014-06-27 01:46 | 510 | 346 | 32680 | 0.099819 | 0.0010568 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power -CB 6777/6 Tripped E/F B O/C Patrolled and found trees in Lines Isolation Point Fuses 8198 No back feed. Mark Patterson Attended. Pole 747659 replaced and approximately 100metres of 16mm - other material to be advised. Tree was outside notice zon | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 94.4509 | 91.4509 | 31642 | 0.096648 | 0.0010568 | 2014-06-26 | C | 0.096648 | 0.0010568 | 2015 | 2014-06-26 | C | 346 | 0.096648 | 0.0010568
1 | 141369 | 2014-06-26 17:03 | 2014-06-26 19:05 | 122 | 666 | 44487 | 0.13588 | 0.0020342 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | INSULATOR | No Power -CB S61 Tripped E/Fpatrolled found Blown Insulator at Pole 738906 Replaced 1 X H/T Insulator Isolation point ABS 5793 & ABS 5776No back feed Nick Webby Attended | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 66.7973 | 63.7973 | 42489 | 0.12978 | 0.0020342 | 2014-06-26 | C | 0.12978 | 0.0020342 | 2015 | 2014-06-26 | C | 666 | 0.12978 | 0.0020342
1 | 141371 | 2014-06-26 17:01 | 2014-06-26 18:10 | 69 | 10 | 690 | 0.0021076 | 3.0544e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | CONDUCTOR | No Power -Shutdown Required as Deadend broken at Fuses LI167 IsolationPoint Fuses LI167 Replaced Dead end Brent Bensley Attended | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 69 | 66 | 660 | 0.0020159 | 3.0544e-05 | 2014-06-26 | C | 0.0020159 | 3.0544e-05 | 2015 | 2014-06-26 | C | 10 | 0.0020159 | 3.0544e-05
1 | 141372 | 2014-06-26 13:00 | 2014-06-26 14:10 | 70 | 10 | 700 | 0.0021381 | 3.0544e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/93623 - Install 400V Disconnector to the LV of the 11kV Transformer TC1000.Transformer remains isolated for additional 2hrs after 11kV has been reinstated for 400V X-arm replacements. Isolation point: 11kV Transformer fuses TC1000 | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 670 | 0.0020465 | 3.0544e-05 | 2014-06-26 | B | 0.0010232 | 1.5272e-05 | 2015 | 2014-06-26 | B | 10 | 0.0020465 | 3.0544e-05
1 | 141375 | 2014-06-11 09:15 | 2014-06-11 10:00 | 45 | 6 | 270 | 0.00082469 | 1.8327e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | FUSE | SIN: 14/92243 - - AP is for 1 hr to install a 400V Disc-Connector to the LV of the 11kV Transformer. The AP can then be cancelled and 11kV Transformer fuses closed, relivening the transformer up to the LV Disc-Connector. This is to be followed by a 400V s | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 252 | 0.00076971 | 1.8327e-05 | 2014-06-11 | B | 0.00038486 | 9.163e-06 | 2015 | 2014-06-11 | B | 6 | 0.00076971 | 1.8327e-05
1 | 141376 | 2014-06-27 08:01 | 2014-06-27 09:46 | 105 | 1 | 105 | 0.00032071 | 3.0544e-06 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93254 - STAGE 3 of 3. Relocate 11kV Local Service Transformer TE5-121 to new location and feeder. Connect to new Fuse/Sw 9818/2. Remove redundant cables from Fuses SE5-176 and SE5-180. Isolation points: 11kV Fuses SE5-176, SE5-180 & Fuse/Sw 98 | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 102 | 0.00031155 | 3.0544e-06 | 2014-06-27 | B | 0.00015578 | 1.527e-06 | 2015 | 2014-06-27 | B | 1 | 0.00031155 | 3.0544e-06
1 | 141377 | 2014-06-26 11:20 | 2014-06-27 13:15 | 1555 | 1 | 1555 | 0.0047496 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component - at 11:20, Kerepehi Sub, CB 6 Ngatea Feeder. Found Transformer TC5082 had blown & also jumper had come out of top of DDO fuse. This transformer had its own associated Fused ABS. Isolated Transformer at Fused ABS TC5082. Customer was h | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 1555 | 1552 | 1552 | 0.0047405 | 3.0544e-06 | 2014-06-26 | C | 0.0047405 | 3.054e-06 | 2015 | 2014-06-26 | C | 1 | 0.0047405 | 3.0544e-06
1 | 141380 | 2014-06-27 14:03 | 2014-06-27 14:34 | 31 | 232 | 7192 | 0.021967 | 0.00070863 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NOT PATROLLED | UNKNOWN | No Power - CB 3 Tripped O/C. Not Patrolled as Faultman was 1 Hour away- waited the 15 Mins Tried reclose. Livened OK. | F4 | THOMAS RD | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 31 | 28 | 6496 | 0.019842 | 0.00070863 | 2014-06-27 | C | 0.019842 | 0.00070863 | 2015 | 2014-06-27 | C | 232 | 0.019842 | 0.00070863
1 | 141381 | 2014-06-27 12:59 | 2014-06-27 15:06 | 127 | 3 | 381 | 0.0011637 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power - Shutdown Required to replace Transformer N2124. Isolation Point Fuses NG290. Used 1X 15KVA Transformer. Bent Bensley Attended. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 127 | 124 | 372 | 0.0011362 | 9.1633e-06 | 2014-06-27 | C | 0.0011362 | 9.163e-06 | 2015 | 2014-06-27 | C | 3 | 0.0011362 | 9.1633e-06
1 | 141382 | 2014-06-27 13:00 | 2014-06-27 13:30 | 30 | 63 | 1890 | 0.0057729 | 0.00019243 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | JOINT FAILURE | JUMPER | Defective Component -Faultman investigating fault found jumper/connection to be burning up. Crew called out to repair. Work area isolated at ABS B16 and connection cleaned up and retightened. Attended by Mike Thompson. Nil materials used | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 1701 | 0.0051956 | 0.00019243 | 2014-06-27 | C | 0.0051956 | 0.00019243 | 2015 | 2014-06-27 | C | 63 | 0.0051956 | 0.00019243
1 | 141384 | 2014-06-27 08:30 | 2014-06-27 14:54 | 384 | 77 | 29568 | 0.090313 | 0.00023519 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/92126 - Install new 11kV Safelink CFC Sw/gear (9794) between Sw/gear 9030/3 and SD4-739. Transfer Transformer TD4-737 from Fuse/Sw SD4-743 to new Fuse/Sw 9794/2. Isolation points: 11kV Sw/gear SD4-739, 9030/3 and Fuse/Sw SD4-743. Job Re-Advertise | F3 | MAUNGATAPU | WELCOME BAY SUB | TP_KAITIMAKO | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 384 | 381 | 29337 | 0.089608 | 0.00023519 | 2014-06-27 | B | 0.044804 | 0.0001176 | 2015 | 2014-06-27 | B | 77 | 0.089608 | 0.00023519
1 | 141387 | 2014-06-27 10:25 | 2014-06-27 12:48 | 143 | 8 | 1144 | 0.0034943 | 2.4435e-05 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | TREE IN NOTICE ZONE | CONDUCTOR | Trees -Call came in from public that a tree had come down through the lines. Work area was isolated at Fuses 405 and tree cleared and lines repaired. Attended by James Prime and Wayne Englebretsen. NDR #41791. Materials used: 6mtrs of squirrel conductor, | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 143 | 140 | 1120 | 0.003421 | 2.4435e-05 | 2014-06-27 | C | 0.003421 | 2.4435e-05 | 2015 | 2014-06-27 | C | 8 | 0.003421 | 2.4435e-05
1 | 141388 | 2014-06-27 09:08 | 2014-06-27 10:53 | 105 | 178 | 15630 | 0.047741 | 0.00054369 | No Power | 22000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird.Rata CB 1350 Trip, O/C B and C phase. This caused an outage to both Hunterville 22kV feeder and the Putorino feeder which was being backfed (See outdef 141389). Putorino feeder was isolated from Hunterville 22kV, and Hunterville 22kV was | F4 | PUTORINO | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 87.809 | 84.809 | 15096 | 0.04611 | 0.00054369 | 2014-06-27 | C | 0.04611 | 0.00054369 | 2015 | 2014-06-27 | C | 178 | 0.04611 | 0.00054369
1 | 141389 | 2014-06-27 09:08 | 2014-06-27 09:37 | 29 | 183 | 5307 | 0.01621 | 0.00055896 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | BIRD STRIKE | CONDUCTOR | Animals - bird. Rata CB 1350 Trip, O/C B and C phase. This caused an outage to Putorino feeder due to being backfed from Hunterville 22kV (See outdef 141388). Feeder was sectionalised until successfully closed in without further tripping. Dead bird found | F4 | PUTORINO | RATA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 29 | 26 | 4758 | 0.014533 | 0.00055896 | 2014-06-27 | C | 0.014533 | 0.00055896 | 2015 | 2014-06-27 | C | 183 | 0.014533 | 0.00055896
1 | 141390 | 2014-06-27 17:35 | 2014-06-27 18:40 | 65 | 14 | 910 | 0.0027795 | 4.2762e-05 | No Power | 6600 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CROSSARM | Defective Component - Floating conductor found as part of Dispatch job - Isolated at Fuses 5516, cross arm was replaced, Feeder returned to service - Attended by Tony Julian - Used 1x crossarm, 3x insulators, 2x Braces plus some bolts | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 868 | 0.0026512 | 4.2762e-05 | 2014-06-27 | C | 0.0026512 | 4.2762e-05 | 2015 | 2014-06-27 | C | 14 | 0.0026512 | 4.2762e-05
1 | 141392 | 2014-06-28 03:54 | 2014-06-28 04:16 | 22 | 515 | 11330 | 0.034607 | 0.001573 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause - Recloser 9220 tripped E/F, L/O feeder patrolled no fault found, Sam Jones attended | F2/F4 | MALEME ST | TP_TAURANGA 11KV | TP_TAURANGA 11 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 9785 | 0.029888 | 0.001573 | 2014-06-28 | C | 0.029888 | 0.001573 | 2015 | 2014-06-28 | C | 515 | 0.029888 | 0.001573
1 | 141395 | 2014-06-28 13:54 | 2014-06-28 15:42 | 108 | 518 | 24859 | 0.07593 | 0.0015822 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | SUSPECT BIRD | UNKNOWN | Unknown Cause -Recloser 9773 Trip. E/F. L/O. Feeder sectionalised but no fault found. Suspect bird strike. All closed back up OK. Iro Ezekiela Faultman. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 47.9903 | 44.9903 | 23305 | 0.071183 | 0.0015822 | 2014-06-28 | C | 0.071183 | 0.0015822 | 2015 | 2014-06-28 | C | 518 | 0.071183 | 0.0015822
1 | 141396 | 2014-06-27 15:53 | 2014-06-28 14:04 | 1331 | 3 | 804 | 0.0024558 | 9.1633e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | DISTRIBUTION TRANSFORMER | Defective Component -Transformer N2124 was found to be faulty requiring replacment. Transformer replaced however the NEW transformer was also faulty and necessitated another shut to install another NEW transformer. Allen Rarere, B Bensley attended. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 268 | 265 | 795 | 0.0024283 | 9.1633e-06 | 2014-06-27 | C | 0.0024283 | 9.163e-06 | 2015 | 2014-06-27 | C | 3 | 0.0024283 | 9.1633e-06
1 | 141397 | 2014-06-28 02:34 | 2014-06-28 05:16 | 162 | 250 | 25352 | 0.077436 | 0.00076361 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | UNKNOWN | Unknown Cause -11kV Recloser10002 tripped E/F L/O. Fully patrolled, no fault found. N Morris and R Turner attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 101.408 | 98.408 | 24602 | 0.075145 | 0.00076361 | 2014-06-28 | C | 0.075145 | 0.00076361 | 2015 | 2014-06-28 | C | 250 | 0.075145 | 0.00076361
1 | 141398 | 2014-06-28 01:55 | 2014-06-28 03:21 | 86 | 637 | 43095 | 0.13163 | 0.0019457 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | Accident -CB 8 tripped L/O due to car V pole at pole P03377. Isolation via H104 & Sw/gr 473, no back fed. All work complete. Only had to Straighten pole, no equipment used. Tenix to provide NDR Monday. N Brown & C naylor Attended | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 67.6531 | 64.6531 | 41184 | 0.12579 | 0.0019457 | 2014-06-28 | C | 0.12579 | 0.0019457 | 2015 | 2014-06-28 | C | 637 | 0.12579 | 0.0019457
1 | 141400 | 2014-06-28 11:48 | 2014-06-28 14:06 | 138 | 364 | 38276 | 0.11691 | 0.0011118 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component -Cb WH2 tripped L/O no flags. Fully patrolled. Found transformer W2263 blown requiring replacment, Single phase 7.5KVA, to be done Monday in agreement with owner (Woolshed). Has own fuses. H Hood, N Webby | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 105.1538 | 102.1538 | 37184 | 0.11358 | 0.0011118 | 2014-06-28 | C | 0.11358 | 0.0011118 | 2015 | 2014-06-28 | C | 364 | 0.11358 | 0.0011118
1 | 141402 | 2014-06-29 22:35 | 2014-06-29 23:50 | 75 | 5 | 375 | 0.0011454 | 1.5272e-05 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | Defective Component -Called to part power via T VD No. 8532405, found transformer 2230T faulty, replaced, iso by fuses 6054. All work complete. N Webby Attended | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 75 | 72 | 360 | 0.0010996 | 1.5272e-05 | 2014-06-29 | C | 0.0010996 | 1.5272e-05 | 2015 | 2014-06-29 | C | 5 | 0.0010996 | 1.5272e-05
1 | 141405 | 2014-06-29 12:18 | 2014-06-29 14:15 | 117 | 364 | 29647 | 0.090555 | 0.0011118 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | CONDUCTOR | Defective Component -11kV CB WH2 tripped L/O, no flags. Cause of trippping due to one phase/line down at Pole 371316 due to a failed sleeve, re-sleeved, all good. Iso by ABS's Wh272, WH217, Wh252, Backfeeds via ABS's ABS's WH290 & Wh278. All works complet | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 81.4478 | 78.4478 | 28555 | 0.087219 | 0.0011118 | 2014-06-29 | C | 0.087219 | 0.0011118 | 2015 | 2014-06-29 | C | 364 | 0.087219 | 0.0011118
1 | 141406 | 2014-06-29 07:03 | 2014-06-29 08:50 | 107 | 17 | 1819 | 0.005556 | 5.1925e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | SWITCHGEAR - UG | SIN: 14/93477 - Change oil on 11kV Sw/gear 120, 121 & Fuse FS44. Isolation Points: 11kV Sw/gear 50 & Sw/gear 192. | F2 | MALDEN ST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107 | 104 | 1768 | 0.0054002 | 5.1925e-05 | 2014-06-29 | B | 0.0027001 | 2.5963e-05 | 2015 | 2014-06-29 | B | 17 | 0.0054002 | 5.1925e-05
1 | 141407 | 2014-06-29 06:30 | 2014-06-29 08:36 | 126 | 7 | 882 | 0.002694 | 2.1381e-05 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | SURGE ARRESTOR | Defective Component -Fuse FP897 Blown for second time in 2 days. Cable isolated for testing. Cable found OK but Lightning arrestor found to be faulty. Lightning arrestor replaced and cable relivened.. Faultman Steve Martin | F3 | MVILLE SOUTH | PIAKO SUB | TP_PIAKO | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 126 | 123 | 861 | 0.0026299 | 2.1381e-05 | 2014-06-29 | C | 0.0026299 | 2.1381e-05 | 2015 | 2014-06-29 | C | 7 | 0.0026299 | 2.1381e-05
1 | 141408 | 2014-06-29 14:26 | 2014-06-29 14:42 | 16 | 165 | 2640 | 0.0080637 | 0.00050398 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component -Faultman found a broken 11KV fuses holder on transformer X1405, line was isolated at ABS 030 and 1125 to replace the 1 fuses holder. Scott Bullock attended | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 16 | 13 | 2145 | 0.0065517 | 0.00050398 | 2014-06-29 | C | 0.0065517 | 0.00050398 | 2015 | 2014-06-29 | C | 165 | 0.0065517 | 0.00050398
1 | 141412 | 2014-06-29 11:20 | 2014-06-29 14:50 | 210 | 691 | 98350 | 0.3004 | 0.0021106 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | Trees -CB Trip. E/F. L/O. Caused by tree outside the notice zone falling across the lines bringing them down between Poles 386213 & 200900. The resulting Fault Current also caused a line to come down between Poles 200987 & 384617. This line was re-joined | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 142.33 | 139.33 | 96277 | 0.29407 | 0.0021106 | 2014-06-29 | C | 0.29407 | 0.0021106 | 2015 | 2014-06-29 | C | 691 | 0.29407 | 0.0021106
1 | 141413 | 2014-06-29 14:30 | 2014-06-29 16:57 | 147 | 238 | 9562 | 0.029206 | 0.00072695 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | JOINT FAILURE | SWITCHGEAR - UG | Defective Component -Large bang heard coming from Fuse/Sw S4582. Sw/gear was isolated at Sw/g IP326, S4546 & 9363/3. Backfeeds via Sw/g S5249 & 9361/1. On invesigation it was found that moisture had entered the Bus Coupler Joint Between Fuse/Sw S4582 and | F3 | GLOUCESTER RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 40.1765 | 37.1765 | 8848 | 0.027026 | 0.00072695 | 2014-06-29 | C | 0.027026 | 0.00072695 | 2015 | 2014-06-29 | C | 238 | 0.027026 | 0.00072695
1 | 141414 | 2014-06-30 08:45 | 2014-06-30 12:55 | 250 | 47 | 11750 | 0.035889 | 0.00014356 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/93537 - Replace broken Pole 817718. Isolation Point: 11kV Fuse 7570. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 11609 | 0.035459 | 0.00014356 | 2014-06-30 | B | 0.017729 | 7.1779e-05 | 2015 | 2014-06-30 | B | 47 | 0.035459 | 0.00014356
1 | 141416 | 2014-06-30 09:30 | 2014-06-30 09:44 | 14 | 165 | 2310 | 0.0070557 | 0.00050398 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Wind - Received initial outage on Wanganui East CB10 on A, B & C Phase O/C. This feeder was backfeeding 2 other feeders at the time (Blink Bonnie CB 3 & 4 due to Blink Bonnie outage). This fault record refers to Wanganui East CB10 feeder. Fault later foun | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 1815 | 0.0055438 | 0.00050398 | 2014-06-30 | C | 0.0055438 | 0.00050398 | 2015 | 2014-06-30 | C | 165 | 0.0055438 | 0.00050398
1 | 141417 | 2014-06-30 09:30 | 2014-06-30 09:44 | 14 | 619 | 8666 | 0.02647 | 0.0018907 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Wind - Received initial outage on Wanganui East CB10 on A, B & C Phase O/C. This feeder was backfeeding 2 other feeders at the time (Blink Bonnie CB 3 & 4 due to Blink Bonnie outage). This fault record refers to Blink Bonnie CB4 feeder. Fault later found | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 6809 | 0.020798 | 0.0018907 | 2014-06-30 | C | 0.020798 | 0.0018907 | 2015 | 2014-06-30 | C | 619 | 0.020798 | 0.0018907
1 | 141418 | 2014-06-30 09:30 | 2014-06-30 10:35 | 65 | 205 | 13325 | 0.0407 | 0.00062616 | No Power | 11000 | Unplanned | Overhead Line | ADVERSE WEATHER | WIND BLOW DEBRIS - TREES | CONDUCTOR | Wind - Received initial outage on Wanganui East CB10 on A, B & C Phase O/C. This feeder was backfeeding 2 other feeders at the time (Blink Bonnie CB 3 & 4 due to Blink Bonnie outage). This fault record refers to Blink Bonnie CB3 feeder. Fault later found | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 12710 | 0.038822 | 0.00062616 | 2014-06-30 | C | 0.038822 | 0.00062616 | 2015 | 2014-06-30 | C | 205 | 0.038822 | 0.00062616
1 | 141419 | 2014-06-30 08:00 | 2014-06-30 08:38 | 38 | 74 | 2812 | 0.008589 | 0.00022603 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | FUSE HOLDER | Defective Component - Short outage required from ABS S366 to end to repair a broken fuse holder on Fuses 7533. Relivened OK. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 38 | 35 | 2590 | 0.007911 | 0.00022603 | 2014-06-30 | C | 0.007911 | 0.00022603 | 2015 | 2014-06-30 | C | 74 | 0.007911 | 0.00022603
1 | 141420 | 2014-06-30 13:11 | 2014-06-30 13:39 | 28 | 597 | 16663 | 0.050896 | 0.0018235 | No Power | 33000 | Unplanned | Distribution Equip. | UNKNOWN | NO FAULT FOUND | PROTECTION | Other/miscellaneous cause - Received initial tripping on TeOreOre 33kv CB C809 causing loss of supply to both Awatoitoi and Tinui Subs. (This record refers to outage on Awatoitoi). Tripping coincident with removal of a "redundant" under frequency cable. S | F1,F2,F3 | Not entered | Not entered | Not entered | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 27.9112 | 24.9112 | 14872 | 0.045425 | 0.0018235 | 2014-06-30 | C | 0.045425 | 0.0018235 | 2015 | 2014-06-30 | C | 597 | 0.045425 | 0.0018235
1 | 141421 | 2014-06-30 13:11 | 2014-06-30 13:38 | 27 | 639 | 17253 | 0.052698 | 0.0019518 | No Power | 33000 | Unplanned | Distribution Equip. | UNKNOWN | NO FAULT FOUND | PROTECTION | Other/miscellaneous cause - Received initial tripping on TeOreOre 33kV CB C809 causing loss of supply to both Awatoitoi and Tinui Subs. (This record refers to outage on Tinui). Tripping coincident with removal of a "redundant" under frequency cable. Suppl | F1,F2,F3 | Not entered | Not entered | Not entered | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 15336 | 0.046843 | 0.0019518 | 2014-06-30 | C | 0.046843 | 0.0019518 | 2015 | 2014-06-30 | C | 639 | 0.046843 | 0.0019518
1 | 141422 | 2014-06-30 08:47 | 2014-06-30 15:25 | 398 | 224 | 71092 | 0.21715 | 0.00068419 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | CAPITAL WORKS | POLE | SIN: 14/93133 - STAGED RESTORATION. Change 11kV pole 206327. Isolation points: Line Break at pole 206339, Sw/gear 9138/3, ABS SC4-689, SC4-687. Refer to SIN 14/93607 for Re-advertising Only. | F3 | VALE ST | OTUMOETAI SUB | TP_TAURANGA 33 | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 317.375 | 314.375 | 70420 | 0.21509 | 0.00068419 | 2014-06-30 | B | 0.10755 | 0.00034209 | 2015 | 2014-06-30 | B | 224 | 0.21509 | 0.00068419
1 | 141423 | 2014-06-30 10:15 | 2014-06-30 15:00 | 285 | 5 | 1425 | 0.0043526 | 1.5272e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | CAPITAL WORKS | DISTRIBUTION TRANSFORMER | SIN: 14/93668 - Upgrade 11kV transformer TC 5938 due to overloading. After transformer is replaced Northpower will have an LV outage on TC 5938 to complete the replacement of the 400V conductor connected to this transformer. (The consumers connected to TC | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 285 | 282 | 1410 | 0.0043067 | 1.5272e-05 | 2014-06-30 | B | 0.0021534 | 7.636e-06 | 2015 | 2014-06-30 | B | 5 | 0.0043067 | 1.5272e-05
1 | 141425 | 2014-06-30 14:30 | 2014-06-30 16:12 | 102 | 1 | 102 | 0.00031155 | 3.0544e-06 | No Power | 11000 | Unplanned | Distribution Equip. | DEFECTIVE EQUIPMENT | BROKEN HARDWARE | DISTRIBUTION TRANSFORMER | No Power. Faulty Transformer changed at W2168. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 102 | 99 | 99 | 0.00030239 | 3.0544e-06 | 2014-06-30 | C | 0.00030239 | 3.054e-06 | 2015 | 2014-06-30 | C | 1 | 0.00030239 | 3.0544e-06
1 | 141426 | 2014-06-30 11:24 | 2014-06-30 12:36 | 72 | 162 | 11664 | 0.035627 | 0.00049482 | No Power | 11000 | Unplanned | Overhead Line | TREE CONTACTS | OTHER VEGETATION | CONDUCTOR | No Power. Recloser 6286 Tripped. L/O. Line patrolled and branch removed from line at pole 762798.No NDR supplied. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 11178 | 0.034142 | 0.00049482 | 2014-06-30 | C | 0.034142 | 0.00049482 | 2015 | 2014-06-30 | C | 162 | 0.034142 | 0.00049482
1 | 141427 | 2014-06-30 12:15 | 2014-06-30 13:45 | 90 | 31 | 2790 | 0.0085218 | 9.4687e-05 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | CONDUCTOR | No Power. Line patrolled. Fuses 8494 Opened and line repaired. Materials used: 2 x 7/16cu Sleeves and 2 metres of 7/16cu conductor. Craig Wellington attended. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 2697 | 0.0082378 | 9.4687e-05 | 2014-06-30 | C | 0.0082378 | 9.4687e-05 | 2015 | 2014-06-30 | C | 31 | 0.0082378 | 9.4687e-05
1 | 141430 | 2014-06-30 21:58 | 2014-07-01 01:31 | 213 | 589 | 125457 | 0.3832 | 0.0017991 | No Power | 11000 | Unplanned | Overhead Line | FOREIGN INTERFERENCE | VEHICLE DAMAGE | POLE | No Power. Car vs Pole 770214. Pole replaced.NDR to be supplied. | F3 | CORNFOOT ST | CASTLECLIFF SUB | TP_BRUNSWICK | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 213 | 210 | 123690 | 0.3778 | 0.0017991 | 2014-06-30 | C | 0.3778 | 0.0017991 | 2015 | 2014-06-30 | C | 589 | 0.3778 | 0.0017991
1 | 141434 | 2014-06-30 11:24 | 2014-06-30 15:08 | 224 | 41 | 9184 | 0.028052 | 0.00012523 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | INSULATOR | No Power. McKee CB191 and Motukawa CB210 tripped L/O. O/C & E/F. Line patrolled and 1 x Pin Insulator was repaired. Restoration compelted. Brent Moratti attended. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 224 | 221 | 9061 | 0.027676 | 0.00012523 | 2014-06-30 | C | 0.027676 | 0.00012523 | 2015 | 2014-06-30 | C | 41 | 0.027676 | 0.00012523
1 | 141437 | 2014-06-30 15:14 | 2014-06-30 17:14 | 120 | 250 | 22053 | 0.067359 | 0.00076361 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | NO FAULT FOUND | CONDUCTOR | Unknown Cause - Apiti Recloser RS10002 tripped on E/F and L/O. Line patrolled and sectionalised but no fault found. Bruce Mehrtens attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88.212 | 85.212 | 21303 | 0.065068 | 0.00076361 | 2014-06-30 | C | 0.065068 | 0.00076361 | 2015 | 2014-06-30 | C | 250 | 0.065068 | 0.00076361
1 | 141438 | 2014-06-30 15:15 | 2014-06-30 17:23 | 128 | 114 | 9457 | 0.028886 | 0.0003482 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | CONDUCTOR | Unknown Cause - Featherston RS C634. Tripped and L/o on O/C B and C phase. Line sectionalised and patrolled but no fault found. Jason Hall attended | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 82.9561 | 79.9561 | 9115 | 0.027841 | 0.0003482 | 2014-06-30 | C | 0.027841 | 0.0003482 | 2015 | 2014-06-30 | C | 114 | 0.027841 | 0.0003482
1 | 141440 | 2014-06-30 21:17 | 2014-06-30 23:19 | 122 | 249 | 25421 | 0.077647 | 0.00076055 | No Power | 11000 | Unplanned | Overhead Line | DEFECTIVE EQUIPMENT | OH EQUIPMENT FAILURE | FUSE | No Power. RS 10002 auto reclosed. L/O. E/F. Sectionalised and patrolled. No fault located. Tripped at a later time and faultmen returned to site. Replaced a Possible faulty DDO. Bruce Mehrtens and Peter Marshall attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 102.0924 | 99.0924 | 24674 | 0.075365 | 0.00076055 | 2014-06-30 | C | 0.075365 | 0.00076055 | 2015 | 2014-06-30 | C | 249 | 0.075365 | 0.00076055
1 | 141442 | 2014-06-30 15:45 | 2014-06-30 21:25 | 340 | 227 | 67000 | 0.20465 | 0.00069335 | No Power | 11000 | Unplanned | Overhead Line | UNKNOWN | PATROLLED | UNKNOWN | No Power. Recloser 9636/2 tripped. L/O. NOC Disabled. Sectionalised - line patrolled and no fault located. Cause unknown. Don Masters and Greg Whyte attended. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 295.1542 | 292.1542 | 66319 | 0.20257 | 0.00069335 | 2014-06-30 | C | 0.20257 | 0.00069335 | 2015 | 2014-06-30 | C | 227 | 0.20257 | 0.00069335
1 | 140592 | 2014-05-14 10:00 | 2014-05-14 14:22 | 262 | 26 | 6812 | 0.020807 | 7.9415e-05 | No Power | 11000 | Planned | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | SWITCHGEAR - OH | SIN: 14/91411 - Cut trees replace pole P41390 replace A57 fuses w/ new ABS and move it to pole P41376. Isolation points: A59. Associated LLP 14/91410. | F3 | AWAPUNI | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 262 | 259 | 6734 | 0.020568 | 7.9415e-05 | 2014-05-14 | B | 0.010284 | 3.9708e-05 | 2015 | 2014-05-14 | B | 26 | 0.020568 | 7.9415e-05
1 | 141021 | 2014-06-10 09:30 | 2014-06-10 14:10 | 280 | 27 | 7560 | 0.023091 | 8.2469e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/92772 - AP needed for tree removal at pole 364441/364482 by Treescape, trees hanging over 11kV lines. Isolation points: Fuses 813 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | WANGANUI | WESTERN ELECTRICITY | Network (Powerco) | 280 | 277 | 7479 | 0.022844 | 8.2469e-05 | 2014-06-10 | B | 0.011422 | 4.1235e-05 | 2015 | 2014-06-10 | B | 27 | 0.022844 | 8.2469e-05
1 | 141393 | 2014-06-28 08:50 | 2014-06-28 13:07 | 257 | 19 | 4883 | 0.014915 | 5.8034e-05 | No Power | 11000 | Planned | Overhead Line | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | CONDUCTOR | SIN: 14/93436 - Tree triming near 11kV lines for PF OLSEN Ltd. Isolation Point: 11kV Fuse SF6-012. | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | TAURANGA | EASTERN ELECTRICITY | Network (Powerco) | 257 | 254 | 4826 | 0.014741 | 5.8034e-05 | 2014-06-28 | B | 0.0073703 | 2.9017e-05 | 2015 | 2014-06-28 | B | 19 | 0.014741 | 5.8034e-05
1 | 377837 | 2014-07-01 08:36 | 2014-07-01 14:11 | 334.3667 | 1 | 334.3667 | 0.0010226 | 3.0584e-06 | Restore Supply on Device TD6-011 | 11000 | UNPLANNED | Distribution Equip. | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | TD6-052 | Repaired 2 x underground cables. 2 x 600mm cable used to repair each cable. NDR 048824 | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 334.3667 | 331.3667 | 331.3667 | 0.0010121 | 3.0544e-06 | 2014-07-01 | C | 0.0010121 | 3.054e-06 | 2015 | 2014-07-01 | C | 1 | 0.0010121 | 3.0544e-06
1 | 377846 | 2014-07-01 08:55 | 2014-07-01 11:27 | 152 | 947 | 130603 | 0.39944 | 0.0028963 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB6 | Sanson CB6 tripped. All phases O/C & E/F Restore supply. Line patrolled, sectionalised and restored. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 137.9124 | 134.9124 | 127762 | 0.39024 | 0.0028925 | 2014-07-01 | C | 0.39024 | 0.0028925 | 2015 | 2014-07-01 | C | 947 | 0.39024 | 0.0028925
1 | 373453 | 2014-07-01 09:10 | 2014-07-01 13:50 | 279.5 | 91 | 25434.5 | 0.077789 | 0.00027832 | NAPA ID:00035 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > PALM BEACH | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5 131 | Creating OMS entry for imported application. Replace existing 11kV G/M Transformer TD5-131 (leaking oil, level low). Isolation points: 11kV Fuse/Sw FP417. Work Location: 249 Gravatt Road, Mount Maunganui. | F3 | PALM BEACH | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 279.5 | 276.5 | 25161.5 | 0.076854 | 0.00027795 | 2014-07-01 | B | 0.038427 | 0.00013898 | 2015 | 2014-07-01 | B | 91 | 0.076854 | 0.00027795
1 | 382179 | 2014-07-01 10:58 | 2014-07-01 11:23 | 25.1333 | 1207 | 30234.1 | 0.092469 | 0.0036915 | Restore Supply on Device KPT-CB1 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | KPT CB1 | During sub checks inadvertently operated transformer trip, sub returned to service. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 25.049 | 22.049 | 26613.1 | 0.081288 | 0.0036867 | 2014-07-01 | C | 0.081288 | 0.0036867 | 2015 | 2014-07-01 | C | 1207 | 0.081288 | 0.0036867
1 | 382981 | 2014-07-01 12:02 | 2014-07-01 15:23 | 201.25 | 1 | 201.25 | 0.00061551 | 3.0584e-06 | Restore Supply on Device 2312T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2312t | replaced set 2x 6amp hv fuses on the tx 2312t due to lightening recently | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 201.25 | 198.25 | 198.25 | 0.00060554 | 3.0544e-06 | 2014-07-01 | C | 0.00060554 | 3.054e-06 | 2015 | 2014-07-01 | C | 1 | 0.00060554 | 3.0544e-06
1 | 383027 | 2014-07-01 12:46 | 2014-07-01 14:19 | 92.9667 | 925 | 83979.9 | 0.25685 | 0.002829 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB5 | CB 5 tripped O/C and L/O. AR disabled. Report of bang near lines. Feeder patrolled and no fault located. Possible bird strike. | F3/F4 | TAIRUA NORTH | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90.7891 | 87.7891 | 81204.9 | 0.24803 | 0.0028253 | 2014-07-01 | C | 0.24803 | 0.0028253 | 2015 | 2014-07-01 | C | 925 | 0.24803 | 0.0028253
1 | 384839 | 2014-07-01 14:27 | 2014-07-01 14:59 | 32 | 898 | 28736 | 0.087887 | 0.0027465 | Unknown | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB6 | 11kV Sanson CB6 tripped. C Phase O/C & E/F. Line reconfiguration for fault location. Cause of fault not recorded. Shazil Khan attended. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 26042 | 0.079543 | 0.0027429 | 2014-07-01 | C | 0.079543 | 0.0027429 | 2015 | 2014-07-01 | C | 898 | 0.079543 | 0.0027429
1 | 386700 | 2014-07-01 16:02 | 2014-07-01 16:29 | 26.7167 | 410 | 9483.8333 | 0.029006 | 0.001254 | Unknown | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB4 | Putaruru CB4 tripped L/O - No Flags. No Patrol undertaken - cause of fault unknown. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 23.1313 | 20.1313 | 8253.8333 | 0.025211 | 0.0012523 | 2014-07-01 | C | 0.025211 | 0.0012523 | 2015 | 2014-07-01 | C | 410 | 0.025211 | 0.0012523
1 | 386681 | 2014-07-01 16:09 | 2014-07-01 17:12 | 62.5333 | 1377 | 69368.7333 | 0.21216 | 0.0042114 | Restore Supply on Device T1/440 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB6 | Sanson CB6 tripped. C Phase O/C & E/F. Line reconfiguration undertaken for fault location. Shazil Khan attended. 1556hrs called cust to see if power restored but got no reply. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 50.3767 | 47.3767 | 65237.7333 | 0.19926 | 0.0042059 | 2014-07-01 | C | 0.19926 | 0.0042059 | 2015 | 2014-07-01 | C | 1377 | 0.19926 | 0.0042059
1 | 391596 | 2014-07-02 04:21 | 2014-07-02 16:00 | 699.25 | 60 | 16099.2 | 0.049238 | 0.00018351 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P03570 | Replace blown insulator x 2 at pole P03570. Network damage report 453271. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 268.32 | 265.32 | 15919.2 | 0.048624 | 0.00018327 | 2014-07-02 | C | 0.048624 | 0.00018327 | 2015 | 2014-07-02 | C | 60 | 0.048624 | 0.00018327
1 | 373485 | 2014-07-02 09:38 | 2014-07-02 10:30 | 52 | 3 | 156 | 0.00047711 | 9.1753e-06 | NAPA ID:00067 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4558 | Own Isolation and AP to install an LV Isolator on Transformer TC4558. HV to be isolated to complete the connection of the LV Fuses. Actual outage times 09:38 - 10:40. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 147 | 0.000449 | 9.1633e-06 | 2014-07-02 | B | 0.0002245 | 4.582e-06 | 2015 | 2014-07-02 | B | 3 | 0.000449 | 9.1633e-06
1 | 397494 | 2014-07-02 09:53 | 2014-07-02 14:37 | 283.5333 | 2 | 554.05 | 0.0016945 | 6.1168e-06 | Restore Supply on Device 2372T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 2372T | Replaced 2x 2amp DDO elements caused by lightening | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 277.025 | 274.025 | 548.05 | 0.001674 | 6.1088e-06 | 2014-07-02 | C | 0.001674 | 6.109e-06 | 2015 | 2014-07-02 | C | 2 | 0.001674 | 6.1088e-06
1 | 373489 | 2014-07-02 12:30 | 2014-07-02 15:30 | 180 | 4 | 720 | 0.0022021 | 1.2234e-05 | NAPA ID:00071 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4642 | Install an LV isolator on Transformer TC4642. HV to be isolated for one hour to connect LV fuses. HV Supply to be restored after one hour and LV shutdown to continue for 2 hours to allow completion of LV works. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 708 | 0.0021625 | 1.2218e-05 | 2014-07-02 | B | 0.0010813 | 6.109e-06 | 2015 | 2014-07-02 | B | 4 | 0.0021625 | 1.2218e-05
1 | 397790 | 2014-07-02 13:47 | 2014-07-02 14:40 | 53.4167 | 8 | 427.3333 | 0.001307 | 2.4467e-05 | Restore Supply on Device TC4506 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4506 | Off time was 13:47. Emergency Shutdown to replace broken cross arm. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 53.4167 | 50.4167 | 403.3333 | 0.001232 | 2.4435e-05 | 2014-07-02 | C | 0.001232 | 2.4435e-05 | 2015 | 2014-07-02 | C | 8 | 0.001232 | 2.4435e-05
1 | 399411 | 2014-07-02 17:52 | 2014-07-02 18:36 | 44 | 322 | 14168 | 0.043332 | 0.00098481 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T1/139 | LV line was found down at transformer T1/139, suspect was cause of feeder fault on CB 6.Disconnected service line for safety on #A8957. This job currently stuck in Test mode. Second stage of this outage is recorded under OMS Job ID 2888629 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 44 | 41 | 13202 | 0.040325 | 0.00098352 | 2014-07-02 | C | 0.040325 | 0.00098352 | 2015 | 2014-07-02 | C | 322 | 0.040325 | 0.00098352
1 | 2888629 | 2014-07-02 17:53 | 2014-07-02 18:57 | 64 | 581 | 37184 | 0.11372 | 0.0017769 | Restore Supply on Device L29 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB6 | Sanson CB6 auto reclosed and tripped A & B Phase O/C. Line patrolled and no fault found. Shazil Khan attended. Second stage of OMS Job 399411. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 35441 | 0.10825 | 0.0017746 | 2014-07-02 | C | 0.10825 | 0.0017746 | 2015 | 2014-07-02 | C | 581 | 0.10825 | 0.0017746
1 | 431029 | 2014-07-02 23:37 | 2014-07-03 06:46 | 429 | 58 | 13377.7333 | 0.040915 | 0.00017739 | Restore Supply on Device F48 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P13870 | Line was sectionalised and patrolled and a opossum was removed from the line at pole P13870 with a hot line stick. Supply was restored. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 230.6506 | 227.6506 | 13203.7333 | 0.04033 | 0.00017716 | 2014-07-02 | C | 0.04033 | 0.00017716 | 2015 | 2014-07-02 | C | 58 | 0.04033 | 0.00017716
1 | 430844 | 2014-07-03 00:57 | 2014-07-03 01:41 | 44.3 | 181 | 8018.3 | 0.024523 | 0.00055357 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9665 | Feeder patrolled beyond Recloser 9665. No fault found. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 44.3 | 41.3 | 7475.3 | 0.022833 | 0.00055285 | 2014-07-03 | C | 0.022833 | 0.00055285 | 2015 | 2014-07-03 | C | 181 | 0.022833 | 0.00055285
1 | 431589 | 2014-07-03 05:53 | 2014-07-04 11:54 | 1800.9808 | 1 | 1800.9833 | 0.0055082 | 3.0584e-06 | Restore Supply on Device T1/232 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TX T1/459 FUSES 23 | job was completed yesterday 3/7 HT fuse on section fuses.. 2x 6amp hv | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1800.9833 | 1797.9833 | 1797.9833 | 0.0054918 | 3.0544e-06 | 2014-07-03 | C | 0.0054918 | 3.054e-06 | 2015 | 2014-07-03 | C | 1 | 0.0054918 | 3.0544e-06
1 | 441945 | 2014-07-03 07:05 | 2014-07-03 11:31 | 266.2879 | 4 | 472.7667 | 0.0014459 | 1.2234e-05 | Restore Supply on Device 3009T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 3009T | hafd 1x 2amp | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 118.1917 | 115.1917 | 460.7667 | 0.0014074 | 1.2218e-05 | 2014-07-03 | C | 0.0014074 | 1.2218e-05 | 2015 | 2014-07-03 | C | 4 | 0.0014074 | 1.2218e-05
1 | 373514 | 2014-07-03 09:28 | 2014-07-03 12:06 | 157.5333 | 2 | 574.3333 | 0.0017566 | 6.1168e-06 | NAPA ID:00096 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3-083 | Creating OMS entry for imported application Power Off 09:28 Power On 11:40.Change Transformer Hanger Arms only. Isolation of transformer TC3-083 only. | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 287.1667 | 284.1667 | 568.3333 | 0.0017359 | 6.1088e-06 | 2014-07-03 | B | 0.00086796 | 3.054e-06 | 2015 | 2014-07-03 | B | 2 | 0.0017359 | 6.1088e-06
1 | 373518 | 2014-07-03 11:00 | 2014-07-03 14:08 | 188 | 14 | 2632 | 0.0080498 | 4.2818e-05 | NAPA ID:00100 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K13386 | Creating OMS entry for imported application. Stage 5: Connect new 11kV cable to jumpers K13386. Commission and liven cable and restore Te Puninga to CB3. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 188 | 185 | 2590 | 0.007911 | 4.2762e-05 | 2014-07-03 | B | 0.0039555 | 2.1381e-05 | 2015 | 2014-07-03 | B | 14 | 0.007911 | 4.2762e-05
1 | 454310 | 2014-07-04 08:24 | 2014-07-04 14:53 | 388.95 | 1 | 388.95 | 0.0011896 | 3.0584e-06 | Restore Supply on Device 5548E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5548E | Wire of an H/T Bush on Transformer 5548E. Isolated at Fuses 8804. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 388.95 | 385.95 | 385.95 | 0.0011789 | 3.0544e-06 | 2014-07-04 | C | 0.0011789 | 3.054e-06 | 2015 | 2014-07-04 | C | 1 | 0.0011789 | 3.0544e-06
1 | 373538 | 2014-07-04 09:00 | 2014-07-04 12:50 | 230 | 7 | 1610 | 0.0049241 | 2.1409e-05 | NAPA ID:00120 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F0130 | Install/connect new spur line with Fuses FP1610 and New Transformer TP2666. | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 230 | 227 | 1589 | 0.0048535 | 2.1381e-05 | 2014-07-04 | B | 0.0024267 | 1.069e-05 | 2015 | 2014-07-04 | B | 7 | 0.0048535 | 2.1381e-05
1 | 456153 | 2014-07-04 20:50 | 2014-07-05 08:20 | 690.05 | 195 | 124657.2833 | 0.38125 | 0.00059639 | Restore Supply on Device RC28 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | R0780 | See Child Job Details: 456147 | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 639.2681 | 636.2681 | 124072.2833 | 0.37897 | 0.00059561 | 2014-07-04 | C | 0.37897 | 0.00059561 | 2015 | 2014-07-04 | C | 195 | 0.37897 | 0.00059561
1 | 456455 | 2014-07-04 22:35 | 2014-07-04 22:44 | 9.1167 | 50 | 455.8333 | 0.0013941 | 0.00015292 | Restore Supply on Device SD4-638 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | SD4-638 |  | F2 | WAIHI RD | WAIHI ROAD SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 9.1167 | 6.1167 | 305.8333 | 0.00093414 | 0.00015272 | 2014-07-04 | C | 0.00093415 | 0.00015272 | 2015 | 2014-07-04 | C | 50 | 0.00093414 | 0.00015272
1 | 373558 | 2014-07-05 09:00 | 2014-07-05 11:16 | 136 | 96 | 13056 | 0.039931 | 0.00029361 | NAPA ID:00140 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P15258 | Creating OMS entry for imported application. Remove fargo sleeves and restrain 11kV lines and install new 11kV Fuse U8 on pole. Isolation Point: 11kV ABS U7. Work Location: Herbert Street, Eketahuna. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 136 | 133 | 12768 | 0.038999 | 0.00029322 | 2014-07-05 | B | 0.019499 | 0.00014661 | 2015 | 2014-07-05 | B | 96 | 0.038999 | 0.00029322
1 | 456933 | 2014-07-05 10:02 | 2014-07-05 12:55 | 172.6333 | 1 | 172.6333 | 0.00052799 | 3.0584e-06 | Restore Supply on Device TC5660 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5660 | blown x2 DDO fuses replaced x2 8amp fuses - due to wind clash HAFW | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 172.6333 | 169.6333 | 169.6333 | 0.00051813 | 3.0544e-06 | 2014-07-05 | C | 0.00051813 | 3.054e-06 | 2015 | 2014-07-05 | C | 1 | 0.00051813 | 3.0544e-06
1 | 456952 | 2014-07-05 10:19 | 2014-07-05 13:03 | 163.8167 | 1 | 163.8167 | 0.00050102 | 3.0584e-06 | Restore Supply on Device TC1461 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 151 KARAHAKI ROAD WAVERLEY | REPLACED 2 X 8 AMP DDO FUSES | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 163.8167 | 160.8167 | 160.8167 | 0.0004912 | 3.0544e-06 | 2014-07-05 | C | 0.0004912 | 3.054e-06 | 2015 | 2014-07-05 | C | 1 | 0.0004912 | 3.0544e-06
1 | 457306 | 2014-07-05 12:24 | 2014-07-05 16:55 | 270.7333 | 25 | 6036.3833 | 0.018462 | 7.6461e-05 | Restore Supply on Device 412 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 772871 | Line down. Isolated beyond Fuses 412 for repair. Gary Fisher attended. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 241.4553 | 238.4553 | 5961.3833 | 0.018209 | 7.6361e-05 | 2014-07-05 | C | 0.018209 | 7.6361e-05 | 2015 | 2014-07-05 | C | 25 | 0.018209 | 7.6361e-05
1 | 457389 | 2014-07-05 13:23 | 2014-07-05 16:32 | 188.3833 | 2 | 364.9167 | 0.0011161 | 6.1168e-06 | Restore Supply on Device T7/402 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole P46436 | wire off the insulator | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 182.4583 | 179.4583 | 358.9167 | 0.0010963 | 6.1088e-06 | 2014-07-05 | C | 0.0010963 | 6.109e-06 | 2015 | 2014-07-05 | C | 2 | 0.0010963 | 6.1088e-06
1 | 457668 | 2014-07-05 16:26 | 2014-07-05 21:29 | 303.35 | 602 | 89914.5667 | 0.275 | 0.0018412 | Restore Supply on Device R21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732438 | 11kV CB R21 tripped O/C L/O. Lines down at pole 732438 due to failed shackles (x1). Is by ABS's 6176 & 6125. All works complete. On relivening ABS 6176 failed requiring a second feeder outage (OMS 459250) to safely open ABS again. ABS 6176 DNO 140707. Bac | F1 | ELTHAM TOWN NORTH | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 149.3597 | 146.3597 | 88108.5667 | 0.26912 | 0.0018388 | 2014-07-05 | C | 0.26912 | 0.0018388 | 2015 | 2014-07-05 | C | 602 | 0.26912 | 0.0018388
1 | 458304 | 2014-07-05 17:34 | 2014-07-05 20:37 | 183.3 | 412 | 28389.75 | 0.086828 | 0.0012601 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | A12557 | 1 insulator and binder used at pole A12557 | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 68.9072 | 65.9072 | 27153.75 | 0.082939 | 0.0012584 | 2014-07-05 | C | 0.082939 | 0.0012584 | 2015 | 2014-07-05 | C | 412 | 0.082939 | 0.0012584
1 | 460363 | 2014-07-06 08:41 | 2014-07-06 10:47 | 125.6667 | 1 | 125.6667 | 0.00038434 | 3.0584e-06 | Restore Supply on Device TC1590 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | Transformer TC2300 | Transformer for this customer is actually TC2300. | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 125.6667 | 122.6667 | 122.6667 | 0.00037468 | 3.0544e-06 | 2014-07-06 | C | 0.00037468 | 3.054e-06 | 2015 | 2014-07-06 | C | 1 | 0.00037468 | 3.0544e-06
1 | 373559 | 2014-07-06 09:00 | 2014-07-06 14:49 | 349 | 119 | 41531 | 0.12702 | 0.00036395 | NAPA ID:00141 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 828820, 828835, 828821, 828827, 828828, 828831, 828841, 828843 | Replace defective poles on 33/11 kV Poles 828820/835/821/827/828/831/841/843, South Belt 33/11kV. This will also isolate for replacing TXs T2522/T2317. Isolation points: S113, Temp links 18, T2317, 8078, T1774, T1607, 8025. Work Location: Solway Crescent, | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 349 | 346 | 41174 | 0.12576 | 0.00036348 | 2014-07-06 | B | 0.062881 | 0.00018174 | 2015 | 2014-07-06 | B | 119 | 0.12576 | 0.00036348
1 | 460448 | 2014-07-06 09:25 | 2014-07-06 12:38 | 193.4 | 1 | 193.4 | 0.0005915 | 3.0584e-06 | Restore Supply on Device T9/485 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P08517 | Replace insulator & pin. Mullet makeoff, Leather washer & binder. 2 HV fuses blown required new links. T Pocock attended. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 193.4 | 190.4 | 190.4 | 0.00058156 | 3.0544e-06 | 2014-07-06 | C | 0.00058156 | 3.054e-06 | 2015 | 2014-07-06 | C | 1 | 0.00058156 | 3.0544e-06
1 | 461608 | 2014-07-06 12:26 | 2014-07-06 15:09 | 163 | 358 | 35631.3 | 0.10898 | 0.0010949 | Restore Supply on Device 172 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 758140 | CB 8 actually tripped at 12:26 but was not picked up by E-Map so ABS 172 was opened on SCADA to show a feeder outage. CB8 is not showing open on e-map?????? MDB 15meters of 16mm conductor, 6 compression sleeves. Brett Moratti and Chris Vivier attended. | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 99.5288 | 96.5288 | 34557.3 | 0.10555 | 0.0010935 | 2014-07-06 | C | 0.10555 | 0.0010935 | 2015 | 2014-07-06 | C | 358 | 0.10555 | 0.0010935
1 | 462459 | 2014-07-06 20:29 | 2014-07-07 01:33 | 304.3833 | 364 | 12427 | 0.038007 | 0.0011133 | Restore Supply on Device WH2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752663 | Line down found fom dispatch job, CB did not trip, CB opened by NOC when line found - Isolated at ABs's 6537 & WH272 and Fuses 8964 - back feed install via ABS Wh 278 - Line repaired and feeder returned to service - attended by Jade Willams - Used 3 x sle | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 34.1401 | 31.1401 | 11335 | 0.034622 | 0.0011118 | 2014-07-06 | C | 0.034622 | 0.0011118 | 2015 | 2014-07-06 | C | 364 | 0.034622 | 0.0011118
1 | 373577 | 2014-07-07 09:30 | 2014-07-07 15:00 | 330 | 3 | 990 | 0.0030278 | 9.1753e-06 | NAPA ID:00160 TP_OPUNAKE GXP > PUNGAREHU SUB > PARIHAKA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7043262 | Change 11kV pole 704264 and build new spur line to feed new 1005V TX 5624E, spur line will have two spans and new fuses 12010 to feed TX. Isolation points: PU410, LL break by pole 704262. LLP To create Line Break 14/93745. LLP to close Line Break 14/93746 | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 981 | 0.0029964 | 9.1633e-06 | 2014-07-07 | B | 0.0014982 | 4.582e-06 | 2015 | 2014-07-07 | B | 3 | 0.0029964 | 9.1633e-06
1 | 373576 | 2014-07-07 09:30 | 2014-07-07 15:02 | 332 | 13 | 4316 | 0.0132 | 3.9759e-05 | NAPA ID:00158 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 5153 | Cut trees near 11kV lines along Puke Rd and some of Ngatoto Rd North by poles 765150, 765122, 765092. Work Order 10130231. Unable to locate outage steps associated with this outage - have included in the parent OMS Job ID (this entry). | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 332 | 329 | 4277 | 0.013064 | 3.9708e-05 | 2014-07-07 | B | 0.0065319 | 1.9854e-05 | 2015 | 2014-07-07 | B | 13 | 0.013064 | 3.9708e-05
1 | 468468 | 2014-07-07 09:45 | 2014-07-07 10:49 | 64 | 1 | 64 | 0.00019574 | 3.0584e-06 | Restore Supply on Device A58 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P44917 | Faultman found line down due to a swans that fly into the lines. Line was isolated at ABS A58 to make the repairs. 2 meters of squirrel conductor was replaced and 2 crimp joints used. David Thomson attended. | F3 | AWAPUNI | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 61 | 0.00018632 | 3.0544e-06 | 2014-07-07 | C | 0.00018632 | 3.054e-06 | 2015 | 2014-07-07 | C | 1 | 0.00018632 | 3.0544e-06
1 | 475582 | 2014-07-07 11:08 | 2014-07-07 13:00 | 112 | 6 | 672 | 0.0020553 | 1.8351e-05 | Restore Supply on Device WH208 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 725864 | Faulty transformer W2263 changed on 7/07/14 under self issued AP - isolated at fuses WH208 - was an historical TVD job, 8528479 - off at 11:08 on at 13:00 - Bevan Hughes attended. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 112 | 109 | 654 | 0.0019976 | 1.8327e-05 | 2014-07-07 | C | 0.0019976 | 1.8327e-05 | 2015 | 2014-07-07 | C | 6 | 0.0019976 | 1.8327e-05
1 | 468572 | 2014-07-07 11:09 | 2014-07-07 18:57 | 467.7333 | 1271 | 170963 | 0.52288 | 0.0038873 | Restore Supply on Device CB2862 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 738722 | Stratford GXP CB2862 tripped on O/C. Loss of Supply to Kaponga & Cardiff Substations. Line patrolled and broken conductors found at 33kV pole 738722 - Possible Bird Strike. Conductor repaired and restoration completed. Phil Webby attended. | F1, F2, F3 | CARDIFF NORTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 134.5106 | 131.5106 | 167150 | 0.51055 | 0.0038822 | 2014-07-07 | C | 0.51055 | 0.0038822 | 2015 | 2014-07-07 | C | 1271 | 0.51055 | 0.0038822
1 | 470826 | 2014-07-07 11:57 | 2014-07-07 15:55 | 237.7167 | 1 | 237.7167 | 0.00072704 | 3.0584e-06 | Restore Supply on Device T2/952 | 11000 | UNPLANNED | Distribution Equip. | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T2/952, H116 | Replaced 3x 10amp HV DDO Fuses caused by bird strike. no arros. Fuses H116 1506hrs fault man calling svs hub to be on sited as unable to progress to complete. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 237.7167 | 234.7167 | 234.7167 | 0.00071692 | 3.0544e-06 | 2014-07-07 | C | 0.00071692 | 3.054e-06 | 2015 | 2014-07-07 | C | 1 | 0.00071692 | 3.0544e-06
1 | 475540 | 2014-07-08 07:25 | 2014-07-08 09:18 | 112.5167 | 9 | 364.9167 | 0.0011161 | 2.7526e-05 | Restore Supply on Device TC4653 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | V0870 | Replaced x 2 binders on pole V0870 due to wind. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 40.5463 | 37.5463 | 337.9167 | 0.0010321 | 2.749e-05 | 2014-07-08 | C | 0.0010321 | 2.749e-05 | 2015 | 2014-07-08 | C | 9 | 0.0010321 | 2.749e-05
1 | 381358 | 2014-07-08 09:19 | 2014-07-08 15:22 | 363 | 9 | 3267 | 0.0099919 | 2.7526e-05 | NAPA ID:00189 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209696, 209697, 209877, 209876, 209874, 268189 | Replace 33kV H structure 209696, 209697. Replace 33kV arms on pole 209877, 209876, 209874, 268189. Work Location: Barrett Road, Omokoroa. Work Order 10149210. | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 363 | 360 | 3240 | 0.0098963 | 2.749e-05 | 2014-07-08 | B | 0.0049482 | 1.3745e-05 | 2015 | 2014-07-08 | B | 9 | 0.0098963 | 2.749e-05
1 | 373609 | 2014-07-08 09:27 | 2014-07-08 10:32 | 65.0333 | 37 | 2406.2333 | 0.0073593 | 0.00011316 | NAPA ID:00192 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | U12699 | Repair damaged conductor at pole 323131. Work Location: Puketui Valley Road, Thames. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 65.0333 | 62.0333 | 2295.2333 | 0.0070106 | 0.00011301 | 2014-07-08 | B | 0.0035053 | 5.6507e-05 | 2015 | 2014-07-08 | B | 37 | 0.0070106 | 0.00011301
1 | 373608 | 2014-07-08 09:29 | 2014-07-08 11:50 | 141.05 | 9 | 1269.45 | 0.0038825 | 2.7526e-05 | NAPA ID:00191 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 776997, 776999 | Creating OMS entry for imported application. Remove trees up through 11kV lines between 11kV Poles 776997 & 776999. Work Location: Mangaeturoa North Road. Job only started at 09:29 due to faultman did not receive the switching from the S.M.C hub, supply | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 141.05 | 138.05 | 1242.45 | 0.003795 | 2.749e-05 | 2014-07-08 | B | 0.0018975 | 1.3745e-05 | 2015 | 2014-07-08 | B | 9 | 0.003795 | 2.749e-05
1 | 844680 | 2014-07-08 11:01 | 2014-07-08 16:05 | 303.8667 | 26 | 7900.5333 | 0.024163 | 7.9519e-05 | Restore Supply on Device 144 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 809639 | Faultman found a broken cross arm on pole 809639 while attending a fault call, line was isolated and cross arm and all it's hardware was changed. (Cross arm, 3 insulators, braces). | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 303.8667 | 300.8667 | 7822.5333 | 0.023893 | 7.9415e-05 | 2014-07-08 | C | 0.023893 | 7.9415e-05 | 2015 | 2014-07-08 | C | 26 | 0.023893 | 7.9415e-05
1 | 475648 | 2014-07-08 11:31 | 2014-07-08 19:54 | 503 | 1 | 503 | 0.0015384 | 3.0584e-06 | Restore Supply on Device TF5-090 | 11000 | UNPLANNED | Underground cable. | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TF5-090 | U/G cable HV fault - need to get the cable located to find the fault on the U/G cable on TX TF5-090 pole # 223385. 10:30am will need to put request 2R to get another f/man to locate and repair fault. Cable repairs completed & supply restored 19:54 | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 503 | 500 | 500 | 0.0015272 | 3.0544e-06 | 2014-07-08 | C | 0.0015272 | 3.054e-06 | 2015 | 2014-07-08 | C | 1 | 0.0015272 | 3.0544e-06
1 | 844578 | 2014-07-08 12:58 | 2014-07-08 15:22 | 144.45 | 2 | 265.85 | 0.00081308 | 6.1168e-06 | Restore Supply on Device T7/150 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | pole # 405. section fuses R48. | CHECK WITH F/MAN IF THIS FAULT WILL BE AFFECTING OTHER PPTY'S IN THIS VACINITY (844583 - UNSURE IF SHOULD BE LINKED TO THIS FAULT OR TREATED AS A SEPARATE ISSUE). section fuse open at r48- closed & all power restored hv o/h pole # p405. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 132.925 | 129.925 | 259.85 | 0.00079369 | 6.1088e-06 | 2014-07-08 | C | 0.00079369 | 6.109e-06 | 2015 | 2014-07-08 | C | 2 | 0.00079369 | 6.1088e-06
1 | 844608 | 2014-07-08 13:24 | 2014-07-08 16:09 | 164.8 | 1 | 164.8 | 0.00050403 | 3.0584e-06 | Restore Supply on Device T1/490 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | pole # p20741 | tx 514 to be replaced 09/07. Todd in control creating a new job for Tx 514 replacement. caused by unknown pole # p20741 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 164.8 | 161.8 | 161.8 | 0.00049421 | 3.0544e-06 | 2014-07-08 | C | 0.00049421 | 3.054e-06 | 2015 | 2014-07-08 | C | 1 | 0.00049421 | 3.0544e-06
1 | 844794 | 2014-07-08 15:58 | 2014-07-08 18:36 | 158.6833 | 1 | 158.6833 | 0.00048532 | 3.0584e-06 | Restore Supply on Device T2013 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2013 | Problem with geese flying into 11kV line, replaced holder and 2 x 10a fuses on one line. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 158.6833 | 155.6833 | 155.6833 | 0.00047552 | 3.0544e-06 | 2014-07-08 | C | 0.00047552 | 3.054e-06 | 2015 | 2014-07-08 | C | 1 | 0.00047552 | 3.0544e-06
1 | 860646 | 2014-07-08 21:05 | 2014-07-08 22:45 | 99.8667 | 865 | 55124.75 | 0.16859 | 0.0026455 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Coromandel CB5 |  | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 63.728 | 60.728 | 52529.75 | 0.16045 | 0.0026421 | 2014-07-08 | C | 0.16045 | 0.0026421 | 2015 | 2014-07-08 | C | 865 | 0.16045 | 0.0026421
1 | 898393 | 2014-07-08 21:17 | 2014-07-11 13:07 | 3830.4667 | 819 | 63375.15 | 0.19383 | 0.0025048 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1446 | Stacey advised needs another faultman to attend to this job. Coromandel CB5 tripped B & C Phase O/C. Line patrolled. Straightened cross arm and repaired lines @ pole T1446. Shane Walker & Justin Kerrison attended. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 77.3811 | 74.3811 | 60918.15 | 0.18607 | 0.0025016 | 2014-07-08 | C | 0.18607 | 0.0025016 | 2015 | 2014-07-08 | C | 819 | 0.18607 | 0.0025016
1 | 861985 | 2014-07-08 21:54 | 2014-07-09 00:16 | 142.0167 | 1 | 142.0167 | 0.00043435 | 3.0584e-06 | Restore Supply on Device TC4688 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TC4688 | patrolled line and found HV DDO fuses blown, spoke with control and has replaced 2x 2amp HV DDo fuses | F4 | PURIRI | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 142.0167 | 139.0167 | 139.0167 | 0.00042462 | 3.0544e-06 | 2014-07-08 | C | 0.00042462 | 3.054e-06 | 2015 | 2014-07-08 | C | 1 | 0.00042462 | 3.0544e-06
1 | 1876589 | 2014-07-08 22:40 | 2014-07-09 14:30 | 950 | 676 | 54761 | 0.16748 | 0.0020675 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | K19751 | CB1 tripped L/O. Line patrolled and tree located through line at pole K19751. Fault restored - Greg Whyte attended. | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 81.0074 | 78.0074 | 52733 | 0.16107 | 0.0020648 | 2014-07-08 | C | 0.16107 | 0.0020648 | 2015 | 2014-07-08 | C | 676 | 0.16107 | 0.0020648
1 | 865186 | 2014-07-08 23:24 | 2014-07-09 00:24 | 60.2833 | 453 | 27298.0833 | 0.083489 | 0.0013855 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB8 | Mikkelsen Road CB8 - Tripped. L/O. Line patrolled - no fault located. Report of line clashing at 4549 State Highway 26. Power restored. Hilton Gardiner attended. | F4/F5 | MOUNTAIN | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 60.2607 | 57.2607 | 25939.0833 | 0.079229 | 0.0013837 | 2014-07-08 | C | 0.079229 | 0.0013837 | 2015 | 2014-07-08 | C | 453 | 0.079229 | 0.0013837
1 | 865645 | 2014-07-08 23:56 | 2014-07-09 11:44 | 707.7667 | 580 | 73023.1667 | 0.22334 | 0.0017739 | Restore Supply on Device 9 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1487 | Parent job is 865642. CB9 tripped. Fault restoration investigation found a floating conductor. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 125.902 | 122.902 | 71283.1667 | 0.21773 | 0.0017716 | 2014-07-08 | C | 0.21773 | 0.0017716 | 2015 | 2014-07-08 | C | 580 | 0.21773 | 0.0017716
1 | 866227 | 2014-07-09 00:02 | 2014-07-09 00:24 | 22.2833 | 77 | 1715.8167 | 0.0052477 | 0.0002355 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB2, IC609 | Part of OMS Job ID 918063. CB 2 tripped during outage already underway. Affected customers between CB2 and IC609. | F4/F5 | MOUNTAIN | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 22.2833 | 19.2833 | 1484.8167 | 0.0045353 | 0.00023519 | 2014-07-09 | C | 0.0045353 | 0.00023519 | 2015 | 2014-07-09 | C | 77 | 0.0045353 | 0.00023519
1 | 2098765 | 2014-07-09 00:59 | 2014-07-09 04:53 | 234 | 249 | 49379 | 0.15102 | 0.00076155 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | W1885 | Tairua CB5 - Recloser 9170/2 Tripped - No flags. Line patrolled and branch removed from line at pole W1885. Steve Johnson attended. | F3/F4 | TAIRUA NORTH | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 198.3092 | 195.3092 | 48632 | 0.14854 | 0.00076055 | 2014-07-09 | C | 0.14854 | 0.00076055 | 2015 | 2014-07-09 | C | 249 | 0.14854 | 0.00076055
1 | 2573007 | 2014-07-09 01:41 | 2014-07-09 03:49 | 128 | 13090 | 340555 | 1.0416 | 0.040035 | Restore Supply on Device 50 | 66000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Kopu CB1092, Tairua CB60 | Line patrol required between CB 60 to ABS 3600 & ABS 3602. Line patrolled with no fault found, returned to service, Steve Johnstone attended. | F1, F2, F3 | KOPU1132-TAIRUA 66KV | TP_KOPU | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 26.0164 | 23.0164 | 301285 | 0.92025 | 0.039982 | 2014-07-09 | C | 0.92025 | 0.039982 | 2015 | 2014-07-09 | C | 13090 | 0.92025 | 0.039982
1 | 873870 | 2014-07-09 01:41 | 2014-07-09 03:51 | 130.45 | 3098 | 398095.95 | 1.2175 | 0.009475 | Restore Supply on Device 22 | 66000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Coromandel Sub | Transpower supply to Tairua, Whitianga and Coromandel substations. . Line patrol required between CB 60 to ABS 3600 & ABS 3602. Line patrolled with no fault found, returned to service, Steve Johnstone attended. | F1, F2, F3 | WHITIANGA-COROMANDEL 66KV | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 128.501 | 125.501 | 388801.95 | 1.1876 | 0.0094626 | 2014-07-09 | C | 1.1876 | 0.0094626 | 2015 | 2014-07-09 | C | 3098 | 1.1876 | 0.0094626
1 | 876969 | 2014-07-09 01:48 | 2014-07-09 02:14 | 25.9167 | 443 | 11481.0833 | 0.035114 | 0.0013549 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 25.9167 | 22.9167 | 10152.0833 | 0.031009 | 0.0013531 | 2014-07-09 | C | 0.031009 | 0.0013531 | 2015 | 2014-07-09 | C | 443 | 0.031009 | 0.0013531
1 | 879715 | 2014-07-09 01:48 | 2014-07-09 02:16 | 27.6167 | 998 | 27561.4333 | 0.084294 | 0.0030523 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB7 | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 27.6167 | 24.6167 | 24567.4333 | 0.075039 | 0.0030483 | 2014-07-09 | C | 0.075039 | 0.0030483 | 2015 | 2014-07-09 | C | 998 | 0.075039 | 0.0030483
1 | 878608 | 2014-07-09 01:48 | 2014-07-09 02:14 | 26.3333 | 1106 | 29124.6667 | 0.089076 | 0.0033826 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB 2 | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F3 | COOK DRIVE | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 26.3333 | 23.3333 | 25806.6667 | 0.078824 | 0.0033782 | 2014-07-09 | C | 0.078824 | 0.0033782 | 2015 | 2014-07-09 | C | 1106 | 0.078824 | 0.0033782
1 | 877413 | 2014-07-09 01:48 | 2014-07-09 02:13 | 25.25 | 1194 | 30148.5 | 0.092207 | 0.0036518 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 6 | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F3 | BUFFALO BEACH | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 25.25 | 22.25 | 26566.5 | 0.081145 | 0.003647 | 2014-07-09 | C | 0.081145 | 0.003647 | 2015 | 2014-07-09 | C | 1194 | 0.081145 | 0.003647
1 | 884029 | 2014-07-09 01:48 | 2014-07-09 02:16 | 28.4667 | 1077 | 30658.6 | 0.093767 | 0.0032939 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | whitianga | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F3 | JOAN GASKELL DR | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 28.4667 | 25.4667 | 27427.6 | 0.083776 | 0.0032896 | 2014-07-09 | C | 0.083776 | 0.0032896 | 2015 | 2014-07-09 | C | 1077 | 0.083776 | 0.0032896
1 | 882478 | 2014-07-09 01:48 | 2014-07-09 02:16 | 27.9667 | 1550 | 43348.3333 | 0.13258 | 0.0047406 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND |  | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 27.9667 | 24.9667 | 38698.3333 | 0.1182 | 0.0047344 | 2014-07-09 | C | 0.1182 | 0.0047344 | 2015 | 2014-07-09 | C | 1550 | 0.1182 | 0.0047344
1 | 880714 | 2014-07-09 01:48 | 2014-07-09 02:15 | 27.1667 | 1763 | 47894.8333 | 0.14648 | 0.005392 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 66 kV Network | Whitianga Substation affected by a tripping on Tairua/Kopu Substation. CB1092/50 tripped. Line patrolled - no fault located. | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 27.1667 | 24.1667 | 42605.8333 | 0.13014 | 0.0053849 | 2014-07-09 | C | 0.13014 | 0.0053849 | 2015 | 2014-07-09 | C | 1763 | 0.13014 | 0.0053849
1 | 893300 | 2014-07-09 06:50 | 2014-07-09 09:43 | 172.4167 | 1 | 172.4167 | 0.00052732 | 3.0584e-06 | Restore Supply on Device TC5794 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FC2327 | 2x hv o/h 20amp ddo fuse (2 of 3). Fuse # fc2327 pole # 389838 caused by wind f/man calling svs hub to be onsited | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 172.4167 | 169.4167 | 169.4167 | 0.00051747 | 3.0544e-06 | 2014-07-09 | C | 0.00051747 | 3.054e-06 | 2015 | 2014-07-09 | C | 1 | 0.00051747 | 3.0544e-06
1 | 897581 | 2014-07-09 08:49 | 2014-07-09 09:19 | 30 | 348 | 10440 | 0.03193 | 0.0010643 | Restore Supply on Device 335 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP77 | Job is complete but cannot get it to restore so cannot complete it. Crew was de-assigned in order for job to be closed, crew status before de-assign was Assigned. Replace Fuse FP77. Materials used: 3 x Fuse Carrier Bases and Leader. Shane Walker attended | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 9396 | 0.028699 | 0.0010629 | 2014-07-09 | C | 0.028699 | 0.0010629 | 2015 | 2014-07-09 | C | 348 | 0.028699 | 0.0010629
1 | 898299 | 2014-07-09 08:59 | 2014-07-10 12:54 | 1675.1833 | 4 | 6412.9 | 0.019613 | 1.2234e-05 | Restore Supply on Device TC4007 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4007 | 12.52pm Stacey advised that HIlton had cleared this job off with control already.. I called HIlton to get clearance details 2x 10amp fuses replaced | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1603.225 | 1600.225 | 6400.9 | 0.019551 | 1.2218e-05 | 2014-07-09 | C | 0.019551 | 1.2218e-05 | 2015 | 2014-07-09 | C | 4 | 0.019551 | 1.2218e-05
1 | 373634 | 2014-07-09 09:00 | 2014-07-09 15:15 | 374.75 | 6 | 2248.5 | 0.0068769 | 1.8351e-05 | NAPA ID:00219 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W2275 | Outage steps in OMS Job ID 898303. Work Order 10137914. Replace transformer structure W2275 - Pukekino Road. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 374.75 | 371.75 | 2230.5 | 0.0068129 | 1.8327e-05 | 2014-07-09 | B | 0.0034064 | 9.163e-06 | 2015 | 2014-07-09 | B | 6 | 0.0068129 | 1.8327e-05
1 | 899291 | 2014-07-09 09:31 | 2014-07-09 12:56 | 205.35 | 242 | 17916.5333 | 0.054796 | 0.00074014 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | C2887 | CB2 tripped. Line patrolled - delays in restoration due to access issues. | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 74.0353 | 71.0353 | 17190.5333 | 0.052507 | 0.00073917 | 2014-07-09 | C | 0.052507 | 0.00073917 | 2015 | 2014-07-09 | C | 242 | 0.052507 | 0.00073917
1 | 899604 | 2014-07-09 09:42 | 2014-07-09 20:27 | 645.45 | 1 | 645.45 | 0.0019741 | 3.0584e-06 | Restore Supply on Device TP1175 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1175 - no pole number on pole | Check on map as there's another job 911208 on next tx - Greg advised that job 911208 would not be affected by this job - have taken this parent job off. replaced 1x hv link at fp65 | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 645.45 | 642.45 | 642.45 | 0.0019623 | 3.0544e-06 | 2014-07-09 | C | 0.0019623 | 3.054e-06 | 2015 | 2014-07-09 | C | 1 | 0.0019623 | 3.0544e-06
1 | 900512 | 2014-07-09 11:07 | 2014-07-09 20:24 | 557.15 | 1 | 557.15 | 0.001704 | 3.0584e-06 | Restore Supply on Device TC5129 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5129 | Replaced blown HV fuses 3A x 2. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 557.15 | 554.15 | 554.15 | 0.0016926 | 3.0544e-06 | 2014-07-09 | C | 0.0016926 | 3.054e-06 | 2015 | 2014-07-09 | C | 1 | 0.0016926 | 3.0544e-06
1 | 931084 | 2014-07-09 12:13 | 2014-07-10 16:50 | 1717.4833 | 2 | 1758.85 | 0.0053793 | 6.1168e-06 | Restore Supply on Device TC3378 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | c13170 | tx fuse 1x 3amp ddo Tree interfering with line | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 879.425 | 876.425 | 1752.85 | 0.0053539 | 6.1088e-06 | 2014-07-09 | C | 0.0053539 | 6.109e-06 | 2015 | 2014-07-09 | C | 2 | 0.0053539 | 6.1088e-06
1 | 861512 | 2014-07-09 13:27 | 2014-07-09 14:10 | 43 | 1 | 43 | 0.00013151 | 3.0584e-06 | Restore Supply on Device TC1653 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13620 | Hilton advises unsafe to climb pole in current winds, customer has been advised and is happy to wait till morning. Repaired existing jumper. Caused by high wind. Pole #C13620. ****Cannot Close out JOB as Hilton Gardener and Josh Reid cannot be deassigned | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 40 | 0.00012218 | 3.0544e-06 | 2014-07-09 | C | 0.00012218 | 3.054e-06 | 2015 | 2014-07-09 | C | 1 | 0.00012218 | 3.0544e-06
1 | 2870311 | 2014-07-09 14:10 | 2014-07-09 15:08 | 58 | 1020 | 56736 | 0.17352 | 0.0031196 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2663 | Replaces OMS Job ID 902795 which was inadvertently cancelled. Parent Job ID 897549. Whitianga CB6 Buffalo Beach. Repair jumper at ABS 2663. Stephen Johnson attended. | F3 | BUFFALO BEACH | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 55.6235 | 52.6235 | 53676 | 0.16395 | 0.0031155 | 2014-07-09 | C | 0.16395 | 0.0031155 | 2015 | 2014-07-09 | C | 1020 | 0.16395 | 0.0031155
1 | 904016 | 2014-07-09 15:08 | 2014-07-12 01:18 | 3489.2986 | 1 | 3489.3 | 0.010672 | 3.0584e-06 | Restore Supply on Device TC3658 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | transformer TC3658 | Replaced 1 x 3amp H/V fuse | F4/F5 | MOUNTAIN | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 3489.3 | 3486.3 | 3486.3 | 0.010649 | 3.0544e-06 | 2014-07-09 | C | 0.010649 | 3.054e-06 | 2015 | 2014-07-09 | C | 1 | 0.010649 | 3.0544e-06
1 | 904634 | 2014-07-09 16:20 | 2014-07-09 16:46 | 25.5667 | 288 | 5725.9 | 0.017512 | 0.00088083 | Restore Supply on Device C945 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C945 | Gladstone C945 tripped - No Flags. Line patrolled and sectionalised with no cause of fault located. Supply restored. Brad Keating attended. | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 19.8816 | 16.8816 | 4861.9 | 0.01485 | 0.00087967 | 2014-07-09 | C | 0.01485 | 0.00087967 | 2015 | 2014-07-09 | C | 288 | 0.01485 | 0.00087967
1 | 4219874 | 2014-07-09 16:39 | 2014-07-09 19:09 | 150 | 798 | 63053 | 0.19284 | 0.0024406 | Restore Supply on Device 5916 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB S51 | CB S51 tripped line was patrolled and sectionalised and no fault was found. Restaged outage | F4 | CLOTON RD WEST | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 79.0138 | 76.0138 | 60659 | 0.18528 | 0.0024374 | 2014-07-09 | C | 0.18528 | 0.0024374 | 2015 | 2014-07-09 | C | 798 | 0.18528 | 0.0024374
1 | 914072 | 2014-07-09 18:15 | 2014-07-09 20:09 | 113.75 | 107 | 9225.7333 | 0.028216 | 0.00032725 | Restore Supply on Device 4445 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4445 | Recloser 4445/2 tripped on O/C B-phase line was patrolled and sectionalised and no fault was found. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 86.2218 | 83.2218 | 8904.7333 | 0.027199 | 0.00032682 | 2014-07-09 | C | 0.027199 | 0.00032682 | 2015 | 2014-07-09 | C | 107 | 0.027199 | 0.00032682
1 | 929987 | 2014-07-09 20:40 | 2014-07-11 10:52 | 2292.0833 | 139 | 35951.8 | 0.10996 | 0.00042512 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | FP1507 | Trees over line beyond Fuses FP1507. Trees could not be removed so Fuses Disconnected for Safety until tree works could be carried out. Restoration completed 10 July 2015. | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 258.646 | 255.646 | 35534.8 | 0.10854 | 0.00042456 | 2014-07-09 | C | 0.10854 | 0.00042457 | 2015 | 2014-07-09 | C | 139 | 0.10854 | 0.00042456
1 | 918063 | 2014-07-09 21:32 | 2014-07-10 22:47 | 1515.2167 | 87 | 23038.8667 | 0.070463 | 0.00026608 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C648 | 2nd response required to repair floating conductor and replace insulator on pole C648 07:00 Dave Davenport rang to find out why Silver Fern farms were left off over night. Contacted SMC who dispatched a Waihi Faultman to site. After further discussions G | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 264.8146 | 261.8146 | 22777.8667 | 0.069573 | 0.00026573 | 2014-07-09 | C | 0.069573 | 0.00026574 | 2015 | 2014-07-09 | C | 87 | 0.069573 | 0.00026573
1 | 1874915 | 2014-07-09 22:19 | 2014-07-10 01:05 | 166 | 1425 | 73580 | 0.22504 | 0.0043583 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9228 | Fault restoration. DNO on Recloser & Bypass ABS 9228. | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.6351 | 48.6351 | 69305 | 0.21169 | 0.0043526 | 2014-07-09 | C | 0.21169 | 0.0043526 | 2015 | 2014-07-09 | C | 1425 | 0.21169 | 0.0043526
1 | 919161 | 2014-07-10 00:33 | 2014-07-10 01:33 | 59.7667 | 107 | 5655.3 | 0.017296 | 0.00032725 | Restore Supply on Device 4445 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4445 | Recloser 4445 tripped on O/C b-phase line was patrolled and sectionalised no fault found only trips when it rains. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 52.8533 | 49.8533 | 5334.3 | 0.016293 | 0.00032682 | 2014-07-10 | C | 0.016293 | 0.00032682 | 2015 | 2014-07-10 | C | 107 | 0.016293 | 0.00032682
1 | 922531 | 2014-07-10 07:53 | 2014-07-10 10:59 | 186.1 | 835 | 51157.8 | 0.15646 | 0.0025538 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 209008 | Omokoroa CB3 tripped L/O O/C A, B Phase. Auto reclose disabled. Line patrolled - conductor down at pole 209008. Note: CB4 backfeeding and also auto reclosed during this outage - refer to OMS Job ID 925069. Dennis Ngatai attended. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 61.2668 | 58.2668 | 48652.8 | 0.14861 | 0.0025504 | 2014-07-10 | C | 0.14861 | 0.0025504 | 2015 | 2014-07-10 | C | 835 | 0.14861 | 0.0025504
1 | 373652 | 2014-07-10 08:30 | 2014-07-10 12:03 | 213 | 21 | 4473 | 0.01368 | 6.4227e-05 | NAPA ID:00239 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 1023 | Outage Steps in OMS Job ID 924765. Trimming trees near 11kV pole numbers 801228 and 810229. Works Location: Turakina Valley Road, Hunterville. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 213 | 210 | 4410 | 0.01347 | 6.4143e-05 | 2014-07-10 | B | 0.006735 | 3.2071e-05 | 2015 | 2014-07-10 | B | 21 | 0.01347 | 6.4143e-05
1 | 924879 | 2014-07-10 09:16 | 2014-07-10 13:53 | 276.6167 | 2 | 553.2333 | 0.001692 | 6.1168e-06 | Restore Supply on Device TP1191 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | F0475 | Crew assignment is jammed and will not let the job close. Job is complete as per close out codes. Replace 11kV cross arms - whole assembly. 3 x 3 Amp Link. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 276.6167 | 273.6167 | 547.2333 | 0.0016715 | 6.1088e-06 | 2014-07-10 | C | 0.0016715 | 6.109e-06 | 2015 | 2014-07-10 | C | 2 | 0.0016715 | 6.1088e-06
1 | 924926 | 2014-07-10 09:34 | 2014-07-10 10:12 | 38.1833 | 66 | 2520.1 | 0.0077075 | 0.00020186 | Restore Supply on Device E67 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | NA | No Paper Work Found - Review at QA. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 38.1833 | 35.1833 | 2322.1 | 0.0070927 | 0.00020159 | 2014-07-10 | C | 0.0070927 | 0.00020159 | 2015 | 2014-07-10 | C | 66 | 0.0070927 | 0.00020159
1 | 926282 | 2014-07-10 09:35 | 2014-07-14 15:15 | 6099.8372 | 2 | 7841.5833 | 0.023983 | 6.1168e-06 | Restore Supply on Device TC4487 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 1007 KENNEDY BAY ROAD - Coromandel. TX T4487 | 2 OF 2 HV TX FUSES 3AMP DDO . POLE # UNKNOWN TX T4487 CAUSED BY WIND. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 3920.7917 | 3917.7917 | 7835.5833 | 0.023933 | 6.1088e-06 | 2014-07-10 | C | 0.023933 | 6.109e-06 | 2015 | 2014-07-10 | C | 2 | 0.023933 | 6.1088e-06
1 | 373656 | 2014-07-10 09:48 | 2014-07-10 15:53 | 365 | 28 | 5839 | 0.017858 | 8.5636e-05 | NAPA ID:00243 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | Creating OMS entry for imported application. Replace 37 HV cross arms, 2 x HV poles, 2 x transformer changers. Work Location: Lockwood Road. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 208.5357 | 205.5357 | 5755 | 0.017578 | 8.5524e-05 | 2014-07-10 | B | 0.0087891 | 4.2762e-05 | 2015 | 2014-07-10 | B | 28 | 0.017578 | 8.5524e-05
1 | 926624 | 2014-07-10 11:08 | 2014-07-10 11:39 | 31 | 50 | 1550 | 0.0047406 | 0.00015292 | Restore Supply on Device P20 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P20672 | No Power. Line Patrolled. Floating Conductor Located at Pole P20672. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 31 | 28 | 1400 | 0.0042762 | 0.00015272 | 2014-07-10 | C | 0.0042762 | 0.00015272 | 2015 | 2014-07-10 | C | 50 | 0.0042762 | 0.00015272
1 | 926991 | 2014-07-10 11:16 | 2014-07-10 15:08 | 232.2 | 2 | 464.4 | 0.0014203 | 6.1168e-06 | Restore Supply on Device 10136 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P372534 | Floating conductor at pole P372534. Jeff Roberts attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 232.2 | 229.2 | 458.4 | 0.0014001 | 6.1088e-06 | 2014-07-10 | C | 0.0014001 | 6.109e-06 | 2015 | 2014-07-10 | C | 2 | 0.0014001 | 6.1088e-06
1 | 4127484 | 2014-07-10 11:57 | 2014-07-10 14:36 | 159 | 868 | 38567 | 0.11795 | 0.0026547 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789727 | Loss of OMS Number 929841, required this manual job to be created. NOTE: Powerco had to progress fault response after numerous calls to SMC to progress. CB 4 tripped O/C L/O.(note this has the three feeders connected via Sw/gear 4537 1, 2, 3) so lost Tai | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 44.432 | 41.432 | 35963 | 0.10985 | 0.0026512 | 2014-07-10 | C | 0.10985 | 0.0026512 | 2015 | 2014-07-10 | C | 868 | 0.10985 | 0.0026512
1 | 929895 | 2014-07-10 12:22 | 2014-07-10 17:05 | 282.1333 | 1 | 282.1333 | 0.00086288 | 3.0584e-06 | Restore Supply on Device TC2643 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2643 | hafw - 1x 6amp fuse | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 282.1333 | 279.1333 | 279.1333 | 0.00085259 | 3.0544e-06 | 2014-07-10 | C | 0.00085259 | 3.054e-06 | 2015 | 2014-07-10 | C | 1 | 0.00085259 | 3.0544e-06
1 | 373663 | 2014-07-10 13:01 | 2014-07-10 16:01 | 180 | 20 | 3600 | 0.01101 | 6.1168e-05 | NAPA ID:00250 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | East Road Substation - Stratford | Creating OMS entry for imported application. Change Fuse Carriers and Commission Regulator 8996, East Road - Stratford. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 3540 | 0.010813 | 6.1088e-05 | 2014-07-10 | B | 0.0054063 | 3.0544e-05 | 2015 | 2014-07-10 | B | 20 | 0.010813 | 6.1088e-05
1 | 931037 | 2014-07-10 13:37 | 2014-07-10 16:03 | 145.9167 | 14 | 561.9167 | 0.0017186 | 4.2818e-05 | Restore Supply on Device FC1492 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 854061 | Repaired jumper at pole 854061. No comms in area - own SIS & A/P. | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 40.1369 | 37.1369 | 519.9167 | 0.001588 | 4.2762e-05 | 2014-07-10 | C | 0.001588 | 4.2762e-05 | 2015 | 2014-07-10 | C | 14 | 0.001588 | 4.2762e-05
1 | 930318 | 2014-07-10 14:00 | 2014-07-10 19:24 | 323.6167 | 10 | 1529.6167 | 0.0046782 | 3.0584e-05 | Restore Supply on Device TP1839 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 380930 | Replace king bolt in cross arm at pole 380930 | F3/F4 | ASHWORTH ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 152.9617 | 149.9617 | 1499.6167 | 0.0045805 | 3.0544e-05 | 2014-07-10 | C | 0.0045805 | 3.0544e-05 | 2015 | 2014-07-10 | C | 10 | 0.0045805 | 3.0544e-05
1 | 933001 | 2014-07-10 18:19 | 2014-07-11 13:44 | 1164.4667 | 241 | 27777.4167 | 0.084955 | 0.00073708 | Restore Supply on Device 4141 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812154 | 2 Faults found, Fault 1 Damaged Conduct at pole 812154 repaired using 1 x Sleeve Fault 2 at Pole 812153 broken binder repaired using 1x binder attended by Kevin Anderson | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 115.259 | 112.259 | 27054.4167 | 0.082636 | 0.00073612 | 2014-07-10 | C | 0.082636 | 0.00073612 | 2015 | 2014-07-10 | C | 241 | 0.082636 | 0.00073612
1 | 934236 | 2014-07-11 01:29 | 2014-07-11 04:46 | 196.5333 | 420 | 34496.3833 | 0.1055 | 0.0012845 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758080 | CB 6 tripped on E/F line was sectionalised and patrolled and a floating wire was found at pole 758080, line was isolated at ABS's 407 and 421, 3 x binders were replaced and 1 phase was re-sleeved, 1 metre on conductor was used. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 82.1342 | 79.1342 | 33236.3833 | 0.10152 | 0.0012829 | 2014-07-11 | C | 0.10152 | 0.0012829 | 2015 | 2014-07-11 | C | 420 | 0.10152 | 0.0012829
1 | 373680 | 2014-07-11 09:03 | 2014-07-11 10:00 | 56.5667 | 235 | 13293.1667 | 0.040656 | 0.00071873 | NAPA ID:00270 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | T6/634 | Creating OMS entry for imported application. Isolate Transformer T6/634 for repair to LV Fuses and burnt Cables. Work Location: Acacia Street, Palmerston North. | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56.5667 | 53.5667 | 12588.1667 | 0.03845 | 0.00071779 | 2014-07-11 | B | 0.019225 | 0.0003589 | 2015 | 2014-07-11 | B | 235 | 0.03845 | 0.00071779
1 | 956060 | 2014-07-11 10:02 | 2014-07-11 12:56 | 174.4167 | 24 | 4186 | 0.012803 | 7.3402e-05 | Restore Supply on Device FP1355 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1355 |  | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 174.4167 | 171.4167 | 4114 | 0.012566 | 7.3306e-05 | 2014-07-11 | C | 0.012566 | 7.3306e-05 | 2015 | 2014-07-11 | C | 24 | 0.012566 | 7.3306e-05
1 | 956234 | 2014-07-11 12:09 | 2014-07-11 14:29 | 139.9167 | 1 | 139.9167 | 0.00042792 | 3.0584e-06 | Restore Supply on Device TC4248 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | FP2297 |  | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 139.9167 | 136.9167 | 136.9167 | 0.0004182 | 3.0544e-06 | 2014-07-11 | C | 0.0004182 | 3.054e-06 | 2015 | 2014-07-11 | C | 1 | 0.0004182 | 3.0544e-06
1 | 955802 | 2014-07-11 12:09 | 2014-07-11 13:52 | 103.0333 | 13 | 1339.4333 | 0.0040966 | 3.9759e-05 | Restore Supply on Device X1311 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 897 | Initial call was for part power. Onsite - Nev advised 11kv jumper burnt off. - advised Nev to contact Control about this. Jumper For Fuses 897 burnt off - Isolated ABS 1065 & ABS 1428 - Back feed installed via ABS 1428 - Jumper Repaired & Feeder returne | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 103.0333 | 100.0333 | 1300.4333 | 0.0039721 | 3.9708e-05 | 2014-07-11 | C | 0.0039721 | 3.9708e-05 | 2015 | 2014-07-11 | C | 13 | 0.0039721 | 3.9708e-05
1 | 956851 | 2014-07-11 15:33 | 2014-07-13 19:07 | 3094.2833 | 6 | 6584.2833 | 0.020138 | 1.8351e-05 | Restore Supply on Device TC1-001 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1-001 | Blown transformer, all isolated. to be replaced tonight, putting into 2FR for extra crew to attend. 956732. 956955. Marcia from Trustpower , re when will be repaired, too dangerous to repair suspect may be Monday, as no as well as no staff. Transformer T | F4 | KATIKATI | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 1097.3806 | 1094.3806 | 6566.2833 | 0.020056 | 1.8327e-05 | 2014-07-11 | C | 0.020056 | 1.8327e-05 | 2015 | 2014-07-11 | C | 6 | 0.020056 | 1.8327e-05
1 | 956839 | 2014-07-11 15:50 | 2014-07-11 18:22 | 152 | 5 | 760 | 0.0023244 | 1.5292e-05 | Restore Supply on Device TC946 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC946 | Change faulty 50 kvA transformer. Own AP/Isolation. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 152 | 149 | 745 | 0.0022755 | 1.5272e-05 | 2014-07-11 | C | 0.0022755 | 1.5272e-05 | 2015 | 2014-07-11 | C | 5 | 0.0022755 | 1.5272e-05
1 | 956609 | 2014-07-11 15:56 | 2014-07-11 16:12 | 16.15 | 16 | 258.4 | 0.0007903 | 4.8935e-05 | Restore Supply on Device T7445 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714540 | Cross arm on Pole 714540 found on angle due to bolt missing - Isolated at Fuses TA989 - Bolt Replaced - attended by Kain MacKay. | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 16.15 | 13.15 | 210.4 | 0.00064265 | 4.8871e-05 | 2014-07-11 | C | 0.00064265 | 4.8871e-05 | 2015 | 2014-07-11 | C | 16 | 0.00064265 | 4.8871e-05
1 | 956896 | 2014-07-11 17:17 | 2014-07-11 23:54 | 396.85 | 10 | 396.85 | 0.0012137 | 3.0584e-05 | Restore Supply on Device T8/4 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T8/4 |  | F3 | EKETAHUNA | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39.685 | 36.685 | 366.85 | 0.0011205 | 3.0544e-05 | 2014-07-11 | C | 0.0011205 | 3.0544e-05 | 2015 | 2014-07-11 | C | 10 | 0.0011205 | 3.0544e-05
1 | 956946 | 2014-07-11 18:09 | 2014-07-11 23:32 | 322.6333 | 3 | 322.6333 | 0.00098675 | 9.1753e-06 | Restore Supply on Device T5/62 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/62 |  | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107.5444 | 104.5444 | 313.6333 | 0.00095797 | 9.1633e-06 | 2014-07-11 | C | 0.00095797 | 9.163e-06 | 2015 | 2014-07-11 | C | 3 | 0.00095797 | 9.1633e-06
1 | 960018 | 2014-07-11 18:44 | 2014-07-12 13:22 | 1118.1167 | 23 | 8148.2167 | 0.024921 | 7.0344e-05 | Restore Supply on Device FP1355 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | FP1355 | This is the Parent job of 956982 that has the crews attached already. Tree through lines will be attended to at 0900. Materials Used: 20M Spans, 6 Sleeves, Clamps. NDR to follow on Monday. *Cannot close out as Parent job is stuck, escalated to Drew to s | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 354.2703 | 351.2703 | 8079.2167 | 0.024677 | 7.0252e-05 | 2014-07-11 | C | 0.024677 | 7.0252e-05 | 2015 | 2014-07-11 | C | 23 | 0.024677 | 7.0252e-05
1 | 957144 | 2014-07-11 21:30 | 2014-07-12 06:59 | 568.8 | 1 | 568.8 | 0.0017396 | 3.0584e-06 | Restore Supply on Device TD2-072 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | transformer TD2 072 | Replace blown 3A H/V fuse | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 568.8 | 565.8 | 565.8 | 0.0017282 | 3.0544e-06 | 2014-07-11 | C | 0.0017282 | 3.054e-06 | 2015 | 2014-07-11 | C | 1 | 0.0017282 | 3.0544e-06
1 | 474735 | 2014-07-12 09:01 | 2014-07-12 11:47 | 165.55 | 16 | 2648.8 | 0.0081011 | 4.8935e-05 | NAPA ID:00705 TP_LINTON GXP > TURITEA SUB > MASSEY | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | H25 | Approved. Replace 11kV ABS H25 and stay wires - straighten pole. Work Location: Tennant Drive, Palmerston North. Work Order 10144259. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 165.55 | 162.55 | 2600.8 | 0.0079439 | 4.8871e-05 | 2014-07-12 | B | 0.003972 | 2.4435e-05 | 2015 | 2014-07-12 | B | 16 | 0.0079439 | 4.8871e-05
1 | 2678753 | 2014-07-12 10:06 | 2014-07-12 10:17 | 11 | 10108 | 53445 | 0.16346 | 0.030915 | Restore Supply on Device Z140 | 33000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | Keith St Substation | Keith Street CB Z180, Z170, Z140, Inc 2. During planned maintenace on 1/2 of the Keith Street substation Bus - tripping occurred on the non-isolated 1/2 of the bus. Bus Z1 Protection Failure. | F1, F2, F3 | EP WEST 33KV | TP_BUNNYTHORPE | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 5.2874 | 2.2874 | 23121 | 0.070621 | 0.030874 | 2014-07-12 | C | 0.070621 | 0.030874 | 2015 | 2014-07-12 | C | 10108 | 0.070621 | 0.030874
1 | 373686 | 2014-07-12 10:25 | 2014-07-13 22:29 | 2163.6167 | 1 | 2163.6167 | 0.0066173 | 3.0584e-06 | NAPA ID:00276 TP_BUNNYTHORPE GXP > KEITH ST SUB | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Keith St Substation | Relay Firmware Upgrade at Keith St Substation. No Loss of Supply. | F2 | MAIN ST 23 | MAIN ST SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 2163.6167 | 2160.6167 | 2160.6167 | 0.0065994 | 3.0544e-06 | 2014-07-12 | B | 0.0032997 | 1.527e-06 | 2015 | 2014-07-12 | B | 1 | 0.0065994 | 3.0544e-06
1 | 968621 | 2014-07-12 16:08 | 2014-07-12 19:01 | 173 | 729 | 42892 | 0.13118 | 0.0022296 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | O12829 | At 16:08 Kerepehi Sub, CB 6 Ngatea Feeder, Tripped E/F, O/C A,B,C Phases, L/O. Faultmen Dispatched. Line Sectionalised. Backfeeds supplied from KPE 3 & KPE 1. Found broken insulator at Pole O12829. Lines Isolated at ABS 471 & 2134. Permit issued & repairs | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 58.8368 | 55.8368 | 40705 | 0.12433 | 0.0022267 | 2014-07-12 | C | 0.12433 | 0.0022267 | 2015 | 2014-07-12 | C | 729 | 0.12433 | 0.0022267
1 | 973583 | 2014-07-12 19:24 | 2014-07-12 22:06 | 162.2167 | 3606 | 85278.3 | 0.26082 | 0.011029 | Restore Supply on Device 1122 | 33000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 855791 | Te Matai CB1122 Tripped B Phase O/C. Line patrolled. Bark found on lines at pole 855791. Ted Glasgow attended. | F1, F2, F3 | TE MATAI1122-PONGAKAWA2007 33KV | TP_TE MATAI | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 23.649 | 20.649 | 74460.3 | 0.22743 | 0.011014 | 2014-07-12 | C | 0.22743 | 0.011014 | 2015 | 2014-07-12 | C | 3606 | 0.22743 | 0.011014
1 | 978944 | 2014-07-13 00:40 | 2014-07-13 10:05 | 564.8 | 3 | 1040.3167 | 0.0031817 | 9.1753e-06 | Restore Supply on Device T5/65 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T5/65 | Recloser N21 had tripped. Closed back in by field operator. | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 346.7722 | 343.7722 | 1031.3167 | 0.0031501 | 9.1633e-06 | 2014-07-13 | C | 0.0031501 | 9.163e-06 | 2015 | 2014-07-13 | C | 3 | 0.0031501 | 9.1633e-06
1 | 980022 | 2014-07-13 02:33 | 2014-07-13 06:09 | 216 | 569 | 29800 | 0.091141 | 0.0017402 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 75702 | Bell Block CB 8 lines down at pole 75702 4 sleeves <1 span 2 phases. | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 52.3726 | 49.3726 | 28093 | 0.085808 | 0.001738 | 2014-07-13 | C | 0.085808 | 0.001738 | 2015 | 2014-07-13 | C | 569 | 0.085808 | 0.001738
1 | 982267 | 2014-07-13 05:27 | 2014-07-13 08:29 | 181.7 | 240 | 24862.6 | 0.07604 | 0.00073402 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | MA411 | Faulty ABS MA481. Jumpers removed and backfeed installed. ABS still to be repaired under DNO | F4 | OKAIAWA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 103.5942 | 100.5942 | 24142.6 | 0.073742 | 0.00073306 | 2014-07-13 | C | 0.073742 | 0.00073306 | 2015 | 2014-07-13 | C | 240 | 0.073742 | 0.00073306
1 | 978155 | 2014-07-13 08:12 | 2014-07-13 09:14 | 61.5833 | 18 | 1108.5 | 0.0033903 | 5.5052e-05 | Restore Supply on Device TP2254 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 9579/2 | 2x HV Fuses Blown. Line Patrolled. Cause - Bird Strike (Bird remains found). Reloaded, Relivened. All Power Restored. Clint Johnstone Attended. Outage included within OMS Job ID 983045. | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 61.5833 | 58.5833 | 1054.5 | 0.0032209 | 5.498e-05 | 2014-07-13 | C | 0.0032209 | 5.498e-05 | 2015 | 2014-07-13 | C | 18 | 0.0032209 | 5.498e-05
1 | 983345 | 2014-07-13 14:21 | 2014-07-13 15:38 | 77.1333 | 360 | 21298.2667 | 0.065139 | 0.001101 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6777/6 | Line Patrol and Sectionalising carried out after CB 6 tripped on E/F | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 59.1619 | 56.1619 | 20218.2667 | 0.061755 | 0.0010996 | 2014-07-13 | C | 0.061755 | 0.0010996 | 2015 | 2014-07-13 | C | 360 | 0.061755 | 0.0010996
1 | 373699 | 2014-07-14 09:32 | 2014-07-14 15:18 | 346 | 13 | 4498 | 0.013757 | 3.9759e-05 | NAPA ID:00292 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | Change 1 x HV Xarms, 9 x HV poles, 6 x DDOs. Isolation points: ABS B5, Temp links 76. Work Location: Lockwood Road. Work Order 10156813. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 346 | 343 | 4459 | 0.01362 | 3.9708e-05 | 2014-07-14 | B | 0.0068098 | 1.9854e-05 | 2015 | 2014-07-14 | B | 13 | 0.01362 | 3.9708e-05
1 | 984579 | 2014-07-14 09:47 | 2014-07-14 13:03 | 195.9333 | 8 | 1567.4667 | 0.004794 | 2.4467e-05 | Restore Supply on Device V75 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | V75 | This outage was also under OMS 373704 which i will cancel. JF Restrain 33kV Conductor on Pole 373072 on Rimu Road. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 195.9333 | 192.9333 | 1543.4667 | 0.0047144 | 2.4435e-05 | 2014-07-14 | C | 0.0047144 | 2.4435e-05 | 2015 | 2014-07-14 | C | 8 | 0.0047144 | 2.4435e-05
1 | 985873 | 2014-07-14 19:10 | 2014-07-15 12:19 | 1029.75 | 1494 | 278236.3333 | 0.85096 | 0.0045693 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T13334 | Sectionalised and found two faults between ABS IC368 & IC380. Rest of area backfed. Isolated area left off over night until patrol carried out during daylight. Repaired conductor pulled through dead end at pole 854054 & line down at pole T13334. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 186.2358 | 183.2358 | 273754.3333 | 0.83616 | 0.0045633 | 2014-07-14 | C | 0.83616 | 0.0045633 | 2015 | 2014-07-14 | C | 1494 | 0.83616 | 0.0045633
1 | 384819 | 2014-07-15 09:16 | 2014-07-15 17:47 | 510.1833 | 12 | 6122.2 | 0.018724 | 3.6701e-05 | NAPA ID:00503 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 725796, 725868 | First application into Napa. AP to climb and prune trees for 11kV line construction - working between 11kV pole numbers 725796 & 725868. Work Location: Tangahoe Valley Road | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 510.1833 | 507.1833 | 6086.2 | 0.01859 | 3.6653e-05 | 2014-07-15 | B | 0.0092949 | 1.8327e-05 | 2015 | 2014-07-15 | B | 12 | 0.01859 | 3.6653e-05
1 | 373697 | 2014-07-15 09:24 | 2014-07-15 11:51 | 147.4333 | 6 | 884.6 | 0.0027055 | 1.8351e-05 | NAPA ID:00289 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses TC 2759 | Alternate Date Applied: Replace 400V cross arms on transformer structure. Work Location: Paparaka Road, Tirau. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 147.4333 | 144.4333 | 866.6 | 0.002647 | 1.8327e-05 | 2014-07-15 | B | 0.0013235 | 9.163e-06 | 2015 | 2014-07-15 | B | 6 | 0.002647 | 1.8327e-05
1 | 2514156 | 2014-07-15 10:02 | 2014-07-15 10:45 | 43 | 5222 | 185588 | 0.56761 | 0.015971 | Restore Supply on Device C805 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 826353 | CB 2212 tripped on O/C, CB C805 tripped on O/C, CB C869 tripped on A and C phase O/C flags. Faultman reported pole 326353 was on fire, the king pin bolt had broken and caused the cross arm to fall causing the pole fire. Line was isolated at ABS 3124, 3125 | F1, F2, F3 | TE ORE ORE 33KV | TP_MASTERTON | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 35.5396 | 32.5396 | 169922 | 0.51901 | 0.01595 | 2014-07-15 | C | 0.51901 | 0.01595 | 2015 | 2014-07-15 | C | 5222 | 0.51901 | 0.01595
1 | 1002435 | 2014-07-15 11:40 | 2014-07-15 16:52 | 311.75 | 31 | 9664.25 | 0.029557 | 9.4811e-05 | Restore Supply on Device IC1204 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | C2136 | Emergency shutdown - broken crossarm at pole C2136 - HV conductors low across State Highway. Job completed & supply restored at 16:52. | F1 | TATUANUI | FARMER ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 311.75 | 308.75 | 9571.25 | 0.029235 | 9.4687e-05 | 2014-07-15 | C | 0.029235 | 9.4687e-05 | 2015 | 2014-07-15 | C | 31 | 0.029235 | 9.4687e-05
1 | 1006696 | 2014-07-15 12:41 | 2014-07-15 14:41 | 120.15 | 2 | 240.3 | 0.00073494 | 6.1168e-06 | Restore Supply on Device M1033 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | M1033 | TX REPLACED TX M1033. APPROX 2MTRS LV / HV CABLE & 7 SLEEVES. 6AMP HV X3 (FUSE ELEMENTS ONLY). 1X 100AMP HRC FUSE LV. HOLD DOWN BOLTS X4. NO ARROS. | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 120.15 | 117.15 | 234.3 | 0.00071565 | 6.1088e-06 | 2014-07-15 | C | 0.00071565 | 6.109e-06 | 2015 | 2014-07-15 | C | 2 | 0.00071565 | 6.1088e-06
1 | 985579 | 2014-07-15 12:47 | 2014-07-15 16:43 | 235.85 | 2 | 471.7 | 0.0014427 | 6.1168e-06 | NAPA ID:00886 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD4-425 | Approved Replace faulty cable between SD4-425 & TD4-527. Outage reflected in OMS Job ID 1006700. | F2 | WAIHI RD | WAIHI ROAD SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 235.85 | 232.85 | 465.7 | 0.0014224 | 6.1088e-06 | 2014-07-15 | B | 0.00071122 | 3.054e-06 | 2015 | 2014-07-15 | B | 2 | 0.0014224 | 6.1088e-06
1 | 2588553 | 2014-07-15 13:18 | 2014-07-15 15:49 | 151 | 1303 | 110387 | 0.33761 | 0.0039851 | Restore Supply on Device CB2862 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738722 | Tripping on CB 2862 - loss of supply to Cardiff & Kaponga <1span conductor 6 sleeves | F1, F2, F3 | CARDIFF NORTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 84.7176 | 81.7176 | 106478 | 0.32523 | 0.0039799 | 2014-07-15 | C | 0.32523 | 0.0039799 | 2015 | 2014-07-15 | C | 1303 | 0.32523 | 0.0039799
1 | 989830 | 2014-07-15 14:00 | 2014-07-15 15:37 | 97 | 1 | 97 | 0.00029667 | 3.0584e-06 | Restore Supply on Device TC5634 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | TC3993 | Stu advised stay wire has been hit and nearly out of ground, advised he will turn road off and remove broken stay from pole#012510 and get power back on, can do this safely on his own under 1FR. Transformer T3993 being taken off. REMOVED THE STAY WIRE IS | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 97 | 94 | 94 | 0.00028712 | 3.0544e-06 | 2014-07-15 | C | 0.00028712 | 3.054e-06 | 2015 | 2014-07-15 | C | 1 | 0.00028712 | 3.0544e-06
1 | 1009683 | 2014-07-16 07:12 | 2014-07-19 06:42 | 4289.8167 | 12 | 38099.9667 | 0.11653 | 3.6701e-05 | Restore Supply on Device X1420 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 053, 780846 | Faultman found a broken jumper at ABS 053 on pole 780846, line was isolated at ABS 101 and 4593/1 to repair the jumper. 1x HV connector was used. Steve Edwards and Garry Fischer attended. Note: Momentary Loss of Supply beyond Temp Regulator 4593/1 when ba | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3174.9972 | 3171.9972 | 38063.9667 | 0.11626 | 3.6653e-05 | 2014-07-16 | C | 0.11626 | 3.6653e-05 | 2015 | 2014-07-16 | C | 12 | 0.11626 | 3.6653e-05
1 | 373709 | 2014-07-16 08:56 | 2014-07-16 10:52 | 116.1 | 8 | 928.8 | 0.0028407 | 2.4467e-05 | NAPA ID:00309 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2062 | Creating OMS entry for imported application. Own Isolation and AP for work to be undertaken at Kakahu Road, Tirau. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 116.1 | 113.1 | 904.8 | 0.0027636 | 2.4435e-05 | 2014-07-16 | B | 0.0013818 | 1.2218e-05 | 2015 | 2014-07-16 | B | 8 | 0.0027636 | 2.4435e-05
1 | 373716 | 2014-07-16 09:00 | 2014-07-16 15:40 | 400 | 13 | 5200 | 0.015904 | 3.9759e-05 | NAPA ID:00322 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/639 | Creating OMS entry for imported application. Change 4 x crossarms, 9 HV Poles and 1 Transfomer. Work Location: Lockwood Road. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 400 | 397 | 5161 | 0.015764 | 3.9708e-05 | 2014-07-16 | B | 0.0078819 | 1.9854e-05 | 2015 | 2014-07-16 | B | 13 | 0.015764 | 3.9708e-05
1 | 373717 | 2014-07-16 09:18 | 2014-07-16 15:29 | 370.5667 | 50 | 18528.3333 | 0.056667 | 0.00015292 | NAPA ID:00323 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P20677, P20676 | Creating OMS entry for imported application. Tree felling near 11kV lines between 11kV pole numbers P20677 and P20676. Work Location: 162 McBeths Road, Kimbolton. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 370.5667 | 367.5667 | 18378.3333 | 0.056135 | 0.00015272 | 2014-07-16 | B | 0.028068 | 7.6361e-05 | 2015 | 2014-07-16 | B | 50 | 0.056135 | 0.00015272
1 | 1011995 | 2014-07-16 11:55 | 2014-07-16 12:03 | 8.1667 | 1204 | 9832.6667 | 0.030072 | 0.0036823 | Restore Supply on Device CB13 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | P18836, T3/307 | Feilding Sub, CB 13 was open due to a report of a person been electrocuted in a tree on 39 Seddon St, faultman found a it was a service line running through the trees service line was isolated and made safe by the faultman, A8869 supply was then restored. | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 8.1667 | 5.1667 | 6220.6667 | 0.019001 | 0.0036775 | 2014-07-16 | C | 0.019001 | 0.0036775 | 2015 | 2014-07-16 | C | 1204 | 0.019001 | 0.0036775
1 | 1013246 | 2014-07-16 12:55 | 2014-07-16 13:54 | 59.0667 | 114 | 6733.6 | 0.020594 | 0.00034866 | Restore Supply on Device SP15 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | SP15 | Lake Road CB3 - SP15 tripped L/O. Line patrolled - no fault located. Sectionaliser reclosed & held ok - no fault found. Greg Whyte attended. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 59.0667 | 56.0667 | 6391.6 | 0.019523 | 0.0003482 | 2014-07-16 | C | 0.019523 | 0.0003482 | 2015 | 2014-07-16 | C | 114 | 0.019523 | 0.0003482
1 | 1014665 | 2014-07-16 16:44 | 2014-07-16 16:57 | 13.55 | 67 | 907.85 | 0.0027766 | 0.00020491 | Restore Supply on Device 630 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 360823 | Faultman found on pole 360823 the cross arm king pin nut was missing, ABS 630 was opened for safety so faultman could put on a new nut and tighten it up. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 13.55 | 10.55 | 706.85 | 0.002159 | 0.00020465 | 2014-07-16 | C | 0.002159 | 0.00020465 | 2015 | 2014-07-16 | C | 67 | 0.002159 | 0.00020465
1 | 1017295 | 2014-07-17 07:55 | 2014-07-17 12:06 | 251.6667 | 92 | 13574.6333 | 0.041517 | 0.00028137 | Restore Supply on Device 7368 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 7607 | Initially found fuses 7368 tripped. Also found Fuses 7607 tripped. (Fuses 7368 reclosed OK). Patrol carried out but nothing found (Suspect bird). Reclosed OK. James Matthews Attended. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 147.5504 | 144.5504 | 13298.6333 | 0.04062 | 0.00028101 | 2014-07-17 | C | 0.04062 | 0.00028101 | 2015 | 2014-07-17 | C | 92 | 0.04062 | 0.00028101
1 | 373737 | 2014-07-17 09:15 | 2014-07-17 15:09 | 354 | 12 | 4248 | 0.012992 | 3.6701e-05 | NAPA ID:00348 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 847842, 725870 | Replacing rotten poles & crossarms between 847842 & 725870 W/O #10138468 Work Location: Tangahoe Valley Road. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 354 | 351 | 4212 | 0.012865 | 3.6653e-05 | 2014-07-17 | B | 0.0064326 | 1.8327e-05 | 2015 | 2014-07-17 | B | 12 | 0.012865 | 3.6653e-05
1 | 1017399 | 2014-07-17 09:28 | 2014-07-17 10:14 | 46 | 1 | 46 | 0.00014069 | 3.0584e-06 | Restore Supply on Device 7598 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 848262 | Fuses 7958 found tripped. Cause: Found Twisted Cross arm. New king bolt fitted / tightened. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 46 | 43 | 43 | 0.00013134 | 3.0544e-06 | 2014-07-17 | C | 0.00013134 | 3.054e-06 | 2015 | 2014-07-17 | C | 1 | 0.00013134 | 3.0544e-06
1 | 1017682 | 2014-07-17 12:38 | 2014-07-17 14:09 | 91.15 | 1 | 91.15 | 0.00027878 | 3.0584e-06 | Restore Supply on Device X2575 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 311 Haunui Road, Whangaehu, Wanganui | replaced 3 x 6 amp HV fuses and fuse holders. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 91.15 | 88.15 | 88.15 | 0.00026925 | 3.0544e-06 | 2014-07-17 | C | 0.00026925 | 3.054e-06 | 2015 | 2014-07-17 | C | 1 | 0.00026925 | 3.0544e-06
1 | 1018338 | 2014-07-17 13:18 | 2014-07-17 14:13 | 55.6667 | 659 | 24775.45 | 0.075774 | 0.0020155 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 204910 | 1 A/R on CB 3 was followed by emergency call from contractor who had made contact with 11kV line - CB 3 tripped by NOC for safety and on site inspection requested - all ok - supply restored following on site checks/audit. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 37.5955 | 34.5955 | 22798.45 | 0.069636 | 0.0020129 | 2014-07-17 | C | 0.069636 | 0.0020129 | 2015 | 2014-07-17 | C | 659 | 0.069636 | 0.0020129
1 | 1021590 | 2014-07-17 15:35 | 2014-07-17 20:33 | 298.4833 | 2 | 399.4667 | 0.0012217 | 6.1168e-06 | Restore Supply on Device T1/18 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN |  | check 512 NGAIO RD and , 479. x2 HV fuses not a full set cause unknown. | F2 | SANSON LS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 199.7333 | 196.7333 | 393.4667 | 0.0012018 | 6.1088e-06 | 2014-07-17 | C | 0.0012018 | 6.109e-06 | 2015 | 2014-07-17 | C | 2 | 0.0012018 | 6.1088e-06
1 | 1021614 | 2014-07-17 16:14 | 2014-07-17 19:59 | 225.7667 | 1 | 225.7667 | 0.00069049 | 3.0584e-06 | Restore Supply on Device T1/349 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | T1/349 | x2 15amp HV fuses not a set | F2 | SANSON LS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 225.7667 | 222.7667 | 222.7667 | 0.00068042 | 3.0544e-06 | 2014-07-17 | C | 0.00068042 | 3.054e-06 | 2015 | 2014-07-17 | C | 1 | 0.00068042 | 3.0544e-06
1 | 1021658 | 2014-07-17 16:42 | 2014-07-18 20:42 | 1679.8167 | 32 | 11125.95 | 0.034028 | 9.787e-05 | Restore Supply on Device T2880 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 811643 | Faultman found Sectionaliser C633/2 had tripped. A patrol was made but too foggy to see much. Sectionaliser was closed and supply was restored, faultman will return in morning to carry out a line patrol of this section of line. Patrol found twisted insula | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 347.6859 | 344.6859 | 11029.95 | 0.03369 | 9.7742e-05 | 2014-07-17 | C | 0.03369 | 9.7742e-05 | 2015 | 2014-07-17 | C | 32 | 0.03369 | 9.7742e-05
1 | 1021671 | 2014-07-17 17:30 | 2014-07-18 10:27 | 1016.7833 | 44 | 12632.9333 | 0.038637 | 0.00013457 | Restore Supply on Device I15 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P49879 | Line down past Fuses I21, will return in morning to repair , have to carry all equipment in on foot. Repairs made Friday morning, conductor rejoined with about 3m required. (Deterioration / Rusty Condition). | F5 | CASTLEHILL | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 287.1121 | 284.1121 | 12500.9333 | 0.038183 | 0.00013439 | 2014-07-17 | C | 0.038183 | 0.00013439 | 2015 | 2014-07-17 | C | 44 | 0.038183 | 0.00013439
1 | 1022440 | 2014-07-17 21:58 | 2014-07-17 23:33 | 94.7833 | 1070 | 51070.1667 | 0.15619 | 0.0032725 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | CB8 | Sectionalised and found dead duck below line no damage to line relivened. | F2 | 18TH AVE | WAIHI ROAD SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 47.7291 | 44.7291 | 47860.1667 | 0.14619 | 0.0032682 | 2014-07-17 | C | 0.14619 | 0.0032682 | 2015 | 2014-07-17 | C | 1070 | 0.14619 | 0.0032682
1 | 1023741 | 2014-07-17 22:01 | 2014-07-23 14:33 | 8191.9167 | 81 | 477165.6 | 1.4594 | 0.00024773 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-737 | Generator connected to transformer TD4-737 at 02:30 18/07/14. Transformer Faulted. Upgrade to 300kVA transformer as load on generator showed it was well over the 200kVA that was installed. Generator Removed 13:17 Power restored 16:22. Job Locked cannot cl | F3 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 5890.9333 | 5887.9333 | 476922.6 | 1.4567 | 0.00024741 | 2014-07-17 | C | 1.4567 | 0.00024741 | 2015 | 2014-07-17 | C | 81 | 1.4567 | 0.00024741
1 | 4222571 | 2014-07-18 04:17 | 2014-07-18 04:41 | 24 | 6823 | 151136 | 0.46224 | 0.020868 | Restore Supply on Device DP_ID | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 815332 | 33KV Line patrol needed at first day light after 33KV tripping from Transpower Greytown. Greytown GXP T2 & T3 tripping, CB 1332 auto closed on O/C and CB C886 at Martinborough auto reclosed on B-phase O/C & E/F flags then lost bulk supply at Greytown GXP, | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 22.151 | 19.151 | 130667 | 0.39911 | 0.02084 | 2014-07-18 | C | 0.39911 | 0.02084 | 2015 | 2014-07-18 | C | 6823 | 0.39911 | 0.02084
1 | 455087 | 2014-07-18 05:12 | 2014-07-22 16:03 | 6411 | 120 | 19770 | 0.060465 | 0.00036701 | NAPA ID:00335 TP_KINLEITH GXP > MARAETAI ROAD SUB > LOMOND AVE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LC1504 | Approved. SIN-14/93422-Approved: AP1: Disconnect cables from the LV bushings of TC3052 and connect a temporary generator to the LV load of TC3052. AP2: Disconnect 11kV cable going to LC1510 from the left hand side box connection of the SD unit. AP3: Cut 1 | F1/F3 | LOMOND AVE | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 164.75 | 161.75 | 19410 | 0.059286 | 0.00036653 | 2014-07-18 | B | 0.029643 | 0.00018327 | 2015 | 2014-07-18 | B | 120 | 0.059286 | 0.00036653
1 | 1053982 | 2014-07-18 06:23 | 2014-07-22 14:47 | 6264.5167 | 182 | 15146.1833 | 0.046323 | 0.00055663 | Restore Supply on Device C216 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 839078 | Line patrolled and Recloser C216/2 found tripped. Tree branch (inside notice zone) contacted lines due to weight of snow. Branch removed from lines. No repairs required. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 83.2208 | 80.2208 | 14600.1833 | 0.044595 | 0.00055591 | 2014-07-18 | C | 0.044595 | 0.0005559 | 2015 | 2014-07-18 | C | 182 | 0.044595 | 0.00055591
1 | 452721 | 2014-07-18 09:34 | 2014-07-18 14:21 | 286.9167 | 15 | 4303.75 | 0.013163 | 4.5876e-05 | NAPA ID:00508 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2425 | Approved. Replace 11kV and 400V crossarms. Work Location: Reservoir Road, Waihi. Work Order 10122692 | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 286.9167 | 283.9167 | 4258.75 | 0.013008 | 4.5816e-05 | 2014-07-18 | B | 0.006504 | 2.2908e-05 | 2015 | 2014-07-18 | B | 15 | 0.013008 | 4.5816e-05
1 | 1028066 | 2014-07-18 17:10 | 2014-07-18 22:11 | 301.6833 | 1 | 301.6833 | 0.00092267 | 3.0584e-06 | Restore Supply on Device TC2769 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Transformer 2769 | Replaced 1 x H/V 10 Amp fuse | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 301.6833 | 298.6833 | 298.6833 | 0.00091231 | 3.0544e-06 | 2014-07-18 | C | 0.0009123 | 3.054e-06 | 2015 | 2014-07-18 | C | 1 | 0.00091231 | 3.0544e-06
1 | 4239424 | 2014-07-19 01:50 | 2014-07-19 01:56 | 6 | 309 | 1854 | 0.0056703 | 0.00094505 | Restore Supply on Device 6419 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | restaged outage | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 6 | 3 | 927 | 0.0028315 | 0.00094382 | 2014-07-19 | C | 0.0028315 | 0.00094382 | 2015 | 2014-07-19 | C | 309 | 0.0028315 | 0.00094382
1 | 1028942 | 2014-07-19 03:15 | 2014-07-19 06:23 | 187.9833 | 311 | 28337.8333 | 0.086669 | 0.00095117 | Restore Supply on Device TA8 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 716327 | CB TA8 Tripped O/C C Phase. Branch found through lines while sectionalising - Isolated at ABS's 6685 & TA838 - Backed put in via ABS 813 - Branches cleared and feeder returned to service. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 91.1184 | 88.1184 | 27404.8333 | 0.083706 | 0.00094993 | 2014-07-19 | C | 0.083706 | 0.00094993 | 2015 | 2014-07-19 | C | 311 | 0.083706 | 0.00094993
1 | 1030152 | 2014-07-19 06:53 | 2014-07-19 10:28 | 214.2 | 1 | 214.2 | 0.00065511 | 3.0584e-06 | Restore Supply on Device TB3-009 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TB3-009 | Replaced 1x 2amp DDO ht ov | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 214.2 | 211.2 | 211.2 | 0.00064509 | 3.0544e-06 | 2014-07-19 | C | 0.00064509 | 3.054e-06 | 2015 | 2014-07-19 | C | 1 | 0.00064509 | 3.0544e-06
1 | 1030159 | 2014-07-19 07:21 | 2014-07-19 11:58 | 277.0167 | 3 | 636.2 | 0.0019458 | 9.1753e-06 | Restore Supply on Device TF8-040 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227855 | check oms 1032138 as grouped & 1032173. Replaced full set of DDO 's 3x 8 Amp fuses HT O/H. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 212.0667 | 209.0667 | 627.2 | 0.0019157 | 9.1633e-06 | 2014-07-19 | C | 0.0019157 | 9.163e-06 | 2015 | 2014-07-19 | C | 3 | 0.0019157 | 9.1633e-06
1 | 1030174 | 2014-07-19 07:38 | 2014-07-19 14:44 | 426.1667 | 74 | 7523.3333 | 0.02301 | 0.00022632 | Restore Supply on Device 581 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 535 | Part of outage OMS 1030174. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 101.6667 | 98.6667 | 7301.3333 | 0.022301 | 0.00022603 | 2014-07-19 | C | 0.022301 | 0.00022603 | 2015 | 2014-07-19 | C | 74 | 0.022301 | 0.00022603
1 | 1032132 | 2014-07-19 08:31 | 2014-07-19 14:24 | 353.0167 | 1 | 353.0167 | 0.0010797 | 3.0584e-06 | Restore Supply on Device TC4819 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H3190 | 11kv fuse fc1428 - 1x 6amp unknown | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 353.0167 | 350.0167 | 350.0167 | 0.0010691 | 3.0544e-06 | 2014-07-19 | C | 0.0010691 | 3.054e-06 | 2015 | 2014-07-19 | C | 1 | 0.0010691 | 3.0544e-06
1 | 1035966 | 2014-07-20 17:09 | 2014-07-21 10:58 | 1069.5333 | 3 | 3005.55 | 0.0091922 | 9.1753e-06 | Restore Supply on Device T7045 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7045 |  | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1001.85 | 998.85 | 2996.55 | 0.0091527 | 9.1633e-06 | 2014-07-20 | C | 0.0091527 | 9.163e-06 | 2015 | 2014-07-20 | C | 3 | 0.0091527 | 9.1633e-06
1 | 1036164 | 2014-07-20 20:20 | 2014-07-20 23:59 | 218.9667 | 110 | 23251.4333 | 0.071113 | 0.00033643 | Restore Supply on Device K45 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P07471 | Tripping on recloser CB K45 on Phase A O/C. Feeder Patrolled and livened to sectionaliser CB K54 also found open (known discrimination problem). Fault found beyond ABS K58 with tree branch on lines. Removed OK and relivened. (No damage). | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 211.3767 | 208.3767 | 22921.4333 | 0.070012 | 0.00033599 | 2014-07-20 | C | 0.070012 | 0.00033599 | 2015 | 2014-07-20 | C | 110 | 0.070012 | 0.00033599
1 | 1049389 | 2014-07-21 07:06 | 2014-07-21 23:17 | 971.9 | 141 | 49348.1667 | 0.15093 | 0.00043124 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4-350 | 21/7 2.38PM MIKE LEFT SITE AT 9.30AM AND MARC ASKIN TOOK OVER FROM THEN Cable Fault between Transformer TC4-165 & Transformer TC4-350. Transformer TC4-350 connected to Generator. Marc Askin fault located & carried out repairs. | F3 | TUI ST | OMANU SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 349.987 | 346.987 | 48925.1667 | 0.14944 | 0.00043067 | 2014-07-21 | C | 0.14944 | 0.00043067 | 2015 | 2014-07-21 | C | 141 | 0.14944 | 0.00043067
1 | 1049573 | 2014-07-21 08:08 | 2014-07-21 09:18 | 69.7167 | 1 | 69.7167 | 0.00021322 | 3.0584e-06 | Restore Supply on Device X2986 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4281A Main Road, Taurakina. TX 2986. | REPLACED 80AMP RE WIREABLE LV O/H FUSE. CAUSED AGE/ DETERIORATION. TX 2986. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 69.7167 | 66.7167 | 66.7167 | 0.00020378 | 3.0544e-06 | 2014-07-21 | C | 0.00020378 | 3.054e-06 | 2015 | 2014-07-21 | C | 1 | 0.00020378 | 3.0544e-06
1 | 442003 | 2014-07-21 09:37 | 2014-07-21 09:46 | 9 | 12 | 108 | 0.00033031 | 3.6701e-05 | NAPA ID:00374 TP_HINUERA GXP > PUTARURU SUB > PUTARURU LS | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3087, Sw/Gear 9821/2 | Detail confirmed after conversion from outdef. 14/93803. Transfer 11kV LS Transformer from TC3087 from CB6 to Sw/Gear 9821/2 Power restored to Transformer TC3087 when transformer transfered to Sw/gear 9821/2 at 10 35 on 21/07/14 MDB | F1, F2, F3 | RC14-PUTARURU 33KV | TP_HINUERA | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 72 | 0.00021992 | 3.6653e-05 | 2014-07-21 | B | 0.00010996 | 1.8327e-05 | 2015 | 2014-07-21 | B | 12 | 0.00021992 | 3.6653e-05
1 | 1049853 | 2014-07-21 11:33 | 2014-07-21 13:30 | 117.3167 | 5 | 461.0333 | 0.00141 | 1.5292e-05 | Restore Supply on Device SE3-026 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE3-066 | Replace 3x DDO Fuses & Fuse Holders. 1 broke under planned SIS NAPA ID 515. Decided to replace all 3 DDO holders as they were all very old and were also about to break. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 92.2067 | 89.2067 | 446.0333 | 0.0013624 | 1.5272e-05 | 2014-07-21 | C | 0.0013624 | 1.5272e-05 | 2015 | 2014-07-21 | C | 5 | 0.0013624 | 1.5272e-05
1 | 1053015 | 2014-07-21 15:08 | 2014-07-22 11:59 | 1250.9333 | 509 | 34612 | 0.10586 | 0.0015567 | Restore Supply on Device IP158 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 219019 | Found cross arm faulty on pole 219019 and 1 DDO sparking . Isolated between ABS SD5-024, IP158 & Sw/Gear 9022/4, Back feed rest of area. Replaced 1 cross arm & 3 DDO units | F2 | GRAVATT RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 33085 | 0.10106 | 0.0015547 | 2014-07-21 | C | 0.10106 | 0.0015547 | 2015 | 2014-07-21 | C | 509 | 0.10106 | 0.0015547
1 | 384838 | 2014-07-22 09:03 | 2014-07-22 15:06 | 362.8333 | 12 | 4354 | 0.013316 | 3.6701e-05 | NAPA ID:00504 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 725796, 725868 | Approved. Tree work near 11kV lines between pole numbers 725796 & 725868. Work Location: Tangahoe Valley Road. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 362.8333 | 359.8333 | 4318 | 0.013189 | 3.6653e-05 | 2014-07-22 | B | 0.0065945 | 1.8327e-05 | 2015 | 2014-07-22 | B | 12 | 0.013189 | 3.6653e-05
1 | 1052048 | 2014-07-22 09:11 | 2014-07-23 07:32 | 1341.6167 | 1 | 524.35 | 0.0016037 | 3.0584e-06 | Restore Supply on Device 3696T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 741424 | Line hanging, insulator off. Second Response crew assigned for safety. Power turned off at Fuses 6225 at 17:17. Back on at 17:55 Line rebound to insulator at Pole 741424 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 524.35 | 521.35 | 521.35 | 0.0015924 | 3.0544e-06 | 2014-07-22 | C | 0.0015924 | 3.054e-06 | 2015 | 2014-07-22 | C | 1 | 0.0015924 | 3.0544e-06
1 | 1052096 | 2014-07-22 09:27 | 2014-07-22 12:08 | 160.9333 | 6 | 2757.6167 | 0.008434 | 1.8351e-05 | Restore Supply on Device T2371 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C945 | Line Patrol carried out & switching to reliven feeder. | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 459.6028 | 456.6028 | 2739.6167 | 0.008368 | 1.8327e-05 | 2014-07-22 | C | 0.008368 | 1.8327e-05 | 2015 | 2014-07-22 | C | 6 | 0.008368 | 1.8327e-05
1 | 473625 | 2014-07-22 09:27 | 2014-07-22 14:55 | 328 | 11 | 3608 | 0.011035 | 3.3643e-05 | NAPA ID:00517 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4286 | Replacing 400v cross arms at TC4286. Open 11kV transformer fuses on transfomer TC4286. Own Isolation and AP. Work Order E1419-VLY-05. Power to TC4286 went off at 09:27 and back on at 14:55. Taking transformer offline on E-Map would not create an outage | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 328 | 325 | 3575 | 0.01092 | 3.3599e-05 | 2014-07-22 | B | 0.0054598 | 1.6799e-05 | 2015 | 2014-07-22 | B | 11 | 0.01092 | 3.3599e-05
1 | 1053995 | 2014-07-22 11:15 | 2014-07-22 14:47 | 212.3833 | 3 | 442.25 | 0.0013526 | 9.1753e-06 | Restore Supply on Device SF7-015 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228419 | Line down at pole 228419. Robyn McLean attended. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 147.4167 | 144.4167 | 433.25 | 0.0013233 | 9.1633e-06 | 2014-07-22 | C | 0.0013233 | 9.163e-06 | 2015 | 2014-07-22 | C | 3 | 0.0013233 | 9.1633e-06
1 | 1055340 | 2014-07-23 09:08 | 2014-07-23 14:24 | 316 | 3 | 948 | 0.0028994 | 9.1753e-06 | NAPA ID:00498 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2121, IP579 | Approved. Remove 11kV Fuses FC2121, Replace 1 span of overhead line and install new ABS IP579. Work Order 10153061. | F3 | BROOKLANDS 6 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 316 | 313 | 939 | 0.0028681 | 9.1633e-06 | 2014-07-23 | B | 0.0014341 | 4.582e-06 | 2015 | 2014-07-23 | B | 3 | 0.0028681 | 9.1633e-06
1 | 1026808 | 2014-07-23 09:32 | 2014-07-23 15:10 | 338 | 50 | 16900 | 0.051687 | 0.00015292 | NAPA ID:00872 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5245E | Confirm Pre Commissioning & Inspection Certificate Completed & Equipment Ready for Livening. Replace Transformer 5245E & HV Cable on Dixon Street. Work Order #10145117. | F3 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 338 | 335 | 16750 | 0.051162 | 0.00015272 | 2014-07-23 | B | 0.025581 | 7.6361e-05 | 2015 | 2014-07-23 | B | 50 | 0.051162 | 0.00015272
1 | 1089112 | 2014-07-23 12:14 | 2014-07-23 14:52 | 158 | 1 | 158 | 0.00048323 | 3.0584e-06 | Restore Supply on Device T2664 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 38 CLIFTON GROVE ROAD, CARTERTON, | TX T6641 REPLACED 1 OF 2 BLOWN 3AMP 11KV FUSE CAUSE : AGE O/H HV | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 158 | 155 | 155 | 0.00047344 | 3.0544e-06 | 2014-07-23 | C | 0.00047344 | 3.054e-06 | 2015 | 2014-07-23 | C | 1 | 0.00047344 | 3.0544e-06
1 | 1089540 | 2014-07-23 15:40 | 2014-07-24 07:50 | 970.8852 | 62 | 7153.1833 | 0.021877 | 0.00018962 | Restore Supply on Device TA720 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713415 | No Power. Line patrolled and Transformer T3145 found to be faulty due to water ingress. Lid extremely corroded on transformer. Transformer replaced with 1 3phase 30kVA. Equipment used 3x HV fuse links and 3x cu sleeves. Henry Hood & Bruce Kerr attended. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 115.3739 | 112.3739 | 6967.1833 | 0.021281 | 0.00018937 | 2014-07-23 | C | 0.021281 | 0.00018937 | 2015 | 2014-07-23 | C | 62 | 0.021281 | 0.00018937
1 | 1089605 | 2014-07-23 20:21 | 2014-07-23 23:42 | 200.3667 | 55 | 2101.1667 | 0.0064263 | 0.00016821 | Restore Supply on Device TC975 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC975 | Dennis Ngatai Attended. Repaired 2x HV Jumpers to top of DDO's at Transformer TC975. No Materials Used. All Power Restored on completion. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 38.203 | 35.203 | 1936.1667 | 0.0059139 | 0.00016799 | 2014-07-23 | C | 0.0059139 | 0.00016799 | 2015 | 2014-07-23 | C | 55 | 0.0059139 | 0.00016799
1 | 373771 | 2014-07-24 09:08 | 2014-07-24 14:52 | 344 | 12 | 4128 | 0.012625 | 3.6701e-05 | NAPA ID:00404 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 847842, 725870 | Creating OMS entry for imported application. Replace rotten poles & cross arms between poles 847842 & 725870. Work Location: Tangahoe Valley Road. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 4092 | 0.012499 | 3.6653e-05 | 2014-07-24 | B | 0.0062494 | 1.8327e-05 | 2015 | 2014-07-24 | B | 12 | 0.012499 | 3.6653e-05
1 | 1101197 | 2014-07-24 14:51 | 2014-07-24 16:11 | 80.5833 | 1 | 80.5833 | 0.00024646 | 3.0584e-06 | Restore Supply on Device T731 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 63 CHESTER ROAD, CLAREVILLE, CARTERTON | hv / bird strike on transformer replaced 3amp hv fuse | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 80.5833 | 77.5833 | 77.5833 | 0.00023697 | 3.0544e-06 | 2014-07-24 | C | 0.00023697 | 3.054e-06 | 2015 | 2014-07-24 | C | 1 | 0.00023697 | 3.0544e-06
1 | 1101665 | 2014-07-24 17:55 | 2014-07-24 20:56 | 181.45 | 8 | 1089.3333 | 0.0033316 | 2.4467e-05 | Restore Supply on Device X1161 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses 586, Waireka Road, Papaiti | REPLACED REWIREABLE HV 20 AMP FUSE. CAUSE UNKNOW OH/HV LINE PARTOLLED AND RELIVENED THRU CONTROL. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 136.1667 | 133.1667 | 1065.3333 | 0.003254 | 2.4435e-05 | 2014-07-24 | C | 0.003254 | 2.4435e-05 | 2015 | 2014-07-24 | C | 8 | 0.003254 | 2.4435e-05
1 | 1101327 | 2014-07-24 17:55 | 2014-07-24 20:43 | 168.2 | 335 | 13521.0333 | 0.041353 | 0.0010246 | Restore Supply on Device LI6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 726532 | Lines and poles on fire (F1657746) - NZFS called to advised 11kV lines. Isolated for safety. Line repaired and power restored. Henry Hood attended. Replaced burnt up ampac joints using 3x EPO joints, 1x 70mm Cu. sleeve, 1mtr Cu. conductor & 1/2 roll of de | F3 | PORTLAND QUAY | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40.3613 | 37.3613 | 12516.0333 | 0.038229 | 0.0010232 | 2014-07-24 | C | 0.038229 | 0.0010232 | 2015 | 2014-07-24 | C | 335 | 0.038229 | 0.0010232
1 | 1049986 | 2014-07-25 09:15 | 2014-07-25 16:19 | 424 | 96 | 40704 | 0.12449 | 0.00029361 | NAPA ID:01043 TP_TAURANGA 33 GXP > AONGATETE SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 205719, 205598 & 205516 | Alternate Date Applied: Moved to alternate date due to Tenix not showing to do switching. Replace 33kV/11kV Poles, Crossarms and Hardware between 11kV poles 205719, 205598 & 205516. Work Location: State Highway 2, Aongatete. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 424 | 421 | 40416 | 0.12345 | 0.00029322 | 2014-07-25 | B | 0.061724 | 0.00014661 | 2015 | 2014-07-25 | B | 96 | 0.12345 | 0.00029322
1 | 844746 | 2014-07-25 09:41 | 2014-07-25 13:59 | 258 | 5 | 1290 | 0.0039454 | 1.5292e-05 | NAPA ID:00683 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/378 | Approved. Replace transformer T1/378. Work Location: Lake Road. Work Order: 10136572. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 258 | 255 | 1275 | 0.0038944 | 1.5272e-05 | 2014-07-25 | B | 0.0019472 | 7.636e-06 | 2015 | 2014-07-25 | B | 5 | 0.0038944 | 1.5272e-05
1 | 454548 | 2014-07-25 09:49 | 2014-07-25 13:15 | 206.0833 | 4 | 824.3333 | 0.0025212 | 1.2234e-05 | NAPA ID:00591 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/445 | Approved. Replace transformer T1/445. Work Location: Lake Road. Work Order 10136572. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 206.0833 | 203.0833 | 812.3333 | 0.0024812 | 1.2218e-05 | 2014-07-25 | B | 0.0012406 | 6.109e-06 | 2015 | 2014-07-25 | B | 4 | 0.0024812 | 1.2218e-05
1 | 1112801 | 2014-07-25 14:25 | 2014-07-25 16:06 | 100.7667 | 1 | 100.7667 | 0.00030819 | 3.0584e-06 | Restore Supply on Device TC1416 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TC1416 | high tension fuse dropped out. closed back in thru control. TX T1416. very high winds currently and trees close by. fuse did not blow. power back on. infrastucture around here is quite old. | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.7667 | 97.7667 | 97.7667 | 0.00029862 | 3.0544e-06 | 2014-07-25 | C | 0.00029862 | 3.054e-06 | 2015 | 2014-07-25 | C | 1 | 0.00029862 | 3.0544e-06
1 | 2479508 | 2014-07-25 15:30 | 2014-07-25 18:15 | 165 | 3698 | 192458 | 0.58862 | 0.01131 | Restore Supply on Device 1122 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 230333 | Floating 33kV conductor at Pole 230333. This line trip a couple of times due to this. 2 binders were replaced on this pole. Line was patrolled, this line prodomantly runs across country & is hard to patrol at night. Supersedes OMS Job 1117228. | F1, F2, F3 | TE MATAI1122-PONGAKAWA2007 33KV | TP_TE MATAI | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 52.0438 | 49.0438 | 181364 | 0.55396 | 0.011295 | 2014-07-25 | C | 0.55396 | 0.011295 | 2015 | 2014-07-25 | C | 3698 | 0.55396 | 0.011295
1 | 1117404 | 2014-07-25 18:58 | 2014-07-25 21:30 | 151.8333 | 1 | 151.8333 | 0.00046437 | 3.0584e-06 | Restore Supply on Device TC2-092 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2069 STATE HIGHWAY 2, KATIKATI | blown ddo. replaced barrel and fuse wire. reliven and power back on. due to age. oh/hv checked transformer, good all. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 151.8333 | 148.8333 | 148.8333 | 0.0004546 | 3.0544e-06 | 2014-07-25 | C | 0.0004546 | 3.054e-06 | 2015 | 2014-07-25 | C | 1 | 0.0004546 | 3.0544e-06
1 | 1117717 | 2014-07-25 23:12 | 2014-07-26 02:27 | 195.1 | 27 | 5267.7 | 0.016111 | 8.2577e-05 | Restore Supply on Device 5728 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738668 | No Power. Line patrolled - Line down at pole 738668. 1 x Line Guard - 8 metres of wire. Jade Williams Attended. | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 195.1 | 192.1 | 5186.7 | 0.015842 | 8.2469e-05 | 2014-07-25 | C | 0.015842 | 8.2469e-05 | 2015 | 2014-07-25 | C | 27 | 0.015842 | 8.2469e-05
1 | 1474020 | 2014-07-26 11:40 | 2014-07-26 12:39 | 59 | 2 | 118 | 0.00036089 | 6.1168e-06 | Restore Supply on Device TC3488 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | FP103 | Fuses FP103 opened. Repairs made and fuses closed. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 59 | 56 | 112 | 0.0003421 | 6.1088e-06 | 2014-07-26 | C | 0.00034209 | 6.109e-06 | 2015 | 2014-07-26 | C | 2 | 0.0003421 | 6.1088e-06
1 | 1119207 | 2014-07-26 15:50 | 2014-07-26 18:15 | 145 | 1 | 145 | 0.00044347 | 3.0584e-06 | Restore Supply on Device TC1714 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer TC1714 | 2 blown HV 3Amp fuses. suspected bird strick | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 145 | 142 | 142 | 0.00043373 | 3.0544e-06 | 2014-07-26 | C | 0.00043373 | 3.054e-06 | 2015 | 2014-07-26 | C | 1 | 0.00043373 | 3.0544e-06
1 | 1119286 | 2014-07-26 18:37 | 2014-07-26 21:09 | 151.7333 | 532 | 58942.1333 | 0.18027 | 0.0016271 | Restore Supply on Device 262 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 369609 | Karl & Garry doing job under 2FR. Line down at pole 366824. | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 110.7935 | 107.7935 | 57346.1333 | 0.17516 | 0.001625 | 2014-07-26 | C | 0.17516 | 0.001625 | 2015 | 2014-07-26 | C | 532 | 0.17516 | 0.001625
1 | 1121671 | 2014-07-27 04:14 | 2014-07-27 16:38 | 744.5167 | 323 | 105735.75 | 0.32338 | 0.00098787 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 383192 | Replace Pole 383192 after car accident. NDR 31109. Material 1x 12.5m Concrete Pole existing hardware reused as it was new. | F3 | SHAW AVE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 327.3553 | 324.3553 | 104766.75 | 0.32 | 0.00098658 | 2014-07-27 | C | 0.32 | 0.00098658 | 2015 | 2014-07-27 | C | 323 | 0.32 | 0.00098658
1 | 1122522 | 2014-07-27 14:13 | 2014-07-27 15:40 | 87.3333 | 8 | 698.6667 | 0.0021368 | 2.4467e-05 | Restore Supply on Device T9/376 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03179 | Fire put out & insulator reattached to arm. | F5 | CASTLEHILL | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.3333 | 84.3333 | 674.6667 | 0.0020607 | 2.4435e-05 | 2014-07-27 | C | 0.0020607 | 2.4435e-05 | 2015 | 2014-07-27 | C | 8 | 0.0020607 | 2.4435e-05
1 | 1122550 | 2014-07-27 14:37 | 2014-07-27 16:54 | 137.0667 | 425 | 33007.5167 | 0.10095 | 0.0012998 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200437 | Fire called to advise of arcing pole F1659118 20min ETA fire advised. Lines down at pole 200437. Line rehung & sagged. NDR 048409. Materials 6 sleeves Binders. | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 77.6647 | 74.6647 | 31732.5167 | 0.096925 | 0.0012981 | 2014-07-27 | C | 0.096925 | 0.0012981 | 2015 | 2014-07-27 | C | 425 | 0.096925 | 0.0012981
1 | 468429 | 2014-07-28 09:00 | 2014-07-28 12:26 | 205.5833 | 52 | 10690.3333 | 0.032696 | 0.00015904 | NAPA ID:00637 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2026 | Approved. Isolate Transformer TC2026 for LV Network. Work Location: 45 Elizabeth Street, Matamata. | F3 | ELIZABETH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 205.5833 | 202.5833 | 10534.3333 | 0.032176 | 0.00015883 | 2014-07-28 | B | 0.016088 | 7.9415e-05 | 2015 | 2014-07-28 | B | 52 | 0.032176 | 0.00015883
1 | 1124753 | 2014-07-28 14:48 | 2014-07-28 16:06 | 77.9167 | 1 | 77.9167 | 0.0002383 | 3.0584e-06 | Restore Supply on Device X1793 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1793, 796798 | Blown transformer X1793. Pole # 796798. Customer happy for transformer to be replaced Wednesday 30/07 as only feeds the wool shed. Unknown cause. All assets adjacent to this fault are fine. 2nd response follow up requested on OMS 1124807. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 77.9167 | 74.9167 | 74.9167 | 0.00022883 | 3.0544e-06 | 2014-07-28 | C | 0.00022883 | 3.054e-06 | 2015 | 2014-07-28 | C | 1 | 0.00022883 | 3.0544e-06
1 | 985586 | 2014-07-29 09:19 | 2014-07-29 15:46 | 387.15 | 136 | 52652.4 | 0.16103 | 0.00041595 | NAPA ID:00732 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R13041 | Approved. Replace cross arms and hardware at various sites. Work Location: Opoutere Road, Whangamata. | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 387.15 | 384.15 | 52244.4 | 0.15958 | 0.0004154 | 2014-07-29 | B | 0.079788 | 0.0002077 | 2015 | 2014-07-29 | B | 136 | 0.15958 | 0.0004154
1 | 382992 | 2014-07-29 09:27 | 2014-07-29 11:44 | 137.4 | 528 | 72547.2 | 0.22188 | 0.0016148 | NAPA ID:00428 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L34 | There was some SAIDI reduction applied to this job by extra resource being on site on the day. SIN-14/93865-Received: Replace 1 span 11kV line between 11kV Poles P33451 & P33441. Straighten 11kV Pole P33702. Lower tap settings on T1/306, T1/296, T1/471, T | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 137.4 | 134.4 | 70963.2 | 0.21675 | 0.0016127 | 2014-07-29 | B | 0.10838 | 0.00080637 | 2015 | 2014-07-29 | B | 528 | 0.21675 | 0.0016127
1 | 1143049 | 2014-07-29 15:35 | 2014-07-29 20:25 | 290.0667 | 1037 | 33536.7167 | 0.10257 | 0.0031716 | Restore Supply on Device U20 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 764228 | 11kV CB U20 tripped, flags unknown. Sectionalising found a blown insulator at pole 764222. Isolated by ABS 5187 & 5128. Note: Recloser 4989 failed to clear fault, protection review required again. (Note this RS has done this in the past not clearing faul | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 32.3401 | 29.3401 | 30425.7167 | 0.092933 | 0.0031674 | 2014-07-29 | C | 0.092933 | 0.0031674 | 2015 | 2014-07-29 | C | 1037 | 0.092933 | 0.0031674
1 | 1150153 | 2014-07-30 08:28 | 2014-07-30 10:31 | 123.05 | 1 | 123.05 | 0.00037634 | 3.0584e-06 | Restore Supply on Device TC2-167 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2-167 | replaced 2 high tension fuses at 2 seperate points 1X 3amp at tx & 1X 6amp at fuses that feed tx- no arros, adjacent assets ok | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 123.05 | 120.05 | 120.05 | 0.00036668 | 3.0544e-06 | 2014-07-30 | C | 0.00036668 | 3.054e-06 | 2015 | 2014-07-30 | C | 1 | 0.00036668 | 3.0544e-06
1 | 1002500 | 2014-07-30 09:08 | 2014-07-30 14:06 | 298 | 12 | 3576 | 0.010937 | 3.6701e-05 | NAPA ID:00560 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 204970, 205156, 205161, 205162 | Planner to add 2x LLP's to application | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 298 | 295 | 3540 | 0.010813 | 3.6653e-05 | 2014-07-30 | B | 0.0054063 | 1.8327e-05 | 2015 | 2014-07-30 | B | 12 | 0.010813 | 3.6653e-05
1 | 442065 | 2014-07-30 09:13 | 2014-07-30 15:00 | 346.1833 | 16 | 5538.9333 | 0.01694 | 4.8935e-05 | NAPA ID:00432 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B15 | Approved. Replace 11kV poles & Crossarms. Work Location: Hoihere Road, Manawatu. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 346.1833 | 343.1833 | 5490.9333 | 0.016772 | 4.8871e-05 | 2014-07-30 | B | 0.0083858 | 2.4435e-05 | 2015 | 2014-07-30 | B | 16 | 0.016772 | 4.8871e-05
1 | 1089163 | 2014-07-30 09:15 | 2014-07-30 13:58 | 283 | 4 | 1132 | 0.0034621 | 1.2234e-05 | NAPA ID:00733 TP_MT MAUNGANUI 33 GXP > TRITON SUB > SOUTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC4-276 | Approved. Move 11kV Transformer TC4-276 onto new Fuse/Sw 9829/2. Work Location: Totara Street & Maui Street. | F1 | SOUTH | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 283 | 280 | 1120 | 0.003421 | 1.2218e-05 | 2014-07-30 | B | 0.0017105 | 6.109e-06 | 2015 | 2014-07-30 | B | 4 | 0.003421 | 1.2218e-05
1 | 901177 | 2014-07-30 09:15 | 2014-07-30 13:00 | 225 | 7 | 1575 | 0.004817 | 2.1409e-05 | NAPA ID:00723 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/228 | Approved. Replace Transformer. Upgrade Transformer from 30kVA to 50kVA Work Location; Hall Mt Stewart Road | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 225 | 222 | 1554 | 0.0047466 | 2.1381e-05 | 2014-07-30 | B | 0.0023733 | 1.069e-05 | 2015 | 2014-07-30 | B | 7 | 0.0047466 | 2.1381e-05
1 | 1158352 | 2014-07-30 09:16 | 2014-07-30 09:39 | 22.4667 | 43 | 269.5667 | 0.00082445 | 0.00013151 | Restore Supply on Device 8410 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 8410 | Nick Patton Attended. Found 2x Fuses 8410 had blown. Line Patrolled, nothing found. Suspect Bird Strike. Reloaded relivened fuses. All Power Restored on Completion. 2x 20A HV Fuses Replaced. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 6.269 | 3.269 | 140.5667 | 0.00042935 | 0.00013134 | 2014-07-30 | C | 0.00042935 | 0.00013134 | 2015 | 2014-07-30 | C | 43 | 0.00042935 | 0.00013134
1 | 1158546 | 2014-07-30 11:54 | 2014-07-30 13:12 | 78.1 | 1 | 76.4833 | 0.00023392 | 3.0584e-06 | Restore Supply on Device 10055 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4 | part of oms 1052070 Momentary outage to test auto change over | F3 | AWAPUNI | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 76.4833 | 73.4833 | 73.4833 | 0.00022445 | 3.0544e-06 | 2014-07-30 | C | 0.00022445 | 3.054e-06 | 2015 | 2014-07-30 | C | 1 | 0.00022445 | 3.0544e-06
1 | 1159019 | 2014-07-30 16:36 | 2014-07-30 18:40 | 124 | 35 | 4340 | 0.013274 | 0.00010704 | Restore Supply on Device TC1207 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1207 | Found Transformer TC1207 faulty Own SIS & AP to replace Transformer. Hard bushing was broken and oil came out of the bushing. Faulty transformer. Just deteriorated. Brand new transformer installed. Power back on. Photos will be taken tomorrow and will com | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 124 | 121 | 4235 | 0.012935 | 0.0001069 | 2014-07-30 | C | 0.012935 | 0.0001069 | 2015 | 2014-07-30 | C | 35 | 0.012935 | 0.0001069
1 | 1159312 | 2014-07-30 18:48 | 2014-07-30 20:56 | 127.8 | 1 | 127.8 | 0.00039087 | 3.0584e-06 | Restore Supply on Device TC1397 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2589 Tairua Road, Hikuai | 1X BLOWN 10AMP DDO HV O/H FUSE - REPLACED CAUSE BY UNKNOWN CALLING TO HOUSE TO CHECK POWER RESTORED ON THE WAY HOME - FULL POWER RESTORED. CHECKED ADJACENT ASSETS - ALL GOOD. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 127.8 | 124.8 | 124.8 | 0.00038119 | 3.0544e-06 | 2014-07-30 | C | 0.00038119 | 3.054e-06 | 2015 | 2014-07-30 | C | 1 | 0.00038119 | 3.0544e-06
1 | 955526 | 2014-07-31 08:45 | 2014-07-31 16:30 | 464.85 | 30 | 13945.5 | 0.042651 | 9.1753e-05 | NAPA ID:00796 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 784219, 784225 | Approved. Tree trimming near 11kV lines between 11kV pole numbers 784219 & 784225. Work location: Rangituatua East Road, Wanganui. PPPD 784219 & PPPD 784225. | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 464.85 | 461.85 | 13855.5 | 0.042321 | 9.1633e-05 | 2014-07-31 | B | 0.02116 | 4.5816e-05 | 2015 | 2014-07-31 | B | 30 | 0.042321 | 9.1633e-05
1 | 1008762 | 2014-07-31 09:00 | 2014-07-31 15:44 | 403.5167 | 79 | 31877.8167 | 0.097496 | 0.00024162 | NAPA ID:00532 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC2-074 | Approved. Change poles and cross arms at 50 sites. Work Location: Wainui South Road. Work Order: not supplied. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 403.5167 | 400.5167 | 31640.8167 | 0.096644 | 0.0002413 | 2014-07-31 | B | 0.048322 | 0.00012065 | 2015 | 2014-07-31 | B | 79 | 0.096644 | 0.0002413
1 | 1160762 | 2014-07-31 09:28 | 2014-07-31 11:13 | 105.55 | 1 | 105.55 | 0.00032282 | 3.0584e-06 | Restore Supply on Device TD3-335 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | td3-335 | replaced ht 1x 3amp fuse & barrell - no arros, all other assets ok. hv ov | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 105.55 | 102.55 | 102.55 | 0.00031323 | 3.0544e-06 | 2014-07-31 | C | 0.00031323 | 3.054e-06 | 2015 | 2014-07-31 | C | 1 | 0.00031323 | 3.0544e-06
1 | 1158528 | 2014-07-31 09:45 | 2014-07-31 13:13 | 208 | 13 | 2704 | 0.00827 | 3.9759e-05 | NAPA ID:01333 TP_HAWERA GXP > WHAREROA SUB > MANUTAHI | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 728394 | Replace broken network pole 728394 at 126 Mokoia Rd. W/O 10149478. | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 208 | 205 | 2665 | 0.00814 | 3.9708e-05 | 2014-07-31 | B | 0.00407 | 1.9854e-05 | 2015 | 2014-07-31 | B | 13 | 0.00814 | 3.9708e-05
1 | 1162161 | 2014-07-31 16:13 | 2014-07-31 19:40 | 207.0833 | 7 | 1361.95 | 0.0041654 | 2.1409e-05 | Restore Supply on Device 949 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 280 OHAUMOKO ROAD, HUNTERVILLE | hv fault. entire road had no power. reliven (replaced) 2 x 10 amp 11kv fuses. line patrol completed. cause unknown. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 194.5643 | 191.5643 | 1340.95 | 0.0040958 | 2.1381e-05 | 2014-07-31 | C | 0.0040958 | 2.1381e-05 | 2015 | 2014-07-31 | C | 7 | 0.0040958 | 2.1381e-05
1 | 1162404 | 2014-07-31 16:46 | 2014-07-31 20:52 | 246.5333 | 1 | 246.5333 | 0.000754 | 3.0584e-06 | Restore Supply on Device N3160 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 38 LOWER KINA ROAD, OPUNAKE | 2 OF 3 BLOWN 6AMP DDO HV O/H CAUSE UNKNOWN (POSSIBLE BIRD) FULL POWER RESTORED ADJACENT ASSETS - ALL NEW (VISUAL OF SPARKING CONNECTION BUT NO SIGN OF DAMAGE ON MAIN LINE POLE - POSSIBLE SALT SPRAY). | F4/F1 | SOUTH RD NGARIKI | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 246.5333 | 243.5333 | 243.5333 | 0.00074385 | 3.0544e-06 | 2014-07-31 | C | 0.00074385 | 3.054e-06 | 2015 | 2014-07-31 | C | 1 | 0.00074385 | 3.0544e-06
1 | 1162459 | 2014-07-31 17:51 | 2014-07-31 19:49 | 117.9167 | 1 | 117.9167 | 0.00036064 | 3.0584e-06 | Restore Supply on Device TC4093 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1661 Morrinsville-Walton Road, Kiwitahi | failed 1x 3amp hv o/h ddo fuse cause unknown full power restored adjacent assets - all good. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 117.9167 | 114.9167 | 114.9167 | 0.000351 | 3.0544e-06 | 2014-07-31 | C | 0.000351 | 3.054e-06 | 2015 | 2014-07-31 | C | 1 | 0.000351 | 3.0544e-06
1 | 2589857 | 2014-08-01 00:01 | 2014-08-01 01:09 | 68 | 2512 | 168107 | 0.51414 | 0.0076828 | Restore Supply on Device Y40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Turitea Substation | Linton/Turitea CB 1182, Y0 & Y10 tripeed. Diff, A, B C Phases O/C. Y10 Tripped BU. Line between LTN1182 & TUR Y40 patrolled. No fault located. Shazil Khan and Zane Marshall attended. | F1, F2, F3 | LINTON-TURITEA 33KV | TP_LINTON | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 66.9216 | 63.9216 | 160571 | 0.49045 | 0.0076727 | 2014-08-01 | C | 0.49045 | 0.0076727 | 2015 | 2014-08-01 | C | 2512 | 0.49045 | 0.0076727
1 | 1173157 | 2014-08-01 13:32 | 2014-08-01 16:40 | 188.3 | 12 | 581.55 | 0.0017786 | 3.6701e-05 | Restore Supply on Device T1832 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 7726 | 2.48pm Tallia called to advise that this job is in masterton not greytown.. deassigned as Adam whale will attend as he is closer. Job is on Akura Sub CB C816 Mt Bruce Feeder | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 48.4625 | 45.4625 | 545.55 | 0.0016663 | 3.6653e-05 | 2014-08-01 | C | 0.0016663 | 3.6653e-05 | 2015 | 2014-08-01 | C | 12 | 0.0016663 | 3.6653e-05
1 | 1173168 | 2014-08-01 13:45 | 2014-08-01 15:29 | 103.95 | 1 | 103.95 | 0.00031792 | 3.0584e-06 | Restore Supply on Device T2498 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 1003 ponatahi road Martinborough | Replaced HV O/H 6amp ddo fuse element at Tx caused by wind Full power restored Checked adjacent pole - all good | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 103.95 | 100.95 | 100.95 | 0.00030834 | 3.0544e-06 | 2014-08-01 | C | 0.00030834 | 3.054e-06 | 2015 | 2014-08-01 | C | 1 | 0.00030834 | 3.0544e-06
1 | 1173183 | 2014-08-01 14:11 | 2014-08-01 17:59 | 228.6527 | 1 | 228.6667 | 0.00069936 | 3.0584e-06 | Restore Supply on Device T8/253 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer T8/253 | 2.13pm advised Tallia at svs hub of job Trevor Pocock replaced 2 x fuse links | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 228.6667 | 225.6667 | 225.6667 | 0.00068928 | 3.0544e-06 | 2014-08-01 | C | 0.00068928 | 3.054e-06 | 2015 | 2014-08-01 | C | 1 | 0.00068928 | 3.0544e-06
1 | 1192598 | 2014-08-01 15:29 | 2014-08-02 16:38 | 1509.25 | 51 | 6660.8333 | 0.020372 | 0.00015598 | Restore Supply on Device Q21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3177T | refer OMS 1192508 | F4 | MAHOE | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 130.6046 | 127.6046 | 6507.8333 | 0.019878 | 0.00015578 | 2014-08-01 | C | 0.019878 | 0.00015578 | 2015 | 2014-08-01 | C | 51 | 0.019878 | 0.00015578
1 | 1173592 | 2014-08-01 17:14 | 2014-08-01 19:23 | 129.692 | 2 | 183.4833 | 0.00056117 | 6.1168e-06 | Restore Supply on Device TE8-033 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 49 NANRIC LANE, TE PUKE | When signing this job off OMS # 1173592, ask if OMS # 1183647 (50 NANRIC LANE) is part of this outage. replaced 8 amp HV fuse. cause unknown. oh/hv. aaok. 50 NANRIC LANE would also have been affected by this outage. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 91.7417 | 88.7417 | 177.4833 | 0.00054211 | 6.1088e-06 | 2014-08-01 | C | 0.00054211 | 6.109e-06 | 2015 | 2014-08-01 | C | 2 | 0.00054211 | 6.1088e-06
1 | 1191754 | 2014-08-02 04:54 | 2014-08-02 12:29 | 455 | 45 | 9751.4333 | 0.029824 | 0.00013763 | Restore Supply on Device 6413 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 709388 | Tripping on CB6413 - (Initial Tripping noted on OMS# 1191446). Broken cross arm found at Transformer structure 3195T. Crossarm and full set DDOs replaced, jumpers repaired. (Isolation from Fuses 5626). relivened OK. | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 216.6985 | 213.6985 | 9616.4333 | 0.029373 | 0.00013745 | 2014-08-02 | C | 0.029373 | 0.00013745 | 2015 | 2014-08-02 | C | 45 | 0.029373 | 0.00013745
1 | 1192385 | 2014-08-02 10:52 | 2014-08-02 15:21 | 269.0167 | 58 | 15602.9667 | 0.04772 | 0.00017739 | Restore Supply on Device S1201 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS S2101 | Replace pole & transformer. Planned outage delayed as TENIX had no paperwork. Supply restored at 15:21 | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 269.0167 | 266.0167 | 15428.9667 | 0.047127 | 0.00017716 | 2014-08-02 | C | 0.047127 | 0.00017716 | 2015 | 2014-08-02 | C | 58 | 0.047127 | 0.00017716
1 | 1192449 | 2014-08-02 11:35 | 2014-08-02 12:54 | 78.5167 | 2 | 133.05 | 0.00040692 | 6.1168e-06 | Restore Supply on Device T4011 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4011 | advised set of 2 DDO fuse links out, going through control to replace replaced set of 2x 10a HV fuse links. no arros. adjacent assets look ok | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 66.525 | 63.525 | 127.05 | 0.00038806 | 6.1088e-06 | 2014-08-02 | C | 0.00038806 | 6.109e-06 | 2015 | 2014-08-02 | C | 2 | 0.00038806 | 6.1088e-06
1 | 1192530 | 2014-08-02 12:56 | 2014-08-02 14:36 | 100.25 | 1 | 100.25 | 0.00030661 | 3.0584e-06 | Restore Supply on Device T3626 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3626 | replaced 2x 3a hv fuse links line clash, no arros. adjacent assets look all good | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 100.25 | 97.25 | 97.25 | 0.00029704 | 3.0544e-06 | 2014-08-02 | C | 0.00029704 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.00029704 | 3.0544e-06
1 | 1192588 | 2014-08-02 15:00 | 2014-08-02 16:57 | 116.3667 | 1 | 116.3667 | 0.0003559 | 3.0584e-06 | Restore Supply on Device T1410 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | - |  | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 116.3667 | 113.3667 | 113.3667 | 0.00034627 | 3.0544e-06 | 2014-08-02 | C | 0.00034627 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.00034627 | 3.0544e-06
1 | 1192657 | 2014-08-02 16:03 | 2014-08-02 17:20 | 77.1667 | 1 | 77.1667 | 0.00023601 | 3.0584e-06 | Restore Supply on Device 659 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 659 |  | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 77.1667 | 74.1667 | 74.1667 | 0.00022654 | 3.0544e-06 | 2014-08-02 | C | 0.00022654 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.00022654 | 3.0544e-06
1 | 1192666 | 2014-08-02 16:06 | 2014-08-03 15:32 | 1405.4 | 4 | 1639.4 | 0.005014 | 1.2234e-05 | Restore Supply on Device X358 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803 | HV ov 2x 15amp fuses at fuses 803, no arros, all other assets ok | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 409.85 | 406.85 | 1627.4 | 0.0049708 | 1.2218e-05 | 2014-08-02 | C | 0.0049708 | 1.2218e-05 | 2015 | 2014-08-02 | C | 4 | 0.0049708 | 1.2218e-05
1 | 1192991 | 2014-08-02 18:34 | 2014-08-03 01:12 | 397.7833 | 1 | 397.7833 | 0.0012166 | 3.0584e-06 | Restore Supply on Device T1027 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | T1027 | 2 wires that have come unbound from the pole. 2x ddo fuses at the tx. Lucas will stay onsite....cut away unused lv temporarily till tomorrow when trees have been cut | F2 | HOLDSWORTH | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 397.7833 | 394.7833 | 394.7833 | 0.0012058 | 3.0544e-06 | 2014-08-02 | C | 0.0012058 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.0012058 | 3.0544e-06
1 | 1192988 | 2014-08-02 19:03 | 2014-08-02 21:40 | 156.65 | 2 | 254.0667 | 0.00077704 | 6.1168e-06 | Restore Supply on Device T2812 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | na | 11kv sectionliser trip out cause weather. No other assets repaired or replaced on site. Checked adjacent assets and all up to Powerco standard. Included in main tripping outage | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 127.0333 | 124.0333 | 248.0667 | 0.0007577 | 6.1088e-06 | 2014-08-02 | C | 0.0007577 | 6.109e-06 | 2015 | 2014-08-02 | C | 2 | 0.0007577 | 6.1088e-06
1 | 1193965 | 2014-08-02 19:46 | 2014-08-03 00:23 | 277 | 120 | 25081 | 0.076708 | 0.00036701 | Restore Supply on Device V35 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04900 | Part of OMS 1193070 Lines down at pole P04900 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 209.0083 | 206.0083 | 24721 | 0.075508 | 0.00036653 | 2014-08-02 | C | 0.075508 | 0.00036653 | 2015 | 2014-08-02 | C | 120 | 0.075508 | 0.00036653
1 | 1199202 | 2014-08-02 20:17 | 2014-08-03 14:33 | 1095.5 | 400 | 68371.0333 | 0.20911 | 0.0012234 | Restore Supply on Device 5483 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | pole 741228 | Outage from fuses 5483 due to large tree falling through conductor. (High winds). Cross arm and length of conductor replaced. Tree cut away. NDR 43270 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 170.9276 | 167.9276 | 67171.0333 | 0.20517 | 0.0012218 | 2014-08-02 | C | 0.20517 | 0.0012218 | 2015 | 2014-08-02 | C | 400 | 0.20517 | 0.0012218
1 | 1194049 | 2014-08-02 21:02 | 2014-08-02 21:20 | 18 | 20 | 360 | 0.001101 | 6.1168e-05 | Restore Supply on Device MA543 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 718614 | part of OMS 1192781 outage. Generated when fuses MA543 were opened | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 18 | 15 | 300 | 0.00091633 | 6.1088e-05 | 2014-08-02 | C | 0.00091633 | 6.1088e-05 | 2015 | 2014-08-02 | C | 20 | 0.00091633 | 6.1088e-05
1 | 1196831 | 2014-08-02 21:28 | 2014-08-03 15:05 | 1057.5833 | 1 | 1057.5833 | 0.0032345 | 3.0584e-06 | Restore Supply on Device X2280 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | fuse |  | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1057.5833 | 1054.5833 | 1054.5833 | 0.0032211 | 3.0544e-06 | 2014-08-02 | C | 0.0032211 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.0032211 | 3.0544e-06
1 | 1196834 | 2014-08-02 21:30 | 2014-08-03 00:06 | 155.3833 | 1 | 155.3833 | 0.00047523 | 3.0584e-06 | Restore Supply on Device X2273 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | fuses 2618 |  | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 155.3833 | 152.3833 | 152.3833 | 0.00046544 | 3.0544e-06 | 2014-08-02 | C | 0.00046544 | 3.054e-06 | 2015 | 2014-08-02 | C | 1 | 0.00046544 | 3.0544e-06
1 | 1197601 | 2014-08-02 22:30 | 2014-08-02 23:22 | 51.6333 | 47 | 2426.7667 | 0.0074221 | 0.00014375 | Restore Supply on Device IC1369 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Pole S0004 | Found jumper broken at pole S0004, Isolated between ABS IC1369, IC395 & IC382. Backfeed rest of area. Repaired jumper & re livened | F4 | PURIRI | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.6333 | 48.6333 | 2285.7667 | 0.0069817 | 0.00014356 | 2014-08-02 | C | 0.0069817 | 0.00014356 | 2015 | 2014-08-02 | C | 47 | 0.0069817 | 0.00014356
1 | 1197806 | 2014-08-03 01:21 | 2014-08-03 03:45 | 143.7833 | 133 | 17697.6167 | 0.054127 | 0.00040677 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND |  | line sectionalised and patrolled with no cause found | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 133.0648 | 130.0648 | 17298.6167 | 0.052837 | 0.00040624 | 2014-08-03 | C | 0.052837 | 0.00040624 | 2015 | 2014-08-03 | C | 133 | 0.052837 | 0.00040624
1 | 1199021 | 2014-08-03 04:30 | 2014-08-03 17:35 | 785 | 5 | 3925 | 0.012004 | 1.5292e-05 | Restore Supply on Device CA465 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | pole 725014 | Tripping on Fuses CA465. Fault tree through lines, all 3 conductors broken and repaired and full crossarm assembly. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 785 | 782 | 3910 | 0.011943 | 1.5272e-05 | 2014-08-03 | C | 0.011943 | 1.5272e-05 | 2015 | 2014-08-03 | C | 5 | 0.011943 | 1.5272e-05
1 | 1199001 | 2014-08-03 06:07 | 2014-08-03 11:39 | 331.45 | 52 | 6847.7667 | 0.020943 | 0.00015904 | Restore Supply on Device 3390T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | pole 761273 | 2x broken hv insulators + binders @ pole 761273 - replaced Cause unknown Full power restored adjacent asset checked & identified the 2nd insulator blown - which as noted above | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 131.6878 | 128.6878 | 6691.7667 | 0.020439 | 0.00015883 | 2014-08-03 | C | 0.020439 | 0.00015883 | 2015 | 2014-08-03 | C | 52 | 0.020439 | 0.00015883
1 | 1199015 | 2014-08-03 07:47 | 2014-08-03 12:31 | 284.1167 | 119 | 11763.4 | 0.035977 | 0.00036395 | Restore Supply on Device T7/606 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | Pole P45184 | Fuse found blown at Recloser Q81. CB Opened Fuses replaced with Solid links as per Powerco standards. Tree found across line at Pole P45184. Isolation at ABS Q85. NDR Report #19109. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 98.8521 | 95.8521 | 11406.4 | 0.03484 | 0.00036348 | 2014-08-03 | C | 0.03484 | 0.00036348 | 2015 | 2014-08-03 | C | 119 | 0.03484 | 0.00036348
1 | 1199428 | 2014-08-03 11:11 | 2014-08-03 14:34 | 202.35 | 1 | 202.35 | 0.00061887 | 3.0584e-06 | Restore Supply on Device X1793 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1000 ruahine road, MANGAWEKA | Replaced broken 2A HV fuse. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 202.35 | 199.35 | 199.35 | 0.0006089 | 3.0544e-06 | 2014-08-03 | C | 0.0006089 | 3.054e-06 | 2015 | 2014-08-03 | C | 1 | 0.0006089 | 3.0544e-06
1 | 1199928 | 2014-08-03 12:37 | 2014-08-03 14:08 | 91.3833 | 361 | 20782.4167 | 0.063561 | 0.0011041 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | KAI IWI - CB8 MISSION RD | CB8 tripped on E/F, C Phase O/C. Patrolled nothing found. Roger Bland attended. | F4 | MISSION RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 57.569 | 54.569 | 19699.4167 | 0.06017 | 0.0011026 | 2014-08-03 | C | 0.06017 | 0.0011026 | 2015 | 2014-08-03 | C | 361 | 0.06017 | 0.0011026
1 | 1200375 | 2014-08-03 14:56 | 2014-08-03 16:06 | 69.8667 | 1 | 69.8667 | 0.00021368 | 3.0584e-06 | Restore Supply on Device W2470 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | W2470 | 3amp HV fuse DDO fuse, No other assets repaired or replaced on site. Adjacent assets checked and they are up to Powerco standard. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 69.8667 | 66.8667 | 66.8667 | 0.00020424 | 3.0544e-06 | 2014-08-03 | C | 0.00020424 | 3.054e-06 | 2015 | 2014-08-03 | C | 1 | 0.00020424 | 3.0544e-06
1 | 1200492 | 2014-08-03 15:36 | 2014-08-03 16:00 | 24.7 | 2 | 42 | 0.00012845 | 6.1168e-06 | Restore Supply on Device T2/333 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | p43903 | HV tx HRC fuse 3amp -OH,No other assets repaired or replaced on site. Checked adjacent assets and all up to Powerco standard. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 21 | 18 | 36 | 0.00010996 | 6.1088e-06 | 2014-08-03 | C | 0.00010996 | 6.109e-06 | 2015 | 2014-08-03 | C | 2 | 0.00010996 | 6.1088e-06
1 | 1200529 | 2014-08-03 16:01 | 2014-08-03 17:10 | 68.9167 | 1 | 68.9167 | 0.00021078 | 3.0584e-06 | Restore Supply on Device TF6-016 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | - |  | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 68.9167 | 65.9167 | 65.9167 | 0.00020134 | 3.0544e-06 | 2014-08-03 | C | 0.00020134 | 3.054e-06 | 2015 | 2014-08-03 | C | 1 | 0.00020134 | 3.0544e-06
1 | 1200540 | 2014-08-03 16:15 | 2014-08-03 19:51 | 216.0167 | 891 | 7403 | 0.022641 | 0.0027251 | Restore Supply on Device 338 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB338 | Dougla Substation CB338 tripped. Line patrolled. Supply restored with no apparent fault found. Nick Webby attended. | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 8.3086 | 5.3086 | 4730 | 0.014447 | 0.0027215 | 2014-08-03 | C | 0.014447 | 0.0027215 | 2015 | 2014-08-03 | C | 891 | 0.014447 | 0.0027215
1 | 1201597 | 2014-08-03 19:55 | 2014-08-03 20:39 | 43.8 | 1 | 43.8 | 0.00013396 | 3.0584e-06 | Restore Supply on Device TC4-005 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | as per details |  | F3 | PILLANS POINT | OTUMOETAI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 43.8 | 40.8 | 40.8 | 0.00012462 | 3.0544e-06 | 2014-08-03 | C | 0.00012462 | 3.054e-06 | 2015 | 2014-08-03 | C | 1 | 0.00012462 | 3.0544e-06
1 | 1201459 | 2014-08-03 20:15 | 2014-08-03 21:05 | 50 | 89 | 4450 | 0.01361 | 0.0002722 | Restore Supply on Device T4121 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 8061 | Repaired jumpers on pole 855621. (1201496 was cancelled) | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 4183 | 0.012777 | 0.00027184 | 2014-08-03 | C | 0.012777 | 0.00027184 | 2015 | 2014-08-03 | C | 89 | 0.012777 | 0.00027184
1 | 1202565 | 2014-08-04 07:03 | 2014-08-04 09:48 | 165.4333 | 2 | 220.9833 | 0.00067586 | 6.1168e-06 | Restore Supply on Device TB1-051 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 20 Hot Springs Road, Katikati | lv line 2 phases twisted together. seperated those and replaced 3amp HV fuse and a 2 x 100 amp transformer fuse. No other assets repaired or replaced on site. Checked adjacent assets and all up to Powerco standard.. cause unknown. Hilton was assigne | F4 | KATIKATI | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 110.4917 | 107.4917 | 214.9833 | 0.00065665 | 6.1088e-06 | 2014-08-04 | C | 0.00065665 | 6.109e-06 | 2015 | 2014-08-04 | C | 2 | 0.00065665 | 6.1088e-06
1 | 1014567 | 2014-08-04 08:46 | 2014-08-04 15:31 | 405.7167 | 57 | 15107.2167 | 0.046204 | 0.00017433 | NAPA ID:00862 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227538 | Approved. Replace pole and arms and reconductor feeder CB2 in Shut 1. Install TEMP Links 26 at pole 227538 for Shuts 2 & 4. Work Location: Old Coach Road and Ohinepanea Road. IR4847 & W/O 10140907 | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 265.0389 | 262.0389 | 14936.2167 | 0.045622 | 0.0001741 | 2014-08-04 | B | 0.022811 | 8.7051e-05 | 2015 | 2014-08-04 | B | 57 | 0.045622 | 0.0001741
1 | 926612 | 2014-08-04 09:40 | 2014-08-04 12:45 | 185 | 3 | 555 | 0.0016974 | 9.1753e-06 | NAPA ID:00702 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2438 | Approved. Change Transformer 2438 and upgrade earths. Work Location is Sibera Station, 7165 Turakina Valley Road. Work Order# 101483231. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 185 | 182 | 546 | 0.0016677 | 9.1633e-06 | 2014-08-04 | B | 0.00083386 | 4.582e-06 | 2015 | 2014-08-04 | B | 3 | 0.0016677 | 9.1633e-06
1 | 1203665 | 2014-08-04 13:17 | 2014-08-04 14:45 | 88 | 2 | 176 | 0.00053828 | 6.1168e-06 | Restore Supply on Device T1/383 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Transformer T1/383 |  | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 170 | 0.00051925 | 6.1088e-06 | 2014-08-04 | C | 0.00051925 | 6.109e-06 | 2015 | 2014-08-04 | C | 2 | 0.00051925 | 6.1088e-06
1 | 386545 | 2014-08-05 07:52 | 2014-08-05 16:16 | 503.6167 | 236 | 118853.5333 | 0.3635 | 0.00072179 | NAPA ID:00447 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Te Ore Ore CB C827 | Replace 11kV poles and install Links TEMP 84 & TEMP85. Work Location: Gordon Street, Masterton. Work Order # 10138778. | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 503.6167 | 500.6167 | 118145.5333 | 0.36087 | 0.00072084 | 2014-08-05 | B | 0.18043 | 0.00036042 | 2015 | 2014-08-05 | B | 236 | 0.36087 | 0.00072084
1 | 1017403 | 2014-08-05 08:34 | 2014-08-05 13:34 | 300.5 | 44 | 8839.0833 | 0.027034 | 0.00013457 | NAPA ID:00833 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 803217, 803264, 803057, 803208, 803262 | Please read additional notes section, part of shut down to be relivened at 11am after new ABS 4690/1 connected and commissioned, Saidi mitigation. Replace poles & conductor along Santoft Road from Lake Alice Road intersection to approx. 1km from Duncan R | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 200.8883 | 197.8883 | 8707.0833 | 0.026595 | 0.00013439 | 2014-08-05 | B | 0.013298 | 6.7197e-05 | 2015 | 2014-08-05 | B | 44 | 0.026595 | 0.00013439
1 | 1027458 | 2014-08-05 08:49 | 2014-08-05 14:26 | 337.1333 | 1 | 337.1333 | 0.0010311 | 3.0584e-06 | NAPA ID:00568 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P1222 | Approved. Replacing 11kV & 400V arms and straightening pole P1222. Work Location: Moore Street, Waihi | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 337.1333 | 334.1333 | 334.1333 | 0.0010206 | 3.0544e-06 | 2014-08-05 | B | 0.00051029 | 1.527e-06 | 2015 | 2014-08-05 | B | 1 | 0.0010206 | 3.0544e-06
1 | 1027647 | 2014-08-05 09:15 | 2014-08-05 14:58 | 342.9833 | 42 | 14405.3 | 0.044057 | 0.00012845 | NAPA ID:00535 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 205773 | Approved. Change poles & cross arms on Stewart Road. Work Location: Stewart Road. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 342.9833 | 339.9833 | 14279.3 | 0.043615 | 0.00012829 | 2014-08-05 | B | 0.021808 | 6.4143e-05 | 2015 | 2014-08-05 | B | 42 | 0.043615 | 0.00012829
1 | 1035892 | 2014-08-05 10:13 | 2014-12-03 09:12 | 172738.6667 | 2 | 276.9167 | 0.00084693 | 6.1168e-06 | NAPA ID:00869 TP_HAWERA GXP > MANAIA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Manaia Substation | Approved. Crane new Sub Transformer into Manaia Sub spare Transformer Bay to be connected at a later date. Work Area: Manaia Substation - corner of Manaia Road and Normanby Road, Taranaki | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 138.4583 | 135.4583 | 270.9167 | 0.00082749 | 6.1088e-06 | 2014-08-05 | B | 0.00041375 | 3.054e-06 | 2015 | 2014-08-05 | B | 2 | 0.00082749 | 6.1088e-06
1 | 1205353 | 2014-08-05 11:56 | 2014-08-05 14:22 | 145.5667 | 533 | 51336.3667 | 0.15701 | 0.0016301 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 219824 | Tripped to L/O - line sectionalised & patrolled - floating conductor located at pole 219824 - isolations for repair between ABS SD5-009 & SD5-008 - delays in backfeeding due to faulty controller on recloser 9462/2 - DNO has been issued for repairs for thi | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 96.3159 | 93.3159 | 49737.3667 | 0.15192 | 0.001628 | 2014-08-05 | C | 0.15192 | 0.001628 | 2015 | 2014-08-05 | C | 533 | 0.15192 | 0.001628
1 | 4217763 | 2014-08-05 17:55 | 2014-08-06 00:15 | 380 | 1246 | 180578 | 0.55228 | 0.0038108 | Restore Supply on Device C855 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Sw/Gear C1015 | Restaged outage | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 144.9262 | 141.9262 | 176840 | 0.54014 | 0.0038058 | 2014-08-05 | C | 0.54014 | 0.0038058 | 2015 | 2014-08-05 | C | 1246 | 0.54014 | 0.0038058
1 | 1261791 | 2014-08-06 02:24 | 2014-08-06 04:22 | 117.7 | 114 | 8778.15 | 0.026847 | 0.00034866 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C634 | Trip on CB C634 on E/F. patrolled / nothing found. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 77.0013 | 74.0013 | 8436.15 | 0.025768 | 0.0003482 | 2014-08-06 | C | 0.025768 | 0.0003482 | 2015 | 2014-08-06 | C | 114 | 0.025768 | 0.0003482
1 | 1262506 | 2014-08-06 08:40 | 2014-08-06 10:26 | 105.2 | 9 | 378.1667 | 0.0011566 | 2.7526e-05 | Restore Supply on Device T1012 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T466 | PLEASE CHECK CLOSE JOBS ON MAP MAY BE LINKED 2 X 11KV HT LINKS DUE TO LINE CLASH | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 42.0185 | 39.0185 | 351.1667 | 0.0010726 | 2.749e-05 | 2014-08-06 | C | 0.0010726 | 2.749e-05 | 2015 | 2014-08-06 | C | 9 | 0.0010726 | 2.749e-05
1 | 1055636 | 2014-08-06 09:26 | 2014-08-06 14:59 | 333 | 33 | 10989 | 0.033609 | 0.00010093 | NAPA ID:00537 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses SC2-117 | Approved. Change poles and cross arms beyond 11kV Fuses SC2-117. Work Location: Turntable Hill Road & Mountier Road AONGATETE | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 333 | 330 | 10890 | 0.033263 | 0.0001008 | 2014-08-06 | B | 0.016631 | 5.0398e-05 | 2015 | 2014-08-06 | B | 33 | 0.033263 | 0.0001008
1 | 1266798 | 2014-08-06 10:15 | 2014-08-06 12:31 | 135.9833 | 1 | 135.9833 | 0.00041589 | 3.0584e-06 | Restore Supply on Device T2/810 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T2/810 | 2X 2 AMP HV LIGHTNING NO ARROS ADJACENT ASSETS UP TO STANDARD | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 135.9833 | 132.9833 | 132.9833 | 0.00040619 | 3.0544e-06 | 2014-08-06 | C | 0.00040619 | 3.054e-06 | 2015 | 2014-08-06 | C | 1 | 0.00040619 | 3.0544e-06
1 | 1268056 | 2014-08-06 10:15 | 2014-08-06 19:08 | 532.7 | 108 | 55891.25 | 0.17094 | 0.00033031 | Restore Supply on Device 6946 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | Cable past FABS 6946 | NEIL WILL OFF FOR SOME TIME, POSSIBILITY OF GENERATOR TO BE PUT IN PLACE TO PROVIDE POWER Cable hit by under boring company for Fibre install - isolated at FABS 6946 - Cable repaired - Used 1 joint kit & 3 sleeves | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 517.5116 | 514.5116 | 55567.25 | 0.16973 | 0.00032988 | 2014-08-06 | C | 0.16973 | 0.00032988 | 2015 | 2014-08-06 | C | 108 | 0.16973 | 0.00032988
1 | 1266803 | 2014-08-06 10:17 | 2014-08-06 10:53 | 36 | 16 | 576 | 0.0017617 | 4.8935e-05 | Restore Supply on Device V85 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses V86, Pole 04287 | Faultman found a broken jumper at Fuses V85 on pole P04287, line was isolated at ABS V85 to repair the jumper. Off Time 10:17 On Time 10:53 | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 36 | 33 | 528 | 0.0016127 | 4.8871e-05 | 2014-08-06 | C | 0.0016127 | 4.8871e-05 | 2015 | 2014-08-06 | C | 16 | 0.0016127 | 4.8871e-05
1 | 1205314 | 2014-08-06 10:31 | 2014-08-06 10:42 | 11 | 20 | 220 | 0.00067285 | 6.1168e-05 | NAPA ID:01495 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | T1628 | Urgent shutdown to rebind 11kV conductor Chlld jobs created due to connectivity problems in GIS while changing points on OSI | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 11 | 8 | 160 | 0.00048871 | 6.1088e-05 | 2014-08-06 | B | 0.00024435 | 3.0544e-05 | 2015 | 2014-08-06 | B | 20 | 0.00048871 | 6.1088e-05
1 | 1271063 | 2014-08-06 13:55 | 2014-08-06 17:15 | 199.5333 | 1 | 199.5333 | 0.00061026 | 3.0584e-06 | Restore Supply on Device T1053 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t1053 | tx 1053 retapped back to normal from 2.5 percent No other assets repaired or replaced on site surrounding assett good | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 199.5333 | 196.5333 | 196.5333 | 0.0006003 | 3.0544e-06 | 2014-08-06 | C | 0.0006003 | 3.054e-06 | 2015 | 2014-08-06 | C | 1 | 0.0006003 | 3.0544e-06
1 | 1272037 | 2014-08-06 18:03 | 2014-08-06 19:18 | 74.6167 | 1 | 74.6167 | 0.00022821 | 3.0584e-06 | Restore Supply on Device TC1435 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1435 | replaced 6amp ddo fuse at tx t1435 hv o/h caused - age nothing else repaired or replaced full power restored adjacent assets - all good | F4 | WAIRERE RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 74.6167 | 71.6167 | 71.6167 | 0.00021875 | 3.0544e-06 | 2014-08-06 | C | 0.00021875 | 3.054e-06 | 2015 | 2014-08-06 | C | 1 | 0.00021875 | 3.0544e-06
1 | 1002508 | 2014-08-07 08:15 | 2014-08-07 15:00 | 405 | 23 | 9315 | 0.028489 | 7.0344e-05 | NAPA ID:00838 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 887 | Approved. Reconductor along Beamish Road, Marton. WO No.10147011. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 405 | 402 | 9246 | 0.028241 | 7.0252e-05 | 2014-08-07 | B | 0.014121 | 3.5126e-05 | 2015 | 2014-08-07 | B | 23 | 0.028241 | 7.0252e-05
1 | 397728 | 2014-08-07 08:30 | 2014-08-07 13:38 | 308 | 95 | 29260 | 0.089489 | 0.00029055 | NAPA ID:00455 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 825743 | Approved, Pole replacement on Gordon Rd between poles 825743 & 825728. WO No.10138778. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 308 | 305 | 28975 | 0.088502 | 0.00029017 | 2014-08-07 | B | 0.044251 | 0.00014509 | 2015 | 2014-08-07 | B | 95 | 0.088502 | 0.00029017
1 | 373803 | 2014-08-07 09:00 | 2014-08-07 14:48 | 348 | 17 | 5916 | 0.018094 | 5.1993e-05 | NAPA ID:00456 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp Links 79 | Replace 4 poles & 8 cross arms on Pyke Road. WO No. 10156813. | F3 | WAOTU | PUTARURU SUB | TP_HINUERA | VALLEY | EASTERN ELECTRICITY | Network (Powerco) | 348 | 345 | 5865 | 0.017914 | 5.1925e-05 | 2014-08-07 | B | 0.0089571 | 2.5963e-05 | 2015 | 2014-08-07 | B | 17 | 0.017914 | 5.1925e-05
1 | 1351950 | 2014-08-07 09:15 | 2014-08-07 11:00 | 105 | 2 | 210 | 0.00064227 | 6.1168e-06 | Restore Supply on Device X1528 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1528 | Replace transformer. Work Order 10148321. Own Isolation and A/P. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 204 | 0.0006231 | 6.1088e-06 | 2014-08-07 | C | 0.0006231 | 6.109e-06 | 2015 | 2014-08-07 | C | 2 | 0.0006231 | 6.1088e-06
1 | 1068837 | 2014-08-07 09:57 | 2014-08-07 16:48 | 411.05 | 1 | 411.05 | 0.0012572 | 3.0584e-06 | NAPA ID:00852 TP_MT MAUNGANUI 33 GXP > TRITON SUB > FERT WORKS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB 6 | Approved. Through joint new section of cable in existing cable. Work Location: Cnr totara Street & Maui Street | F1 | FERT WORKS | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 411.05 | 408.05 | 408.05 | 0.0012464 | 3.0544e-06 | 2014-08-07 | B | 0.00062318 | 1.527e-06 | 2015 | 2014-08-07 | B | 1 | 0.0012464 | 3.0544e-06
1 | 1351948 | 2014-08-07 11:15 | 2014-08-14 15:46 | 10351.3333 | 1 | 75 | 0.00022938 | 3.0584e-06 | Restore Supply on Device X2652 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2652 | Replace transformer. Work Order 10148321. Own Isolation and A/P. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 75 | 72 | 72 | 0.00021992 | 3.0544e-06 | 2014-08-07 | C | 0.00021992 | 3.054e-06 | 2015 | 2014-08-07 | C | 1 | 0.00021992 | 3.0544e-06
1 | 1273104 | 2014-08-07 14:26 | 2014-08-07 16:17 | 110.9667 | 10 | 1109.6667 | 0.0033938 | 3.0584e-05 | Restore Supply on Device 5158 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 763763 | Untangled HV lines. Resagged line that was hanging low. Materials used 1Cu sleeve for no. 8 wire. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 110.9667 | 107.9667 | 1079.6667 | 0.0032978 | 3.0544e-05 | 2014-08-07 | C | 0.0032978 | 3.0544e-05 | 2015 | 2014-08-07 | C | 10 | 0.0032978 | 3.0544e-05
1 | 1273457 | 2014-08-07 17:21 | 2014-08-07 19:34 | 133.3 | 1 | 133.3 | 0.00040769 | 3.0584e-06 | Restore Supply on Device T4016 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 387C JOHNS WAY, MARTINBOROUGH | REPLACED 2X 10 AMP 11KV FUSE 7385 hv o/h cause - branch on line full power restored no other asset repaired or replaced adjacent assets - all good | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 133.3 | 130.3 | 130.3 | 0.00039799 | 3.0544e-06 | 2014-08-07 | C | 0.00039799 | 3.054e-06 | 2015 | 2014-08-07 | C | 1 | 0.00039799 | 3.0544e-06
1 | 1273401 | 2014-08-07 18:23 | 2014-08-07 18:45 | 22 | 1 | 22 | 6.7285e-05 | 3.0584e-06 | Restore Supply on Device T1/487 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses L35 | 11kv jumper broken. Assistance required to repair broken 11kv jumper Please assign Dave Whale Repaired broken jumper to transformer T1/520 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 19 | 5.8034e-05 | 3.0544e-06 | 2014-08-07 | C | 5.8034e-05 | 3.054e-06 | 2015 | 2014-08-07 | C | 1 | 5.8034e-05 | 3.0544e-06
1 | 1275375 | 2014-08-08 04:42 | 2014-08-08 14:46 | 603.9 | 1 | 603.9 | 0.001847 | 3.0584e-06 | Restore Supply on Device 4140T | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | ABS5619 | GO TO ABS 5229 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 603.9 | 600.9 | 600.9 | 0.0018354 | 3.0544e-06 | 2014-08-08 | C | 0.0018354 | 3.054e-06 | 2015 | 2014-08-08 | C | 1 | 0.0018354 | 3.0544e-06
1 | 1287088 | 2014-08-08 06:44 | 2014-08-08 14:36 | 472.2501 | 3 | 26476.1167 | 0.080975 | 9.1753e-06 | Restore Supply on Device T6/251 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T6/251 | BLOWN TX T6/251 2R REQUEST SENT TO CHANGE TX replaced blown tx with temp tx until powerco approve permanent repair. Transformer that was replaced was a tx that is no longer used - David advised that they will either need to refurbish a tx they have | F3 | PIONEER | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 8825.3722 | 8822.3722 | 26467.1167 | 0.080842 | 9.1633e-06 | 2014-08-08 | C | 0.080842 | 9.163e-06 | 2015 | 2014-08-08 | C | 3 | 0.080842 | 9.1633e-06
1 | 1297339 | 2014-08-08 07:23 | 2014-08-08 12:49 | 326 | 258 | 53686.6667 | 0.1642 | 0.00078907 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 709060 | Line Down. Opened feeder due to line down burning on ground. Materials used 5 Comp Sleeves, 3 Metres Ferret Wire. Privately owned trees contacted lines. NDR43021. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 208.0879 | 205.0879 | 52912.6667 | 0.16162 | 0.00078804 | 2014-08-08 | C | 0.16162 | 0.00078804 | 2015 | 2014-08-08 | C | 258 | 0.16162 | 0.00078804
1 | 1112721 | 2014-08-08 08:15 | 2014-08-12 14:01 | 6105.6833 | 13 | 17271.3667 | 0.052823 | 3.9759e-05 | NAPA ID:00863 TP_TE MATAI GXP > PONGAKAWA SUB | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 321260 | Approved. Create an 11kV Line Break and apply cover ups at pole 321260. Work Location: Ohinepanea Road, Pongakawa Project Number IR4847 | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 1328.5667 | 1325.5667 | 17232.3667 | 0.052635 | 3.9708e-05 | 2014-08-08 | B | 0.026317 | 1.9854e-05 | 2015 | 2014-08-08 | B | 13 | 0.052635 | 3.9708e-05
1 | 1049745 | 2014-08-08 09:00 | 2014-08-08 10:00 | 60 | 7 | 420 | 0.0012845 | 2.1409e-05 | NAPA ID:00620 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2581 | Approved. Change 15kVA transformer X2581. Work Location: 1039 Ruanui Road. OFF AT 09:00 ON AT 10:00. | F3 | BROOKLANDS 6 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 399 | 0.0012187 | 2.1381e-05 | 2014-08-08 | B | 0.00060936 | 1.069e-05 | 2015 | 2014-08-08 | B | 7 | 0.0012187 | 2.1381e-05
1 | 1297604 | 2014-08-08 09:07 | 2014-08-08 17:21 | 493.9167 | 4 | 1474.4167 | 0.0045094 | 1.2234e-05 | Restore Supply on Device V52 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | v53 | 2x 6amp ddos due to wind no other assets repaired or replaced adjacent assets up to powerco standard | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 368.6042 | 365.6042 | 1462.4167 | 0.0044668 | 1.2218e-05 | 2014-08-08 | C | 0.0044668 | 1.2218e-05 | 2015 | 2014-08-08 | C | 4 | 0.0044668 | 1.2218e-05
1 | 1089283 | 2014-08-08 09:15 | 2014-08-08 10:45 | 90 | 10 | 900 | 0.0027526 | 3.0584e-05 | NAPA ID:00950 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 223813 | Approved. Repairs to HV Stay Wires. Work Location: Mangatoi Road | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 870 | 0.0026573 | 3.0544e-05 | 2014-08-08 | B | 0.0013287 | 1.5272e-05 | 2015 | 2014-08-08 | B | 10 | 0.0026573 | 3.0544e-05
1 | 1068902 | 2014-08-08 09:22 | 2014-08-08 14:43 | 320.6 | 20 | 6412 | 0.019611 | 6.1168e-05 | NAPA ID:00571 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | cb1 | Alternate Date Applied: Short of staff for 07.08. | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 320.6 | 317.6 | 6352 | 0.019402 | 6.1088e-05 | 2014-08-08 | B | 0.0097009 | 3.0544e-05 | 2015 | 2014-08-08 | B | 20 | 0.019402 | 6.1088e-05
1 | 1026545 | 2014-08-08 09:23 | 2014-08-08 12:15 | 171.9667 | 1 | 171.9667 | 0.00052595 | 3.0584e-06 | NAPA ID:00738 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC947 | Approved. To replace 400v cross arms. Work Location: 252 Waghorn Road. Outage Steps reflected in OMS Job ID 1297940 | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 171.9667 | 168.9667 | 168.9667 | 0.0005161 | 3.0544e-06 | 2014-08-08 | B | 0.00025805 | 1.527e-06 | 2015 | 2014-08-08 | B | 1 | 0.0005161 | 3.0544e-06
1 | 1297943 | 2014-08-08 09:24 | 2014-08-08 11:17 | 112.7167 | 4 | 318.3833 | 0.00097375 | 1.2234e-05 | Restore Supply on Device T3/250 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | na | heard a pop noise before the power went out. 11kv fault, recloser had opened unknown why. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 79.5958 | 76.5958 | 306.3833 | 0.00093582 | 1.2218e-05 | 2014-08-08 | C | 0.00093583 | 1.2218e-05 | 2015 | 2014-08-08 | C | 4 | 0.00093582 | 1.2218e-05
1 | 1026217 | 2014-08-08 09:24 | 2014-08-08 12:14 | 170.4 | 4 | 681.6 | 0.0020846 | 1.2234e-05 | NAPA ID:00712 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3390 | Thanks Murray good work. To replace LV Crossarms on TC3390. Work Lcoation: Wardville Road, Walton | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 170.4 | 167.4 | 669.6 | 0.0020452 | 1.2218e-05 | 2014-08-08 | B | 0.0010226 | 6.109e-06 | 2015 | 2014-08-08 | B | 4 | 0.0020452 | 1.2218e-05
1 | 1124673 | 2014-08-08 09:36 | 2014-08-08 11:57 | 141 | 3 | 406.2667 | 0.0012425 | 9.1753e-06 | NAPA ID:00509 TP_HINUERA GXP > TOWER ROAD SUB | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2934, TC3157 | Approved. Isolate section of feeder beyond FP79 and reconfigure 11kV jumpers to supply TC2934 and TC3157 from CB 2 to CB3 Tower Road. Then remove 11kV Fuses FP79 from CB3 Tower Road. | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 135.4222 | 132.4222 | 397.2667 | 0.0012134 | 9.1633e-06 | 2014-08-08 | B | 0.00060671 | 4.582e-06 | 2015 | 2014-08-08 | B | 3 | 0.0012134 | 9.1633e-06
1 | 1298016 | 2014-08-08 09:41 | 2014-08-08 13:37 | 235.6167 | 16 | 3769.8667 | 0.01153 | 4.8935e-05 | Restore Supply on Device V77 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04216 | Floating conductor located at pole. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 235.6167 | 232.6167 | 3721.8667 | 0.011368 | 4.8871e-05 | 2014-08-08 | C | 0.011368 | 4.8871e-05 | 2015 | 2014-08-08 | C | 16 | 0.011368 | 4.8871e-05
1 | 1298062 | 2014-08-08 09:50 | 2014-08-08 13:13 | 202.6 | 1 | 202.6 | 0.00061964 | 3.0584e-06 | Restore Supply on Device T927 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 819275 | 2X 10 AMP FUSES AND FUSE HOLDER NO OTHER ASSETS REPAIRED OR REPLACED WHILE ON SITE DEFECTING LINKS AT POLE Adjacent assets checked and they are up to Powerco standard. | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 202.6 | 199.6 | 199.6 | 0.00060966 | 3.0544e-06 | 2014-08-08 | C | 0.00060966 | 3.054e-06 | 2015 | 2014-08-08 | C | 1 | 0.00060966 | 3.0544e-06
1 | 1049718 | 2014-08-08 10:30 | 2014-08-08 12:30 | 120 | 2 | 240 | 0.00073402 | 6.1168e-06 | NAPA ID:00629 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2313 | Approved. Change 15kVA transformer X2313. Work Location: 1243 Ruanui Road, Taihape. Off At 10:30 On At 12:30. | F3 | BROOKLANDS 6 | BROOKLANDS SUB | TP_CARRINGTON | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 234 | 0.00071474 | 6.1088e-06 | 2014-08-08 | B | 0.00035737 | 3.054e-06 | 2015 | 2014-08-08 | B | 2 | 0.00071474 | 6.1088e-06
1 | 1299545 | 2014-08-08 12:45 | 2014-08-08 13:52 | 67.6833 | 108 | 7248.9833 | 0.02217 | 0.00033031 | Restore Supply on Device 789 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | pole 790969 | Rotten cross arm at pole 790969. Isolated for safety. Cross arm assembly replaced. Power restored. | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 67.1202 | 64.1202 | 6924.9833 | 0.021152 | 0.00032988 | 2014-08-08 | C | 0.021152 | 0.00032988 | 2015 | 2014-08-08 | C | 108 | 0.021152 | 0.00032988
1 | 1308509 | 2014-08-08 14:54 | 2014-08-08 17:13 | 138.6333 | 1942 | 112411.7667 | 0.3438 | 0.0059395 | Restore Supply on Device 178 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole P30613 | Combines with OMS Outage 1310824. CB21 TRipped E/F Ph A O/C. Blown Insulator located at Pole P30613. Insulator replaced. Dave Whale attended. Also refer to OMS Outage 1310824 for subsequent tripping of CB 21during staged restoration of this outage. Pr | F2 | BUSINESS | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 57.8845 | 54.8845 | 106585.7667 | 0.32556 | 0.0059317 | 2014-08-08 | C | 0.32556 | 0.0059317 | 2015 | 2014-08-08 | C | 1942 | 0.32556 | 0.0059317
1 | 1312774 | 2014-08-08 17:40 | 2014-08-08 21:35 | 234.7833 | 1 | 234.7833 | 0.00071807 | 3.0584e-06 | Restore Supply on Device T5/109 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N | 3 X HT FUSE LINKS 3AMP HV OH TX T5109 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 234.7833 | 231.7833 | 231.7833 | 0.00070796 | 3.0544e-06 | 2014-08-08 | C | 0.00070796 | 3.054e-06 | 2015 | 2014-08-08 | C | 1 | 0.00070796 | 3.0544e-06
1 | 1312813 | 2014-08-08 18:30 | 2014-08-08 22:07 | 216.8167 | 18 | 3902.7 | 0.011936 | 5.5052e-05 | Restore Supply on Device 6774 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE |  | REPLACED 10 AMP HV FUSES OH COMPLETE SET. Control approved second response this is 2 r activity but they did not request this. Locked referred to Richard. | F3 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 216.8167 | 213.8167 | 3848.7 | 0.011756 | 5.498e-05 | 2014-08-08 | C | 0.011756 | 5.498e-05 | 2015 | 2014-08-08 | C | 18 | 0.011756 | 5.498e-05
1 | 1273038 | 2014-08-08 22:21 | 2014-08-08 22:55 | 34 | 226 | 7684 | 0.023501 | 0.0006912 | NAPA ID:01460 TP_GREYTOWN GXP > KEMPTON SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Kempton T1 | FIrmware upgrade on T1 relays. Secondary injection. Works location: Kempton Zone Substation. WO 10119573. | F1 | FERT WORKS | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 7006 | 0.021399 | 0.0006903 | 2014-08-08 | B | 0.0107 | 0.00034515 | 2015 | 2014-08-08 | B | 226 | 0.021399 | 0.0006903
1 | 1313254 | 2014-08-08 22:30 | 2014-08-09 12:00 | 809.2667 | 28 | 1103.5667 | 0.0033752 | 8.5636e-05 | Restore Supply on Device T741 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | POLE 817359 | Car V Pole at Pole 817359. Pole being held up by Hiab until morning. Pole to be replaced in the morning. Pole replaced under OMS# 1324239 (Switching Instruction # 144626) on 09/08/2014. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 39.4131 | 36.4131 | 1019.5667 | 0.0031142 | 8.5524e-05 | 2014-08-08 | C | 0.0031142 | 8.5524e-05 | 2015 | 2014-08-08 | C | 28 | 0.0031142 | 8.5524e-05
1 | 1313315 | 2014-08-09 00:16 | 2014-08-09 05:41 | 325.3167 | 142 | 13184.55 | 0.040324 | 0.0004343 | Restore Supply on Device 575 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 405 | line down found while sectionlising past Fuses 405- due to coms issues control of lines past Fuses 405 handed over to fultman - isolated at fuses 405 line repairred - used 2x sleeves & 2m of conductor. Faultman still to provide pole number. This FR covers | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 92.8489 | 89.8489 | 12758.55 | 0.03897 | 0.00043373 | 2014-08-09 | C | 0.03897 | 0.00043373 | 2015 | 2014-08-09 | C | 142 | 0.03897 | 0.00043373
1 | 1323954 | 2014-08-09 06:50 | 2014-08-09 22:33 | 943 | 293 | 14283 | 0.043683 | 0.00089612 | Restore Supply on Device C423 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 7101 | Replaced 2 blown HV fuses at Fuses 7101 | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 48.7474 | 45.7474 | 13404 | 0.040941 | 0.00089495 | 2014-08-09 | C | 0.040941 | 0.00089495 | 2015 | 2014-08-09 | C | 293 | 0.040941 | 0.00089495
1 | 1324119 | 2014-08-09 08:10 | 2014-08-09 09:36 | 86.1167 | 1 | 86.1167 | 0.00026338 | 3.0584e-06 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Switch Gear 4518/1 | OMS Job Number 1158940. Access to 4691W,4692W,4693W to check Transformer connections at Dairy Factory. Work Order # 10148749 | F2 | KINGS AVENUE | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 86.1167 | 83.1167 | 83.1167 | 0.00025387 | 3.0544e-06 | 2014-08-09 | C | 0.00025387 | 3.054e-06 | 2015 | 2014-08-09 | C | 1 | 0.00025387 | 3.0544e-06
1 | 1324138 | 2014-08-09 08:51 | 2014-08-09 14:09 | 318 | 27 | 8586 | 0.02626 | 8.2577e-05 | Restore Supply on Device Q38 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer T7/456 | Replace broken 11kV pole - Temporary Line Break created at pole P16382. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 318 | 315 | 8505 | 0.025978 | 8.2469e-05 | 2014-08-09 | C | 0.025978 | 8.2469e-05 | 2015 | 2014-08-09 | C | 27 | 0.025978 | 8.2469e-05
1 | 1324189 | 2014-08-09 08:51 | 2014-08-09 14:09 | 318 | 28 | 8904 | 0.027232 | 8.5636e-05 | Restore Supply on Device T7/456 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer T7/454 | PART OF SHUTDOWN NAPA 842 | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 318 | 315 | 8820 | 0.02694 | 8.5524e-05 | 2014-08-09 | C | 0.02694 | 8.5524e-05 | 2015 | 2014-08-09 | C | 28 | 0.02694 | 8.5524e-05
1 | 1324239 | 2014-08-09 09:12 | 2014-08-09 11:40 | 148.1167 | 27 | 3999.15 | 0.012231 | 8.2577e-05 | Restore Supply on Device S349 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 817359 | Used 1X Pole 1X H/T Arm 2X L/V Arms 3X H/T Insulators 8X L/V Isulators Charge to customer. Pole repaired following car vs pole (refer OMS 131254/131287). | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 148.1167 | 145.1167 | 3918.15 | 0.011968 | 8.2469e-05 | 2014-08-09 | C | 0.011968 | 8.2469e-05 | 2015 | 2014-08-09 | C | 27 | 0.011968 | 8.2469e-05
1 | 1324491 | 2014-08-09 17:47 | 2014-08-09 19:40 | 112.5333 | 1 | 112.5333 | 0.00034417 | 3.0584e-06 | Restore Supply on Device TP556 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP518 | 2 15amp fuses | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 112.5333 | 109.5333 | 109.5333 | 0.00033456 | 3.0544e-06 | 2014-08-09 | C | 0.00033456 | 3.054e-06 | 2015 | 2014-08-09 | C | 1 | 0.00033456 | 3.0544e-06
1 | 1324626 | 2014-08-09 22:34 | 2014-08-09 23:37 | 63.6 | 1 | 63.6 | 0.00019452 | 3.0584e-06 | Restore Supply on Device 2075T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 732769 | Pot head on pole 732769 has com away from pole and hanging by jumper, access not good and pole suspect, faultman to orginise team to attend in morning. Customer advised and happy | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 63.6 | 60.6 | 60.6 | 0.0001851 | 3.0544e-06 | 2014-08-09 | C | 0.0001851 | 3.054e-06 | 2015 | 2014-08-09 | C | 1 | 0.0001851 | 3.0544e-06
1 | 1298581 | 2014-08-09 23:15 | 2014-08-10 00:08 | 53.1667 | 374 | 19884.3333 | 0.060815 | 0.0011438 | NAPA ID:01642 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 828890 | Approved. Non outage job. Reconnect 11kV cable at pole 828890. Work Location: Taranaki Street. Work Order 10150690. | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 53.1667 | 50.1667 | 18762.3333 | 0.057308 | 0.0011424 | 2014-08-09 | B | 0.028654 | 0.00057118 | 2015 | 2014-08-09 | B | 374 | 0.057308 | 0.0011424
1 | 1327145 | 2014-08-10 08:03 | 2014-08-10 10:39 | 156.7 | 3 | 1854.6167 | 0.0056722 | 9.1753e-06 | Restore Supply on Device TP1625 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | K1028 | Repair H/V line down (1 x ) at pole K1028. 3 meters of conductor, 2 x H/V sleeves & re bind conductor to insulator. | F3 | MOFFAT RD | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 618.2056 | 615.2056 | 1845.6167 | 0.0056373 | 9.1633e-06 | 2014-08-10 | C | 0.0056373 | 9.163e-06 | 2015 | 2014-08-10 | C | 3 | 0.0056373 | 9.1633e-06
1 | 1327541 | 2014-08-10 14:30 | 2014-08-10 16:06 | 95.6833 | 3 | 263 | 0.00080436 | 9.1753e-06 | Restore Supply on Device T7/462 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7/462 | 2:35pm Replacing HV Transformer T7/462 | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.6667 | 84.6667 | 254 | 0.00077582 | 9.1633e-06 | 2014-08-10 | C | 0.00077582 | 9.163e-06 | 2015 | 2014-08-10 | C | 3 | 0.00077582 | 9.1633e-06
1 | 1327621 | 2014-08-10 15:49 | 2014-08-10 18:31 | 161.45 | 1 | 161.45 | 0.00049378 | 3.0584e-06 | Restore Supply on Device T1128 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | pole 810937 | No other assets repaired or replaced on site. Checked adjacent assets and up to Powerco standard. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 161.45 | 158.45 | 158.45 | 0.00048397 | 3.0544e-06 | 2014-08-10 | C | 0.00048397 | 3.054e-06 | 2015 | 2014-08-10 | C | 1 | 0.00048397 | 3.0544e-06
1 | 1327695 | 2014-08-10 19:51 | 2014-08-10 22:06 | 134.6667 | 1 | 134.6667 | 0.00041187 | 3.0584e-06 | Restore Supply on Device P2250 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | P2250 | Replaced Connection with new ALI 2 Copper connection | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 134.6667 | 131.6667 | 131.6667 | 0.00040217 | 3.0544e-06 | 2014-08-10 | C | 0.00040217 | 3.054e-06 | 2015 | 2014-08-10 | C | 1 | 0.00040217 | 3.0544e-06
1 | 1328021 | 2014-08-11 07:12 | 2014-08-11 10:20 | 188 | 501 | 16356 | 0.050024 | 0.0015323 | Restore Supply on Device WH820 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | WH840 | Replace 3x11kV DDO Fuses WH840. Pole 703330. Recloser 8820/2 used as back feed, recloser 8220 opened when ABS in Field. Need to look at earth settings this is set to fine. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 32.6467 | 29.6467 | 14853 | 0.045367 | 0.0015303 | 2014-08-11 | C | 0.045367 | 0.0015303 | 2015 | 2014-08-11 | C | 501 | 0.045367 | 0.0015303
1 | 1327906 | 2014-08-11 07:33 | 2014-08-11 09:34 | 121.4167 | 2 | 195 | 0.00059639 | 6.1168e-06 | Restore Supply on Device T2/337 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/337 | blown hv fuse - 1x 6amp hv - replaced lv fuse holder No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard? | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 97.5 | 94.5 | 189 | 0.00057729 | 6.1088e-06 | 2014-08-11 | C | 0.00057729 | 6.109e-06 | 2015 | 2014-08-11 | C | 2 | 0.00057729 | 6.1088e-06
1 | 1327933 | 2014-08-11 08:17 | 2014-08-11 13:24 | 307.1 | 1 | 307.1 | 0.00093924 | 3.0584e-06 | Restore Supply on Device TC1403 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TC1403 | replaced 2 x cut outs and 2 x 60 amp fuse and 1 x HT 2amp fuse. nothing else repaired or replaced on site. adjacent assets ok. cause: unknow, may be weatehr. oh/lv and ht. | F3 | BUFFALO BEACH | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 307.1 | 304.1 | 304.1 | 0.00092885 | 3.0544e-06 | 2014-08-11 | C | 0.00092885 | 3.054e-06 | 2015 | 2014-08-11 | C | 1 | 0.00092885 | 3.0544e-06
1 | 1026205 | 2014-08-11 09:21 | 2014-08-11 15:25 | 364.6667 | 5 | 1823.3333 | 0.0055765 | 1.5292e-05 | NAPA ID:00843 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2485. TC1080 | Thanks Wilf. Replace crossarms and other line equipment on 11kV Spur line fused via drop-out fuses FP654 Work Location: 59 Arapuni Road, Putaruru | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 364.6667 | 361.6667 | 1808.3333 | 0.0055234 | 1.5272e-05 | 2014-08-11 | B | 0.0027617 | 7.636e-06 | 2015 | 2014-08-11 | B | 5 | 0.0055234 | 1.5272e-05
1 | 373808 | 2014-08-11 09:27 | 2014-08-11 15:03 | 336 | 22 | 7389.6667 | 0.022601 | 6.7285e-05 | NAPA ID:00462 TP_LINTON GXP > KAIRANGA SUB | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | - | Creating OMS entry for imported application. Replace 4 poles and 20 crossarms and 3 transformers. Work Location is Pyke Road. Work Order #10156813. NOTE: E-map updated, appears all transformers that were offline were selected back online by OMS. to be | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 335.8939 | 332.8939 | 7323.6667 | 0.02237 | 6.7197e-05 | 2014-08-11 | B | 0.011185 | 3.3599e-05 | 2015 | 2014-08-11 | B | 22 | 0.02237 | 6.7197e-05
1 | 1053666 | 2014-08-11 09:43 | 2014-08-11 12:15 | 152.1167 | 2 | 304.2333 | 0.00093047 | 6.1168e-06 | NAPA ID:00633 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X789 | Approved. Change Transformer X789. Work Location: 230 Wairepu East Road. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 152.1167 | 149.1167 | 298.2333 | 0.00091093 | 6.1088e-06 | 2014-08-11 | B | 0.00045547 | 3.054e-06 | 2015 | 2014-08-11 | B | 2 | 0.00091093 | 6.1088e-06
1 | 1328099 | 2014-08-11 09:44 | 2014-08-11 14:23 | 278.7667 | 1 | 278.7667 | 0.00085259 | 3.0584e-06 | Restore Supply on Device 1273 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Corbett Road, | Replaced 2 x 6amp HV OH fuses. Tx1273N. Last storm the power went out. | F3 | BELL BLOCK 7 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 278.7667 | 275.7667 | 275.7667 | 0.00084231 | 3.0544e-06 | 2014-08-11 | C | 0.00084231 | 3.054e-06 | 2015 | 2014-08-11 | C | 1 | 0.00084231 | 3.0544e-06
1 | 1328706 | 2014-08-11 10:16 | 2014-08-11 15:25 | 308.25 | 5 | 1172.0333 | 0.0035846 | 1.5292e-05 | Restore Supply on Device T974 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC1752 | REPLACED 2X 15 AMP DDO FUSES HV LINK 7466 OH SURROUNDING ASSETTS ALL GOOD NOTHING ELSE REAPIRED OR REPALCED | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 234.4067 | 231.4067 | 1157.0333 | 0.0035341 | 1.5272e-05 | 2014-08-11 | C | 0.0035341 | 1.5272e-05 | 2015 | 2014-08-11 | C | 5 | 0.0035341 | 1.5272e-05
1 | 1328998 | 2014-08-11 10:50 | 2014-08-11 13:21 | 150.5833 | 78 | 11538.15 | 0.035289 | 0.00023856 | Restore Supply on Device 1133 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | Pole 854256 | Outage to Replace pole after Car accident | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 147.925 | 144.925 | 11304.15 | 0.034528 | 0.00023825 | 2014-08-11 | C | 0.034528 | 0.00023824 | 2015 | 2014-08-11 | C | 78 | 0.034528 | 0.00023825
1 | 1329710 | 2014-08-11 15:44 | 2014-08-13 11:37 | 2633.5667 | 1 | 2633.5667 | 0.0080546 | 3.0584e-06 | Restore Supply on Device 2167T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736739 | staywire is banging on a pole do not have equipment requested another crew to attend tomorrow pole 736739 33kv pole this is safe but needs to be done tomorrw and the other 4 staywires need tightening replaced 1x staywire, No other assets repaired or rep | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2633.5667 | 2630.5667 | 2630.5667 | 0.0080349 | 3.0544e-06 | 2014-08-11 | C | 0.0080349 | 3.054e-06 | 2015 | 2014-08-11 | C | 1 | 0.0080349 | 3.0544e-06
1 | 1329713 | 2014-08-11 15:51 | 2014-08-11 16:36 | 44.6167 | 2 | 89.2333 | 0.00027291 | 6.1168e-06 | Restore Supply on Device TB2-007 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TB2-007 | Replace faulty transformer. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 44.6167 | 41.6167 | 83.2333 | 0.00025423 | 6.1088e-06 | 2014-08-11 | C | 0.00025423 | 6.109e-06 | 2015 | 2014-08-11 | C | 2 | 0.00025423 | 6.1088e-06
1 | 1329850 | 2014-08-11 21:42 | 2014-08-12 04:05 | 382.7333 | 10 | 3827.3333 | 0.011706 | 3.0584e-05 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer | Part of NAPA ID 1311 | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 382.7333 | 379.7333 | 3797.3333 | 0.011599 | 3.0544e-05 | 2014-08-11 | C | 0.011599 | 3.0544e-05 | 2015 | 2014-08-11 | C | 10 | 0.011599 | 3.0544e-05
1 | 1329861 | 2014-08-11 21:42 | 2014-08-12 04:05 | 382.55 | 20 | 7651 | 0.0234 | 6.1168e-05 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Swichgear |  | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 382.55 | 379.55 | 7591 | 0.023186 | 6.1088e-05 | 2014-08-11 | C | 0.023186 | 6.1088e-05 | 2015 | 2014-08-11 | C | 20 | 0.023186 | 6.1088e-05
1 | 1329891 | 2014-08-12 05:36 | 2014-08-13 15:02 | 2006.6333 | 1 | 200.6667 | 0.00061372 | 3.0584e-06 | Restore Supply on Device 3136T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 170 Stuart Road, Hawera | 2 x hv 6 amp cause: bird flew into line. nothing else repaired or replaced on site. adjacent assets are ok. oh/hv. | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 200.6667 | 197.6667 | 197.6667 | 0.00060376 | 3.0544e-06 | 2014-08-12 | C | 0.00060376 | 3.054e-06 | 2015 | 2014-08-12 | C | 1 | 0.00060376 | 3.0544e-06
1 | 1329913 | 2014-08-12 07:15 | 2014-08-12 11:32 | 257.6833 | 1 | 257.6833 | 0.0007881 | 3.0584e-06 | Restore Supply on Device TP272 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TP266 | replaced 3amp HV fuse - cause unknown at TX TP266 No other assets repaired or replaced Adjacent assets were checked ? confirmed as being ok | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 257.6833 | 254.6833 | 254.6833 | 0.00077791 | 3.0544e-06 | 2014-08-12 | C | 0.00077791 | 3.054e-06 | 2015 | 2014-08-12 | C | 1 | 0.00077791 | 3.0544e-06
1 | 1329934 | 2014-08-12 07:45 | 2014-08-13 15:08 | 1882.9667 | 3 | 69.85 | 0.00021363 | 9.1753e-06 | Restore Supply on Device T1946 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 214 Gordon Street, Lansdowne, Masterton | replaced 2 x 6 amp fuses. cause: bird strike. oh/hv. all assets looks good from the ground. nothing else repaired or replaced on site. | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 23.2833 | 20.2833 | 60.85 | 0.00018586 | 9.1633e-06 | 2014-08-12 | C | 0.00018586 | 9.163e-06 | 2015 | 2014-08-12 | C | 3 | 0.00018586 | 9.1633e-06
1 | 1329972 | 2014-08-12 08:22 | 2014-08-12 11:20 | 178 | 8 | 1424 | 0.0043552 | 2.4467e-05 | Restore Supply on Device TC1280 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TC1280 | TC1280 - transformer blown up, and straighten poles - straighten 2 poles and a stay pole, re-sag conductors think logging truck hit the lines. Power is still off. Poles F0684 F0683 to be straightened, also a stay pole as well. 8.40am Brian advised that | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 178 | 175 | 1400 | 0.0042762 | 2.4435e-05 | 2014-08-12 | C | 0.0042762 | 2.4435e-05 | 2015 | 2014-08-12 | C | 8 | 0.0042762 | 2.4435e-05
1 | 441981 | 2014-08-12 08:30 | 2014-08-12 15:45 | 435.05 | 330 | 90364 | 0.27637 | 0.0010093 | NAPA ID:00464 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS S63 | Staged Outage | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 273.8303 | 270.8303 | 89374 | 0.27299 | 0.001008 | 2014-08-12 | B | 0.13649 | 0.00050398 | 2015 | 2014-08-12 | B | 330 | 0.27299 | 0.001008
1 | 1089260 | 2014-08-12 09:00 | 2014-08-12 14:14 | 314 | 4 | 1256 | 0.0038414 | 1.2234e-05 | NAPA ID:01029 TP_MARTON GXP > PUKEPAPA SUB > TURAKINA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1819 | Approved. Replacing transformer X1819 and poles & cross arms. Work Location: 591 Wanganui Road, Marton. Work Order 10147631. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 314 | 311 | 1244 | 0.0037997 | 1.2218e-05 | 2014-08-12 | B | 0.0018999 | 6.109e-06 | 2015 | 2014-08-12 | B | 4 | 0.0037997 | 1.2218e-05
1 | 1068847 | 2014-08-12 10:53 | 2014-08-12 14:47 | 233.2333 | 12 | 2798.8 | 0.0085599 | 3.6701e-05 | NAPA ID:01092 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 6863 | This application is to populate schedular only REF NAPA 988. Planned Job Replace Poles, Arms Between 847842 & 725869 on Tangahoe Valley Road | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 233.2333 | 230.2333 | 2762.8 | 0.0084388 | 3.6653e-05 | 2014-08-12 | B | 0.0042194 | 1.8327e-05 | 2015 | 2014-08-12 | B | 12 | 0.0084388 | 3.6653e-05
1 | 1331567 | 2014-08-12 13:59 | 2014-08-12 15:55 | 115.45 | 2 | 172.0833 | 0.0005263 | 6.1168e-06 | Restore Supply on Device TC1448 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | TC1448 | 2amp hv fuse oh removed some branches surrounding assett looks fabulous nothing else repiared or replaced | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 86.0417 | 83.0417 | 166.0833 | 0.00050729 | 6.1088e-06 | 2014-08-12 | C | 0.00050729 | 6.109e-06 | 2015 | 2014-08-12 | C | 2 | 0.00050729 | 6.1088e-06
1 | 1331677 | 2014-08-12 16:43 | 2014-08-12 17:26 | 43 | 877 | 14078 | 0.043056 | 0.0026822 | Restore Supply on Device 338 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Douglas CB 338 | CB 338 Tripped at Douglas Sub with loss of supply to Douglas & Strathmore. Back feed through Recloser 6298. Had to carryout off load of Cloton Rd CB S51 as load was to high. Need to have Regulators 8996 commissioned as voltage gets to low at Douglas. UR | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 16.0525 | 13.0525 | 11447 | 0.034964 | 0.0026787 | 2014-08-12 | C | 0.034964 | 0.0026787 | 2015 | 2014-08-12 | C | 877 | 0.034964 | 0.0026787
1 | 1332590 | 2014-08-12 17:15 | 2014-08-12 19:14 | 119.0167 | 1 | 119.0167 | 0.000364 | 3.0584e-06 | Restore Supply on Device 4401W | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 809486 | REPLACED HV FUSE 6AMP POLE 809486 HV OH DUE TO UNKNOWN COULD BE LIGHTNING SURROUNDING ASSET IS GOOD. No other assets repaired or replaced on site. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 119.0167 | 116.0167 | 116.0167 | 0.00035436 | 3.0544e-06 | 2014-08-12 | C | 0.00035436 | 3.054e-06 | 2015 | 2014-08-12 | C | 1 | 0.00035436 | 3.0544e-06
1 | 1333570 | 2014-08-13 01:37 | 2014-08-13 05:22 | 225.25 | 406 | 32736.1333 | 0.10012 | 0.0012417 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 228327 | Repair line down ( 1 x ) at pole 228327 Change to 2 fr due to materials used. 8 meters conductor & 4 x H/V sleeves | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 80.6309 | 77.6309 | 31518.1333 | 0.09627 | 0.0012401 | 2014-08-13 | C | 0.09627 | 0.0012401 | 2015 | 2014-08-13 | C | 406 | 0.09627 | 0.0012401
1 | 1335725 | 2014-08-13 06:48 | 2014-08-13 09:10 | 142.6167 | 2 | 274.9667 | 0.00084096 | 6.1168e-06 | Restore Supply on Device 7205 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | T990 | 2 X HV LINKS RELOADED 10 AMP , UNKNOWN NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | TAWAHA | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 137.4833 | 134.4833 | 268.9667 | 0.00082154 | 6.1088e-06 | 2014-08-13 | C | 0.00082154 | 6.109e-06 | 2015 | 2014-08-13 | C | 2 | 0.00082154 | 6.1088e-06
1 | 1334900 | 2014-08-13 06:59 | 2014-08-13 09:53 | 174 | 405 | 20862 | 0.063805 | 0.0012387 | Restore Supply on Device TF7-068 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 228356 | Lines Down at Pole 228356, 229 Pongakawa Bush Rd. at 06:59, Pongakawa Sub, CB 3 Rotoehu Feeder. found lines down at pole 228356. Feeder CB was opened by NOC as faultman believed lines down may still be alive. Isolated lines down at ABS SF7-011. Feeder | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 51.5111 | 48.5111 | 19647 | 0.06001 | 0.001237 | 2014-08-13 | C | 0.06001 | 0.001237 | 2015 | 2014-08-13 | C | 405 | 0.06001 | 0.001237
1 | 1336257 | 2014-08-13 08:17 | 2014-08-13 12:59 | 281.7833 | 12 | 3381.4 | 0.010342 | 3.6701e-05 | Restore Supply on Device S10 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RURAL 9 PEAKS RD MASTERTON | PART OF PLANNED SHUT DOWN NAPA:1013. Links to OMS Job# 1089133. | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 281.7833 | 278.7833 | 3345.4 | 0.010218 | 3.6653e-05 | 2014-08-13 | C | 0.010218 | 3.6653e-05 | 2015 | 2014-08-13 | C | 12 | 0.010218 | 3.6653e-05
1 | 1124639 | 2014-08-13 08:45 | 2014-08-13 14:57 | 372 | 143 | 53196 | 0.1627 | 0.00043735 | NAPA ID:00756 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 217141, 217274 | REPLACE 40 HV POLES AND ARMS, RECONDUCTOR 5 KM OF FEEDER LINE, PREP GAP AT POLE 212204 AND AT POLE 212166, INSTALL TEMP ABS 19 AT POLE 212166 , INSTALL TEMP ABS 24 AT POLE 212214. Work Location: Omanawa Road. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 372 | 369 | 52767 | 0.16117 | 0.00043678 | 2014-08-13 | B | 0.080586 | 0.00021839 | 2015 | 2014-08-13 | B | 143 | 0.16117 | 0.00043678
1 | 1124121 | 2014-08-13 09:45 | 2014-08-13 12:06 | 140.6833 | 5 | 703.4167 | 0.0021513 | 1.5292e-05 | NAPA ID:00945 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2677 | Approved. Upgrade t/f 2677 from 30 kva to 50 kva. Work Location: Napier Taihape Road | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140.6833 | 137.6833 | 688.4167 | 0.0021027 | 1.5272e-05 | 2014-08-13 | B | 0.0010514 | 7.636e-06 | 2015 | 2014-08-13 | B | 5 | 0.0021027 | 1.5272e-05
1 | 1337554 | 2014-08-13 10:21 | 2014-08-13 12:11 | 110.05 | 1 | 110.05 | 0.00033658 | 3.0584e-06 | Restore Supply on Device T5/299 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | k77 | 1 X HV 3 amp fuse due to weather no assets repaired or replaced on site adjacent assets up to standard | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 110.05 | 107.05 | 107.05 | 0.00032698 | 3.0544e-06 | 2014-08-13 | C | 0.00032698 | 3.054e-06 | 2015 | 2014-08-13 | C | 1 | 0.00032698 | 3.0544e-06
1 | 1337568 | 2014-08-13 10:46 | 2014-08-13 14:27 | 220.9833 | 2 | 376.5333 | 0.0011516 | 6.1168e-06 | Restore Supply on Device TD2-109 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD2-109 | *** When signing this job off, ask FM if oms 1337603 (1018 B Work Road, Katikati) is part of this *** actually this outage affected # 994, feeding off transformer T5017 and not TD2-109 as indicated on OMS system. Property at # 1018 B is feeding off the | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 188.2667 | 185.2667 | 370.5333 | 0.0011318 | 6.1088e-06 | 2014-08-13 | C | 0.0011318 | 6.109e-06 | 2015 | 2014-08-13 | C | 2 | 0.0011318 | 6.1088e-06
1 | 1677727 | 2014-08-13 11:34 | 2014-08-13 11:40 | 6 | 156 | 936 | 0.0028627 | 0.00047711 | Restore Supply on Device TempLine_298450 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | RC35 | tripped when battery test done. AC Power off 11:34/REclose Opened 11:37 - RC35 tripped and Sectionaliser 9720 Closed - Power restored. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 6 | 3 | 468 | 0.0014295 | 0.00047649 | 2014-08-13 | C | 0.0014295 | 0.00047649 | 2015 | 2014-08-13 | C | 156 | 0.0014295 | 0.00047649
1 | 1337645 | 2014-08-13 12:04 | 2014-08-13 14:42 | 157.9333 | 2 | 215.7167 | 0.00065975 | 6.1168e-06 | Restore Supply on Device 4026T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4026t | ht link down at tx 4026t 3 amp replaced link due to de lamination no assests repaired or replaced adjacent assets ok | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 107.8583 | 104.8583 | 209.7167 | 0.00064056 | 6.1088e-06 | 2014-08-13 | C | 0.00064056 | 6.109e-06 | 2015 | 2014-08-13 | C | 2 | 0.00064056 | 6.1088e-06
1 | 1337680 | 2014-08-13 14:10 | 2014-08-13 15:21 | 71 | 94 | 6674 | 0.020412 | 0.00028749 | Restore Supply on Device TF7-126 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 228404 | Pongakawa Sub, CB 3 Rotoehu Feeder. Found Broken 11kV Jumper at Pole 228404. Lines isolated at ABS SF7-011. Permit issued & repairs carried out. All power restored on completion. Trevor Drury Attended. 2x Conductor Joints Replaced & 1 Jumper Replaced. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 6392 | 0.019524 | 0.00028712 | 2014-08-13 | C | 0.019524 | 0.00028712 | 2015 | 2014-08-13 | C | 94 | 0.019524 | 0.00028712
1 | 1339149 | 2014-08-13 15:29 | 2014-08-13 16:16 | 47 | 877 | 13577 | 0.041524 | 0.0026822 | Restore Supply on Device 338 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Douglas Sub | CB 338 Trip E/F No fault found, this CB needs an urgent protection investigation. CB 338 By Passed Nick webby down loading event logs & settings. | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15.4812 | 12.4812 | 10946 | 0.033434 | 0.0026787 | 2014-08-13 | C | 0.033434 | 0.0026787 | 2015 | 2014-08-13 | C | 877 | 0.033434 | 0.0026787
1 | 1340041 | 2014-08-13 15:48 | 2014-08-13 18:21 | 153.5 | 1 | 153.5 | 0.00046947 | 3.0584e-06 | Restore Supply on Device 1618 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1618 | replaced 2a hv fuse o/h. deterioration, nothing else repaired or replaced, adjacent assets all good | F3 | BROOKLANDS 7 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 153.5 | 150.5 | 150.5 | 0.00045969 | 3.0544e-06 | 2014-08-13 | C | 0.00045969 | 3.054e-06 | 2015 | 2014-08-13 | C | 1 | 0.00045969 | 3.0544e-06
1 | 1340097 | 2014-08-13 16:53 | 2014-08-13 17:01 | 8 | 877 | 7016 | 0.021458 | 0.0026822 | Restore Supply on Device 338 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Douglas Sub | CB 338 Trip E/F No fault found, this CB needs an urgent protection investigation. CB 338 By Passed Nick webby down loading event logs & settings. This tripping occured before we could by pass CB 338 | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 8 | 5 | 4385 | 0.013394 | 0.0026787 | 2014-08-13 | C | 0.013394 | 0.0026787 | 2015 | 2014-08-13 | C | 877 | 0.013394 | 0.0026787
1 | 1342578 | 2014-08-13 20:29 | 2014-08-14 00:50 | 260.6833 | 146 | 19406.4 | 0.059353 | 0.00044653 | Restore Supply on Device 5475 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | Pole 764617 | CB 5475 on E/f, O/C B Phase. feeder patrolled & sectionalised. Opossum found on cross arm on johnson Rd. Removed, relivened OK. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 132.9205 | 129.9205 | 18968.4 | 0.057938 | 0.00044595 | 2014-08-13 | C | 0.057938 | 0.00044595 | 2015 | 2014-08-13 | C | 146 | 0.057938 | 0.00044595
1 | 1343012 | 2014-08-13 22:31 | 2014-08-13 23:40 | 69.6833 | 1 | 69.6833 | 0.00021312 | 3.0584e-06 | Restore Supply on Device X1532 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | pole 786016 |  | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 69.6833 | 66.6833 | 66.6833 | 0.00020368 | 3.0544e-06 | 2014-08-13 | C | 0.00020368 | 3.054e-06 | 2015 | 2014-08-13 | C | 1 | 0.00020368 | 3.0544e-06
1 | 1343314 | 2014-08-14 03:37 | 2014-08-14 13:00 | 563.1 | 1 | 563.1 | 0.0017222 | 3.0584e-06 | Restore Supply on Device L4285 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Niagara Road, Patea, transformer L4285 | Faulty transformer L4285 to be changed on Niagara rd, Patea - Refer OMS 1343296 (Partial Power). 14/8 1.28pm - replaced transformer. lightning last night. hv/oh. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 563.1 | 560.1 | 560.1 | 0.0017108 | 3.0544e-06 | 2014-08-14 | C | 0.0017108 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0017108 | 3.0544e-06
1 | 1343318 | 2014-08-14 03:49 | 2014-08-14 08:25 | 275.95 | 1 | 275.95 | 0.00084397 | 3.0584e-06 | Restore Supply on Device TC1647 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP660 fuses | replaced 2x 10amp hv fuse cause unknown No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard 7.20am unable to progress this job via locating, have emailed Wayne Hosking | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 275.95 | 272.95 | 272.95 | 0.0008337 | 3.0544e-06 | 2014-08-14 | C | 0.00083371 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0008337 | 3.0544e-06
1 | 1343321 | 2014-08-14 04:07 | 2014-08-14 06:58 | 171.2333 | 1 | 171.2333 | 0.0005237 | 3.0584e-06 | Restore Supply on Device TC1646 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC1646 | 2X HV DDO FUSES 10 AMP UNKNOWN NO OTHER ASSETS REPAIRED OR REPLACED ALL ADJACENT ASSETS OK | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 171.2333 | 168.2333 | 168.2333 | 0.00051386 | 3.0544e-06 | 2014-08-14 | C | 0.00051386 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00051386 | 3.0544e-06
1 | 1343344 | 2014-08-14 06:51 | 2014-08-14 12:35 | 344.6167 | 1 | 344.6167 | 0.001054 | 3.0584e-06 | Restore Supply on Device 5091E | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5091E | replaced 3 amp hv fuse. cause: lightning. oh/hv. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 344.6167 | 341.6167 | 341.6167 | 0.0010434 | 3.0544e-06 | 2014-08-14 | C | 0.0010434 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0010434 | 3.0544e-06
1 | 1343350 | 2014-08-14 07:11 | 2014-08-14 11:26 | 255.45 | 2 | 442.1167 | 0.0013522 | 6.1168e-06 | Restore Supply on Device X4007 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | 4510 MANGAOHANE ROAD, TAIHAPE | replace 2 x 8 amp fuses ddo rewireable fueses. cause: weather, snow. oh/hv. Also cause the outage at 5335 Mangohane Road, Taihape (oms 1343577). The fuse # 4036 went out and affected both these properties. No other assets repaired or replaced on site. Adj | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 221.0583 | 218.0583 | 436.1167 | 0.0013321 | 6.1088e-06 | 2014-08-14 | C | 0.0013321 | 6.109e-06 | 2015 | 2014-08-14 | C | 2 | 0.0013321 | 6.1088e-06
1 | 1343366 | 2014-08-14 07:24 | 2014-08-14 09:58 | 154.15 | 2 | 299.9 | 0.00091722 | 6.1168e-06 | Restore Supply on Device X358 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781477 | **** When signing off this job ask FM if oms 1343401 (618 OKAHUTIRIA ROAD) is related *** - this job is not related, also oms 1346021 not related. FM confirmed not related. James replaced 2amp HV fuse, HV ov. No other assets repaired or replaced and all a | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 149.95 | 146.95 | 293.9 | 0.0008977 | 6.1088e-06 | 2014-08-14 | C | 0.0008977 | 6.109e-06 | 2015 | 2014-08-14 | C | 2 | 0.0008977 | 6.1088e-06
1 | 1343394 | 2014-08-14 07:35 | 2014-08-14 09:03 | 88.0333 | 3 | 222.3333 | 0.00067999 | 9.1753e-06 | Restore Supply on Device TD3-038 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TBC | HV barrell/fuse was broken. 3 amp fuse replaced and a barrel also. no other assets repaired or replaced on site.- checked the adjacent assets. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 74.1111 | 71.1111 | 213.3333 | 0.00065161 | 9.1633e-06 | 2014-08-14 | C | 0.00065161 | 9.163e-06 | 2015 | 2014-08-14 | C | 3 | 0.00065161 | 9.1633e-06
1 | 1343401 | 2014-08-14 07:39 | 2014-08-14 11:49 | 249.7167 | 1 | 249.7167 | 0.00076374 | 3.0584e-06 | Restore Supply on Device X269 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X269 | Replaced 2x 2amp HV fuses and the fuse holders pole 781011. No other assets repaired or replaced and all adjacent assets checked and are ok / up to Powerco standard? Faultman was sent 618 OKAHUTIRIA ROAD not the destination specified this took an extra h | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 249.7167 | 246.7167 | 246.7167 | 0.00075358 | 3.0544e-06 | 2014-08-14 | C | 0.00075358 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00075358 | 3.0544e-06
1 | 442009 | 2014-08-14 08:30 | 2014-08-14 15:42 | 432.4333 | 136 | 27813.3333 | 0.085065 | 0.00041595 | NAPA ID:00467 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | as per | Approved | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 204.5098 | 201.5098 | 27405.3333 | 0.083708 | 0.0004154 | 2014-08-14 | B | 0.041854 | 0.0002077 | 2015 | 2014-08-14 | B | 136 | 0.083708 | 0.0004154
1 | 1343620 | 2014-08-14 08:46 | 2014-08-14 15:52 | 426.0167 | 325 | 30360 | 0.092854 | 0.00099399 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole I2687 | Recloser 9121 Auto Reclosed and tripped L/O E/F. Line Patrolled and broken termination arm found on pole I2687. Isolated between ABS 2605 & ABS 1220. Back feed applied from Recloser 9718. Broken Termination Arm replaced. Materials used: 2 HV arms, 3 m | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 93.4154 | 90.4154 | 29385 | 0.089754 | 0.00099269 | 2014-08-14 | C | 0.089754 | 0.00099269 | 2015 | 2014-08-14 | C | 325 | 0.089754 | 0.00099269
1 | 1344909 | 2014-08-14 08:54 | 2014-08-14 13:54 | 300.3167 | 1 | 300.3167 | 0.0009185 | 3.0584e-06 | Restore Supply on Device L4295 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | L4295 | replaced 3 amp fuse cause: lightning. oh/hv. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. FM confirms that he has spoken with the customer and that the fuse was out at 870 KAHAROA ROAD, Pat | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 300.3167 | 297.3167 | 297.3167 | 0.00090813 | 3.0544e-06 | 2014-08-14 | C | 0.00090813 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00090813 | 3.0544e-06
1 | 1345906 | 2014-08-14 09:07 | 2014-08-14 11:10 | 122.6167 | 2 | 156.9333 | 0.00047997 | 6.1168e-06 | Restore Supply on Device 7760 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 7760 | Fuses 7760 tripped. Cause by bird strike, replaced fuses | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 78.4667 | 75.4667 | 150.9333 | 0.00046101 | 6.1088e-06 | 2014-08-14 | C | 0.00046101 | 6.109e-06 | 2015 | 2014-08-14 | C | 2 | 0.00046101 | 6.1088e-06
1 | 1068849 | 2014-08-14 09:43 | 2014-08-14 13:37 | 234.0333 | 12 | 2808.4 | 0.0085893 | 3.6701e-05 | NAPA ID:00988 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 847842, 725869 | Approved. Replacing 11kV poles & cross arms between pole numbers 847842 & 725869. Work Location: Tangahoe Valley Road. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 234.0333 | 231.0333 | 2772.4 | 0.0084681 | 3.6653e-05 | 2014-08-14 | B | 0.004234 | 1.8327e-05 | 2015 | 2014-08-14 | B | 12 | 0.0084681 | 3.6653e-05
1 | 1351544 | 2014-08-14 14:54 | 2014-08-18 15:35 | 5800.7167 | 42 | 10050.35 | 0.030738 | 0.00012845 | Restore Supply on Device C875 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Norfolk Sub | Large tree through lines and lines down on State Highway. Unsafe to coniune until traffic management can be arranged. Cut a line break at pole 855030 and restored feeder with Transformers T2490 & T3894 offloaded via e-map, will remain off over night. Rep | F4 | WAINGAWA RD | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 239.294 | 236.294 | 9924.35 | 0.030313 | 0.00012829 | 2014-08-14 | C | 0.030313 | 0.00012829 | 2015 | 2014-08-14 | C | 42 | 0.030313 | 0.00012829
1 | 1349794 | 2014-08-14 15:09 | 2014-08-14 19:53 | 284.2333 | 1 | 284.2333 | 0.00086931 | 3.0584e-06 | Restore Supply on Device T1021 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1021 | Faultman found 2 blown on transformer T1021. Replaced 2x 2Amp 11KV Fuses. | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 284.2333 | 281.2333 | 281.2333 | 0.00085901 | 3.0544e-06 | 2014-08-14 | C | 0.00085901 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00085901 | 3.0544e-06
1 | 1359729 | 2014-08-14 15:15 | 2014-08-14 18:50 | 215.0333 | 3 | 645.1 | 0.001973 | 9.1753e-06 | Restore Supply on Device T268 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | T268 | faultman found 2 blown fuses, replaced 2x 3Amp 11KV Fuses. | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 215.0333 | 212.0333 | 636.1 | 0.0019429 | 9.1633e-06 | 2014-08-14 | C | 0.0019429 | 9.163e-06 | 2015 | 2014-08-14 | C | 3 | 0.0019429 | 9.1633e-06
1 | 1350869 | 2014-08-14 15:19 | 2014-08-15 21:20 | 1800.6167 | 209 | 46520 | 0.14228 | 0.00063921 | Restore Supply on Device R11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734171 | CB R11 A/R and locked out. No flags. Line patrolled and rebound insulator at pole 734171. | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 222.5837 | 219.5837 | 45893 | 0.14018 | 0.00063837 | 2014-08-14 | C | 0.14018 | 0.00063838 | 2015 | 2014-08-14 | C | 209 | 0.14018 | 0.00063837
1 | 1381297 | 2014-08-14 15:37 | 2014-08-15 10:40 | 1142.9833 | 17 | 1670.9833 | 0.0051106 | 5.1993e-05 | Restore Supply on Device LC4181 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4123 | Parent Job of OMS 1351607. Repair broken jumper at Fuses FC4123. Isolation beyond LC4181. Kim Lambert attended. | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 98.2931 | 95.2931 | 1619.9833 | 0.0049481 | 5.1925e-05 | 2014-08-14 | C | 0.0049481 | 5.1925e-05 | 2015 | 2014-08-14 | C | 17 | 0.0049481 | 5.1925e-05
1 | 1357141 | 2014-08-14 16:43 | 2014-08-14 20:05 | 202.25 | 231 | 25976.5 | 0.079447 | 0.0007065 | Restore Supply on Device 6497 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 735582 | RS 6497 A/R, L/O. Line patrolled. HV Insulator replaced and rebound at pole 735582. Materials used: HV Insualtor and Binder. Bevan Hughes attended. | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 112.4524 | 109.4524 | 25283.5 | 0.077227 | 0.00070557 | 2014-08-14 | C | 0.077227 | 0.00070557 | 2015 | 2014-08-14 | C | 231 | 0.077227 | 0.00070557
1 | 1357715 | 2014-08-14 16:50 | 2014-08-14 18:16 | 86.7167 | 193 | 16684.1167 | 0.051027 | 0.00059028 | Restore Supply on Device 8764 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | rs8764 | Patrolled. No fault found. Recloser 8764 tripped. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 86.4462 | 83.4462 | 16105.1167 | 0.049192 | 0.0005895 | 2014-08-14 | C | 0.049192 | 0.0005895 | 2015 | 2014-08-14 | C | 193 | 0.049192 | 0.0005895
1 | 1358414 | 2014-08-14 17:15 | 2014-08-14 20:00 | 164.9833 | 307 | 24292.6333 | 0.074297 | 0.00093894 | Restore Supply on Device 1218 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 1394 & Pole 769474 | Faultman found line down at pole 769474.Line was repaired. 3 meters of squirrell conductor was used. On relivening the the section of the feeder from Fuses 1394, faultman found a fault on one phase at the pot head, this was isolated again and repaired. | F3 | WESTMERE PEAT ST | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 79.1291 | 76.1291 | 23371.6333 | 0.071387 | 0.00093771 | 2014-08-14 | C | 0.071387 | 0.00093771 | 2015 | 2014-08-14 | C | 307 | 0.071387 | 0.00093771
1 | 1358427 | 2014-08-14 17:27 | 2014-08-15 00:28 | 421.1 | 25 | 10527.5 | 0.032198 | 7.6461e-05 | Restore Supply on Device 175 | 33000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 175 | Faultman found 2x11KV Fuses 175 blown, line was patrolled and Fuses were replaced. 2x 8Amp 11Kv Fuses used | F1, F2, F3 | TAIHAPE A 33KV | TP_MATAROA | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 421.1 | 418.1 | 10452.5 | 0.031926 | 7.6361e-05 | 2014-08-14 | C | 0.031926 | 7.6361e-05 | 2015 | 2014-08-14 | C | 25 | 0.031926 | 7.6361e-05
1 | 1359116 | 2014-08-14 17:34 | 2014-08-14 22:35 | 301.0167 | 3 | 856.7667 | 0.0026204 | 9.1753e-06 | Restore Supply on Device TC1323 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1323 | replaced 2x 3a HV fuse links. o/h wind. nothing else repaired or replaced. adjacent assets all good Email sent to Jo to QA as job has SAIDI | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 285.5889 | 282.5889 | 847.7667 | 0.0025894 | 9.1633e-06 | 2014-08-14 | C | 0.0025894 | 9.163e-06 | 2015 | 2014-08-14 | C | 3 | 0.0025894 | 9.1633e-06
1 | 1359687 | 2014-08-14 18:09 | 2014-08-14 21:39 | 209.8667 | 1 | 209.8667 | 0.00064186 | 3.0584e-06 | Restore Supply on Device T318 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T318 | replace 2a fuse o/h lightning, nothing else repaired or rpelaced. adjacent assets all good | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 209.8667 | 206.8667 | 206.8667 | 0.00063186 | 3.0544e-06 | 2014-08-14 | C | 0.00063186 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00063186 | 3.0544e-06
1 | 1380299 | 2014-08-14 18:12 | 2014-08-15 10:56 | 1003.7833 | 20 | 4566.7667 | 0.013967 | 6.1168e-05 | Restore Supply on Device 113 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Fuses 113 | Tree through lines. NDR 23178 Replaced 10m condustor 3 phases and 6 sleeves | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 228.3383 | 225.3383 | 4506.7667 | 0.013766 | 6.1088e-05 | 2014-08-14 | C | 0.013766 | 6.1088e-05 | 2015 | 2014-08-14 | C | 20 | 0.013766 | 6.1088e-05
1 | 1380652 | 2014-08-14 18:54 | 2014-08-15 10:02 | 907.85 | 30 | 3824.75 | 0.011698 | 9.1753e-05 | Restore Supply on Device 8484 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 8484 | Replaced 2x 15Amp HV links | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 127.4917 | 124.4917 | 3734.75 | 0.011408 | 9.1633e-05 | 2014-08-14 | C | 0.011408 | 9.1633e-05 | 2015 | 2014-08-14 | C | 30 | 0.011408 | 9.1633e-05
1 | 1360308 | 2014-08-14 19:16 | 2014-08-19 08:00 | 6523.8333 | 14 | 133407.4 | 0.40802 | 4.2818e-05 | Restore Supply on Device C6536 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole 722146 | Temp Repair to Crossarm & Insulator to restore Power. D Embling to Defect to repair at a later date. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 9529.1 | 9526.1 | 133365.4 | 0.40735 | 4.2762e-05 | 2014-08-14 | C | 0.40735 | 4.2762e-05 | 2015 | 2014-08-14 | C | 14 | 0.40735 | 4.2762e-05
1 | 1360723 | 2014-08-14 19:20 | 2014-08-15 10:03 | 882.8055 | 1 | 882.8167 | 0.0027 | 3.0584e-06 | Restore Supply on Device 4463T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761332 | replaced 1x 2amp ht link 4463T No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 882.8167 | 879.8167 | 879.8167 | 0.0026873 | 3.0544e-06 | 2014-08-14 | C | 0.0026873 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0026873 | 3.0544e-06
1 | 1360753 | 2014-08-14 19:41 | 2014-08-15 06:08 | 626.9067 | 1 | 626.9167 | 0.0019174 | 3.0584e-06 | Restore Supply on Device L4360 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | L4360 | Replaced 2x 3Amp 11KV fuses on transformer L4360 On Time 06:05 Email sent to Jo to QA as job has SAIDI | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 626.9167 | 623.9167 | 623.9167 | 0.0019057 | 3.0544e-06 | 2014-08-14 | C | 0.0019057 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0019057 | 3.0544e-06
1 | 1361301 | 2014-08-14 19:41 | 2014-08-14 23:02 | 200.7833 | 1 | 200.7833 | 0.00061408 | 3.0584e-06 | Restore Supply on Device C6758 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C6758 | replaced 2x 5a hv fuse links due to lightning o/h. nothing else repaired or replaced. adjacent assets all good Email sent to Jo to QA as job has SAIDI | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 200.7833 | 197.7833 | 197.7833 | 0.00060411 | 3.0544e-06 | 2014-08-14 | C | 0.00060411 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.00060411 | 3.0544e-06
1 | 1361343 | 2014-08-14 19:59 | 2014-08-15 11:41 | 942.0923 | 1 | 942.1 | 0.0028813 | 3.0584e-06 | Restore Supply on Device 3199T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3199T - tx fuse | 1 x 3amp HV OH fuse. no other assets repaired or replaced on site. - checked adjacent assets - up to powerco standard | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 942.1 | 939.1 | 939.1 | 0.0028684 | 3.0544e-06 | 2014-08-14 | C | 0.0028684 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0028684 | 3.0544e-06
1 | 1361389 | 2014-08-14 20:16 | 2014-08-15 13:31 | 1035.857 | 1 | 1035.8667 | 0.0031681 | 3.0584e-06 | Restore Supply on Device X1840 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1840 | 1x 2amp ht fuse No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard kevin attended, kevin to call hub to get job deassigned from Neville and reassigned to kevin | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1035.8667 | 1032.8667 | 1032.8667 | 0.0031548 | 3.0544e-06 | 2014-08-14 | C | 0.0031548 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0031548 | 3.0544e-06
1 | 1358354 | 2014-08-14 20:40 | 2014-08-14 20:40 | 0 | 58 | 11334.1667 | 0.034665 | 0.00017739 | Restore Supply on Device 266 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | Recloser 266 | Recloser 266 trip at 17:24, due to no comms faultman found Recloser 266 was open after a check of line Recloser 266 was closed and supply restored. Faultman had problems getting to site due to heavy snow on the roads. Off Time:17:24 On Time 20:40 | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 195.4167 | 192.4167 | 11160.1667 | 0.034088 | 0.00017716 | 2014-08-14 | C | 0.034088 | 0.00017716 | 2015 | 2014-08-14 | C | 58 | 0.034088 | 0.00017716
1 | 1361521 | 2014-08-14 21:34 | 2014-08-15 11:51 | 857.1668 | 1 | 857.1833 | 0.0026216 | 3.0584e-06 | Restore Supply on Device 3243T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3243T | 2 X 2AMP TX LINKS LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS UP TO STANDARD | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 857.1833 | 854.1833 | 854.1833 | 0.002609 | 3.0544e-06 | 2014-08-14 | C | 0.002609 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.002609 | 3.0544e-06
1 | 1361588 | 2014-08-14 22:19 | 2014-08-15 12:34 | 855.0335 | 2 | 1013.8 | 0.0031006 | 6.1168e-06 | Restore Supply on Device TF7-069 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF7-069 SF7-024 | plz ask faultman if this would have affected oms 1381155 497 bush Road, te puke no power? Clint advised that this job would have been affected. 2x 8amp hv fuses - in line ddo's No other assets repaired or replaced and all adjacent assets checked an | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 506.9 | 503.9 | 1007.8 | 0.0030782 | 6.1088e-06 | 2014-08-14 | C | 0.0030782 | 6.109e-06 | 2015 | 2014-08-14 | C | 2 | 0.0030782 | 6.1088e-06
1 | 1359553 | 2014-08-14 22:22 | 2014-08-14 22:46 | 24 | 1 | 24 | 7.3402e-05 | 3.0584e-06 | Restore Supply on Device T1/520 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/520 | Fuses L35 opended and tagged. Faultman found a burnt jumper at transformer T1/520. Jumper was repaired with 1x 11KV connector. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 24 | 21 | 21 | 6.4143e-05 | 3.0544e-06 | 2014-08-14 | C | 6.4143e-05 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 6.4143e-05 | 3.0544e-06
1 | 1362198 | 2014-08-14 22:37 | 2014-08-15 01:10 | 153 | 292 | 23592.65 | 0.072156 | 0.00089306 | Restore Supply on Device C917 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT TREE CONTACT | CB C917 | CB C917 tripped on E/F, line was sectionalised and patrolled and all the faultman could find was a tree that had come down in a slip that could have brushed along the line as it fell over. Faultman also found 2 fuses blown at Fuses 7227. 2x 10Amp fuses w | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 80.7967 | 77.7967 | 22716.65 | 0.069386 | 0.00089189 | 2014-08-14 | C | 0.069386 | 0.00089189 | 2015 | 2014-08-14 | C | 292 | 0.069386 | 0.00089189
1 | 1362196 | 2014-08-14 22:37 | 2014-08-15 10:23 | 706.3842 | 1 | 706.4 | 0.0021605 | 3.0584e-06 | Restore Supply on Device 4909T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4909T | 3 AMP HV FUSE DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPALCED ADJACENT ASSETS UP TO STANDARD | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 706.4 | 703.4 | 703.4 | 0.0021485 | 3.0544e-06 | 2014-08-14 | C | 0.0021485 | 3.054e-06 | 2015 | 2014-08-14 | C | 1 | 0.0021485 | 3.0544e-06
1 | 1362493 | 2014-08-14 22:37 | 2014-08-15 11:30 | 772.7667 | 593 | 81858.2167 | 0.25036 | 0.0018136 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS IC 368 | Fault somewhere between ABS IC368 and ABS IC380. Cannot find fault in the dark. Will need to come back in the daylight to find fault. This job cannot be closed off until power is shown as restored on E-Map. 8.46am Joanne at svs hub advised shane walker | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 138.0408 | 135.0408 | 80079.2167 | 0.2446 | 0.0018113 | 2014-08-14 | C | 0.2446 | 0.0018113 | 2015 | 2014-08-14 | C | 593 | 0.2446 | 0.0018113
1 | 1679198 | 2014-08-14 23:49 | 2014-08-15 00:31 | 42 | 2474 | 103908 | 0.31779 | 0.0075665 | Restore Supply on Device 307 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer T1 | burnt wiring in tapchanger | F1, F2, F3 | TAIHAPE A 33KV | TP_MATAROA | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 96486 | 0.29471 | 0.0075566 | 2014-08-14 | C | 0.29471 | 0.0075566 | 2015 | 2014-08-14 | C | 2474 | 0.29471 | 0.0075566
1 | 1368220 | 2014-08-15 02:07 | 2014-08-15 04:45 | 157.7167 | 295 | 27001.8167 | 0.082583 | 0.00090223 | Restore Supply on Device C917 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole 812811 | CB C917 tripped on E/F line was sectionalised and patrolled and a line down was found at pole 812811. 2 metres of Gofer conductor was used and 3 connectors. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 91.5316 | 88.5316 | 26116.8167 | 0.079772 | 0.00090105 | 2014-08-15 | C | 0.079772 | 0.00090105 | 2015 | 2014-08-15 | C | 295 | 0.079772 | 0.00090105
1 | 1369313 | 2014-08-15 02:33 | 2014-08-15 05:20 | 166.8333 | 16 | 736.8333 | 0.0022535 | 4.8935e-05 | Restore Supply on Device 5564E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 517 south Rd Patea | Faultman found blown jumper at pole 723925, line was isolated at Fuses LI107. 1X sleeve and 1X binder was used Off Time 04:27 On Time 05:05 | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 46.0521 | 43.0521 | 688.8333 | 0.002104 | 4.8871e-05 | 2014-08-15 | C | 0.002104 | 4.8871e-05 | 2015 | 2014-08-15 | C | 16 | 0.002104 | 4.8871e-05
1 | 1379354 | 2014-08-15 06:03 | 2014-08-15 08:10 | 127.9667 | 109 | 12050.3667 | 0.036855 | 0.00033337 | Restore Supply on Device T42/6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Recloser T42 | Mangamutu CB 8 Tripped. O/C. Line patrolled and no fault located. Trevor Pocock found a tree with burn marks on it and a local resident who saw a flash at about the tripping time in that area. He has put through for the tree owner to be notified. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 110.5538 | 107.5538 | 11723.3667 | 0.035808 | 0.00033293 | 2014-08-15 | C | 0.035808 | 0.00033293 | 2015 | 2014-08-15 | C | 109 | 0.035808 | 0.00033293
1 | 1379591 | 2014-08-15 06:41 | 2014-08-15 13:37 | 416.0833 | 4 | 1584.5333 | 0.0048462 | 1.2234e-05 | Restore Supply on Device TE3-045 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE3-045 | when faultman clears job please check job 1379615 No power 48 williams Road south & 1379614 198 Williams road south & 1379674 196 Williams road Replaced 2 x 10 amp DDO fuses. Power restored. No other repairs. Weather or bird may have caused fault. HV wor | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 396.1333 | 393.1333 | 1572.5333 | 0.0048032 | 1.2218e-05 | 2014-08-15 | C | 0.0048032 | 1.2218e-05 | 2015 | 2014-08-15 | C | 4 | 0.0048032 | 1.2218e-05
1 | 1379624 | 2014-08-15 07:01 | 2014-08-15 10:54 | 232.8333 | 1 | 232.8333 | 0.0007121 | 3.0584e-06 | Restore Supply on Device 3347T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3347T | Ruth from Nova called to advise this address is 229 Cross Road not 133 Cross Road 3 AMP HV FUSE DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS UP TO STANDARD | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 232.8333 | 229.8333 | 229.8333 | 0.00070201 | 3.0544e-06 | 2014-08-15 | C | 0.00070201 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00070201 | 3.0544e-06
1 | 1379753 | 2014-08-15 07:08 | 2014-08-20 08:08 | 7259.75 | 287 | 105832.5167 | 0.32368 | 0.00087777 | Restore Supply on Device C945 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | CB C945 |  | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 368.7544 | 365.7544 | 104971.5167 | 0.32063 | 0.00087662 | 2014-08-15 | C | 0.32063 | 0.00087662 | 2015 | 2014-08-15 | C | 287 | 0.32063 | 0.00087662
1 | 1379656 | 2014-08-15 07:14 | 2014-08-15 16:25 | 550.3167 | 2 | 931.05 | 0.0028475 | 6.1168e-06 | Restore Supply on Device T1065 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1065 | Replaced 1x 3amp 11kv fuse on tx 1065 also disconnected a service line a9900 needs to clear trees and will ask for reconnection on monday | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 465.525 | 462.525 | 925.05 | 0.0028255 | 6.1088e-06 | 2014-08-15 | C | 0.0028255 | 6.109e-06 | 2015 | 2014-08-15 | C | 2 | 0.0028255 | 6.1088e-06
1 | 1379670 | 2014-08-15 07:22 | 2014-08-15 10:39 | 197.1667 | 1 | 197.1667 | 0.00060302 | 3.0584e-06 | Restore Supply on Device 2305T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2305T | hv fuse blown. 1x 3amp hv fuse cause lightning No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 197.1667 | 194.1667 | 194.1667 | 0.00059307 | 3.0544e-06 | 2014-08-15 | C | 0.00059307 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00059307 | 3.0544e-06
1 | 1379690 | 2014-08-15 07:28 | 2014-08-15 16:24 | 536.05 | 1 | 536.05 | 0.0016395 | 3.0584e-06 | Restore Supply on Device X416 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | X416 | replaced 2amp at tx oh hv weather | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 536.05 | 533.05 | 533.05 | 0.0016282 | 3.0544e-06 | 2014-08-15 | C | 0.0016282 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.0016282 | 3.0544e-06
1 | 1381483 | 2014-08-15 08:08 | 2014-08-15 22:06 | 837.85 | 8 | 5231.5167 | 0.016 | 2.4467e-05 | Restore Supply on Device X373 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 997 | Replaced blown 20A HV fuse at links 997. Cause unknown. No other assets repaired or replaced. All other surrounding assets appear fine. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 653.9396 | 650.9396 | 5207.5167 | 0.015906 | 2.4435e-05 | 2014-08-15 | C | 0.015906 | 2.4435e-05 | 2015 | 2014-08-15 | C | 8 | 0.015906 | 2.4435e-05
1 | 1379915 | 2014-08-15 08:40 | 2014-08-16 09:24 | 1484.0333 | 1 | 1484.0333 | 0.0045388 | 3.0584e-06 | Restore Supply on Device T1242 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | JAMES RD MASTERTON | 2 x 10 amp hv fuses cause: weather. hv/oh. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1484.0333 | 1481.0333 | 1481.0333 | 0.0045237 | 3.0544e-06 | 2014-08-15 | C | 0.0045237 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.0045237 | 3.0544e-06
1 | 1379951 | 2014-08-15 08:48 | 2014-08-15 12:57 | 248.2 | 1 | 248.2 | 0.0007591 | 3.0584e-06 | Restore Supply on Device TC3619 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3619 | blown ht fuse. replaced 1x 2amp No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 248.2 | 245.2 | 245.2 | 0.00074894 | 3.0544e-06 | 2014-08-15 | C | 0.00074894 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00074894 | 3.0544e-06
1 | 1379962 | 2014-08-15 08:53 | 2014-08-15 17:24 | 511.7833 | 1 | 511.7833 | 0.0015652 | 3.0584e-06 | Restore Supply on Device M2155 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KAUPOKONUI HEADS RD MANAIA | Replaced 2 x blown HV 2A fuse. Too busy to check if Control have completed appropriate paperwork. Email sent to Jo to QA as job has SAIDI | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 511.7833 | 508.7833 | 508.7833 | 0.001554 | 3.0544e-06 | 2014-08-15 | C | 0.001554 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.001554 | 3.0544e-06
1 | 1158532 | 2014-08-15 09:00 | 2014-08-15 14:08 | 308 | 77 | 23716 | 0.072534 | 0.0002355 | NAPA ID:00794 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212274, 212214 | Approved. Replace pole & hardware. Work Location: Omanawa Road. Work Order 10140535 | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 308 | 305 | 23485 | 0.071733 | 0.00023519 | 2014-08-15 | B | 0.035867 | 0.0001176 | 2015 | 2014-08-15 | B | 77 | 0.071733 | 0.00023519
1 | 1380968 | 2014-08-15 09:32 | 2014-08-15 14:55 | 323.2667 | 1 | 323.2667 | 0.00098869 | 3.0584e-06 | Restore Supply on Device 2805T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2805T | 12:11pm - Bruce leaving site , all safe NP crew on way up Kaine advised needs to replace blown transformer tx 2805t pole 741659 New plymouth team to change this tx need 3 fm and 4x4 truck as bad access Replaced blown transformer 2805T. Forced down | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 323.2667 | 320.2667 | 320.2667 | 0.00097823 | 3.0544e-06 | 2014-08-15 | C | 0.00097823 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00097823 | 3.0544e-06
1 | 1380993 | 2014-08-15 09:38 | 2014-08-15 10:42 | 63.3167 | 9 | 391.7167 | 0.001198 | 2.7526e-05 | Restore Supply on Device 5631 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 5631 | Germaine Anaha attended. Repaced two fuseholders and two 6Amp links | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 43.5241 | 40.5241 | 364.7167 | 0.001114 | 2.749e-05 | 2014-08-15 | C | 0.001114 | 2.749e-05 | 2015 | 2014-08-15 | C | 9 | 0.001114 | 2.749e-05
1 | 1381069 | 2014-08-15 09:51 | 2014-08-16 14:00 | 1688.6667 | 72 | 29887.7 | 0.091409 | 0.00022021 | Restore Supply on Device 1406 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 780603 | Pole and lines down at pole 780603 . Temp line break made at pole 780601. Faultman to return in morning to replace the pole too dangerous to carry on working at night. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 415.1069 | 412.1069 | 29671.7 | 0.09063 | 0.00021992 | 2014-08-15 | C | 0.09063 | 0.00021992 | 2015 | 2014-08-15 | C | 72 | 0.09063 | 0.00021992
1 | 1381333 | 2014-08-15 10:20 | 2014-08-15 18:12 | 471.4833 | 3 | 1369.9667 | 0.0041899 | 9.1753e-06 | Restore Supply on Device T1421 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1421 | 5.12 PHONED TENIX WHO ADVISED GETTING A FM ON WAY Replaced 1x blown 3A DDO fuse. Possibly weather. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 456.6556 | 453.6556 | 1360.9667 | 0.004157 | 9.1633e-06 | 2014-08-15 | C | 0.004157 | 9.163e-06 | 2015 | 2014-08-15 | C | 3 | 0.004157 | 9.1633e-06
1 | 1381371 | 2014-08-15 10:30 | 2014-08-15 13:12 | 162 | 9 | 1458 | 0.0044592 | 2.7526e-05 | Restore Supply on Device FC4133 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | w12877 | Found line down beyound fuses FC4133. Isolated at fuses. Repaired line and re livened | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 162 | 159 | 1431 | 0.0043709 | 2.749e-05 | 2014-08-15 | C | 0.0043709 | 2.749e-05 | 2015 | 2014-08-15 | C | 9 | 0.0043709 | 2.749e-05
1 | 1381481 | 2014-08-15 11:07 | 2014-08-15 15:02 | 235.3833 | 1 | 235.3833 | 0.0007199 | 3.0584e-06 | Restore Supply on Device 2435T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 454 NORFOLK RD | 2 AMP HV FUSE DUE TO UNKNOWN REASON NO OTHER ASSETS ADJACENT ASSETS OK TAG A7538 DISCO PUMP AS LINE TO IT FAULTY LINE , ADVISED RETAILER TO ADVISE CUSTOMER OF THIS | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.3833 | 232.3833 | 232.3833 | 0.0007098 | 3.0544e-06 | 2014-08-15 | C | 0.0007098 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.0007098 | 3.0544e-06
1 | 1381479 | 2014-08-15 11:07 | 2014-08-15 18:16 | 428.9667 | 1 | 428.9667 | 0.001312 | 3.0584e-06 | Restore Supply on Device L4467 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | L4467 | RPELACED HV OH 3AMP DUE TO WEATHER No other assets repaired or replaced at site. Checked adjacent assets and all up to Powerco standard. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 428.9667 | 425.9667 | 425.9667 | 0.0013011 | 3.0544e-06 | 2014-08-15 | C | 0.0013011 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.0013011 | 3.0544e-06
1 | 1381638 | 2014-08-15 12:02 | 2014-08-15 15:20 | 197.1833 | 2 | 332.6 | 0.0010172 | 6.1168e-06 | Restore Supply on Device X2789 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | 777788 | 1420HRS SVS HUB ADVISED THAT THIS AFFECTS THE WHOLE TOWN & F/MAN HAS BEEN IN CONTACT WITH SEWER PLANT. Main line fuse which also affects a few other jobs links 182 1x 10amp ht fuse snow. No other assets repaired or replaced and all adjacent assets checke | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 166.3 | 163.3 | 326.6 | 0.00099757 | 6.1088e-06 | 2014-08-15 | C | 0.00099757 | 6.109e-06 | 2015 | 2014-08-15 | C | 2 | 0.00099757 | 6.1088e-06
1 | 1381672 | 2014-08-15 12:22 | 2014-08-15 16:10 | 227.3 | 244 | 19168.1833 | 0.058624 | 0.00074625 | Restore Supply on Device S6031 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 221848 | requires bucket truck to replace insulator on hv xarm but dave is still doing line patrol. 4:20pm FM advises replaced HV xarm and hardware | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 78.5581 | 75.5581 | 18436.1833 | 0.056312 | 0.00074528 | 2014-08-15 | C | 0.056312 | 0.00074528 | 2015 | 2014-08-15 | C | 244 | 0.056312 | 0.00074528
1 | 1384112 | 2014-08-15 16:07 | 2014-08-15 22:45 | 398.3167 | 1 | 398.3167 | 0.0012182 | 3.0584e-06 | Restore Supply on Device X317 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5456 OMATEA ROAD WANGANUI | Replaced blown 3A HV transformer fuse due to weather. No other assets repaired or replaced at site. Checked adjacent assets and all up to Powerco standard. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 398.3167 | 395.3167 | 395.3167 | 0.0012075 | 3.0544e-06 | 2014-08-15 | C | 0.0012075 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.0012075 | 3.0544e-06
1 | 1384781 | 2014-08-15 17:34 | 2014-08-17 06:46 | 2232.3833 | 18 | 7602 | 0.02325 | 5.5052e-05 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6050 | Line to be patrolled in morning. Faultman to contact hub. Span down found when line patrolled in morning. Isolated past ABS 6050 to replace 30m of conductor. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 422.3333 | 419.3333 | 7548 | 0.023055 | 5.498e-05 | 2014-08-15 | B | 0.011527 | 2.749e-05 | 2015 | 2014-08-15 | B | 18 | 0.023055 | 5.498e-05
1 | 1384135 | 2014-08-15 20:07 | 2014-08-15 21:10 | 63 | 1 | 63 | 0.00019268 | 3.0584e-06 | Restore Supply on Device TP1098 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TP1098 | at 20:07 Pongakawa Sub, CB 1 Tainui feeder. Found Crossarm Arm strap bolt had broken and crossarm had come off of pole. Isolated Lines at Fuses FP748. Permit Issued & Repairs Carried out and bolt replaced. All Power restored on completion. Wayne Neutroski | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 60 | 0.00018327 | 3.0544e-06 | 2014-08-15 | C | 0.00018327 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00018327 | 3.0544e-06
1 | 1385017 | 2014-08-15 20:32 | 2014-08-15 23:45 | 193.0667 | 1 | 193.0667 | 0.00059048 | 3.0584e-06 | Restore Supply on Device TE4-166 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TE4-166 | Replace 1x HV Fuse 2A. All Power Restored. | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 193.0667 | 190.0667 | 190.0667 | 0.00058054 | 3.0544e-06 | 2014-08-15 | C | 0.00058054 | 3.054e-06 | 2015 | 2014-08-15 | C | 1 | 0.00058054 | 3.0544e-06
1 | 1385211 | 2014-08-16 07:27 | 2014-08-16 09:58 | 150.5 | 1 | 150.5 | 0.00046029 | 3.0584e-06 | Restore Supply on Device 2149T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2149T | Replaced 2 x 15amp HV isolation fuses. Cause: Bird strike. OH/HV. No other assets repaired or replaced on site. Adjacent assets are checked and are ok/up to Powerco standard. | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 150.5 | 147.5 | 147.5 | 0.00045053 | 3.0544e-06 | 2014-08-16 | C | 0.00045053 | 3.054e-06 | 2015 | 2014-08-16 | C | 1 | 0.00045053 | 3.0544e-06
1 | 1385344 | 2014-08-16 10:36 | 2014-08-16 13:42 | 185.7333 | 1 | 185.7333 | 0.00056805 | 3.0584e-06 | Restore Supply on Device T1782 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 577 Hughes Line, Carterton | tree is touching 33 kv line. FM to arrange for tree cutters to attend now as line is arcing and sparking. Removed trees. FM advise tree cutters will be onsite soon. he does not need to be onsite when they work. | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 185.7333 | 182.7333 | 182.7333 | 0.00055815 | 3.0544e-06 | 2014-08-16 | C | 0.00055815 | 3.054e-06 | 2015 | 2014-08-16 | C | 1 | 0.00055815 | 3.0544e-06
1 | 1386377 | 2014-08-16 16:24 | 2014-08-16 20:29 | 244.8833 | 2 | 465.1833 | 0.0014227 | 6.1168e-06 | Restore Supply on Device N2280 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N2280 | Replaced 2x LV 1X HV fuses No other assets repaired or replaced on site. Checked adjacent assets and all up to Powerco standard. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 232.5917 | 229.5917 | 459.1833 | 0.0014025 | 6.1088e-06 | 2014-08-16 | C | 0.0014025 | 6.109e-06 | 2015 | 2014-08-16 | C | 2 | 0.0014025 | 6.1088e-06
1 | 1273112 | 2014-08-17 09:01 | 2014-08-17 10:10 | 69.0333 | 14 | 966.4667 | 0.0029559 | 4.2818e-05 | NAPA ID:00540 TP_HINUERA GXP > TOWER ROAD SUB > BANKS ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F1991 | NC: NOTE: At the copmpletion of this works the network configuration change is required. Remove span of 11kV conductor between poles F1991 and F1988. Works location: Garland St Matamata WO 10153061 | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 69.0333 | 66.0333 | 924.4667 | 0.0028237 | 4.2762e-05 | 2014-08-17 | B | 0.0014119 | 2.1381e-05 | 2015 | 2014-08-17 | B | 14 | 0.0028237 | 4.2762e-05
1 | 1387086 | 2014-08-17 11:10 | 2014-08-17 12:14 | 64.6 | 1 | 64.6 | 0.00019757 | 3.0584e-06 | Restore Supply on Device 3185T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3185T | 3 Amp H/V Fuse. No other assets repaired or replaced on site. Adjacent assets checked and they are up to Powerco standard | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 64.6 | 61.6 | 61.6 | 0.00018815 | 3.0544e-06 | 2014-08-17 | C | 0.00018815 | 3.054e-06 | 2015 | 2014-08-17 | C | 1 | 0.00018815 | 3.0544e-06
1 | 1387342 | 2014-08-17 17:09 | 2014-08-18 03:55 | 646 | 420 | 101187.85 | 0.30948 | 0.0012845 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 248754 | Car hit pole 248754. Isolated between CB2, ABS 541 & ABS 621. Backfeed rest of area. Replace pole and associated equipment. Check houses for damage due to 11kV hitting 400V. Re livened. NDR 31897. ABS 558 welded closed due to fault current. Note: Delay o | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 240.9235 | 237.9235 | 99927.85 | 0.30522 | 0.0012829 | 2014-08-17 | C | 0.30522 | 0.0012829 | 2015 | 2014-08-17 | C | 420 | 0.30522 | 0.0012829
1 | 1388755 | 2014-08-18 08:55 | 2014-08-18 14:07 | 312.1333 | 1 | 312.1333 | 0.00095464 | 3.0584e-06 | Restore Supply on Device X644 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X644 | replaced 1x 2amp hv ddo fuse No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 312.1333 | 309.1333 | 309.1333 | 0.00094422 | 3.0544e-06 | 2014-08-18 | C | 0.00094422 | 3.054e-06 | 2015 | 2014-08-18 | C | 1 | 0.00094422 | 3.0544e-06
1 | 1388984 | 2014-08-18 11:00 | 2014-08-18 12:20 | 80 | 6 | 480 | 0.001468 | 1.8351e-05 | Restore Supply on Device M4055 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer M4055 | Replace Transformer M4055 due to Oil leak. <1/2 Litres of oil spilt. 3 x 50kVa Transformer. Kaine McKay attended. | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 462 | 0.0014111 | 1.8327e-05 | 2014-08-18 | C | 0.0014111 | 1.8327e-05 | 2015 | 2014-08-18 | C | 6 | 0.0014111 | 1.8327e-05
1 | 1391300 | 2014-08-18 16:30 | 2014-08-18 18:36 | 125.7 | 858 | 59475.7 | 0.1819 | 0.0026241 | Restore Supply on Device 6283 | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB S31 | Line Patrolled & sectionalized in Stratford. Suspect possible cable fault between S31 & 6541/3. Maybe possible DC fault. AJ on Site Tomorrow. No Comms when feeder faulted so had to wait for multiple contacts to ring in. Back feed from VS 6283 no good as l | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 69.319 | 66.319 | 56901.7 | 0.1738 | 0.0026207 | 2014-08-18 | C | 0.1738 | 0.0026207 | 2015 | 2014-08-18 | C | 858 | 0.1738 | 0.0026207
1 | 1389482 | 2014-08-18 17:01 | 2014-08-19 08:39 | 937.45 | 2 | 1862.7 | 0.0056969 | 6.1168e-06 | Restore Supply on Device S21 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB S31 | Part of OMS 1391300: "Line Patrolled & sectionalized in Stratford. Suspect possible cable fault between S31 & 6541/3. Maybe possible DC fault. AJ on Site Tomorrow. No Comms when feeder faulted so had to wait for multiple contacts to ring in. Back feed | F4 | CLOTON RD NORTH EAST | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 931.35 | 928.35 | 1856.7 | 0.0056711 | 6.1088e-06 | 2014-08-18 | C | 0.0056711 | 6.109e-06 | 2015 | 2014-08-18 | C | 2 | 0.0056711 | 6.1088e-06
1 | 1393370 | 2014-08-18 19:02 | 2014-08-18 21:00 | 117.85 | 1 | 117.85 | 0.00036044 | 3.0584e-06 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CC9 | Found jumper broken at CC9 Isolated between LC2136, IC1360 & CB 5. Backfeed rest of area. Repaired jumper and re livened. Grant Jordan/Peter Waite attended. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 117.85 | 114.85 | 114.85 | 0.0003508 | 3.0544e-06 | 2014-08-18 | C | 0.0003508 | 3.054e-06 | 2015 | 2014-08-18 | C | 1 | 0.0003508 | 3.0544e-06
1 | 1393480 | 2014-08-19 06:19 | 2014-08-19 07:36 | 76.8833 | 1 | 76.8833 | 0.00023514 | 3.0584e-06 | Restore Supply on Device T2/926 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03951 | replaced 2x 10amp hv fuses - cause ducks flying through the lines. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 76.8833 | 73.8833 | 73.8833 | 0.00022567 | 3.0544e-06 | 2014-08-19 | C | 0.00022567 | 3.054e-06 | 2015 | 2014-08-19 | C | 1 | 0.00022567 | 3.0544e-06
1 | 1158509 | 2014-08-19 08:15 | 2014-08-19 15:37 | 442 | 2 | 884 | 0.0027036 | 6.1168e-06 | NAPA ID:01114 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 63, 64, 65, 73,& 74 | Approved. Replacing poles 63, 64, 65, 73,& 74. Work Location: Santoft Road Work Order: 10151679. OMS fault When ABS 4515/4 open. Showed a loss of supply to Pukepapa Sub - Paul Investiagting | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 442 | 439 | 878 | 0.0026818 | 6.1088e-06 | 2014-08-19 | B | 0.0013409 | 3.054e-06 | 2015 | 2014-08-19 | B | 2 | 0.0026818 | 6.1088e-06
1 | 1173248 | 2014-08-19 08:31 | 2014-08-19 13:07 | 275.6167 | 79 | 21773.7167 | 0.066593 | 0.00024162 | NAPA ID:00811 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212204 | Replace poles and arms and reconductor HV network. Open LL gap at pole 212204. Works location: Omanawa Rd WO 10140535 Due to ABS Temp 24 and ABS IP183 not showing in E-Map Full scale of outage has not being recorded Outage between Temp24 and IP183 08: | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 275.6167 | 272.6167 | 21536.7167 | 0.065782 | 0.0002413 | 2014-08-19 | B | 0.032891 | 0.00012065 | 2015 | 2014-08-19 | B | 79 | 0.065782 | 0.0002413
1 | 1049904 | 2014-08-19 09:30 | 2014-08-19 15:02 | 332.4 | 54 | 17949.6 | 0.054897 | 0.00016515 | NAPA ID:00769 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 4 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole 741961 to 741936 | Approved. Reconductor from pole 741961 to 741936. This will close the span break between CB2 & CB4 Bell Block. | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 332.4 | 329.4 | 17787.6 | 0.054331 | 0.00016494 | 2014-08-19 | B | 0.027165 | 8.2469e-05 | 2015 | 2014-08-19 | B | 54 | 0.054331 | 0.00016494
1 | 1396473 | 2014-08-19 12:28 | 2014-08-19 12:33 | 5.0667 | 259 | 1312.2667 | 0.0040135 | 0.00079213 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | ABS 928 | This Outage was caused by reconfiguration of the 11kV network. The ABS was not a load buster type & was opening across 2 GXP's. There is a lot of circulating current between Hinera & Kinlieth GXP's | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 5.0667 | 2.0667 | 535.2667 | 0.0016349 | 0.0007911 | 2014-08-19 | C | 0.0016349 | 0.0007911 | 2015 | 2014-08-19 | C | 259 | 0.0016349 | 0.0007911
1 | 1398193 | 2014-08-19 15:35 | 2014-08-19 18:13 | 158.6 | 1 | 158.6 | 0.00048507 | 3.0584e-06 | Restore Supply on Device T1261 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1261 | replaced 2x 10a hv fuses due to unknown o/h nothing else rerpaired or replaced. adjacent assets all good Email sent to Jo to QA as job has SAIDI | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 158.6 | 155.6 | 155.6 | 0.00047527 | 3.0544e-06 | 2014-08-19 | C | 0.00047527 | 3.054e-06 | 2015 | 2014-08-19 | C | 1 | 0.00047527 | 3.0544e-06
1 | 1398347 | 2014-08-19 18:09 | 2014-08-20 09:29 | 920 | 594 | 55600.5667 | 0.17005 | 0.0018167 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole T13160 | 19/08/14 - at 18:09 Coromandel Sub, CB 5 Manaia Feeder, Tripped, Auto Recloser. Sectionaliser 9839 Tripped, L/O. Faultman Dispatched & Investigation Began. Fault between ABS IP448 & IC368. Faultmen will need to attend at first light tomorrow morning. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 93.6036 | 90.6036 | 53818.5667 | 0.16438 | 0.0018143 | 2014-08-19 | C | 0.16438 | 0.0018143 | 2015 | 2014-08-19 | C | 594 | 0.16438 | 0.0018143
1 | 1399928 | 2014-08-20 06:02 | 2014-08-20 09:05 | 183.3 | 1 | 183.3 | 0.00056061 | 3.0584e-06 | Restore Supply on Device TD6-016 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 339 Bell Rd, Papamoa | replaced 3amp DDO fuse. cause: wind. hv/oh. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 183.3 | 180.3 | 180.3 | 0.00055071 | 3.0544e-06 | 2014-08-20 | C | 0.00055071 | 3.054e-06 | 2015 | 2014-08-20 | C | 1 | 0.00055071 | 3.0544e-06
1 | 1399987 | 2014-08-20 07:18 | 2014-08-20 08:24 | 66.05 | 1 | 66.05 | 0.00020201 | 3.0584e-06 | Restore Supply on Device TC3388 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | Fuses FC4026 | Confirmed bird Strike (Duck) Two Fuses blown at FC4026 | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 66.05 | 63.05 | 63.05 | 0.00019258 | 3.0544e-06 | 2014-08-20 | C | 0.00019258 | 3.054e-06 | 2015 | 2014-08-20 | C | 1 | 0.00019258 | 3.0544e-06
1 | 1400040 | 2014-08-20 07:58 | 2014-08-20 12:40 | 281.9 | 1 | 281.9 | 0.00086217 | 3.0584e-06 | Restore Supply on Device TC3-199 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses SC3-035 | ***when signing off job pls ask fm if oms 1400058 and oms 1400059 and oms 1400093 and oms 1400171 is also affected by this outage*** These jobs confirmed restored when this job restored Power restored by 11:30 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 281.9 | 278.9 | 278.9 | 0.00085188 | 3.0544e-06 | 2014-08-20 | C | 0.00085188 | 3.054e-06 | 2015 | 2014-08-20 | C | 1 | 0.00085188 | 3.0544e-06
1 | 1400135 | 2014-08-20 08:45 | 2014-08-20 11:27 | 162.05 | 1 | 162.05 | 0.00049562 | 3.0584e-06 | Restore Supply on Device TC3984 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | FP761 | No other assets repaired or replaced on site. Checked adjacent assets and up to Powerco standard. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 162.05 | 159.05 | 159.05 | 0.00048581 | 3.0544e-06 | 2014-08-20 | C | 0.00048581 | 3.054e-06 | 2015 | 2014-08-20 | C | 1 | 0.00048581 | 3.0544e-06
1 | 1329721 | 2014-08-20 09:00 | 2014-08-20 13:44 | 284 | 38 | 10792 | 0.033006 | 0.00011622 | NAPA ID:00812 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212212 | Replace HV poles and arms and reconductor HV lines. Works location: Omanawa Rd. WO 10140535. No job created by OMS when power taken off. Power off between ABS Temp19 & ABS Temp 24. Power Off from 0900 to 1344. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 284 | 281 | 10678 | 0.032615 | 0.00011607 | 2014-08-20 | B | 0.016308 | 5.8034e-05 | 2015 | 2014-08-20 | B | 38 | 0.032615 | 0.00011607
1 | 1450461 | 2014-08-21 02:01 | 2014-08-21 03:32 | 90.4833 | 1 | 90.4833 | 0.00027674 | 3.0584e-06 | Restore Supply on Device TD6-041 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | SD6-006 | Replaced 2x Blown HV Fuses at SD6-006. 15A Fuses. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 90.4833 | 87.4833 | 87.4833 | 0.00026721 | 3.0544e-06 | 2014-08-21 | C | 0.00026721 | 3.054e-06 | 2015 | 2014-08-21 | C | 1 | 0.00026721 | 3.0544e-06
1 | 1450494 | 2014-08-21 06:35 | 2014-08-21 09:16 | 161 | 695 | 50048 | 0.15307 | 0.0021256 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P35878 | CB 8 tripped on Aphase O/C and E/F, line was sectionalised and patrolled and a line down was found at pole P35878. 5 meters of 25 mm copper was used and 4 11KV sleeves. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72.0115 | 69.0115 | 47963 | 0.1465 | 0.0021228 | 2014-08-21 | C | 0.1465 | 0.0021228 | 2015 | 2014-08-21 | C | 695 | 0.1465 | 0.0021228
1 | 1451183 | 2014-08-21 06:54 | 2014-08-21 08:35 | 101.3167 | 1 | 101.3167 | 0.00030987 | 3.0584e-06 | Restore Supply on Device TE7-109 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses FP892 | replaced 2x 3amp hv DDO & 2x fuse carriers - rusted carriers No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 101.3167 | 98.3167 | 98.3167 | 0.0003003 | 3.0544e-06 | 2014-08-21 | C | 0.0003003 | 3.054e-06 | 2015 | 2014-08-21 | C | 1 | 0.0003003 | 3.0544e-06
1 | 1173220 | 2014-08-21 08:30 | 2014-08-21 15:50 | 440 | 76 | 33440 | 0.10227 | 0.00023244 | NAPA ID:00897 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S173 | Replace 33kV poles w/ 11kV and LV on poles. Works location: South Belt Rd WO 10130702 | F1, F2, F3 | AKURA-TE ORE ORE TIE 33KV | TP_MASTERTON | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 440 | 437 | 33212 | 0.10144 | 0.00023214 | 2014-08-21 | B | 0.050722 | 0.00011607 | 2015 | 2014-08-21 | B | 76 | 0.10144 | 0.00023214
1 | 956104 | 2014-08-21 09:08 | 2014-08-21 15:07 | 359 | 4 | 1436 | 0.0043919 | 1.2234e-05 | NAPA ID:00475 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses B46 | Approved. Change cross arms and pole structures. Work location: Karere Road, Manawatu Rural. Work Order# 10156813 | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 359 | 356 | 1424 | 0.0043495 | 1.2218e-05 | 2014-08-21 | B | 0.0021748 | 6.109e-06 | 2015 | 2014-08-21 | B | 4 | 0.0043495 | 1.2218e-05
1 | 1329663 | 2014-08-21 09:21 | 2014-08-21 17:05 | 464.0333 | 38 | 17633.2667 | 0.05393 | 0.00011622 | NAPA ID:00814 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 212166 | date Change Requested | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 464.0333 | 461.0333 | 17519.2667 | 0.053511 | 0.00011607 | 2014-08-21 | B | 0.026756 | 5.8034e-05 | 2015 | 2014-08-21 | B | 38 | 0.053511 | 0.00011607
1 | 1162828 | 2014-08-21 09:30 | 2014-08-21 10:05 | 35 | 7 | 245 | 0.00074931 | 2.1409e-05 | NAPA ID:01200 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer TC1714 | NOTE: Contact NOC prior to isolation and again on restoration of the HV. Own isolation and AP. Install 400V disconnector on TC1714. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 224 | 0.00068419 | 2.1381e-05 | 2014-08-21 | B | 0.00034209 | 1.069e-05 | 2015 | 2014-08-21 | B | 7 | 0.00068419 | 2.1381e-05
1 | 1161857 | 2014-08-21 09:30 | 2014-08-21 13:07 | 216.25 | 54 | 11677.5 | 0.035715 | 0.00016515 | NAPA ID:01100 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 10 | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 751690 | Replace 11kV pole 751690. Works location: 20 Awanui St New Plymouth WO 10138965 | F3 | BROOKLANDS 10 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 216.25 | 213.25 | 11515.5 | 0.035173 | 0.00016494 | 2014-08-21 | B | 0.017587 | 8.2469e-05 | 2015 | 2014-08-21 | B | 54 | 0.035173 | 0.00016494
1 | 1457716 | 2014-08-21 14:49 | 2014-08-21 14:55 | 5.6167 | 95 | 533.5833 | 0.0016319 | 0.00029055 | Restore Supply on Device SE6-009 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 9744 | TePuke CB 3 tripped and A/R. Line patrolled and isolated at recloser 9744 as blown fuse found. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 5.6167 | 2.6167 | 248.5833 | 0.00075928 | 0.00029017 | 2014-08-21 | C | 0.00075928 | 0.00029017 | 2015 | 2014-08-21 | C | 95 | 0.00075928 | 0.00029017
1 | 1458864 | 2014-08-21 18:09 | 2014-08-21 19:55 | 106 | 49 | 5194 | 0.015885 | 0.00014986 | Restore Supply on Device P1405 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 704019 | 2FR part of lines down job oms 1458726. Conductor down caused by broken binder (Burnt through). 10m replaced. Blair Gregg attended. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 106 | 103 | 5047 | 0.015416 | 0.00014967 | 2014-08-21 | C | 0.015416 | 0.00014967 | 2015 | 2014-08-21 | C | 49 | 0.015416 | 0.00014967
1 | 1459119 | 2014-08-21 19:01 | 2014-08-22 10:30 | 929.2333 | 177 | 5388 | 0.016479 | 0.00054134 | Restore Supply on Device 7318 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 848532 | Broken Binder at Pole 848532. - requires 33kV off above during high winds for safety. (Full loss of Hau Nui Sub). Decision made to leave isolated at Fuses7318 until morning with only 2 transformers off. (May be able to repair OK when wind has died down). | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 30.4407 | 27.4407 | 4857 | 0.014835 | 0.00054063 | 2014-08-21 | C | 0.014835 | 0.00054063 | 2015 | 2014-08-21 | C | 177 | 0.014835 | 0.00054063
1 | 1459819 | 2014-08-21 22:58 | 2014-08-21 23:38 | 40 | 21 | 840 | 0.0025691 | 6.4227e-05 | Restore Supply on Device LI718 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 728642 | 2FR Isolation between ABS LI702 and LI718 to replace a 3 HT fuses to Transformer L1235. Damaged in high winds / poor condition. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 777 | 0.0023733 | 6.4143e-05 | 2014-08-21 | C | 0.0023733 | 6.4143e-05 | 2015 | 2014-08-21 | C | 21 | 0.0023733 | 6.4143e-05
1 | 1134643 | 2014-08-22 08:15 | 2014-08-22 16:43 | 508 | 2 | 148 | 0.00045265 | 6.1168e-06 | NAPA ID:01057 TP_PIAKO GXP > PIAKO SUB | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I12405 | Carry out relocation, replacement of 33kV and 11kV Cables, 11kV Switchgear and transformer for installation of substation building. Work Location: Piako Substation, 72 Roache Rd, Morrinsville | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 74 | 71 | 142 | 0.00043373 | 6.1088e-06 | 2014-08-22 | B | 0.00021686 | 3.054e-06 | 2015 | 2014-08-22 | B | 2 | 0.00043373 | 6.1088e-06
1 | 1161823 | 2014-08-22 09:15 | 2014-08-22 14:16 | 301 | 13 | 3913 | 0.011968 | 3.9759e-05 | NAPA ID:01349 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole P11890 | Cut trees away from 11kV line. Works location: Ridge Rd Kimbolton PPPD 43730 | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 301 | 298 | 3874 | 0.011833 | 3.9708e-05 | 2014-08-22 | B | 0.0059164 | 1.9854e-05 | 2015 | 2014-08-22 | B | 13 | 0.011833 | 3.9708e-05
1 | 1458271 | 2014-08-22 10:40 | 2014-08-22 14:51 | 251 | 80 | 20080 | 0.061413 | 0.00024467 | NAPA ID:02052 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 777626 | Reinstate 11kv conductor pole 777626. Works location: River Rd, Raetihi. WO 10153184. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 251 | 248 | 19840 | 0.0606 | 0.00024435 | 2014-08-22 | B | 0.0303 | 0.00012218 | 2015 | 2014-08-22 | B | 80 | 0.0606 | 0.00024435
1 | 1464767 | 2014-08-22 13:38 | 2014-08-22 15:44 | 126.4167 | 1 | 126.4167 | 0.00038664 | 3.0584e-06 | Restore Supply on Device X1309 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 807303 | REPLACED 3 X FUSE HT , UNKNOWN NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK Email sent to Jo to QA as job has SAIDI | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 126.4167 | 123.4167 | 123.4167 | 0.00037697 | 3.0544e-06 | 2014-08-22 | C | 0.00037697 | 3.054e-06 | 2015 | 2014-08-22 | C | 1 | 0.00037697 | 3.0544e-06
1 | 1465008 | 2014-08-22 22:55 | 2014-08-23 00:53 | 118 | 908 | 66257 | 0.20264 | 0.002777 | Restore Supply on Device F21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Links 6204 | CB F21 tripped no flags, line was sectionalised and patrolled abd blown lightning arrestors were found on Links 6204. Links 6204 are now defected and need to be replaced. | F1 | BLAKE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 72.9703 | 69.9703 | 63533 | 0.19406 | 0.0027734 | 2014-08-22 | C | 0.19406 | 0.0027734 | 2015 | 2014-08-22 | C | 908 | 0.19406 | 0.0027734
1 | 1465920 | 2014-08-22 22:59 | 2014-08-23 00:42 | 103.15 | 361 | 16978.2833 | 0.051927 | 0.0011041 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | Walton CB 4 | Feeder Sectionalised. No fault found. Backfeed put in at 2312 via recloser 9705 up to RC25. This did not show on E-Map due to a map connection problem. Many ducks around suspect bird strike. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 47.0313 | 44.0313 | 15895.2833 | 0.048551 | 0.0011026 | 2014-08-22 | C | 0.048551 | 0.0011026 | 2015 | 2014-08-22 | C | 361 | 0.048551 | 0.0011026
1 | 1466326 | 2014-08-23 08:05 | 2014-08-23 10:09 | 123.85 | 2 | 246.05 | 0.00075252 | 6.1168e-06 | Restore Supply on Device TP2086 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | TP2086 & SD5-036. | also affecting OMS 1466329 (Tx TD5-013) - checked with f/man. 2 POSSUMS ON TOP TRANSFORMER TP2086 -BLOWN 3AMP TX FUSE AT TP2086 & BLOWN 8AMP LINE FUSE AT SD5-036. HV, O/H. CAUSED BY POSSUMS FULL POWER RESTORED NOTHING ELSE REPAIRED OR REPLACED ADJA | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 123.025 | 120.025 | 240.05 | 0.00073321 | 6.1088e-06 | 2014-08-23 | C | 0.00073321 | 6.109e-06 | 2015 | 2014-08-23 | C | 2 | 0.00073321 | 6.1088e-06
1 | 1468586 | 2014-08-23 16:02 | 2014-08-23 20:03 | 241.0667 | 53 | 13346.6 | 0.04082 | 0.0001621 | Restore Supply on Device 821 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758032 | Line was isolated at ABS's 252 & 407. Faultman straightened pole 758033. 2 meters of Ngamu conductor was used, 3X 11KV sleeves and line was rehung and rebound. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 251.8226 | 248.8226 | 13187.6 | 0.040281 | 0.00016188 | 2014-08-23 | C | 0.040281 | 0.00016188 | 2015 | 2014-08-23 | C | 53 | 0.040281 | 0.00016188
1 | 1469751 | 2014-08-24 02:01 | 2014-08-24 02:58 | 56.5833 | 850 | 22378.5167 | 0.068443 | 0.0025997 | Restore Supply on Device 717 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Recloser 717 | CB 5 tripped on O/C & Recloser 717 tripped on B phase O/C flags. Line was sectionalised and no fault found.Suspect a opossum. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 26.3277 | 23.3277 | 19828.5167 | 0.060565 | 0.0025963 | 2014-08-24 | C | 0.060565 | 0.0025963 | 2015 | 2014-08-24 | C | 850 | 0.060565 | 0.0025963
1 | 1400165 | 2014-08-24 06:00 | 2014-08-24 07:18 | 78 | 51 | 3978 | 0.012166 | 0.00015598 | NAPA ID:01963 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FS72 | Replace LV disconnector on TX due to burn up. Works location: 21 Manchester St WO 10153174 | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 78 | 75 | 3825 | 0.011683 | 0.00015578 | 2014-08-24 | B | 0.0058416 | 7.7888e-05 | 2015 | 2014-08-24 | B | 51 | 0.011683 | 0.00015578
1 | 1162786 | 2014-08-24 08:30 | 2014-08-24 15:05 | 395 | 138 | 54510 | 0.16671 | 0.00042206 | NAPA ID:00940 TP_MASTERTON GXP > TP_MASTERTON > CHAPEL 33KV | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S173 | Replace 33kV and 11kV LV poles along SH2. Works location: SH2 WO 10130702 09:22 generator currently being set up to cover retirement village. | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 395 | 392 | 54096 | 0.16523 | 0.00042151 | 2014-08-24 | B | 0.082616 | 0.00021075 | 2015 | 2014-08-24 | B | 138 | 0.16523 | 0.00042151
1 | 1471093 | 2014-08-24 16:51 | 2014-08-24 17:35 | 43.85 | 214 | 9383.9 | 0.0287 | 0.0006545 | Restore Supply on Device S173 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7958 | Following Switching Instruction 940 (planned OMS 1470149). Fused ABS 7958 did not operate as designed (not closing). Crew already on site as part of planned shut down replaced components of the Fused ABS. (Crew request not undertaken for this unplanned | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 43.85 | 40.85 | 8741.9 | 0.026701 | 0.00065365 | 2014-08-24 | C | 0.026701 | 0.00065365 | 2015 | 2014-08-24 | C | 214 | 0.026701 | 0.00065365
1 | 1472948 | 2014-08-25 06:53 | 2014-08-25 13:36 | 403.2833 | 281 | 7779.15 | 0.023792 | 0.00085942 | Restore Supply on Device TA9 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P713881 | Repair blown jumper at pole 713881 with live line procedures. Materials included 3 x H/V connectors & approx 1 meter of conductor. Momentary power loss to create back feed at 09:14. C Katene attended. | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 27.6838 | 24.6838 | 6936.15 | 0.021186 | 0.00085829 | 2014-08-25 | C | 0.021186 | 0.00085829 | 2015 | 2014-08-25 | C | 281 | 0.021186 | 0.00085829
1 | 1472476 | 2014-08-25 08:44 | 2014-08-25 15:07 | 382.8167 | 1 | 382.8167 | 0.0011708 | 3.0584e-06 | Restore Supply on Device TC1469 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tc1469 | Karl Lynderman from Powerco wants tx changed because it is running higher voltage and very old. This is at the very end of the line, not many people here in winter but summer there is a lot load. Tx T1469 to be replaced on pole W12378. Changed tx 10 kva r | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 382.8167 | 379.8167 | 379.8167 | 0.0011601 | 3.0544e-06 | 2014-08-25 | C | 0.0011601 | 3.054e-06 | 2015 | 2014-08-25 | C | 1 | 0.0011601 | 3.0544e-06
1 | 1401894 | 2014-08-25 12:11 | 2014-08-25 15:32 | 200.75 | 41 | 8230.75 | 0.025173 | 0.0001254 | NAPA ID:01786 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole M0064 | Replace crossarms and other line equipment on section of network between ABS's 879 and IP585 | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 200.75 | 197.75 | 8107.75 | 0.024765 | 0.00012523 | 2014-08-25 | B | 0.012382 | 6.2616e-05 | 2015 | 2014-08-25 | B | 41 | 0.024765 | 0.00012523
1 | 1474200 | 2014-08-25 20:10 | 2014-08-26 01:13 | 302.9 | 1 | 302.9 | 0.0009264 | 3.0584e-06 | Restore Supply on Device TC2-186 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SC2-089 | Keegan @ contact asked for Andrew customer to be called when on the way. Asked Tarns @ svs hub if faultman can call customer when enroute. 9.54pm Hilton advised 11kv cable blown off top of 11kv metering unit, x4 tx off this line, 5 cool store business. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 302.9 | 299.9 | 299.9 | 0.00091602 | 3.0544e-06 | 2014-08-25 | C | 0.00091602 | 3.054e-06 | 2015 | 2014-08-25 | C | 1 | 0.00091602 | 3.0544e-06
1 | 1474316 | 2014-08-25 21:44 | 2014-08-25 23:23 | 99.3167 | 1 | 99.3167 | 0.00030375 | 3.0584e-06 | Restore Supply on Device T848 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T848 | Patrolled line and replaced 2x 10amp HV fuse links. No other assets repaired or replaced on site. Adjacent assets checked and they are up to Powerco standard Email sent to Jo to QA as job has SAIDI | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 99.3167 | 96.3167 | 96.3167 | 0.00029419 | 3.0544e-06 | 2014-08-25 | C | 0.00029419 | 3.054e-06 | 2015 | 2014-08-25 | C | 1 | 0.00029419 | 3.0544e-06
1 | 1505993 | 2014-08-26 13:21 | 2014-08-26 15:28 | 127.4667 | 929 | 43439.25 | 0.13286 | 0.0028413 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 218307 | at 13:21 Pongakawa Sub, CB 1 Tainui Feeder, Recloser 9513 Tripped, O/C, L/O. This was also backfeeding part of Te Puke CB 3 Maketu Feeder, Recloser 9460 Closed Recloser 9147 Open. Faultmen Dispatched & Investigation Began. Call came in from fire service, | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 46.7591 | 43.7591 | 40652.25 | 0.12417 | 0.0028376 | 2014-08-26 | C | 0.12417 | 0.0028376 | 2015 | 2014-08-26 | C | 929 | 0.12417 | 0.0028376
1 | 453047 | 2014-08-27 08:05 | 2014-08-27 14:18 | 373.45 | 100 | 22013.2 | 0.067326 | 0.00030584 | NAPA ID:00476 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | gorden st, masterton | Approved - Replace poles - temp line break installed pole 828369 to reduce outage. | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 220.132 | 217.132 | 21713.2 | 0.066321 | 0.00030544 | 2014-08-27 | B | 0.033161 | 0.00015272 | 2015 | 2014-08-27 | B | 100 | 0.066321 | 0.00030544
1 | 1329737 | 2014-08-27 08:46 | 2014-08-27 14:56 | 370.1167 | 28 | 10363.2667 | 0.031695 | 8.5636e-05 | NAPA ID:00816 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 212168 | Replace poles and arms and recon HV wire. Works location" Omanawa Rd WO 10140535 Power actually off between ABS Temp19 and Recloser 9806 | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 370.1167 | 367.1167 | 10279.2667 | 0.031397 | 8.5524e-05 | 2014-08-27 | B | 0.015699 | 4.2762e-05 | 2015 | 2014-08-27 | B | 28 | 0.031397 | 8.5524e-05
1 | 1401900 | 2014-08-27 09:00 | 2014-08-27 15:25 | 384.6 | 39 | 14999.4 | 0.045874 | 0.00011928 | NAPA ID:00848 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 585 | Replace crossarms and OH line equipment on the section of network isolated between ABS's IP585 and TEMP86 | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 384.6 | 381.6 | 14882.4 | 0.045457 | 0.00011912 | 2014-08-27 | B | 0.022729 | 5.9561e-05 | 2015 | 2014-08-27 | B | 39 | 0.045457 | 0.00011912
1 | 1528228 | 2014-08-27 09:09 | 2014-08-27 09:24 | 14.6167 | 3 | 41.3167 | 0.00012636 | 9.1753e-06 | Restore Supply on Device C6040 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 16A Arthur Street, Hawera | Related to oms 1527972. The tap in oms job 1527972 was forced down to transformer level. However, this created two new separate oms jobs. The two new jobs were grouped together in this job oms job 1528228. I pressed the "unlock" button but that action can | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 13.7722 | 10.7722 | 32.3167 | 9.8709e-05 | 9.1633e-06 | 2014-08-27 | C | 9.8709e-05 | 9.163e-06 | 2015 | 2014-08-27 | C | 3 | 9.8709e-05 | 9.1633e-06
1 | 1532345 | 2014-08-27 14:19 | 2014-08-27 14:50 | 31 | 1 | 31 | 9.4811e-05 | 3.0584e-06 | Restore Supply on Device C20 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 778519 | Outage required from Fuses 2945 to replace a broken DDO. (Helwan Army camp) | F3/F4 | RUAPEHU | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 31 | 28 | 28 | 8.5524e-05 | 3.0544e-06 | 2014-08-27 | C | 8.5524e-05 | 3.054e-06 | 2015 | 2014-08-27 | C | 1 | 8.5524e-05 | 3.0544e-06
1 | 1532720 | 2014-08-27 15:56 | 2014-08-27 18:27 | 150.6667 | 1 | 150.6667 | 0.0004608 | 3.0584e-06 | Restore Supply on Device 1336 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuses 8446 | replaced 2x3amp HT fuses blown at spur line, due to bird strike No other assets repaired or replaced and all adjacent assets checked and areup to Powerco standard Email sent to Jo to QA as job has SAIDI | F3 | BROOKLANDS 7 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 150.6667 | 147.6667 | 147.6667 | 0.00045104 | 3.0544e-06 | 2014-08-27 | C | 0.00045104 | 3.054e-06 | 2015 | 2014-08-27 | C | 1 | 0.00045104 | 3.0544e-06
1 | 1532782 | 2014-08-27 18:01 | 2014-08-27 20:23 | 142 | 4 | 352.8167 | 0.0010791 | 1.2234e-05 | Restore Supply on Device T3/42 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M71 | check oms 1532979 - part power at 787 Reu Reu Road, Halcombe check 171 reu reu road part power 1533039 also, also oms 1533043 part power 52 reu reu road replaced 1x 15amp ht fuse No other assets repaired or replaced and all adjacent assets checked and | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88.2042 | 85.2042 | 340.8167 | 0.001041 | 1.2218e-05 | 2014-08-27 | C | 0.001041 | 1.2218e-05 | 2015 | 2014-08-27 | C | 4 | 0.001041 | 1.2218e-05
1 | 1532832 | 2014-08-27 19:23 | 2014-08-28 01:55 | 391.6333 | 219 | 61063.9833 | 0.18676 | 0.00066979 | Restore Supply on Device FC731 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5976 | at 20:20 Thames Sub, CB 3 Queen St Feeder. Found LV Board at Transformer TC5976 was burning up and melting. Isolated at Fuses FC731. Was determined that we could not Earth at Fuses FC731 - Isolated at ABS IC2714, IC2716 & IC2724. Partial Backfeed from THS | F2/F3 | QUEEN ST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 278.831 | 275.831 | 60406.9833 | 0.18451 | 0.00066892 | 2014-08-27 | C | 0.18451 | 0.00066892 | 2015 | 2014-08-27 | C | 219 | 0.18451 | 0.00066892
1 | 1534272 | 2014-08-28 06:16 | 2014-08-28 07:56 | 100.6833 | 2 | 122.05 | 0.00037328 | 6.1168e-06 | Restore Supply on Device T7/246 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/246 | replaced 2x 10a hv fuse links. nothing else repaired or replaced. adjacent assets all good Email sent to Jo to QA as job has SAIDI | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 61.025 | 58.025 | 116.05 | 0.00035447 | 6.1088e-06 | 2014-08-28 | C | 0.00035447 | 6.109e-06 | 2015 | 2014-08-28 | C | 2 | 0.00035447 | 6.1088e-06
1 | 1401905 | 2014-08-28 09:00 | 2014-08-28 16:07 | 426.5833 | 13 | 5545.5833 | 0.016961 | 3.9759e-05 | NAPA ID:00855 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Arapuni Rd | Replace crossarms and OH line equipment between ABS TEMP86 and Regulator 9307 | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 426.5833 | 423.5833 | 5506.5833 | 0.016819 | 3.9708e-05 | 2014-08-28 | B | 0.0084097 | 1.9854e-05 | 2015 | 2014-08-28 | B | 13 | 0.016819 | 3.9708e-05
1 | 1395679 | 2014-08-28 10:00 | 2014-08-28 14:15 | 254.7333 | 26 | 6623.0667 | 0.020256 | 7.9519e-05 | NAPA ID:01883 TP_CARRINGTON GXP > OAKURA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 485 | Replace 11kV ABS 485 (DNO 140716). ABS 187 (DNO 140720) replace pole. Works location: Lower Pitone Rd Okato WO 10149812 | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 254.7333 | 251.7333 | 6545.0667 | 0.019991 | 7.9415e-05 | 2014-08-28 | B | 0.0099957 | 3.9708e-05 | 2015 | 2014-08-28 | B | 26 | 0.019991 | 7.9415e-05
1 | 1541984 | 2014-08-28 12:14 | 2014-08-28 13:20 | 66.5 | 1 | 66.5 | 0.00020339 | 3.0584e-06 | Restore Supply on Device 4876T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | nn | brett advised this is related to planned shutdown for replacing HV cross arms. Job should have rolled up to NAPA job | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 66.5 | 63.5 | 63.5 | 0.00019396 | 3.0544e-06 | 2014-08-28 | C | 0.00019396 | 3.054e-06 | 2015 | 2014-08-28 | C | 1 | 0.00019396 | 3.0544e-06
1 | 1542277 | 2014-08-28 14:10 | 2014-08-28 15:57 | 106.9833 | 1 | 106.9833 | 0.0003272 | 3.0584e-06 | Restore Supply on Device TC4505 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | W13011 | replaced 1x 3amp ddo fuse cause ducks flying through lines, lines by estuary - 3.46pm Lft msge Justin No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 106.9833 | 103.9833 | 103.9833 | 0.00031761 | 3.0544e-06 | 2014-08-28 | C | 0.00031761 | 3.054e-06 | 2015 | 2014-08-28 | C | 1 | 0.00031761 | 3.0544e-06
1 | 1542305 | 2014-08-28 14:41 | 2014-08-28 15:51 | 69.5 | 1 | 69.5 | 0.00021256 | 3.0584e-06 | Restore Supply on Device TC4749 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 264290 tc4749 (no number on the tx) | replaced 2x 3amp Hv fuses & 1x 80amp din fuse lv due to wind No other assets repaired or replaced and all adjacent assets checked and are ok / up to Powerco standard Email sent to Jo to QA as job has SAIDI | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 69.5 | 66.5 | 66.5 | 0.00020312 | 3.0544e-06 | 2014-08-28 | C | 0.00020312 | 3.054e-06 | 2015 | 2014-08-28 | C | 1 | 0.00020312 | 3.0544e-06
1 | 1542329 | 2014-08-28 15:26 | 2014-08-28 17:15 | 108.9833 | 1 | 108.9833 | 0.00033332 | 3.0584e-06 | Restore Supply on Device 3267T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx 3267t | replaced HT HV 1x 3amp fuse No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 108.9833 | 105.9833 | 105.9833 | 0.00032372 | 3.0544e-06 | 2014-08-28 | C | 0.00032372 | 3.054e-06 | 2015 | 2014-08-28 | C | 1 | 0.00032372 | 3.0544e-06
1 | 1542537 | 2014-08-28 18:23 | 2014-08-28 20:12 | 109.5667 | 2 | 219.1333 | 0.0006702 | 6.1168e-06 | Restore Supply on Device T2/124 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | H65 | Line down on road - affecting 3 properties - goose flew through line 6.09pm advised Shannon at the hub 2 X HT FUSES AT H65, 2 X 6 AMP FUSES NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 109.5667 | 106.5667 | 213.1333 | 0.000651 | 6.1088e-06 | 2014-08-28 | C | 0.000651 | 6.109e-06 | 2015 | 2014-08-28 | C | 2 | 0.000651 | 6.1088e-06
1 | 1542112 | 2014-08-28 19:35 | 2014-08-28 23:42 | 246.7833 | 15 | 3701.75 | 0.011322 | 4.5876e-05 | NAPA ID:02220 TP_WANGANUI GXP > TAUPO QUAY SUB > TAUPO 1 | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 705314 | Replace rotten 11kv X arms on pole 705314 | F2 | TAUPO 1 | TAUPO QUAY SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 246.7833 | 243.7833 | 3656.75 | 0.011169 | 4.5816e-05 | 2014-08-28 | B | 0.0055846 | 2.2908e-05 | 2015 | 2014-08-28 | B | 15 | 0.011169 | 4.5816e-05
1 | 1555204 | 2014-08-30 13:23 | 2014-08-30 17:21 | 238.4 | 90 | 21456 | 0.065622 | 0.00027526 | Restore Supply on Device T102 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T102 | at TX102 on pole 796841 found 2x drop out holder broken this will require full 11kv shutdown will work through control shortly need another faultman to assit and a bucket truck and 2 dropouts and traffic managment and lengthen jumpers only 2 out of three | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 238.4 | 235.4 | 21186 | 0.064711 | 0.0002749 | 2014-08-30 | C | 0.064711 | 0.0002749 | 2015 | 2014-08-30 | C | 90 | 0.064711 | 0.0002749
1 | 1555720 | 2014-08-31 02:41 | 2014-08-31 04:29 | 108.5333 | 1 | 108.5333 | 0.00033194 | 3.0584e-06 | Restore Supply on Device X1071 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses 2644 | Faultman replaced 1 x 10Amp HV fuse. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 108.5333 | 105.5333 | 105.5333 | 0.00032234 | 3.0544e-06 | 2014-08-31 | C | 0.00032234 | 3.054e-06 | 2015 | 2014-08-31 | C | 1 | 0.00032234 | 3.0544e-06
1 | 1557976 | 2014-08-31 06:40 | 2014-08-31 13:17 | 396.75 | 544 | 66702.0333 | 0.204 | 0.0016638 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | P1948 & P13331 | CB 6 L/O on O/C & E/F Secvtionalised & found two faults. Lines down between ABS IC1223, IC200 & IC247. 2nd fault beyound ABS IC246. Back feed rest of area. Repaired lines down and re livened. 20m of squirrel wire 2 sleeves, 2m of ferret wire & 2 sleeves | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 122.614 | 119.614 | 65070.0333 | 0.19875 | 0.0016616 | 2014-08-31 | C | 0.19875 | 0.0016616 | 2015 | 2014-08-31 | C | 544 | 0.19875 | 0.0016616
1 | 1557962 | 2014-08-31 08:24 | 2014-08-31 12:49 | 264.6833 | 2 | 435.45 | 0.0013318 | 6.1168e-06 | Restore Supply on Device X1630 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 796592 | replaced 2x hv link fuses 450 10 amp pole 796592 due to bird strike surround ing asett good nothing else repaired or replaced | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 217.725 | 214.725 | 429.45 | 0.0013117 | 6.1088e-06 | 2014-08-31 | C | 0.0013117 | 6.109e-06 | 2015 | 2014-08-31 | C | 2 | 0.0013117 | 6.1088e-06
1 | 1557966 | 2014-08-31 08:25 | 2014-08-31 12:44 | 259.4167 | 1 | 259.4167 | 0.00079341 | 3.0584e-06 | Restore Supply on Device X1795 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 796592 | replaced 2x hv link fuses 10 amp pole 796592 due to bird strike surround ing asett good nothing else repaired or replaced | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 259.4167 | 256.4167 | 256.4167 | 0.00078321 | 3.0544e-06 | 2014-08-31 | C | 0.00078321 | 3.054e-06 | 2015 | 2014-08-31 | C | 1 | 0.00078321 | 3.0544e-06
1 | 1569119 | 2014-08-31 10:12 | 2014-08-31 11:47 | 94.4 | 1 | 94.4 | 0.00028872 | 3.0584e-06 | Restore Supply on Device TC281 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t281 | c769 stay wire touched the low voltage and caused 2 fuses to blow at tx t281 so replaced 2x 3amp ddo high voltage fuses at t281 and the staywire needs to be replaced at pole c769 may also need anchor this is Amber 1 defected photos taken. No other asset | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 94.4 | 91.4 | 91.4 | 0.00027917 | 3.0544e-06 | 2014-08-31 | C | 0.00027917 | 3.054e-06 | 2015 | 2014-08-31 | C | 1 | 0.00027917 | 3.0544e-06
1 | 1571328 | 2014-08-31 17:49 | 2014-08-31 19:35 | 105.4833 | 1 | 105.4833 | 0.00032261 | 3.0584e-06 | Restore Supply on Device 2207T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 2207T | Faultman replaced 1 X 3Amp HV fuse at transformer 2207T. No other assets repaired or replaced on site. Checked adjacent assets and all up to Powerco Standard. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 105.4833 | 102.4833 | 102.4833 | 0.00031303 | 3.0544e-06 | 2014-08-31 | C | 0.00031303 | 3.054e-06 | 2015 | 2014-08-31 | C | 1 | 0.00031303 | 3.0544e-06
1 | 1573100 | 2014-09-01 08:37 | 2014-09-01 13:48 | 311.3333 | 619 | 65699.8667 | 0.20094 | 0.0018932 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R1541 | CB 1 L/O on O/C & E/F. Sectionalised and found fault between ABS IC251 & IC424. Back feed rest of area. Repaired lines down & re livened. | F4 | WHIRITOA | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 106.1387 | 103.1387 | 63842.8667 | 0.195 | 0.0018907 | 2014-09-01 | C | 0.195 | 0.0018907 | 2015 | 2014-09-01 | C | 619 | 0.195 | 0.0018907
1 | 1336266 | 2014-09-01 08:47 | 2014-09-01 11:37 | 169.5833 | 5 | 847.9167 | 0.0025933 | 1.5292e-05 | NAPA ID:01635 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2997 | Change transformer X2997, tree cutting between transformers 738/739. Works location: 599 Kaweka Rd Taihape. WO 10141784 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 169.5833 | 166.5833 | 832.9167 | 0.0025441 | 1.5272e-05 | 2014-09-01 | B | 0.001272 | 7.636e-06 | 2015 | 2014-09-01 | B | 5 | 0.0025441 | 1.5272e-05
1 | 1574256 | 2014-09-01 10:16 | 2014-09-01 12:13 | 116.4833 | 1 | 116.4833 | 0.00035626 | 3.0584e-06 | Restore Supply on Device TE3-145 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 216676 | Replaced blown 3amp HV fuse, o/h cause was due to a possum. No other assets repaired or replaced on site. Checked adjacent assets and up to Powerco standard. | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 116.4833 | 113.4833 | 113.4833 | 0.00034663 | 3.0544e-06 | 2014-09-01 | C | 0.00034663 | 3.054e-06 | 2015 | 2014-09-01 | C | 1 | 0.00034663 | 3.0544e-06
1 | 1574907 | 2014-09-01 10:56 | 2014-09-01 12:16 | 79.1 | 536 | 20362.1333 | 0.062276 | 0.0016393 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | B0456 | CB 5 tripped on E/F. Magpie on line at pole B0456, removed by hotstick. | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 37.9891 | 34.9891 | 18754.1333 | 0.057283 | 0.0016372 | 2014-09-01 | C | 0.057283 | 0.0016372 | 2015 | 2014-09-01 | C | 536 | 0.057283 | 0.0016372
1 | 1400115 | 2014-09-02 08:52 | 2014-09-02 12:40 | 228.0667 | 2 | 456.1333 | 0.001395 | 6.1168e-06 | NAPA ID:01385 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH864 | Replace 11kV poles. Works location: Hawera Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 228.0667 | 225.0667 | 450.1333 | 0.0013749 | 6.1088e-06 | 2014-09-02 | B | 0.00068745 | 3.054e-06 | 2015 | 2014-09-02 | B | 2 | 0.0013749 | 6.1088e-06
1 | 1579857 | 2014-09-02 11:59 | 2014-09-11 11:22 | 12922.9167 | 8 | 796.1333 | 0.0024349 | 2.4467e-05 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | TP300 | mid span damage on 11kv spur line possibly caused by branches blown onto the line and now clear damage to phases and an lv conductor has similar damage. This needs to be repaired tomorrow by a gloving crew Dave James advised The Thames guy may do this. S | F4 | CAMPBELL RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 99.5167 | 96.5167 | 772.1333 | 0.0023584 | 2.4435e-05 | 2014-09-02 | B | 0.0011792 | 1.2218e-05 | 2015 | 2014-09-02 | B | 8 | 0.0023584 | 2.4435e-05
1 | 1580420 | 2014-09-02 22:10 | 2014-09-03 02:26 | 255.6 | 674 | 114446.0333 | 0.35002 | 0.0020614 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 215657 | Car hit Poles 215657 & 654060. Poles replaced. Back feed from Sectionalizer 9694 WRD 8. Isolation ABS 9517/1 Links 9517/6 ABS IP425. NDR 048838. | F3 | OROPI RD | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 169.8012 | 166.8012 | 112424.0333 | 0.34339 | 0.0020587 | 2014-09-02 | C | 0.34339 | 0.0020587 | 2015 | 2014-09-02 | C | 674 | 0.34339 | 0.0020587
1 | 1582066 | 2014-09-03 07:06 | 2014-09-03 10:10 | 183.6167 | 1 | 183.6167 | 0.00056158 | 3.0584e-06 | Restore Supply on Device X209 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 804686 | Replaced 2 x 10amp HV fuses OH. Unknown, poss birds at pole 804686. Also replaced 1 of 2 candles. Adjacent assets checked, no other repairs or replacements. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 183.6167 | 180.6167 | 180.6167 | 0.00055168 | 3.0544e-06 | 2014-09-03 | C | 0.00055168 | 3.054e-06 | 2015 | 2014-09-03 | C | 1 | 0.00055168 | 3.0544e-06
1 | 454399 | 2014-09-03 08:34 | 2014-09-03 14:05 | 331.0167 | 2 | 662.0333 | 0.0020248 | 6.1168e-06 | NAPA ID:00478 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11000 | PLANNED | Distribution Equip. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7490 | Replace 11kV poles and reconductor. Work Location: Gordon Street, Masterton. Line isolated at 11kV Links 7490 so pole can be replaced and new conductor run between pole numbers 357725 and 837427. Work Order 10138778. | F3/F4 | GORDON ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 331.0167 | 328.0167 | 656.0333 | 0.0020038 | 6.1088e-06 | 2014-09-03 | B | 0.0010019 | 3.054e-06 | 2015 | 2014-09-03 | B | 2 | 0.0020038 | 6.1088e-06
1 | 1383671 | 2014-09-03 08:46 | 2014-09-03 12:55 | 249.3167 | 1 | 249.3167 | 0.00076252 | 3.0584e-06 | NAPA ID:01838 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 788746, X2579 | LLP: Cut 11kV jumpers at pole 787746. AP: Lower 11kV lines for tree cutting. Works location: Koeke Rd Taihape. PPPD 48660 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 249.3167 | 246.3167 | 246.3167 | 0.00075236 | 3.0544e-06 | 2014-09-03 | B | 0.00037618 | 1.527e-06 | 2015 | 2014-09-03 | B | 1 | 0.00075236 | 3.0544e-06
1 | 1388913 | 2014-09-03 09:18 | 2014-09-03 13:30 | 252 | 11 | 2772 | 0.0084779 | 3.3643e-05 | NAPA ID:01808 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36243 | Inform control of time T1/152 is livened. Replace 11kV poles (P36243 T1/1582), P43637, P43636, P36031. Works location: Hwy 56 Rangiotu. WO 10156813. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 252 | 249 | 2739 | 0.0083661 | 3.3599e-05 | 2014-09-03 | B | 0.004183 | 1.6799e-05 | 2015 | 2014-09-03 | B | 11 | 0.0083661 | 3.3599e-05
1 | 1583698 | 2014-09-03 09:44 | 2014-09-03 15:00 | 316.1333 | 1 | 316.1333 | 0.00096687 | 3.0584e-06 | Restore Supply on Device 3705T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708259 | Repaired stay wire, replaced 2 x 2 amp DDO fuse at pole 708259. HV OH. Unknown cause. No other repairs or replacements and adjacent assets checked. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 316.1333 | 313.1333 | 313.1333 | 0.00095644 | 3.0544e-06 | 2014-09-03 | C | 0.00095644 | 3.054e-06 | 2015 | 2014-09-03 | C | 1 | 0.00095644 | 3.0544e-06
1 | 1584683 | 2014-09-04 01:01 | 2014-09-04 10:39 | 578 | 1 | 578 | 0.0017678 | 3.0584e-06 | Restore Supply on Device X1600 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 779729 | This was missed by Control, request was put through at 6:45am by dispatch. Replaced 2 x 5amp OH HV glass fuses rewireable on pole 779729 . Due to lightning. Adjacent assets checked and no other repairs or replacements made. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 578 | 575 | 575 | 0.0017563 | 3.0544e-06 | 2014-09-04 | C | 0.0017563 | 3.054e-06 | 2015 | 2014-09-04 | C | 1 | 0.0017563 | 3.0544e-06
1 | 1584894 | 2014-09-04 06:29 | 2014-09-04 09:33 | 184.5833 | 2 | 344.6 | 0.0010539 | 6.1168e-06 | Restore Supply on Device T975 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815018 | Replaced 2 x 10amp HV OH fuses at pole 815018, possibly bird strike for cause. Adjacent assets checked and no other repairs or replacements made. | F4 | TAWAHA | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 172.3 | 169.3 | 338.6 | 0.0010342 | 6.1088e-06 | 2014-09-04 | C | 0.0010342 | 6.109e-06 | 2015 | 2014-09-04 | C | 2 | 0.0010342 | 6.1088e-06
1 | 1584918 | 2014-09-04 08:10 | 2014-09-04 09:57 | 106.6167 | 1 | 106.6167 | 0.00032608 | 3.0584e-06 | Restore Supply on Device X1311 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 779699 | Replaced 2 x 8amp OH HV fuses at pole 779699. Due to lightening. Adjacent assets checked and no other repairs or replacements. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 106.6167 | 103.6167 | 103.6167 | 0.00031649 | 3.0544e-06 | 2014-09-04 | C | 0.00031649 | 3.054e-06 | 2015 | 2014-09-04 | C | 1 | 0.00031649 | 3.0544e-06
1 | 1584970 | 2014-09-04 08:19 | 2014-09-04 10:52 | 152.8167 | 351 | 9586.1 | 0.029318 | 0.0010735 | Restore Supply on Device U40 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | U40 | Tripping on CBU40 on Y Phase E/F. Feeder initially backfed from VS8801 to Recloser CB6224. Patrol / sectionalising carried out but all restored OK. Suspect bird Strike. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 27.3108 | 24.3108 | 8533.1 | 0.026064 | 0.0010721 | 2014-09-04 | C | 0.026064 | 0.0010721 | 2015 | 2014-09-04 | C | 351 | 0.026064 | 0.0010721
1 | 1400083 | 2014-09-04 08:38 | 2014-09-04 14:59 | 380.5833 | 12 | 4010.3333 | 0.012265 | 3.6701e-05 | NAPA ID:00820 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212138 | REPLACE HV POLES AND HV WIRES. Works location: Omanawa Rd. WO 10140535. Actual outage is between Line Break at Pole 212138 and ABS Temp 19. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 334.1944 | 331.1944 | 3974.3333 | 0.012139 | 3.6653e-05 | 2014-09-04 | B | 0.0060696 | 1.8327e-05 | 2015 | 2014-09-04 | B | 12 | 0.012139 | 3.6653e-05
1 | 1388909 | 2014-09-04 08:56 | 2014-09-04 13:34 | 277.35 | 7 | 1941.45 | 0.0059378 | 2.1409e-05 | NAPA ID:01393 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH836 | Replace poles. Works location: Nowell Rd, Hawera. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 277.35 | 274.35 | 1920.45 | 0.0058659 | 2.1381e-05 | 2014-09-04 | B | 0.0029329 | 1.069e-05 | 2015 | 2014-09-04 | B | 7 | 0.0058659 | 2.1381e-05
1 | 1402057 | 2014-09-04 08:59 | 2014-09-04 12:07 | 188.45 | 2 | 376.9 | 0.0011527 | 6.1168e-06 | NAPA ID:00858 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2186 | Replace 11kV cross arm on pole M0184 and install a set of LV fuses on transformer TC3560. | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 188.45 | 185.45 | 370.9 | 0.0011329 | 6.1088e-06 | 2014-09-04 | B | 0.00056644 | 3.054e-06 | 2015 | 2014-09-04 | B | 2 | 0.0011329 | 6.1088e-06
1 | 1400241 | 2014-09-04 09:42 | 2014-09-04 14:15 | 272.9333 | 3 | 429.5 | 0.0013136 | 9.1753e-06 | NAPA ID:01754 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-029 | Replace L/V transformer cross arms | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 143.1667 | 140.1667 | 420.5 | 0.0012844 | 9.1633e-06 | 2014-09-04 | B | 0.00064219 | 4.582e-06 | 2015 | 2014-09-04 | B | 3 | 0.0012844 | 9.1633e-06
1 | 1585567 | 2014-09-04 10:01 | 2014-09-04 11:43 | 102.2 | 1 | 102.2 | 0.00031257 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P13193 | Blown x2 HV fuses due to swan hitting the lines replaced x2 60amp Fuses. No other assets repaired or replaced. Adjacent assets were checked and confirm as being ok | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 102.2 | 99.2 | 99.2 | 0.000303 | 3.0544e-06 | 2014-09-04 | C | 0.000303 | 3.054e-06 | 2015 | 2014-09-04 | C | 1 | 0.000303 | 3.0544e-06
1 | 1586405 | 2014-09-04 11:42 | 2014-09-04 14:23 | 160.5667 | 1 | 160.5667 | 0.00049108 | 3.0584e-06 | Restore Supply on Device T1/643 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | P34414 | Replaced 2 x 10amp HV OH fuse at P34414. Cause line clash or bird strike. Adjacent assets checked and no other repairs or replacements. | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 160.5667 | 157.5667 | 157.5667 | 0.00048128 | 3.0544e-06 | 2014-09-04 | C | 0.00048127 | 3.054e-06 | 2015 | 2014-09-04 | C | 1 | 0.00048128 | 3.0544e-06
1 | 1401237 | 2014-09-04 13:00 | 2014-09-04 17:01 | 241.3833 | 1 | 151.1167 | 0.00046218 | 3.0584e-06 | NAPA ID:01755 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-036 | Replace L/V transformer cross arms | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 151.1167 | 148.1167 | 148.1167 | 0.00045241 | 3.0544e-06 | 2014-09-04 | B | 0.00022621 | 1.527e-06 | 2015 | 2014-09-04 | B | 1 | 0.00045241 | 3.0544e-06
1 | 1587887 | 2014-09-04 14:01 | 2014-09-04 15:13 | 71.65 | 1 | 71.65 | 0.00021914 | 3.0584e-06 | Restore Supply on Device T9/243 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T9-251 | Bolt has come off the cross arm but hasn't fallen off the pole yet. 2.06pm adv Tallia at svs hub of job. Repairs to be carried out through Urgent planned shutdown. King bolt to be replaced on 1st pole (pole number not available) from takeoff that goes to | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.65 | 68.65 | 68.65 | 0.00020969 | 3.0544e-06 | 2014-09-04 | C | 0.00020969 | 3.054e-06 | 2015 | 2014-09-04 | C | 1 | 0.00020969 | 3.0544e-06
1 | 1591190 | 2014-09-04 19:31 | 2014-09-05 02:21 | 409.6667 | 354 | 38324.9 | 0.11721 | 0.0010827 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | K1849 | At 19:31 Tahuna Sub, CB 1 Hoe - O - Tainui Feeder, Tripped, Ph B & C Fault, E/F, L/O. Faultmen Dispatched & Investigation Began. A member of the public contacted WEL Networks and informed them that a car had hit a Pole at 642 Tainui Rd, Tahuna & had left | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 108.2624 | 105.2624 | 37262.9 | 0.11382 | 0.0010813 | 2014-09-04 | C | 0.11382 | 0.0010813 | 2015 | 2014-09-04 | C | 354 | 0.11382 | 0.0010813
1 | 1592358 | 2014-09-05 01:24 | 2014-09-05 06:57 | 333 | 2294 | 20552.3 | 0.062858 | 0.007016 | restore supply | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | huirangi 1342 | at 01:24 Huirangi GXP CB 1342 Tripped Nuetral Over Current - No OMS Outage was created for this Inglewood auto Change over system switched Inglewood over to Motukawa via CB 220 - Waitara East was transferred to Huirangi CB 1282 via CB613, Mckee was transf | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 8.9592 | 5.9592 | 13670.3 | 0.041755 | 0.0070068 | 2014-09-05 | C | 0.041755 | 0.0070068 | 2015 | 2014-09-05 | C | 2294 | 0.041755 | 0.0070068
1 | 1594836 | 2014-09-05 02:13 | 2014-09-05 12:11 | 597.4333 | 118 | 49479.7 | 0.15133 | 0.00036089 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758411 | Recloser RC8763/2 tripped to L/O - line patrolled & sectionalised to fault beyond fuses 5481 but fault not located & supply left off for remainder of night past this point - patrol recommenced at daylight - broken polymer strain insulator located on pole | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 419.3195 | 416.3195 | 49125.7 | 0.15005 | 0.00036042 | 2014-09-05 | C | 0.15005 | 0.00036042 | 2015 | 2014-09-05 | C | 118 | 0.15005 | 0.00036042
1 | 1595158 | 2014-09-05 04:35 | 2014-09-05 08:35 | 239.55 | 718 | 59981.8 | 0.18345 | 0.0021959 | Restore Supply on Device 4138 | 22000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4138/2 | CB 4138/2 tripped on B-phase O/C, line was sectionalised and patrolled and no fault was found. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 83.5401 | 80.5401 | 57827.8 | 0.17663 | 0.0021931 | 2014-09-05 | C | 0.17663 | 0.0021931 | 2015 | 2014-09-05 | C | 718 | 0.17663 | 0.0021931
1 | 1596833 | 2014-09-05 06:27 | 2014-09-05 09:56 | 209.0667 | 3 | 461 | 0.0014099 | 9.1753e-06 | Restore Supply on Device T1762 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798606 | Replaced 2 x 10amp HV links through control, cause possible bird strike at pole 798606 Adjacent assets checked and no repairs or replacements. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 153.6667 | 150.6667 | 452 | 0.0013806 | 9.1633e-06 | 2014-09-05 | C | 0.0013806 | 9.163e-06 | 2015 | 2014-09-05 | C | 3 | 0.0013806 | 9.1633e-06
1 | 1596876 | 2014-09-05 07:57 | 2014-09-05 11:24 | 206.6833 | 212 | 21800.9333 | 0.066676 | 0.00064839 | Restore Supply on Device T31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 730312 | CB T31 tripped to L/O - report of arcing on pole 730312 in Eltham Rd - faulty insulator located - line sectionalised - isolations for repairs at ABS 5968 & 5977 - all supply restored following insulator replacement - Chris Katene attended. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 102.8346 | 99.8346 | 21164.9333 | 0.064647 | 0.00064754 | 2014-09-05 | C | 0.064647 | 0.00064754 | 2015 | 2014-09-05 | C | 212 | 0.064647 | 0.00064754
1 | 1598466 | 2014-09-05 15:05 | 2014-09-05 17:47 | 161.4333 | 1 | 1376.6333 | 0.0042103 | 3.0584e-06 | Restore Supply on Device TC1639 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 02575 | Lines down cross arm broken - 3.20pm advised Shannon at svs hub of job. Please ask faultman if property 566 Canal West Road would have been affected re oms 1599918? HV cross arm complete assembly replaced at Pole 02575. Isolation at Fuses FP1168. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1376.6333 | 1373.6333 | 1373.6333 | 0.0041957 | 3.0544e-06 | 2014-09-05 | C | 0.0041957 | 3.054e-06 | 2015 | 2014-09-05 | C | 1 | 0.0041957 | 3.0544e-06
1 | 1598638 | 2014-09-05 15:36 | 2014-09-05 20:17 | 280.9 | 5 | 1404.5 | 0.0042956 | 1.5292e-05 | Restore Supply on Device 2894 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793309 | Replaced broken crossarm (rotten), 3x11kV Pins & Insulators, Associated Bolts, 3x Binders, 2x HV Fuse Carriers, 3x 10Amp HV Fuse elements . Outage commencement time taken form SMC Log (15:36). | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 280.9 | 277.9 | 1389.5 | 0.0042441 | 1.5272e-05 | 2014-09-05 | C | 0.0042441 | 1.5272e-05 | 2015 | 2014-09-05 | C | 5 | 0.0042441 | 1.5272e-05
1 | 1600230 | 2014-09-05 18:08 | 2014-09-05 19:41 | 92.9333 | 2 | 136.45 | 0.00041732 | 6.1168e-06 | Restore Supply on Device TC1511 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 013146 | TC1511 replaced 3x 3amp HV Fuses. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 68.225 | 65.225 | 130.45 | 0.00039845 | 6.1088e-06 | 2014-09-05 | C | 0.00039845 | 6.109e-06 | 2015 | 2014-09-05 | C | 2 | 0.00039845 | 6.1088e-06
1 | 1600284 | 2014-09-05 20:48 | 2014-09-05 22:31 | 103.15 | 1398 | 124372.1667 | 0.38038 | 0.0042757 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 5 | Feeder tripped, O/C B & C Phase, Sectionalised & Patrolled with no fault found | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 88.9644 | 85.9644 | 120178.1667 | 0.36708 | 0.0042701 | 2014-09-05 | C | 0.36708 | 0.0042701 | 2015 | 2014-09-05 | C | 1398 | 0.36708 | 0.0042701
1 | 1602096 | 2014-09-05 22:37 | 2014-09-06 00:20 | 102.55 | 1 | 102.55 | 0.00031364 | 3.0584e-06 | Restore Supply on Device 5351E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6865 | Replaced 2x 6Amp fuse links No other assets repaired or replaced on site. Checked all adjacent assets and all up to Powerco Standard. | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 102.55 | 99.55 | 99.55 | 0.00030407 | 3.0544e-06 | 2014-09-05 | C | 0.00030407 | 3.054e-06 | 2015 | 2014-09-05 | C | 1 | 0.00030407 | 3.0544e-06
1 | 1597395 | 2014-09-06 09:46 | 2014-09-06 09:53 | 6.7 | 1 | 6.7 | 2.0491e-05 | 3.0584e-06 | NAPA ID:02520 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > TE MAUNGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TD4-248 | Isolate SD4-203 remove fuses and cable and remove TX TD4-248 | F3 | TE MAUNGA | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 6.7 | 3.7 | 3.7 | 1.1301e-05 | 3.0544e-06 | 2014-09-06 | B | 5.651e-06 | 1.527e-06 | 2015 | 2014-09-06 | B | 1 | 1.1301e-05 | 3.0544e-06
1 | 1602138 | 2014-09-06 11:47 | 2014-09-06 12:42 | 55 | 26 | 1430 | 0.0043735 | 7.9519e-05 | Restore Supply on Device X1407 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 772471 | Faultman found a broken 11KV jumper at pole 772471 feeding transformer X1407, line was isolated at Fuses 038 to replace the jumper. 1 X 11KV Jumper & 2 Sleeves were used. Outage reflected in OMS Job ID 1603606 | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 1352 | 0.0041296 | 7.9415e-05 | 2014-09-06 | C | 0.0041296 | 7.9415e-05 | 2015 | 2014-09-06 | C | 26 | 0.0041296 | 7.9415e-05
1 | 1606900 | 2014-09-06 21:33 | 2014-09-06 22:52 | 79.6 | 1 | 79.6 | 0.00024345 | 3.0584e-06 | Restore Supply on Device TC2556 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | TC2556 | 2 x 3A DDO's Suspect Duck Strike | F4 | HORRELLS RD | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 79.6 | 76.6 | 76.6 | 0.00023397 | 3.0544e-06 | 2014-09-06 | C | 0.00023397 | 3.054e-06 | 2015 | 2014-09-06 | C | 1 | 0.00023397 | 3.0544e-06
1 | 1622742 | 2014-09-07 15:08 | 2014-09-07 16:24 | 76 | 236 | 17936 | 0.054856 | 0.00072179 | Restore Supply on Device NG2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND |  | Patrol carried out and breaker closed with no apparent fault found. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 76 | 73 | 17228 | 0.052622 | 0.00072084 | 2014-09-07 | C | 0.052622 | 0.00072084 | 2015 | 2014-09-07 | C | 236 | 0.052622 | 0.00072084
1 | 1625230 | 2014-09-08 02:10 | 2014-09-08 04:04 | 114.0167 | 2 | 214.9167 | 0.00065731 | 6.1168e-06 | Restore Supply on Device T1402 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7046 | Faultman found blown and damaged fuse holder at Fuses 7046. 2 X 10Amp HV rewireable fuses were replaced & 1 X fuse holder. | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 107.4583 | 104.4583 | 208.9167 | 0.00063812 | 6.1088e-06 | 2014-09-08 | C | 0.00063812 | 6.109e-06 | 2015 | 2014-09-08 | C | 2 | 0.00063812 | 6.1088e-06
1 | 1625886 | 2014-09-08 07:13 | 2014-09-08 12:02 | 288.9 | 297 | 37816.2 | 0.11566 | 0.00090835 | Restore Supply on Device SD2-009 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | SD2-009 | 2 x 25 A HV Fuse Links Blown at Fuses SD2-009. Main Line Patrolled No Fault found. Recloser 9560 Opened to replace fuses as fuses located on top of bank. Recloser could not be operated by SCADA or locally due to ANT Nest in controller. DNO'd recloser 1409 | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 127.3273 | 124.3273 | 36925.2 | 0.11279 | 0.00090716 | 2014-09-08 | C | 0.11279 | 0.00090716 | 2015 | 2014-09-08 | C | 297 | 0.11279 | 0.00090716
1 | 1389275 | 2014-09-08 09:09 | 2014-09-08 14:29 | 319.7833 | 2 | 639.5667 | 0.0019561 | 6.1168e-06 | NAPA ID:01720 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227852 | Replace TX pole TF8-008 pole 227852 by crane. Install new inline DDOs unit IP1583 at pole 227851. Works location: Otamarakau Valley Rd. WO 10160439. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 319.7833 | 316.7833 | 633.5667 | 0.0019352 | 6.1088e-06 | 2014-09-08 | B | 0.00096759 | 3.054e-06 | 2015 | 2014-09-08 | B | 2 | 0.0019352 | 6.1088e-06
1 | 1396756 | 2014-09-08 09:51 | 2014-09-08 15:16 | 325.0333 | 50 | 13756.3333 | 0.042073 | 0.00015292 | NAPA ID:01557 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA815 | Install crossarms. Replace ABS TA815 - Upgrade earths. Works location: 2426 South Rd. WO 10147441. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 275.1267 | 272.1267 | 13606.3333 | 0.04156 | 0.00015272 | 2014-09-08 | B | 0.02078 | 7.6361e-05 | 2015 | 2014-09-08 | B | 50 | 0.04156 | 0.00015272
1 | 1625743 | 2014-09-08 10:08 | 2014-09-08 17:13 | 424.9333 | 1 | 424.9333 | 0.0012996 | 3.0584e-06 | Restore Supply on Device P2030 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P2030 | All 3 fuses found blown for transformer P2030 - Transformer tested and found to be faulty - job escalated to a 2FR - Transformer Isolated and earthed at it's own fuses - outage time from time of reported outage until 17:00 - Used 1 X 30 kVA 3 phase transf | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 424.9333 | 421.9333 | 421.9333 | 0.0012888 | 3.0544e-06 | 2014-09-08 | C | 0.0012888 | 3.054e-06 | 2015 | 2014-09-08 | C | 1 | 0.0012888 | 3.0544e-06
1 | 1625824 | 2014-09-08 10:53 | 2014-09-08 14:51 | 238.1667 | 1 | 238.1667 | 0.00072841 | 3.0584e-06 | Restore Supply on Device 5436E | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 5436E | Two HV fuses found blown for Transformer 5436E. Line Patrolled and bird found below lines. Fuses replaced. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 238.1667 | 235.1667 | 235.1667 | 0.0007183 | 3.0544e-06 | 2014-09-08 | C | 0.0007183 | 3.054e-06 | 2015 | 2014-09-08 | C | 1 | 0.0007183 | 3.0544e-06
1 | 1395914 | 2014-09-08 21:04 | 2014-09-09 15:11 | 1087.3167 | 17 | 10652.1833 | 0.032579 | 5.1993e-05 | NAPA ID:01874 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/72 | Change TX pole T9/72 and run five spans of new conductor to replace damaged existing conductor. Works location: Akaroa St, Pongaroa. WO 10104790. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 626.599 | 623.599 | 10601.1833 | 0.032381 | 5.1925e-05 | 2014-09-08 | B | 0.01619 | 2.5963e-05 | 2015 | 2014-09-08 | B | 17 | 0.032381 | 5.1925e-05
1 | 1650924 | 2014-09-08 22:24 | 2014-09-09 14:14 | 950.2667 | 1 | 470.8833 | 0.0014402 | 3.0584e-06 | Restore Supply on Device T3/516 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | tx3/516 | Replaced 2 x 3amp HV fuses TX3/516 due to bird strike. Nothing else repaired or replaced surrounding asset all good. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 470.8833 | 467.8833 | 467.8833 | 0.0014291 | 3.0544e-06 | 2014-09-08 | C | 0.0014291 | 3.054e-06 | 2015 | 2014-09-08 | C | 1 | 0.0014291 | 3.0544e-06
1 | 1583774 | 2014-09-09 09:15 | 2014-09-09 15:14 | 359 | 10 | 3560 | 0.010888 | 3.0584e-05 | NAPA ID:01420 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH848 | Change pole and wire run on. Nowell Road. This application has been returned twice and was changed to incorporate a live line to reduce the outage area. (Note this may mean that switching may arrive at Tenix SMC with minimal turnaround time). Applicant | F1, F2, F3 | WHITE 33KV | TP_HAWERA | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 356 | 353 | 3530 | 0.010782 | 3.0544e-05 | 2014-09-09 | B | 0.0053911 | 1.5272e-05 | 2015 | 2014-09-09 | B | 10 | 0.010782 | 3.0544e-05
1 | 1579524 | 2014-09-09 09:30 | 2014-09-09 14:37 | 306.9 | 70 | 21483 | 0.065704 | 0.00021409 | NAPA ID:02225 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 791327, 791325 | Tree Felling Whangaehu Valley Rd between pole numbers 791327 & 791325 (between transformer X1509 & X2449). PPPD 46493. | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 306.9 | 303.9 | 21273 | 0.064977 | 0.00021381 | 2014-09-09 | B | 0.032488 | 0.0001069 | 2015 | 2014-09-09 | B | 70 | 0.064977 | 0.00021381
1 | 1672589 | 2014-09-09 14:22 | 2014-09-09 18:06 | 224 | 242 | 28760.6333 | 0.087962 | 0.00074014 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 266816 | Repair lines down at pole 266816. Tree fallen through lines. Isolation at ABS SF3-010, ABS 9807/1 Links 9807/6. No Backfeeds available. NDR 38634. Faultman Hilton Gardner, Clint Johnson. Materials: 50m of conductor & sleeves. 9/9 8.07pm - Received a call | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 118.8456 | 115.8456 | 28034.6333 | 0.08563 | 0.00073917 | 2014-09-09 | C | 0.08563 | 0.00073917 | 2015 | 2014-09-09 | C | 242 | 0.08563 | 0.00073917
1 | 1573060 | 2014-09-09 16:14 | 2014-09-12 10:30 | 3975.65 | 1 | 3975.65 | 0.012159 | 3.0584e-06 | NAPA ID:02183 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 760882, 760881 | Install TEMP ABS68 using G & B Techniques between poles 760882 & 760881. Jumper removed before ABS completely Connected Feeder dropped out to allow ABS to be connected properly. Work Location: 1194 Otaraoa Road, Waitara. Work Order: 10151691. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 3975.65 | 3972.65 | 3972.65 | 0.012134 | 3.0544e-06 | 2014-09-09 | B | 0.0060671 | 1.527e-06 | 2015 | 2014-09-09 | B | 1 | 0.012134 | 3.0544e-06
1 | 1673649 | 2014-09-09 20:11 | 2014-09-09 20:39 | 28.1167 | 236 | 6635.5333 | 0.020294 | 0.00072179 | Restore Supply on Device NG2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN |  | CB NG2 Tripped. Successfuly closed after stat time. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 28.1167 | 25.1167 | 5927.5333 | 0.018105 | 0.00072084 | 2014-09-09 | C | 0.018105 | 0.00072084 | 2015 | 2014-09-09 | C | 236 | 0.018105 | 0.00072084
1 | 1673945 | 2014-09-09 21:44 | 2014-09-10 03:05 | 321.7667 | 166 | 20914.4833 | 0.063965 | 0.0005077 | Restore Supply on Device S6040 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201923 | Recloser S6040 tripped to L/O - E/F flag - line sectionalised to fault beyond ABS IP443 - broken conductor located & repaired at pole # 201923 - all supply restored following repairs - TJ & Tom Tanoa attended. | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 125.9909 | 122.9909 | 20416.4833 | 0.062361 | 0.00050703 | 2014-09-09 | C | 0.062361 | 0.00050703 | 2015 | 2014-09-09 | C | 166 | 0.062361 | 0.00050703
1 | 1674849 | 2014-09-10 04:51 | 2014-09-10 06:40 | 108.1833 | 1 | 108.1833 | 0.00033087 | 3.0584e-06 | Restore Supply on Device 4933T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 731288 | Replaced x2 8amp HV fuses at links 6014 on pole 731288. Cause was bird strike. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok. | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 108.1833 | 105.1833 | 105.1833 | 0.00032127 | 3.0544e-06 | 2014-09-10 | C | 0.00032127 | 3.054e-06 | 2015 | 2014-09-10 | C | 1 | 0.00032127 | 3.0544e-06
1 | 1674860 | 2014-09-10 06:18 | 2014-09-10 07:49 | 91 | 161 | 13311 | 0.040711 | 0.00049241 | Restore Supply on Device H41 | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Motukawa Sub | CB H41 Tripped - Line patrolled with no fault found. | F3 | TARATA | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 82.677 | 79.677 | 12828 | 0.039182 | 0.00049176 | 2014-09-10 | C | 0.039182 | 0.00049176 | 2015 | 2014-09-10 | C | 161 | 0.039182 | 0.00049176
1 | 1676530 | 2014-09-10 06:51 | 2014-09-10 08:17 | 86 | 10 | 375.5333 | 0.0011485 | 3.0584e-05 | Restore Supply on Device TE4-026 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 386199 | At time of closing job check with Hilton if this fault would have affected 1675041 & 1676514. Replaced 2 x HT 15amp OH fuse at fuses SE4-010. Cause unknown. Adjacent assets checked no other repairs or replacement. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 37.5533 | 34.5533 | 345.5333 | 0.0010554 | 3.0544e-05 | 2014-09-10 | C | 0.0010554 | 3.0544e-05 | 2015 | 2014-09-10 | C | 10 | 0.0010554 | 3.0544e-05
1 | 1488337 | 2014-09-10 09:01 | 2014-09-10 14:08 | 307.7167 | 91 | 28002.2167 | 0.085643 | 0.00027832 | NAPA ID:00822 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212141 | REPLACE HV POLES AND HV WIRES. Works location: Omanawa Rd. WO 10140535. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 307.7167 | 304.7167 | 27729.2167 | 0.084697 | 0.00027795 | 2014-09-10 | B | 0.042348 | 0.00013898 | 2015 | 2014-09-10 | B | 91 | 0.084697 | 0.00027795
1 | 1507044 | 2014-09-10 09:11 | 2014-09-10 15:21 | 370 | 38 | 14060 | 0.043001 | 0.00011622 | NAPA ID:01585 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754773 | Stage 1 of 25. Replace11kV/33kV poles and crossarms. Ngatimaru Road between poles 754773 and 754730. Work order 10151691. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 370 | 367 | 13946 | 0.042597 | 0.00011607 | 2014-09-10 | B | 0.021298 | 5.8034e-05 | 2015 | 2014-09-10 | B | 38 | 0.042597 | 0.00011607
1 | 1687517 | 2014-09-10 09:30 | 2014-09-10 11:00 | 90 | 8 | 720 | 0.0022021 | 2.4467e-05 | Restore Supply on Device TC2148 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2148 | Part of LV planned work. At 09:30 Paeroa Sub, CB 9 Tirohia-Karangahake Feeder. Tenix had applied for an LV Shut today to replace LV Crossarms fed from Transformer TC2148. On arrival to site, they discovered that they also needed to replace an LV crossarm | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 696 | 0.0021259 | 2.4435e-05 | 2014-09-10 | C | 0.0021259 | 2.4435e-05 | 2015 | 2014-09-10 | C | 8 | 0.0021259 | 2.4435e-05
1 | 1400517 | 2014-09-10 10:00 | 2014-09-10 12:21 | 140.3667 | 41 | 5755.0333 | 0.017601 | 0.0001254 | NAPA ID:01630 TP_TE MATAI GXP > TE PUKE SUB > PAPAMOA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-105 | TO TIGHTEN LV BUSHING TO STOP OIL LEAKS. Works location: 1 Conifer Place Te Puke WO 10150521. Dennis Ngatai Attended. They Replaced the whole transformer for this job. | F3 | PAPAMOA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 140.3667 | 137.3667 | 5632.0333 | 0.017203 | 0.00012523 | 2014-09-10 | B | 0.0086013 | 6.2616e-05 | 2015 | 2014-09-10 | B | 41 | 0.017203 | 0.00012523
1 | 1528264 | 2014-09-10 10:24 | 2014-09-10 15:20 | 295.7333 | 28 | 8280.5333 | 0.025325 | 8.5636e-05 | NAPA ID:01758 TP_MT MAUNGANUI 33 GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 219638 | Replace 33kV pole 219638 and cross arms on poles 219639, 219643 and 219644. Works location: SH29, Tauranga. WO 10148262. | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 295.7333 | 292.7333 | 8196.5333 | 0.025036 | 8.5524e-05 | 2014-09-10 | B | 0.012518 | 4.2762e-05 | 2015 | 2014-09-10 | B | 28 | 0.025036 | 8.5524e-05
1 | 1402085 | 2014-09-10 10:58 | 2014-09-10 14:23 | 204.2167 | 35 | 7147.5833 | 0.02186 | 0.00010704 | NAPA ID:01572 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA824 | Replace 11kV ABS TA 824 & cross arms, upgrade earths. Works location: 3264 South Rd. WO 10147441 | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 204.2167 | 201.2167 | 7042.5833 | 0.021511 | 0.0001069 | 2014-09-10 | B | 0.010756 | 5.3452e-05 | 2015 | 2014-09-10 | B | 35 | 0.021511 | 0.0001069
1 | 1676819 | 2014-09-10 15:55 | 2014-09-10 15:25 | -30.4 | 2 | 749.8333 | 0.0022933 | 6.1168e-06 | Restore Supply on Device cut side 1 temp line [380-0-100-0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/390 |  | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 374.9167 | 371.9167 | 743.8333 | 0.002272 | 6.1088e-06 | 2014-09-10 | C | 0.002272 | 6.109e-06 | 2015 | 2014-09-10 | C | 2 | 0.002272 | 6.1088e-06
1 | 1694673 | 2014-09-11 04:27 | 2014-09-11 10:45 | 378.4167 | 35 | 4337.1833 | 0.013265 | 0.00010704 | Restore Supply on Device H139 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03921 | Repaired 11kV Line Down. 11kV to 400V clash which neccessitated Transformer T2/659 to be taken out of service until inspection carried out. Materials used: 2 mtrs squirrel conductor, 2 o/h joints, 1x ali binder, 1x ali-copper ampac connector. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 123.9195 | 120.9195 | 4232.1833 | 0.012927 | 0.0001069 | 2014-09-11 | C | 0.012927 | 0.0001069 | 2015 | 2014-09-11 | C | 35 | 0.012927 | 0.0001069
1 | 1695109 | 2014-09-11 07:02 | 2014-09-11 08:06 | 64.8167 | 27 | 1092.25 | 0.0033406 | 8.2577e-05 | Restore Supply on Device TA718 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | TA718 | Tripping on Fuses TA718 - Patrol carried out but nothing found. Reclosed OK. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40.4537 | 37.4537 | 1011.25 | 0.0030888 | 8.2469e-05 | 2014-09-11 | C | 0.0030888 | 8.2469e-05 | 2015 | 2014-09-11 | C | 27 | 0.0030888 | 8.2469e-05
1 | 1528087 | 2014-09-11 09:00 | 2014-09-11 15:07 | 367.3 | 38 | 13957.4 | 0.042688 | 0.00011622 | NAPA ID:01694 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754773 | Replace 33/11kV Poles and Crossarms. Works location: Ngatimaru Rd. WO 10151691. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 367.3 | 364.3 | 13843.4 | 0.042284 | 0.00011607 | 2014-09-11 | B | 0.021142 | 5.8034e-05 | 2015 | 2014-09-11 | B | 38 | 0.042284 | 0.00011607
1 | 1532319 | 2014-09-11 09:00 | 2014-09-11 12:26 | 205.3 | 91 | 18682.3 | 0.057138 | 0.00027832 | NAPA ID:00823 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 212141 | REPLACE HV POLES AND HV WIRES. Works location: Omanawa Rd. WO 10140535. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 205.3 | 202.3 | 18409.3 | 0.05623 | 0.00027795 | 2014-09-11 | B | 0.028115 | 0.00013898 | 2015 | 2014-09-11 | B | 91 | 0.05623 | 0.00027795
1 | 1569203 | 2014-09-11 09:31 | 2014-09-11 15:40 | 369 | 2 | 738 | 0.0022571 | 6.1168e-06 | NAPA ID:01426 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 722735, 722744 | AP Run new conductor on Hawera Road between poles 722735 & 722744. LLP install LL covers connect new conductor to WH864 fuse pole 722735. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 369 | 366 | 732 | 0.0022358 | 6.1088e-06 | 2014-09-11 | B | 0.0011179 | 3.054e-06 | 2015 | 2014-09-11 | B | 2 | 0.0022358 | 6.1088e-06
1 | 1727224 | 2014-09-11 09:35 | 2014-09-11 17:30 | 475 | 4 | 1900 | 0.005811 | 1.2234e-05 | Restore Supply on Device cut side 1 temp line [425-0-100-0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 802469 | OMS 1457058. Replace 11kV pole 802469, cross arms & transformer. Work Location: Glencairn Road, Marton. Work Order: 10147631. | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 475 | 472 | 1888 | 0.0057668 | 1.2218e-05 | 2014-09-11 | C | 0.0057668 | 1.2218e-05 | 2015 | 2014-09-11 | C | 4 | 0.0057668 | 1.2218e-05
1 | 1473813 | 2014-09-11 09:49 | 2014-09-11 14:35 | 286.05 | 58 | 16590.9 | 0.050742 | 0.00017739 | NAPA ID:01873 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5466 | Replace all HV and LV crossarms on Surrey Road, Inglewood. 6.6kV lines. Works location: Surrey Rd, Tariki, Inglewood. WO 10150398. | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 286.05 | 283.05 | 16416.9 | 0.050144 | 0.00017716 | 2014-09-11 | B | 0.025072 | 8.8578e-05 | 2015 | 2014-09-11 | B | 58 | 0.050144 | 0.00017716
1 | 1552975 | 2014-09-11 12:02 | 2014-09-11 16:31 | 269.4 | 30 | 8082 | 0.024718 | 9.1753e-05 | NAPA ID:02127 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Y61 | Change 4 x 11kV poles. Work order 10156813. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 269.4 | 266.4 | 7992 | 0.024411 | 9.1633e-05 | 2014-09-11 | B | 0.012205 | 4.5816e-05 | 2015 | 2014-09-11 | B | 30 | 0.024411 | 9.1633e-05
1 | 4221867 | 2014-09-11 12:44 | 2014-09-11 14:40 | 116 | 652 | 66441 | 0.2032 | 0.0019941 | Restore Supply on Device 3081 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB 3094 | Restaged Outage. Total Sub Outage. Neville did attend. Suspect protection worked incorrectly. Outage reflected under OMS 4221867. | F2 | WAIOURU LS | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 101.9034 | 98.9034 | 64485 | 0.19696 | 0.0019915 | 2014-09-11 | C | 0.19696 | 0.0019915 | 2015 | 2014-09-11 | C | 652 | 0.19696 | 0.0019915
1 | 1699395 | 2014-09-11 14:11 | 2014-09-11 16:14 | 122.7833 | 1 | 122.7833 | 0.00037552 | 3.0584e-06 | Restore Supply on Device 4361W | 22000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4053, 4361W | Replaced 2x 3a DOO fuse due to unknown. Nothing else repaired or replaced. Adjacent assets all good. Email sent to Jo to QA as job has SAIDI. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 122.7833 | 119.7833 | 119.7833 | 0.00036587 | 3.0544e-06 | 2014-09-11 | C | 0.00036587 | 3.054e-06 | 2015 | 2014-09-11 | C | 1 | 0.00036587 | 3.0544e-06
1 | 1553084 | 2014-09-11 14:40 | 2014-09-11 14:53 | 12.6833 | 1961 | 19732.6167 | 0.060351 | 0.0059976 | NAPA ID:01925 TP_TAURANGA 33 GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 204606 | Replace 33kV cross arms on pole 204606 useing G&B methods. Assurance on 33kV line required. LLP required on the same pole 204606 to cover up 11kV. While carrying out this Live Line Work, the crew had an incident, recorded in Safety Manager 398515. While r | F3 | MURAL TOWN | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 10.0625 | 7.0625 | 13849.6167 | 0.042303 | 0.0059897 | 2014-09-11 | B | 0.021151 | 0.0029949 | 2015 | 2014-09-11 | B | 1961 | 0.042303 | 0.0059897
1 | 1702218 | 2014-09-11 16:26 | 2014-09-11 20:15 | 229 | 331 | 12480.9333 | 0.038172 | 0.0010123 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x2520 | Turakina CB 4. Recloser RS4217 tripped. Replace faulty transformer X2520 | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 37.7067 | 34.7067 | 11487.9333 | 0.035089 | 0.001011 | 2014-09-11 | C | 0.035089 | 0.001011 | 2015 | 2014-09-11 | C | 331 | 0.035089 | 0.001011
1 | 1703170 | 2014-09-11 19:03 | 2014-09-11 19:35 | 32 | 57 | 1824 | 0.0055786 | 0.00017433 | Restore Supply on Device NG2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | NG2 | Ngariki CB2 tripped. Feeder sectionalised to try and isolate the fault area. Request sent to hub at 19:03 and hub called at 20:02 to say someone going to investigate soon. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 1653 | 0.005049 | 0.0001741 | 2014-09-11 | C | 0.005049 | 0.0001741 | 2015 | 2014-09-11 | C | 57 | 0.005049 | 0.0001741
1 | 1703264 | 2014-09-11 23:21 | 2014-09-11 23:34 | 13 | 22 | 286 | 0.00087471 | 6.7285e-05 | Restore Supply on Device NG2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | NG2 | Ngariki CB 2 tripped. (3 amps). | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 13 | 10 | 220 | 0.00067197 | 6.7197e-05 | 2014-09-11 | C | 0.00067197 | 6.7197e-05 | 2015 | 2014-09-11 | C | 22 | 0.00067197 | 6.7197e-05
1 | 1724888 | 2014-09-12 07:13 | 2014-09-12 09:49 | 155.2833 | 12 | 1667.6 | 0.0051002 | 3.6701e-05 | Restore Supply on Device 4969 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 735833 | REPLACED 10 AMP HV 2X FUSES DDO PARITAL SET DUE TO A POSSUM. POLE 735833. SURROUNDING ASSET ALL GOOD NOTHING ELSE REPAIRED OR REPLACED. | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 138.9667 | 135.9667 | 1631.6 | 0.0049836 | 3.6653e-05 | 2014-09-12 | C | 0.0049836 | 3.6653e-05 | 2015 | 2014-09-12 | C | 12 | 0.0049836 | 3.6653e-05
1 | 1585596 | 2014-09-12 09:17 | 2014-09-12 12:10 | 172.8833 | 6 | 1037.3 | 0.0031725 | 1.8351e-05 | NAPA ID:02434 TP_LINTON GXP > TURITEA SUB > LINTON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/337 | Replace 11kV Transformer T2/337 From 30kV to 50kV. Work Location: Eyre Road, Linton. Work Order: 10154823. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 172.8833 | 169.8833 | 1019.3 | 0.0031134 | 1.8327e-05 | 2014-09-12 | B | 0.0015567 | 9.163e-06 | 2015 | 2014-09-12 | B | 6 | 0.0031134 | 1.8327e-05
1 | 1727329 | 2014-09-12 09:29 | 2014-09-12 10:41 | 71.8 | 2 | 110.5667 | 0.00033816 | 6.1168e-06 | Restore Supply on Device TC262 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC262 | HT Fuses blown at TC262 - suspect fuse incorrect amperage - replaced with 3A OK. Relivened. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 55.2833 | 52.2833 | 104.5667 | 0.00031939 | 6.1088e-06 | 2014-09-12 | C | 0.00031939 | 6.109e-06 | 2015 | 2014-09-12 | C | 2 | 0.00031939 | 6.1088e-06
1 | 1727194 | 2014-09-12 10:45 | 2014-09-12 12:54 | 129.15 | 1 | 129.15 | 0.000395 | 3.0584e-06 | Restore Supply on Device T1725 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1725 | Replaced 3x DDO fuse assembly and 3x 2amp fuse links at Transformer T1725. | F4 | OTARAIA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 129.15 | 126.15 | 126.15 | 0.00038532 | 3.0544e-06 | 2014-09-12 | C | 0.00038532 | 3.054e-06 | 2015 | 2014-09-12 | C | 1 | 0.00038532 | 3.0544e-06
1 | 1727877 | 2014-09-12 12:53 | 2014-09-12 15:40 | 167.1667 | 2 | 167.1667 | 0.00051127 | 6.1168e-06 | Restore Supply on Device 2224T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2242T | Replace Transformer 2242T. Email sent to Jo to QA as job has SAIDI. | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 83.5833 | 80.5833 | 161.1667 | 0.00049227 | 6.1088e-06 | 2014-09-12 | C | 0.00049227 | 6.109e-06 | 2015 | 2014-09-12 | C | 2 | 0.00049227 | 6.1088e-06
1 | 1728899 | 2014-09-12 16:08 | 2014-09-12 18:04 | 116.3667 | 5 | 408.8333 | 0.0012504 | 1.5292e-05 | Restore Supply on Device LI701 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726858 | Replaced 2x 15a DDO fuse links O/H. Cause of fault unknown. Nothing else repaired or replaced. Adjacent assets all good. Email sent to Jo to QA as job has SAIDI. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 81.7667 | 78.7667 | 393.8333 | 0.0012029 | 1.5272e-05 | 2014-09-12 | C | 0.0012029 | 1.5272e-05 | 2015 | 2014-09-12 | C | 5 | 0.0012029 | 1.5272e-05
1 | 1730082 | 2014-09-13 05:31 | 2014-09-13 05:52 | 21.1667 | 275 | 5820.8333 | 0.017803 | 0.00084107 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Te Puke CB 3 | Sectionaliser 9460 tripped on Rev E/F. TPV3 being fed from PKW1 via Secion 9460. Feeder Patrolled. No Fault Found. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 21.1667 | 18.1667 | 4995.8333 | 0.015259 | 0.00083997 | 2014-09-13 | C | 0.015259 | 0.00083997 | 2015 | 2014-09-13 | C | 275 | 0.015259 | 0.00083997
1 | 1573095 | 2014-09-13 09:01 | 2014-09-13 16:09 | 428.0167 | 15 | 6420.25 | 0.019636 | 4.5876e-05 | NAPA ID:01723 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 754725, 754672 | 11/33kV crossarm and pole changes between poles #754725 & #754672. Job had 20 minute overrun to stop having another outage. Northpower contractor spoke to customers affected and they were happy for 20 minute longer shut than to have another outage. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 428.0167 | 425.0167 | 6375.25 | 0.019473 | 4.5816e-05 | 2014-09-13 | B | 0.0097364 | 2.2908e-05 | 2015 | 2014-09-13 | B | 15 | 0.019473 | 4.5816e-05
1 | 1733114 | 2014-09-13 09:47 | 2014-09-13 12:08 | 140.6667 | 1 | 140.6667 | 0.00043022 | 3.0584e-06 | Restore Supply on Device TC2817 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2817 | 2 x DDO Fuse 2 amp due to lightning. All adjacent assets ok. No other assets repaired or replaced. Email sent to Jo to QA as job has SAIDI. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 140.6667 | 137.6667 | 137.6667 | 0.00042049 | 3.0544e-06 | 2014-09-13 | C | 0.00042049 | 3.054e-06 | 2015 | 2014-09-13 | C | 1 | 0.00042049 | 3.0544e-06
1 | 1774512 | 2014-09-13 13:29 | 2014-09-13 16:20 | 170.55 | 4 | 682.2 | 0.0020865 | 1.2234e-05 | Restore Supply on Device TC2377 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T2377 | Replaced Transformer T2377 damaged by Lightning. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 170.55 | 167.55 | 670.2 | 0.0020471 | 1.2218e-05 | 2014-09-13 | C | 0.0020471 | 1.2218e-05 | 2015 | 2014-09-13 | C | 4 | 0.0020471 | 1.2218e-05
1 | 1774614 | 2014-09-13 16:36 | 2014-09-13 21:16 | 279.8333 | 237 | 38339.8 | 0.11726 | 0.00072485 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 773351 | Car vs Pole. NDR #41821. Replace 11mtr Busck Pole and all associated hardware. Also replaced 10mtrs of 25mm Cu conductor & 25mm sleeves. | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 161.7713 | 158.7713 | 37628.8 | 0.11493 | 0.0007239 | 2014-09-13 | C | 0.11493 | 0.0007239 | 2015 | 2014-09-13 | C | 237 | 0.11493 | 0.0007239
1 | 1774604 | 2014-09-13 17:14 | 2014-09-13 17:46 | 31.7833 | 6 | 33.5 | 0.00010246 | 1.8351e-05 | Restore Supply on Device TC2543 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2544 | Tempory Repairs done to HV DDO's to Transformer TC2544. A shutdown will be applied for to replace all 3 DDO"s on 15th Sept. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 5.5833 | 2.5833 | 15.5 | 4.7344e-05 | 1.8327e-05 | 2014-09-13 | C | 4.7344e-05 | 1.8327e-05 | 2015 | 2014-09-13 | C | 6 | 4.7344e-05 | 1.8327e-05
1 | 1775351 | 2014-09-13 18:12 | 2014-09-13 19:48 | 95.9833 | 1 | 95.9833 | 0.00029356 | 3.0584e-06 | Restore Supply on Device 3547T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3547T | Replaced 2x 2Amp fuse links - Email sent to Jo to QA as job has SAIDI | F4 | RATAPIKO | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 95.9833 | 92.9833 | 92.9833 | 0.00028401 | 3.0544e-06 | 2014-09-13 | C | 0.00028401 | 3.054e-06 | 2015 | 2014-09-13 | C | 1 | 0.00028401 | 3.0544e-06
1 | 1782459 | 2014-09-14 06:07 | 2014-09-14 08:06 | 118.3167 | 92 | 527.6 | 0.0016136 | 0.00028137 | Restore Supply on Device 1492 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 8260 | Faultman found blown fuse at Fuses 8260, ABS 180 was opened to reload the fuse. 1X 30Amp HV rewirable fuse was used. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 5.7348 | 2.7348 | 251.6 | 0.00076849 | 0.00028101 | 2014-09-14 | C | 0.00076849 | 0.00028101 | 2015 | 2014-09-14 | C | 92 | 0.00076849 | 0.00028101
1 | 1804018 | 2014-09-14 08:38 | 2014-09-14 10:03 | 84.8 | 1 | 84.8 | 0.00025935 | 3.0584e-06 | Restore Supply on Device TC4658 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4658 | REPLACED 2X HV FUSES 6AMP REASON UNKNOWN. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 84.8 | 81.8 | 81.8 | 0.00024985 | 3.0544e-06 | 2014-09-14 | C | 0.00024985 | 3.054e-06 | 2015 | 2014-09-14 | C | 1 | 0.00024985 | 3.0544e-06
1 | 1825517 | 2014-09-14 10:00 | 2014-09-14 16:05 | 364.8671 | 1 | 364.8833 | 0.001116 | 3.0584e-06 | Restore Supply on Device TC2-222 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2079595, SC2121 | 2 X HT FUSES BLOWN REASON UNKNOWN. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 364.8833 | 361.8833 | 361.8833 | 0.0011053 | 3.0544e-06 | 2014-09-14 | C | 0.0011053 | 3.054e-06 | 2015 | 2014-09-14 | C | 1 | 0.0011053 | 3.0544e-06
1 | 1804001 | 2014-09-14 12:25 | 2014-09-14 13:18 | 53 | 1 | 53 | 0.0001621 | 3.0584e-06 | Restore Supply on Device 3030T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3030T | Faultman found broken HV fuse holders on transformer 3030T. Line was isolated at Fused ABS 5291 to replace broken fuse holders. 3X 3Amp HV Fuses replaced & 3x Fuse holders. | F3 | TARATA | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 50 | 0.00015272 | 3.0544e-06 | 2014-09-14 | C | 0.00015272 | 3.054e-06 | 2015 | 2014-09-14 | C | 1 | 0.00015272 | 3.0544e-06
1 | 1803856 | 2014-09-14 15:45 | 2014-09-14 18:00 | 135 | 1 | 135 | 0.00041289 | 3.0584e-06 | Restore Supply on Device T7278 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T7278 | Faultman found transformer T7278 faulty suspect lightening strike. !x 15kVA transformer was replaced. Off Time 15:45 On Time 18:00. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 135 | 132 | 132 | 0.00040318 | 3.0544e-06 | 2014-09-14 | C | 0.00040318 | 3.054e-06 | 2015 | 2014-09-14 | C | 1 | 0.00040318 | 3.0544e-06
1 | 1854768 | 2014-09-14 16:56 | 2014-09-14 19:37 | 161.1833 | 6 | 823.35 | 0.0025182 | 1.8351e-05 | Restore Supply on Device 250 | 22000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 250 | Replaced 3x 6Amp fuse links. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 137.225 | 134.225 | 805.35 | 0.0024599 | 1.8327e-05 | 2014-09-14 | C | 0.0024599 | 1.8327e-05 | 2015 | 2014-09-14 | C | 6 | 0.0024599 | 1.8327e-05
1 | 1854774 | 2014-09-14 17:16 | 2014-09-14 18:47 | 91.1667 | 1 | 91.1667 | 0.00027883 | 3.0584e-06 | Restore Supply on Device T2/89 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B40 | Replace 2x DDO candles (carriers) & 2x10 Amp links. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 91.1667 | 88.1667 | 88.1667 | 0.0002693 | 3.0544e-06 | 2014-09-14 | C | 0.0002693 | 3.054e-06 | 2015 | 2014-09-14 | C | 1 | 0.0002693 | 3.0544e-06
1 | 1855295 | 2014-09-15 04:36 | 2014-09-15 14:33 | 596.9167 | 140 | 14783.6333 | 0.045215 | 0.00042818 | Restore Supply on Device S6029 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 227727 | 11kV Recloser S6029 tripped E/F L/O. Cause was due to lines down at pole 227729 due to bird strike. Isolated via a temp break at pole 2277727. Replaced 10 metres of conductor and four sleeves (two phases). Open & Closed temp break via Live Line methods. R | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 105.5974 | 102.5974 | 14363.6333 | 0.043873 | 0.00042762 | 2014-09-15 | C | 0.043873 | 0.00042762 | 2015 | 2014-09-15 | C | 140 | 0.043873 | 0.00042762
1 | 1855488 | 2014-09-15 07:39 | 2014-09-15 08:26 | 47.2167 | 1 | 47.2167 | 0.00014441 | 3.0584e-06 | Restore Supply on Device E90 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | E90 | Fuses E90 found tripped. Reload relivened OK. Replaced 2 x 20A Fuse links. | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 47.2167 | 44.2167 | 44.2167 | 0.00013506 | 3.0544e-06 | 2014-09-15 | C | 0.00013506 | 3.054e-06 | 2015 | 2014-09-15 | C | 1 | 0.00013506 | 3.0544e-06
1 | 1855777 | 2014-09-15 10:35 | 2014-09-15 13:37 | 182 | 4 | 728 | 0.0022265 | 1.2234e-05 | Restore Supply on Device 7986 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1488 | During line patrol found Transformer T1488 hanging by cable, the transformer arm was rotten and snapped. Replaced 1 x 2m transformer arm. Relivened OK | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 716 | 0.002187 | 1.2218e-05 | 2014-09-15 | C | 0.002187 | 1.2218e-05 | 2015 | 2014-09-15 | C | 4 | 0.002187 | 1.2218e-05
1 | 1856373 | 2014-09-16 02:06 | 2014-09-16 09:44 | 458.3833 | 401 | 16735.9833 | 0.051186 | 0.0012264 | Restore Supply on Device D11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 741108 | CB 7111 tripped no flags line was sectionalised and patrolled and a blown insulator and burnt cross arm was found at pole 741108, line was isolated at Links 4997 to make replace insulator & cross arm. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 41.7356 | 38.7356 | 15532.9833 | 0.047444 | 0.0012248 | 2014-09-16 | C | 0.047444 | 0.0012248 | 2015 | 2014-09-16 | C | 401 | 0.047444 | 0.0012248
1 | 1857720 | 2014-09-16 06:19 | 2014-09-16 08:35 | 136.1 | 11 | 1496.7333 | 0.0045776 | 3.3643e-05 | Restore Supply on Device TP2116 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE5-057 | Fuses SE5-057 Blown 2 links. Line Patrolled. No fault found. Materials: 2 x 20A HV fuse links. Faultman:Hilton Gardner. | F3 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 136.0667 | 133.0667 | 1463.7333 | 0.0044709 | 3.3599e-05 | 2014-09-16 | C | 0.0044709 | 3.3599e-05 | 2015 | 2014-09-16 | C | 11 | 0.0044709 | 3.3599e-05
1 | 1694390 | 2014-09-16 08:36 | 2014-09-16 12:33 | 236.7333 | 1 | 236.7333 | 0.00072403 | 3.0584e-06 | NAPA ID:01466 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH819 | Replace poles. Works location: Rifle Range Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 236.7333 | 233.7333 | 233.7333 | 0.00071392 | 3.0544e-06 | 2014-09-16 | B | 0.00035696 | 1.527e-06 | 2015 | 2014-09-16 | B | 1 | 0.00071392 | 3.0544e-06
1 | 1858512 | 2014-09-16 08:40 | 2014-09-16 11:11 | 150.6833 | 700 | 35476.8 | 0.1085 | 0.0021409 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | I2431 | Replaced 2 X H/T Insulators At Pole I2431. 11.28 Perry called to advise he is completed off this job. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 50.6811 | 47.6811 | 33376.8 | 0.10195 | 0.0021381 | 2014-09-16 | C | 0.10195 | 0.0021381 | 2015 | 2014-09-16 | C | 700 | 0.10195 | 0.0021381
1 | 1575741 | 2014-09-16 09:03 | 2014-09-16 17:02 | 478.9667 | 8 | 3804.15 | 0.011635 | 2.4467e-05 | NAPA ID:01124 TP_TAURANGA 33 GXP > KAURI POINT > LINDERMANN RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TB2-001 | REPLACE SERIES ONE RMU UNIT AND UPGRADE TB2-001 TO A THREE PHASE TX FROM A 2 PHASE TX. Work Location: SH2, Kauri Point. IR5880. W/O 10144545. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 475.5188 | 472.5188 | 3780.15 | 0.011546 | 2.4435e-05 | 2014-09-16 | B | 0.0057731 | 1.2218e-05 | 2015 | 2014-09-16 | B | 8 | 0.011546 | 2.4435e-05
1 | 1583712 | 2014-09-16 09:15 | 2014-09-16 12:53 | 218 | 41 | 8938 | 0.027336 | 0.0001254 | NAPA ID:01859 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 749212 | Replace 33kV xarm and broken 33kV insulators. Work Location: Smart Road. Work Order 10144419. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 218 | 215 | 8815 | 0.026925 | 0.00012523 | 2014-09-16 | B | 0.013462 | 6.2616e-05 | 2015 | 2014-09-16 | B | 41 | 0.026925 | 0.00012523
1 | 1861293 | 2014-09-16 12:06 | 2014-09-16 13:36 | 89.9 | 121 | 10877.9 | 0.033269 | 0.00037007 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Recloser V27 | 11kV Recloser V27 tripped A & B Phase & L/O. Treescape working on CAC 2480-01 unable to establish contact, sent Tenix Fault man to investigate safety of crew. NOTE: Andrew Tahura sent NOT Robin Smith. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 89.9 | 86.9 | 10514.9 | 0.032117 | 0.00036959 | 2014-09-16 | C | 0.032117 | 0.00036959 | 2015 | 2014-09-16 | C | 121 | 0.032117 | 0.00036959
1 | 1861704 | 2014-09-16 14:41 | 2014-09-16 17:52 | 191.2167 | 1 | 191.2167 | 0.00058482 | 3.0584e-06 | Restore Supply on Device T3626 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T3626 | Replaced 2 of 3, 3 amp HV tx fuses at tx T3626. Cause bird strike. Did not work through control. Adjacent assets checked and no other repairs or replacements made. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 191.2167 | 188.2167 | 188.2167 | 0.00057489 | 3.0544e-06 | 2014-09-16 | C | 0.00057489 | 3.054e-06 | 2015 | 2014-09-16 | C | 1 | 0.00057489 | 3.0544e-06
1 | 1863524 | 2014-09-17 00:40 | 2014-09-17 03:41 | 180.7 | 554 | 23913.6667 | 0.073138 | 0.0016944 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P13193 | CB 6 tripped to L/O - E/F flag - 2 x 1r requested - line sectionalised & patrolled - broken conductor located at pole P13193 caused by bird strike - isolations points for repairs were ABS 252 & 299 with back feed established from ABS IC238 - all supply re | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 43.1655 | 40.1655 | 22251.6667 | 0.067966 | 0.0016922 | 2014-09-17 | C | 0.067966 | 0.0016922 | 2015 | 2014-09-17 | C | 554 | 0.067966 | 0.0016922
1 | 1860731 | 2014-09-17 08:45 | 2014-09-17 12:37 | 231.6333 | 337 | 76114.8333 | 0.23279 | 0.0010307 | NAPA ID:01849 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2647 | REPLACE 11KV XARMS. Work Location: Captain Cook Road, Whitianga. Work Order 10141701. | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 225.86 | 222.86 | 75103.8333 | 0.2294 | 0.0010293 | 2014-09-17 | B | 0.1147 | 0.00051467 | 2015 | 2014-09-17 | B | 337 | 0.2294 | 0.0010293
1 | 1584437 | 2014-09-17 08:49 | 2014-09-17 14:54 | 364.8 | 10 | 3648 | 0.011157 | 3.0584e-05 | NAPA ID:02165 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 840310, 370340 | Replacing 15 11kv poles between pole 840310 & 370340. Work Location: Wirihana Road, Hawera. W/O 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 364.8 | 361.8 | 3618 | 0.011051 | 3.0544e-05 | 2014-09-17 | B | 0.0055255 | 1.5272e-05 | 2015 | 2014-09-17 | B | 10 | 0.011051 | 3.0544e-05
1 | 1583943 | 2014-09-17 09:05 | 2014-09-17 15:32 | 386.6333 | 33 | 12758.9 | 0.039022 | 0.00010093 | NAPA ID:02108 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/108 | Install poles for new reg site 10214. Work Location: Kimbolton Road. Work Order 10141262. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 386.6333 | 383.6333 | 12659.9 | 0.038669 | 0.0001008 | 2014-09-17 | B | 0.019334 | 5.0398e-05 | 2015 | 2014-09-17 | B | 33 | 0.038669 | 0.0001008
1 | 1553067 | 2014-09-17 09:15 | 2014-09-17 14:05 | 289.65 | 25 | 7241.25 | 0.022147 | 7.6461e-05 | NAPA ID:01945 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12024 | Stage 1 of 2 for Mot CB 5 Automation. Install, connect, test and commission new Automated Safelink CCC as per attached methodology. | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 289.65 | 286.65 | 7166.25 | 0.021889 | 7.6361e-05 | 2014-09-17 | B | 0.010944 | 3.818e-05 | 2015 | 2014-09-17 | B | 25 | 0.021889 | 7.6361e-05
1 | 1580339 | 2014-09-17 09:31 | 2014-09-17 14:45 | 314.4167 | 98 | 22613.7333 | 0.069162 | 0.00029973 | NAPA ID:01733 TP_KOPU GXP > TAIRUA SUB > PEPE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4363, TC4362 | Replace Transformer TC4363. Disconnect cables from TC4362 as temporary disconnect. Work Order 10111704 | F3 | PEPE RD | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 230.7524 | 227.7524 | 22319.7333 | 0.068174 | 0.00029933 | 2014-09-17 | B | 0.034087 | 0.00014967 | 2015 | 2014-09-17 | B | 98 | 0.068174 | 0.00029933
1 | 1866102 | 2014-09-17 09:46 | 2014-09-17 12:41 | 175.0667 | 1 | 175.0667 | 0.00053543 | 3.0584e-06 | Restore Supply on Device L1412 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728006, L1412 | Photos of burnt hv crossarm & submitted for defect. Signs of burning on paddock side & centre of crossarm. Voltage readings r 238, y 239, b 239. Phase to phase 415 to 417. When rains water is seeping into ddo fuses. Customer has been advised. House is va | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 175.0667 | 172.0667 | 172.0667 | 0.00052556 | 3.0544e-06 | 2014-09-17 | C | 0.00052556 | 3.054e-06 | 2015 | 2014-09-17 | C | 1 | 0.00052556 | 3.0544e-06
1 | 1881792 | 2014-09-18 08:11 | 2014-09-18 13:49 | 337.7167 | 38 | 12833.2333 | 0.039249 | 0.00011622 | Restore Supply on Device U40 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Ngatimaru Road |  | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 337.7167 | 334.7167 | 12719.2333 | 0.03885 | 0.00011607 | 2014-09-18 | C | 0.03885 | 0.00011607 | 2015 | 2014-09-18 | C | 38 | 0.03885 | 0.00011607
1 | 1541431 | 2014-09-18 08:25 | 2014-09-18 13:57 | 332.35 | 87 | 28914.45 | 0.088433 | 0.00026608 | NAPA ID:01966 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/499 | Replace transformer T3/499. Works location: West St, Feilding. WO 10144416. | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 332.35 | 329.35 | 28653.45 | 0.08752 | 0.00026573 | 2014-09-18 | B | 0.04376 | 0.00013287 | 2015 | 2014-09-18 | B | 87 | 0.08752 | 0.00026573
1 | 1583094 | 2014-09-18 08:32 | 2014-09-18 14:59 | 387.8167 | 39 | 15124.85 | 0.046258 | 0.00011928 | NAPA ID:01952 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P0033, P13501 | REPLACE XARMS AND HARDWARE TRIGG & MATHERS ROADS. Work Order 10145664 | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 387.8167 | 384.8167 | 15007.85 | 0.04584 | 0.00011912 | 2014-09-18 | B | 0.02292 | 5.9561e-05 | 2015 | 2014-09-18 | B | 39 | 0.04584 | 0.00011912
1 | 1583096 | 2014-09-18 08:45 | 2014-09-18 16:04 | 438.4833 | 58 | 25432.0333 | 0.077782 | 0.00017739 | NAPA ID:01283 TP_TAURANGA 33 GXP > MATUA SUB > BEACH RD MATUA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-040 | REPLACE SERIES ONE SWITCH GEAR SC4-439. Work Location: Ranui Street. Work Order #10148295 | F3 | BEACH RD MATUA | MATUA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 438.4833 | 435.4833 | 25258.0333 | 0.077149 | 0.00017716 | 2014-09-18 | B | 0.038574 | 8.8578e-05 | 2015 | 2014-09-18 | B | 58 | 0.077149 | 0.00017716
1 | 1676509 | 2014-09-18 08:47 | 2014-09-18 14:17 | 329.9167 | 1 | 329.9167 | 0.001009 | 3.0584e-06 | NAPA ID:01474 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH819 | Live line break & Wire run Rifle Range Rd. Works location: Rifle Range Rd. WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 329.9167 | 326.9167 | 326.9167 | 0.00099854 | 3.0544e-06 | 2014-09-18 | B | 0.00049927 | 1.527e-06 | 2015 | 2014-09-18 | B | 1 | 0.00099854 | 3.0544e-06
1 | 1570791 | 2014-09-18 09:23 | 2014-09-18 12:56 | 213.7333 | 58 | 12396.5333 | 0.037914 | 0.00017739 | NAPA ID:01875 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 757844 | Replace all HV and LV crossarms on Surrey Road Inglewood 6.6kv lines. Work Order 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 213.7333 | 210.7333 | 12222.5333 | 0.037333 | 0.00017716 | 2014-09-18 | B | 0.018666 | 8.8578e-05 | 2015 | 2014-09-18 | B | 58 | 0.037333 | 0.00017716
1 | 1574103 | 2014-09-18 09:27 | 2014-09-18 13:49 | 261.6667 | 24 | 6280 | 0.019207 | 7.3402e-05 | NAPA ID:02198 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/137, T8/140 | Install new 11kv pole and run new LV conductors and install a new set of 11kv DDO's on tx T/140. Work Order 10120655. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 261.6667 | 258.6667 | 6208 | 0.018962 | 7.3306e-05 | 2014-09-18 | B | 0.0094809 | 3.6653e-05 | 2015 | 2014-09-18 | B | 24 | 0.018962 | 7.3306e-05
1 | 1580284 | 2014-09-18 10:02 | 2014-09-18 11:15 | 73 | 24 | 1752 | 0.0053584 | 7.3402e-05 | NAPA ID:02097 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1734 | Replace 11kV Transformer Fuses TC1734. Work Locaiton: 1305 Tiki Road, Coromandel. Work Order #10160348 | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 73 | 70 | 1680 | 0.0051314 | 7.3306e-05 | 2014-09-18 | B | 0.0025657 | 3.6653e-05 | 2015 | 2014-09-18 | B | 24 | 0.0051314 | 7.3306e-05
1 | 1583091 | 2014-09-18 10:05 | 2014-09-18 13:40 | 214.85 | 18 | 3867.3 | 0.011828 | 5.5052e-05 | NAPA ID:02160 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | O3489 | Straighten Pole and Install Breast Block. Re-Sag 11kv Conductors. Work Location: 93 River Road. Work Order 10151289. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 214.85 | 211.85 | 3813.3 | 0.011647 | 5.498e-05 | 2014-09-18 | B | 0.0058237 | 2.749e-05 | 2015 | 2014-09-18 | B | 18 | 0.011647 | 5.498e-05
1 | 1883585 | 2014-09-18 14:53 | 2014-09-18 17:15 | 141.5833 | 2 | 213.65 | 0.00065343 | 6.1168e-06 | Restore Supply on Device T3617 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | T3617 | On patrolling the line found trees which require cutting . Tree contractor to be advised and arrangements made to cut trees. Power restored and Jason advises the tree contractors will need to trim trees near the HV lines as there are burnt branches along | F4 | MOROA | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106.825 | 103.825 | 207.65 | 0.00063425 | 6.1088e-06 | 2014-09-18 | C | 0.00063425 | 6.109e-06 | 2015 | 2014-09-18 | C | 2 | 0.00063425 | 6.1088e-06
1 | 1884184 | 2014-09-18 19:22 | 2014-09-18 20:51 | 89.2333 | 1 | 89.2333 | 0.00027291 | 3.0584e-06 | Restore Supply on Device T1581 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 815836 | 8:41pm retailer called as customer has stock (chickens onsite that are dying as they have no power) advised Grant from Genesis that f/man was onsite. Replaced x2 10amp fuses at pole 815386 Fuse 7495 due to poss bird strike. No other assets repaired or re | F4 | MOROA | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 89.2333 | 86.2333 | 86.2333 | 0.00026339 | 3.0544e-06 | 2014-09-18 | C | 0.00026339 | 3.054e-06 | 2015 | 2014-09-18 | C | 1 | 0.00026339 | 3.0544e-06
1 | 1884279 | 2014-09-19 00:29 | 2014-09-19 13:22 | 772.8 | 4 | 2645.65 | 0.0080915 | 1.2234e-05 | Restore Supply on Device 4035T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Transformer 4035T and 2980t | Transformer 2980T (50kva 3 phase) struck by lightning and found on fire on the ground also 2Xcrossarms and associated gear requires replacement . Pole 760880 Transformer 4035T (15 kva 3 Phase) Blown by lightning strike also requires replacement . pole 76 | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 661.4125 | 658.4125 | 2633.65 | 0.0080443 | 1.2218e-05 | 2014-09-19 | C | 0.0080443 | 1.2218e-05 | 2015 | 2014-09-19 | C | 4 | 0.0080443 | 1.2218e-05
1 | 1884292 | 2014-09-19 01:59 | 2014-09-19 06:51 | 291.4667 | 1 | 291.4667 | 0.00089143 | 3.0584e-06 | Restore Supply on Device 3108T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE |  | Replaced 2 X HV Fuses | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 291.4667 | 288.4667 | 288.4667 | 0.0008811 | 3.0544e-06 | 2014-09-19 | C | 0.0008811 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.0008811 | 3.0544e-06
1 | 1908546 | 2014-09-19 06:04 | 2014-09-19 11:25 | 321.1333 | 1 | 321.1333 | 0.00098216 | 3.0584e-06 | Restore Supply on Device 4030T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC 4030 | REPLACED 3X DDO FUSES AT TX 4030 CAUSED BY LIGHTNING SET OF 3 FUSES NOT THE HOLDERS SURROUNDING ASSET ALL GOOD. Email sent to Jo to QA as has SAIDI attached. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 321.1333 | 318.1333 | 318.1333 | 0.00097171 | 3.0544e-06 | 2014-09-19 | C | 0.00097171 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00097171 | 3.0544e-06
1 | 1908563 | 2014-09-19 06:50 | 2014-09-19 11:03 | 252.95 | 1 | 252.95 | 0.00077363 | 3.0584e-06 | Restore Supply on Device TC3-139 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3-139 | F/man requesting another 1R as heading to island & believes there could be trees in the line. Replaced 2x 3a HV DDO fuse links due to weather. Nothing else repaired or replaced. Adjacent assets all good. Email sent to Jo to QA, as this job has SAIDI comp | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 252.95 | 249.95 | 249.95 | 0.00076345 | 3.0544e-06 | 2014-09-19 | C | 0.00076345 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00076345 | 3.0544e-06
1 | 1908580 | 2014-09-19 07:06 | 2014-09-19 08:26 | 79.75 | 2 | 111.3167 | 0.00034045 | 6.1168e-06 | Restore Supply on Device 677 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 677 | Lightening blew 2 HV fuses at tx. Replaced 2x 20amp ddo fuses hv o/h. Pole # unknown tx up this pole is 677. Full power restored. Nothing else repaired or replaced. Adjacent assets - as far as could see looked ok. Email sent to JO as 2 x HV fuses have SA | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 55.6583 | 52.6583 | 105.3167 | 0.00032168 | 6.1088e-06 | 2014-09-19 | C | 0.00032168 | 6.109e-06 | 2015 | 2014-09-19 | C | 2 | 0.00032168 | 6.1088e-06
1 | 1908594 | 2014-09-19 07:09 | 2014-09-19 09:37 | 147.8333 | 2 | 280.35 | 0.00085743 | 6.1168e-06 | Restore Supply on Device TD3-034 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD3-034 | replaced 2 x high tension 3 amp fuse. cause: lighting. Transformer: TD3-034. hv/oh. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. Email sent to JO as has SAIDI component. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 140.175 | 137.175 | 274.35 | 0.00083798 | 6.1088e-06 | 2014-09-19 | C | 0.00083798 | 6.109e-06 | 2015 | 2014-09-19 | C | 2 | 0.00083798 | 6.1088e-06
1 | 1908598 | 2014-09-19 07:10 | 2014-09-19 12:57 | 347.2 | 1 | 347.2 | 0.0010619 | 3.0584e-06 | Restore Supply on Device 3799T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 764415 | Replaced 2amp ddo fuse at tx 3799 hv o/h. Pole # 764415. Cause : lightning. Full power restored. Nothing else repaired or replaced. Adjacent assets - all good. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 347.2 | 344.2 | 344.2 | 0.0010513 | 3.0544e-06 | 2014-09-19 | C | 0.0010513 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.0010513 | 3.0544e-06
1 | 1908709 | 2014-09-19 07:43 | 2014-09-19 11:32 | 228.5333 | 1 | 228.5333 | 0.00069895 | 3.0584e-06 | Restore Supply on Device 4192T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4192T | REPLACED 2X HV 3AMP AT TX 4192T HV OH CAUSED BY LIGHTENING SURROUNDING ASSET UP TO POWERCO STANDARD. Email sent to Jo to QA, as this job has SAIDI component. | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 228.5333 | 225.5333 | 225.5333 | 0.00068887 | 3.0544e-06 | 2014-09-19 | C | 0.00068887 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00068887 | 3.0544e-06
1 | 1908833 | 2014-09-19 09:15 | 2014-09-19 13:14 | 239.2833 | 1 | 239.2833 | 0.00073183 | 3.0584e-06 | Restore Supply on Device 4236T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708131 | Replaced 2x 2a HV fuse links due to lightning. Nothing else repaired or replaced. Adjacent assets all good. Email sent to Jo to QA, as this job has SAIDI component. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 239.2833 | 236.2833 | 236.2833 | 0.00072171 | 3.0544e-06 | 2014-09-19 | C | 0.00072171 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00072171 | 3.0544e-06
1 | 1908844 | 2014-09-19 09:21 | 2014-09-19 15:08 | 346.7333 | 1 | 346.7333 | 0.0010605 | 3.0584e-06 | Restore Supply on Device 3250T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Tx 3250T pole 708287. | Tx 3250T blown up. Isolated on tag a3392 at pole 708287. 1 Cust affected & has been notified. Tx 30kVa. Cause: lightning. Adjacent assets - appear ok. Tx to be replaced 20/09 - due to location unable to replace tx today : Follow up job in OMS 1911957. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 346.7333 | 343.7333 | 343.7333 | 0.0010499 | 3.0544e-06 | 2014-09-19 | C | 0.0010499 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.0010499 | 3.0544e-06
1 | 1584474 | 2014-09-19 09:36 | 2014-09-19 15:20 | 344.0667 | 33 | 11354.2 | 0.034726 | 0.00010093 | NAPA ID:02109 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/108 | Install Kimbolton regulators 10214/2. Wiring up Regulator Site. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 344.0667 | 341.0667 | 11255.2 | 0.034378 | 0.0001008 | 2014-09-19 | B | 0.017189 | 5.0398e-05 | 2015 | 2014-09-19 | B | 33 | 0.034378 | 0.0001008
1 | 1908999 | 2014-09-19 11:01 | 2014-09-19 13:45 | 164.3833 | 1 | 164.3833 | 0.00050275 | 3.0584e-06 | Restore Supply on Device TC180 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC180 | Replaced 2x 3a HV fuse links due lightning. Nothing else repaired or replaced. Adjacent assets all good. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 164.3833 | 161.3833 | 161.3833 | 0.00049293 | 3.0544e-06 | 2014-09-19 | C | 0.00049293 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00049293 | 3.0544e-06
1 | 1909008 | 2014-09-19 11:15 | 2014-09-19 15:01 | 225.5 | 1 | 225.5 | 0.00068967 | 3.0584e-06 | Restore Supply on Device 3587T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 759795 | Replaced 2x 3amp ddo fuse links at tx 3587T hv o/h. pole # 759795. Cause lightning. Full power restored. Nothing else repaired or replaced. Adjacent assets - all working but wouldn't say they were up to current Powerco standards. Asked f/man if he was tak | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 225.5 | 222.5 | 222.5 | 0.00067961 | 3.0544e-06 | 2014-09-19 | C | 0.00067961 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00067961 | 3.0544e-06
1 | 1909107 | 2014-09-19 13:01 | 2014-09-19 14:38 | 96.7833 | 1 | 96.7833 | 0.000296 | 3.0584e-06 | Restore Supply on Device TD3-035 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 317529 | Replaced 2x 2amp ddo fuses due to lightning td3035 hv oh on pole 317529 surrounding asset all good. Email sent to Jo to QA, as this job has SAIDI component. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 96.7833 | 93.7833 | 93.7833 | 0.00028645 | 3.0544e-06 | 2014-09-19 | C | 0.00028645 | 3.054e-06 | 2015 | 2014-09-19 | C | 1 | 0.00028645 | 3.0544e-06
1 | 1909121 | 2014-09-19 13:27 | 2014-09-19 17:39 | 252 | 588 | 65383.25 | 0.19997 | 0.0017984 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | Fuses 4962 | Explosion/flashes seen at 27 Ocean View parade. Control advised. Replaced 3 X DDOs at Fuses 4962. | F2 | MOTUROA 7 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 111.196 | 108.196 | 63619.25 | 0.19432 | 0.001796 | 2014-09-19 | C | 0.19432 | 0.001796 | 2015 | 2014-09-19 | C | 588 | 0.19432 | 0.001796
1 | 1912832 | 2014-09-19 15:44 | 2014-09-19 17:32 | 107.85 | 27 | 587.1 | 0.0017956 | 8.2577e-05 | Restore Supply on Device T7/466 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P15672 | Check if related to OMS 1912017. Replaced 2 of 3 10amp HT fuse at pole P15672. Cause unknown. Adjacent assets checked and no other repairs or replacements. Signed off to help control. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 21.7444 | 18.7444 | 506.1 | 0.0015458 | 8.2469e-05 | 2014-09-19 | C | 0.0015458 | 8.2469e-05 | 2015 | 2014-09-19 | C | 27 | 0.0015458 | 8.2469e-05
1 | 1912658 | 2014-09-19 16:06 | 2014-09-19 18:42 | 156.05 | 162 | 19788.0333 | 0.06052 | 0.00049546 | Restore Supply on Device RC4 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | O2882 | Tree across line at pole O2882. Isolation at ABS 2572 ABS 9724/1 Links 9724/4 No Back Feeds available. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 122.1484 | 119.1484 | 19302.0333 | 0.058957 | 0.00049482 | 2014-09-19 | C | 0.058957 | 0.00049482 | 2015 | 2014-09-19 | C | 162 | 0.058957 | 0.00049482
1 | 1913392 | 2014-09-19 17:13 | 2014-09-19 19:30 | 137.0833 | 123 | 14714.4 | 0.045003 | 0.00037619 | Restore Supply on Device C936 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 838398 | Tripping on CBC936 on O/C A-B phase. Feeder patrolled and fault found at Pole 838398. Centre insulator had come dislodged and was resting on side of crossarm. Required new nut to retighten back in place. Relivened OK. | F5 | ANNEDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 119.6293 | 116.6293 | 14345.4 | 0.043817 | 0.00037569 | 2014-09-19 | C | 0.043817 | 0.00037569 | 2015 | 2014-09-19 | C | 123 | 0.043817 | 0.00037569
1 | 1914475 | 2014-09-20 07:03 | 2014-09-20 11:02 | 238.7667 | 239 | 37350.05 | 0.11423 | 0.00073096 | Restore Supply on Device T21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735011 | Kaponga CB T21 tripped, auto reclosed. E/F O/C L/O. Line patrolled, fault located and power restored. Materials Used: 11kV Pin Insulator and Ali Binder. Nick Webby and Jade Williams attended. | F4 | MANAIA RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 156.2764 | 153.2764 | 36633.05 | 0.11189 | 0.00073001 | 2014-09-20 | C | 0.11189 | 0.00073001 | 2015 | 2014-09-20 | C | 239 | 0.11189 | 0.00073001
1 | 1914993 | 2014-09-20 07:30 | 2014-09-20 10:00 | 149.2 | 1 | 149.2 | 0.00045632 | 3.0584e-06 | Restore Supply on Device 2692T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - SUSPECT LIGHTNING STRIKE | 759826 | 2x ht links down due to lightning 2x 3amp. Email sent to Jo to QA, as this job has SAIDI component. | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 149.2 | 146.2 | 146.2 | 0.00044656 | 3.0544e-06 | 2014-09-20 | C | 0.00044656 | 3.054e-06 | 2015 | 2014-09-20 | C | 1 | 0.00044656 | 3.0544e-06
1 | 1584484 | 2014-09-20 07:54 | 2014-09-20 09:20 | 86.25 | 10 | 235.6667 | 0.00072077 | 3.0584e-05 | NAPA ID:02445 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RMU9827 | Install and liven new RMU 9827 Tauranga Sub. TGA18. Cutaway ripple plant from TGA12 circuit cable. Connect ripple plant to new RMU 9827 on TGA 18 job not completed siwtching returned to normal | F2 | RIPPLE PLANT | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 23.5667 | 20.5667 | 205.6667 | 0.00062819 | 3.0544e-05 | 2014-09-20 | B | 0.0003141 | 1.5272e-05 | 2015 | 2014-09-20 | B | 10 | 0.00062819 | 3.0544e-05
1 | 1915011 | 2014-09-20 07:55 | 2014-09-20 12:38 | 283.6833 | 3 | 843.3833 | 0.0025794 | 9.1753e-06 | Restore Supply on Device 6725 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4128T | Replaced HT fuse on TX 4128T replaced 2x 3amp fuses - TX 3707T replaced 2x3amp fuses 4818T replaced 3x 3amp fuses - unable to unlock this TX. | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 281.1278 | 278.1278 | 834.3833 | 0.0025486 | 9.1633e-06 | 2014-09-20 | C | 0.0025486 | 9.163e-06 | 2015 | 2014-09-20 | C | 3 | 0.0025486 | 9.1633e-06
1 | 1915662 | 2014-09-20 08:44 | 2014-09-20 17:41 | 537.2667 | 1 | 537.2667 | 0.0016432 | 3.0584e-06 | Restore Supply on Device 3685T | 6600 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 762237 | Replaced 2 x 2amp 11kv fuses at tx 3685T pole 762237. Cause lightning. Adjacent assets checked and no other repairs or replacements. Email sent to Jo to QA, as this job has SAIDI component. | F3 | TARATA | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 537.2667 | 534.2667 | 534.2667 | 0.0016319 | 3.0544e-06 | 2014-09-20 | C | 0.0016319 | 3.054e-06 | 2015 | 2014-09-20 | C | 1 | 0.0016319 | 3.0544e-06
1 | 1916263 | 2014-09-20 10:24 | 2014-09-20 15:20 | 296.2167 | 1 | 296.2167 | 0.00090596 | 3.0584e-06 | Restore Supply on Device TC3132 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | K12782 | 2.41pm phoned hub for update on this job 2x 3amp ddo fuses No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. Email sent to Jo to QA, as this job has SAIDI component. | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 296.2167 | 293.2167 | 293.2167 | 0.00089561 | 3.0544e-06 | 2014-09-20 | C | 0.00089561 | 3.054e-06 | 2015 | 2014-09-20 | C | 1 | 0.00089561 | 3.0544e-06
1 | 1916299 | 2014-09-20 10:54 | 2014-09-20 14:53 | 238.5 | 39 | 2440.7833 | 0.0074649 | 0.00011928 | Restore Supply on Device TC4245 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4245 | James advised needs help to replace HV jumper into top of ddo. HV Jumper Replaced | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 62.5842 | 59.5842 | 2323.7833 | 0.0070978 | 0.00011912 | 2014-09-20 | C | 0.0070978 | 0.00011912 | 2015 | 2014-09-20 | C | 39 | 0.0070978 | 0.00011912
1 | 1916430 | 2014-09-20 11:04 | 2014-09-20 21:51 | 646.3333 | 112 | 42067.2667 | 0.12866 | 0.00034254 | Restore Supply on Device 513 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 780222 | RS 513 A/R, L/O, E/F, O/C B Phase. Line brought down by tree branch inside notice zone. NDR 41472. Used 25mtrs of Squirrel conductor & 3 sleeves. Jeremy Hill attended. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 375.6006 | 372.6006 | 41731.2667 | 0.12746 | 0.0003421 | 2014-09-20 | C | 0.12746 | 0.00034209 | 2015 | 2014-09-20 | C | 112 | 0.12746 | 0.0003421
1 | 1916548 | 2014-09-20 11:22 | 2014-09-20 16:21 | 299 | 97 | 6984 | 0.02136 | 0.00029667 | Restore Supply on Device 2007T | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 734112 | at 13:55 Cloton Rd Sub, CB S51 West Feeder. Trees found on lines that had also damaged transformer 2007T at Pole 734112. Isolated Lines at ABS 5703 & 5576. Backfeed supplied from Cloton Rd S31 via ABS 5699. Permit Issued & Repairs carried out. All Power R | F4 | CLOTON RD WEST | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 6693 | 0.020443 | 0.00029628 | 2014-09-20 | C | 0.020443 | 0.00029628 | 2015 | 2014-09-20 | C | 97 | 0.020443 | 0.00029628
1 | 1917048 | 2014-09-20 11:47 | 2014-09-20 14:39 | 172.1167 | 444 | 38996.4333 | 0.11927 | 0.0013579 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36604 | CB 11 Trip, E/F Closed last ABS at 1439. Job stuck in Verified talked to IT and OMS People. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.8298 | 84.8298 | 37664.4333 | 0.11504 | 0.0013562 | 2014-09-20 | C | 0.11504 | 0.0013562 | 2015 | 2014-09-20 | C | 444 | 0.11504 | 0.0013562
1 | 1918114 | 2014-09-20 12:05 | 2014-09-20 13:09 | 64 | 1008 | 49853 | 0.15247 | 0.0030829 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Hatricks Wharf CB11 | 2.14pm Peter Control advised they line patrolled and no fault found. Job will not close | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 49.4573 | 46.4573 | 46829 | 0.14304 | 0.0030789 | 2014-09-20 | C | 0.14304 | 0.0030789 | 2015 | 2014-09-20 | C | 1008 | 0.14304 | 0.0030789
1 | 1921571 | 2014-09-20 13:48 | 2014-09-20 16:27 | 159 | 1215 | 148615 | 0.45453 | 0.003716 | Restore Supply on Device CB14 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 383 | Switch Gear 383 Blown Up | F3 | RESIDENTIAL | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 122.3169 | 119.3169 | 144970 | 0.4428 | 0.0037111 | 2014-09-20 | C | 0.4428 | 0.0037111 | 2015 | 2014-09-20 | C | 1215 | 0.4428 | 0.0037111
1 | 1924246 | 2014-09-20 15:42 | 2014-09-20 18:28 | 166.2333 | 2 | 284.9667 | 0.00087155 | 6.1168e-06 | Restore Supply on Device TC1697 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tc1697 | 2x 3A HV Fuses Replaced at TC1697. Perry Hicks Attended. Email sent to Jo to check, as may have SAIDI component. | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 142.4833 | 139.4833 | 278.9667 | 0.00085208 | 6.1088e-06 | 2014-09-20 | C | 0.00085208 | 6.109e-06 | 2015 | 2014-09-20 | C | 2 | 0.00085208 | 6.1088e-06
1 | 1924512 | 2014-09-20 16:05 | 2014-09-23 08:04 | 3838.9167 | 2 | 7434.75 | 0.022739 | 6.1168e-06 | Restore Supply on Device TC4071 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4071 | Fuses TC4071 opened and tagged. Transformer TC4071 replaced and 3 x 2A fuses. Perry Hicks attended. | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 3717.375 | 3714.375 | 7428.75 | 0.022691 | 6.1088e-06 | 2014-09-20 | C | 0.022691 | 6.109e-06 | 2015 | 2014-09-20 | C | 2 | 0.022691 | 6.1088e-06
1 | 1925486 | 2014-09-20 16:40 | 2014-09-20 20:11 | 210.7333 | 595 | 35427.6667 | 0.10835 | 0.0018198 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 754748 | 20/9 6.40 pm Neil Woodhead leaving site now to Otaraoa Tripping on CB6777/5 on O/C A-B Phase. Fault caused by car accident with isolation from ABS315. 2 Broken conductors repaired. 2 HT fuses at 8186 replaced which were damaged. NDR 43766. Paul Sullivan | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 59.5423 | 56.5423 | 33642.6667 | 0.10276 | 0.0018174 | 2014-09-20 | C | 0.10276 | 0.0018174 | 2015 | 2014-09-20 | C | 595 | 0.10276 | 0.0018174
1 | 1927215 | 2014-09-20 19:02 | 2014-09-21 00:59 | 357.5167 | 11 | 3880.6833 | 0.011869 | 3.3643e-05 | Restore Supply on Device 2930 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 769172 | Heard a loud bang then power went out. Notified HUB. Replaced 2 x 11kV 15 amp fuses. Pole # 769172. Cause: unknown. | F3 | WESTMERE PEAT ST | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 352.7894 | 349.7894 | 3847.6833 | 0.011752 | 3.3599e-05 | 2014-09-20 | C | 0.011752 | 3.3599e-05 | 2015 | 2014-09-20 | C | 11 | 0.011752 | 3.3599e-05
1 | 1927425 | 2014-09-20 20:29 | 2014-09-20 22:40 | 130.7667 | 2 | 187.0333 | 0.00057203 | 6.1168e-06 | Restore Supply on Device TD3-272 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | SD3-159 | Replaced 2x HV Fuses. Hilton Gardiner Attended. Email sent to Jo to QA, as this job has SAIDI component. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 93.5167 | 90.5167 | 181.0333 | 0.00055295 | 6.1088e-06 | 2014-09-20 | C | 0.00055295 | 6.109e-06 | 2015 | 2014-09-20 | C | 2 | 0.00055295 | 6.1088e-06
1 | 1928545 | 2014-09-20 22:06 | 2014-09-21 02:59 | 292.6167 | 736 | 83210.15 | 0.25449 | 0.002251 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole F0189 | at 22:06, Browne St Sub, CB 3 Smith St Feeder Tripped, Ph A & B O/C, Auto Reclosed. at 22:40 Browner St Sub, CB 3 Smith St Feeder Tripped, Ph A & B O/C, L/O. Faultmen Dispatched & Investigation Began. Sectionalised Feeder. Found Line Down at Pole F0189 | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 113.0573 | 110.0573 | 81002.15 | 0.24741 | 0.0022481 | 2014-09-20 | C | 0.24741 | 0.0022481 | 2015 | 2014-09-20 | C | 736 | 0.24741 | 0.0022481
1 | 1929792 | 2014-09-20 23:01 | 2014-09-21 01:57 | 175.8167 | 279 | 29604.0833 | 0.090542 | 0.0008533 | Restore Supply on Device RC01 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole F12700 | at 23:00 Tower Rd Sub, CB 1 Gordan Feeder, Recloser RC01, Tripped, E/F, L/O. Faultmen Dispatched & Investigation began. Feeder Sectionalised. Found Broken Insulator at Pole F12700. Isolated Lines at ABS IC1066. Permit Issued & Repairs Carried Out. All Pow | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 106.1078 | 103.1078 | 28767.0833 | 0.087867 | 0.00085218 | 2014-09-20 | C | 0.087867 | 0.00085218 | 2015 | 2014-09-20 | C | 279 | 0.087867 | 0.00085218
1 | 1931449 | 2014-09-21 02:15 | 2014-09-21 06:07 | 232.4333 | 10 | 840.45 | 0.0025705 | 3.0584e-05 | Restore Supply on Device TE7-149 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 217914 | at 05:17 Pongakawa Sub, CB 1 Tainui Feeder. Found Line Down at Pole 217914. Isolated Lines at Fuses FP1462. Permit Issued & repairs carried out. All Power restored on completion. Dennis Ngatai Attended. Less than 1 span of conductor not all phases, 4x HV | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 84.045 | 81.045 | 810.45 | 0.0024755 | 3.0544e-05 | 2014-09-21 | C | 0.0024755 | 3.0544e-05 | 2015 | 2014-09-21 | C | 10 | 0.0024755 | 3.0544e-05
1 | 1861746 | 2014-09-21 09:42 | 2014-09-21 14:36 | 294 | 27 | 7938 | 0.024278 | 8.2577e-05 | NAPA ID:02393 TP_STRATFORD GXP > DOUGLAS SUB > TOKO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5629 | Install cross arms replace DNO 140823 (Cracked Insulators) at 11Kv Abs 5629. Works location: East Rd Toko. WO 10154699. This job was done on Sunday 21/09/14 due to school having Polling Booth at it. | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 294 | 291 | 7857 | 0.023999 | 8.2469e-05 | 2014-09-21 | B | 0.011999 | 4.1235e-05 | 2015 | 2014-09-21 | B | 27 | 0.023999 | 8.2469e-05
1 | 1931714 | 2014-09-21 10:38 | 2014-09-21 12:48 | 130.3333 | 1 | 130.3333 | 0.00039861 | 3.0584e-06 | Restore Supply on Device X2176 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | Fuses 563 | Check for safety, iron on roof of shed blew off in wind and touched 11kv lines on the road - now cust has no power. Faultman found 2 fuses blown at Fuses 563, faultman replaced 2x 6Amp HV fuses. Email sent to Jo, as job has SAIDI component. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 130.3333 | 127.3333 | 127.3333 | 0.00038893 | 3.0544e-06 | 2014-09-21 | C | 0.00038893 | 3.054e-06 | 2015 | 2014-09-21 | C | 1 | 0.00038893 | 3.0544e-06
1 | 1931762 | 2014-09-21 15:00 | 2014-09-21 15:37 | 37.1167 | 11 | 408.2833 | 0.0012487 | 3.3643e-05 | Restore Supply on Device TC3186 | 11000 | UNPLANNED | Distribution Equip. | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | tc3186 | Fuse burning up in tx. Will need to isolate the tx to replace the fuse. Don Masters will help with doing this. 1X LV HRC Fuse Holder and Fuse Replaced. 1 Fuse Holder Tightened. | F3 | CAMPBELL ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 37.1167 | 34.1167 | 375.2833 | 0.0011463 | 3.3599e-05 | 2014-09-21 | C | 0.0011463 | 3.3599e-05 | 2015 | 2014-09-21 | C | 11 | 0.0011463 | 3.3599e-05
1 | 1931896 | 2014-09-21 15:30 | 2014-09-21 16:37 | 67.2167 | 1 | 67.2167 | 0.00020558 | 3.0584e-06 | Restore Supply on Device TC4142 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4142 | 2 X 2A DDO Fuses. Lightning. Email sent to Jo, as job has SAIDI component. | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 67.2167 | 64.2167 | 64.2167 | 0.00019614 | 3.0544e-06 | 2014-09-21 | C | 0.00019614 | 3.054e-06 | 2015 | 2014-09-21 | C | 1 | 0.00019614 | 3.0544e-06
1 | 1932147 | 2014-09-22 05:00 | 2014-09-22 09:47 | 287.0833 | 5 | 720.3333 | 0.0022031 | 1.5292e-05 | Restore Supply on Device TE7-110 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | SE7-035 | Replaced 2 x 10amp fuse and fuse carriers HV at pole 218335 at fuse SE7-035. Cause Opossum. Adjacent assets checked and no other repairs or replacements. Email sent to Jo, as job has SAIDI component. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 144.0667 | 141.0667 | 705.3333 | 0.0021544 | 1.5272e-05 | 2014-09-22 | C | 0.0021544 | 1.5272e-05 | 2015 | 2014-09-22 | C | 5 | 0.0021544 | 1.5272e-05
1 | 1932656 | 2014-09-22 06:28 | 2014-09-22 14:04 | 455.7333 | 261 | 118946.4 | 0.36379 | 0.00079825 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 6709006 | CB 7131 Stratmore sub tripped to L/O. Broken Binder and insulator at pole 6709006. All work complete. No Back feed available, is by ABS 5229. NOTE: Lines down was not affiliated to this fault, it was a later event, however this job was stuck in verified. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 455.7333 | 452.7333 | 118163.4 | 0.36092 | 0.0007972 | 2014-09-22 | C | 0.36092 | 0.00079721 | 2015 | 2014-09-22 | C | 261 | 0.36092 | 0.0007972
1 | 1934032 | 2014-09-22 07:39 | 2014-09-22 18:48 | 669.25 | 378 | 252583.6833 | 0.77251 | 0.0011561 | Restore Supply on Device 4812 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 758592 | 11kV Recloser 4812 tripped E/F O/C L/O, Due to broken binder at pole 758592, all work complete on OMS 1965534. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 668.2108 | 665.2108 | 251449.6833 | 0.76803 | 0.0011546 | 2014-09-22 | C | 0.76803 | 0.0011546 | 2015 | 2014-09-22 | C | 378 | 0.76803 | 0.0011546
1 | 1934415 | 2014-09-22 07:42 | 2014-09-22 11:11 | 209.4167 | 148 | 26049.6833 | 0.079671 | 0.00045265 | Restore Supply on Device CB3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27764 | CB 3 tripped no flags, line was been sectionalised when received call from customer of line down, line was isolated at ABS V55 to make repairs. 10 meters of Goffer Aluminium conductor was used & 3 x sleeves. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 176.0114 | 173.0114 | 25605.6833 | 0.078211 | 0.00045205 | 2014-09-22 | C | 0.078211 | 0.00045205 | 2015 | 2014-09-22 | C | 148 | 0.078211 | 0.00045205
1 | 1935470 | 2014-09-22 08:03 | 2014-09-22 14:26 | 382.9333 | 1 | 382.9333 | 0.0011712 | 3.0584e-06 | Restore Supply on Device Z147 | 22000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 2756 | Replaced 2 x 6A HV fuse elements. Carried out line patrol and all other assets okay. Nothing else replaced. | F4 | LEEDSTOWN 22KV | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 382.9333 | 379.9333 | 379.9333 | 0.0011605 | 3.0544e-06 | 2014-09-22 | C | 0.0011605 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.0011605 | 3.0544e-06
1 | 1935510 | 2014-09-22 08:22 | 2014-09-22 12:48 | 265.8167 | 234 | 21227.65 | 0.064923 | 0.00071567 | Restore Supply on Device C927 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 799142 | CB C927 tripped on A & B phase O/C, line was sectionalised and patrolled and branch was found on the line at pole 799142, line was isolated at Fuses 7308 and branch was removed with hot line stick, section of feeder was back fed by opening Recloser C630/2 | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 90.7165 | 87.7165 | 20525.65 | 0.062694 | 0.00071474 | 2014-09-22 | C | 0.062694 | 0.00071473 | 2015 | 2014-09-22 | C | 234 | 0.062694 | 0.00071474
1 | 1935778 | 2014-09-22 08:28 | 2014-09-22 12:35 | 246.65 | 27 | 842.9333 | 0.002578 | 8.2577e-05 | Restore Supply on Device X1625 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 803873 | NDR 41796. Replaced 2 x 10A HV fuses. Untangled lines from trees. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 31.2198 | 28.2198 | 761.9333 | 0.0023273 | 8.2469e-05 | 2014-09-22 | C | 0.0023273 | 8.2469e-05 | 2015 | 2014-09-22 | C | 27 | 0.0023273 | 8.2469e-05
1 | 1936592 | 2014-09-22 08:42 | 2014-09-22 11:25 | 163.5167 | 1 | 163.5167 | 0.0005001 | 3.0584e-06 | Restore Supply on Device TD6-049 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SD5-006 | Replaced 2 x 10amp DDO HV fuse at fuses SD5-006. Cause weather. Adjacent assets checked and no other repairs or replacements. Control are busy so have signed this off for Hilton Email sent to Jo, as job has SAIDI component. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 163.5167 | 160.5167 | 160.5167 | 0.00049029 | 3.0544e-06 | 2014-09-22 | C | 0.00049029 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.00049029 | 3.0544e-06
1 | 1936634 | 2014-09-22 08:55 | 2014-09-22 16:19 | 443.75 | 1 | 443.75 | 0.0013572 | 3.0584e-06 | Restore Supply on Device L1412 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728006, L1412 | L1412 pole 728006. Replaced Faulty 30kVa Tx Pole # 728006 Tx # L1412 cause : Internal fault in Tx. Full power restored. Nothing Adjacent assets - all ok. Email sent to Jo, as job has SAIDI component. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 443.75 | 440.75 | 440.75 | 0.0013462 | 3.0544e-06 | 2014-09-22 | C | 0.0013462 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.0013462 | 3.0544e-06
1 | 1936644 | 2014-09-22 08:59 | 2014-09-22 10:01 | 62 | 156 | 9672 | 0.029581 | 0.00047711 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 217272 | Sectionaliser 9270 tripped L/O. Feeder sectionalised & tree found through lines at pole 217272. Isolations at ABS SE2 013. NDR # 48253 | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 9204 | 0.028113 | 0.00047649 | 2014-09-22 | C | 0.028113 | 0.00047649 | 2015 | 2014-09-22 | C | 156 | 0.028113 | 0.00047649
1 | 1583778 | 2014-09-22 09:10 | 2014-09-22 11:50 | 160 | 4 | 640 | 0.0019574 | 1.2234e-05 | NAPA ID:02118 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/18 | Replace TX and TX arms. Work Location: Mt Biggs Road. Work Order 10152157 | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 628 | 0.0019182 | 1.2218e-05 | 2014-09-22 | B | 0.00095909 | 6.109e-06 | 2015 | 2014-09-22 | B | 4 | 0.0019182 | 1.2218e-05
1 | 1933617 | 2014-09-22 09:20 | 2014-09-22 12:37 | 196.8333 | 14 | 2755.6667 | 0.008428 | 4.2818e-05 | Restore Supply on Device 2244T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 730193 | Pole #730193. TX 2244T. replaced pole, cross arm, 3x insulators, 3 fuse sets, 15kVA transformer. All work complete. traffic management required. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 196.8333 | 193.8333 | 2713.6667 | 0.0082887 | 4.2762e-05 | 2014-09-22 | C | 0.0082887 | 4.2762e-05 | 2015 | 2014-09-22 | C | 14 | 0.0082887 | 4.2762e-05
1 | 1936899 | 2014-09-22 09:39 | 2014-09-22 18:55 | 555.4833 | 6 | 1414.4667 | 0.004326 | 1.8351e-05 | Restore Supply on Device 3028T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fused ABS 5291 | Check to see if 1938330, 1943979,1954608 are related before signing off. Blown 11kV Fuse at Fused ABS 5291 (15Amp). Links to the larger outage job 1943979. Have retained the outage step for this affected transformer as they were without power prior to | F3 | TARATA | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.7444 | 232.7444 | 1396.4667 | 0.0042654 | 1.8327e-05 | 2014-09-22 | C | 0.0042654 | 1.8327e-05 | 2015 | 2014-09-22 | C | 6 | 0.0042654 | 1.8327e-05
1 | 1937590 | 2014-09-22 10:42 | 2014-09-22 17:42 | 419.9667 | 112 | 41233.4333 | 0.12611 | 0.00034254 | Restore Supply on Device 513 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 780214 | Recloser513 tripped on A & bphase O/C flags, line was sectionalised and patrolled and faultman found a tree in the lines, line was isolated at ABS's 199 & 545 to cut the tree away. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 368.1557 | 365.1557 | 40897.4333 | 0.12492 | 0.0003421 | 2014-09-22 | C | 0.12492 | 0.00034209 | 2015 | 2014-09-22 | C | 112 | 0.12492 | 0.0003421
1 | 1938633 | 2014-09-22 11:04 | 2014-09-22 13:51 | 166.6667 | 306 | 34199.6833 | 0.1046 | 0.00093588 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | PUT CB 4 | CB 4 tripped to L/O - F/man to contact control ASAP. Contractor offsite at 14.30 was not completed off. No fault found. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 111.7637 | 108.7637 | 33281.6833 | 0.10166 | 0.00093465 | 2014-09-22 | C | 0.10166 | 0.00093465 | 2015 | 2014-09-22 | C | 306 | 0.10166 | 0.00093465
1 | 1938980 | 2014-09-22 11:12 | 2014-09-22 15:57 | 284.95 | 1 | 284.95 | 0.0008715 | 3.0584e-06 | Restore Supply on Device T2515 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Fuse 7717 | Replaced 2x blown 10amp hv links o/h pole # unknown but fuse on pole is 7717 Cause: wind. Full power restored. Nothing else repaired or replaced adjacent assets - all fine. Email sent to Jo, as job has SAIDI component. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 284.95 | 281.95 | 281.95 | 0.00086119 | 3.0544e-06 | 2014-09-22 | C | 0.0008612 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.00086119 | 3.0544e-06
1 | 1938984 | 2014-09-22 11:12 | 2014-09-22 15:04 | 231.8167 | 25 | 4159.15 | 0.01272 | 7.6461e-05 | Restore Supply on Device FP1220 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | K12670 | HV lines down. Replace more than 3m of HV OH conductor. Pole K12670. Repaired with 4 full tension squirrel sleeves, 2 of 3 20amp HT DDO fuses. Adjacent assets checked and no other repairs or replacements. Signed off for control as they were too busy | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 166.366 | 163.366 | 4084.15 | 0.012475 | 7.6361e-05 | 2014-09-22 | C | 0.012475 | 7.6361e-05 | 2015 | 2014-09-22 | C | 25 | 0.012475 | 7.6361e-05
1 | 1938994 | 2014-09-22 11:14 | 2014-09-22 17:06 | 352.1667 | 157 | 24483.1667 | 0.07488 | 0.00048017 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 229060 | Recloser 9556 tripped E/F, L/O. Feeder sectionalised & tree found through lines ( 3 x phases ) at pole 229060. Isolations at ABS SF7 027 ( no back feeds ) Lines repaired all service restored, Hilton Gardner attended. Materials 60 meters conductor, 12 x H | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 155.9437 | 152.9437 | 24012.1667 | 0.073343 | 0.00047954 | 2014-09-22 | C | 0.073343 | 0.00047955 | 2015 | 2014-09-22 | C | 157 | 0.073343 | 0.00047954
1 | 1970909 | 2014-09-22 11:15 | 2014-09-22 13:52 | 157 | 295 | 28873 | 0.088306 | 0.00090223 | Restore Supply on Device C917 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 363156 | CBC917 tripped and L/O on E/f. Line patrolled and branch on line at pole 363156. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 97.8746 | 94.8746 | 27988 | 0.085487 | 0.00090105 | 2014-09-22 | C | 0.085487 | 0.00090105 | 2015 | 2014-09-22 | C | 295 | 0.085487 | 0.00090105
1 | 1939323 | 2014-09-22 11:16 | 2014-09-22 15:10 | 234.3667 | 295 | 61799.9 | 0.18901 | 0.00090223 | Restore Supply on Device C917 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 363156 | CB C917 tripped on E/F flags, line was sectionalised and patrolled and a burnt off branch was found at pole 363156 on the ground. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 209.4912 | 206.4912 | 60914.9 | 0.18606 | 0.00090105 | 2014-09-22 | C | 0.18606 | 0.00090105 | 2015 | 2014-09-22 | C | 295 | 0.18606 | 0.00090105
1 | 1941089 | 2014-09-22 11:27 | 2014-09-22 14:39 | 192.0667 | 953 | 113896.1 | 0.34834 | 0.0029147 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 218600 | Recloser 9513 tripped E/F, A/R, L/O. Feeder sectionalised & found tree through lines ( 3 x Phases ) at pole 218600 during high winds. Isolations at ABS SE7 003 ( no back feeds ) lines repaired, all service restored, Mike strange attended. Materials 40 met | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 119.5132 | 116.5132 | 111037.1 | 0.33915 | 0.0029109 | 2014-09-22 | C | 0.33915 | 0.0029109 | 2015 | 2014-09-22 | C | 953 | 0.33915 | 0.0029109
1 | 1945697 | 2014-09-22 11:30 | 2014-09-22 14:26 | 176 | 1425 | 180314 | 0.55148 | 0.0043583 | Restore Supply on Device IC3114 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 263580 | CB4 tripped A/R, L/O. Feeder sectionalised & branch found across lines at pole 263580. Branch removed all service restored, Stu Simpson attended. No materials. | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 126.5361 | 123.5361 | 176039 | 0.5377 | 0.0043526 | 2014-09-22 | C | 0.5377 | 0.0043526 | 2015 | 2014-09-22 | C | 1425 | 0.5377 | 0.0043526
1 | 1943532 | 2014-09-22 11:48 | 2014-09-22 11:56 | 8.6167 | 430 | 3705.1667 | 0.011332 | 0.0013151 | Restore Supply on Device 3094 | 33000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | CB 3094 | 33kV CB 3094 tripped no flags. Tech on site checked all protection all OK, it is snowing at the substation, suspect tripping due to the weather. | F2 | WAIOURU LS | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 8.6167 | 5.6167 | 2415.1667 | 0.0073769 | 0.0013134 | 2014-09-22 | C | 0.0073769 | 0.0013134 | 2015 | 2014-09-22 | C | 430 | 0.0073769 | 0.0013134
1 | 1945173 | 2014-09-22 12:27 | 2014-09-22 14:21 | 113.4833 | 293 | 31890.2833 | 0.097534 | 0.00089612 | Restore Supply on Device 1011 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 790451 | Branch removed from HV line at pole # 79045 with Hot Line Sticks. NDR # 41797 Full power restored. Adjacent assets - all good. Roger Bland attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 108.8406 | 105.8406 | 31011.2833 | 0.094722 | 0.00089495 | 2014-09-22 | C | 0.094722 | 0.00089495 | 2015 | 2014-09-22 | C | 293 | 0.094722 | 0.00089495
1 | 1945569 | 2014-09-22 12:57 | 2014-09-23 15:42 | 1605.4167 | 9 | 3630.75 | 0.011104 | 2.7526e-05 | Restore Supply on Device TC2405 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2405 | 4:41pm retailer called for an update, advised taila at the hub. 7:30pm Called back through to the hub as customer called to Powerco wanting an update - Gloria advised she will get some one asap. Transformer TC2405 Blown and needs replacing. To be acti | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 403.4167 | 400.4167 | 3603.75 | 0.011007 | 2.749e-05 | 2014-09-22 | C | 0.011007 | 2.749e-05 | 2015 | 2014-09-22 | C | 9 | 0.011007 | 2.749e-05
1 | 1946382 | 2014-09-22 13:18 | 2014-09-22 15:07 | 108.7 | 156 | 14275.2 | 0.04366 | 0.00047711 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | UNKNOWN - NO FAULT FOUND | 9270 | Note trip time 13:18 ( duration time showing 731 min ) Restored 15:05 | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 91.5077 | 88.5077 | 13807.2 | 0.042173 | 0.00047649 | 2014-09-22 | C | 0.042173 | 0.00047649 | 2015 | 2014-09-22 | C | 156 | 0.042173 | 0.00047649
1 | 1947308 | 2014-09-22 13:18 | 2014-09-22 15:43 | 145.0667 | 438 | 58412.8333 | 0.17865 | 0.0013396 | Restore Supply on Device C850 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C850 | 11kV CB C850 tripped L/O, no flags. Fully patrolled and sectionalised, no fault found. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 133.3626 | 130.3626 | 57098.8333 | 0.1744 | 0.0013378 | 2014-09-22 | C | 0.1744 | 0.0013378 | 2015 | 2014-09-22 | C | 438 | 0.1744 | 0.0013378
1 | 1949689 | 2014-09-22 14:15 | 2014-09-22 17:34 | 199 | 261 | 24802.35 | 0.075856 | 0.00079825 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 709010 | NOC opened CB7131. Insulator and binder replaced on pole 709010. 8:16 Jade called to request 2R to organise tree trimming. Checked with Kris, and this is not 2R work. No request made. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 95.0282 | 92.0282 | 24019.35 | 0.073365 | 0.0007972 | 2014-09-22 | C | 0.073365 | 0.00079721 | 2015 | 2014-09-22 | C | 261 | 0.073365 | 0.0007972
1 | 2005424 | 2014-09-22 14:15 | 2014-09-22 15:20 | 65 | 23 | 1495 | 0.0045723 | 7.0344e-05 | Restore Supply on Device 7148 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 832397 | Broken pole at pole 832442. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 65 | 62 | 1426 | 0.0043556 | 7.0252e-05 | 2014-09-22 | C | 0.0043556 | 7.0252e-05 | 2015 | 2014-09-22 | C | 23 | 0.0043556 | 7.0252e-05
1 | 1949346 | 2014-09-22 14:20 | 2014-09-22 19:32 | 311.9667 | 7 | 1533.8167 | 0.0046911 | 2.1409e-05 | Restore Supply on Device T9/417 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB I32 | Advised Tarn to tell F/man to go the Rongomai Sub as feeder fault. reset the chain breaker at sub Closed the Breaker CB I 32 Tripped Email sent to Jo, as job has SAIDI component. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 219.1167 | 216.1167 | 1512.8167 | 0.0046208 | 2.1381e-05 | 2014-09-22 | C | 0.0046208 | 2.1381e-05 | 2015 | 2014-09-22 | C | 7 | 0.0046208 | 2.1381e-05
1 | 1950141 | 2014-09-22 14:33 | 2014-09-22 20:51 | 378.4667 | 548 | 57868.7667 | 0.17699 | 0.001676 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | E0214 | CB 5 tripped to L/O - F/man to contact control ASAP to discuss sectionalising options James 0274 535 298 - tree through HV lines on his ppty adjacent to 55 Rangitanuku Road, Matamata - advising tree through line, lines down and broken x arm 1 X HV Cross | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 105.5999 | 102.5999 | 56224.7667 | 0.17173 | 0.0016738 | 2014-09-22 | C | 0.17173 | 0.0016738 | 2015 | 2014-09-22 | C | 548 | 0.17173 | 0.0016738
1 | 1952015 | 2014-09-22 14:44 | 2014-09-22 19:36 | 291.75 | 30 | 3673.4667 | 0.011235 | 9.1753e-05 | Restore Supply on Device X1759 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 784265 | Line patrolled and branch located on the line at pole #784265. Isolated & removed branch. Wooden pole was straightened as it had been twisted due to weight of branch. NDR #784265. Full power restored. Nothing else repaired or replaced. Adjacent asset | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 122.4489 | 119.4489 | 3583.4667 | 0.010945 | 9.1633e-05 | 2014-09-22 | C | 0.010945 | 9.1633e-05 | 2015 | 2014-09-22 | C | 30 | 0.010945 | 9.1633e-05
1 | 1952895 | 2014-09-22 15:14 | 2014-09-23 11:15 | 1200.7667 | 49 | 4803.0667 | 0.01469 | 0.00014986 | Restore Supply on Device 7775 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 855148 | Left off overnight due to trees through lines. Removed trees and rehung conductor @ pole 855148. Jason Hall, Lee Wilton and Brian Butler attended. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98.0218 | 95.0218 | 4656.0667 | 0.014222 | 0.00014967 | 2014-09-22 | C | 0.014222 | 0.00014967 | 2015 | 2014-09-22 | C | 49 | 0.014222 | 0.00014967
1 | 1965479 | 2014-09-22 15:15 | 2014-09-24 07:53 | 2438 | 84 | 7001 | 0.021412 | 0.00025691 | Restore Supply on Device X480 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X480 | F/man was onsited at OMS 1973613. Conversation betweeen dispatch & svs hub at 1630hrs asking if they would still get paid for the job that they onsited as was part of feeder & should never have been sent to them. Advised will be determined at invoicing le | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 83.3452 | 80.3452 | 6749 | 0.020614 | 0.00025657 | 2014-09-22 | C | 0.020614 | 0.00025657 | 2015 | 2014-09-22 | C | 84 | 0.020614 | 0.00025657
1 | 1952920 | 2014-09-22 15:19 | 2014-09-22 19:26 | 247.1167 | 383 | 8497.5833 | 0.025989 | 0.0011714 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Mikkelsen Rd CB 10 | CB 10 keeps A/R - urgent line patrol required Feeder sectionalised no fault found. | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 22.1869 | 19.1869 | 7348.5833 | 0.022446 | 0.0011698 | 2014-09-22 | C | 0.022446 | 0.0011698 | 2015 | 2014-09-22 | C | 383 | 0.022446 | 0.0011698
1 | 1953307 | 2014-09-22 15:21 | 2014-09-22 20:48 | 327.5667 | 26 | 7888.4 | 0.024126 | 7.9519e-05 | Restore Supply on Device S11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S11 | Replaced 10amp x2 section fuses ddo hv o/h. Section fuse S11. Cause: wind. Full power restored. Nothing else repaired or replaced. Adjacent assets - all good. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 303.4 | 300.4 | 7810.4 | 0.023856 | 7.9415e-05 | 2014-09-22 | C | 0.023856 | 7.9415e-05 | 2015 | 2014-09-22 | C | 26 | 0.023856 | 7.9415e-05
1 | 2867161 | 2014-09-22 15:40 | 2014-09-22 16:09 | 29 | 62 | 1798 | 0.005499 | 0.00018962 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 802514 | Emergency outage to replaced bolt on crossarm. On dashboard. Line was isolated at ABS 557, ABS 4510/1 & ABS 4510/6 to replace broken kingpin on pole 802514. Alan Cox attended. | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 29 | 26 | 1612 | 0.0049237 | 0.00018937 | 2014-09-22 | C | 0.0049237 | 0.00018937 | 2015 | 2014-09-22 | C | 62 | 0.0049237 | 0.00018937
1 | 1954599 | 2014-09-22 15:59 | 2014-09-25 07:27 | 3808.0167 | 6 | 11362.2833 | 0.034751 | 1.8351e-05 | Restore Supply on Device T50 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 836914 | Top of pole has burnt off and crossarm has come adrift. Power left isolated overnight at Fuses 7761. Replaced Pole 836914 & cross arm. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1893.7139 | 1890.7139 | 11344.2833 | 0.03465 | 1.8327e-05 | 2014-09-22 | C | 0.03465 | 1.8327e-05 | 2015 | 2014-09-22 | C | 6 | 0.03465 | 1.8327e-05
1 | 1955307 | 2014-09-22 16:12 | 2014-09-22 18:46 | 154.2667 | 411 | 41406.5167 | 0.12664 | 0.001257 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB7 | CB7 tripped and L/O. Line sectionalised and patrolled but no fault found. | F4 | PROSPECT ST | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.7458 | 97.7458 | 40173.5167 | 0.12271 | 0.0012554 | 2014-09-22 | C | 0.12271 | 0.0012554 | 2015 | 2014-09-22 | C | 411 | 0.12271 | 0.0012554
1 | 1956587 | 2014-09-22 16:32 | 2014-09-22 17:57 | 85.0833 | 108 | 9100.8 | 0.027834 | 0.00033031 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4196 | Recloser 4196 tripped on A & B phase O/C, line was patrolled and no fault was found suspect line clash due to high winds in area. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 84.2667 | 81.2667 | 8776.8 | 0.026808 | 0.00032988 | 2014-09-22 | C | 0.026808 | 0.00032988 | 2015 | 2014-09-22 | C | 108 | 0.026808 | 0.00032988
1 | 1965516 | 2014-09-22 17:22 | 2014-09-22 18:47 | 85 | 5 | 425 | 0.0012998 | 1.5292e-05 | Restore Supply on Device 1198 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 1198 | Attended by Jeremy Hill. Lines had been clashing in winds. Lines rebound to poles. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 85 | 82 | 410 | 0.0012523 | 1.5272e-05 | 2014-09-22 | C | 0.0012523 | 1.5272e-05 | 2015 | 2014-09-22 | C | 5 | 0.0012523 | 1.5272e-05
1 | 1965979 | 2014-09-22 17:56 | 2014-09-22 19:36 | 100 | 771 | 77100 | 0.2358 | 0.002358 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 384506 | Feeder Tripping caused by plastic foil wrapping around lines near Pole 384506. Removed with Fuse Stick and feeder restored | F3 | TE MAUNGA | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 74787 | 0.22843 | 0.002355 | 2014-09-22 | C | 0.22843 | 0.002355 | 2015 | 2014-09-22 | C | 771 | 0.22843 | 0.002355
1 | 1966833 | 2014-09-22 18:24 | 2014-09-22 18:48 | 23.8333 | 13 | 309.8333 | 0.0009476 | 3.9759e-05 | Restore Supply on Device 5552 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 758592 | Works done on OMS 1945572. Broken 11kV Binder at pole 758592. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 23.8333 | 20.8333 | 270.8333 | 0.00082724 | 3.9708e-05 | 2014-09-22 | C | 0.00082724 | 3.9708e-05 | 2015 | 2014-09-22 | C | 13 | 0.00082724 | 3.9708e-05
1 | 1966818 | 2014-09-22 19:00 | 2014-09-23 13:55 | 1135 | 9 | 10215 | 0.031242 | 2.7526e-05 | Restore Supply on Device 5369 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 4110T | Trees through lines. Attended by Scott Van Dyke (Powerworx) Tenix to return next day to complete. Broken crossarm repaired 23/09/14 and all supply restored. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1135 | 1132 | 10188 | 0.031118 | 2.749e-05 | 2014-09-22 | C | 0.031118 | 2.749e-05 | 2015 | 2014-09-22 | C | 9 | 0.031118 | 2.749e-05
1 | 1965466 | 2014-09-22 19:12 | 2014-09-22 21:09 | 116.85 | 166 | 8242.2 | 0.025208 | 0.0005077 | Restore Supply on Device C946 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Gladstone C946 | Sectionalised and partial patrol of feeder. Feeder went back in when wind died down. Lee Wilton and Brad Keating attended. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 49.6518 | 46.6518 | 7744.2 | 0.023654 | 0.00050703 | 2014-09-22 | C | 0.023654 | 0.00050703 | 2015 | 2014-09-22 | C | 166 | 0.023654 | 0.00050703
1 | 1967150 | 2014-09-22 19:16 | 2014-09-23 02:11 | 415 | 1 | 415 | 0.0012692 | 3.0584e-06 | Restore Supply on Device TC4164 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC 4164 | 2 X 8A HV DDO Fuses 1 X Fuse Holder. No other assets repaired or replaced on site, checked adjacent assets and all up to Powerco Standard. Email sent to Jo, as job has SAIDI component. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 415 | 412 | 412 | 0.0012584 | 3.0544e-06 | 2014-09-22 | C | 0.0012584 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.0012584 | 3.0544e-06
1 | 1967566 | 2014-09-22 21:37 | 2014-09-23 00:29 | 171.7833 | 1 | 171.7833 | 0.00052539 | 3.0584e-06 | Restore Supply on Device X2409 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | FUSES 2539 | Replaced 2 x 10amp HV DDO at fuses 2539. Cause weather. Adjacent assets checked and no other repairs or replacements made. Sent email to Jo, as appears to have SAIDI component. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 171.7833 | 168.7833 | 168.7833 | 0.00051554 | 3.0544e-06 | 2014-09-22 | C | 0.00051554 | 3.054e-06 | 2015 | 2014-09-22 | C | 1 | 0.00051554 | 3.0544e-06
1 | 1967100 | 2014-09-22 22:22 | 2014-09-22 23:26 | 63.25 | 128 | 8053.3333 | 0.02463 | 0.00039148 | Restore Supply on Device TP2621 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | IC314 | Jumper broken at ABS IC314. Jumper re-connected | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 62.9167 | 59.9167 | 7669.3333 | 0.023425 | 0.00039097 | 2014-09-22 | C | 0.023425 | 0.00039097 | 2015 | 2014-09-22 | C | 128 | 0.023425 | 0.00039097
1 | 1968861 | 2014-09-23 06:04 | 2014-09-23 08:01 | 116.3167 | 38 | 1370.6167 | 0.0041919 | 0.00011622 | Restore Supply on Device 1068 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuse FC1410 | Replaced 1 DDO - full unit - fuse 6amp and fuse base. 1 of 3, not a full set. Nothing else repaired or replaced on site. Checked adjacent assets and all up to Powerco standard. Caused by deterioration. . | F4 | WAIRERE RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 36.0689 | 33.0689 | 1256.6167 | 0.0038382 | 0.00011607 | 2014-09-23 | C | 0.0038382 | 0.00011607 | 2015 | 2014-09-23 | C | 38 | 0.0038382 | 0.00011607
1 | 1584446 | 2014-09-23 08:59 | 2014-09-23 12:42 | 223.45 | 10 | 2234.5 | 0.006834 | 3.0584e-05 | NAPA ID:02175 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 840310, 370340 | Replace 15 X 11kv poles 840310 to 370340. Work Location: Wirihana Road, Hawera. W/O 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 223.45 | 220.45 | 2204.5 | 0.0067335 | 3.0544e-05 | 2014-09-23 | B | 0.0033667 | 1.5272e-05 | 2015 | 2014-09-23 | B | 10 | 0.0067335 | 3.0544e-05
1 | 1625366 | 2014-09-23 09:08 | 2014-09-23 16:18 | 430 | 89 | 38270 | 0.11705 | 0.0002722 | NAPA ID:02188 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | replace 11kv poles P18100 and pole p15490 in preparation for new RMU switch 10215 | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 430 | 427 | 38003 | 0.11608 | 0.00027184 | 2014-09-23 | B | 0.058039 | 0.00013592 | 2015 | 2014-09-23 | B | 89 | 0.11608 | 0.00027184
1 | 2005409 | 2014-09-23 09:47 | 2014-09-23 15:48 | 361 | 6 | 2166 | 0.0066245 | 1.8351e-05 | Restore Supply on Device B33 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | fuses b33 | Restore supply at fuses B33 | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 361 | 358 | 2148 | 0.0065609 | 1.8327e-05 | 2014-09-23 | C | 0.0065609 | 1.8327e-05 | 2015 | 2014-09-23 | C | 6 | 0.0065609 | 1.8327e-05
1 | 1585613 | 2014-09-23 10:04 | 2014-09-23 13:57 | 233.1333 | 61 | 14221.1333 | 0.043494 | 0.00018656 | NAPA ID:01872 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 748189 | Replace 33kV xarm and broken 33kV insulators resag 33kV lines. 11kV replace pole 748189 and install tempory 11kV line fuses (temp 76). Install second set of tempory 11kV line fuses (temp 75) at pole 748160 for future shuts to reduce SAIDI. | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 233.1333 | 230.1333 | 14038.1333 | 0.042878 | 0.00018632 | 2014-09-23 | B | 0.021439 | 9.316e-05 | 2015 | 2014-09-23 | B | 61 | 0.042878 | 0.00018632
1 | 1970036 | 2014-09-23 10:31 | 2014-09-23 19:30 | 538.8667 | 1 | 538.8667 | 0.0016481 | 3.0584e-06 | Restore Supply on Device 1112 | 33000 | UNPLANNED | OVERHEAD LINE | VEGETATION | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | non outage gis error | F1, F2, F3 | PUKEPAPA 33KV | TP_MARTON | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 538.8667 | 535.8667 | 535.8667 | 0.0016368 | 3.0544e-06 | 2014-09-23 | C | 0.0016368 | 3.054e-06 | 2015 | 2014-09-23 | C | 1 | 0.0016368 | 3.0544e-06
1 | 1970124 | 2014-09-23 11:08 | 2014-09-23 19:02 | 474 | 167 | 6823 | 0.020868 | 0.00051076 | Restore Supply on Device C946 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | C946 | Line patrolled and trees removed with hotstick from pole 821814. Transformer T351 was also found to be faulty and this was replaced. Unknown if the trees or the distribution transformer were the cause of the fault. Joe Matthews attended. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 40.8563 | 37.8563 | 6322 | 0.01931 | 0.00051009 | 2014-09-23 | C | 0.01931 | 0.00051009 | 2015 | 2014-09-23 | C | 167 | 0.01931 | 0.00051009
1 | 1597486 | 2014-09-23 12:00 | 2014-09-23 14:56 | 176.2 | 22 | 3876.4 | 0.011856 | 6.7285e-05 | NAPA ID:01852 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W0712, W12913 | REPLACE XARMS AND REPLACE HOT STICK CLAMPS. Work Order 10141701. | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 176.2 | 173.2 | 3810.4 | 0.011639 | 6.7197e-05 | 2014-09-23 | B | 0.0058193 | 3.3599e-05 | 2015 | 2014-09-23 | B | 22 | 0.011639 | 6.7197e-05
1 | 1969236 | 2014-09-23 12:30 | 2014-09-23 15:49 | 199 | 3 | 597 | 0.0018259 | 9.1753e-06 | Restore Supply on Device T504 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE |  | 9.31am - Customer called to advised that tree is on line and line is smoking. Line is down in paddock. Still have part power. 9.44am - Customer advised they are only house on the road, faultman just need to keep on driving. Tree on lines, 11 kv conductor | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 199 | 196 | 588 | 0.001796 | 9.1633e-06 | 2014-09-23 | C | 0.001796 | 9.163e-06 | 2015 | 2014-09-23 | C | 3 | 0.001796 | 9.1633e-06
1 | 1971305 | 2014-09-23 14:08 | 2014-09-23 18:14 | 245.1333 | 1207 | 16715.5833 | 0.051123 | 0.0036915 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN |  | Reports received of lines bouncing and touching together. Isolated from ABS E68 and line restored to that point. Section of line patrolled from ABS E68 , nothing found and supply restored. Chris Naylor attended. | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 13.8489 | 10.8489 | 13094.5833 | 0.039996 | 0.0036867 | 2014-09-23 | C | 0.039996 | 0.0036867 | 2015 | 2014-09-23 | C | 1207 | 0.039996 | 0.0036867
1 | 1972715 | 2014-09-23 15:21 | 2014-09-23 18:44 | 202.3667 | 1 | 202.3667 | 0.00061892 | 3.0584e-06 | Restore Supply on Device 466 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 466 | Replaced 3 x 3amp HT DDO element at 466. Cause: weather. Adjacent assets checked and no other repairs or replacements made. Sent email to Jo, as appears to have SAIDI component. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 202.3667 | 199.3667 | 199.3667 | 0.00060895 | 3.0544e-06 | 2014-09-23 | C | 0.00060895 | 3.054e-06 | 2015 | 2014-09-23 | C | 1 | 0.00060895 | 3.0544e-06
1 | 2069179 | 2014-09-23 16:15 | 2014-09-23 16:42 | 27 | 44 | 1188 | 0.0036334 | 0.00013457 | Restore Supply on Device X2188 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2188 | Remove transformer X2188 due to oil leak. To be replaced at later date. | F2 | POLSON ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 1056 | 0.0032255 | 0.00013439 | 2014-09-23 | C | 0.0032255 | 0.00013439 | 2015 | 2014-09-23 | C | 44 | 0.0032255 | 0.00013439
1 | 1974943 | 2014-09-23 16:49 | 2014-09-24 02:37 | 587.7167 | 41 | 3300.3833 | 0.010094 | 0.0001254 | Restore Supply on Device TC598 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | TC598 | Broken Jumper to DDO TC598. Jumper re-attached. Isolation Between ABS's 560, IP191, 552 & 1041. Bacfeed via IC373 | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 80.4972 | 77.4972 | 3177.3833 | 0.0097051 | 0.00012523 | 2014-09-23 | C | 0.0097051 | 0.00012523 | 2015 | 2014-09-23 | C | 41 | 0.0097051 | 0.00012523
1 | 1968875 | 2014-09-23 17:43 | 2014-09-23 18:33 | 50 | 11 | 550 | 0.0016821 | 3.3643e-05 | Restore Supply on Device X702 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 785415 | DDO fuse broken at the top, replaced x1 DDO fuse and carrires (1 of three) Worked through control - cause old age X702 HV o/h No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 517 | 0.0015791 | 3.3599e-05 | 2014-09-23 | C | 0.0015791 | 3.3599e-05 | 2015 | 2014-09-23 | C | 11 | 0.0015791 | 3.3599e-05
1 | 1982190 | 2014-09-23 18:59 | 2014-09-23 21:13 | 134.35 | 303 | 24676.2 | 0.07547 | 0.0009267 | Restore Supply on Device 282 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 282 | CB 282 tripped, Transpower reported no flags, line was patrolled and sectionalised and no fault was found. Faultman Karl Rodgers did come across people shooting opossum. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 81.4396 | 78.4396 | 23767.2 | 0.072595 | 0.00092549 | 2014-09-23 | C | 0.072595 | 0.00092549 | 2015 | 2014-09-23 | C | 303 | 0.072595 | 0.00092549
1 | 1986412 | 2014-09-23 21:32 | 2014-09-24 01:28 | 236.0333 | 1 | 236.0333 | 0.00072189 | 3.0584e-06 | Restore Supply on Device TC5084 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC 2146 | 2 X 10A HV DDO Fuses. No other assets repaired or replaced on site, checked adjacent assets, and all up to Powerco standard. Sent email to Jo, as appears to have SAIDI component. | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 236.0333 | 233.0333 | 233.0333 | 0.00071178 | 3.0544e-06 | 2014-09-23 | C | 0.00071178 | 3.054e-06 | 2015 | 2014-09-23 | C | 1 | 0.00071178 | 3.0544e-06
1 | 1583773 | 2014-09-24 09:00 | 2014-09-24 15:20 | 380 | 49 | 18620 | 0.056948 | 0.00014986 | NAPA ID:01686 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS1066 | Replacing 11kv poles & Xarms from ABS 1066 to the end of the line. Work Location: Whangaehu Beach Road. Work Order 10140836. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 380 | 377 | 18473 | 0.056424 | 0.00014967 | 2014-09-24 | B | 0.028212 | 7.4833e-05 | 2015 | 2014-09-24 | B | 49 | 0.056424 | 0.00014967
1 | 1625617 | 2014-09-24 09:01 | 2014-09-24 15:45 | 404.5833 | 228 | 90320.2 | 0.27624 | 0.00069732 | NAPA ID:02280 TP_TAURANGA 33 GXP > OTUMOETAI SUB > VALE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 206349 | REPLACE POLES AND ARMS SURGE ARRESTORS. Works location: Vale St. WO 10147282/IR6632 | F3 | VALE ST | OTUMOETAI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 396.1412 | 393.1412 | 89636.2 | 0.27379 | 0.00069641 | 2014-09-24 | B | 0.13689 | 0.0003482 | 2015 | 2014-09-24 | B | 228 | 0.27379 | 0.00069641
1 | 1994582 | 2014-09-24 10:11 | 2014-09-24 10:22 | 11.4 | 3 | 34.2 | 0.0001046 | 9.1753e-06 | Restore Supply on Device D11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D11 | Fuses D11 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 11.4 | 8.4 | 25.2 | 7.6971e-05 | 9.1633e-06 | 2014-09-24 | C | 7.6971e-05 | 9.163e-06 | 2015 | 2014-09-24 | C | 3 | 7.6971e-05 | 9.1633e-06
1 | 2007384 | 2014-09-24 22:24 | 2014-09-24 23:19 | 54.9 | 1 | 54.9 | 0.00016791 | 3.0584e-06 | Restore Supply on Device T8/243 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | Fuses S11 | Faultman found 2 blown fuses at Fuses S11, suspect trees contact when windy, need to return in morning to carry out a line patrol. 2 X 10Amp HV rewirable fuses were replaced. Email sent to Jo, as appears has SAIDI component. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54.9 | 51.9 | 51.9 | 0.00015852 | 3.0544e-06 | 2014-09-24 | C | 0.00015852 | 3.054e-06 | 2015 | 2014-09-24 | C | 1 | 0.00015852 | 3.0544e-06
1 | 2051281 | 2014-09-25 03:58 | 2014-09-25 06:15 | 137 | 316 | 29603 | 0.090538 | 0.00096646 | Restore Supply on Device 282 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN |  | Line patrolled nothing found. Suspect possums | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 93.6804 | 90.6804 | 28655 | 0.087525 | 0.0009652 | 2014-09-25 | C | 0.087525 | 0.0009652 | 2015 | 2014-09-25 | C | 316 | 0.087525 | 0.0009652
1 | 2007398 | 2014-09-25 04:01 | 2014-09-25 06:44 | 162.6667 | 316 | 50764.4167 | 0.15526 | 0.00096646 | Restore Supply on Device 282 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 282 | CB 282 tripped no flags, line was patrolled and sectionalised and no fault was found. Suspect Opossums, as a few running around in area. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 160.6469 | 157.6469 | 49816.4167 | 0.15216 | 0.0009652 | 2014-09-25 | C | 0.15216 | 0.0009652 | 2015 | 2014-09-25 | C | 316 | 0.15216 | 0.0009652
1 | 1672298 | 2014-09-25 08:10 | 2014-09-25 15:47 | 456.6333 | 31 | 14155.6333 | 0.043294 | 9.4811e-05 | NAPA ID:02294 TP_GREYTOWN GXP > KEMPTON SUB > WEST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 818503 | Isolate t1355 and change 11kV transformer and pole live line. Works location: West St. WO 10149405/IR6938. | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 456.6333 | 453.6333 | 14062.6333 | 0.042953 | 9.4687e-05 | 2014-09-25 | B | 0.021477 | 4.7344e-05 | 2015 | 2014-09-25 | B | 31 | 0.042953 | 9.4687e-05
1 | 2009075 | 2014-09-25 09:30 | 2014-09-25 13:23 | 233.1904 | 242 | 55566.8 | 0.16995 | 0.00074014 | Restore Supply on Device 144 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/636 | Tripping on Kelvin Grove CB12 on E/F. Feeder sectionalised with fault area located between Sw/gear 450 and 144. Remainder of feeder backfed via sw/gear 192 and 381. Cable fault found between Sw/gear 144 and T6/636. Cables Disconnected at Transformer and | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 229.6149 | 226.6149 | 54840.8 | 0.16751 | 0.00073917 | 2014-09-25 | C | 0.16751 | 0.00073917 | 2015 | 2014-09-25 | C | 242 | 0.16751 | 0.00073917
1 | 1994210 | 2014-09-25 09:37 | 2014-09-25 13:21 | 224 | 15 | 3360 | 0.010276 | 4.5876e-05 | NAPA ID:03070 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 759178 | Replace 33kv xarms and strain insulators. | F2 | BELL BLOCK 5 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 224 | 221 | 3315 | 0.010125 | 4.5816e-05 | 2014-09-25 | B | 0.0050627 | 2.2908e-05 | 2015 | 2014-09-25 | B | 15 | 0.010125 | 4.5816e-05
1 | 2009348 | 2014-09-25 09:45 | 2014-09-25 10:00 | 15.3167 | 565 | 8562.45 | 0.026188 | 0.001728 | Restore Supply on Device 133 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | cb12 | Tripping on CB12 on E/F. Feeder sectionalised with fault area located between Sw/gear 450 and 144. Remainder of feeder backfed via sw/gear 192 and 381. | F2 | ARMSTRONG ST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 15.1548 | 12.1548 | 6867.45 | 0.020976 | 0.0017257 | 2014-09-25 | C | 0.020976 | 0.0017257 | 2015 | 2014-09-25 | C | 565 | 0.020976 | 0.0017257
1 | 1626587 | 2014-09-25 10:07 | 2014-09-25 12:22 | 134.2833 | 10 | 1342.8333 | 0.004107 | 3.0584e-05 | NAPA ID:02176 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 840309 | 11kv reconductor from pole 840309 to pole 370340. Works location: Wirihana Rd, Hawera. WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 134.2833 | 131.2833 | 1312.8333 | 0.0040099 | 3.0544e-05 | 2014-09-25 | B | 0.002005 | 1.5272e-05 | 2015 | 2014-09-25 | B | 10 | 0.0040099 | 3.0544e-05
1 | 2006485 | 2014-09-25 10:10 | 2014-09-25 12:02 | 111.8167 | 10 | 1118.1667 | 0.0034198 | 3.0584e-05 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4007 | CREW TO ATTEND 25/09 (KEVIN). FULL POWER. CROSS ARM & 3X HV FUSES (SET)TO BE REPLACED 25/09. FOLLOW UP JOB FROM OMS 1995203. All completed (Double crossarms with insulators and TX fuses). | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 111.8167 | 108.8167 | 1088.1667 | 0.0033237 | 3.0544e-05 | 2014-09-25 | B | 0.0016619 | 1.5272e-05 | 2015 | 2014-09-25 | B | 10 | 0.0033237 | 3.0544e-05
1 | 1672297 | 2014-09-25 11:48 | 2014-09-25 13:23 | 94.9333 | 39 | 3702.4 | 0.011324 | 0.00011928 | NAPA ID:02421 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P03094 | Trim trees under 11kV overhead line between P03094 and P03729. Works location: Te Parapara Rd. WO 10199999. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 94.9333 | 91.9333 | 3585.4 | 0.010951 | 0.00011912 | 2014-09-25 | B | 0.0054757 | 5.9561e-05 | 2015 | 2014-09-25 | B | 39 | 0.010951 | 0.00011912
1 | 2008876 | 2014-09-25 15:15 | 2014-09-25 14:20 | -54.7 | 191 | 61957.2167 | 0.18949 | 0.00058416 | Restore Supply on Device SC4-024 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC4-024 | Replace Poles & Crossarms & Surge arrestors. Works location: Vale St. WO 10147282/IR6632 Part of OMS No. 1662249 Parent | F3 | VALE ST | OTUMOETAI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 324.3833 | 321.3833 | 61384.2167 | 0.18749 | 0.00058339 | 2014-09-25 | C | 0.18749 | 0.0005834 | 2015 | 2014-09-25 | C | 191 | 0.18749 | 0.00058339
1 | 2020886 | 2014-09-25 15:55 | 2014-09-26 11:37 | 1181.95 | 2 | 3061.3667 | 0.009363 | 6.1168e-06 | Restore Supply on Device 7760 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 836987 | Outage required to isolate a floating conductor. (Isolation from fuses 7760). Initially considered unsafe to repair due to terrain and working conditions. Conductors rebound (on all 3 insulators next day and relivened). | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1530.6833 | 1527.6833 | 3055.3667 | 0.0093324 | 6.1088e-06 | 2014-09-25 | C | 0.0093324 | 6.109e-06 | 2015 | 2014-09-25 | C | 2 | 0.0093324 | 6.1088e-06
1 | 2020918 | 2014-09-25 23:53 | 2014-09-26 01:08 | 75.1667 | 98 | 7366.3333 | 0.022529 | 0.00029973 | Restore Supply on Device 2884T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 732326 | Polymer insulator replaced on pole 732326. F/man requested : assign Jade Williams to assist with sparking HV Polymor up pole | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 75.1667 | 72.1667 | 7072.3333 | 0.021602 | 0.00029933 | 2014-09-25 | C | 0.021602 | 0.00029933 | 2015 | 2014-09-25 | C | 98 | 0.021602 | 0.00029933
1 | 2021163 | 2014-09-26 05:51 | 2014-09-26 11:28 | 337.2833 | 12 | 3464.2167 | 0.010595 | 3.6701e-05 | Restore Supply on Device 8221 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8221 | GO TO DEVICE 8221. 2x hv fuses 2 x10 amp due to bird strike. No other assets repaired or replaced. Adjacent assets ok. | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 288.6847 | 285.6847 | 3428.2167 | 0.010471 | 3.6653e-05 | 2014-09-26 | C | 0.010471 | 3.6653e-05 | 2015 | 2014-09-26 | C | 12 | 0.010471 | 3.6653e-05
1 | 1681761 | 2014-09-26 08:44 | 2014-09-26 13:59 | 315.5 | 108 | 34074 | 0.10421 | 0.00033031 | NAPA ID:02425 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > GREEN PARK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP121 | REPLACE POLE AND 15 ARMS. Works location: Joyce Rd. WO 1014564/ IR6874. | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 315.5 | 312.5 | 33750 | 0.10309 | 0.00032988 | 2014-09-26 | B | 0.051543 | 0.00016494 | 2015 | 2014-09-26 | B | 108 | 0.10309 | 0.00032988
1 | 2053899 | 2014-09-26 08:50 | 2014-09-26 14:30 | 340 | 6 | 2040 | 0.0062392 | 1.8351e-05 | Restore Supply on Device cut side 1 temp line [738,0,100,0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP 88 | Reconducting on 11kV poles and relocate Temp 52. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 340 | 337 | 2022 | 0.006176 | 1.8327e-05 | 2014-09-26 | C | 0.006176 | 1.8327e-05 | 2015 | 2014-09-26 | C | 6 | 0.006176 | 1.8327e-05
1 | 2021204 | 2014-09-26 09:08 | 2014-09-26 09:58 | 50 | 8 | 400 | 0.0012234 | 2.4467e-05 | Restore Supply on Device T9/246 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE |  |  | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 376 | 0.0011485 | 2.4435e-05 | 2014-09-26 | C | 0.0011485 | 2.4435e-05 | 2015 | 2014-09-26 | C | 8 | 0.0011485 | 2.4435e-05
1 | 2022572 | 2014-09-27 05:49 | 2014-09-27 10:56 | 307.2667 | 23 | 4896.8833 | 0.014977 | 7.0344e-05 | Restore Supply on Device TC442 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O2838 | at 07:15, Kerepehi Sub, CB 6 Ngatea Feeder. Fautlman dispatched to job and found line down at Pole O2838. Isolated lines at Fuses FC803. Permit Issued & Repairs Carried out. All Power Restored on completion. Grant Jordan Attended. Child Job is for actual | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 212.908 | 209.908 | 4827.8833 | 0.014746 | 7.0252e-05 | 2014-09-27 | C | 0.014746 | 7.0252e-05 | 2015 | 2014-09-27 | C | 23 | 0.014746 | 7.0252e-05
1 | 2033591 | 2014-09-27 06:47 | 2014-09-27 06:56 | 8.7333 | 293 | 2558.8667 | 0.0078261 | 0.00089612 | Restore Supply on Device 321 | 11000 | UNPLANNED | Underground cable. | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | T6/533 | Repair 400V cable burning at Transformer T6/633. NAPA 2539 | F1 | RUAHINE | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 8.7333 | 5.7333 | 1679.8667 | 0.005131 | 0.00089495 | 2014-09-27 | C | 0.005131 | 0.00089495 | 2015 | 2014-09-27 | C | 293 | 0.005131 | 0.00089495
1 | 2033885 | 2014-09-27 07:35 | 2014-09-27 09:28 | 112.7761 | 12 | 741.4333 | 0.0022676 | 3.6701e-05 | Restore Supply on Device LI719 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 728944 | Replaced 2x 10Amp Links due to bird strike | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 61.7861 | 58.7861 | 705.4333 | 0.0021547 | 3.6653e-05 | 2014-09-27 | C | 0.0021547 | 3.6653e-05 | 2015 | 2014-09-27 | C | 12 | 0.0021547 | 3.6653e-05
1 | 2033931 | 2014-09-27 08:43 | 2014-09-27 14:00 | 316.7 | 2 | 624.6333 | 0.0019104 | 6.1168e-06 | Restore Supply on Device TC2038 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | H2238 | at 09:50 Waharoa Sub, CB 1 Mowbray Rd Feeder. Job came in of a Tractor that had hit a Pole and Broken the Pole H2238. Isolated Lines at Fuses FP1106. Permit Issued & Repairs carried out. All power restored on completion. Marty Keenan Attended. Replaced: 1 | F3 | MOWBRAY RD | WAHAROA SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 312.3167 | 309.3167 | 618.6333 | 0.0018896 | 6.1088e-06 | 2014-09-27 | C | 0.0018896 | 6.109e-06 | 2015 | 2014-09-27 | C | 2 | 0.0018896 | 6.1088e-06
1 | 1994664 | 2014-09-27 08:46 | 2014-09-27 14:34 | 347.4 | 4 | 1389.6 | 0.00425 | 1.2234e-05 | NAPA ID:03075 TP_MARTON GXP > PUKEPAPA SUB > BULLS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 801951 | Replace broken 11kV pole 801951 being held by Digger. Works location: Farmlands, Tennets Rd, Bulls. WO 10152448. | F4 | BULLS | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 347.4 | 344.4 | 1377.6 | 0.0042078 | 1.2218e-05 | 2014-09-27 | B | 0.0021039 | 6.109e-06 | 2015 | 2014-09-27 | B | 4 | 0.0042078 | 1.2218e-05
1 | 2046369 | 2014-09-27 23:11 | 2014-09-28 08:30 | 559 | 171 | 12223 | 0.037383 | 0.00052299 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc2350 | Recloser 9320 Trip. Batteries flat no comms to recloser so did not record that it had opened. Feeder patrolled, fault found to be past Fuses FC2350. Possible cable crutch blown. Marty Keenan to investigate in the morning. Fault found to be a broken Binder | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 71.4795 | 68.4795 | 11710 | 0.035767 | 0.00052231 | 2014-09-27 | C | 0.035767 | 0.00052231 | 2015 | 2014-09-27 | C | 171 | 0.035767 | 0.00052231
1 | 2046709 | 2014-09-28 05:07 | 2014-09-28 08:19 | 192.1833 | 118 | 21937.3 | 0.067094 | 0.00036089 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741691 | Recloser CB 8763 tripped on E/F. Staging to find fault. Faulty insulator found at pole 741961. 1 x 11kV pin insulator and binder used for repair. Nick Webby and K McKay attended. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 185.9093 | 182.9093 | 21583.3 | 0.065925 | 0.00036042 | 2014-09-28 | C | 0.065925 | 0.00036042 | 2015 | 2014-09-28 | C | 118 | 0.065925 | 0.00036042
1 | 2047784 | 2014-09-28 08:22 | 2014-09-28 11:46 | 203.9667 | 1 | 203.9667 | 0.00062382 | 3.0584e-06 | Restore Supply on Device X1038 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 133 | replaced 2 x 6 amp fuses. fuse # 133. cause: bark on 11 kv line, removed by FM. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 203.9667 | 200.9667 | 200.9667 | 0.00061384 | 3.0544e-06 | 2014-09-28 | C | 0.00061384 | 3.054e-06 | 2015 | 2014-09-28 | C | 1 | 0.00061384 | 3.0544e-06
1 | 2047837 | 2014-09-28 09:07 | 2014-09-28 14:07 | 299.5833 | 105 | 11525.8333 | 0.035251 | 0.00032113 | Restore Supply on Device 311 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 702252 | Replace 2 termination arms, set of 3 ddo's, 3x polymers and miscellaneous hardware. Traffic management required to close off one lane | F2 | MOTUROA 5 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.7698 | 106.7698 | 11210.8333 | 0.034243 | 0.00032071 | 2014-09-28 | C | 0.034243 | 0.00032071 | 2015 | 2014-09-28 | C | 105 | 0.034243 | 0.00032071
1 | 2047861 | 2014-09-28 09:32 | 2014-09-28 13:18 | 225.65 | 15 | 2556.4167 | 0.0078186 | 4.5876e-05 | Restore Supply on Device LI171 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 850586 | Fuses LI171 Open and tagged. Line down at pole 850586. 2 sleeves and 4 metres of 16mm CU conductor used to repair. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 170.4278 | 167.4278 | 2511.4167 | 0.0076709 | 4.5816e-05 | 2014-09-28 | C | 0.0076709 | 4.5816e-05 | 2015 | 2014-09-28 | C | 15 | 0.0076709 | 4.5816e-05
1 | 2048752 | 2014-09-28 13:16 | 2014-09-28 15:50 | 154.05 | 45 | 6932.25 | 0.021202 | 0.00013763 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 790514 | Remove tree branch blown onto lines during strong winds | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 154.05 | 151.05 | 6797.25 | 0.020762 | 0.00013745 | 2014-09-28 | C | 0.020762 | 0.00013745 | 2015 | 2014-09-28 | C | 45 | 0.020762 | 0.00013745
1 | 2049062 | 2014-09-28 14:11 | 2014-09-28 17:24 | 192.6667 | 1 | 192.6667 | 0.00058926 | 3.0584e-06 | Restore Supply on Device T1172 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1172 | Disconnected T1172 for safety. Cable fault on tx structure. FM needs faultman with bucket truck to assist. Cable that supplies OH circuitary was completely electrically damaged. Reterminated at tx T1172. Cause age. Adjacent assets checked and no other re | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 192.6667 | 189.6667 | 189.6667 | 0.00057932 | 3.0544e-06 | 2014-09-28 | C | 0.00057932 | 3.054e-06 | 2015 | 2014-09-28 | C | 1 | 0.00057932 | 3.0544e-06
1 | 2050139 | 2014-09-28 16:24 | 2014-09-28 22:51 | 387.7667 | 11 | 2736.9333 | 0.0083707 | 3.3643e-05 | Restore Supply on Device LI774 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 748721 | Outage required from Fuses Li774 to repair a broken conductor - high winds | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 248.8121 | 245.8121 | 2703.9333 | 0.008259 | 3.3599e-05 | 2014-09-28 | C | 0.008259 | 3.3599e-05 | 2015 | 2014-09-28 | C | 11 | 0.008259 | 3.3599e-05
1 | 2049668 | 2014-09-28 18:20 | 2014-09-29 13:00 | 1120.0167 | 29 | 30166.05 | 0.092261 | 8.8694e-05 | Restore Supply on Device 6289 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 704538 | 5M 16 MM COPPER WIRE, BINDER 2 X SLEEVES. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. ADVISED ALSO USED TRAFFIC MANAGEMENT, NO 2R REQUESTED. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1040.2086 | 1037.2086 | 30079.05 | 0.091874 | 8.8578e-05 | 2014-09-28 | C | 0.091874 | 8.8578e-05 | 2015 | 2014-09-28 | C | 29 | 0.091874 | 8.8578e-05
1 | 2049574 | 2014-09-28 19:52 | 2014-09-28 20:55 | 63.5333 | 19 | 1207.1333 | 0.0036919 | 5.811e-05 | Restore Supply on Device M4305 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 718744 | Outage required from fuses MA550 to repair a broken Conductor. Jointed OK.- High winds. | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 63.5333 | 60.5333 | 1150.1333 | 0.003513 | 5.8034e-05 | 2014-09-28 | C | 0.003513 | 5.8034e-05 | 2015 | 2014-09-28 | C | 19 | 0.003513 | 5.8034e-05
1 | 2049892 | 2014-09-28 20:01 | 2014-09-28 22:02 | 121.2667 | 1 | 121.2667 | 0.00037088 | 3.0584e-06 | Restore Supply on Device TC3984 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE |  | Replaced 2X hv fuses @ fuses FP761. Email sent to Jo as appears job may have SAIDI component. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 121.2667 | 118.2667 | 118.2667 | 0.00036124 | 3.0544e-06 | 2014-09-28 | C | 0.00036124 | 3.054e-06 | 2015 | 2014-09-28 | C | 1 | 0.00036124 | 3.0544e-06
1 | 2050495 | 2014-09-28 21:20 | 2014-09-29 10:17 | 777.2167 | 332 | 9425.6833 | 0.028828 | 0.0010154 | Restore Supply on Device PU265 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 704472 | replaced crossarm 11KV CROSS ARM 2 X FUSE INSERTS , DUE TO WEATHER NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 28.3906 | 25.3906 | 8429.6833 | 0.025748 | 0.0010141 | 2014-09-28 | C | 0.025748 | 0.0010141 | 2015 | 2014-09-28 | C | 332 | 0.025748 | 0.0010141
1 | 2050777 | 2014-09-28 21:59 | 2014-09-28 22:48 | 49.5833 | 98 | 4859.1667 | 0.014861 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 756227 | Tripping on Recloser CB 6748 on Ph B, O/C. Patrol carried out and fault caused by palm tree branches hitting line during high wind gusts. CB reclosed OK when gusts slowed down. Trees to be cut back. NOTE: B.Moratti on site for this job, problem with OMS | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 49.5833 | 46.5833 | 4565.1667 | 0.013944 | 0.00029933 | 2014-09-28 | C | 0.013944 | 0.00029933 | 2015 | 2014-09-28 | C | 98 | 0.013944 | 0.00029933
1 | 2050146 | 2014-09-28 22:01 | 2014-09-29 14:27 | 986.2167 | 25 | 24655.4167 | 0.075407 | 7.6461e-05 | Restore Supply on Device Y67 | 6600 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 775557 | 9:05pm Rang job through to the hub, advised Leanne Made safe for the night to be attended tomorrow with tree crews etc. Line was isolated at Fuses 481 to repair cross arms and lines due to tree falling through them due to very high winds.Tree out of not | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 986.2167 | 983.2167 | 24580.4167 | 0.075079 | 7.6361e-05 | 2014-09-28 | C | 0.075079 | 7.6361e-05 | 2015 | 2014-09-28 | C | 25 | 0.075079 | 7.6361e-05
1 | 2051068 | 2014-09-28 23:00 | 2014-09-29 11:38 | 758 | 2 | 1516 | 0.0046366 | 6.1168e-06 | Restore Supply on Device F30 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P49593 | Faultman found a big gum tree had fallen and broken the conductors at pole P49593, line was isolated at Fuses F30 to repair the lines. Tree was out of notice zone. 40 meters of Squirrell conductor was used and 7 sleeves. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 758 | 755 | 1510 | 0.0046122 | 6.1088e-06 | 2014-09-28 | C | 0.0046122 | 6.109e-06 | 2015 | 2014-09-28 | C | 2 | 0.0046122 | 6.1088e-06
1 | 2051620 | 2014-09-29 08:23 | 2014-09-29 19:28 | 665 | 3 | 168.95 | 0.00051672 | 9.1753e-06 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 714830 | Fuses TA809 opened and tagged. 2 x connectors. Polymer strain and Cu deadend uses. 2R required to bring gear and help replaced HV insulator for safety reasons. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 56.3167 | 53.3167 | 159.95 | 0.00048856 | 9.1633e-06 | 2014-09-29 | B | 0.00024428 | 4.582e-06 | 2015 | 2014-09-29 | B | 3 | 0.00048856 | 9.1633e-06
1 | 1681801 | 2014-09-29 08:30 | 2014-09-29 12:12 | 222 | 72 | 15984 | 0.048886 | 0.00022021 | NAPA ID:02184 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | ABS S162 | Tree cutting under A/P. Works location: Kaka Amu Rd. PPPD 41762. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 222 | 219 | 15768 | 0.048162 | 0.00021992 | 2014-09-29 | B | 0.024081 | 0.00010996 | 2015 | 2014-09-29 | B | 72 | 0.048162 | 0.00021992
1 | 1880697 | 2014-09-29 09:19 | 2014-09-29 16:39 | 440.55 | 307 | 125300.3333 | 0.38322 | 0.00093894 | NAPA ID:02202 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Strathmore CB 7131 | Shut 1 Tenix to change 11kv double cross arms at pole 709165 arms roten Shut 2 Install set of 11kv links either side x2 at re closer 6813/2 pole 846905 links 6813/4 and 6813/6 to minimize saidi count. Shut 3 Install 11kv temporary Links 12028 to pole 70 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 408.1444 | 405.1444 | 124379.3333 | 0.37991 | 0.00093771 | 2014-09-29 | B | 0.18995 | 0.00046885 | 2015 | 2014-09-29 | B | 307 | 0.37991 | 0.00093771
1 | 1687455 | 2014-09-29 09:30 | 2014-09-29 15:40 | 370 | 2 | 740 | 0.0022632 | 6.1168e-06 | NAPA ID:02384 TP_LINTON GXP > KAIRANGA SUB > BAINESSE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/421 | Cut jumpers live line on pole P36676, fit new 15 kva tx and Hardware Re-Connect jumpers Liven and test TX. Works location: SH1/ Paranui Rd. WO 1056813. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 370 | 367 | 734 | 0.0022419 | 6.1088e-06 | 2014-09-29 | B | 0.001121 | 3.054e-06 | 2015 | 2014-09-29 | B | 2 | 0.0022419 | 6.1088e-06
1 | 1626192 | 2014-09-29 09:42 | 2014-09-29 13:47 | 244.5 | 27 | 6601.5 | 0.02019 | 8.2577e-05 | NAPA ID:02288 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > GREEN PARK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 249564 | 1/ CREATE GAP AT POLE 249564. 2/ REPLACE DOUBLE POLE TERM POINT ANGLE 216244. 3/ REPLACE HV ARM POLE 216245 4/ REMAKE GAP Works location: Cheyne Rd WO 10145644 IR 6874 | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 244.5 | 241.5 | 6520.5 | 0.019916 | 8.2469e-05 | 2014-09-29 | B | 0.0099582 | 4.1235e-05 | 2015 | 2014-09-29 | B | 27 | 0.019916 | 8.2469e-05
1 | 1688118 | 2014-09-29 10:03 | 2014-09-29 12:01 | 117.6667 | 15 | 1765 | 0.0053981 | 4.5876e-05 | NAPA ID:02521 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC280 | Unbind H/V and L/V lines for re-sagging. Works location: Hollis Rd, Waikino. WO 10150814. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 117.6667 | 114.6667 | 1720 | 0.0052536 | 4.5816e-05 | 2014-09-29 | B | 0.0026268 | 2.2908e-05 | 2015 | 2014-09-29 | B | 15 | 0.0052536 | 4.5816e-05
1 | 2062900 | 2014-09-29 15:34 | 2014-09-29 17:04 | 90.1667 | 1 | 90.1667 | 0.00027577 | 3.0584e-06 | Restore Supply on Device TE7-020 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218076 | Replaced 1x ddo holder & 2x 6amp fuse elements hv o/h. Pole 218076. Cause unknown. Full power restored. Nothing else repaired or replaced. Adjacent assets - ok. Email sent to Jo as appears job may have SAIDI component. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 90.1667 | 87.1667 | 87.1667 | 0.00026624 | 3.0544e-06 | 2014-09-29 | C | 0.00026624 | 3.054e-06 | 2015 | 2014-09-29 | C | 1 | 0.00026624 | 3.0544e-06
1 | 2062923 | 2014-09-29 16:07 | 2014-09-29 20:18 | 251.45 | 1 | 251.45 | 0.00076904 | 3.0584e-06 | Restore Supply on Device X622 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X622 | Replaced 2x 3a HV fuse links. Nothing else repaired or replaced, adjacent assets all good. Email sent to Jo as appears job may have SAIDI component. | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 251.45 | 248.45 | 248.45 | 0.00075887 | 3.0544e-06 | 2014-09-29 | C | 0.00075887 | 3.054e-06 | 2015 | 2014-09-29 | C | 1 | 0.00075887 | 3.0544e-06
1 | 2052401 | 2014-09-29 17:38 | 2014-09-29 18:28 | 50.6667 | 58 | 2600.8167 | 0.0079544 | 0.00017739 | Restore Supply on Device P2075 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 846657 | Replace center bolt an cross arm at pole 846657. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 44.8417 | 41.8417 | 2426.8167 | 0.0074125 | 0.00017716 | 2014-09-29 | C | 0.0074125 | 0.00017716 | 2015 | 2014-09-29 | C | 58 | 0.0074125 | 0.00017716
1 | 2053965 | 2014-09-29 19:50 | 2014-09-29 21:43 | 113 | 1 | 113 | 0.0003456 | 3.0584e-06 | Restore Supply on Device 3113W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844954 | Fuses 4626 opened and tagged. Broken poly strain insulator found on poles 844594. 1 x Polymer, 2 x 6 amp fuse link. Carried out tests at 1 Okiwa Tce & at the Waste treatment site further down the beach - Full voltage at both sites. No fault located. F/man | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 113 | 110 | 110 | 0.00033599 | 3.0544e-06 | 2014-09-29 | C | 0.00033599 | 3.054e-06 | 2015 | 2014-09-29 | C | 1 | 0.00033599 | 3.0544e-06
1 | 2062930 | 2014-09-29 20:54 | 2014-09-29 21:42 | 47.65 | 9 | 428.85 | 0.0013116 | 2.7526e-05 | Restore Supply on Device P2280 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 711021 | Refix DDO Holder to crossarm. 1 x 130mm bolt | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 47.65 | 44.65 | 401.85 | 0.0012274 | 2.749e-05 | 2014-09-29 | C | 0.0012274 | 2.749e-05 | 2015 | 2014-09-29 | C | 9 | 0.0012274 | 2.749e-05
1 | 2064200 | 2014-09-30 07:29 | 2014-09-30 13:51 | 382.5167 | 4 | 990.4833 | 0.0030293 | 1.2234e-05 | Restore Supply on Device X1074 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2601 FUSES | 2X 15 AMP LINE FUSES SUSPECT LINE CLASH DUE TO BIRD STRIKE. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. Email sent to Jo as appears job may have SAIDI component. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 247.6208 | 244.6208 | 978.4833 | 0.0029887 | 1.2218e-05 | 2014-09-30 | C | 0.0029887 | 1.2218e-05 | 2015 | 2014-09-30 | C | 4 | 0.0029887 | 1.2218e-05
1 | 2098555 | 2014-09-30 08:00 | 2014-09-30 15:14 | 434 | 8 | 1228 | 0.0037557 | 2.4467e-05 | Restore Supply on Device cut side 1 temp line [780,0,100,0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TEMP 53 | Replace 11kV Poles. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 153.5 | 150.5 | 1204 | 0.0036775 | 2.4435e-05 | 2014-09-30 | C | 0.0036775 | 2.4435e-05 | 2015 | 2014-09-30 | C | 8 | 0.0036775 | 2.4435e-05
1 | 1676673 | 2014-09-30 08:48 | 2014-09-30 15:20 | 391.5667 | 106 | 41506.0667 | 0.12694 | 0.00032419 | NAPA ID:02510 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 783930 | Trimming & felling trees close to 11kV lines between pole 783930 & 791306. Works location: Mangamahu Rd. PPPD 46583. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 391.5667 | 388.5667 | 41188.0667 | 0.12581 | 0.00032377 | 2014-09-30 | B | 0.062903 | 0.00016188 | 2015 | 2014-09-30 | B | 106 | 0.12581 | 0.00032377
1 | 1672588 | 2014-09-30 09:00 | 2014-09-30 14:55 | 355 | 3 | 1065 | 0.0032572 | 9.1753e-06 | NAPA ID:01833 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 794025 | Running new conductor from pole 794025 to transformer pole X48 pole 794032. Works location: Whangaehu Beach Rd. WO 10140836. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 355 | 352 | 1056 | 0.0032255 | 9.1633e-06 | 2014-09-30 | B | 0.0016127 | 4.582e-06 | 2015 | 2014-09-30 | B | 3 | 0.0032255 | 9.1633e-06
1 | 1728843 | 2014-09-30 09:08 | 2014-09-30 11:37 | 149.5167 | 72 | 10765.2 | 0.032925 | 0.00022021 | NAPA ID:02152 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W0618 | REPLACING XARMS POLE W0618. Works location: Captain Cook Rd/Hicks Place. WO 0141701 | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 149.5167 | 146.5167 | 10549.2 | 0.032222 | 0.00021992 | 2014-09-30 | B | 0.016111 | 0.00010996 | 2015 | 2014-09-30 | B | 72 | 0.032222 | 0.00021992
1 | 2098595 | 2014-09-30 09:13 | 2014-09-30 15:05 | 352 | 39 | 7744 | 0.023684 | 0.00011928 | Restore Supply on Device cut side 1 temp line [789,0,100,0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36205 | planned switching 1687543. To change two poles and two span of conductor that was found to be in very poor condition. Works location: Pyke Rd. WO 10156813 | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 198.5641 | 195.5641 | 7627 | 0.023296 | 0.00011912 | 2014-09-30 | C | 0.023296 | 0.00011912 | 2015 | 2014-09-30 | C | 39 | 0.023296 | 0.00011912
1 | 1970005 | 2014-09-30 09:14 | 2014-09-30 15:28 | 373.9 | 10 | 3739 | 0.011435 | 3.0584e-05 | NAPA ID:02207 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5666 | Upgrade network poles and cross arms between isolation points. Works location: Mohakau Rd and Ohura Rd. WO IR1872. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 373.9 | 370.9 | 3709 | 0.011329 | 3.0544e-05 | 2014-09-30 | B | 0.0056644 | 1.5272e-05 | 2015 | 2014-09-30 | B | 10 | 0.011329 | 3.0544e-05
1 | 1696054 | 2014-09-30 10:00 | 2014-09-30 14:12 | 252 | 44 | 11088 | 0.033912 | 0.00013457 | NAPA ID:02543 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/182 | Install New LV panel @ T3/182 due to Overload. Works location: Aotea St, Feilding. WO 10149582 | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 252 | 249 | 10956 | 0.033464 | 0.00013439 | 2014-09-30 | B | 0.016732 | 6.7197e-05 | 2015 | 2014-09-30 | B | 44 | 0.033464 | 0.00013439
1 | 1700156 | 2014-09-30 10:15 | 2014-09-30 12:20 | 125 | 52 | 6500 | 0.01988 | 0.00015904 | NAPA ID:02567 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 775663 | Replace pole 775663 and transformer Y77. Works location: Ohura Rd, Raetihi. WO 10145871. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 125 | 122 | 6344 | 0.019377 | 0.00015883 | 2014-09-30 | B | 0.0096886 | 7.9415e-05 | 2015 | 2014-09-30 | B | 52 | 0.019377 | 0.00015883
1 | 2069715 | 2014-09-30 10:55 | 2014-09-30 15:04 | 249.2667 | 1 | 249.2667 | 0.00076236 | 3.0584e-06 | Restore Supply on Device T3/503 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P07620 | Replaced 2 x 3 amp hv fuses on fuse K75. Pole P07620. Cause: line clash due to high winds the other day. Also replaced the candle part of fuse holder replaced. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Po | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 249.2667 | 246.2667 | 246.2667 | 0.0007522 | 3.0544e-06 | 2014-09-30 | C | 0.0007522 | 3.054e-06 | 2015 | 2014-09-30 | C | 1 | 0.0007522 | 3.0544e-06
1 | 2069729 | 2014-09-30 11:06 | 2014-09-30 19:28 | 501.6833 | 1 | 501.6833 | 0.0015344 | 3.0584e-06 | Restore Supply on Device X1100 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1100 | Blown transformer to be changed, making safe, no crews or trucks available. Replaced transformer. 3x HV fuse links replaced 3a ddo fuse links. Nothing else repaired or replaced. Adjacent assets all good. | F3 | NGATAWA | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 501.6833 | 498.6833 | 498.6833 | 0.0015232 | 3.0544e-06 | 2014-09-30 | C | 0.0015232 | 3.054e-06 | 2015 | 2014-09-30 | C | 1 | 0.0015232 | 3.0544e-06
1 | 1693375 | 2014-10-01 08:56 | 2014-10-01 15:27 | 390.9333 | 2 | 781.8667 | 0.0023913 | 6.1168e-06 | NAPA ID:02414 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B51 | Change 7 x 11kv poles 1 x TX. Works location: SHW 56. WO 1156813. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 390.9333 | 387.9333 | 775.8667 | 0.0023698 | 6.1088e-06 | 2014-10-01 | B | 0.0011849 | 3.054e-06 | 2015 | 2014-10-01 | B | 2 | 0.0023698 | 6.1088e-06
1 | 1727267 | 2014-10-01 09:00 | 2014-10-01 15:07 | 367 | 119 | 43673 | 0.13357 | 0.00036395 | NAPA ID:02279 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Links 4100 | Replace 11kv poles and X arms between links 4100 and the end of the line also install temp links at pole 792820 isolation for next shutdown no 4250. Works location: Hanui Rd and Ruatangata Rd. WO 10141993. | F3 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 367 | 364 | 43316 | 0.13231 | 0.00036348 | 2014-10-01 | B | 0.066153 | 0.00018174 | 2015 | 2014-10-01 | B | 119 | 0.13231 | 0.00036348
1 | 1855916 | 2014-10-01 09:02 | 2014-10-01 15:56 | 413.6667 | 95 | 39298.3333 | 0.12019 | 0.00029055 | NAPA ID:02522 TP_WAIKINO GXP > PAEROA SUB > WILLOUGHBY ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2216 | Replace poles and crossarms at various sites. Works location: Miller Ave, Paeroa. WO 10148669. | F2 | WILLOUGHBY ST | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 413.6667 | 410.6667 | 39013.3333 | 0.11916 | 0.00029017 | 2014-10-01 | B | 0.059582 | 0.00014509 | 2015 | 2014-10-01 | B | 95 | 0.11916 | 0.00029017
1 | 2071319 | 2014-10-01 09:26 | 2014-10-01 11:22 | 116 | 1833 | 149695 | 0.45783 | 0.0056061 | Restore Supply on Device 14 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | CB 14 | High hit L/V which went up into H/V CB 12 & CB 14 OMS number 2073166 is Number for CB 12. removed L/V off H/V Then Liven up | F3 | PIONEER | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 81.6667 | 78.6667 | 144196 | 0.44044 | 0.0055988 | 2014-10-01 | C | 0.44044 | 0.0055988 | 2015 | 2014-10-01 | C | 1833 | 0.44044 | 0.0055988
1 | 1857788 | 2014-10-01 09:51 | 2014-10-01 15:29 | 338 | 4 | 1352 | 0.004135 | 1.2234e-05 | NAPA ID:02597 TP_TAURANGA 33 GXP > AONGATETE SUB > MATAKANA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-080 | Replace 200kVA unitised transformer TC2-080 with 100kVA unitised. Works location: Matahui Rd, Aongatete. WO 10161621. | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 338 | 335 | 1340 | 0.0040929 | 1.2218e-05 | 2014-10-01 | B | 0.0020465 | 6.109e-06 | 2015 | 2014-10-01 | B | 4 | 0.0040929 | 1.2218e-05
1 | 1908784 | 2014-10-01 10:23 | 2014-10-01 16:05 | 342 | 293 | 55692 | 0.17033 | 0.00089612 | NAPA ID:02365 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 7 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Moturoa CB7 | 11kV network pole replacement poles 750956 and 750957 Lorna Street. | F2 | MOTUROA 7 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 190.0751 | 187.0751 | 54813 | 0.16742 | 0.00089495 | 2014-10-01 | B | 0.083711 | 0.00044747 | 2015 | 2014-10-01 | B | 293 | 0.16742 | 0.00089495
1 | 2053914 | 2014-10-01 11:10 | 2014-10-01 12:23 | 72.8833 | 304 | 22156.5333 | 0.067764 | 0.00092976 | NAPA ID:03209 TP_KOPU GXP > THAMES SUB > THAMES COAST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RC9228/2 | Remove RC9228/2 as hole found in top of Recloser body. DNO140708. Works location: Thames Coast, Te Puru. WO 10148807. | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 72.8833 | 69.8833 | 21244.5333 | 0.06489 | 0.00092854 | 2014-10-01 | B | 0.032445 | 0.00046427 | 2015 | 2014-10-01 | B | 304 | 0.06489 | 0.00092854
1 | 1662237 | 2014-10-01 22:00 | 2014-10-01 23:57 | 116.9333 | 290 | 33910.6667 | 0.10371 | 0.00088694 | NAPA ID:02311 TP_GREYTOWN GXP > KEMPTON SUB > WEST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1431 | Transfer 11kV conductors and transformer T1431 to new pole structure. Isolate 11kv line at T1431 by opening S314 and S310. Works location: West St, Greytown. WO 10140873 IR6938 | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 116.9333 | 113.9333 | 33040.6667 | 0.10092 | 0.00088578 | 2014-10-01 | B | 0.05046 | 0.00044289 | 2015 | 2014-10-01 | B | 290 | 0.10092 | 0.00088578
1 | 2400517 | 2014-10-02 02:36 | 2014-10-03 07:18 | 1722 | 1133 | 152048 | 0.46503 | 0.0034652 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | P14896 | This job was created because when OMS did the update at 03:00 the job created when CB 8 tripped was cancelled- Tripping OMS number was 2084483. CB 8 tripped on E/F flags, auto backfeed system closed at Recloser F48 to Recloser F26, line was patrolled an | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 134.1995 | 131.1995 | 148649 | 0.45404 | 0.0034607 | 2014-10-02 | C | 0.45404 | 0.0034607 | 2015 | 2014-10-02 | C | 1133 | 0.45404 | 0.0034607
1 | 1861482 | 2014-10-02 08:45 | 2014-10-02 14:08 | 323 | 41 | 13243 | 0.040503 | 0.0001254 | NAPA ID:02314 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 386273 | REPLACE HV POLES. INSTALL TEMP ABS 21 ON POLE 386273 DURING SHUTDOWN. Works location: Maketu Rd. WO 10145449 | F3 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 323 | 320 | 13120 | 0.040074 | 0.00012523 | 2014-10-02 | B | 0.020037 | 6.2616e-05 | 2015 | 2014-10-02 | B | 41 | 0.040074 | 0.00012523
1 | 1874883 | 2014-10-02 08:48 | 2014-10-02 13:35 | 287 | 44 | 12628 | 0.038622 | 0.00013457 | NAPA ID:02328 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 8202 | Replace 33kV xarms and broken 33kV insulators on Carrington no. 2 line. Works location: Paraite Rd. WO 10144419. | F1 | BELL BLOCK 3 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 287 | 284 | 12496 | 0.038168 | 0.00013439 | 2014-10-02 | B | 0.019084 | 6.7197e-05 | 2015 | 2014-10-02 | B | 44 | 0.038168 | 0.00013439
1 | 1697160 | 2014-10-02 09:00 | 2014-10-02 14:42 | 342 | 8 | 2736 | 0.0083678 | 2.4467e-05 | NAPA ID:01835 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 1198 | Install new 11kV poles between Fuses 1198 & Transformer X1585 & X50 also reconductor from pole 792974 & X50. Works location: Whangaehu Beach Rd. WO 10140836. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 342 | 339 | 2712 | 0.0082836 | 2.4435e-05 | 2014-10-02 | B | 0.0041418 | 1.2218e-05 | 2015 | 2014-10-02 | B | 8 | 0.0082836 | 2.4435e-05
1 | 1696167 | 2014-10-02 09:08 | 2014-10-02 15:05 | 357 | 57 | 20349 | 0.062236 | 0.00017433 | NAPA ID:02514 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 791168 | Trimming & felling trees near 11kv lines between poles 791168. Works location: Mangamahu Rd. PPPD 491306. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 357 | 354 | 20178 | 0.061632 | 0.0001741 | 2014-10-02 | B | 0.030816 | 8.7051e-05 | 2015 | 2014-10-02 | B | 57 | 0.061632 | 0.0001741
1 | 1855535 | 2014-10-02 12:30 | 2014-10-02 15:33 | 183 | 40 | 7320 | 0.022388 | 0.00012234 | NAPA ID:02643 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC800 | To replace 11kV and LV cross arms. Works location: SH29 Te Poi. WO 10160662. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 183 | 180 | 7200 | 0.021992 | 0.00012218 | 2014-10-02 | B | 0.010996 | 6.1088e-05 | 2015 | 2014-10-02 | B | 40 | 0.021992 | 0.00012218
1 | 2153565 | 2014-10-02 19:25 | 2014-10-02 20:57 | 92.2 | 1 | 92.2 | 0.00028199 | 3.0584e-06 | Restore Supply on Device 1573 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 755015 | Moturoa CB3. Fuses 6463 opened and tagged. Faultman found a broken 11KV cross arm at pole 755015 while attending a fault call, line was isolated at Fuses 6463 to replace the cross arm. 1 X 11KV cross arm with all it's hardware. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 92.2 | 89.2 | 89.2 | 0.00027245 | 3.0544e-06 | 2014-10-02 | C | 0.00027246 | 3.054e-06 | 2015 | 2014-10-02 | C | 1 | 0.00027245 | 3.0544e-06
1 | 2153245 | 2014-10-02 19:26 | 2014-10-02 20:31 | 65.2167 | 1 | 65.2167 | 0.00019946 | 3.0584e-06 | Restore Supply on Device T9/257 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | P04221 | Faultman found a floating wire at pole P04221 while attending a fault call, line was isolated at Fuses V80 to rebind in the conductor. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 65.2167 | 62.2167 | 62.2167 | 0.00019004 | 3.0544e-06 | 2014-10-02 | C | 0.00019004 | 3.054e-06 | 2015 | 2014-10-02 | C | 1 | 0.00019004 | 3.0544e-06
1 | 2153602 | 2014-10-02 19:37 | 2014-10-02 23:15 | 218.15 | 237 | 21751.4333 | 0.066525 | 0.00072485 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 780231 | CB 6 tripped on A phase O/C and E/F flags, line was patrolled and sectionalised, back feed was closed at VS 516 up to ABS 249, line down was found at pole 780231, line was isolated at ABS's 053 and 249 to make the repairs. 4 meters of 25mm Bear copper con | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 91.7782 | 88.7782 | 21040.4333 | 0.064266 | 0.0007239 | 2014-10-02 | C | 0.064266 | 0.0007239 | 2015 | 2014-10-02 | C | 237 | 0.064266 | 0.0007239
1 | 2155212 | 2014-10-02 21:00 | 2014-10-02 22:11 | 70.9333 | 759 | 53838.4 | 0.16466 | 0.0023213 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 222247 | WBY CB4 tripped A/R, L/O. Feeder patrolled/sectionalised & possum found on lines at pole 222247 (had traversed the guard). Possum removed, all service restored, Ted Glasgow & Clint Johnstone attended. No materials. | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 70.9333 | 67.9333 | 51561.4 | 0.15749 | 0.0023183 | 2014-10-02 | C | 0.15749 | 0.0023183 | 2015 | 2014-10-02 | C | 759 | 0.15749 | 0.0023183
1 | 2156557 | 2014-10-02 21:46 | 2014-10-02 23:40 | 113.0833 | 1 | 113.0833 | 0.00034586 | 3.0584e-06 | Restore Supply on Device X1874 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 612 | Faultman found blown fuses at Fuses 612, line patrolled was carried out and no fault was found, fuses were reloaded. 2 X 8 amp rewirable were used. Email sent to Jo as appears has SAIDI component. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 113.0833 | 110.0833 | 110.0833 | 0.00033624 | 3.0544e-06 | 2014-10-02 | C | 0.00033624 | 3.054e-06 | 2015 | 2014-10-02 | C | 1 | 0.00033624 | 3.0544e-06
1 | 2156673 | 2014-10-03 06:58 | 2014-10-03 10:56 | 238.25 | 7 | 405.15 | 0.0012391 | 2.1409e-05 | Restore Supply on Device T2378 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7408 | 2 x 11kV Fuses @ 7408 found blown - OMS 2157479 created - line patrol being carried out - branch removed from line. REMOVED BRANCH AND REPLACED 2X 10 AMP HV FUSES LINK 7408 DUE TO WIND AND TREES. Email sent to JO | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 57.8786 | 54.8786 | 384.15 | 0.0011734 | 2.1381e-05 | 2014-10-03 | C | 0.0011734 | 2.1381e-05 | 2015 | 2014-10-03 | C | 7 | 0.0011734 | 2.1381e-05
1 | 2156915 | 2014-10-03 07:19 | 2014-10-03 12:05 | 286 | 50 | 6083.55 | 0.018606 | 0.00015292 | Restore Supply on Device C218 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837457 | Sectionaliser C218/2 tripped to L/O - line sectionalised & patrolled - broken conductor repaired at pole 837457 - all supply restored following repairs. Joe Mathews attended. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 121.671 | 118.671 | 5933.55 | 0.018124 | 0.00015272 | 2014-10-03 | C | 0.018124 | 0.00015272 | 2015 | 2014-10-03 | C | 50 | 0.018124 | 0.00015272
1 | 2156917 | 2014-10-03 08:29 | 2014-10-03 12:36 | 246.4833 | 336 | 72061.7833 | 0.2204 | 0.0010276 | Restore Supply on Device L10 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P34076 | Recloser L10 tripped to L/O - no flags available - Line sectionalised & patrolled - conductor found pulled out of termination deadend on pole P34076 - deadend replaced all supply restored - Anjay Prasad & Shaz Kan attended. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 214.4696 | 211.4696 | 71053.7833 | 0.21703 | 0.0010263 | 2014-10-03 | C | 0.21703 | 0.0010263 | 2015 | 2014-10-03 | C | 336 | 0.21703 | 0.0010263
1 | 2157280 | 2014-10-03 09:03 | 2014-10-03 14:12 | 308.4667 | 11 | 3393.1333 | 0.010378 | 3.3643e-05 | Restore Supply on Device B6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB23 | To replace 11kV & LV Crossarms. Work Location: Kerr Road. Work Order 10160662. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 308.4667 | 305.4667 | 3360.1333 | 0.010263 | 3.3599e-05 | 2014-10-03 | C | 0.010263 | 3.3599e-05 | 2015 | 2014-10-03 | C | 11 | 0.010263 | 3.3599e-05
1 | 2379635 | 2014-10-03 09:11 | 2014-10-03 12:11 | 180 | 8 | 1440 | 0.0044041 | 2.4467e-05 | Restore Supply on Device FP1449 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1449 | Parent Job 1857740. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 1416 | 0.0043251 | 2.4435e-05 | 2014-10-03 | C | 0.0043251 | 2.4435e-05 | 2015 | 2014-10-03 | C | 8 | 0.0043251 | 2.4435e-05
1 | 1857740 | 2014-10-03 09:40 | 2014-10-03 13:10 | 210.85 | 8 | 1686.8 | 0.0051589 | 2.4467e-05 | NAPA ID:02644 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1449 | To replace 11kV and LV cross arms. Works location: Kerr Rd WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 210.85 | 207.85 | 1662.8 | 0.0050789 | 2.4435e-05 | 2014-10-03 | B | 0.0025394 | 1.2218e-05 | 2015 | 2014-10-03 | B | 8 | 0.0050789 | 2.4435e-05
1 | 2157456 | 2014-10-03 10:05 | 2014-10-03 11:32 | 87.7333 | 1 | 87.7333 | 0.00026833 | 3.0584e-06 | Restore Supply on Device T8/243 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | T8/243 | Replaced 2 x 10amp HV fuses ov at F11. Trees in the line Powerco know about it and Treescape knows about it - will have to keep attending until someone cuts trees. Email sent to Jo, as job appears to have SAIDI component. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.7333 | 84.7333 | 84.7333 | 0.00025881 | 3.0544e-06 | 2014-10-03 | C | 0.00025881 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00025881 | 3.0544e-06
1 | 2157522 | 2014-10-03 10:34 | 2014-10-03 12:39 | 124.9333 | 1 | 124.9333 | 0.0003821 | 3.0584e-06 | Restore Supply on Device X2292 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuse 2977 | Replaced 2 x 5 amp HV fuse links at Fuse 2977. Cause: weather. 2 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are ok / up to Powerco standard. 12.26pm - e-map update. Cannot verify or restore transformer | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 124.9333 | 121.9333 | 121.9333 | 0.00037244 | 3.0544e-06 | 2014-10-03 | C | 0.00037244 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00037244 | 3.0544e-06
1 | 2157803 | 2014-10-03 10:58 | 2014-10-03 12:58 | 120.3 | 126 | 10960.5667 | 0.033522 | 0.00038536 | Restore Supply on Device 573 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 282 | Recloser 573 on CB 282 feeder tripped to L/O - line patrolled & sectionalised - no fault found - all supply restored. Gary Fisher attended. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 86.9886 | 83.9886 | 10582.5667 | 0.032324 | 0.00038486 | 2014-10-03 | C | 0.032324 | 0.00038486 | 2015 | 2014-10-03 | C | 126 | 0.032324 | 0.00038486
1 | 2157539 | 2014-10-03 11:00 | 2014-10-03 13:49 | 168.8333 | 129 | 21779.5 | 0.066611 | 0.00039454 | Restore Supply on Device C437 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 845289 | 1.17pm working through control and someone had rejected controls 2r request by mistake as thought Nevill pope attending but Brad keating is doing the work so 2r request put through as requested by talia to replace the rejected 2r found recloser in off | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 168.8333 | 165.8333 | 21392.5 | 0.065342 | 0.00039402 | 2014-10-03 | C | 0.065342 | 0.00039402 | 2015 | 2014-10-03 | C | 129 | 0.065342 | 0.00039402
1 | 2157437 | 2014-10-03 13:00 | 2014-10-03 13:28 | 28 | 5 | 140 | 0.00042818 | 1.5292e-05 | Restore Supply on Device T8/90 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12910 | HT jumper at top of DDO fuse at transformer. Repaired jumper; worked through control -also repaired other 2 DDO fuses while there - just the connection onto main line cause age deterioration. No other assets repaired or replaced and all adjacent assets | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 125 | 0.0003818 | 1.5272e-05 | 2014-10-03 | C | 0.0003818 | 1.5272e-05 | 2015 | 2014-10-03 | C | 5 | 0.0003818 | 1.5272e-05
1 | 2158261 | 2014-10-03 13:20 | 2014-10-03 13:40 | 20 | 2 | 40 | 0.00012234 | 6.1168e-06 | Restore Supply on Device PU241 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 704883 | Replaced pole 704883. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 20 | 17 | 34 | 0.00010385 | 6.1088e-06 | 2014-10-03 | C | 0.00010385 | 6.109e-06 | 2015 | 2014-10-03 | C | 2 | 0.00010385 | 6.1088e-06
1 | 2158133 | 2014-10-03 13:23 | 2014-10-03 18:31 | 308.5833 | 119 | 10896.3333 | 0.033326 | 0.00036395 | Restore Supply on Device RC36 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | M2440 | 1.52pm - Jason from Downers 021 284 1173 phoned to advise he is 10 km up Leslie Road, Putaruru and he has found a broken power line due to tree branches that came down on the lines. Jason is waiting onsite till FM arrives as he needs to remove the tree br | F4 | TAUMANGI RD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 91.5658 | 88.5658 | 10539.3333 | 0.032192 | 0.00036348 | 2014-10-03 | C | 0.032192 | 0.00036348 | 2015 | 2014-10-03 | C | 119 | 0.032192 | 0.00036348
1 | 2158754 | 2014-10-03 13:52 | 2014-10-03 17:56 | 244.1833 | 557 | 44915.9 | 0.13737 | 0.0017035 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB6 |  | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 80.639 | 77.639 | 43244.9 | 0.13209 | 0.0017013 | 2014-10-03 | C | 0.13209 | 0.0017013 | 2015 | 2014-10-03 | C | 557 | 0.13209 | 0.0017013
1 | 2159729 | 2014-10-03 14:06 | 2014-10-04 17:49 | 1663.05 | 155 | 78986.8 | 0.24157 | 0.00047406 | Restore Supply on Device RC18 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 263789 | Recloser RC18 tripped L/O. Feeder sectionalised & lines down found at pole 263789 spanning a gully. Attempts made to repair during the evening but strong wind made unsafe to carry out. Will reassess in morning. Lines repaired by Andy Wreaks on the 04/10/ | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 509.5923 | 506.5923 | 78521.8 | 0.23984 | 0.00047344 | 2014-10-03 | C | 0.23984 | 0.00047344 | 2015 | 2014-10-03 | C | 155 | 0.23984 | 0.00047344
1 | 2159923 | 2014-10-03 14:20 | 2014-10-03 15:15 | 55 | 18 | 990 | 0.0030278 | 5.5052e-05 | Restore Supply on Device LI773 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726816 | Tree branch removed from line at pole 726816 using sticks. Brett Barnsley attended. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 936 | 0.0028589 | 5.498e-05 | 2014-10-03 | C | 0.0028589 | 5.498e-05 | 2015 | 2014-10-03 | C | 18 | 0.0028589 | 5.498e-05
1 | 2165010 | 2014-10-03 15:39 | 2014-10-03 20:01 | 261.95 | 816 | 31162.4833 | 0.095308 | 0.0024957 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 389756 | trees on lines, removed trees and put line back up. used 20 meters of conductor and 6x full tension links. nothing else repaired or replaced. adjacent assets all good. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 38.1893 | 35.1893 | 28714.4833 | 0.087706 | 0.0024924 | 2014-10-03 | C | 0.087706 | 0.0024924 | 2015 | 2014-10-03 | C | 816 | 0.087706 | 0.0024924
1 | 2166410 | 2014-10-03 15:45 | 2014-10-03 18:00 | 135.1 | 1090 | 53573.4333 | 0.16385 | 0.0033337 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P39533 | 4:10pm - Contact reporting lines down outside 64 HENAGHANS ROAD - Advised Control. HV lines down at pole P39533. Replaced 5 meter of o/h line and x4 sleeves. 1 span on all phases. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 49.1499 | 46.1499 | 50303.4333 | 0.15365 | 0.0033293 | 2014-10-03 | C | 0.15365 | 0.0033293 | 2015 | 2014-10-03 | C | 1090 | 0.15365 | 0.0033293
1 | 2168058 | 2014-10-03 16:24 | 2014-10-03 21:02 | 277.45 | 1 | 277.45 | 0.00084856 | 3.0584e-06 | Restore Supply on Device T5/137 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/137 | FM needs to replace the transformer. Dave whale to assist. Requesting 2R to replace a transformer. Dave Whale to assist. replaced transformer. nothing else repaired or replaced. adjacent assets all good. Email sent to Jo, as job appears to have SAIDI | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 277.45 | 274.45 | 274.45 | 0.00083829 | 3.0544e-06 | 2014-10-03 | C | 0.00083829 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00083829 | 3.0544e-06
1 | 2168329 | 2014-10-03 16:53 | 2014-10-04 12:05 | 1151.35 | 1 | 1151.35 | 0.0035213 | 3.0584e-06 | Restore Supply on Device T5/212 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P12135 | 3x DDO fuse assembly's require replacing, nick does not have the gear for this right now will re attend in the morning to replace, customer advised 4/10/14 12:02pm - Didn't need to replace assemblies, found some spare parts which restored the full power | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1151.35 | 1148.35 | 1148.35 | 0.0035075 | 3.0544e-06 | 2014-10-03 | C | 0.0035075 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0035075 | 3.0544e-06
1 | 2168332 | 2014-10-03 16:55 | 2014-10-03 19:37 | 161.4167 | 413 | 22928.1333 | 0.070124 | 0.0012631 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 228327 | PKW CB3 tripped O/C, E/F L/O. Feeder sectionalised & lines down found at pole 228327 beyond isolation point of ABS SF7 011. (no back feeds) . 3 x lines repaired all service restored. Clint Johnstone & Ted Glasgow attended. Strong winds suspected of bring | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 55.5161 | 52.5161 | 21689.1333 | 0.066248 | 0.0012615 | 2014-10-03 | C | 0.066248 | 0.0012615 | 2015 | 2014-10-03 | C | 413 | 0.066248 | 0.0012615
1 | 2169842 | 2014-10-03 17:05 | 2014-10-03 18:12 | 67.2167 | 181 | 8715.4833 | 0.026656 | 0.00055357 | Restore Supply on Device 12 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | KAIRANGA CB12 | Kairanga CB12 tripped (A & C Phase O/C) L/O. Line patrolled and tree branch removed from line at pole P43765. auto reclose also on OMS Job ID 2169662 | F3 | AWAPUNI | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 48.1518 | 45.1518 | 8172.4833 | 0.024962 | 0.00055285 | 2014-10-03 | C | 0.024962 | 0.00055285 | 2015 | 2014-10-03 | C | 181 | 0.024962 | 0.00055285
1 | 2171866 | 2014-10-03 17:17 | 2014-10-03 19:21 | 124.55 | 854 | 17686.1 | 0.054092 | 0.0026119 | Restore Supply on Device 575 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND |  | Recloser 575 tripped O.C & E/F. Line patrolled and no cause of fault located. 1 x HT Fuse replaced at X4129. Recloser in and holding - power restored. Ben Englebretsen and James Prime attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 20.7097 | 17.7097 | 15124.1 | 0.046195 | 0.0026085 | 2014-10-03 | C | 0.046195 | 0.0026085 | 2015 | 2014-10-03 | C | 854 | 0.046195 | 0.0026085
1 | 2171818 | 2014-10-03 17:17 | 2014-10-04 13:24 | 1207.55 | 1 | 1207.55 | 0.0036932 | 3.0584e-06 | Restore Supply on Device X2663 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 781620 | WAS 11KV LINE DOWN RE HUNG LINE AT POLE 781620 WAS DUE TO WEATHER. Email sent to Jo, as job appears to have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1207.55 | 1204.55 | 1204.55 | 0.0036792 | 3.0544e-06 | 2014-10-03 | C | 0.0036792 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0036792 | 3.0544e-06
1 | 2172904 | 2014-10-03 17:35 | 2014-10-03 20:09 | 154.3167 | 1 | 154.3167 | 0.00047197 | 3.0584e-06 | Restore Supply on Device X2921 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2921 | replaced 2x 3a ddo fuse links due to lightning.nothing else repaired or replaced. adjacent assets all good. Email sent to Jo, as job appears to have SAIDI component. | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 154.3167 | 151.3167 | 151.3167 | 0.00046219 | 3.0544e-06 | 2014-10-03 | C | 0.00046218 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00046219 | 3.0544e-06
1 | 2172930 | 2014-10-03 17:51 | 2014-10-03 18:36 | 44.4667 | 11 | 489.1333 | 0.001496 | 3.3643e-05 | Restore Supply on Device 6061 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 736027 | Repaired conductor @ pole 736027 | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 44.4667 | 41.4667 | 456.1333 | 0.0013932 | 3.3599e-05 | 2014-10-03 | C | 0.0013932 | 3.3599e-05 | 2015 | 2014-10-03 | C | 11 | 0.0013932 | 3.3599e-05
1 | 2172942 | 2014-10-03 17:52 | 2014-10-04 00:26 | 393.9833 | 1 | 393.9833 | 0.001205 | 3.0584e-06 | Restore Supply on Device X2227 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | x2227 | 2 x 2 amps fuses replace. No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. Email sent to Jo, as job appears to have SAIDI component. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 393.9833 | 390.9833 | 390.9833 | 0.0011942 | 3.0544e-06 | 2014-10-03 | C | 0.0011942 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0011942 | 3.0544e-06
1 | 2172992 | 2014-10-03 18:15 | 2014-10-03 23:55 | 339.8667 | 2 | 539.3167 | 0.0016495 | 6.1168e-06 | Restore Supply on Device X2428 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X2428 | Replaced 3 x 2 amp fuses. No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. Email sent to Jo, as job appears to have SAIDI component | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 269.6583 | 266.6583 | 533.3167 | 0.001629 | 6.1088e-06 | 2014-10-03 | C | 0.001629 | 6.109e-06 | 2015 | 2014-10-03 | C | 2 | 0.001629 | 6.1088e-06
1 | 2172996 | 2014-10-03 18:16 | 2014-10-03 20:11 | 114.7833 | 105 | 12052.25 | 0.036861 | 0.00032113 | Restore Supply on Device 4445 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Recloser 4445 | kimbolton Recloser 4445 tripped L/O. NOC disabled Auto Reclose. Line patrolled - no fault located. Shazil Khan and Shane Robinson attended. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 114.7833 | 111.7833 | 11737.25 | 0.035851 | 0.00032071 | 2014-10-03 | C | 0.035851 | 0.00032071 | 2015 | 2014-10-03 | C | 105 | 0.035851 | 0.00032071
1 | 2173104 | 2014-10-03 18:17 | 2014-10-04 15:49 | 1292.3 | 1 | 1292.3 | 0.0039524 | 3.0584e-06 | Restore Supply on Device X1637 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1637 | 2 X 2 AMP HV FUSES DUE TO LIGHTNING No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. Email sent to Jo, as job appears to have SAIDI component | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1292.3 | 1289.3 | 1289.3 | 0.0039381 | 3.0544e-06 | 2014-10-03 | C | 0.0039381 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0039381 | 3.0544e-06
1 | 2173120 | 2014-10-03 18:32 | 2014-10-04 16:59 | 1346.6833 | 1 | 1346.6833 | 0.0041187 | 3.0584e-06 | Restore Supply on Device X2333 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 790756 | Please attend to 50 Longacre Rd not 417 3 x 2 amp hv tx fuses due to lightning No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. Email sent to Jo, as job appears to have SAIDI component | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1346.6833 | 1343.6833 | 1343.6833 | 0.0041042 | 3.0544e-06 | 2014-10-03 | C | 0.0041042 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0041042 | 3.0544e-06
1 | 2372014 | 2014-10-03 18:55 | 2014-10-03 22:17 | 202 | 480 | 65604 | 0.20064 | 0.001468 | Restore Supply on Device 262 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771842 | TP Waverley CB262 tripped. Line patrolled and line found down. Isolated beyond Fuses 1257 and repaired. Ben Englebretsen attended. | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 136.675 | 133.675 | 64164 | 0.19598 | 0.0014661 | 2014-10-03 | C | 0.19598 | 0.0014661 | 2015 | 2014-10-03 | C | 480 | 0.19598 | 0.0014661
1 | 2173963 | 2014-10-03 19:02 | 2014-10-04 01:16 | 374.2 | 2 | 745.45 | 0.0022799 | 6.1168e-06 | Restore Supply on Device X826 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | x826 | 3 x 3amp fuses replaced No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. Email sent to Jo, as job appears to have SAIDI component | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 372.725 | 369.725 | 739.45 | 0.0022586 | 6.1088e-06 | 2014-10-03 | C | 0.0022586 | 6.109e-06 | 2015 | 2014-10-03 | C | 2 | 0.0022586 | 6.1088e-06
1 | 2174350 | 2014-10-03 19:03 | 2014-10-03 20:17 | 74.5167 | 126 | 9315.6 | 0.028491 | 0.00038536 | Restore Supply on Device 573 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 573 | Recloser 573 L/O Reclosed | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 73.9333 | 70.9333 | 8937.6 | 0.027299 | 0.00038486 | 2014-10-03 | C | 0.027299 | 0.00038486 | 2015 | 2014-10-03 | C | 126 | 0.027299 | 0.00038486
1 | 2175283 | 2014-10-03 19:46 | 2014-10-04 00:30 | 283.7 | 1 | 283.7 | 0.00086767 | 3.0584e-06 | Restore Supply on Device X1086 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | x1087 | 3 x 3 amps fuses replaced. No other assets repaired or replaced on site, FM check adjacent assets and all up to Powerco Standard. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 283.7 | 280.7 | 280.7 | 0.00085738 | 3.0544e-06 | 2014-10-03 | C | 0.00085738 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00085738 | 3.0544e-06
1 | 2175286 | 2014-10-03 19:48 | 2014-10-03 23:10 | 202.8667 | 1 | 202.8667 | 0.00062045 | 3.0584e-06 | Restore Supply on Device X2446 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 790629 | 3 x 2 amp ht fuses pole 790629 Email sent to Jo, as appears may have SAIDI component. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 202.8667 | 199.8667 | 199.8667 | 0.00061048 | 3.0544e-06 | 2014-10-03 | C | 0.00061048 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00061048 | 3.0544e-06
1 | 2175336 | 2014-10-03 20:18 | 2014-10-04 16:09 | 1191.5833 | 1 | 1191.5833 | 0.0036444 | 3.0584e-06 | Restore Supply on Device X571 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 791832 | 2 X 3 AMP FUSES DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED OTHER ASSETS OK Email sent to Jo, as appears may have SAIDI component. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1191.5833 | 1188.5833 | 1188.5833 | 0.0036304 | 3.0544e-06 | 2014-10-03 | C | 0.0036304 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0036304 | 3.0544e-06
1 | 2175383 | 2014-10-03 20:41 | 2014-10-04 01:54 | 313.45 | 121 | 26392.0333 | 0.080718 | 0.00037007 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | A0262 | Maraetai CB3 (Old Cambridge Road). Recloser R9539 tripped E/F. Adverse weather - high winds. Materials Used 10metres of conductore (2 x HV Liens). A Wreaks attended. See 2175505 for details. | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 218.116 | 215.116 | 26029.0333 | 0.079504 | 0.00036959 | 2014-10-03 | C | 0.079504 | 0.00036959 | 2015 | 2014-10-03 | C | 121 | 0.079504 | 0.00036959
1 | 2175551 | 2014-10-03 21:10 | 2014-10-03 23:30 | 140 | 32 | 4480 | 0.013702 | 9.787e-05 | Restore Supply on Device 2719 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 781620 | Found line down near transformer X2260. Isolated at fuses 2719 Repaired & relivened. James Prime attended. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140 | 137 | 4384 | 0.013391 | 9.7742e-05 | 2014-10-03 | C | 0.013391 | 9.7742e-05 | 2015 | 2014-10-03 | C | 32 | 0.013391 | 9.7742e-05
1 | 2175618 | 2014-10-03 21:51 | 2014-10-04 13:13 | 921.5667 | 1 | 921.5667 | 0.0028185 | 3.0584e-06 | Restore Supply on Device X2981 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2981 | REPLACED 2 X 6 AMP DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS 5/10 emailed svs hub for update Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 921.5667 | 918.5667 | 918.5667 | 0.0028057 | 3.0544e-06 | 2014-10-03 | C | 0.0028057 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0028057 | 3.0544e-06
1 | 2175626 | 2014-10-03 21:53 | 2014-10-04 15:19 | 1045.6667 | 1 | 1045.6667 | 0.0031981 | 3.0584e-06 | Restore Supply on Device X1425 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1425 | 1 X 2 AMP FUSE LINK DUE TO LIGHTNING. SHOCK WAS NOT DUE TO NETWORK , WAS LIGHTING HIT TX AND CHILD WAS ON IPAD AND GOT SHOCK FROM THIS NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1045.6667 | 1042.6667 | 1042.6667 | 0.0031847 | 3.0544e-06 | 2014-10-03 | C | 0.0031847 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.0031847 | 3.0544e-06
1 | 2175650 | 2014-10-03 22:13 | 2014-10-03 23:36 | 82.6667 | 1 | 82.6667 | 0.00025283 | 3.0584e-06 | Restore Supply on Device X1306 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 807246 | replace 2 x 3 amp fuse links Email sent to Jo, as appears may have SAIDI component. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 82.6667 | 79.6667 | 79.6667 | 0.00024334 | 3.0544e-06 | 2014-10-03 | C | 0.00024334 | 3.054e-06 | 2015 | 2014-10-03 | C | 1 | 0.00024334 | 3.0544e-06
1 | 2176835 | 2014-10-03 22:14 | 2014-10-03 22:46 | 32.2167 | 393 | 12412.25 | 0.037962 | 0.001202 | Restore Supply on Device 6561-2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 6561 | Recloser 6561 L/O O/C A & B phase, reclosed | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 31.5833 | 28.5833 | 11233.25 | 0.034311 | 0.0012004 | 2014-10-03 | C | 0.034311 | 0.0012004 | 2015 | 2014-10-03 | C | 393 | 0.034311 | 0.0012004
1 | 2177819 | 2014-10-04 04:55 | 2014-10-04 08:49 | 234.2833 | 2 | 432.95 | 0.0013241 | 6.1168e-06 | Restore Supply on Device 5310E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718468 | broken LV insulator, replaced LV insulator and 2x 6a hv fuse at transformer. nothing else repaired or replaced. adjacent assets all good. Email sent to Jo, as appears may have SAIDI component. | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 216.475 | 213.475 | 426.95 | 0.0013041 | 6.1088e-06 | 2014-10-04 | C | 0.0013041 | 6.109e-06 | 2015 | 2014-10-04 | C | 2 | 0.0013041 | 6.1088e-06
1 | 2177824 | 2014-10-04 05:36 | 2014-10-04 08:00 | 143.2333 | 1 | 143.2333 | 0.00043807 | 3.0584e-06 | Restore Supply on Device 2353T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2353T | Faultman replaced 1 X 3Amp HV rewirable fuse. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 143.2333 | 140.2333 | 140.2333 | 0.00042833 | 3.0544e-06 | 2014-10-04 | C | 0.00042833 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00042833 | 3.0544e-06
1 | 2177834 | 2014-10-04 06:06 | 2014-10-04 15:35 | 569.4667 | 1 | 569.4667 | 0.0017417 | 3.0584e-06 | Restore Supply on Device X1031 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 785990 | No Power Have generator connected, please attend in morning 2 X 3 AMP HT FUSES DUE TO WIND ADJACENT ASSETS OK NO OTHER ASSETS REPAIRED OR REPLACED. Email sent to Jo, as appears may have SAIDI component. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 569.4667 | 566.4667 | 566.4667 | 0.0017302 | 3.0544e-06 | 2014-10-04 | C | 0.0017302 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0017302 | 3.0544e-06
1 | 2178168 | 2014-10-04 06:24 | 2014-10-04 15:20 | 535.55 | 125 | 38562.7833 | 0.11794 | 0.0003823 | Restore Supply on Device 2620 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 776141 | Recloser 2620 tripped on C phase O/C & E/F flags,line was sectionalised and patrolled and a tree was found that had come down through the lines at pole 77614, line was isolated at Fuses 740 . waiting on contractors to remove trees. 20 meters of squirrell | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 308.5023 | 305.5023 | 38187.7833 | 0.11664 | 0.0003818 | 2014-10-04 | C | 0.11664 | 0.0003818 | 2015 | 2014-10-04 | C | 125 | 0.11664 | 0.0003818
1 | 2178286 | 2014-10-04 06:49 | 2014-10-04 14:14 | 445.1167 | 1 | 445.1167 | 0.0013614 | 3.0584e-06 | Restore Supply on Device X1532 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | 786016 | 2 X 6 AMP HT FUSES DUE TO SNOW ADJACENT ASSETS OK NO OTHER ASSETS REPAIRED OR REPLACED. Email sent to Jo, as appears may have SAIDI component. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 445.1167 | 442.1167 | 442.1167 | 0.0013504 | 3.0544e-06 | 2014-10-04 | C | 0.0013504 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0013504 | 3.0544e-06
1 | 2178296 | 2014-10-04 07:00 | 2014-10-04 20:30 | 809.95 | 1 | 809.95 | 0.0024772 | 3.0584e-06 | Restore Supply on Device X1540 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1540 | 3 x glass 11kv fuses caused lightning. Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 809.95 | 806.95 | 806.95 | 0.0024648 | 3.0544e-06 | 2014-10-04 | C | 0.0024648 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0024648 | 3.0544e-06
1 | 2179098 | 2014-10-04 07:26 | 2014-10-04 09:00 | 94.05 | 393 | 33992.3333 | 0.10396 | 0.001202 | Restore Supply on Device 6561-2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | Recloser 6561/2 | Recloser 6561/2 tripped on B & C phase O/C flags, line was patrolled and sectionalised and patrolled and no fault was found, suspect tripping was due to lightning as at tripping lightning was striking in the area. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 86.4945 | 83.4945 | 32813.3333 | 0.10023 | 0.0012004 | 2014-10-04 | C | 0.10023 | 0.0012004 | 2015 | 2014-10-04 | C | 393 | 0.10023 | 0.0012004
1 | 2179492 | 2014-10-04 07:26 | 2014-10-04 17:32 | 605.35 | 1 | 605.35 | 0.0018514 | 3.0584e-06 | Restore Supply on Device X686 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X686 | 2 X 3 AMP FUSE LINKS AND HOLDER NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 605.35 | 602.35 | 602.35 | 0.0018398 | 3.0544e-06 | 2014-10-04 | C | 0.0018398 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0018398 | 3.0544e-06
1 | 2179501 | 2014-10-04 07:37 | 2014-10-04 19:59 | 741.1 | 1 | 741.1 | 0.0022666 | 3.0584e-06 | Restore Supply on Device X1541 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X1541 | 2 x 3 amp fuse links due to weather, nothing else repaired or replaced. Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 741.1 | 738.1 | 738.1 | 0.0022545 | 3.0544e-06 | 2014-10-04 | C | 0.0022545 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0022545 | 3.0544e-06
1 | 2179506 | 2014-10-04 07:40 | 2014-10-04 10:11 | 151.1333 | 1 | 151.1333 | 0.00046223 | 3.0584e-06 | Restore Supply on Device TC1265 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1265. | lines not down, lines had clashed and wound together blowing fuse. replaced 3A hv fuse link.nothing else repaired or replaced. adjacent assets all good. | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 151.1333 | 148.1333 | 148.1333 | 0.00045246 | 3.0544e-06 | 2014-10-04 | C | 0.00045246 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00045246 | 3.0544e-06
1 | 2179510 | 2014-10-04 07:46 | 2014-10-04 16:00 | 494.4 | 1 | 494.4 | 0.0015121 | 3.0584e-06 | Restore Supply on Device X1031 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | X1013 | 1 X 3 AMP HT FUSE DUE TO SNOW NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 494.4 | 491.4 | 491.4 | 0.0015009 | 3.0544e-06 | 2014-10-04 | C | 0.0015009 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0015009 | 3.0544e-06
1 | 2179513 | 2014-10-04 07:52 | 2014-10-04 14:00 | 368.1833 | 1 | 368.1833 | 0.0011261 | 3.0584e-06 | Restore Supply on Device X697 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X 697 | 3 X 2 AMP FUSE LINKS DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 368.1833 | 365.1833 | 365.1833 | 0.0011154 | 3.0544e-06 | 2014-10-04 | C | 0.0011154 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0011154 | 3.0544e-06
1 | 2180308 | 2014-10-04 08:30 | 2014-10-04 21:08 | 757.6167 | 1 | 757.6167 | 0.0023171 | 3.0584e-06 | Restore Supply on Device Z125 | 22000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 807081 | Replaced 2 x 2A HV fuses. All other assets appear okay; nothing else replaced. Email sent to Jo, as appears may have SAIDI component. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 757.6167 | 754.6167 | 754.6167 | 0.0023049 | 3.0544e-06 | 2014-10-04 | C | 0.0023049 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0023049 | 3.0544e-06
1 | 2070973 | 2014-10-04 08:50 | 2014-10-04 13:33 | 282.75 | 397 | 106930.3167 | 0.32704 | 0.0012142 | NAPA ID:03041 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > GREEN PARK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 216259 | REPLACE POLES AND 15 ARMS. Works location: Joyce Rd WO 10145644 IR6874 | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 269.3459 | 266.3459 | 105739.3167 | 0.32297 | 0.0012126 | 2014-10-04 | B | 0.16149 | 0.0006063 | 2015 | 2014-10-04 | B | 397 | 0.32297 | 0.0012126
1 | 2180707 | 2014-10-04 08:52 | 2014-10-04 20:08 | 676.3 | 1 | 676.3 | 0.0020684 | 3.0584e-06 | Restore Supply on Device X2041 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2041 | Replaced blown 2A HV OH transformer fuse due to lightning. All other assets okay; nothing else replaced. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 676.3 | 673.3 | 673.3 | 0.0020565 | 3.0544e-06 | 2014-10-04 | C | 0.0020565 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0020565 | 3.0544e-06
1 | 1969124 | 2014-10-04 09:43 | 2014-10-04 20:34 | 651 | 6 | 5839.6 | 0.01786 | 1.8351e-05 | NAPA ID:03032 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB 18 tauranga | Install and liven new RMU 9827 Tauranga Sub. TGA18. Cutaway ripple plant from TGA12 circuit cable. Connect ripple plant to new RMU 9827 on TGA 18. Isolate cables TGA CB's19 & 20 to assist cable ID | F2 | RIPPLE PLANT | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 973.2667 | 970.2667 | 5821.6 | 0.017782 | 1.8327e-05 | 2014-10-04 | B | 0.0088908 | 9.163e-06 | 2015 | 2014-10-04 | B | 6 | 0.017782 | 1.8327e-05
1 | 2180992 | 2014-10-04 10:14 | 2014-10-04 18:54 | 520.4167 | 1 | 520.4167 | 0.0015917 | 3.0584e-06 | Restore Supply on Device X2896 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2896 | Replaced 1 x blown 2A HV OH fuse due to lightning. All other assets okay; nothing else replaced. | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 520.4167 | 517.4167 | 517.4167 | 0.0015804 | 3.0544e-06 | 2014-10-04 | C | 0.0015804 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0015804 | 3.0544e-06
1 | 2180995 | 2014-10-04 10:14 | 2014-10-04 19:05 | 530.45 | 2 | 588.7 | 0.0018005 | 6.1168e-06 | Restore Supply on Device X260 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X260 | Replaced blown 2A HV OH transformer fuse, caused by lightning. All other assets okay; nothing else replaced. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 294.35 | 291.35 | 582.7 | 0.0017798 | 6.1088e-06 | 2014-10-04 | C | 0.0017798 | 6.109e-06 | 2015 | 2014-10-04 | C | 2 | 0.0017798 | 6.1088e-06
1 | 2181013 | 2014-10-04 10:18 | 2014-10-04 12:53 | 154.7667 | 1 | 154.7667 | 0.00047334 | 3.0584e-06 | Restore Supply on Device Y22 | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Y22 | REPLACED 2 X 2AMP FUSES DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. Email sent to Jo, as appears may have SAIDI component. | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 154.7667 | 151.7667 | 151.7667 | 0.00046356 | 3.0544e-06 | 2014-10-04 | C | 0.00046356 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00046356 | 3.0544e-06
1 | 2372496 | 2014-10-04 10:29 | 2014-10-04 17:53 | 444 | 261 | 104159 | 0.31856 | 0.00079825 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 709049 | Adverse Weather/Extreme Wind. Line patrolled and tree located through lines at pole 709049. Materials Used: 40 metre Rango conductor and 3 x sleeves used. NDR number to be forwarded at a later date. Brett Bensley attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 399.0766 | 396.0766 | 103376 | 0.31575 | 0.0007972 | 2014-10-04 | C | 0.31575 | 0.00079721 | 2015 | 2014-10-04 | C | 261 | 0.31575 | 0.0007972
1 | 2182289 | 2014-10-04 13:09 | 2014-10-04 18:11 | 302.1167 | 1 | 302.1167 | 0.000924 | 3.0584e-06 | Restore Supply on Device X20 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X20 | 2 AMP TX FUSE DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 302.1167 | 299.1167 | 299.1167 | 0.00091363 | 3.0544e-06 | 2014-10-04 | C | 0.00091363 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00091363 | 3.0544e-06
1 | 2182329 | 2014-10-04 13:24 | 2014-10-05 11:58 | 1354.2167 | 359 | 151779.0833 | 0.4642 | 0.001098 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | I1792 | CB 5 tripped to L/O - O/C & E/F flags - line sectionalised & patrolled broken conductor located beyond ABS 779 - all supply restored up to ABS 779 - repairs not completed until 05/10/14 due to access issues - all supply restored following repairs carried | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 422.783 | 419.783 | 150702.0833 | 0.46031 | 0.0010965 | 2014-10-04 | C | 0.46031 | 0.0010965 | 2015 | 2014-10-04 | C | 359 | 0.46031 | 0.0010965
1 | 2183328 | 2014-10-04 13:28 | 2014-10-04 16:56 | 207.95 | 481 | 56197.3 | 0.17188 | 0.0014711 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 758010 | CB 6 tripped on E/F flags line was sectionalised and patrolled and line was found down at pole 758010, line was isolated at ABS's 252 and 407 to repair the lines down. A backfeed from ABS 421 could not be put in place, faultman found the pentigfaf on the | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 116.8343 | 113.8343 | 54754.3 | 0.16724 | 0.0014692 | 2014-10-04 | C | 0.16724 | 0.0014692 | 2015 | 2014-10-04 | C | 481 | 0.16724 | 0.0014692
1 | 2184514 | 2014-10-04 14:34 | 2014-10-04 17:55 | 201.1667 | 1 | 201.1667 | 0.00061525 | 3.0584e-06 | Restore Supply on Device X946 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | FUSE 2853 , POLE 786843 | 1 x 15 amp LINE FUSE DUE TO SNOW NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 201.1667 | 198.1667 | 198.1667 | 0.00060528 | 3.0544e-06 | 2014-10-04 | C | 0.00060529 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00060528 | 3.0544e-06
1 | 2184523 | 2014-10-04 14:40 | 2014-10-04 18:17 | 216.6667 | 433 | 51723.8333 | 0.15819 | 0.0013243 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 200558 | Bethlehem CB2 Tripped E/F. Line patrolled. Lines down at Pole 200558. Two blown jumpers replaced. Paul Cooper attended. | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 119.4546 | 116.4546 | 50424.8333 | 0.15402 | 0.0013226 | 2014-10-04 | C | 0.15402 | 0.0013226 | 2015 | 2014-10-04 | C | 433 | 0.15402 | 0.0013226
1 | 2185167 | 2014-10-04 15:17 | 2014-10-04 19:30 | 253.2833 | 147 | 9933.2167 | 0.03038 | 0.00044959 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 386462 | Recloser 9463 Trip Flags E/F. Line Patrolled & sectionalized. fault found Beyond fuses SF6-012 at pole 386462. Tree Through Lines all 3 phases down. Faultman: Ted Glasgow. NDR 34371. Materials: 50m Conductor, Sleeves. | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 67.5729 | 64.5729 | 9492.2167 | 0.028993 | 0.000449 | 2014-10-04 | C | 0.028993 | 0.000449 | 2015 | 2014-10-04 | C | 147 | 0.028993 | 0.000449
1 | 2185405 | 2014-10-04 16:14 | 2014-10-05 14:11 | 1317.4333 | 1 | 1317.4333 | 0.0040293 | 3.0584e-06 | Restore Supply on Device TC4164 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | M13126 | 5/10 emailed svs hub for update Please call customer on arrival. Replaced 2 x ddo 3 amp fuses. cause: lines were clashing and customer advised contractors are regularly attending to replace fuses due to lines clashing. 2 out 3 phases. pole# M13126. Powe | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1317.4333 | 1314.4333 | 1314.4333 | 0.0040148 | 3.0544e-06 | 2014-10-04 | C | 0.0040148 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.0040148 | 3.0544e-06
1 | 2185415 | 2014-10-04 16:17 | 2014-10-04 20:29 | 252.65 | 527 | 53452.8667 | 0.16348 | 0.0016118 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D1572 | Broken conductor at pole D1572 feeder patrolled & sectionalized. Isolation ABS 821 Repaired lines. Andy Wreaks faultman. Materials: <5m conductor 2 sleeves | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 101.4286 | 98.4286 | 51871.8667 | 0.15844 | 0.0016097 | 2014-10-04 | C | 0.15844 | 0.0016097 | 2015 | 2014-10-04 | C | 527 | 0.15844 | 0.0016097
1 | 2186678 | 2014-10-04 17:00 | 2014-10-04 18:40 | 100 | 16 | 1600 | 0.0048935 | 4.8935e-05 | Restore Supply on Device B30 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36107 | Temp repair done to cross arm. Shifted 1 insulator to good area of wood. Nick Lake attended. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 1552 | 0.0047405 | 4.8871e-05 | 2014-10-04 | C | 0.0047405 | 4.8871e-05 | 2015 | 2014-10-04 | C | 16 | 0.0047405 | 4.8871e-05
1 | 2186676 | 2014-10-04 17:06 | 2014-10-04 18:51 | 105.6833 | 1 | 105.6833 | 0.00032322 | 3.0584e-06 | Restore Supply on Device X1538 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1538 | 3 x 3amp fuse links at tx, lightning. no other assets repaired or replaced, adjacent assets all good. Email sent to Jo, as appears may have SAIDI component. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 105.6833 | 102.6833 | 102.6833 | 0.00031364 | 3.0544e-06 | 2014-10-04 | C | 0.00031364 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00031364 | 3.0544e-06
1 | 2187205 | 2014-10-04 18:45 | 2014-10-04 19:08 | 23.45 | 149 | 3494.05 | 0.010686 | 0.0004557 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 5 | Outage occured because recloser 9665 didn't see fault. NOC opened Recloser 9665 & closed CB 5. Outage continued on OMS 2187023 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 23.45 | 20.45 | 3047.05 | 0.009307 | 0.00045511 | 2014-10-04 | C | 0.009307 | 0.00045511 | 2015 | 2014-10-04 | C | 149 | 0.009307 | 0.00045511
1 | 2187413 | 2014-10-04 19:43 | 2014-10-04 23:21 | 218.2 | 1 | 218.2 | 0.00066735 | 3.0584e-06 | Restore Supply on Device TC852 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TC852 | HV Fuse blown. 25 amp Fuse replaced. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F4 | PURIRI | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 218.2 | 215.2 | 215.2 | 0.00065731 | 3.0544e-06 | 2014-10-04 | C | 0.00065731 | 3.054e-06 | 2015 | 2014-10-04 | C | 1 | 0.00065731 | 3.0544e-06
1 | 2191872 | 2014-10-05 09:34 | 2014-10-05 17:25 | 471.3833 | 6 | 1403.9 | 0.0042937 | 1.8351e-05 | Restore Supply on Device TC2761 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuse fc2444 | replaced 1 x 10 amp hv link at fuse fc2444. cause: deterioration. oh/hv. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F4 | HORRELLS RD | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 233.9833 | 230.9833 | 1385.9 | 0.0042331 | 1.8327e-05 | 2014-10-05 | C | 0.0042331 | 1.8327e-05 | 2015 | 2014-10-05 | C | 6 | 0.0042331 | 1.8327e-05
1 | 2188170 | 2014-10-05 09:52 | 2014-10-05 12:53 | 180.2167 | 1 | 180.2167 | 0.00055118 | 3.0584e-06 | Restore Supply on Device TC3984 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP751 | 2x 8amp ddo hv fuse cause wind clash No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard Email sent to Jo, as appears may have SAIDI component. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 180.2167 | 177.2167 | 177.2167 | 0.00054129 | 3.0544e-06 | 2014-10-05 | C | 0.0005413 | 3.054e-06 | 2015 | 2014-10-05 | C | 1 | 0.00054129 | 3.0544e-06
1 | 2215340 | 2014-10-05 10:07 | 2014-10-05 13:54 | 226.9333 | 224 | 50833.0667 | 0.15547 | 0.00068509 | Restore Supply on Device Q11 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 727625 | Feeder trippin g caused by floating conductor at Pole 727625. Conductor rebound and feeder restored. | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 226.9333 | 223.9333 | 50161.0667 | 0.15321 | 0.00068419 | 2014-10-05 | C | 0.15321 | 0.00068419 | 2015 | 2014-10-05 | C | 224 | 0.15321 | 0.00068419
1 | 2188275 | 2014-10-05 10:50 | 2014-10-05 13:55 | 185.8333 | 2 | 221.2167 | 0.00067657 | 6.1168e-06 | Restore Supply on Device 5223E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 6635 | HV Fuses blown. Suspect bird strike. Replaced 2x 15Amp Links at Fuses 6635 | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 110.6083 | 107.6083 | 215.2167 | 0.00065736 | 6.1088e-06 | 2014-10-05 | C | 0.00065736 | 6.109e-06 | 2015 | 2014-10-05 | C | 2 | 0.00065736 | 6.1088e-06
1 | 2188301 | 2014-10-05 11:07 | 2014-10-05 13:58 | 170.85 | 1 | 170.85 | 0.00052253 | 3.0584e-06 | Restore Supply on Device P4015 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | fuse # 6635 and pole # 710460 | Fuse hanging off pole. reloaded 2 x 15 amp ddo fuses. 2 out of 3 phases. cause: bird strike. fuse # 6635 and pole # 710460. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 170.85 | 167.85 | 167.85 | 0.00051269 | 3.0544e-06 | 2014-10-05 | C | 0.00051269 | 3.054e-06 | 2015 | 2014-10-05 | C | 1 | 0.00051269 | 3.0544e-06
1 | 2188324 | 2014-10-05 11:30 | 2014-10-05 15:27 | 237.0167 | 2 | 288.1 | 0.00088113 | 6.1168e-06 | Restore Supply on Device TA2-121 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 207191 | 1x 2amp hv fuse on tx ta2/121 hv oh on pole 207191 due to wind. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 144.05 | 141.05 | 282.1 | 0.00086165 | 6.1088e-06 | 2014-10-05 | C | 0.00086165 | 6.109e-06 | 2015 | 2014-10-05 | C | 2 | 0.00086165 | 6.1088e-06
1 | 2188773 | 2014-10-05 11:36 | 2014-10-05 16:08 | 271.55 | 432 | 61037.5333 | 0.18668 | 0.0013212 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 200438 & 200478 | 1.37 clint leaving site to go another job andy and hayden staying at site CB 2 tripped to L/O - E/F flag - report of lines down at two sites pole 200438 & 200478 - apparent tree branch contact with line creating cascading fault on line - isolation for | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 141.2906 | 138.2906 | 59741.5333 | 0.18248 | 0.0013195 | 2014-10-05 | C | 0.18248 | 0.0013195 | 2015 | 2014-10-05 | C | 432 | 0.18248 | 0.0013195
1 | 2189228 | 2014-10-05 12:01 | 2014-10-05 16:08 | 246.3333 | 100 | 7289.0167 | 0.022293 | 0.00030584 | Restore Supply on Device TC4659 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | v13258 | this turned into 2r as replaced set off ddo fuse holder and fuses 3amp caused by age on tc4659 hv oh at pole v13258 | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 72.8902 | 69.8902 | 6989.0167 | 0.021347 | 0.00030544 | 2014-10-05 | C | 0.021347 | 0.00030544 | 2015 | 2014-10-05 | C | 100 | 0.021347 | 0.00030544
1 | 2175289 | 2014-10-05 13:24 | 2014-10-05 13:55 | 30.15 | 40 | 1206 | 0.0036885 | 0.00012234 | Restore Supply on Device TP1460 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1371 | Broken fuse holder at transformer TC1371 non urgent will re visit in morning Jaydan advised broken DDO fuse holder 1 broken and the other is old, will fail shortly so will need to be replaced may be 2fr work to replace (haven't put through another reques | F4 | TAUMANGI RD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 30.15 | 27.15 | 1086 | 0.0033171 | 0.00012218 | 2014-10-05 | C | 0.0033171 | 0.00012218 | 2015 | 2014-10-05 | C | 40 | 0.0033171 | 0.00012218
1 | 2191914 | 2014-10-05 15:43 | 2014-10-05 17:15 | 92.3667 | 1 | 92.3667 | 0.0002825 | 3.0584e-06 | Restore Supply on Device TE7-128 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227130 | It is the 11kv undergournd cable's termination point up the pole that burned up. FM can't fix it now. no reason to rush in fixing it. FM will amber defect. pole # 227130. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 92.3667 | 89.3667 | 89.3667 | 0.00027296 | 3.0544e-06 | 2014-10-05 | C | 0.00027296 | 3.054e-06 | 2015 | 2014-10-05 | C | 1 | 0.00027296 | 3.0544e-06
1 | 2192035 | 2014-10-05 16:20 | 2014-10-05 16:52 | 31.8 | 148 | 4706.4 | 0.014394 | 0.00045265 | Restore Supply on Device SD3-014 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200439 | On restoration of supply on OMS number 2188773, two blown jumpers were identified on pole 200439. Line was isolated between ABS SD3-148, SD3118, SD3-014 to repair jumpers. All supply restored following repairs. Conductor on this line appears to require in | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 31.8 | 28.8 | 4262.4 | 0.013019 | 0.00045205 | 2014-10-05 | C | 0.013019 | 0.00045205 | 2015 | 2014-10-05 | C | 148 | 0.013019 | 0.00045205
1 | 2192202 | 2014-10-05 16:52 | 2014-10-05 19:05 | 133.25 | 1 | 133.25 | 0.00040753 | 3.0584e-06 | Restore Supply on Device X3013 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer X3013 | replaced 2 x 2amp HV fuses | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 133.25 | 130.25 | 130.25 | 0.00039784 | 3.0544e-06 | 2014-10-05 | C | 0.00039784 | 3.054e-06 | 2015 | 2014-10-05 | C | 1 | 0.00039784 | 3.0544e-06
1 | 2889350 | 2014-10-05 17:13 | 2014-10-05 18:48 | 95 | 1328 | 15861 | 0.04851 | 0.0040616 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Pukepapa Sub CB1 | Pukepapa CB 1 tripped B & C Phase O/C. Unknown fault - line patrolled with nothing found. Possible shoot through of protection on CB6. Protection review to be considered. | F1, F2, F3 | PUKEPAPA 33KV | TP_MARTON | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 11.9435 | 8.9435 | 11877 | 0.036277 | 0.0040563 | 2014-10-05 | C | 0.036277 | 0.0040563 | 2015 | 2014-10-05 | C | 1328 | 0.036277 | 0.0040563
1 | 2534858 | 2014-10-06 01:22 | 2014-10-06 02:48 | 86 | 303 | 26058 | 0.079696 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB XT40 | Parkville CB XT40 auto reclosed and tripped - No flags. Line patrolled - no fault located, suspect line clash. Andrew Tuhura attended. | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 86 | 83 | 25149 | 0.076816 | 0.00092549 | 2014-10-06 | C | 0.076816 | 0.00092549 | 2015 | 2014-10-06 | C | 303 | 0.076816 | 0.00092549
1 | 2192736 | 2014-10-06 02:17 | 2014-10-06 03:42 | 85.35 | 303 | 25861.05 | 0.079094 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND |  | Sectionalised and supply restore with no apparent fault | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 85.35 | 82.35 | 24952.05 | 0.076214 | 0.00092549 | 2014-10-06 | C | 0.076214 | 0.00092549 | 2015 | 2014-10-06 | C | 303 | 0.076214 | 0.00092549
1 | 2195479 | 2014-10-06 03:11 | 2014-10-06 11:31 | 499.7167 | 91 | 22523.0333 | 0.068885 | 0.00027832 | Restore Supply on Device T459 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 363468 | CB C632 tripped. Line patrolled and C632/2 found open. (System created outage at 03:11) No comms - own AP. Materials to follow. Gavin Gray & Adam Whale attended. NDR34879 | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 247.5059 | 244.5059 | 22250.0333 | 0.067961 | 0.00027795 | 2014-10-06 | C | 0.067961 | 0.00027795 | 2015 | 2014-10-06 | C | 91 | 0.067961 | 0.00027795
1 | 2198483 | 2014-10-06 04:09 | 2014-10-06 09:11 | 302.9333 | 385 | 43269.6833 | 0.13234 | 0.0011775 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 789161 | taihape cb 8 Trip trees in line at pole 789161 isolated at abs 222 ,112 & 490 also 33 kv line trip at Cb 1092 materials to be supplied later | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 112.3888 | 109.3888 | 42114.6833 | 0.12864 | 0.001176 | 2014-10-06 | C | 0.12864 | 0.001176 | 2015 | 2014-10-06 | C | 385 | 0.12864 | 0.001176
1 | 2534552 | 2014-10-06 05:33 | 2014-10-06 06:56 | 83 | 303 | 25149 | 0.076916 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB XT40 | Parkville CB XT40 auto reclosed and tripped. Line not patrolled - Unknown fault. | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 83 | 80 | 24240 | 0.074039 | 0.00092549 | 2014-10-06 | C | 0.074039 | 0.00092549 | 2015 | 2014-10-06 | C | 303 | 0.074039 | 0.00092549
1 | 2200595 | 2014-10-06 06:28 | 2014-10-06 07:50 | 82.75 | 303 | 25073.25 | 0.076685 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | XT40 | XT40 | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 82.75 | 79.75 | 24164.25 | 0.073808 | 0.00092549 | 2014-10-06 | C | 0.073808 | 0.00092549 | 2015 | 2014-10-06 | C | 303 | 0.073808 | 0.00092549
1 | 2201769 | 2014-10-06 07:00 | 2014-10-06 19:47 | 766.85 | 183 | 5641 | 0.017253 | 0.00055969 | Restore Supply on Device T1235 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 834755 | plz check oms 2202175 if related. Ben Taylor is onsite and looking for cause of HV outage. Part of feeder fault. Fault now restored, power back on in James Road .replace Transformer T2413 and cut trees from lines | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 30.8251 | 27.8251 | 5092 | 0.015553 | 0.00055896 | 2014-10-06 | C | 0.015553 | 0.00055896 | 2015 | 2014-10-06 | C | 183 | 0.015553 | 0.00055896
1 | 2201877 | 2014-10-06 07:22 | 2014-10-06 07:45 | 23.1833 | 1 | 23.1833 | 7.0904e-05 | 3.0584e-06 | Restore Supply on Device TB2-042 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TB2-042 | "replaced 2x 8amp ddo ht fuses possible bird strike No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard" Email sent to Jo, as appears may have SAIDI component. | F3/F4 | WILLS RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 23.1833 | 20.1833 | 20.1833 | 6.1648e-05 | 3.0544e-06 | 2014-10-06 | C | 6.1648e-05 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 6.1648e-05 | 3.0544e-06
1 | 2202922 | 2014-10-06 07:59 | 2014-10-06 20:41 | 762.2 | 1 | 762.2 | 0.0023311 | 3.0584e-06 | Restore Supply on Device 2602T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2602T | replaced hv 3 amp fuse at TX 2602T. cause: weather. oh/hv. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco standard | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 762.2 | 759.2 | 759.2 | 0.0023189 | 3.0544e-06 | 2014-10-06 | C | 0.0023189 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0023189 | 3.0544e-06
1 | 2202961 | 2014-10-06 08:06 | 2014-10-06 13:26 | 320.75 | 1 | 320.75 | 0.00098099 | 3.0584e-06 | Restore Supply on Device T9/55 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t9/55 | replace 2 x 6 amp fuses at fuse V13. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco standard. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 320.75 | 317.75 | 317.75 | 0.00097054 | 3.0544e-06 | 2014-10-06 | C | 0.00097054 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.00097054 | 3.0544e-06
1 | 1908934 | 2014-10-06 08:17 | 2014-10-06 14:01 | 344 | 471 | 14261 | 0.043616 | 0.0014405 | NAPA ID:02318 TP_TE MATAI GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE7-028 | REPLACE POLE AND RECON HV FEEDER WIRES. LLWP UNDER A CACL IS TO INSTALL A LL GAP IN THE 16MM WIRE DUE FOR SAFTEY REASONS AND TO REMAKE AT THE END OF THE DAY UNDER A NEW CACL. Works location: Maketu Rd. WO 10145449. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 30.2781 | 27.2781 | 12848 | 0.039243 | 0.0014386 | 2014-10-06 | B | 0.019622 | 0.00071932 | 2015 | 2014-10-06 | B | 471 | 0.039243 | 0.0014386
1 | 2203070 | 2014-10-06 08:18 | 2014-10-06 11:23 | 184.9167 | 92 | 2811.6167 | 0.0085991 | 0.00028137 | Restore Supply on Device C268 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | t1064 | cb c268 tripped fuse at t1064 tripped causing recloser to trip Suspect line clash due to wind | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 30.5611 | 27.5611 | 2535.6167 | 0.0077448 | 0.00028101 | 2014-10-06 | C | 0.0077448 | 0.00028101 | 2015 | 2014-10-06 | C | 92 | 0.0077448 | 0.00028101
1 | 2596378 | 2014-10-06 08:41 | 2014-10-06 11:08 | 147 | 176 | 24570 | 0.075145 | 0.00053828 | Restore Supply on Device CB3 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P01000 | Tree touching lines - removed with hotstick by Treescape. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 139.6023 | 136.6023 | 24042 | 0.073434 | 0.00053758 | 2014-10-06 | C | 0.073434 | 0.00053758 | 2015 | 2014-10-06 | C | 176 | 0.073434 | 0.00053758
1 | 2203843 | 2014-10-06 08:48 | 2014-10-06 11:43 | 175.4333 | 354 | 34697.3333 | 0.10612 | 0.0010827 | Restore Supply on Device C834 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 826238 | A/R, L/O, O/C cb 834 trip found twisted crossarm at pole 826238 no materials used | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98.0151 | 95.0151 | 33635.3333 | 0.10274 | 0.0010813 | 2014-10-06 | C | 0.10274 | 0.0010813 | 2015 | 2014-10-06 | C | 354 | 0.10274 | 0.0010813
1 | 2206348 | 2014-10-06 09:28 | 2014-10-06 17:01 | 452.6 | 207 | 1170.5667 | 0.0035801 | 0.00063309 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB7 |  | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 5.6549 | 2.6549 | 549.5667 | 0.0016786 | 0.00063227 | 2014-10-06 | C | 0.0016786 | 0.00063227 | 2015 | 2014-10-06 | C | 207 | 0.0016786 | 0.00063227
1 | 2535167 | 2014-10-06 09:38 | 2014-10-06 15:50 | 372 | 237 | 45170 | 0.13815 | 0.00072485 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | - | Kai Iwi CB6 tripped. No Flags. Adverse Weather/Extreme Wind. Line patrolled. Tree through lines just up from 22 Bushy Park Road. Alan Cox attended. | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 190.5907 | 187.5907 | 44459 | 0.1358 | 0.0007239 | 2014-10-06 | C | 0.1358 | 0.0007239 | 2015 | 2014-10-06 | C | 237 | 0.1358 | 0.0007239
1 | 2206810 | 2014-10-06 09:38 | 2014-10-06 18:12 | 513.9833 | 119 | 57060.0167 | 0.17451 | 0.00036395 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 793535 |  | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 479.4959 | 476.4959 | 56703.0167 | 0.1732 | 0.00036348 | 2014-10-06 | C | 0.1732 | 0.00036348 | 2015 | 2014-10-06 | C | 119 | 0.1732 | 0.00036348
1 | 2207634 | 2014-10-06 09:41 | 2014-10-06 12:30 | 168.8 | 12 | 2025.6 | 0.0061951 | 3.6701e-05 | Restore Supply on Device 687 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 803212 | 11kV Recloser 687 Tripped and L/O. Line sectionalised and faulty equipment found at transformer X1058 and X3198. Repairs made. NDR 30455. On sectionalising the feeder it was found the physical network did not reflect what was drawn on the SCADA tile. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 168.8 | 165.8 | 1989.6 | 0.0060771 | 3.6653e-05 | 2014-10-06 | C | 0.0060771 | 3.6653e-05 | 2015 | 2014-10-06 | C | 12 | 0.0060771 | 3.6653e-05
1 | 2207651 | 2014-10-06 09:42 | 2014-10-06 10:53 | 71 | 544 | 36464 | 0.11152 | 0.0016638 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | n/a | CB2 tripped on O/E and E/F. Patrolled but no fault found. | F3 | DURIE HILL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 67.0294 | 64.0294 | 34832 | 0.10639 | 0.0016616 | 2014-10-06 | C | 0.10639 | 0.0016616 | 2015 | 2014-10-06 | C | 544 | 0.10639 | 0.0016616
1 | 2216807 | 2014-10-06 09:45 | 2014-10-07 17:03 | 1877.9 | 332 | 87937.9 | 0.26895 | 0.0010154 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 802017 | line down on car | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 264.8732 | 261.8732 | 86941.9 | 0.26556 | 0.0010141 | 2014-10-06 | C | 0.26556 | 0.0010141 | 2015 | 2014-10-06 | C | 332 | 0.26556 | 0.0010141
1 | 2208673 | 2014-10-06 09:48 | 2014-10-06 12:14 | 145.3667 | 1180 | 75755.4167 | 0.23169 | 0.0036089 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 800535 | cb 7 trip Insulator at pole 800535 defective isolated at ABs 211 ,467 and swgear 2038/1 materials used 1 insiulator | F2 | MARTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 64.1995 | 61.1995 | 72215.4167 | 0.22058 | 0.0036042 | 2014-10-06 | C | 0.22058 | 0.0036042 | 2015 | 2014-10-06 | C | 1180 | 0.22058 | 0.0036042
1 | 2210684 | 2014-10-06 09:50 | 2014-10-06 18:27 | 517.1333 | 26 | 13125.8833 | 0.040144 | 7.9519e-05 | Restore Supply on Device S11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | s11 | patrolled line. 15.36pm closed s11 fuses. worked through control. replaced 2 x 10 amp fuse line clash suspect | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 504.8417 | 501.8417 | 13047.8833 | 0.039854 | 7.9415e-05 | 2014-10-06 | C | 0.039854 | 7.9415e-05 | 2015 | 2014-10-06 | C | 26 | 0.039854 | 7.9415e-05
1 | 2871454 | 2014-10-06 10:00 | 2014-10-06 19:20 | 560 | 1263 | 104993 | 0.32111 | 0.0038628 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P41124 | Kelvin Grove CB 8 auto reclosed L/O - no flags. Line patrolled and floating conductor located at pole P41124. D Whale & C Naylor attended. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 83.1298 | 80.1298 | 101204 | 0.30912 | 0.0038577 | 2014-10-06 | C | 0.30912 | 0.0038577 | 2015 | 2014-10-06 | C | 1263 | 0.30912 | 0.0038577
1 | 2214175 | 2014-10-06 10:02 | 2014-10-07 16:53 | 1850.9833 | 1 | 1850.9833 | 0.0056611 | 3.0584e-06 | Restore Supply on Device T2/683 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Tx G91 | 11kv fuse blown at G91 Replaced 15amp ddo fuse hv o/h cause wind full power restored. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco standard. | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1850.9833 | 1847.9833 | 1847.9833 | 0.0056445 | 3.0544e-06 | 2014-10-06 | C | 0.0056445 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0056445 | 3.0544e-06
1 | 2215578 | 2014-10-06 10:10 | 2014-10-08 12:22 | 3011.9833 | 83 | 171748.1167 | 0.52528 | 0.00025385 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 794474 | 4237 tripped found broken crossarm at pole 794474. Materials used: 2 x crossarms whole assembly and 4 x HV Inxulators, 100m of 16mm copper & 18 sleeves. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 2069.2544 | 2066.2544 | 171499.1167 | 0.52383 | 0.00025352 | 2014-10-06 | C | 0.52383 | 0.00025352 | 2015 | 2014-10-06 | C | 83 | 0.52383 | 0.00025352
1 | 2207297 | 2014-10-06 10:11 | 2014-10-07 10:00 | 1428.75 | 336 | 470122.35 | 1.4378 | 0.0010276 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 782369 |  | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1399.1737 | 1396.1737 | 469114.35 | 1.4329 | 0.0010263 | 2014-10-06 | C | 1.4329 | 0.0010263 | 2015 | 2014-10-06 | C | 336 | 1.4329 | 0.0010263
1 | 2216672 | 2014-10-06 10:13 | 2014-10-07 14:43 | 1709.35 | 1 | 1709.35 | 0.0052279 | 3.0584e-06 | Restore Supply on Device X248 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X248 | reset hv fuse, power restored. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco standard. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1709.35 | 1706.35 | 1706.35 | 0.0052119 | 3.0544e-06 | 2014-10-06 | C | 0.0052119 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0052119 | 3.0544e-06
1 | 2217927 | 2014-10-06 10:36 | 2014-10-08 17:04 | 3267.4333 | 1 | 3267.4333 | 0.0099932 | 3.0584e-06 | Restore Supply on Device T7/66 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | r19 | Replaced 2x 10Amp Fuses r 19. Email sent to Jo, as job appears to have SAIDI component. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 3267.4333 | 3264.4333 | 3264.4333 | 0.009971 | 3.0544e-06 | 2014-10-06 | C | 0.009971 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.009971 | 3.0544e-06
1 | 2218358 | 2014-10-06 10:51 | 2014-10-06 12:24 | 92.95 | 24 | 2230.8 | 0.0068227 | 7.3402e-05 | Restore Supply on Device V16 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | p06802 | Fuses v16 opened due to line down through gully to be repaired later | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 92.95 | 89.95 | 2158.8 | 0.0065939 | 7.3306e-05 | 2014-10-06 | C | 0.0065939 | 7.3306e-05 | 2015 | 2014-10-06 | C | 24 | 0.0065939 | 7.3306e-05
1 | 2220061 | 2014-10-06 11:00 | 2014-10-06 12:00 | 60 | 442 | 26520 | 0.081109 | 0.0013518 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | p43888 | Cb 11 trip found branch on line at pole P43888 removed with hot stick | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 25194 | 0.076953 | 0.0013501 | 2014-10-06 | C | 0.076953 | 0.0013501 | 2015 | 2014-10-06 | C | 442 | 0.076953 | 0.0013501
1 | 2258428 | 2014-10-06 11:09 | 2014-10-08 10:09 | 2820.2167 | 667 | 104984.5167 | 0.32109 | 0.00204 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P08669 | CB 7 tripped and L/O. NOC disable A/R. Floating conductor found and repaired. Jeff Roberts attended. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 157.3981 | 154.3981 | 102983.5167 | 0.31456 | 0.0020373 | 2014-10-06 | C | 0.31456 | 0.0020373 | 2015 | 2014-10-06 | C | 667 | 0.31456 | 0.0020373
1 | 2220924 | 2014-10-06 11:17 | 2014-10-06 18:53 | 456.4 | 469 | 205516.2 | 0.62856 | 0.0014344 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 224890 | 11:46am tx blown up outside 47 Mark road 12:48p, Clint advises 3 x HV lines down, broken insulator and blown HV insulator multiple faults on feeder | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 438.2009 | 435.2009 | 204109.2 | 0.62344 | 0.0014325 | 2014-10-06 | C | 0.62344 | 0.0014325 | 2015 | 2014-10-06 | C | 469 | 0.62344 | 0.0014325
1 | 2221494 | 2014-10-06 11:22 | 2014-10-06 18:14 | 411.3333 | 1 | 411.3333 | 0.001258 | 3.0584e-06 | Restore Supply on Device TC4164 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N13126 | REPLACED 2X 3AMP HV OH DUE TO WIND AT POLE N13126. Email sent to Jo, as job appears to have SAIDI component. | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 411.3333 | 408.3333 | 408.3333 | 0.0012472 | 3.0544e-06 | 2014-10-06 | C | 0.0012472 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0012472 | 3.0544e-06
1 | 2221504 | 2014-10-06 11:24 | 2014-10-06 19:27 | 482.85 | 1 | 482.85 | 0.0014768 | 3.0584e-06 | Restore Supply on Device T7/233 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuses t3 | customer saw power pole flashed and was an explosion flames shot out 12.38pm advised Shannon at hub replaced blown 6amp 11kv hv oh fuses t3. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 482.85 | 479.85 | 479.85 | 0.0014657 | 3.0544e-06 | 2014-10-06 | C | 0.0014657 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0014657 | 3.0544e-06
1 | 2255388 | 2014-10-06 11:27 | 2014-10-06 18:25 | 418.4667 | 465 | 194587 | 0.59513 | 0.0014222 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 803886 | CB7 tripped. Isolations made and line patrolled. Repairs made. Carl Rogers and James attended. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 418.4667 | 415.4667 | 193192 | 0.59009 | 0.0014203 | 2014-10-06 | C | 0.59009 | 0.0014203 | 2015 | 2014-10-06 | C | 465 | 0.59009 | 0.0014203
1 | 2231277 | 2014-10-06 11:37 | 2014-10-06 13:00 | 83.8 | 456 | 23275.75 | 0.071187 | 0.0013946 | Restore Supply on Device S124 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 833045 | abs 583 Opened and tagged. Broken 11kV jumper. | F2 | COLOMBO RD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 51.0433 | 48.0433 | 21907.75 | 0.066916 | 0.0013928 | 2014-10-06 | C | 0.066916 | 0.0013928 | 2015 | 2014-10-06 | C | 456 | 0.066916 | 0.0013928
1 | 2236256 | 2014-10-06 11:46 | 2014-10-06 15:16 | 210.0333 | 4 | 673.5167 | 0.0020599 | 1.2234e-05 | Restore Supply on Device TD2-083 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | f sD2-021 | 2x 5amp ddo fuses - not full set replaced No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard? | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 168.3792 | 165.3792 | 661.5167 | 0.0020206 | 1.2218e-05 | 2014-10-06 | C | 0.0020206 | 1.2218e-05 | 2015 | 2014-10-06 | C | 4 | 0.0020206 | 1.2218e-05
1 | 2233696 | 2014-10-06 11:50 | 2014-10-06 17:35 | 344.2 | 693 | 176550.95 | 0.53997 | 0.0021195 | Restore Supply on Device T1/137 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 33262 | repaired binder @ pole 33262 | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 254.7633 | 251.7633 | 174471.95 | 0.53291 | 0.0021167 | 2014-10-06 | C | 0.53291 | 0.0021167 | 2015 | 2014-10-06 | C | 693 | 0.53291 | 0.0021167
1 | 2233713 | 2014-10-06 11:54 | 2014-10-08 18:42 | 3288.0333 | 1 | 3288.0333 | 0.010056 | 3.0584e-06 | Restore Supply on Device X1601 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1601 | 8/10 1313hrs still part power - affecting whole station Can see fuse hanging at pole infront of woolshed by the fuse box. In the middle of shearing - 2nd day customer has had to send the shearers home due to part power. Replaced 1 x 2A HV fuse; probab | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3288.0333 | 3285.0333 | 3285.0333 | 0.010034 | 3.0544e-06 | 2014-10-06 | C | 0.010034 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.010034 | 3.0544e-06
1 | 2233738 | 2014-10-06 12:00 | 2014-10-06 13:25 | 84.95 | 1443 | 53093.75 | 0.16238 | 0.0044133 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P12874 | Recloser 9603 Tripped Kensington Rd | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 36.794 | 33.794 | 48764.75 | 0.14895 | 0.0044075 | 2014-10-06 | C | 0.14895 | 0.0044075 | 2015 | 2014-10-06 | C | 1443 | 0.14895 | 0.0044075
1 | 2235445 | 2014-10-06 12:07 | 2014-10-06 20:23 | 496.1167 | 1 | 496.1167 | 0.0015173 | 3.0584e-06 | Restore Supply on Device T7/60 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t7/90 | 2x of 3 blown 6amp hv fuses. Email sent to Jo, as job appears to have SAIDI component. No Paperwork available for this outage. Time estimated to 8 hours for restoration. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 496.1167 | 493.1167 | 493.1167 | 0.0015062 | 3.0544e-06 | 2014-10-06 | C | 0.0015062 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0015062 | 3.0544e-06
1 | 2238560 | 2014-10-06 12:24 | 2014-10-07 17:57 | 1773.1167 | 1 | 1773.1167 | 0.0054229 | 3.0584e-06 | Restore Supply on Device T7/56 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t7/56 | 2 out of 3 phases. replaced 2 x 10 amp fuses at tx t7/56. cause: yesterday's feeder fault. Email sent to Jo, as job appears to have SAIDI component. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1773.1167 | 1770.1167 | 1770.1167 | 0.0054067 | 3.0544e-06 | 2014-10-06 | C | 0.0054067 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0054067 | 3.0544e-06
1 | 2238576 | 2014-10-06 12:24 | 2014-10-06 15:10 | 165.9667 | 678 | 69950 | 0.21394 | 0.0020736 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Recloser 9513 | Recloser 9513 tripped - no flags/ Auto Reclose disabled. Adverse Weather/Extreme Wind at time of fault. Line patrolled- reason for fault not identified on switching instruction sheet. Dennis Ngatai and Ted Glasgow attended. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 103.1711 | 100.1711 | 67916 | 0.20744 | 0.0020709 | 2014-10-06 | C | 0.20744 | 0.0020709 | 2015 | 2014-10-06 | C | 678 | 0.20744 | 0.0020709
1 | 2239953 | 2014-10-06 12:42 | 2014-10-06 15:12 | 149.4333 | 64 | 3675.75 | 0.011242 | 0.00019574 | Restore Supply on Device C637 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 816966 | Tree through lines at pole 816966 | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 57.4336 | 54.4336 | 3483.75 | 0.010641 | 0.00019548 | 2014-10-06 | C | 0.010641 | 0.00019548 | 2015 | 2014-10-06 | C | 64 | 0.010641 | 0.00019548
1 | 2290783 | 2014-10-06 12:45 | 2014-10-06 20:15 | 450 | 1 | 450 | 0.0013763 | 3.0584e-06 | Restore Supply on Device X248 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT TREE CONTACT | X248 | 2 X 60 AMP HRC. Fault due to trees. No other assets repaired or replaced. All adjacent assets OK. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 450 | 447 | 447 | 0.0013653 | 3.0544e-06 | 2014-10-06 | C | 0.0013653 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0013653 | 3.0544e-06
1 | 2241794 | 2014-10-06 12:52 | 2014-10-07 13:07 | 1455.3333 | 31 | 43462.3333 | 0.13293 | 9.4811e-05 | Restore Supply on Device M56 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M56 | 10:07am customer their cows will be electrocuted. isolated customer pole, 2x 60a lv 1x 6a ddo fuse link and 1x 6a ddo barrel | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1402.0108 | 1399.0108 | 43369.3333 | 0.13247 | 9.4687e-05 | 2014-10-06 | C | 0.13247 | 9.4687e-05 | 2015 | 2014-10-06 | C | 31 | 0.13247 | 9.4687e-05
1 | 2241824 | 2014-10-06 12:56 | 2014-10-07 20:56 | 1919.4 | 3 | 3888.9333 | 0.011894 | 9.1753e-06 | Restore Supply on Device T2/88 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | ABS 10200 | If not an HV fault, please request on further LV jobs on this feeder. Check if switch closed. Email sent to Jo, as job appears to have SAIDI component. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1296.3111 | 1293.3111 | 3879.9333 | 0.011851 | 9.1633e-06 | 2014-10-06 | C | 0.011851 | 9.163e-06 | 2015 | 2014-10-06 | C | 3 | 0.011851 | 9.1633e-06
1 | 2242480 | 2014-10-06 12:59 | 2014-10-06 15:54 | 175.05 | 943 | 68499.15 | 0.2095 | 0.0028841 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Hatricks Wharf CB11 | Hatricks Wharf CB 11 tripped O/C. Adverse Weather/Extreme Wind at time of tripping. Line patrolled and sectionalised. Reason for fault not recorded on switching sheet. Scott Bullock attended. | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 72.6396 | 69.6396 | 65670.15 | 0.20058 | 0.0028803 | 2014-10-06 | C | 0.20058 | 0.0028803 | 2015 | 2014-10-06 | C | 943 | 0.20058 | 0.0028803
1 | 2293840 | 2014-10-06 12:59 | 2014-10-07 11:32 | 1352.5833 | 241 | 85057.0333 | 0.26014 | 0.00073708 | Restore Supply on Device 1447 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 812031 | Recloser 4141 tripped. Multiple faults repaired and power restored. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 352.9337 | 349.9337 | 84334.0333 | 0.25759 | 0.00073612 | 2014-10-06 | C | 0.25759 | 0.00073612 | 2015 | 2014-10-06 | C | 241 | 0.25759 | 0.00073612
1 | 2269637 | 2014-10-06 13:08 | 2014-10-08 00:53 | 2145.5 | 27 | 54120.6 | 0.16552 | 8.2577e-05 | Restore Supply on Device 5193 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 5193 | 7/10 2120hrs Customer at 84 Piko Rd increasingly upset at time this is taking to restore. Advised svs hub. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2004.4667 | 2001.4667 | 54039.6 | 0.16506 | 8.2469e-05 | 2014-10-06 | C | 0.16506 | 8.2469e-05 | 2015 | 2014-10-06 | C | 27 | 0.16506 | 8.2469e-05
1 | 2244366 | 2014-10-06 13:08 | 2014-10-07 15:22 | 1573.75 | 292 | 155215.2 | 0.47471 | 0.00089306 | Restore Supply on Device X2309 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 782531 | lines down replaced conductor and pole, and crossarm, x3 insulators (30meter of condictor) 3 phases on 2 spans all phases on all spans due to wind and tree No other assets repaired or replaced. Adjacent assets were checked and confirmed as bein | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 531.5589 | 528.5589 | 154339.2 | 0.47142 | 0.00089189 | 2014-10-06 | C | 0.47142 | 0.00089189 | 2015 | 2014-10-06 | C | 292 | 0.47142 | 0.00089189
1 | 2247753 | 2014-10-06 13:13 | 2014-10-06 17:32 | 259.3833 | 116 | 26829.4667 | 0.082056 | 0.00035478 | Restore Supply on Device T42/2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | recloser T42 | patrolled line and feeder held. no fault found. recloser T42. hv/oh. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 231.2885 | 228.2885 | 26481.4667 | 0.080886 | 0.00035431 | 2014-10-06 | C | 0.080886 | 0.00035431 | 2015 | 2014-10-06 | C | 116 | 0.080886 | 0.00035431
1 | 2244801 | 2014-10-06 13:18 | 2014-10-06 20:18 | 419.7667 | 9 | 3381.9 | 0.010343 | 2.7526e-05 | Restore Supply on Device FP1405 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | m1895 | replaced 2x 10a hv fuse links, fitted 11kn pin bacvk in cross arm | F4 | TAUMANGI RD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 375.7667 | 372.7667 | 3354.9 | 0.010247 | 2.749e-05 | 2014-10-06 | C | 0.010247 | 2.749e-05 | 2015 | 2014-10-06 | C | 9 | 0.010247 | 2.749e-05
1 | 2246427 | 2014-10-06 13:25 | 2014-10-06 15:27 | 121.6333 | 533 | 41947.1 | 0.12829 | 0.0016301 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Te Puke CB3, Recloser 9744 | Te Puke CB3 tripped. Recloser 9744 tripped. No Flags. CB3 Auto Reclose disabled and line patrolled. Lines found down at pole 222535. Adverse Weather/Extreme Wind. Dennis Ngatai attended. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 78.7 | 75.7 | 40348.1 | 0.12324 | 0.001628 | 2014-10-06 | C | 0.12324 | 0.001628 | 2015 | 2014-10-06 | C | 533 | 0.12324 | 0.001628
1 | 2247759 | 2014-10-06 13:32 | 2014-10-07 20:01 | 1828.9 | 1 | 1828.9 | 0.0055935 | 3.0584e-06 | Restore Supply on Device C6805 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | c805 | 07/10 1616hrs still no power but neighbors all have power now - as advised by retailer. Blown HV tx fuse 3amp replaced | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1828.9 | 1825.9 | 1825.9 | 0.0055771 | 3.0544e-06 | 2014-10-06 | C | 0.0055771 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0055771 | 3.0544e-06
1 | 2247889 | 2014-10-06 13:33 | 2014-10-06 14:33 | 60.2167 | 1215 | 73163.25 | 0.22376 | 0.003716 | Restore Supply on Device 42 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB42 |  | F1, F2, F3 | AONGATETE42-KAURI POINT 33KV | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 60.2167 | 57.2167 | 69518.25 | 0.21234 | 0.0037111 | 2014-10-06 | C | 0.21234 | 0.0037111 | 2015 | 2014-10-06 | C | 1215 | 0.21234 | 0.0037111
1 | 2249115 | 2014-10-06 13:35 | 2014-10-07 20:13 | 1838.5167 | 1 | 1838.5167 | 0.005623 | 3.0584e-06 | Restore Supply on Device W2168 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | pole unknown but tx is on the pole tx W2168 | hv jumper reattached at tx W2168 Replaced 1x 3amp ddo fuse hv o/h pole unknown but tx is on the pole cause newish tx, possibly overtightened lug broken - replaced 1x 16mm lug full power restored | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1838.5167 | 1835.5167 | 1835.5167 | 0.0056064 | 3.0544e-06 | 2014-10-06 | C | 0.0056064 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0056064 | 3.0544e-06
1 | 2249137 | 2014-10-06 13:37 | 2014-10-10 20:50 | 6192.7167 | 1 | 6192.7167 | 0.01894 | 3.0584e-06 | Restore Supply on Device T2/595 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2/595 | can't reach cust, 2:31pm, please phone back later. 3 phase 30kVA transformer and stolen earth wire requires replacement. Safety Incident created #405820. 10/10 REPLACED TX AND 10 METERS OF EARTH DUE TO STORM AT T2/595 | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 6192.7167 | 6189.7167 | 6189.7167 | 0.018906 | 3.0544e-06 | 2014-10-06 | C | 0.018906 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.018906 | 3.0544e-06
1 | 2249148 | 2014-10-06 13:39 | 2014-10-06 18:01 | 262.45 | 47 | 1937.95 | 0.0059271 | 0.00014375 | Restore Supply on Device C218 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 838305 | Tree come down through lines at pole 838305. Broken conductor and cross arm. Joe Matthews attended. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 41.233 | 38.233 | 1796.95 | 0.0054886 | 0.00014356 | 2014-10-06 | C | 0.0054886 | 0.00014356 | 2015 | 2014-10-06 | C | 47 | 0.0054886 | 0.00014356
1 | 2251321 | 2014-10-06 14:01 | 2014-10-06 18:45 | 284.6 | 1 | 284.6 | 0.00087043 | 3.0584e-06 | Restore Supply on Device TC1560 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P13379 | UNABLE TO GET THROUGH TO SVS HUB TO REQUEST 2R JAMES KENNERLY ASSIST James Brier on site, TO PULL UP 2 LINES AT POLE IT IS VERY WINDY SO THEY WILL WORK TOGETHER FOR SAFETY ONE SPAN ON 2 PHASES AND 1X 3 AMP HV FUSE 1X DDO CARRIER 6X 16 ML SLEEVES 100 AM | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 284.6 | 281.6 | 281.6 | 0.00086013 | 3.0544e-06 | 2014-10-06 | C | 0.00086013 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.00086013 | 3.0544e-06
1 | 2254065 | 2014-10-06 14:01 | 2014-10-06 19:32 | 330.7333 | 393 | 30422.9833 | 0.093046 | 0.001202 | Restore Supply on Device 6561-2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Recloser 6561 | Feeder Patrolled. Disused transformer C6642 found with one HV fuse blown. Transformer isolated and feeder restored. Not sure if this was the problem. Also found a wire wrapped around center phase at pole 724766 this was removed. not sure if this was a pro | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 77.4122 | 74.4122 | 29243.9833 | 0.089324 | 0.0012004 | 2014-10-06 | C | 0.089324 | 0.0012004 | 2015 | 2014-10-06 | C | 393 | 0.089324 | 0.0012004
1 | 2252423 | 2014-10-06 14:08 | 2014-10-07 20:00 | 1792.2167 | 2 | 2257.85 | 0.0069055 | 6.1168e-06 | Restore Supply on Device 7379 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7379 | REPLACED 10AMP LINK 7379 DUE TO WIND. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1128.925 | 1125.925 | 2251.85 | 0.0068781 | 6.1088e-06 | 2014-10-06 | C | 0.0068781 | 6.109e-06 | 2015 | 2014-10-06 | C | 2 | 0.0068781 | 6.1088e-06
1 | 2249107 | 2014-10-06 14:11 | 2014-10-06 17:29 | 197.75 | 202 | 18270.05 | 0.055878 | 0.0006178 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | SD5-055 | CB 3 tripped. Initial inspection found no fault and CB 3 closed. Fault later found to be a blown jumper at ABS SD5-055. DNO 141006. | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 90.4458 | 87.4458 | 17664.05 | 0.053953 | 0.00061699 | 2014-10-06 | C | 0.053953 | 0.00061699 | 2015 | 2014-10-06 | C | 202 | 0.053953 | 0.00061699
1 | 2254049 | 2014-10-06 14:13 | 2014-10-07 17:21 | 1627.85 | 66 | 107438.1 | 0.32859 | 0.00020186 | Restore Supply on Device 266 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Recloser 266 | Recloser RS266 tripped L/O A Phase O/C. Adverse Weather/Extreme Winds. Line patrolled - no fault found. Suspect line clash due to high winds. Glen Most attended. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1627.85 | 1624.85 | 107240.1 | 0.32756 | 0.00020159 | 2014-10-06 | C | 0.32756 | 0.00020159 | 2015 | 2014-10-06 | C | 66 | 0.32756 | 0.00020159
1 | 2254368 | 2014-10-06 14:18 | 2014-10-06 19:30 | 311.9833 | 759 | 197986.75 | 0.60553 | 0.0023213 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 222231 | Hazard - Tree in lines. Phone 075440357 for location from Customer who reported. | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 260.8521 | 257.8521 | 195709.75 | 0.59778 | 0.0023183 | 2014-10-06 | C | 0.59778 | 0.0023183 | 2015 | 2014-10-06 | C | 759 | 0.59778 | 0.0023183
1 | 2254407 | 2014-10-06 14:24 | 2014-10-06 22:09 | 465.2333 | 466 | 67017.9167 | 0.20497 | 0.0014252 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 207375 | No Power. Adverse Weather/Extreme Wind. Line patrolled and found lines down due to tree at pole 207375. Material used: 7 x Links. Wayne Seath attended. | F3 | ATHENREE | WAIHI BEACH SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 143.8153 | 140.8153 | 65619.9167 | 0.20043 | 0.0014234 | 2014-10-06 | C | 0.20043 | 0.0014234 | 2015 | 2014-10-06 | C | 466 | 0.20043 | 0.0014234
1 | 2254894 | 2014-10-06 14:28 | 2014-10-06 19:44 | 316.1167 | 102 | 18644.2667 | 0.057022 | 0.00031196 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TE6-069 | Recloser 9513 tripped. Approx out 877 SH 2 lines are down. Materials Used: 20m conductor (less than 1 span - not all phases). 6 x Links, 6 x Lugs. Ted Glasgow attended. 9513 tripped whilst OMS Outage ID 2238579 was underway. SE7-031 was already Open | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 182.7869 | 179.7869 | 18338.2667 | 0.056013 | 0.00031155 | 2014-10-06 | C | 0.056013 | 0.00031155 | 2015 | 2014-10-06 | C | 102 | 0.056013 | 0.00031155
1 | 2255050 | 2014-10-06 14:34 | 2014-10-06 14:52 | 17.8667 | 54 | 964.8 | 0.0029508 | 0.00016515 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 4246 |  | F4 | PUTORINO | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 17.8667 | 14.8667 | 802.8 | 0.0024521 | 0.00016494 | 2014-10-06 | C | 0.0024521 | 0.00016494 | 2015 | 2014-10-06 | C | 54 | 0.0024521 | 0.00016494
1 | 2255133 | 2014-10-06 14:39 | 2014-10-06 18:50 | 250.7333 | 253 | 47805.8167 | 0.14621 | 0.00077378 | Restore Supply on Device S6031 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | S6031 | Te Puke CB4. Recloser S6031 tripped no flags. Lines patrolled and line found down. Reloaded and relivened 1 DDO at SF6-008. D Ngatai attended. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 188.9558 | 185.9558 | 47046.8167 | 0.1437 | 0.00077277 | 2014-10-06 | C | 0.1437 | 0.00077277 | 2015 | 2014-10-06 | C | 253 | 0.1437 | 0.00077277
1 | 2258269 | 2014-10-06 14:49 | 2014-10-07 09:28 | 1118.35 | 7 | 6448.9833 | 0.019724 | 2.1409e-05 | Restore Supply on Device TD3-122 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 854225 | 2x DDO fuses replaced tx td3/122 cause wind, line clash | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 921.2833 | 918.2833 | 6427.9833 | 0.019634 | 2.1381e-05 | 2014-10-06 | C | 0.019634 | 2.1381e-05 | 2015 | 2014-10-06 | C | 7 | 0.019634 | 2.1381e-05
1 | 2270041 | 2014-10-06 15:00 | 2014-10-06 17:44 | 164 | 22 | 3608 | 0.011035 | 6.7285e-05 | Restore Supply on Device SG5-001 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SG5-001 | Lines down beyond 11kV Fuses SG5-001. Adverse Weather/Extreme Wind. Paul Cooper attended. | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 164 | 161 | 3542 | 0.010819 | 6.7197e-05 | 2014-10-06 | C | 0.010819 | 6.7197e-05 | 2015 | 2014-10-06 | C | 22 | 0.010819 | 6.7197e-05
1 | 2266629 | 2014-10-06 15:01 | 2014-10-08 18:48 | 3106.7667 | 6 | 4668 | 0.014277 | 1.8351e-05 | Restore Supply on Device 1433 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 745748 | Tx 1433. lv insulator, caused wire to go into the house, which dropped HT link 745748 | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 778 | 775 | 4650 | 0.014203 | 1.8327e-05 | 2014-10-06 | C | 0.014203 | 1.8327e-05 | 2015 | 2014-10-06 | C | 6 | 0.014203 | 1.8327e-05
1 | 2269687 | 2014-10-06 15:21 | 2014-10-06 18:13 | 171.7 | 9 | 1545.3 | 0.0047262 | 2.7526e-05 | Restore Supply on Device 7768 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 837165 | Fuses 7768 open and tagged. Large branch through lines at pole 837165. Repairs made and relivened. Nil materials. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 171.7 | 168.7 | 1518.3 | 0.0046375 | 2.749e-05 | 2014-10-06 | C | 0.0046375 | 2.749e-05 | 2015 | 2014-10-06 | C | 9 | 0.0046375 | 2.749e-05
1 | 2269705 | 2014-10-06 15:23 | 2014-10-08 21:34 | 3250.8 | 1 | 3250.8 | 0.0099423 | 3.0584e-06 | Restore Supply on Device X2409 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 791542 | REPLACED 2X HV 10AMP FUSES AT POLE 791542. Email sent to Jo, as appears to have SAIDI component. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3250.8 | 3247.8 | 3247.8 | 0.0099202 | 3.0544e-06 | 2014-10-06 | C | 0.0099202 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0099202 | 3.0544e-06
1 | 2269743 | 2014-10-06 15:27 | 2014-10-06 23:14 | 466.7333 | 4 | 1866.9333 | 0.0057099 | 1.2234e-05 | Restore Supply on Device SD6-011 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | NA |  | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 466.7333 | 463.7333 | 1854.9333 | 0.0056658 | 1.2218e-05 | 2014-10-06 | C | 0.0056658 | 1.2218e-05 | 2015 | 2014-10-06 | C | 4 | 0.0056658 | 1.2218e-05
1 | 2315596 | 2014-10-06 15:38 | 2014-10-07 18:25 | 1606.9 | 2 | 2179.1667 | 0.0066648 | 6.1168e-06 | Restore Supply on Device I26 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I26 | Fuses I26 put back in and holding, power restore,. pine tree has been defected | F4 | BROOKLANDS | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1089.5833 | 1086.5833 | 2173.1667 | 0.0066378 | 6.1088e-06 | 2014-10-06 | C | 0.0066378 | 6.109e-06 | 2015 | 2014-10-06 | C | 2 | 0.0066378 | 6.1088e-06
1 | 2270477 | 2014-10-06 15:41 | 2014-10-08 18:04 | 3022.6333 | 1 | 3022.6333 | 0.0092445 | 3.0584e-06 | Restore Supply on Device X434 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | x434 | 8.23am Retailer called for update replaced hv 5amp fuse on x434 hv oh. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3022.6333 | 3019.6333 | 3019.6333 | 0.0092232 | 3.0544e-06 | 2014-10-06 | C | 0.0092232 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0092232 | 3.0544e-06
1 | 2270482 | 2014-10-06 15:41 | 2014-10-06 18:05 | 144.0333 | 54 | 7777.8 | 0.023788 | 0.00016515 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2270482 | Recloser 4246 tripped on E/F B ph. Line patrolled and lines found down at 806858. Repairs made and relivened. | F4 | PUTORINO | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 144.0333 | 141.0333 | 7615.8 | 0.023262 | 0.00016494 | 2014-10-06 | C | 0.023262 | 0.00016494 | 2015 | 2014-10-06 | C | 54 | 0.023262 | 0.00016494
1 | 2273244 | 2014-10-06 15:48 | 2014-10-08 15:19 | 2851.1 | 143 | 359993.2 | 1.101 | 0.00043735 | Restore Supply on Device X2108 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x2108 Pole 844945 | Powerline going to house one of the pine trees has fallen ontop of the powerline. powerline isn't on the ground but powerline poles is quite bent. isolated customer line 512 koatanui road 3x 63a hrc fuse at transformer can not close job because come | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 2517.435 | 2514.435 | 359564.2 | 1.0983 | 0.00043678 | 2014-10-06 | C | 1.0983 | 0.00043678 | 2015 | 2014-10-06 | C | 143 | 1.0983 | 0.00043678
1 | 2274558 | 2014-10-06 15:53 | 2014-10-08 17:04 | 2950.2667 | 1 | 2950.2667 | 0.0090232 | 3.0584e-06 | Restore Supply on Device Y129 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | y129 | replaced 6x insulator & 30m conductor to get poles back up 3 span 1phase hv | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 2950.2667 | 2947.2667 | 2947.2667 | 0.0090022 | 3.0544e-06 | 2014-10-06 | C | 0.0090022 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0090022 | 3.0544e-06
1 | 2609621 | 2014-10-06 15:54 | 2014-10-06 20:28 | 274 | 943 | 258382 | 0.79024 | 0.0028841 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | CB11 | TWO FAULTS. 1 X blown jumper at CB11 and tree on line beyond Recloser 4261. Staged restoration completed and faults repaired. Scott Bullock and Roger Bland attended each separate fault. | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 274 | 271 | 255553 | 0.78057 | 0.0028803 | 2014-10-06 | C | 0.78057 | 0.0028803 | 2015 | 2014-10-06 | C | 943 | 0.78057 | 0.0028803
1 | 2270094 | 2014-10-06 15:57 | 2014-10-06 18:55 | 178.1667 | 217 | 26702.5667 | 0.081668 | 0.00066368 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P02734 | Line Down. Possible 11kV to 400V clash. Needs to be inspected before re livening line down at pole P02734 isolated ABS E87 | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 123.0533 | 120.0533 | 26051.5667 | 0.079573 | 0.00066281 | 2014-10-06 | C | 0.079573 | 0.00066281 | 2015 | 2014-10-06 | C | 217 | 0.079573 | 0.00066281
1 | 2275053 | 2014-10-06 15:58 | 2014-10-06 19:39 | 221.4333 | 341 | 46800.9 | 0.14314 | 0.0010429 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P44363 | Broken crossarm found at pole P44363. Tempory repairs made. Robin Smith and Trevor Pocock attended. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 137.246 | 134.246 | 45777.9 | 0.13983 | 0.0010416 | 2014-10-06 | C | 0.13983 | 0.0010416 | 2015 | 2014-10-06 | C | 341 | 0.13983 | 0.0010416
1 | 2290850 | 2014-10-06 16:00 | 2014-10-06 18:14 | 133.6333 | 1083 | 144724.9 | 0.44263 | 0.0033123 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 205960 |  | F3 | BROOKFIELD TCE | OTUMOETAI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 133.6333 | 130.6333 | 141475.9 | 0.43213 | 0.0033079 | 2014-10-06 | C | 0.43213 | 0.0033079 | 2015 | 2014-10-06 | C | 1083 | 0.43213 | 0.0033079
1 | 2520470 | 2014-10-06 16:04 | 2014-10-06 16:58 | 54 | 914 | 37252 | 0.11393 | 0.0027954 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | CB4 | Te Puke CB4 tripped - No flags. line patrolled and tree located against line at pole number 382886. Tree removed with long stick. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 40.7571 | 37.7571 | 34510 | 0.10541 | 0.0027917 | 2014-10-06 | C | 0.10541 | 0.0027917 | 2015 | 2014-10-06 | C | 914 | 0.10541 | 0.0027917
1 | 2284992 | 2014-10-06 16:17 | 2014-10-07 18:21 | 1564.55 | 26 | 38277.55 | 0.11707 | 7.9519e-05 | Restore Supply on Device 7233 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X1004 | Cust reporting fuses out on pole 812780 and 812781 - customer also reporting in Southerly winds, just down from 153 Hikinui Rd, the lines flash, no trees around. Please investigate if need spreaders or any trees around 2.33pm deassigned james mathews av | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1472.2135 | 1469.2135 | 38199.55 | 0.11668 | 7.9415e-05 | 2014-10-06 | C | 0.11668 | 7.9415e-05 | 2015 | 2014-10-06 | C | 26 | 0.11668 | 7.9415e-05
1 | 2278659 | 2014-10-06 16:19 | 2014-10-07 00:43 | 504.0167 | 1 | 504.0167 | 0.0015415 | 3.0584e-06 | Restore Supply on Device TE4-020 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE |  | replaced 2 X 10a HV Fuses @ FP1586. Email sent to Jo, as appears to have SAIDI component. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 504.0167 | 501.0167 | 501.0167 | 0.0015303 | 3.0544e-06 | 2014-10-06 | C | 0.0015303 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0015303 | 3.0544e-06
1 | 2278685 | 2014-10-06 16:21 | 2014-10-08 22:41 | 3259.6167 | 1 | 3259.6167 | 0.0099693 | 3.0584e-06 | Restore Supply on Device X1038 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X1038 | blown hv fuse (glass one) don't carry these in the truck or at the depot so Jeremy Hill sending Tony Sinclair to carry out replacement of fuse 2amp ddo hv o/h caused wind pole 804190 Actual address is : 492 Fern Flat Rd. REPLACED HV 3AMP FUSE HV OH X | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3259.6167 | 3256.6167 | 3256.6167 | 0.0099471 | 3.0544e-06 | 2014-10-06 | C | 0.0099471 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0099471 | 3.0544e-06
1 | 2278702 | 2014-10-06 16:23 | 2014-10-07 21:56 | 1773.55 | 1 | 1773.55 | 0.0054243 | 3.0584e-06 | Restore Supply on Device 2801T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 736879 | 7/10 6.37pm retailer doing followup customer still has no power stock stressed svs advised tarns following up. actual addres is 217 Barleymans Road, Stratford. REPLACED FUSE BOX AT POLE 736879 AND DISCO FOR SAFTEY AT PUMP AND WOOLSHED AS NEEDS METER RE | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1773.55 | 1770.55 | 1770.55 | 0.005408 | 3.0544e-06 | 2014-10-06 | C | 0.005408 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.005408 | 3.0544e-06
1 | 2296101 | 2014-10-06 16:43 | 2014-10-06 21:56 | 312.35 | 4 | 402.6667 | 0.0012315 | 1.2234e-05 | Restore Supply on Device FC2251 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses FC2251 | 2x 6A HV Fuses Replaced. All Power Restored completion. Marty Keenan Attended. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.6667 | 97.6667 | 390.6667 | 0.0011933 | 1.2218e-05 | 2014-10-06 | C | 0.0011933 | 1.2218e-05 | 2015 | 2014-10-06 | C | 4 | 0.0011933 | 1.2218e-05
1 | 2280901 | 2014-10-06 16:46 | 2014-10-06 17:08 | 22.15 | 121 | 1506.15 | 0.0046064 | 0.00037007 | Restore Supply on Device I32 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | RS I32 | RS I32 found tripped and closed | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 12.4475 | 9.4475 | 1143.15 | 0.0034917 | 0.00036959 | 2014-10-06 | C | 0.0034917 | 0.00036959 | 2015 | 2014-10-06 | C | 121 | 0.0034917 | 0.00036959
1 | 2689239 | 2014-10-06 16:59 | 2014-10-06 20:48 | 229 | 107 | 22723 | 0.069497 | 0.00032725 | Restore Supply on Device E33 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | n/a | Kelvin Grove RS E33 auto reclosed L/O B & C Phase. Broken cross arms located. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 212.3645 | 209.3645 | 22402 | 0.068425 | 0.00032682 | 2014-10-06 | C | 0.068425 | 0.00032682 | 2015 | 2014-10-06 | C | 107 | 0.068425 | 0.00032682
1 | 2281593 | 2014-10-06 17:03 | 2014-10-06 20:20 | 197.5 | 2 | 364.1167 | 0.0011136 | 6.1168e-06 | Restore Supply on Device TC3314 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | a12453 | replaced 2x 3a hv fuses due to wind. no lines down here. Email sent to Jo, as appears to have SAIDI component. | F3/F4 | ASHWORTH ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 182.0583 | 179.0583 | 358.1167 | 0.0010938 | 6.1088e-06 | 2014-10-06 | C | 0.0010938 | 6.109e-06 | 2015 | 2014-10-06 | C | 2 | 0.0010938 | 6.1088e-06
1 | 2285903 | 2014-10-06 17:26 | 2014-10-06 21:47 | 261.4 | 11 | 2875.4 | 0.0087942 | 3.3643e-05 | Restore Supply on Device LI725 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 729997 | branch on line at 30 wilson st removed branch from hv at line729997 fuse li275 2 x 10amp fuses | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 261.4 | 258.4 | 2842.4 | 0.0086819 | 3.3599e-05 | 2014-10-06 | C | 0.0086819 | 3.3599e-05 | 2015 | 2014-10-06 | C | 11 | 0.0086819 | 3.3599e-05
1 | 2285908 | 2014-10-06 17:26 | 2014-10-06 20:17 | 171.3667 | 903 | 128141.9167 | 0.39191 | 0.0027618 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB6 | Sanson CB6 auto reclosed - no flags. Line patrolled - no fault located. C Naylor attended. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 141.9069 | 138.9069 | 125432.9167 | 0.38313 | 0.0027581 | 2014-10-06 | C | 0.38313 | 0.0027581 | 2015 | 2014-10-06 | C | 903 | 0.38313 | 0.0027581
1 | 2608624 | 2014-10-06 17:31 | 2014-10-07 20:50 | 1639 | 719 | 189175 | 0.57858 | 0.002199 | Restore Supply on Device 4138 | 22000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 807122 | Rata CB4138 tripped - no flages. Line patrolled and lines down loctaed at pole 807122. Lines repaired. Materials used: 5 metres of 10mm Copper and 6 sleeves/ NDR 23180. During this outage a subsequent fault was located. This secondary fault (OMS J | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 263.1085 | 260.1085 | 187018 | 0.57123 | 0.0021961 | 2014-10-06 | C | 0.57123 | 0.0021961 | 2015 | 2014-10-06 | C | 719 | 0.57123 | 0.0021961
1 | 2290564 | 2014-10-06 17:51 | 2014-10-07 16:09 | 1337.3333 | 1 | 1337.3333 | 0.0040901 | 3.0584e-06 | Restore Supply on Device T1093 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | link # 7236 | 107 Buicks Road. replaced 10 amp fuse on link # 7236 cause: trees, has been defected. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1337.3333 | 1334.3333 | 1334.3333 | 0.0040756 | 3.0544e-06 | 2014-10-06 | C | 0.0040756 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0040756 | 3.0544e-06
1 | 2290631 | 2014-10-06 17:58 | 2014-10-07 00:45 | 406.8333 | 1 | 406.8333 | 0.0012443 | 3.0584e-06 | Restore Supply on Device TE4-063 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | SE4/010 | replaced 2 fuses @ SE4/010. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 406.8333 | 403.8333 | 403.8333 | 0.0012335 | 3.0544e-06 | 2014-10-06 | C | 0.0012335 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0012335 | 3.0544e-06
1 | 2290696 | 2014-10-06 18:06 | 2014-10-09 14:58 | 4131.4833 | 1 | 4131.4833 | 0.012636 | 3.0584e-06 | Restore Supply on Device X379 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 772635 | HV LINES DOWN 4 X 10 MM SLEEVES NO OTHER ASSETS REPAIRED OR REPLACED NO ADJACENT ASSETS OK. Email sent to Jo, as appears to have SAIDI component. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 4131.4833 | 4128.4833 | 4128.4833 | 0.01261 | 3.0544e-06 | 2014-10-06 | C | 0.01261 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.01261 | 3.0544e-06
1 | 2291984 | 2014-10-06 18:19 | 2014-10-07 13:19 | 1140.4833 | 14 | 12291.6667 | 0.037593 | 4.2818e-05 | Restore Supply on Device TE6-088 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SE6-084 | CB4 Paengaroa. Line patrolled and 2 x fuses found to be blown. Patrolled line past fuses SE6-084. No fault found. Reclosed fuses. Shane Pepperel & Paul Cooper attended. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 877.9762 | 874.9762 | 12249.6667 | 0.037416 | 4.2762e-05 | 2014-10-06 | C | 0.037416 | 4.2762e-05 | 2015 | 2014-10-06 | C | 14 | 0.037416 | 4.2762e-05
1 | 2292175 | 2014-10-06 18:34 | 2014-10-06 21:32 | 178.7 | 2 | 270.85 | 0.00082837 | 6.1168e-06 | Restore Supply on Device TF5-078 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 221395 | at 19:58 Te Puke Sub, CB 4 Paengaroa Feeder. Fuses FP347 found blown due to lines down at Pole 221395. Isolated Lines at Fuses FP347. Permit Issued & Repairs carried out. All Power Restored on completion. 10x Links Replaced & 1 Span all phases of conducto | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 135.425 | 132.425 | 264.85 | 0.00080896 | 6.1088e-06 | 2014-10-06 | C | 0.00080896 | 6.109e-06 | 2015 | 2014-10-06 | C | 2 | 0.00080896 | 6.1088e-06
1 | 2292400 | 2014-10-06 18:37 | 2014-10-06 21:02 | 145 | 711 | 103095 | 0.31531 | 0.0021745 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Wanganui East CB6 | Wanganui East CB6 Tripped - No FLags. Tripping due to feeder fault on HAT CB11. | F3 | IKITARA RD | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 145 | 142 | 100962 | 0.30838 | 0.0021717 | 2014-10-06 | C | 0.30838 | 0.0021717 | 2015 | 2014-10-06 | C | 711 | 0.30838 | 0.0021717
1 | 2293114 | 2014-10-06 18:38 | 2014-10-09 19:49 | 4390.45 | 1 | 4390.45 | 0.013428 | 3.0584e-06 | Restore Supply on Device T3/533 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tx t3/533 | 15kva tx t3/533 blown requiring replacement on pole P30788 2R requested as Shaz leaving site replaced tx tc 3/533 Email sent to Jo, as appears to have SAIDI component. | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 4390.45 | 4387.45 | 4387.45 | 0.013401 | 3.0544e-06 | 2014-10-06 | C | 0.013401 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.013401 | 3.0544e-06
1 | 2319518 | 2014-10-06 19:48 | 2014-10-08 20:04 | 2895.5333 | 14 | 27757.7833 | 0.084895 | 4.2818e-05 | Restore Supply on Device 707 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Fuses 707 | PLEASE CHECK GET FAULT MAN AT PUMP 93 HOLMWOOD ROAD. Adverse Weather/Extreme Wind on 6th October 2014. Replaced 2x 10Amp DDO Links | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1982.6988 | 1979.6988 | 27715.7833 | 0.084656 | 4.2762e-05 | 2014-10-06 | C | 0.084656 | 4.2762e-05 | 2015 | 2014-10-06 | C | 14 | 0.084656 | 4.2762e-05
1 | 2319602 | 2014-10-06 19:51 | 2014-10-07 11:30 | 939 | 1 | 939 | 0.0028719 | 3.0584e-06 | Restore Supply on Device TC5077 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 386497 | lines down past fuses FC 4058 At pole 386497 2 line guards 6 binders 1 6Amp Fuse | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 939 | 936 | 936 | 0.0028589 | 3.0544e-06 | 2014-10-06 | C | 0.0028589 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0028589 | 3.0544e-06
1 | 2295470 | 2014-10-06 20:00 | 2014-10-06 23:03 | 182.6667 | 575 | 99746.6667 | 0.30507 | 0.0017586 | Restore Supply on Device 242 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 772115 | Waverley SB C242 Tripped. Customer at 50 Weraroa Rd, by 4 Square, advising tx went up like lightning. Kane MacKay attended - no further information on NOC switching instruction sheet. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 173.4725 | 170.4725 | 98021.6667 | 0.2994 | 0.0017563 | 2014-10-06 | C | 0.2994 | 0.0017563 | 2015 | 2014-10-06 | C | 575 | 0.2994 | 0.0017563
1 | 2314687 | 2014-10-06 20:20 | 2014-10-07 11:07 | 887 | 200 | 147286.9667 | 0.45047 | 0.00061168 | Restore Supply on Device 4141 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | FUSES 2664 | Lines found to be down past Fuses 2664. Neville Ashton and Glen Most attended. Materials Used: 12 Sleeves and 20 metres of No 8 Wire. Related to 2293840 | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 736.4348 | 733.4348 | 146686.9667 | 0.44804 | 0.00061088 | 2014-10-06 | C | 0.44804 | 0.00061089 | 2015 | 2014-10-06 | C | 200 | 0.44804 | 0.00061088
1 | 2307337 | 2014-10-06 20:39 | 2014-10-07 14:21 | 1061.6167 | 610 | 415874.5667 | 1.2719 | 0.0018656 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB4225 | Arahina CB4225 tripped. O/C & E/F. Backfeed put in place and line patrolled - no known fault located. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 681.7616 | 678.7616 | 414044.5667 | 1.2647 | 0.0018632 | 2014-10-06 | C | 1.2647 | 0.0018632 | 2015 | 2014-10-06 | C | 610 | 1.2647 | 0.0018632
1 | 2294000 | 2014-10-06 21:00 | 2014-10-06 22:15 | 75 | 24 | 1800 | 0.0055052 | 7.3402e-05 | Restore Supply on Device T801 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 820113 | 11kv cross arm burning at pole 820113. Isolated for safety - links pulled. Bucket truck, cross arm, pins & insulators for 11kv. Faultman requested 2R. Email sent to Jo, as appears to have SAIDI component. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 75 | 72 | 1728 | 0.005278 | 7.3306e-05 | 2014-10-06 | C | 0.005278 | 7.3306e-05 | 2015 | 2014-10-06 | C | 24 | 0.005278 | 7.3306e-05
1 | 2298121 | 2014-10-06 21:10 | 2014-10-06 22:18 | 67.6167 | 661 | 44694.6167 | 0.13669 | 0.0020216 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND |  | POWER ACROSS ROAD JUST BLEW UP line Patrolled and branch on lines at pole | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 67.6167 | 64.6167 | 42711.6167 | 0.13046 | 0.002019 | 2014-10-06 | C | 0.13046 | 0.002019 | 2015 | 2014-10-06 | C | 661 | 0.13046 | 0.002019
1 | 2328582 | 2014-10-06 21:12 | 2014-10-08 03:28 | 1816.2667 | 550 | 473298.6 | 1.4475 | 0.0016821 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/gear IC1999 | at 17:22 Tairua Sub, CB 4 Pauanui Feeder, CB 9655/3 Tripped, No Flags (E/F O/C flagged up later on reclose attempt). Faultmen dispatched and investigation began. Feeder sectionalised. Isolated cables between Sw/gear 9630/3 & 9682/1. Permit issued and faul | F3 | PAUANUI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 860.5429 | 857.5429 | 471648.6 | 1.4406 | 0.0016799 | 2014-10-06 | C | 1.4406 | 0.0016799 | 2015 | 2014-10-06 | C | 550 | 1.4406 | 0.0016799
1 | 2299487 | 2014-10-06 22:00 | 2014-10-07 16:36 | 1115.9 | 1 | 1115.9 | 0.0034129 | 3.0584e-06 | Restore Supply on Device L4440 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728905 | replaced 6 amp hv fuse. pole 728905. cause: wind. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1115.9 | 1112.9 | 1112.9 | 0.0033993 | 3.0544e-06 | 2014-10-06 | C | 0.0033993 | 3.054e-06 | 2015 | 2014-10-06 | C | 1 | 0.0033993 | 3.0544e-06
1 | 2300214 | 2014-10-06 22:53 | 2014-10-07 00:30 | 96.9333 | 653 | 44770.3 | 0.13693 | 0.0019971 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T5/168 |  | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 68.5609 | 65.5609 | 42811.3 | 0.13076 | 0.0019945 | 2014-10-06 | C | 0.13076 | 0.0019945 | 2015 | 2014-10-06 | C | 653 | 0.13076 | 0.0019945
1 | 2521488 | 2014-10-06 23:12 | 2014-10-07 16:00 | 1008 | 6 | 6048 | 0.018497 | 1.8351e-05 | Restore Supply on Device SF7-024 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SF7-024 | Transformer exploded and is now hanging off the pole 648 rotoehu road, Te Puke 6.24pm advised Tarns at svs hub about job Patrolled line found NO fault Relivened 2 X 8amp fuses | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 1008 | 1005 | 6030 | 0.018418 | 1.8327e-05 | 2014-10-06 | C | 0.018418 | 1.8327e-05 | 2015 | 2014-10-06 | C | 6 | 0.018418 | 1.8327e-05
1 | 2301905 | 2014-10-06 23:26 | 2014-10-07 07:36 | 490.4667 | 911 | 115734.9167 | 0.35397 | 0.0027862 | Restore Supply on Device F21 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 843893 | Adverse Weather/Extreme Wind. Repair line and straighten pole 843893 and cross arm. | F1 | BLAKE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 127.0416 | 124.0416 | 113001.9167 | 0.34516 | 0.0027826 | 2014-10-06 | C | 0.34516 | 0.0027826 | 2015 | 2014-10-06 | C | 911 | 0.34516 | 0.0027826
1 | 2305766 | 2014-10-07 00:25 | 2014-10-07 16:05 | 939.8 | 36 | 33832.8 | 0.10347 | 0.0001101 | Restore Supply on Device 586 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784588 | Lines down at pole 784588. Materials used: 16 sleeves, 60m Bear Copper conductor, 2 x 6AMP HV Rewireable Fuses and 3 x 20AMP Rewireable Fuse. Craig Brogden and Paul Osborne attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 939.8 | 936.8 | 33724.8 | 0.10301 | 0.00010996 | 2014-10-07 | C | 0.10301 | 0.00010996 | 2015 | 2014-10-07 | C | 36 | 0.10301 | 0.00010996
1 | 2307932 | 2014-10-07 01:50 | 2014-10-07 04:18 | 147.7833 | 689 | 32837.3167 | 0.10043 | 0.0021073 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole P3145 | CB 8 ARC and tripped. Repaired floater on pole P33145. Chris Naylor and Mike Thompson attended. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 47.6594 | 44.6594 | 30770.3167 | 0.093986 | 0.0021045 | 2014-10-07 | C | 0.093986 | 0.0021045 | 2015 | 2014-10-07 | C | 689 | 0.093986 | 0.0021045
1 | 2311716 | 2014-10-07 05:07 | 2014-10-07 06:59 | 111.8667 | 759 | 51668.45 | 0.15802 | 0.0023213 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB4 | CB 4 L/O No flags. Sectionalised feeder and found no fault | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 68.0744 | 65.0744 | 49391.45 | 0.15086 | 0.0023183 | 2014-10-07 | C | 0.15086 | 0.0023183 | 2015 | 2014-10-07 | C | 759 | 0.15086 | 0.0023183
1 | 2315370 | 2014-10-07 08:17 | 2014-10-11 10:58 | 5920.7667 | 1 | 5920.7667 | 0.018108 | 3.0584e-06 | Restore Supply on Device T9/152 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V42 | x2 10amp fuses blwon at links V42 due to weather No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 5920.7667 | 5917.7667 | 5917.7667 | 0.018075 | 3.0544e-06 | 2014-10-07 | C | 0.018075 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.018075 | 3.0544e-06
1 | 2328400 | 2014-10-07 08:24 | 2014-10-07 18:19 | 594.9333 | 54 | 2661.9333 | 0.0081413 | 0.00016515 | Restore Supply on Device SE4-014 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TE4-158 | Found DDO broken at transformer TE4-158. Isolated between ABS 9705/1, SE4-014 & links 9507/6. Replaced broken DDO unit and relivened | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 49.2951 | 46.2951 | 2499.9333 | 0.0076359 | 0.00016494 | 2014-10-07 | C | 0.0076359 | 0.00016494 | 2015 | 2014-10-07 | C | 54 | 0.0076359 | 0.00016494
1 | 2529117 | 2014-10-07 08:42 | 2014-10-07 08:50 | 8 | 196 | 1568 | 0.0047956 | 0.00059945 | Restore Supply on Device D75 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS D77 | No Power - line patrolled and blown jumper located and ABS D77. DNO Tag 141007 assigned to ABS D77. Power restored. Dave Thomson attended. | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 8 | 5 | 980 | 0.0029933 | 0.00059867 | 2014-10-07 | C | 0.0029933 | 0.00059867 | 2015 | 2014-10-07 | C | 196 | 0.0029933 | 0.00059867
1 | 2315550 | 2014-10-07 08:42 | 2014-10-09 10:47 | 3005.1167 | 1 | 3005.1167 | 0.0091909 | 3.0584e-06 | Restore Supply on Device T470 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T470 | 1 x 3 amp hv fuse replaced. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 3005.1167 | 3002.1167 | 3002.1167 | 0.0091697 | 3.0544e-06 | 2014-10-07 | C | 0.0091697 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0091697 | 3.0544e-06
1 | 2316636 | 2014-10-07 08:57 | 2014-10-07 14:20 | 323.3167 | 9 | 1408.6667 | 0.0043083 | 2.7526e-05 | Restore Supply on Device 361 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8455 | replaced 2x 10a hv fuse links | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 156.5185 | 153.5185 | 1381.6667 | 0.0042202 | 2.749e-05 | 2014-10-07 | C | 0.0042202 | 2.749e-05 | 2015 | 2014-10-07 | C | 9 | 0.0042202 | 2.749e-05
1 | 2332319 | 2014-10-07 08:58 | 2014-10-08 13:48 | 1730 | 17 | 7814.9333 | 0.023901 | 5.1993e-05 | Restore Supply on Device X1595 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 772 | roger has been dealing with control at 2.08pm 23/10 Email sent to hub for follow up gum tree bark on line removed by hot stick and relivened | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 459.702 | 456.702 | 7763.9333 | 0.023714 | 5.1925e-05 | 2014-10-07 | C | 0.023714 | 5.1925e-05 | 2015 | 2014-10-07 | C | 17 | 0.023714 | 5.1925e-05
1 | 2369188 | 2014-10-07 09:05 | 2014-10-07 10:17 | 72 | 17 | 1224 | 0.0037435 | 5.1993e-05 | Restore Supply on Device 10105 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | P21370 | Faultman found lines down at pole P21370, line was made safe, faultman to return in morning. Line was isolated at FusedABS 10105 to repair line down. 5 meters of squirrel conductor was used and 2 x sleeves. Shazil Khan attended. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 1173 | 0.0035828 | 5.1925e-05 | 2014-10-07 | C | 0.0035828 | 5.1925e-05 | 2015 | 2014-10-07 | C | 17 | 0.0035828 | 5.1925e-05
1 | 2317456 | 2014-10-07 09:15 | 2014-10-07 15:50 | 394.5833 | 2 | 695.6167 | 0.0021275 | 6.1168e-06 | Restore Supply on Device TD4-642 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 210811 | Replaced 11KV fuse. Caused by wind and trees. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 347.8083 | 344.8083 | 689.6167 | 0.0021064 | 6.1088e-06 | 2014-10-07 | C | 0.0021064 | 6.109e-06 | 2015 | 2014-10-07 | C | 2 | 0.0021064 | 6.1088e-06
1 | 1941078 | 2014-10-07 09:25 | 2014-10-07 14:20 | 295.6333 | 41 | 12120.9667 | 0.037071 | 0.0001254 | NAPA ID:02210 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP564 | To replace 11kV cross arms and hardware between ABS IP564 and IP585. Works location: Arapuni Rd. WO 10158134. | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 295.6333 | 292.6333 | 11997.9667 | 0.036647 | 0.00012523 | 2014-10-07 | B | 0.018323 | 6.2616e-05 | 2015 | 2014-10-07 | B | 41 | 0.036647 | 0.00012523
1 | 1882046 | 2014-10-07 09:31 | 2014-10-07 14:58 | 327.4 | 10 | 3274 | 0.010013 | 3.0584e-05 | NAPA ID:02057 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3720T | Replace all HV and LV crossarms on Surrey Rd Inglewood 6.6kV lines. Works location: Surrey Rd, Tariki, Inglewood. WO 10150398. | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 327.4 | 324.4 | 3244 | 0.0099086 | 3.0544e-05 | 2014-10-07 | B | 0.0049543 | 1.5272e-05 | 2015 | 2014-10-07 | B | 10 | 0.0099086 | 3.0544e-05
1 | 2402386 | 2014-10-07 09:31 | 2014-10-07 11:30 | 119 | 6 | 714 | 0.0021837 | 1.8351e-05 | Restore Supply on Device 638 | 22000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 808345 | Line down at pole 808345.kevin Anderson attended. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 119 | 116 | 696 | 0.0021259 | 1.8327e-05 | 2014-10-07 | C | 0.0021259 | 1.8327e-05 | 2015 | 2014-10-07 | C | 6 | 0.0021259 | 1.8327e-05
1 | 2317203 | 2014-10-07 10:00 | 2014-10-07 15:50 | 350 | 66 | 23100 | 0.07065 | 0.00020186 | Restore Supply on Device 7607 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1420 |  | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 350 | 347 | 22902 | 0.069952 | 0.00020159 | 2014-10-07 | C | 0.069952 | 0.00020159 | 2015 | 2014-10-07 | C | 66 | 0.069952 | 0.00020159
1 | 2316539 | 2014-10-07 10:06 | 2014-10-07 15:05 | 298.8333 | 1 | 298.8333 | 0.00091396 | 3.0584e-06 | Restore Supply on Device SE6-152 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SE6-152 | Found cross arm broken & lines down beyound fuses SE6-152. Isolated at fuses, carried out repairs & relivened. Jayden Milburn attended. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 298.8333 | 295.8333 | 295.8333 | 0.0009036 | 3.0544e-06 | 2014-10-07 | C | 0.0009036 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0009036 | 3.0544e-06
1 | 2317476 | 2014-10-07 10:51 | 2014-10-08 15:36 | 1725.1833 | 1 | 1725.1833 | 0.0052763 | 3.0584e-06 | Restore Supply on Device T5/209 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 91 MANGORIRA ROAD | 8/10 11:33am Cust still has low voltage since Monday 2 x 6amp ht fuses due to wind nothing else repaired or replaced adjacent assets ok Email to Jo to check | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1725.1833 | 1722.1833 | 1722.1833 | 0.0052603 | 3.0544e-06 | 2014-10-07 | C | 0.0052603 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0052603 | 3.0544e-06
1 | 2319663 | 2014-10-07 11:28 | 2014-10-07 11:56 | 28 | 8 | 224 | 0.00068509 | 2.4467e-05 | Restore Supply on Device SE6-096 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SE6-096 | Found jumper broken on ABS SE6-096. Opened ABS SE6-096 and carried out repairs. Closed. | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 200 | 0.00061088 | 2.4435e-05 | 2014-10-07 | C | 0.00061089 | 2.4435e-05 | 2015 | 2014-10-07 | C | 8 | 0.00061088 | 2.4435e-05
1 | 2319490 | 2014-10-07 11:30 | 2014-10-09 14:58 | 3087.5333 | 1 | 3087.5333 | 0.009443 | 3.0584e-06 | Restore Supply on Device T4/151 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | t4/151 | 1 x hd line tap caused by weather, FM advises adjacent assets are not up to POCO standard, asked him to defect as he see's necessary. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 3087.5333 | 3084.5333 | 3084.5333 | 0.0094215 | 3.0544e-06 | 2014-10-07 | C | 0.0094215 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0094215 | 3.0544e-06
1 | 2319724 | 2014-10-07 11:43 | 2014-10-07 14:00 | 137 | 1 | 137 | 0.000419 | 3.0584e-06 | Restore Supply on Device FP1243 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FP1243 | Found line down at FP1243. Isolated at fuses and repaired line down. Relivened | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 137 | 134 | 134 | 0.00040929 | 3.0544e-06 | 2014-10-07 | C | 0.00040929 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.00040929 | 3.0544e-06
1 | 2320003 | 2014-10-07 12:34 | 2014-10-09 09:17 | 2682.7167 | 1 | 2682.7167 | 0.0082049 | 3.0584e-06 | Restore Supply on Device M4310 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 717732 | 8/10 1558hrs called customer to see if power restored - no response 3 x 2 hv fuses due to lightning no other assets repaired or replaced adjacent assets ok Email to Jo to check | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2682.7167 | 2679.7167 | 2679.7167 | 0.008185 | 3.0544e-06 | 2014-10-07 | C | 0.008185 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.008185 | 3.0544e-06
1 | 2320069 | 2014-10-07 12:46 | 2014-10-07 14:55 | 128.6 | 1 | 128.6 | 0.00039331 | 3.0584e-06 | Restore Supply on Device TC2583 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | fp1409 | replaced 2x by hv 6amp fuses hv oh at fuse fp1409 due to wind. | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 128.6 | 125.6 | 125.6 | 0.00038364 | 3.0544e-06 | 2014-10-07 | C | 0.00038364 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.00038364 | 3.0544e-06
1 | 2327970 | 2014-10-07 12:57 | 2014-10-07 14:50 | 113 | 41 | 4308 | 0.013176 | 0.0001254 | Restore Supply on Device I4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB I4 | Ihuraua CB I4 tripped. No fault found. | F4 | IHURAUA | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 105.0732 | 102.0732 | 4185 | 0.012783 | 0.00012523 | 2014-10-07 | C | 0.012783 | 0.00012523 | 2015 | 2014-10-07 | C | 41 | 0.012783 | 0.00012523
1 | 2316379 | 2014-10-07 12:59 | 2014-10-07 19:26 | 387.4833 | 35 | 13561.9167 | 0.041478 | 0.00010704 | Restore Supply on Device TB1-028 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 208561 | at 16:25, Katikati Sub, CB 4 Wharawhara Rd Feeder. Found broken crossarm at Pole 208561. Isolated Lines at Fuses SB1-003. Permit Issued & Repairs carried out. all power restored on completion. Paul Cooper Attended. 1x Crossarm, 1x HV Fuse Holder & 1x 6A H | F4 | WHARAWHARA ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 387.4833 | 384.4833 | 13456.9167 | 0.041103 | 0.0001069 | 2014-10-07 | C | 0.041103 | 0.0001069 | 2015 | 2014-10-07 | C | 35 | 0.041103 | 0.0001069
1 | 2322890 | 2014-10-07 13:20 | 2014-10-09 16:02 | 3042.6 | 1 | 3042.6 | 0.0093056 | 3.0584e-06 | Restore Supply on Device X2462 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | switch4189 | replaced 3 ddo fsues at switch 4189 due wind set of ddo fuses email to Jo to check | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 3042.6 | 3039.6 | 3039.6 | 0.0092842 | 3.0544e-06 | 2014-10-07 | C | 0.0092842 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0092842 | 3.0544e-06
1 | 2326668 | 2014-10-07 14:49 | 2014-10-08 12:56 | 1327.3833 | 1 | 1327.3833 | 0.0040597 | 3.0584e-06 | Restore Supply on Device X1563 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 780559 | 2 X 11KV 2 AMP DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK sent to Jo to check | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1327.3833 | 1324.3833 | 1324.3833 | 0.0040452 | 3.0544e-06 | 2014-10-07 | C | 0.0040452 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0040452 | 3.0544e-06
1 | 1857808 | 2014-10-07 22:06 | 2014-10-07 23:48 | 101.8667 | 367 | 37385.0667 | 0.11434 | 0.0011224 | NAPA ID:02467 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814892 | To make line break 814892 to be used for shutdown following day to change T1844. Works location: East St Greytown WO 10140873. IR6938 | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 101.8667 | 98.8667 | 36284.0667 | 0.11083 | 0.001121 | 2014-10-07 | B | 0.055413 | 0.00056049 | 2015 | 2014-10-07 | B | 367 | 0.11083 | 0.001121
1 | 2331357 | 2014-10-07 23:53 | 2014-10-08 18:43 | 1130.0333 | 1 | 1130.0333 | 0.0034561 | 3.0584e-06 | Restore Supply on Device X1134 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1134 | Replaced 2 x 2A HV fuse due to lightning. All other assets okay; nothing else replaced. email to Jo to check | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1130.0333 | 1127.0333 | 1127.0333 | 0.0034424 | 3.0544e-06 | 2014-10-07 | C | 0.0034424 | 3.054e-06 | 2015 | 2014-10-07 | C | 1 | 0.0034424 | 3.0544e-06
1 | 2331964 | 2014-10-08 04:50 | 2014-10-08 06:22 | 92.25 | 3 | 125.95 | 0.00038521 | 9.1753e-06 | Restore Supply on Device TC3939 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses FC4011 | 2x 6A HV Fuses Replaced at FC4011. Don Watson Attended. No Pole Was down. | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 41.9833 | 38.9833 | 116.95 | 0.00035721 | 9.1633e-06 | 2014-10-08 | C | 0.00035721 | 9.163e-06 | 2015 | 2014-10-08 | C | 3 | 0.00035721 | 9.1633e-06
1 | 2332193 | 2014-10-08 08:20 | 2014-10-09 13:39 | 1759.85 | 1 | 1759.85 | 0.0053824 | 3.0584e-06 | Restore Supply on Device X588 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 792122 | need glass hv fuse tx 903 this one customer pump does not have the equipment will be reapired tomorrow replaced 2x 5amp rewireable glass fuses 11kv on tx x903 | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1759.85 | 1756.85 | 1756.85 | 0.0053662 | 3.0544e-06 | 2014-10-08 | C | 0.0053662 | 3.054e-06 | 2015 | 2014-10-08 | C | 1 | 0.0053662 | 3.0544e-06
1 | 1945500 | 2014-10-08 08:42 | 2014-10-08 13:04 | 262 | 1 | 262 | 0.00080131 | 3.0584e-06 | NAPA ID:02952 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B34 | Change two x 11kv poles and 1 x tx fitout. Works location: Hwy 56 WO 10156813 | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 262 | 259 | 259 | 0.0007911 | 3.0544e-06 | 2014-10-08 | B | 0.00039555 | 1.527e-06 | 2015 | 2014-10-08 | B | 1 | 0.0007911 | 3.0544e-06
1 | 2332272 | 2014-10-08 08:43 | 2014-10-08 22:22 | 819.05 | 1 | 819.05 | 0.002505 | 3.0584e-06 | Restore Supply on Device X267 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | pole 804546 | replaced 3amp hv ddo tx fuse hv o/h pole 804546 cause lightning full power restored | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 819.05 | 816.05 | 816.05 | 0.0024926 | 3.0544e-06 | 2014-10-08 | C | 0.0024926 | 3.054e-06 | 2015 | 2014-10-08 | C | 1 | 0.0024926 | 3.0544e-06
1 | 1936850 | 2014-10-08 08:45 | 2014-10-08 14:28 | 343 | 16 | 5488 | 0.016785 | 4.8935e-05 | NAPA ID:02323 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 386273 | REPLACE POLES AND RECON 16MM CU HV FEEDER WIRES. Works location: Maketu Rd WO 10145449 | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 343 | 340 | 5440 | 0.016616 | 4.8871e-05 | 2014-10-08 | B | 0.008308 | 2.4435e-05 | 2015 | 2014-10-08 | B | 16 | 0.016616 | 4.8871e-05
1 | 1855979 | 2014-10-08 08:45 | 2014-10-08 14:32 | 347.3 | 9 | 3125.7 | 0.0095597 | 2.7526e-05 | NAPA ID:02727 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Fuse Links V42 | To Cut Trees Clear of 11Kv Lines. Works location: Soldiers Rd WO 10149505 | F3 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 347.3 | 344.3 | 3098.7 | 0.0094647 | 2.749e-05 | 2014-10-08 | B | 0.0047324 | 1.3745e-05 | 2015 | 2014-10-08 | B | 9 | 0.0094647 | 2.749e-05
1 | 1909095 | 2014-10-08 09:19 | 2014-10-08 15:24 | 364.3833 | 33 | 12024.65 | 0.036776 | 0.00010093 | NAPA ID:02797 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 6600 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC552 | Replace poles and arms between IC552 & IC2566. Works location: Tahuna Rd Paeroa WO 10148309 | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 364.3833 | 361.3833 | 11925.65 | 0.036426 | 0.0001008 | 2014-10-08 | B | 0.018213 | 5.0398e-05 | 2015 | 2014-10-08 | B | 33 | 0.036426 | 0.0001008
1 | 1970790 | 2014-10-08 09:27 | 2014-10-08 16:01 | 394.0833 | 10 | 3940.8333 | 0.012053 | 3.0584e-05 | NAPA ID:02209 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5666 | 11kv pole and cross arm upgrade. Works location: Mohakau Rd WO IR1872 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 394.0833 | 391.0833 | 3910.8333 | 0.011945 | 3.0544e-05 | 2014-10-08 | B | 0.0059727 | 1.5272e-05 | 2015 | 2014-10-08 | B | 10 | 0.011945 | 3.0544e-05
1 | 1672295 | 2014-10-08 09:31 | 2014-10-08 14:37 | 306.3 | 1 | 306.3 | 0.00093679 | 3.0584e-06 | NAPA ID:01789 TP_STRATFORD GXP > ELTHAM SUB > MANGATOKI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4566T | AP1: Replace Tx 4566T like-for-like. AP2: 10 Yearly 11kV metering calibration switch gear 4963 Works location: Riverlands WO 10144542 | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 306.3 | 303.3 | 303.3 | 0.00092641 | 3.0544e-06 | 2014-10-08 | B | 0.0004632 | 1.527e-06 | 2015 | 2014-10-08 | B | 1 | 0.00092641 | 3.0544e-06
1 | 1970757 | 2014-10-08 10:00 | 2014-10-08 12:55 | 174.9 | 26 | 4547.4 | 0.013908 | 7.9519e-05 | NAPA ID:03009 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 313 | Replace ABS313 And Pole. Works location: Dorset Rd New Plymouth WO 10152115 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 174.9 | 171.9 | 4469.4 | 0.013651 | 7.9415e-05 | 2014-10-08 | B | 0.0068257 | 3.9708e-05 | 2015 | 2014-10-08 | B | 26 | 0.013651 | 7.9415e-05
1 | 2333220 | 2014-10-08 10:09 | 2014-10-08 13:52 | 223 | 88 | 14398 | 0.044035 | 0.00026914 | Restore Supply on Device C926 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 798055 | Tuhitarata CB C926 Tripped. L/O A/B Phase O/C. Line patrolled - Burnt cross arm located. Repair burnt cross arm on pole 798055. Temporary repair made to cross arm. Material used: 3 x binders. Joe Mathews attended. | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 163.6136 | 160.6136 | 14134 | 0.043171 | 0.00026879 | 2014-10-08 | C | 0.043171 | 0.00026879 | 2015 | 2014-10-08 | C | 88 | 0.043171 | 0.00026879
1 | 2334015 | 2014-10-08 11:21 | 2014-10-08 13:02 | 100.9333 | 16 | 100.9333 | 0.0003087 | 4.8935e-05 | Restore Supply on Device V77 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V80 | Parent job is OMS 233017. Isolation at Fuses V77. Jumper replaced on fuses V80. 1 metre of squirrel | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 6.3083 | 3.3083 | 52.9333 | 0.00016168 | 4.8871e-05 | 2014-10-08 | C | 0.00016168 | 4.8871e-05 | 2015 | 2014-10-08 | C | 16 | 0.00016168 | 4.8871e-05
1 | 2335104 | 2014-10-08 11:51 | 2014-10-08 12:22 | 31.1833 | 29 | 904.3167 | 0.0027658 | 8.8694e-05 | Restore Supply on Device 058 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 794463 | Pa Koru attended site - second fault on feeder. Patrol found lines down at pole 794463. Materials: 3m of conductor 4 joins | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 31.1833 | 28.1833 | 817.3167 | 0.0024964 | 8.8578e-05 | 2014-10-08 | C | 0.0024964 | 8.8578e-05 | 2015 | 2014-10-08 | C | 29 | 0.0024964 | 8.8578e-05
1 | 2334751 | 2014-10-08 12:23 | 2014-10-08 13:01 | 38.0167 | 300 | 7051.4833 | 0.021566 | 0.00091753 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB XT40 | Parkville CB XT40 tripped and L/O at 11:44. Alfredton ABS XT45 opened. Fault unknown. Need to do line patrol on 33kV line between Parkville and Alfredton. | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 23.5049 | 20.5049 | 6151.4833 | 0.018789 | 0.00091633 | 2014-10-08 | C | 0.018789 | 0.00091633 | 2015 | 2014-10-08 | C | 300 | 0.018789 | 0.00091633
1 | 2335876 | 2014-10-08 12:38 | 2014-10-09 11:22 | 1364.1333 | 1 | 1364.1333 | 0.0041721 | 3.0584e-06 | Restore Supply on Device X4241 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 360706 | 2x 6amp hv fuses & candle ?No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1364.1333 | 1361.1333 | 1361.1333 | 0.0041575 | 3.0544e-06 | 2014-10-08 | C | 0.0041575 | 3.054e-06 | 2015 | 2014-10-08 | C | 1 | 0.0041575 | 3.0544e-06
1 | 2335886 | 2014-10-08 12:40 | 2014-10-08 14:52 | 131.9167 | 66 | 5756.5 | 0.017606 | 0.00020186 | Restore Supply on Device CB12 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P32798 | Feilding CB12 tripped L/O B phase O/C & E/F. Line patrolled and blown insulator located at pole P32798. 1 x 11kV insulator and binder used. Les Robinson and Bruce Mehrtens attended. | F1 | KAWAKAWA | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 87.2197 | 84.2197 | 5558.5 | 0.016978 | 0.00020159 | 2014-10-08 | C | 0.016978 | 0.00020159 | 2015 | 2014-10-08 | C | 66 | 0.016978 | 0.00020159
1 | 2337204 | 2014-10-08 13:16 | 2014-10-08 16:43 | 206.7167 | 331 | 15989.55 | 0.048903 | 0.0010123 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4258/2 | Recloser 4258/2 tripped, L/O. Line patrolled and broken cross arm located. Cross arm replaced (temporary repair) and 3 x 11kV insulators replaced. Note: Cross arm will be replaced at a later time. Tracey Hall attended. | F4 | BUNNYTHORPE | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 48.3068 | 45.3068 | 14996.55 | 0.045806 | 0.001011 | 2014-10-08 | C | 0.045806 | 0.001011 | 2015 | 2014-10-08 | C | 331 | 0.045806 | 0.001011
1 | 2372947 | 2014-10-08 13:17 | 2014-10-09 12:41 | 1404 | 109 | 148084 | 0.4529 | 0.00033337 | Restore Supply on Device M79 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P19832 |  | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1358.5688 | 1355.5688 | 147757 | 0.45131 | 0.00033293 | 2014-10-08 | C | 0.45131 | 0.00033293 | 2015 | 2014-10-08 | C | 109 | 0.45131 | 0.00033293
1 | 2337659 | 2014-10-08 13:18 | 2014-10-08 18:42 | 324.0333 | 1239 | 371032 | 1.1348 | 0.0037894 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P13215 |  | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 299.4609 | 296.4609 | 367315 | 1.1219 | 0.0037844 | 2014-10-08 | C | 1.1219 | 0.0037844 | 2015 | 2014-10-08 | C | 1239 | 1.1219 | 0.0037844
1 | 2327743 | 2014-10-08 14:38 | 2014-10-08 16:14 | 96 | 40 | 3840 | 0.011744 | 0.00012234 | Restore Supply on Device U39 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P15280 | Mauriceville U39 tripped. Floating conductor found at Pole P15280. 3 x 11kV clamp top insulators replaced. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 96 | 93 | 3720 | 0.011362 | 0.00012218 | 2014-10-08 | C | 0.011362 | 0.00012218 | 2015 | 2014-10-08 | C | 40 | 0.011362 | 0.00012218
1 | 2351378 | 2014-10-08 15:15 | 2014-10-09 14:38 | 1403.0667 | 20 | 2722.7 | 0.0083272 | 6.1168e-05 | Restore Supply on Device S11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | p26397 | 2x 10amp 11kv fuses No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard? | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 136.135 | 133.135 | 2662.7 | 0.008133 | 6.1088e-05 | 2014-10-08 | C | 0.008133 | 6.1088e-05 | 2015 | 2014-10-08 | C | 20 | 0.008133 | 6.1088e-05
1 | 2350071 | 2014-10-08 15:41 | 2014-10-09 22:42 | 1860.6333 | 211 | 28274 | 0.086474 | 0.00064533 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3/223 | CB4 tripped and L/O on E/F. Insulator replaced at T3/323 and also branch emoved from the line at pole P29657 with hot line sticks. 11kV insulator replaced. | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 134 | 131 | 27641 | 0.084427 | 0.00064448 | 2014-10-08 | C | 0.084427 | 0.00064448 | 2015 | 2014-10-08 | C | 211 | 0.084427 | 0.00064448
1 | 2351487 | 2014-10-08 15:42 | 2014-10-08 22:04 | 381.7 | 49 | 11926.4833 | 0.036476 | 0.00014986 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P11946 | RS 4443/2 tripped on E/F. Broken insulator found at pole P11946. 11kV insulator and binder used. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 243.3976 | 240.3976 | 11779.4833 | 0.03598 | 0.00014967 | 2014-10-08 | C | 0.03598 | 0.00014967 | 2015 | 2014-10-08 | C | 49 | 0.03598 | 0.00014967
1 | 2351283 | 2014-10-08 16:08 | 2014-10-10 08:40 | 2432.6833 | 43 | 94521.55 | 0.28909 | 0.00013151 | Restore Supply on Device P47 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P13479 | Two floating conductors found at pole P13479. Chris Naylor attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 2198.1756 | 2195.1756 | 94392.55 | 0.28831 | 0.00013134 | 2014-10-08 | C | 0.28831 | 0.00013134 | 2015 | 2014-10-08 | C | 43 | 0.28831 | 0.00013134
1 | 2355903 | 2014-10-08 17:13 | 2014-10-08 21:45 | 272.25 | 242 | 25808.3 | 0.078933 | 0.00074014 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB LI 1 | Livingstone LI1 tripped. A/R, L/O, E/F. Sectionalised & Patrolled, No fault found. Kaine Mackay attended. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 106.6459 | 103.6459 | 25082.3 | 0.076612 | 0.00073917 | 2014-10-08 | C | 0.076612 | 0.00073917 | 2015 | 2014-10-08 | C | 242 | 0.076612 | 0.00073917
1 | 2379559 | 2014-10-08 17:54 | 2014-10-09 14:26 | 1232 | 5 | 6160 | 0.01884 | 1.5292e-05 | Restore Supply on Device 052 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 052 |  | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1232 | 1229 | 6145 | 0.018769 | 1.5272e-05 | 2014-10-08 | C | 0.018769 | 1.5272e-05 | 2015 | 2014-10-08 | C | 5 | 0.018769 | 1.5272e-05
1 | 2332324 | 2014-10-08 21:48 | 2014-10-09 03:28 | 340 | 7 | 2380 | 0.007279 | 2.1409e-05 | Restore Supply on Device V42 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 794463 | pa koru attended site second fault on feeder found lines down at pole 794463 materials 3m of cionductor 4 joins | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 340 | 337 | 2359 | 0.0072054 | 2.1381e-05 | 2014-10-08 | C | 0.0072054 | 2.1381e-05 | 2015 | 2014-10-08 | C | 7 | 0.0072054 | 2.1381e-05
1 | 2357222 | 2014-10-09 06:39 | 2014-10-09 10:56 | 256.5833 | 2 | 513.1667 | 0.0015695 | 6.1168e-06 | Restore Supply on Device FC913 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | D12877 | Pole D12877 burning. Shortened pole & Replaced Crossarm. Materials used: 1 x arm and 3 x insulators. Perry Hicks attended. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 256.5833 | 253.5833 | 507.1667 | 0.0015491 | 6.1088e-06 | 2014-10-09 | C | 0.0015491 | 6.109e-06 | 2015 | 2014-10-09 | C | 2 | 0.0015491 | 6.1088e-06
1 | 1936851 | 2014-10-09 08:46 | 2014-10-09 12:17 | 210.7333 | 16 | 3356 | 0.010264 | 4.8935e-05 | NAPA ID:02324 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 386273 | REPLACE POLES AND RECON 16MM CU HV FEEDER WIRES. Works location: Maketu Rd WO 10145449 | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 209.75 | 206.75 | 3308 | 0.010104 | 4.8871e-05 | 2014-10-09 | B | 0.005052 | 2.4435e-05 | 2015 | 2014-10-09 | B | 16 | 0.010104 | 4.8871e-05
1 | 1883557 | 2014-10-09 09:01 | 2014-10-09 15:04 | 363.1167 | 42 | 15250.9 | 0.046644 | 0.00012845 | NAPA ID:02861 TP_MASTERTON GXP > CLAREVILLE SUB > WYNDHAM ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Links 7595 | Lower Sw/gear 11027 by 150mm. Works location: Hornsby St Carterton WO 10125724 | F2 | WYNDHAM ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 363.1167 | 360.1167 | 15124.9 | 0.046198 | 0.00012829 | 2014-10-09 | B | 0.023099 | 6.4143e-05 | 2015 | 2014-10-09 | B | 42 | 0.046198 | 0.00012829
1 | 2074737 | 2014-10-09 09:02 | 2014-10-09 17:22 | 499.3833 | 5 | 2496.9167 | 0.0076366 | 1.5292e-05 | NAPA ID:03080 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36227 | Isolate 11kv spur line and change 8 x 11kv poles, change 1 x TX pole complete re use existing transformer. Works location: Hwy 56 WO 10156813 | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 499.3833 | 496.3833 | 2481.9167 | 0.0075808 | 1.5272e-05 | 2014-10-09 | B | 0.0037904 | 7.636e-06 | 2015 | 2014-10-09 | B | 5 | 0.0075808 | 1.5272e-05
1 | 1936904 | 2014-10-09 09:20 | 2014-10-09 12:34 | 194.2167 | 84 | 16314.2 | 0.049896 | 0.00025691 | NAPA ID:02738 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > GRAVATT RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-101 | REPLACE NOISEY TX TD5-101 FOR NEW UNIT. Works location: McAllum Place/Gravatt Rd WO 10148648 | F2 | GRAVATT RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 194.2167 | 191.2167 | 16062.2 | 0.049061 | 0.00025657 | 2014-10-09 | B | 0.02453 | 0.00012829 | 2015 | 2014-10-09 | B | 84 | 0.049061 | 0.00025657
1 | 2371908 | 2014-10-09 09:31 | 2014-10-09 14:55 | 324 | 6 | 1944 | 0.0059456 | 1.8351e-05 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS3281 | Install new 33kV ABS 3281 and associated cross member. | F4 | TOTMANS RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 324 | 321 | 1926 | 0.0058828 | 1.8327e-05 | 2014-10-09 | C | 0.0058828 | 1.8327e-05 | 2015 | 2014-10-09 | C | 6 | 0.0058828 | 1.8327e-05
1 | 1970330 | 2014-10-09 09:34 | 2014-10-09 13:35 | 241.1 | 16 | 3857.6 | 0.011798 | 4.8935e-05 | NAPA ID:02813 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | O3300 | Change arms on poles O3300 & O3299. Works location: Bush Rd Pipiroa WO 10147779 | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 241.1 | 238.1 | 3809.6 | 0.011636 | 4.8871e-05 | 2014-10-09 | B | 0.0058181 | 2.4435e-05 | 2015 | 2014-10-09 | B | 16 | 0.011636 | 4.8871e-05
1 | 2379491 | 2014-10-09 09:45 | 2014-10-09 14:54 | 309 | 8 | 2472 | 0.0075604 | 2.4467e-05 | Restore Supply on Device V42 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Fuses V42 |  | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 309 | 306 | 2448 | 0.0074772 | 2.4435e-05 | 2014-10-09 | C | 0.0074772 | 2.4435e-05 | 2015 | 2014-10-09 | C | 8 | 0.0074772 | 2.4435e-05
1 | 1855994 | 2014-10-09 09:45 | 2014-10-09 14:54 | 309.25 | 7 | 2164.75 | 0.0066207 | 2.1409e-05 | NAPA ID:02728 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Fuse Links V42 | Replace burnt of compression dead end and tree trimming. Works location: Soldiers Rd WO 10149505 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 309.25 | 306.25 | 2143.75 | 0.0065479 | 2.1381e-05 | 2014-10-09 | B | 0.003274 | 1.069e-05 | 2015 | 2014-10-09 | B | 7 | 0.0065479 | 2.1381e-05
1 | 2369234 | 2014-10-09 09:54 | 2014-10-09 14:06 | 252.0667 | 1 | 252.0667 | 0.00077093 | 3.0584e-06 | Restore Supply on Device TP2272 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | tf7148 | replaced 2 x 15 amp hv fuses. tf7148 - transformer for pumps. cause: rat. ug/hv. 2 of 3 phases. Email to Jo to check | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 252.0667 | 249.0667 | 249.0667 | 0.00076076 | 3.0544e-06 | 2014-10-09 | C | 0.00076076 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.00076076 | 3.0544e-06
1 | 2315565 | 2014-10-09 13:26 | 2014-10-10 14:13 | 1487 | 1 | 1487 | 0.0045479 | 3.0584e-06 | Restore Supply on Device T1/408 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole P20257 | Attending ABS L1 to look for HV fault. If no fault here, will need to attend T1/408 as individual fault and create crew requests for further LV jobs on this feeder. Broken HV crossarm found. Left off overnight via Fuses L46. Crossarm replaced 10/10/14. Em | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1487 | 1484 | 1484 | 0.0045328 | 3.0544e-06 | 2014-10-09 | C | 0.0045328 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.0045328 | 3.0544e-06
1 | 2371731 | 2014-10-09 14:15 | 2014-10-09 15:53 | 98.2 | 35 | 3403.5667 | 0.01041 | 0.00010704 | Restore Supply on Device TA824 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 714989 | REplace broken cross arm. Bruce Kerr and Bevan Hughes attended. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 97.2448 | 94.2448 | 3298.5667 | 0.010075 | 0.0001069 | 2014-10-09 | C | 0.010075 | 0.0001069 | 2015 | 2014-10-09 | C | 35 | 0.010075 | 0.0001069
1 | 2372784 | 2014-10-09 15:25 | 2014-10-09 15:40 | 15.85 | 141 | 2234.85 | 0.0068351 | 0.00043124 | Restore Supply on Device C21 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P26610 | This is a child job of 2373121 | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 15.85 | 12.85 | 1811.85 | 0.0055342 | 0.00043067 | 2014-10-09 | C | 0.0055342 | 0.00043067 | 2015 | 2014-10-09 | C | 141 | 0.0055342 | 0.00043067
1 | 2372938 | 2014-10-09 15:29 | 2014-10-09 19:46 | 256.9667 | 44 | 10992.6333 | 0.03362 | 0.00013457 | Restore Supply on Device FP839 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | FP839 | fm advise blown up tx tc 5243 will be off line Replaced 2 x 25amp fuses | F2/F3 | QUEEN ST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 249.8326 | 246.8326 | 10860.6333 | 0.033173 | 0.00013439 | 2014-10-09 | C | 0.033173 | 0.00013439 | 2015 | 2014-10-09 | C | 44 | 0.033173 | 0.00013439
1 | 2373161 | 2014-10-09 16:07 | 2014-10-09 22:00 | 352.8333 | 1 | 352.8333 | 0.0010791 | 3.0584e-06 | Restore Supply on Device T1501 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx T1501 | 9/10 7.51 9/10 line down no power for 30 hours stacey sending some one tonight blown tx 30 kva t1501 requested 2r to replace transformer tomorrow customer advised crew will attend at 9.30 am 10/10. 23/10 email sent to hub for follow up. 28/10 another em | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 352.8333 | 349.8333 | 349.8333 | 0.0010685 | 3.0544e-06 | 2014-10-09 | C | 0.0010685 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.0010685 | 3.0544e-06
1 | 2373258 | 2014-10-09 16:58 | 2014-10-10 00:29 | 450.85 | 1 | 450.85 | 0.0013789 | 3.0584e-06 | Restore Supply on Device X224 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4446 Greatford Rd | faultman replaced 1X 60Amp HV rewirable fuse. | F4 | CROFTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 450.85 | 447.85 | 447.85 | 0.0013679 | 3.0544e-06 | 2014-10-09 | C | 0.0013679 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.0013679 | 3.0544e-06
1 | 2373479 | 2014-10-09 18:15 | 2014-10-10 08:21 | 845.8833 | 1 | 845.8833 | 0.0025871 | 3.0584e-06 | Restore Supply on Device TA2-152 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 207430 | replaced 2 x 2amp DDO links/elements (2 out of 2) 1 x drop out - candle holder. caused by weather. checked adjacent assets on pole, confirm up to POCO standard emailed Jo to check | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 845.8833 | 842.8833 | 842.8833 | 0.0025745 | 3.0544e-06 | 2014-10-09 | C | 0.0025745 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.0025745 | 3.0544e-06
1 | 2373586 | 2014-10-09 19:57 | 2014-10-10 01:01 | 303.9333 | 1 | 303.9333 | 0.00092956 | 3.0584e-06 | Restore Supply on Device 3899T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 493 | At end of Mayne St. Multi business complex Cad Tess Properties Sign of Broker Panel & Paint MLB Manufacturers Speed Tools NZ Craig advised that several workshops are on one phase of electricity in the area. Cant activate alarms & close doors. | F1 | BLAKE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 303.9333 | 300.9333 | 300.9333 | 0.00091918 | 3.0544e-06 | 2014-10-09 | C | 0.00091918 | 3.054e-06 | 2015 | 2014-10-09 | C | 1 | 0.00091918 | 3.0544e-06
1 | 2374005 | 2014-10-10 00:27 | 2014-10-10 07:07 | 400.8333 | 237 | 14658.0833 | 0.044831 | 0.00072485 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 727608 | CB LI 1 tripped on E/F flags, line was sectionalised and patrolled and a broken insulator was found on pole 727608, line was isolated at ABS's LI122, LI170 & LI180 to rerplace the insulator. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 61.8485 | 58.8485 | 13947.0833 | 0.0426 | 0.0007239 | 2014-10-10 | C | 0.0426 | 0.0007239 | 2015 | 2014-10-10 | C | 237 | 0.0426 | 0.0007239
1 | 2373727 | 2014-10-10 01:10 | 2014-10-10 15:40 | 870.4167 | 2 | 588.8667 | 0.001801 | 6.1168e-06 | Restore Supply on Device FC913 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C12647 | Found pole on fire. Isolated at fuses FC913. Cut jumpers at pole C12647 to isolte fault. Reclosed fuses to restore power to cow shed. replaced pole which was on fire and a cross arm. Greg Whyte attended. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 294.4333 | 291.4333 | 582.8667 | 0.0017803 | 6.1088e-06 | 2014-10-10 | C | 0.0017803 | 6.109e-06 | 2015 | 2014-10-10 | C | 2 | 0.0017803 | 6.1088e-06
1 | 2375339 | 2014-10-10 05:30 | 2014-10-14 09:25 | 5995.4 | 1 | 5995.4 | 0.018336 | 3.0584e-06 | Restore Supply on Device 504 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 504 | hv fuse blown, f6603 2x 3amp ddo fuses | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 5995.4 | 5992.4 | 5992.4 | 0.018303 | 3.0544e-06 | 2014-10-10 | C | 0.018303 | 3.054e-06 | 2015 | 2014-10-10 | C | 1 | 0.018303 | 3.0544e-06
1 | 2381146 | 2014-10-10 06:53 | 2014-10-11 15:30 | 1957 | 2 | 3914 | 0.011971 | 6.1168e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Fuses 4671 on Heads Rd | Repair cable from Fuses 4671 to Transformer X3215 after car vs pole on 10/10/14. REF to OMS:2378131. Replaced 8 meters of u.g HV cable NDR is under the oms ref to OMS 2378131. No other assets repaired or replaced. Adjacent assets were checked and confi | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1957 | 1954 | 3908 | 0.011937 | 6.1088e-06 | 2014-10-10 | B | 0.0059683 | 3.054e-06 | 2015 | 2014-10-10 | B | 2 | 0.011937 | 6.1088e-06
1 | 2378131 | 2014-10-10 06:53 | 2014-10-10 08:29 | 96.5 | 2539 | 114937.6167 | 0.35153 | 0.0077653 | Restore Supply on Device 336 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | pole 790697 | Car vs Pole 33kV & 11kV lines down. Lines were isolated at 33KV CB's 3102/5, 3072, ABS 3096 and a Temp. line break was make on 11KV lines at pole 790697. 33KV pole with all it's hardware was replaced. 11KV Cable from Fuses 4671 to transformer X3215 wil | F1, F2, F3 | BEACH ROAD 33KV | TAUPO QUAY SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 45.2689 | 42.2689 | 107320.6167 | 0.3278 | 0.0077552 | 2014-10-10 | C | 0.3278 | 0.0077552 | 2015 | 2014-10-10 | C | 2539 | 0.3278 | 0.0077552
1 | 2379577 | 2014-10-10 09:00 | 2014-10-10 15:43 | 402.6333 | 10 | 4026.3333 | 0.012314 | 3.0584e-05 | Restore Supply on Device 5666 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS5666 |  | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 402.6333 | 399.6333 | 3996.3333 | 0.012206 | 3.0544e-05 | 2014-10-10 | C | 0.012206 | 3.0544e-05 | 2015 | 2014-10-10 | C | 10 | 0.012206 | 3.0544e-05
1 | 2069429 | 2014-10-10 09:04 | 2014-10-10 13:16 | 252 | 2 | 504 | 0.0015414 | 6.1168e-06 | NAPA ID:03240 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE5-244 | REPLACE DDO ARM, REPLACE TX ARMS, REMOVE ONE SPAN OF LV WIRE FROM TX TE5-244. Works location: No2 Rd. WO 10155539 & 10161868 | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 252 | 249 | 498 | 0.0015211 | 6.1088e-06 | 2014-10-10 | B | 0.00076055 | 3.054e-06 | 2015 | 2014-10-10 | B | 2 | 0.0015211 | 6.1088e-06
1 | 2379538 | 2014-10-10 09:25 | 2014-10-10 14:50 | 324.6833 | 1 | 324.6833 | 0.00099302 | 3.0584e-06 | Restore Supply on Device X2718 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 784685 | 2 X 2 AMP HT FUSES DUE TO LIGHTNING NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 324.6833 | 321.6833 | 321.6833 | 0.00098256 | 3.0544e-06 | 2014-10-10 | C | 0.00098256 | 3.054e-06 | 2015 | 2014-10-10 | C | 1 | 0.00098256 | 3.0544e-06
1 | 2379593 | 2014-10-10 09:45 | 2014-10-10 10:56 | 70.5333 | 1 | 70.5333 | 0.00021572 | 3.0584e-06 | Restore Supply on Device TC4122 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | m13088 | been through control tc4122 pole m13088 HT fuse dropped out, 3amp ht fuse re loaded. email to Jo to check | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 70.5333 | 67.5333 | 67.5333 | 0.00020628 | 3.0544e-06 | 2014-10-10 | C | 0.00020628 | 3.054e-06 | 2015 | 2014-10-10 | C | 1 | 0.00020628 | 3.0544e-06
1 | 2490643 | 2014-10-10 12:40 | 2014-10-10 13:52 | 72 | 1 | 72 | 0.00022021 | 3.0584e-06 | Restore Supply on Device T5/294 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P19735 | Replaced pole and lines down during storm. Materials used: 11m busck, 3 x 3 amp Links. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 69 | 0.00021076 | 3.0544e-06 | 2014-10-10 | C | 0.00021075 | 3.054e-06 | 2015 | 2014-10-10 | C | 1 | 0.00021076 | 3.0544e-06
1 | 2380312 | 2014-10-10 13:13 | 2014-10-10 15:28 | 135.25 | 1 | 135.25 | 0.00041365 | 3.0584e-06 | Restore Supply on Device TP937 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 119132 | 2 x 3amp fuses blown - at TP625 on pole 119132 email to Jo to check | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 135.25 | 132.25 | 132.25 | 0.00040395 | 3.0544e-06 | 2014-10-10 | C | 0.00040395 | 3.054e-06 | 2015 | 2014-10-10 | C | 1 | 0.00040395 | 3.0544e-06
1 | 2156816 | 2014-10-10 23:00 | 2014-10-11 05:59 | 418.3167 | 8 | 3346.5333 | 0.010235 | 2.4467e-05 | NAPA ID:03371 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV pole 220936 | Replace 33kV Poles and crossarms Between poles 220936 & 220979. Works location: John Bird Rd WO 10153754 | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 418.3167 | 415.3167 | 3322.5333 | 0.010148 | 2.4435e-05 | 2014-10-10 | B | 0.0050742 | 1.2218e-05 | 2015 | 2014-10-10 | B | 8 | 0.010148 | 2.4435e-05
1 | 2381266 | 2014-10-11 08:47 | 2014-10-11 15:48 | 420.5167 | 1 | 420.5167 | 0.0012861 | 3.0584e-06 | Restore Supply on Device 1 | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3096T |  | F3 | RATA ST | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 420.5167 | 417.5167 | 417.5167 | 0.0012753 | 3.0544e-06 | 2014-10-11 | C | 0.0012753 | 3.054e-06 | 2015 | 2014-10-11 | C | 1 | 0.0012753 | 3.0544e-06
1 | 2381208 | 2014-10-11 09:01 | 2014-10-11 15:08 | 367.1333 | 78 | 28636.4 | 0.087582 | 0.00023856 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 830007 | Replace 33/11KV pole 830007 hit by a car, this is a follow up job from OMS number 2381185. | F3 | TOTARA ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 367.1333 | 364.1333 | 28402.4 | 0.086753 | 0.00023825 | 2014-10-11 | B | 0.043376 | 0.00011912 | 2015 | 2014-10-11 | B | 78 | 0.086753 | 0.00023825
1 | 2381895 | 2014-10-11 12:14 | 2014-10-11 22:00 | 586.1 | 2 | 1172.2 | 0.0035851 | 6.1168e-06 | Restore Supply on Device U45 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P15292 | Mauriceville Pole P15292 broken. Gen set connected at 22:00. Pole replace on NAPA 3619. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 586.1 | 583.1 | 1166.2 | 0.0035621 | 6.1088e-06 | 2014-10-11 | C | 0.0035621 | 6.109e-06 | 2015 | 2014-10-11 | C | 2 | 0.0035621 | 6.1088e-06
1 | 2381838 | 2014-10-11 14:18 | 2014-10-11 15:12 | 53.05 | 1 | 53.05 | 0.00016225 | 3.0584e-06 | Restore Supply on Device TD5-234 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 316838 | replace 63amp HRC fuse at pole 316838 - cause due to overload No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F3 | DOMAIN RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 53.05 | 50.05 | 50.05 | 0.00015287 | 3.0544e-06 | 2014-10-11 | C | 0.00015287 | 3.054e-06 | 2015 | 2014-10-11 | C | 1 | 0.00015287 | 3.0544e-06
1 | 2380688 | 2014-10-11 23:51 | 2014-10-12 05:38 | 346.75 | 8 | 2774 | 0.0084841 | 2.4467e-05 | NAPA ID:03565 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6 232 | Replace 33kV Poles and crossarms Between poles 220936 & 220996 | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 346.75 | 343.75 | 2750 | 0.0083997 | 2.4435e-05 | 2014-10-11 | B | 0.0041998 | 1.2218e-05 | 2015 | 2014-10-11 | B | 8 | 0.0083997 | 2.4435e-05
1 | 2382038 | 2014-10-12 06:12 | 2014-10-12 16:07 | 594.5667 | 10 | 1824.5667 | 0.0055803 | 3.0584e-05 | Restore Supply on Device TF4-049 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TP398 | 3x HV Fuses Replaced. All Power Restored on Completion. This job took a long time to complete. Faultman who attended was unsure as to what the problem was exactly. Incorrectly diagnosed Transformer TP398 to be faulty (SWER). Unknown cause of fault. Was p | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 182.4567 | 179.4567 | 1794.5667 | 0.0054814 | 3.0544e-05 | 2014-10-12 | C | 0.0054814 | 3.0544e-05 | 2015 | 2014-10-12 | C | 10 | 0.0054814 | 3.0544e-05
1 | 1911995 | 2014-10-12 08:01 | 2014-10-12 09:15 | 73.3333 | 48 | 3520 | 0.010766 | 0.0001468 | NAPA ID:02945 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 7 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G224C | 11kv metering checks. Works location: The Arena Manawatu WO 10160487 | F3 | PASCAL ST 7 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 73.3333 | 70.3333 | 3376 | 0.010312 | 0.00014661 | 2014-10-12 | B | 0.0051559 | 7.3306e-05 | 2015 | 2014-10-12 | B | 48 | 0.010312 | 0.00014661
1 | 1883412 | 2014-10-12 08:40 | 2014-10-12 14:15 | 335 | 2 | 670 | 0.0020491 | 6.1168e-06 | NAPA ID:02798 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS Q1 | To change ABS Pole and Switch Q1. Works location: Mangahao Rd Pahiatua WO 10144449 | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 335 | 332 | 664 | 0.0020281 | 6.1088e-06 | 2014-10-12 | B | 0.0010141 | 3.054e-06 | 2015 | 2014-10-12 | B | 2 | 0.0020281 | 6.1088e-06
1 | 2383873 | 2014-10-12 10:03 | 2014-10-12 10:40 | 36.85 | 328 | 12086.8 | 0.036967 | 0.0010032 | Restore Supply on Device S124 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 833037 | Emergency shutdown to repair Jumpers at Pole 833037 Burning up Repaired all 3 Jumpers | F2 | COLOMBO RD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 36.85 | 33.85 | 11102.8 | 0.033913 | 0.0010019 | 2014-10-12 | C | 0.033913 | 0.0010019 | 2015 | 2014-10-12 | C | 328 | 0.033913 | 0.0010019
1 | 1883446 | 2014-10-13 09:35 | 2014-10-13 15:24 | 348.7333 | 40 | 13949.3333 | 0.042663 | 0.00012234 | NAPA ID:02628 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/88 | Replace 11kV cross arms and install temp DDO's at T5/88. Works location: Lower Pakihikura Rd. WO 10142182 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 348.7333 | 345.7333 | 13829.3333 | 0.042241 | 0.00012218 | 2014-10-13 | B | 0.02112 | 6.1088e-05 | 2015 | 2014-10-13 | B | 40 | 0.042241 | 0.00012218
1 | 1883418 | 2014-10-13 09:46 | 2014-10-13 11:25 | 99.1167 | 1 | 99.1167 | 0.00030314 | 3.0584e-06 | NAPA ID:02698 TP_MATAROA GXP > TAIHAPE SUB > PAPAKAI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X938 | Replace t/f x938 due to oil leak and replace 11 kv DDO fuses at transformer if necessary. Works location: Hiwarea Rd Taihape. WO 10151759. | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 99.1167 | 96.1167 | 96.1167 | 0.00029358 | 3.0544e-06 | 2014-10-13 | B | 0.00014679 | 1.527e-06 | 2015 | 2014-10-13 | B | 1 | 0.00029358 | 3.0544e-06
1 | 2385544 | 2014-10-13 13:00 | 2014-10-13 15:34 | 153.7667 | 1 | 153.7667 | 0.00047028 | 3.0584e-06 | Restore Supply on Device TC741 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC180 | at 12:55 Kerepehi Sub, CB 2 Awaiti Feeder. Found transformer TC180 had blown. Transformer lid bolts had rusted and lid of transformer was opening and closing with the wind. Found that transformer had filled up with water because of this and blown. Own Iso | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 153.7667 | 150.7667 | 150.7667 | 0.00046051 | 3.0544e-06 | 2014-10-13 | C | 0.0004605 | 3.054e-06 | 2015 | 2014-10-13 | C | 1 | 0.00046051 | 3.0544e-06
1 | 2385757 | 2014-10-13 14:50 | 2014-10-13 20:58 | 368 | 2 | 429.8333 | 0.0013146 | 6.1168e-06 | Restore Supply on Device T7/366 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | FM requested 2 r as tx T7/366 has blown up will replace tonight | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 214.9167 | 211.9167 | 423.8333 | 0.0012946 | 6.1088e-06 | 2014-10-13 | C | 0.0012946 | 6.109e-06 | 2015 | 2014-10-13 | C | 2 | 0.0012946 | 6.1088e-06
1 | 2385778 | 2014-10-13 14:57 | 2014-10-13 23:09 | 491.8 | 94 | 11836.5833 | 0.036201 | 0.00028749 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Recloser RS 8156 | A/R, O/C B & C Phase | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 125.9211 | 122.9211 | 11554.5833 | 0.035293 | 0.00028712 | 2014-10-13 | C | 0.035293 | 0.00028712 | 2015 | 2014-10-13 | C | 94 | 0.035293 | 0.00028712
1 | 2386291 | 2014-10-14 06:18 | 2014-10-14 06:50 | 31.7667 | 4 | 164.7167 | 0.00050377 | 1.2234e-05 | Restore Supply on Device FP767 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O13108 | Found line off insulator. Isolated at fuses FP767. repaired line * relivened | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 41.1792 | 38.1792 | 152.7167 | 0.00046646 | 1.2218e-05 | 2014-10-14 | C | 0.00046646 | 1.2218e-05 | 2015 | 2014-10-14 | C | 4 | 0.00046646 | 1.2218e-05
1 | 1936617 | 2014-10-14 08:30 | 2014-10-14 15:23 | 413 | 73 | 30149 | 0.092208 | 0.00022326 | NAPA ID:02459 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer T751 | isolate t751and t1133 so a line break can be made at pole 814960. so that t751,818178 & t1133,818194 can be replaced. Works location: Reading St Greytown WO 10140873 IR6938 | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 413 | 410 | 29930 | 0.091419 | 0.00022297 | 2014-10-14 | B | 0.045709 | 0.00011149 | 2015 | 2014-10-14 | B | 73 | 0.091419 | 0.00022297
1 | 2380531 | 2014-10-14 09:15 | 2014-10-14 16:55 | 460 | 38 | 16255 | 0.049715 | 0.00011622 | NAPA ID:02456 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 222834 | REPLACE HV ARMS AND HV POLES AS PER WORK PARK. Works location: SH2 Te Puke. WO 10145672. On Restoring TE5-071 1 DDO unit broke. Repaired via LLP 144716. | F1/F3 | TE PUKE NORTH | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 427.7632 | 424.7632 | 16141 | 0.049301 | 0.00011607 | 2014-10-14 | B | 0.024651 | 5.8034e-05 | 2015 | 2014-10-14 | B | 38 | 0.049301 | 0.00011607
1 | 1883452 | 2014-10-14 09:38 | 2014-10-14 15:28 | 350.45 | 10 | 3504.5 | 0.010718 | 3.0584e-05 | NAPA ID:02632 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K58 | Replace 11kv xarms. Works location: Lower Pakihikura Rd WO 10142182 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 350.45 | 347.45 | 3474.5 | 0.010613 | 3.0544e-05 | 2014-10-14 | B | 0.0053063 | 1.5272e-05 | 2015 | 2014-10-14 | B | 10 | 0.010613 | 3.0544e-05
1 | 1911997 | 2014-10-14 09:55 | 2014-10-14 15:00 | 305 | 20 | 6100 | 0.018656 | 6.1168e-05 | NAPA ID:02899 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV poles 842105 | treescape felling trees near poles 842105 & 842109. Works location: Taumatatahi Rd Waitotara Valley PPPD 46331 | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 305 | 302 | 6040 | 0.018449 | 6.1088e-05 | 2014-10-14 | B | 0.0092244 | 3.0544e-05 | 2015 | 2014-10-14 | B | 20 | 0.018449 | 6.1088e-05
1 | 2389663 | 2014-10-14 12:19 | 2014-10-15 09:43 | 1283.5667 | 64 | 35339.3 | 0.10808 | 0.00019574 | Restore Supply on Device V5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04228 | Line patrolled and supply restored to Fuses V11 will return in daylight to patrol further with additional staff due to unfreindly terrain . Floating conductor found at Pole P04228. Rebound to insulator. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 552.1766 | 549.1766 | 35147.3 | 0.10735 | 0.00019548 | 2014-10-14 | C | 0.10735 | 0.00019548 | 2015 | 2014-10-14 | C | 64 | 0.10735 | 0.00019548
1 | 2389021 | 2014-10-14 14:06 | 2014-10-14 15:02 | 55.5 | 9 | 499.5 | 0.0015277 | 2.7526e-05 | Restore Supply on Device 172 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 787618 | As a result of the recent bad weather. Temp repair done at the time and this is permanent repair to floating 11 kv wire ay pole 787617. Neville Ashton | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 55.5 | 52.5 | 472.5 | 0.0014432 | 2.749e-05 | 2014-10-14 | C | 0.0014432 | 2.749e-05 | 2015 | 2014-10-14 | C | 9 | 0.0014432 | 2.749e-05
1 | 2326771 | 2014-10-14 14:55 | 2014-10-14 15:32 | 37.0333 | 193 | 3743.0667 | 0.011448 | 0.00059028 | NAPA ID:03347 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD INDUSTRIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Recloser 8764 | Battery Tests on 11kV control unit. Works location: Mountain Rd WO 10143204 This outage was caused by a switching error under SIN 3347 OMS 2326771. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 19.3941 | 16.3941 | 3164.0667 | 0.0096644 | 0.0005895 | 2014-10-14 | B | 0.0048322 | 0.00029475 | 2015 | 2014-10-14 | B | 193 | 0.0096644 | 0.0005895
1 | 2389359 | 2014-10-14 19:10 | 2014-10-14 19:55 | 45 | 24 | 1080 | 0.0033031 | 7.3402e-05 | Restore Supply on Device W2335 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 725977 | 2r request to replace hv pin and insulator at pole 725977 | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 1008 | 0.0030789 | 7.3306e-05 | 2014-10-14 | C | 0.0030789 | 7.3306e-05 | 2015 | 2014-10-14 | C | 24 | 0.0030789 | 7.3306e-05
1 | 1952051 | 2014-10-15 08:45 | 2014-10-15 14:56 | 370.6833 | 2 | 741.3667 | 0.0022674 | 6.1168e-06 | NAPA ID:02645 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 810905 | REPLACING 11KV POLES BURNSIDE FEEDER. Works location: Pirinoa Rd Martinborough WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 370.6833 | 367.6833 | 735.3667 | 0.0022461 | 6.1088e-06 | 2014-10-15 | B | 0.0011231 | 3.054e-06 | 2015 | 2014-10-15 | B | 2 | 0.0022461 | 6.1088e-06
1 | 2069852 | 2014-10-15 09:00 | 2014-10-15 13:20 | 260 | 24 | 6240 | 0.019085 | 7.3402e-05 | NAPA ID:03232 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC720 | To replace 11kV and LV cross arms as result of broken binders ect. Works location: Tauranga Rd WO 10162662 | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 260 | 257 | 6168 | 0.01884 | 7.3306e-05 | 2014-10-15 | B | 0.0094198 | 3.6653e-05 | 2015 | 2014-10-15 | B | 24 | 0.01884 | 7.3306e-05
1 | 1473270 | 2014-10-15 09:00 | 2014-10-15 13:45 | 285.1 | 8 | 2280.8 | 0.0069756 | 2.4467e-05 | NAPA ID:01841 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer X1585 | 11kv reconductor from fuses 1198 to X1585. Works location: Whangaehu Beach Rd WO 10140836 | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 285.1 | 282.1 | 2256.8 | 0.0068932 | 2.4435e-05 | 2014-10-15 | B | 0.0034466 | 1.2218e-05 | 2015 | 2014-10-15 | B | 8 | 0.0068932 | 2.4435e-05
1 | 1935499 | 2014-10-15 09:21 | 2014-10-15 14:58 | 336.6333 | 7 | 2356.4333 | 0.007207 | 2.1409e-05 | NAPA ID:02731 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Pole 807920 | isolation and a/p needed for tree cutting between poles 807920 to 807922 mangawekea. Works location: Shtate Hwy 1 Mangaweka PPPD 42763 | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 336.6333 | 333.6333 | 2335.4333 | 0.0071334 | 2.1381e-05 | 2014-10-15 | B | 0.0035667 | 1.069e-05 | 2015 | 2014-10-15 | B | 7 | 0.0071334 | 2.1381e-05
1 | 2006421 | 2014-10-15 09:34 | 2014-10-15 14:21 | 287 | 3 | 861 | 0.0026333 | 9.1753e-06 | NAPA ID:02067 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 4986 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd Tariki Inglewood WO 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 287 | 284 | 852 | 0.0026024 | 9.1633e-06 | 2014-10-15 | B | 0.0013012 | 4.582e-06 | 2015 | 2014-10-15 | B | 3 | 0.0026024 | 9.1633e-06
1 | 1883461 | 2014-10-15 09:55 | 2014-10-15 15:20 | 324.95 | 15 | 4874.25 | 0.014908 | 4.5876e-05 | NAPA ID:02633 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K59 | Replace 11kv xarms. Works location: Lower Pakihikura Rd WO 10142182 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 324.95 | 321.95 | 4829.25 | 0.014751 | 4.5816e-05 | 2014-10-15 | B | 0.0073753 | 2.2908e-05 | 2015 | 2014-10-15 | B | 15 | 0.014751 | 4.5816e-05
1 | 2391129 | 2014-10-15 13:00 | 2014-10-15 19:32 | 391.9167 | 1415 | 190241.1 | 0.58184 | 0.0043277 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 750158 | car vs pole. intersection Omata Road and Endevour Street, Marfell, New Plymouth. Fire Comms Event # F1707787. ETA required. pole was burning but now only sparking. Replaced pole & all associated hardware. NDR #38755 Attended by Traffic Management. Wes | F3 | MOTUROA 8 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 134.446 | 131.446 | 185996.1 | 0.56811 | 0.004322 | 2014-10-15 | C | 0.56811 | 0.004322 | 2015 | 2014-10-15 | C | 1415 | 0.56811 | 0.004322
1 | 2395335 | 2014-10-15 19:51 | 2014-10-15 20:52 | 60.5833 | 11 | 666.4167 | 0.0020382 | 3.3643e-05 | Restore Supply on Device T1274 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1274 | 15/10 8.52PM FM ADVISED A BURST LEAD AT BACK OF T 1274 WILL BE TAKING THIS OFF FOR APPROX ONE HOUR TO MAKE REPAIRS MADE TEMP REPAIRS WITH A JUMPER NEED TO GET MORE EQUIPMENT FOR TOMORROW AND WILL MAKE PERMANENT REPAIRS THEN ALL POWER BACK ON NOW BUT WIL | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 60.5833 | 57.5833 | 633.4167 | 0.0019347 | 3.3599e-05 | 2014-10-15 | C | 0.0019347 | 3.3599e-05 | 2015 | 2014-10-15 | C | 11 | 0.0019347 | 3.3599e-05
1 | 2395411 | 2014-10-16 01:20 | 2014-10-16 02:54 | 94 | 1101 | 97799.2667 | 0.29911 | 0.0033673 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses FC764 | at 01:21 Whangamata Sub, CB 3 Opoutere Feeder, Tripped, Ph A B O/C, E/F, L/O. Faultman was dispatched and investigation began. Feeder sectionalised. Opened Sw/gear IC1487. CB 3 Closed. Opened ABS 2576. When closing Sw/gear IC1487, faultman saw fire, so im | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 88.8277 | 85.8277 | 94496.2667 | 0.28863 | 0.0033629 | 2014-10-16 | C | 0.28863 | 0.0033629 | 2015 | 2014-10-16 | C | 1101 | 0.28863 | 0.0033629
1 | 2398605 | 2014-10-16 06:10 | 2014-10-16 08:46 | 156 | 33 | 277.7333 | 0.00084943 | 0.00010093 | Restore Supply on Device SC2-126 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | sc2-126 | 2 hv fuses replaced due to bird strike | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 8.4162 | 5.4162 | 178.7333 | 0.00054593 | 0.0001008 | 2014-10-16 | C | 0.00054593 | 0.0001008 | 2015 | 2014-10-16 | C | 33 | 0.00054593 | 0.0001008
1 | 2398676 | 2014-10-16 07:37 | 2014-10-16 15:43 | 485.3167 | 1 | 485.3167 | 0.0014843 | 3.0584e-06 | Restore Supply on Device TC1006 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1006 | pole M12360 - TX 106 Blown 30KVA TX (need to replace TX ) x6 3amp HV fuses used to try and reliven TX but then needed to replace TX (Isolated TX) - need to 2R crew request for crew to replace TX transformer replaced and used 3x 3a fuse links.noth | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 485.3167 | 482.3167 | 482.3167 | 0.0014732 | 3.0544e-06 | 2014-10-16 | C | 0.0014732 | 3.054e-06 | 2015 | 2014-10-16 | C | 1 | 0.0014732 | 3.0544e-06
1 | 2380112 | 2014-10-16 08:25 | 2014-10-16 12:22 | 237.3 | 2 | 474.6 | 0.0014515 | 6.1168e-06 | NAPA ID:03436 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P35931 | Change 11kv xarms, on pole P35931. Works location: Main Drain Rd. WO 10156813. | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 237.3 | 234.3 | 468.6 | 0.0014313 | 6.1088e-06 | 2014-10-16 | B | 0.00071565 | 3.054e-06 | 2015 | 2014-10-16 | B | 2 | 0.0014313 | 6.1088e-06
1 | 2021722 | 2014-10-16 08:27 | 2014-10-16 12:19 | 231.8 | 59 | 13642.35 | 0.041724 | 0.00018045 | NAPA ID:02568 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer T1833 | isolate t1833 & t790 so that a live line break can be made at pole 818028 so the 11kv at t1833 can be moved on to new pole which will be installed prior to 16/10/14. Works location: Main St Greytown WO 10140873 IR6938 | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 231.2263 | 228.2263 | 13465.35 | 0.041129 | 0.00018021 | 2014-10-16 | B | 0.020564 | 9.0105e-05 | 2015 | 2014-10-16 | B | 59 | 0.041129 | 0.00018021
1 | 2379388 | 2014-10-16 08:45 | 2014-10-16 14:53 | 368 | 37 | 13616 | 0.041643 | 0.00011316 | NAPA ID:02664 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses FP1627 | To replace 11kV hardware on existing Poles and install new 11kV fuses FP1627. Works location: Rangitanuku Rd WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 368 | 365 | 13505 | 0.04125 | 0.00011301 | 2014-10-16 | B | 0.020625 | 5.6507e-05 | 2015 | 2014-10-16 | B | 37 | 0.04125 | 0.00011301
1 | 1994536 | 2014-10-16 08:45 | 2014-10-16 14:22 | 337 | 86 | 28982 | 0.088639 | 0.00026302 | NAPA ID:02800 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2566 | Replace poles and arms between IC2566 & IC373. Works location: Tahuna Rd and Awaiti Rd Paeroa. WO 10148309. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 337 | 334 | 28724 | 0.087735 | 0.00026268 | 2014-10-16 | B | 0.043868 | 0.00013134 | 2015 | 2014-10-16 | B | 86 | 0.087735 | 0.00026268
1 | 2069979 | 2014-10-16 08:58 | 2014-10-16 15:20 | 382.2333 | 10 | 3822.3333 | 0.01169 | 3.0584e-05 | NAPA ID:02218 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P07089 | Replace Crossarms from pole P07089 to P07060. Works location: Waipuru Rd. WO 10160678 | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 382.2333 | 379.2333 | 3792.3333 | 0.011583 | 3.0544e-05 | 2014-10-16 | B | 0.0057917 | 1.5272e-05 | 2015 | 2014-10-16 | B | 10 | 0.011583 | 3.0544e-05
1 | 2021670 | 2014-10-16 09:00 | 2014-10-16 16:05 | 425 | 4 | 1700 | 0.0051993 | 1.2234e-05 | NAPA ID:02526 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Recloser 6813 | 11kv pole and cross arm upgrade. Works location: Mohakau Rd WO IR1872 | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 425 | 422 | 1688 | 0.0051559 | 1.2218e-05 | 2014-10-16 | B | 0.0025779 | 6.109e-06 | 2015 | 2014-10-16 | B | 4 | 0.0051559 | 1.2218e-05
1 | 1994683 | 2014-10-16 09:19 | 2014-10-16 15:33 | 374.3833 | 13 | 4866.9833 | 0.014885 | 3.9759e-05 | NAPA ID:02458 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-011 | REPLACE HV ARMS AND HV POLES AS PER WORK PARK [ Q 2 JOB] Works location: SH2 Collins Lane No 3 Rd WO 10145672 IR7224 | F1/F3 | TE PUKE NORTH | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 374.3833 | 371.3833 | 4827.9833 | 0.014747 | 3.9708e-05 | 2014-10-16 | B | 0.0073734 | 1.9854e-05 | 2015 | 2014-10-16 | B | 13 | 0.014747 | 3.9708e-05
1 | 2021707 | 2014-10-16 09:34 | 2014-10-16 14:43 | 309.85 | 2 | 619.7 | 0.0018953 | 6.1168e-06 | NAPA ID:02646 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 810928 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd. WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 309.85 | 306.85 | 613.7 | 0.0018745 | 6.1088e-06 | 2014-10-16 | B | 0.00093725 | 3.054e-06 | 2015 | 2014-10-16 | B | 2 | 0.0018745 | 6.1088e-06
1 | 2402295 | 2014-10-16 12:43 | 2014-10-16 15:28 | 165.2667 | 4 | 661.0667 | 0.0020218 | 1.2234e-05 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | TC4 276 | Emergency switching to investgate/repair 11kV U/G cable hit by Connel Contractors. Isolation at Fused/Sw 9829/2 supplying 1 x transformer TC4 276. 1 x single core H/V cable damaged & repaired & 1 x cable had zip cover added, all service restored, Dave Jo | F1 | SOUTH | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 165.2667 | 162.2667 | 649.0667 | 0.0019825 | 1.2218e-05 | 2014-10-16 | C | 0.0019825 | 1.2218e-05 | 2015 | 2014-10-16 | C | 4 | 0.0019825 | 1.2218e-05
1 | 2252417 | 2014-10-17 08:17 | 2014-10-17 13:00 | 282.8167 | 239 | 67574.8667 | 0.20667 | 0.00073096 | NAPA ID:03380 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | IC380 | Drop lines to allow Asplundh to safely cut tree. Works location: Thames Coast Rd WO 10160489. A King identified conductor needing repair inside isolation area completed under OMS 2403018 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 282.74 | 279.74 | 66857.8667 | 0.20421 | 0.00073001 | 2014-10-17 | B | 0.10211 | 0.000365 | 2015 | 2014-10-17 | B | 239 | 0.20421 | 0.00073001
1 | 2052211 | 2014-10-17 09:00 | 2014-10-17 15:15 | 375 | 5 | 1875 | 0.0057345 | 1.5292e-05 | NAPA ID:03059 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses WH856 | Replace poles. Works location: Paroa East Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 375 | 372 | 1860 | 0.0056812 | 1.5272e-05 | 2014-10-17 | B | 0.0028406 | 7.636e-06 | 2015 | 2014-10-17 | B | 5 | 0.0056812 | 1.5272e-05
1 | 2077596 | 2014-10-17 09:00 | 2014-10-17 11:41 | 161.4 | 2 | 322.8 | 0.00098726 | 6.1168e-06 | NAPA ID:02227 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV poles P08370 | Replace crossarms between poles P08370 and P13418. Works location: Side road off of Beaconsfield Valley Rd WO 10160678 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 161.4 | 158.4 | 316.8 | 0.00096764 | 6.1088e-06 | 2014-10-17 | B | 0.00048382 | 3.054e-06 | 2015 | 2014-10-17 | B | 2 | 0.00096764 | 6.1088e-06
1 | 2052189 | 2014-10-17 09:45 | 2014-10-18 02:57 | 1032 | 118 | 30968 | 0.094713 | 0.00036089 | NAPA ID:03057 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS WH802 | Replace Abs WH802 & xarms on existing pole. Works location: Dives Ave Manawapou Rd WO 10147441 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 262.4407 | 259.4407 | 30614 | 0.093508 | 0.00036042 | 2014-10-17 | B | 0.046754 | 0.00018021 | 2015 | 2014-10-17 | B | 118 | 0.093508 | 0.00036042
1 | 2403263 | 2014-10-17 14:27 | 2014-10-17 14:57 | 30.5 | 1 | 1337.5 | 0.0040906 | 3.0584e-06 | Restore Supply on Device TP1852 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | IC633 | Faultman found a blown jumper at ABS IC633, line was isolated at ABS's IC 633 & IC 1204 to cut away the jumper at ABS IC 633.ABS IC646 was closed for a back feed. ABS IC 633 has been DNO'd | F1 | TATUANUI | FARMER ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1337.5 | 1334.5 | 1334.5 | 0.0040761 | 3.0544e-06 | 2014-10-17 | C | 0.0040761 | 3.054e-06 | 2015 | 2014-10-17 | C | 1 | 0.0040761 | 3.0544e-06
1 | 2403538 | 2014-10-17 16:23 | 2014-10-17 19:28 | 184.5 | 196 | 25725.6667 | 0.07868 | 0.00059945 | Restore Supply on Device TA7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 715016 | Tasman CB TA7 tripped and L/O on E/F. Line patrolled and broken insulator found on po0le 715016. Replace 1X H/T Insulator. Jade Williams attended. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 131.2534 | 128.2534 | 25137.6667 | 0.076781 | 0.00059867 | 2014-10-17 | C | 0.076781 | 0.00059867 | 2015 | 2014-10-17 | C | 196 | 0.076781 | 0.00059867
1 | 2405077 | 2014-10-18 02:12 | 2014-10-18 04:10 | 117.9667 | 466 | 54319.6667 | 0.16613 | 0.0014252 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 7 | Bulls CB7 tipped on O/C and E/F. Line patrolled and no fault found. Allen Cox and Garry Fisher attended. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 116.5658 | 113.5658 | 52921.6667 | 0.16165 | 0.0014234 | 2014-10-18 | C | 0.16165 | 0.0014234 | 2015 | 2014-10-18 | C | 466 | 0.16165 | 0.0014234
1 | 2407894 | 2014-10-18 03:35 | 2014-10-18 03:48 | 13 | 371 | 4810 | 0.014711 | 0.0011347 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | NA | Moturoa CB 4 tripped. Not patrolled as thought to be associated with OMS 2406341. | F4 | MOTUROA 4 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 12.965 | 9.965 | 3697 | 0.011292 | 0.0011332 | 2014-10-18 | C | 0.011292 | 0.0011332 | 2015 | 2014-10-18 | C | 371 | 0.011292 | 0.0011332
1 | 2406341 | 2014-10-18 03:35 | 2014-10-18 05:40 | 125 | 1552 | 83422.5667 | 0.25514 | 0.0047467 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CB 4 | CB2 tripped. Line patrolled and lines down found at pole 700175. 1m wire, 1HT pin and insulator and 1 x 20amp fuse replaced. Chris Viviers attended. Associated with OMS 2407894 which affected Moturoa 4. | F4 | MOTUROA 2 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 53.7517 | 50.7517 | 78766.5667 | 0.24059 | 0.0047405 | 2014-10-18 | C | 0.24059 | 0.0047405 | 2015 | 2014-10-18 | C | 1552 | 0.24059 | 0.0047405
1 | 2408374 | 2014-10-18 08:17 | 2014-10-18 10:36 | 138.7333 | 1099 | 101538.2667 | 0.31055 | 0.0033612 | Restore Supply on Device CB22 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/245 | Feilding CB22 Trip on B, E/F at 08:17. Fault caused by blown cable crutch between Transformer t3/245 and Pole P20315. Isolation made between sw/gear 227 and 326 to isolate faulty cable.. Both Sw/Gear closed at 227 and 326 to reliven both sides. Cable to b | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 92.3915 | 89.3915 | 98241.2667 | 0.30007 | 0.0033568 | 2014-10-18 | C | 0.30007 | 0.0033568 | 2015 | 2014-10-18 | C | 1099 | 0.30007 | 0.0033568
1 | 2409485 | 2014-10-18 08:29 | 2014-10-18 10:27 | 118.1833 | 5 | 423.7667 | 0.0012961 | 1.5292e-05 | Restore Supply on Device X1468 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 765393 | Outage required from Fuses 1412 to replace a cracked insulator - pole 765393. Email sent to Jo, as appears to have SAIDI component. | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 84.7533 | 81.7533 | 408.7667 | 0.0012485 | 1.5272e-05 | 2014-10-18 | C | 0.0012485 | 1.5272e-05 | 2015 | 2014-10-18 | C | 5 | 0.0012485 | 1.5272e-05
1 | 2410158 | 2014-10-18 10:19 | 2014-10-18 11:05 | 46.4167 | 1 | 46.4167 | 0.00014196 | 3.0584e-06 | Restore Supply on Device X2904 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2904 | This job turned out to be part of OMS 2409485 - power restored OK (Insulator replaced) | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 46.4167 | 43.4167 | 43.4167 | 0.00013261 | 3.0544e-06 | 2014-10-18 | C | 0.00013261 | 3.054e-06 | 2015 | 2014-10-18 | C | 1 | 0.00013261 | 3.0544e-06
1 | 2410243 | 2014-10-18 12:20 | 2014-10-18 14:59 | 158.95 | 466 | 44442.2 | 0.13592 | 0.0014252 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803886 | Trip on CB7 on E/F, C Phase. Patrol carried out with blown insulator found at Pole 803886, Isolation between ABS 1384, 4229/6. Centre insulator replaced and relivened OK. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 95.3695 | 92.3695 | 43044.2 | 0.13148 | 0.0014234 | 2014-10-18 | C | 0.13148 | 0.0014234 | 2015 | 2014-10-18 | C | 466 | 0.13148 | 0.0014234
1 | 2412908 | 2014-10-18 15:29 | 2014-10-19 09:36 | 1086.8667 | 907 | 18572 | 0.056801 | 0.002774 | Restore Supply on Device T1/402 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole P20262 | Contractor initially found 1 fuse out on L43. Patrol carried out, nothing found and fuse relivened. Sanson CB6 tripped a short while later on E/F. Fuses L43 open, CB6 reclosed. Further patrol carried out, suspect insulator.Pole P20262 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 20.4763 | 17.4763 | 15851 | 0.048416 | 0.0027704 | 2014-10-18 | C | 0.048416 | 0.0027704 | 2015 | 2014-10-18 | C | 907 | 0.048416 | 0.0027704
1 | 2416043 | 2014-10-18 21:29 | 2014-10-18 21:43 | 14.0167 | 119 | 1667.9833 | 0.0051014 | 0.00036395 | Restore Supply on Device 2824 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | RC2754 | FM advise: worked through Control. Control advise to bypass recloser and tag as faulty. recloser will need to be taken away from site. FM will sort the removal of recloser from site. oh/hv. cause: unknown. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 14.0167 | 11.0167 | 1310.9833 | 0.0040043 | 0.00036348 | 2014-10-18 | C | 0.0040043 | 0.00036348 | 2015 | 2014-10-18 | C | 119 | 0.0040043 | 0.00036348
1 | 2416205 | 2014-10-19 06:50 | 2014-10-19 14:44 | 474.3667 | 270 | 23063.9 | 0.070539 | 0.00082577 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/gear 9450 | Hamilton St CB6 tripped - No Flags. Line patrolled. Feeder Sectionalised and Sw/gear 9450 found to be faulty. Sw/gear replaced as a unit and relivened. Sam Jones and Steve Doran attended. | F1 | CHAPEL ST | HAMILTON STREET SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 85.4219 | 82.4219 | 22253.9 | 0.067973 | 0.00082469 | 2014-10-19 | C | 0.067973 | 0.00082469 | 2015 | 2014-10-19 | C | 270 | 0.067973 | 0.00082469
1 | 2417531 | 2014-10-19 07:09 | 2014-10-19 08:41 | 91.7 | 19 | 1188.6333 | 0.0036353 | 5.811e-05 | Restore Supply on Device 371 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 63 | ABS 63 Failed during switching for planned outage (SIS 2460) Isolated at ABS 371 & Links 8667/4 and 6876/4 - back feeds installed via ABS 386 and RS 8819 - Jumper on both sides of ABS 63 cut open and all power restored - attended by Chris Viviers | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 62.5596 | 59.5596 | 1131.6333 | 0.0034565 | 5.8034e-05 | 2014-10-19 | C | 0.0034565 | 5.8034e-05 | 2015 | 2014-10-19 | C | 19 | 0.0034565 | 5.8034e-05
1 | 2417311 | 2014-10-19 07:46 | 2014-10-20 22:47 | 2340.6667 | 215 | 22254 | 0.068062 | 0.00065756 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Sanson Sub | CB 4 Tripped - No fault found during sectionlising | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 103.507 | 100.507 | 21609 | 0.066003 | 0.0006567 | 2014-10-19 | C | 0.066003 | 0.0006567 | 2015 | 2014-10-19 | C | 215 | 0.066003 | 0.0006567
1 | 2069913 | 2014-10-19 09:46 | 2014-10-19 11:18 | 92.6833 | 43 | 3985.3833 | 0.012189 | 0.00013151 | NAPA ID:03199 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T8/135 | Install New 11Kv pole and run new L.V conductor at TX T8/135. Works location: Opaki Kaiparoro Rd WO 10120655 | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 92.6833 | 89.6833 | 3856.3833 | 0.011779 | 0.00013134 | 2014-10-19 | B | 0.0058895 | 6.567e-05 | 2015 | 2014-10-19 | B | 43 | 0.011779 | 0.00013134
1 | 2418785 | 2014-10-20 04:44 | 2014-10-20 07:39 | 175.4 | 215 | 15090.1667 | 0.046152 | 0.00065756 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P18516 | CB 4 tripped L/O - Line down found at Pole P18516 during sectionlising - Isolated at ABS's M37 & M41 - Repair carried out - feeder returned to Service - Used 1X HV insulator and pin, 2X sleeves, .6 mtr conductor & binder wire. | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 70.1868 | 67.1868 | 14445.1667 | 0.044122 | 0.0006567 | 2014-10-20 | C | 0.044122 | 0.0006567 | 2015 | 2014-10-20 | C | 215 | 0.044122 | 0.0006567
1 | 2069796 | 2014-10-20 05:02 | 2014-10-23 05:32 | 4350 | 71 | 4473 | 0.01368 | 0.00021715 | NAPA ID:02874 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TX TC3805 | Break CB3 feeder cable away from T Blade switch "A" on TC3805 and aplpy PED's to cable ends. Retrofit new control panel to CB3. Primary test new protection system. Reconnect CB3 feeder cable to T Blade switch "A" on TC3805. Works location: Browne St S | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 4260 | 0.013012 | 0.00021686 | 2014-10-20 | B | 0.0065059 | 0.00010843 | 2015 | 2014-10-20 | B | 71 | 0.013012 | 0.00021686
1 | 2052223 | 2014-10-20 08:49 | 2014-10-20 12:08 | 199.4667 | 5 | 997.3333 | 0.0030503 | 1.5292e-05 | NAPA ID:03138 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses WH856 | Replace poles. Works location: Paroa Rd East WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 199.4667 | 196.4667 | 982.3333 | 0.0030005 | 1.5272e-05 | 2014-10-20 | B | 0.0015002 | 7.636e-06 | 2015 | 2014-10-20 | B | 5 | 0.0030005 | 1.5272e-05
1 | 2006368 | 2014-10-20 09:01 | 2014-10-20 13:05 | 244.7 | 1 | 244.7 | 0.0007484 | 3.0584e-06 | NAPA ID:02667 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole E0608 | Replace 11kV cross arms. Works location: SH29 Hinuera WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 244.7 | 241.7 | 241.7 | 0.00073825 | 3.0544e-06 | 2014-10-20 | B | 0.00036913 | 1.527e-06 | 2015 | 2014-10-20 | B | 1 | 0.00073825 | 3.0544e-06
1 | 2052255 | 2014-10-20 09:30 | 2014-10-20 11:15 | 105 | 4 | 420 | 0.0012845 | 1.2234e-05 | NAPA ID:02750 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 2508 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd Tariki Inglewood WO 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 105 | 102 | 408 | 0.0012462 | 1.2218e-05 | 2014-10-20 | B | 0.0006231 | 6.109e-06 | 2015 | 2014-10-20 | B | 4 | 0.0012462 | 1.2218e-05
1 | 2490231 | 2014-10-20 09:50 | 2014-10-20 16:26 | 396 | 31 | 12276 | 0.037545 | 9.4811e-05 | Restore Supply on Device K54 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp fuses 07 | plamnned outage | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 396 | 393 | 12183 | 0.037212 | 9.4687e-05 | 2014-10-20 | C | 0.037212 | 9.4687e-05 | 2015 | 2014-10-20 | C | 31 | 0.037212 | 9.4687e-05
1 | 2453288 | 2014-10-20 15:03 | 2014-10-20 19:17 | 253.9833 | 26 | 2051.1 | 0.0062731 | 7.9519e-05 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 771086 | Tripping on BCH RD CB3 caused by fault lightning arrestor. Isolation required between CB3, ABS 2567, 1181 and 1441 with backfeed at Sw/Gear 4518/3. 3 Lightning Arrestors replaced along with standoffs and some earthing repairs. | F2 | BEACH RD | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 78.8885 | 75.8885 | 1973.1 | 0.0060267 | 7.9415e-05 | 2014-10-20 | C | 0.0060267 | 7.9415e-05 | 2015 | 2014-10-20 | C | 26 | 0.0060267 | 7.9415e-05
1 | 2453798 | 2014-10-20 16:25 | 2014-10-20 19:13 | 168.6833 | 277 | 16936.5833 | 0.051799 | 0.00084718 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 742481 | 2R REQUESTED TO REPLACE HV XARM AND 20 METER OF CONDUCTOR REPLACED XARM INSULAOTORS BOLTS ETC 742481 ONE SPAN ON 2 PHASES HV OH | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 61.1429 | 58.1429 | 16105.5833 | 0.049193 | 0.00084608 | 2014-10-20 | C | 0.049193 | 0.00084607 | 2015 | 2014-10-20 | C | 277 | 0.049193 | 0.00084608
1 | 2453044 | 2014-10-21 08:00 | 2014-10-21 10:12 | 132.3 | 47 | 6218.1 | 0.019018 | 0.00014375 | NAPA ID:03820 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > PALM BEACH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/Gear 9024 | REPAIR OR REPLACE SW GEAR 9024. Works location; Palomino Place. WO 10162805. | F3 | PALM BEACH | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 132.3 | 129.3 | 6077.1 | 0.018562 | 0.00014356 | 2014-10-21 | B | 0.009281 | 7.1779e-05 | 2015 | 2014-10-21 | B | 47 | 0.018562 | 0.00014356
1 | 2075816 | 2014-10-21 08:45 | 2014-10-21 15:39 | 413.9167 | 12 | 4967 | 0.015191 | 3.6701e-05 | NAPA ID:02438 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-035 | REPLACE HV POLE AND ARMS FOR RECON WORK. Works location: Rangiuru Rd. WO 10154633 TA-2014-26 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 413.9167 | 410.9167 | 4931 | 0.015061 | 3.6653e-05 | 2014-10-21 | B | 0.0075307 | 1.8327e-05 | 2015 | 2014-10-21 | B | 12 | 0.015061 | 3.6653e-05
1 | 2157955 | 2014-10-21 08:46 | 2014-10-21 15:28 | 402.4833 | 5 | 2012.4167 | 0.0061548 | 1.5292e-05 | NAPA ID:02787 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 779166 | change 11 kv xarms under live 33 kv , from pole 779160 to 779166 ,also incl pole 779163. Works location: Decons Rd Taihape WO 10141707 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 402.4833 | 399.4833 | 1997.4167 | 0.006101 | 1.5272e-05 | 2014-10-21 | B | 0.0030505 | 7.636e-06 | 2015 | 2014-10-21 | B | 5 | 0.006101 | 1.5272e-05
1 | 2075250 | 2014-10-21 09:20 | 2014-10-21 14:39 | 318.65 | 24 | 7647.6 | 0.02339 | 7.3402e-05 | NAPA ID:02973 TP_WAIKINO GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WKOWHI077 | replace poles wkowhi077 & 074. Works location: Tauranga and Frankton Roads WO 10141294 | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 318.65 | 315.65 | 7575.6 | 0.023139 | 7.3306e-05 | 2014-10-21 | B | 0.01157 | 3.6653e-05 | 2015 | 2014-10-21 | B | 24 | 0.023139 | 7.3306e-05
1 | 2069435 | 2014-10-21 09:30 | 2014-10-21 16:51 | 441 | 10 | 4410 | 0.013488 | 3.0584e-05 | NAPA ID:02534 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 709138 | 11kv lines and equipment upgrade Remove 11kv temporary Links 12028 at pole 709138 Quarry Road. Works location: Mohakau Rd Ohura Rd WO IR1872 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 441 | 438 | 4380 | 0.013378 | 3.0544e-05 | 2014-10-21 | B | 0.0066892 | 1.5272e-05 | 2015 | 2014-10-21 | B | 10 | 0.013378 | 3.0544e-05
1 | 2053912 | 2014-10-21 09:41 | 2014-10-21 13:41 | 239.5167 | 3 | 718.55 | 0.0021976 | 9.1753e-06 | NAPA ID:02744 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 6214 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd Tariki Inglewood WO 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 239.5167 | 236.5167 | 709.55 | 0.0021673 | 9.1633e-06 | 2014-10-21 | B | 0.0010836 | 4.582e-06 | 2015 | 2014-10-21 | B | 3 | 0.0021673 | 9.1633e-06
1 | 2069562 | 2014-10-21 09:44 | 2014-10-21 15:18 | 333.8333 | 15 | 5007.5 | 0.015315 | 4.5876e-05 | NAPA ID:02635 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV K59 | Replace 11kv xarms. Works location: Lower Pakihikura Rd WO 10142182 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 333.8333 | 330.8333 | 4962.5 | 0.015158 | 4.5816e-05 | 2014-10-21 | B | 0.0075788 | 2.2908e-05 | 2015 | 2014-10-21 | B | 15 | 0.015158 | 4.5816e-05
1 | 2077239 | 2014-10-21 09:46 | 2014-10-21 14:48 | 302 | 3 | 906 | 0.0027709 | 9.1753e-06 | NAPA ID:02838 TP_MARTON GXP > PUKEPAPA SUB > TURAKINA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer X1829 | Replaceing Transformers, pole, & X arms X1829, X1865, X144. Works location: SHW3 Turakina WO 10147631 | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 302 | 299 | 897 | 0.0027398 | 9.1633e-06 | 2014-10-21 | B | 0.0013699 | 4.582e-06 | 2015 | 2014-10-21 | B | 3 | 0.0027398 | 9.1633e-06
1 | 2070362 | 2014-10-21 10:00 | 2014-10-21 14:59 | 298.9 | 175 | 52307.5 | 0.15998 | 0.00053522 | NAPA ID:03071 TP_OPUNAKE GXP > NGARIKI SUB > NGARIKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG434 | Replace Abs NG434 pole/switch. Replace Abs NG326 & xarms. Works location: Ngariki and Kina Rds WO 10147441 | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 298.9 | 295.9 | 51782.5 | 0.15817 | 0.00053452 | 2014-10-21 | B | 0.079083 | 0.00026726 | 2015 | 2014-10-21 | B | 175 | 0.15817 | 0.00053452
1 | 2157262 | 2014-10-22 06:01 | 2014-10-22 06:37 | 36.3 | 428 | 12420.4 | 0.037987 | 0.001309 | NAPA ID:02558 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 820907 | Install 2 line breaks for use in shutdown on 25/10/11 at poles 820907 & 820877. Works location: High St, Carterton. WO 10140873 IR6938 | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 29.0196 | 26.0196 | 11136.4 | 0.034015 | 0.0013073 | 2014-10-22 | B | 0.017008 | 0.00065365 | 2015 | 2014-10-22 | B | 428 | 0.034015 | 0.0013073
1 | 2075985 | 2014-10-22 08:45 | 2014-10-22 15:21 | 396 | 12 | 4752 | 0.014534 | 3.6701e-05 | NAPA ID:02440 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-035 | REPLACE HV POLE AND ARMS FOR RECON WORK. Works location: Rangiuru Rd WO 10154633 TA-2014-26 | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 396 | 393 | 4716 | 0.014405 | 3.6653e-05 | 2014-10-22 | B | 0.0072023 | 1.8327e-05 | 2015 | 2014-10-22 | B | 12 | 0.014405 | 3.6653e-05
1 | 2157318 | 2014-10-22 09:11 | 2014-10-22 14:55 | 344.1667 | 3 | 1032.5 | 0.0031578 | 9.1753e-06 | NAPA ID:02647 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 7430 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd. WO 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 344.1667 | 341.1667 | 1023.5 | 0.0031262 | 9.1633e-06 | 2014-10-22 | B | 0.0015631 | 4.582e-06 | 2015 | 2014-10-22 | B | 3 | 0.0031262 | 9.1633e-06
1 | 2152567 | 2014-10-22 09:15 | 2014-10-22 15:15 | 360.2 | 15 | 5403 | 0.016525 | 4.5876e-05 | NAPA ID:03201 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 6604 | 11kv poles and overhead lines upgrade of Pheney Road. Please Note: the 33kv line crossing Pheney Road 11kv has a line clearance of approximately eight metres and no extra isolations or precautions required between MAD. Works location: Pheney Rd New Plymo | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 360.2 | 357.2 | 5358 | 0.016366 | 4.5816e-05 | 2014-10-22 | B | 0.0081828 | 2.2908e-05 | 2015 | 2014-10-22 | B | 15 | 0.016366 | 4.5816e-05
1 | 2053953 | 2014-10-22 09:31 | 2014-10-22 13:46 | 255.0167 | 13 | 3315.2167 | 0.010139 | 3.9759e-05 | NAPA ID:03015 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 741824 | To remove pole 741824 plus upgrade transforner to new 100kVA plus new earths. Works location: Brown St, Waitara. WO 10149207. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 255.0167 | 252.0167 | 3276.2167 | 0.010007 | 3.9708e-05 | 2014-10-22 | B | 0.0050035 | 1.9854e-05 | 2015 | 2014-10-22 | B | 13 | 0.010007 | 3.9708e-05
1 | 2052445 | 2014-10-22 09:42 | 2014-10-22 14:26 | 284.1833 | 110 | 27473.35 | 0.084025 | 0.00033643 | NAPA ID:03058 TP_HAWERA GXP > MANAIA SUB > AUROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | MA164 | Replace 11Kv Abs MA164 & xarms on existing pole. Works location: Manaia Rd. WO 10147441 | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 249.7577 | 246.7577 | 27143.35 | 0.082907 | 0.00033599 | 2014-10-22 | B | 0.041454 | 0.00016799 | 2015 | 2014-10-22 | B | 110 | 0.082907 | 0.00033599
1 | 2548383 | 2014-10-22 14:41 | 2014-10-22 17:46 | 185 | 93 | 12648 | 0.038683 | 0.00028443 | Restore Supply on Device FP1154 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2127 | Found 1 wire down at pole N2127. Isolated at fuses FP1154. Repaired line and relivened | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 136 | 133 | 12369 | 0.03778 | 0.00028406 | 2014-10-22 | C | 0.03778 | 0.00028406 | 2015 | 2014-10-22 | C | 93 | 0.03778 | 0.00028406
1 | 2541976 | 2014-10-22 15:01 | 2014-10-22 15:33 | 32.4333 | 6 | 194.6 | 0.00059517 | 1.8351e-05 | Restore Supply on Device 7261 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 798561 | Replace HV fuseholder complete. This was required after made a second break at Links 7262 to comply with Powerco's equipotential bonding requirements. Attended by James Matthews | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 32.4333 | 29.4333 | 176.6 | 0.00053941 | 1.8327e-05 | 2014-10-22 | C | 0.00053941 | 1.8327e-05 | 2015 | 2014-10-22 | C | 6 | 0.00053941 | 1.8327e-05
1 | 2535492 | 2014-10-22 15:08 | 2014-10-22 19:01 | 232.9 | 1 | 232.9 | 0.00071231 | 3.0584e-06 | Restore Supply on Device T2/624 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 045315 | Tractor V pole - Isolated at Fuses D88 - Pole Replaced, feeder returned to service - used 1 x pole, 2x Blocks (Top & Bottom), 1 x Complete HV cross arm, 3x fuse carrier and base, 1x possium gaurd | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 232.9 | 229.9 | 229.9 | 0.00070221 | 3.0544e-06 | 2014-10-22 | C | 0.00070221 | 3.054e-06 | 2015 | 2014-10-22 | C | 1 | 0.00070221 | 3.0544e-06
1 | 2548549 | 2014-10-22 19:48 | 2014-10-22 20:45 | 57 | 35 | 1995 | 0.0061016 | 0.00010704 | Restore Supply on Device T5/129 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21167 | IS 2548463 LINKED NOT THE SAME BROKEN 11KV FUSE HOLDER NEED ASSSTIANCE AS WORKING ON 11KV AVALANCHE AS TAKING 14 TX S OFF Isolated at ABS K24 & ABS K70 - Fuse carrier and base replace - feeder restored to service - used 1x fuse carrier and base | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 57 | 54 | 1890 | 0.0057729 | 0.0001069 | 2014-10-22 | C | 0.0057729 | 0.0001069 | 2015 | 2014-10-22 | C | 35 | 0.0057729 | 0.0001069
1 | 2593391 | 2014-10-23 05:49 | 2014-10-23 09:58 | 249 | 1020 | 78565.3 | 0.24029 | 0.0031196 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 776901 | Replaced 100 m Conductor after Duck Hit lines at Pole 776901 | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 77.0248 | 74.0248 | 75505.3 | 0.23063 | 0.0031155 | 2014-10-23 | C | 0.23063 | 0.0031155 | 2015 | 2014-10-23 | C | 1020 | 0.23063 | 0.0031155
1 | 2595595 | 2014-10-23 06:06 | 2014-10-23 08:01 | 114.9667 | 1 | 114.9667 | 0.00035162 | 3.0584e-06 | Restore Supply on Device 3275T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 730343 | repplaced x2 3amp DDO (2 of 3)fuses to TX at pole 730343 due to bird strike No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 114.9667 | 111.9667 | 111.9667 | 0.00034199 | 3.0544e-06 | 2014-10-23 | C | 0.00034199 | 3.054e-06 | 2015 | 2014-10-23 | C | 1 | 0.00034199 | 3.0544e-06
1 | 2596235 | 2014-10-23 08:09 | 2014-10-23 10:02 | 112.55 | 1 | 112.55 | 0.00034423 | 3.0584e-06 | Restore Supply on Device TE7-062 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TE7-062 | Replaced 2 x 15A DDO HV fuses. Suspected bird strike. All other assets okay; nothing else replaced. Email sent to Jo, as appears could have SAIDI component. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 112.55 | 109.55 | 109.55 | 0.00033461 | 3.0544e-06 | 2014-10-23 | C | 0.00033461 | 3.054e-06 | 2015 | 2014-10-23 | C | 1 | 0.00033461 | 3.0544e-06
1 | 2159719 | 2014-10-23 08:17 | 2014-10-23 12:12 | 234.8167 | 9 | 2105.4 | 0.0064392 | 2.7526e-05 | NAPA ID:03291 TP_LINTON GXP > KAIRANGA SUB > BAINESSE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P43035 | Change 11kv pole P43035. Work Location: State Highway 56. W/O 10156813 | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 233.9333 | 230.9333 | 2078.4 | 0.0063483 | 2.749e-05 | 2014-10-23 | B | 0.0031742 | 1.3745e-05 | 2015 | 2014-10-23 | B | 9 | 0.0063483 | 2.749e-05
1 | 2596262 | 2014-10-23 08:36 | 2014-10-23 14:06 | 329.2833 | 106 | 34904.0333 | 0.10675 | 0.00032419 | Restore Supply on Device S180 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2264 | This is the Childern job from 2160799 | F3 | ESSEX ST | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 329.2833 | 326.2833 | 34586.0333 | 0.10564 | 0.00032377 | 2014-10-23 | C | 0.10564 | 0.00032377 | 2015 | 2014-10-23 | C | 106 | 0.10564 | 0.00032377
1 | 2153326 | 2014-10-23 09:00 | 2014-10-23 12:04 | 184 | 15 | 2760 | 0.0084412 | 4.5876e-05 | NAPA ID:02669 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP798 | To replace 11kV and LV cross arms. Work Location: Moore Road, Hinuera. Work Order# 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 184 | 181 | 2715 | 0.0082928 | 4.5816e-05 | 2014-10-23 | B | 0.0041464 | 2.2908e-05 | 2015 | 2014-10-23 | B | 15 | 0.0082928 | 4.5816e-05
1 | 2596686 | 2014-10-23 09:11 | 2014-10-23 14:57 | 346.1167 | 30 | 10383.5 | 0.031757 | 9.1753e-05 | Restore Supply on Device K62 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | ABS K62 | This is a chil job for 2159992 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 346.1167 | 343.1167 | 10293.5 | 0.031441 | 9.1633e-05 | 2014-10-23 | C | 0.031441 | 9.1633e-05 | 2015 | 2014-10-23 | C | 30 | 0.031441 | 9.1633e-05
1 | 2077626 | 2014-10-23 09:15 | 2014-10-23 14:56 | 341 | 35 | 11935 | 0.036502 | 0.00010704 | NAPA ID:02815 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 248637 | Change arms between 248637, O3415 & O3388. Work Location: Buchanan & Moehau Street, Pipiroa. W/O 10147779 | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 341 | 338 | 11830 | 0.036134 | 0.0001069 | 2014-10-23 | B | 0.018067 | 5.3452e-05 | 2015 | 2014-10-23 | B | 35 | 0.036134 | 0.0001069
1 | 2153323 | 2014-10-23 09:30 | 2014-10-23 13:15 | 225 | 3 | 675 | 0.0020644 | 9.1753e-06 | NAPA ID:02754 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 3722 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd, Tariki; Inglewood. WO 10150398 | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 225 | 222 | 666 | 0.0020342 | 9.1633e-06 | 2014-10-23 | B | 0.0010171 | 4.582e-06 | 2015 | 2014-10-23 | B | 3 | 0.0020342 | 9.1633e-06
1 | 2609457 | 2014-10-23 10:08 | 2014-10-23 13:52 | 224.2167 | 1 | 224.2167 | 0.00068575 | 3.0584e-06 | Restore Supply on Device X1804 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | x1804 | replace 2 amp hv fuse at tx x1804. 1 of 3 phases. cause: magpie. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 224.2167 | 221.2167 | 221.2167 | 0.00067569 | 3.0544e-06 | 2014-10-23 | C | 0.00067569 | 3.054e-06 | 2015 | 2014-10-23 | C | 1 | 0.00067569 | 3.0544e-06
1 | 2220908 | 2014-10-23 10:44 | 2014-10-23 14:58 | 254 | 37 | 9398 | 0.028743 | 0.00011316 | NAPA ID:02877 TP_OPUNAKE GXP > TASMAN SUB > TE KIRI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 376536 | Installing new ABS & xarms on existing 10m Busck pole 376536 2span past existing ABS TA920 new ABS will have a temp # TEMP10. Also replacing ABS TA906 & xarms on existing pole. Work Location: 2586 Eltham Road. W/O 10147441. Job was later coming out o | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 254 | 251 | 9287 | 0.028366 | 0.00011301 | 2014-10-23 | B | 0.014183 | 5.6507e-05 | 2015 | 2014-10-23 | B | 37 | 0.028366 | 0.00011301
1 | 2609569 | 2014-10-23 10:49 | 2014-10-23 11:04 | 15.0333 | 27 | 405.9 | 0.0012414 | 8.2577e-05 | Restore Supply on Device TA991 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | ABS TA975 | When faultman was carring out switching on NAPA 2877, OMS Number:2220908, when opening ABS TA975 they found that one of the contact arms where broken and stuck in the closed position, line was isolated at ABS's TA920 and TA991 to cut away the jumpers on t | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15.0333 | 12.0333 | 324.9 | 0.00099238 | 8.2469e-05 | 2014-10-23 | C | 0.00099238 | 8.2469e-05 | 2015 | 2014-10-23 | C | 27 | 0.00099238 | 8.2469e-05
1 | 2662414 | 2014-10-23 14:55 | 2014-10-23 17:34 | 158.8333 | 141 | 16166 | 0.049442 | 0.00043124 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 318959 | Recloser 9281 L/O. No Flags Sectionalised and found service line had been pulled off house by tractor. Line flicked across 11kV line. Removed from line and relivened. NDR 31158 | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 114.6525 | 111.6525 | 15743 | 0.048086 | 0.00043067 | 2014-10-23 | C | 0.048086 | 0.00043067 | 2015 | 2014-10-23 | C | 141 | 0.048086 | 0.00043067
1 | 2675089 | 2014-10-23 17:59 | 2014-10-23 20:20 | 140.7833 | 1 | 7277.45 | 0.022258 | 3.0584e-06 | Restore Supply on Device TC1727 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1727 | Transformer T1727 found to be faulty and needs replacing. 7.40 CREW COMING TO REPLACE THIS TRANSFORMER Transformer blew when feeder was re-livened see OMS 2662412 T1727 included within OMS ID 2675390 - this is the initial outage prior to isolation bein | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 7277.45 | 7274.45 | 7274.45 | 0.022219 | 3.0544e-06 | 2014-10-23 | C | 0.022219 | 3.054e-06 | 2015 | 2014-10-23 | C | 1 | 0.022219 | 3.0544e-06
1 | 2675286 | 2014-10-23 19:19 | 2014-10-23 22:23 | 183.7 | 32 | 2646.4 | 0.0080938 | 9.787e-05 | Restore Supply on Device TA994 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715526 | Line Down. Materials used 2mtrs of cu conductor and 2x sleeves | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 82.7 | 79.7 | 2550.4 | 0.00779 | 9.7742e-05 | 2014-10-23 | C | 0.00779 | 9.7742e-05 | 2015 | 2014-10-23 | C | 32 | 0.00779 | 9.7742e-05
1 | 2689025 | 2014-10-24 06:45 | 2014-10-24 08:40 | 115 | 31 | 3565 | 0.010903 | 9.4811e-05 | Restore Supply on Device T1136 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer T1136 | Urgent replacement of transformer T1136 due to voltage problems. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 115 | 112 | 3472 | 0.010605 | 9.4687e-05 | 2014-10-24 | C | 0.010605 | 9.4687e-05 | 2015 | 2014-10-24 | C | 31 | 0.010605 | 9.4687e-05
1 | 2349709 | 2014-10-24 08:46 | 2014-10-24 16:23 | 456.15 | 30 | 13684.5 | 0.041853 | 9.1753e-05 | NAPA ID:02989 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P08370 | Replace crossarms from pole P08370 to P12174. Works location: Beaconsfield Valley Rd WO 10160678 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 456.15 | 453.15 | 13594.5 | 0.041523 | 9.1633e-05 | 2014-10-24 | B | 0.020762 | 4.5816e-05 | 2015 | 2014-10-24 | B | 30 | 0.041523 | 9.1633e-05
1 | 2269733 | 2014-10-24 09:42 | 2014-10-24 13:40 | 238.6167 | 40 | 9544.6667 | 0.029192 | 0.00012234 | NAPA ID:03323 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGAMAIRE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse S23 | Replacing section fuse pole S23 and Tx pole T8/321, installing new road crossing pole for clearance between fuses and TX. Works location: Te Awe Awe Rd WO 10144737 | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 238.6167 | 235.6167 | 9424.6667 | 0.028787 | 0.00012218 | 2014-10-24 | B | 0.014393 | 6.1088e-05 | 2015 | 2014-10-24 | B | 40 | 0.028787 | 0.00012218
1 | 2313829 | 2014-10-24 10:01 | 2014-10-25 04:01 | 1080 | 44 | 26848.7 | 0.082115 | 0.00013457 | NAPA ID:03072 TP_OPUNAKE GXP > NGARIKI SUB > NGARIKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG408 | Replace Abs NG408 & xarms upgrade earth. Works location: Wiremu Rd WO 10147441 | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 610.1977 | 607.1977 | 26716.7 | 0.081604 | 0.00013439 | 2014-10-24 | B | 0.040802 | 6.7197e-05 | 2015 | 2014-10-24 | B | 44 | 0.081604 | 0.00013439
1 | 2402300 | 2014-10-24 10:30 | 2014-10-24 12:44 | 134.1667 | 552 | 73803.2167 | 0.22572 | 0.0016882 | NAPA ID:03716 TP_MASTERTON GXP > TINUI SUB | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Sub | isolate 11kv line which is backfeeding tinui sub at the moment so that the 33kv line which was broken in the last storm can be rehung above it See Job 2194313 | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 133.7015 | 130.7015 | 72147.2167 | 0.22037 | 0.001686 | 2014-10-24 | B | 0.11018 | 0.00084302 | 2015 | 2014-10-24 | B | 552 | 0.22037 | 0.001686
1 | 2773902 | 2014-10-25 13:00 | 2014-10-25 16:00 | 180.2 | 8 | 1441.6 | 0.004409 | 2.4467e-05 | Restore Supply on Device X4016 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 376185 | Outage required from Fuses 2709 on Pukerimu Rd. A twisted cross arm had caused 2 conductors to come down. (Loose King pin). Conductors rejoined, kingbolt retightened. | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 180.2 | 177.2 | 1417.6 | 0.00433 | 2.4435e-05 | 2014-10-25 | C | 0.00433 | 2.4435e-05 | 2015 | 2014-10-25 | C | 8 | 0.00433 | 2.4435e-05
1 | 2805153 | 2014-10-25 20:27 | 2014-10-26 01:59 | 331.5167 | 509 | 50103.7 | 0.15324 | 0.0015567 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 794733 | Found Fault at Pole 794733 after a report from home owner of sparking pole. fixed it try to reliven with no luck found another fault at pole 794699 which had a swam at bottom of pole Faultman now thinks fault Current could have Cause 1st fault Used 30m | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 98.4356 | 95.4356 | 48576.7 | 0.14837 | 0.0015547 | 2014-10-25 | C | 0.14837 | 0.0015547 | 2015 | 2014-10-25 | C | 509 | 0.14837 | 0.0015547
1 | 2822341 | 2014-10-26 08:37 | 2014-10-26 11:27 | 170.1833 | 132 | 14563.3333 | 0.044541 | 0.00040371 | Restore Supply on Device CB4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P04934 | Tripping on Pongaroa CB4. Feeder sectionalised / patrolled with floating conductor found at Pole P04934. Isolation between ABS Temp58 and V76 with backfeed at ABS I29. One Clamp top Insulator replaced. relivened OK. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 110.3283 | 107.3283 | 14167.3333 | 0.043273 | 0.00040318 | 2014-10-26 | C | 0.043273 | 0.00040318 | 2015 | 2014-10-26 | C | 132 | 0.043273 | 0.00040318
1 | 2822815 | 2014-10-26 14:06 | 2014-10-26 15:20 | 73.7333 | 126 | 3866.1 | 0.011824 | 0.00038536 | Restore Supply on Device T3/184 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3/184 | 2:25pm 2R Rquest as require to replace DDO assembly. HT Outage required between sw/Gear 10010 and ABS J52 to replace a DDO unit on T3/184 (One Phase). Backfeed at Sw/Gear 371. | F1, F2, F3 | FEILDING WEST 33KV | TP_BUNNYTHORPE | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 30.6833 | 27.6833 | 3488.1 | 0.010654 | 0.00038486 | 2014-10-26 | C | 0.010654 | 0.00038486 | 2015 | 2014-10-26 | C | 126 | 0.010654 | 0.00038486
1 | 2823023 | 2014-10-26 16:14 | 2014-10-26 19:24 | 189.1667 | 1 | 189.1667 | 0.00057855 | 3.0584e-06 | Restore Supply on Device TD3-141 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TD3 141 | Rewire 1 x 3 A H/V Fuse link. No other assets repaired or replaced on site, FM checked adjacent assets and up to Powerco Standard | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 189.1667 | 186.1667 | 186.1667 | 0.00056863 | 3.0544e-06 | 2014-10-26 | C | 0.00056863 | 3.054e-06 | 2015 | 2014-10-26 | C | 1 | 0.00056863 | 3.0544e-06
1 | 2823036 | 2014-10-26 16:36 | 2014-10-26 18:32 | 116.2667 | 323 | 18294.2833 | 0.055952 | 0.00098787 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 212643 | Recloser 9209/2 Trip. E/F P Trip. Line Patrolled & sectionalized. LFI's not flashing at ABS SE4-011. Fault beyond these LFI's. Line down at pole 212463. Repaired Faultman Dennis Ngatai Isolation at ABS SE4-011, No back feeds available | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 56.6386 | 53.6386 | 17325.2833 | 0.052919 | 0.00098658 | 2014-10-26 | C | 0.052919 | 0.00098658 | 2015 | 2014-10-26 | C | 323 | 0.052919 | 0.00098658
1 | 2823365 | 2014-10-26 16:50 | 2014-10-26 18:26 | 95.45 | 42 | 3322.6333 | 0.010162 | 0.00012845 | Restore Supply on Device SC2-042 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses SC2-056 | Fuse blown at SC2-056. Wrong fuse size installed at some stage. Only 8 Amp. Fuses reloaded with 25Amp, down stream fuses SC2-042 check, Loaded with 15amp fuses Fuses Possibly blown with Overload due to incorrect sizing Materials 6 HV fuse links | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 79.1103 | 76.1103 | 3196.6333 | 0.0097639 | 0.00012829 | 2014-10-26 | C | 0.0097639 | 0.00012829 | 2015 | 2014-10-26 | C | 42 | 0.0097639 | 0.00012829
1 | 2824335 | 2014-10-26 21:14 | 2014-10-27 03:12 | 358.6333 | 80 | 28674.6667 | 0.087699 | 0.00024467 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 835933 | Patrolled line Found tree in lines at Pole 835933 Had trouble getting tree Trimmings Out Removed Tree liven up ok | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 358.4333 | 355.4333 | 28434.6667 | 0.086852 | 0.00024435 | 2014-10-26 | C | 0.086852 | 0.00024435 | 2015 | 2014-10-26 | C | 80 | 0.086852 | 0.00024435
1 | 2856580 | 2014-10-27 02:52 | 2014-10-27 05:20 | 147.9167 | 1 | 147.9167 | 0.00045239 | 3.0584e-06 | Restore Supply on Device TE7-149 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TE7 149 | re wire 1 x O/H, H/V fuse line patrolled no fault found suspect wind. No other assets repaired or replaced on site, FM checked adjacent assets and up to Powerco Standard. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 147.9167 | 144.9167 | 144.9167 | 0.00044264 | 3.0544e-06 | 2014-10-27 | C | 0.00044264 | 3.054e-06 | 2015 | 2014-10-27 | C | 1 | 0.00044264 | 3.0544e-06
1 | 2856584 | 2014-10-27 04:55 | 2014-10-27 07:50 | 175.2667 | 126 | 19283.1333 | 0.058976 | 0.00038536 | Restore Supply on Device 573 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772923 | Recloser 573 Tripped E/F - Jumper found contacting cross arm during sectionalising at Pole 772923 - Cleared using hot sticks - Faultman to raise defect for cross arm replacement. | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 153.0407 | 150.0407 | 18905.1333 | 0.057744 | 0.00038486 | 2014-10-27 | C | 0.057744 | 0.00038486 | 2015 | 2014-10-27 | C | 126 | 0.057744 | 0.00038486
1 | 2858089 | 2014-10-27 06:47 | 2014-10-27 08:35 | 107.1167 | 6 | 358.6 | 0.0010968 | 1.8351e-05 | Restore Supply on Device X1161 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784519 | worked through control, replaced 2x 20a HV fuse links.nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 59.7667 | 56.7667 | 340.6 | 0.0010403 | 1.8327e-05 | 2014-10-27 | C | 0.0010403 | 1.8327e-05 | 2015 | 2014-10-27 | C | 6 | 0.0010403 | 1.8327e-05
1 | 2858180 | 2014-10-27 09:44 | 2014-10-27 10:59 | 75.6 | 8 | 604.8 | 0.0018497 | 2.4467e-05 | Restore Supply on Device X1056 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 802708 | 1 Fuse found blown at Fuses 1100 - Isolated at Fuses 1100 - Insulator replacedon Pole 802708 - | F2 | MARTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 75.6 | 72.6 | 580.8 | 0.001774 | 2.4435e-05 | 2014-10-27 | C | 0.001774 | 2.4435e-05 | 2015 | 2014-10-27 | C | 8 | 0.001774 | 2.4435e-05
1 | 2858800 | 2014-10-27 11:01 | 2014-10-27 13:15 | 133.7167 | 231 | 15301.9333 | 0.0468 | 0.0007065 | Restore Supply on Device T21 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | RS T21 | RS T21 Tripped, line patrolled with no fault found | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 66.2421 | 63.2421 | 14608.9333 | 0.044622 | 0.00070557 | 2014-10-27 | C | 0.044622 | 0.00070557 | 2015 | 2014-10-27 | C | 231 | 0.044622 | 0.00070557
1 | 2866068 | 2014-10-28 08:57 | 2014-10-28 14:42 | 345 | 12 | 4140 | 0.012662 | 3.6701e-05 | Restore Supply on Device TF5-078 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF5-078 | Planned outage | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 4104 | 0.012535 | 3.6653e-05 | 2014-10-28 | C | 0.012535 | 3.6653e-05 | 2015 | 2014-10-28 | C | 12 | 0.012535 | 3.6653e-05
1 | 2369791 | 2014-10-28 09:03 | 2014-10-28 15:32 | 388.7167 | 83 | 32263.4833 | 0.098675 | 0.00025385 | NAPA ID:02816 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O3360 | Change poles & arms between pole sitesO3360 & O12997. Works location: SH25 Pipiroa WO 10147779 | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 388.7167 | 385.7167 | 32014.4833 | 0.097786 | 0.00025352 | 2014-10-28 | B | 0.048893 | 0.00012676 | 2015 | 2014-10-28 | B | 83 | 0.097786 | 0.00025352
1 | 2318127 | 2014-10-28 09:39 | 2014-10-28 13:55 | 256.2 | 97 | 24836.5 | 0.07596 | 0.00029667 | NAPA ID:03017 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W8123 | Replace badly corroded transformer W8123 and W8125 with same size units. Works location: Manawapou Rd. WO 10148889. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 256.0464 | 253.0464 | 24545.5 | 0.074972 | 0.00029628 | 2014-10-28 | B | 0.037486 | 0.00014814 | 2015 | 2014-10-28 | B | 97 | 0.074972 | 0.00029628
1 | 2861326 | 2014-10-28 10:00 | 2014-10-28 11:58 | 118 | 6 | 708 | 0.0021654 | 1.8351e-05 | Restore Supply on Device T7325 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Tasman TA9 | This job was part of a planned outage under NAPA 2886, OMS 2319533. Operator linked this job incorrectly to another job. Power Off: 10:00. Power On: 11:58 | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 118 | 115 | 690 | 0.0021076 | 1.8327e-05 | 2014-10-28 | C | 0.0021076 | 1.8327e-05 | 2015 | 2014-10-28 | C | 6 | 0.0021076 | 1.8327e-05
1 | 2388195 | 2014-10-28 10:14 | 2014-10-28 15:28 | 314 | 41 | 12874 | 0.039374 | 0.0001254 | NAPA ID:02806 TP_BRUNSWICK GXP > PEAT ST SUB > ST JOHNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X341 | Replace X341 Tasman View.No 400V backfeed. As discussed with Kevin Horn. Works location: Babbage Place Brunswick. WO 10147439. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 314 | 311 | 12751 | 0.038947 | 0.00012523 | 2014-10-28 | B | 0.019473 | 6.2616e-05 | 2015 | 2014-10-28 | B | 41 | 0.038947 | 0.00012523
1 | 2861499 | 2014-10-28 14:12 | 2014-10-28 15:53 | 100.45 | 1 | 100.45 | 0.00030722 | 3.0584e-06 | Restore Supply on Device X2009 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | x2009 | re-terminated ug cable going up a pole. used 3 x connectors. 3 phase cable. tx x2009. cause: weather and deterioration. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 100.45 | 97.45 | 97.45 | 0.00029765 | 3.0544e-06 | 2014-10-28 | C | 0.00029765 | 3.054e-06 | 2015 | 2014-10-28 | C | 1 | 0.00029765 | 3.0544e-06
1 | 2861521 | 2014-10-28 14:33 | 2014-10-28 17:26 | 172.7833 | 6 | 1036.7 | 0.0031707 | 1.8351e-05 | Restore Supply on Device L1037 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 727848 | No Power at L1037. Brett Bensley Attended. No Paper work available for this outage. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 172.7833 | 169.7833 | 1018.7 | 0.0031115 | 1.8327e-05 | 2014-10-28 | C | 0.0031115 | 1.8327e-05 | 2015 | 2014-10-28 | C | 6 | 0.0031115 | 1.8327e-05
1 | 2861655 | 2014-10-28 16:39 | 2014-10-28 17:19 | 40 | 2 | 80 | 0.00024467 | 6.1168e-06 | unknown | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 727848 |  | F3 | PORTLAND QUAY | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 74 | 0.00022603 | 6.1088e-06 | 2014-10-28 | C | 0.00022603 | 6.109e-06 | 2015 | 2014-10-28 | C | 2 | 0.00022603 | 6.1088e-06
1 | 2862996 | 2014-10-28 19:21 | 2014-10-29 01:05 | 343.65 | 4 | 384.2 | 0.001175 | 1.2234e-05 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N3340 | Blown transformer. Requesting 2R for replacing transformer and for Paul Fitzpatrick to come to site with hi-ab truck. Isolation from Fuses NG380, Transformer N3340 replaced after original received a nasty lightning strike. Relivened OK. Kane MacKay and C | F4/F1 | SOUTH RD NGARIKI | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 96.05 | 93.05 | 372.2 | 0.0011369 | 1.2218e-05 | 2014-10-28 | B | 0.00056843 | 6.109e-06 | 2015 | 2014-10-28 | B | 4 | 0.0011369 | 1.2218e-05
1 | 2863060 | 2014-10-28 20:44 | 2014-10-28 23:58 | 193.7167 | 3 | 547.9167 | 0.0016758 | 9.1753e-06 | Restore Supply on Device 6259 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 6259 | Lightning in area - Initially thought Transf. 2786T required changing. (LV fuses blown). HT Fuse 6259 found tripped, reclosed OK. (10A replaced0. All 3 fuses replaced on 2786T (3A). | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 182.6389 | 179.6389 | 538.9167 | 0.0016461 | 9.1633e-06 | 2014-10-28 | C | 0.0016461 | 9.163e-06 | 2015 | 2014-10-28 | C | 3 | 0.0016461 | 9.1633e-06
1 | 2863073 | 2014-10-28 20:57 | 2014-10-28 21:18 | 20.3167 | 1316 | 12816.0667 | 0.039197 | 0.0040249 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | n/A | Suspect o/L due to back feed on PMA CB 3 due to Fire under lines | F3 | TARA RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 9.7387 | 6.7387 | 8868.0667 | 0.027087 | 0.0040196 | 2014-10-28 | C | 0.027087 | 0.0040196 | 2015 | 2014-10-28 | C | 1316 | 0.027087 | 0.0040196
1 | 2865207 | 2014-10-29 03:53 | 2014-10-29 10:40 | 407 | 7 | 2849 | 0.0087134 | 2.1409e-05 | Restore Supply on Device T5395 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5395 | Lightning Strike on Transformer T5395. Transformer to be changed. Outage reflected in OMS Job ID 2867264. Nick Webby attended. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 407 | 404 | 2828 | 0.0086379 | 2.1381e-05 | 2014-10-29 | C | 0.0086379 | 2.1381e-05 | 2015 | 2014-10-29 | C | 7 | 0.0086379 | 2.1381e-05
1 | 2865226 | 2014-10-29 06:14 | 2014-10-29 10:45 | 271.25 | 817 | 15719.4833 | 0.048077 | 0.0024987 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 220615 | CB 3 tripped to L/O - no flags - immediate backfeed put in from sectionaliser 9675/2 to recloser 9488/2 line sectionalised & patrolled - broken crossarm at pole 220616 brought line down set pole on fire - crossarm was rotten. Pole & crossarm replaced a | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 19.2405 | 16.2405 | 13268.4833 | 0.040528 | 0.0024955 | 2014-10-29 | C | 0.040528 | 0.0024955 | 2015 | 2014-10-29 | C | 817 | 0.040528 | 0.0024955
1 | 2866058 | 2014-10-29 07:10 | 2014-10-29 09:18 | 128.0667 | 1 | 128.0667 | 0.00039168 | 3.0584e-06 | Restore Supply on Device TE4-054 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 222298 | x3 blown fuses 50amp DDO - SE4015 set of 3 just the fuses not the Assembly cause car v pole from last night - pole 222298 No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 128.0667 | 125.0667 | 125.0667 | 0.00038201 | 3.0544e-06 | 2014-10-29 | C | 0.00038201 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.00038201 | 3.0544e-06
1 | 2866061 | 2014-10-29 07:10 | 2014-10-29 09:21 | 131.8167 | 1 | 131.8167 | 0.00040315 | 3.0584e-06 | Restore Supply on Device TE4-149 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 222298 | SAME AS OMS 2866058. x3 blown fuses 50amp DDO - SE4015 set of 3 just the fuses not the Assembly. Cause car v pole from last night (2864690)- pole 222298. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok. | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 131.8167 | 128.8167 | 128.8167 | 0.00039346 | 3.0544e-06 | 2014-10-29 | C | 0.00039346 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.00039346 | 3.0544e-06
1 | 2866549 | 2014-10-29 08:01 | 2014-10-29 11:27 | 205.7 | 250 | 29528.9333 | 0.090312 | 0.00076461 | Restore Supply on Device T2868 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Tuhitarata Substation C627 | Possibly part of OMS : 2866396. Tuhitarata CB C627 auto reclosed at 07:39. Line patrolled ans Sectionaliser C639 found open at 09:22. Feeder sectionalised, no fault found. Suspect line clash. Gavin Gray attended. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 118.1157 | 115.1157 | 28778.9333 | 0.087903 | 0.00076361 | 2014-10-29 | C | 0.087903 | 0.00076361 | 2015 | 2014-10-29 | C | 250 | 0.087903 | 0.00076361
1 | 2866454 | 2014-10-29 08:39 | 2014-10-29 15:20 | 401.6833 | 64 | 25707.7333 | 0.078625 | 0.00019574 | Restore Supply on Device IC247 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P1948 | Replace 11kV pole P1948. Work location: 91 Pukekauri Road, Waikino, Work Order 10156775 | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 401.6833 | 398.6833 | 25515.7333 | 0.077936 | 0.00019548 | 2014-10-29 | C | 0.077936 | 0.00019548 | 2015 | 2014-10-29 | C | 64 | 0.077936 | 0.00019548
1 | 2323073 | 2014-10-29 09:00 | 2014-10-29 10:50 | 109.6333 | 5 | 475 | 0.0014528 | 1.5292e-05 | NAPA ID:02682 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses TC2603 | To replace an existing 3 phase 30kVA Transformer with a 3 phase 50kVA. Works location: Te Tuhi Rd Matamata. WO 10162109. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 95 | 92 | 460 | 0.001405 | 1.5272e-05 | 2014-10-29 | B | 0.00070252 | 7.636e-06 | 2015 | 2014-10-29 | B | 5 | 0.001405 | 1.5272e-05
1 | 2357783 | 2014-10-29 09:10 | 2014-10-29 13:45 | 275 | 2 | 550 | 0.0016821 | 6.1168e-06 | NAPA ID:02655 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 797697 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd. WO 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 275 | 272 | 544 | 0.0016616 | 6.1088e-06 | 2014-10-29 | B | 0.0008308 | 3.054e-06 | 2015 | 2014-10-29 | B | 2 | 0.0016616 | 6.1088e-06
1 | 2323023 | 2014-10-29 09:15 | 2014-10-29 15:19 | 363.6667 | 15 | 5455 | 0.016684 | 4.5876e-05 | NAPA ID:03205 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6604 | 11kv poles and overhead lines upgrade of Pheney Road. Works location: Pheney Rd New Plymouth WO IR7213 | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 363.6667 | 360.6667 | 5410 | 0.016524 | 4.5816e-05 | 2014-10-29 | B | 0.0082622 | 2.2908e-05 | 2015 | 2014-10-29 | B | 15 | 0.016524 | 4.5816e-05
1 | 2380666 | 2014-10-29 09:30 | 2014-10-29 13:20 | 230 | 13 | 2990 | 0.0091447 | 3.9759e-05 | NAPA ID:03377 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ASHHURST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T4/423 | Upgrade Existing TX T4/423 to 100KVA Micropad Mount. Works location: Wyndham St Ashhurst WO 10139708 | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 230 | 227 | 2951 | 0.0090136 | 3.9708e-05 | 2014-10-29 | B | 0.0045068 | 1.9854e-05 | 2015 | 2014-10-29 | B | 13 | 0.0090136 | 3.9708e-05
1 | 2322854 | 2014-10-29 09:40 | 2014-10-29 16:12 | 391.9 | 4 | 966.2 | 0.002955 | 1.2234e-05 | NAPA ID:02755 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 2512 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location:Surrey Rd Tariki Inglewood WO 10153098 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 241.55 | 238.55 | 954.2 | 0.0029145 | 1.2218e-05 | 2014-10-29 | B | 0.0014573 | 6.109e-06 | 2015 | 2014-10-29 | B | 4 | 0.0029145 | 1.2218e-05
1 | 2867279 | 2014-10-29 11:29 | 2014-10-29 18:15 | 405.7667 | 416 | 168628.3 | 0.51574 | 0.0012723 | Restore Supply on Device C937 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 838558, 838557 | CB C937 Tripped O/C A&C Ph E/F - Tree found through lines at Pole 838558 - Isolated at ABS S165 - Pole Replaced including Cross arm, plus complete cross arm on Pole 838557 - Tree outside notice zone - Used 1 x Pole, 1 x Block, 1 x Donut block, 2 x Complet | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 405.3565 | 402.3565 | 167380.3 | 0.51125 | 0.0012706 | 2014-10-29 | C | 0.51125 | 0.0012706 | 2015 | 2014-10-29 | C | 416 | 0.51125 | 0.0012706
1 | 2867737 | 2014-10-29 12:09 | 2014-10-29 16:00 | 231.45 | 294 | 20542.05 | 0.062826 | 0.00089918 | Restore Supply on Device C917 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 799906 | CB C917 Tripped - no flags. Line patrolled and t ree found through lines. Faultman made safe and 2R sent through for second crew to replace pole. NDR 34880. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 69.8709 | 66.8709 | 19660.05 | 0.06005 | 0.000898 | 2014-10-29 | C | 0.06005 | 0.000898 | 2015 | 2014-10-29 | C | 294 | 0.06005 | 0.000898
1 | 2869107 | 2014-10-29 12:34 | 2014-10-29 12:54 | 19.6 | 195 | 3822 | 0.011689 | 0.00059639 | Restore Supply on Device TA7 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB TA7 | CB TA7 Trip. A & B Phase Pick up. High Winds in the area at the time. Possible Line Clash. Closed back in OK | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 19.6 | 16.6 | 3237 | 0.0098872 | 0.00059561 | 2014-10-29 | C | 0.0098872 | 0.00059561 | 2015 | 2014-10-29 | C | 195 | 0.0098872 | 0.00059561
1 | 2529107 | 2014-10-29 12:35 | 2014-10-29 14:25 | 109.9167 | 183 | 20114.75 | 0.061519 | 0.00055969 | NAPA ID:03812 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 839272 | Tree work near 11kV Lines. 11kV pole 839272 and 839281 between transformer T2563 and T2541. Works location: Palmer Rd Mauriceville. WO 10152356 Resulted in a tripping of Fuses 7054 on job 2869304 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 109.9167 | 106.9167 | 19565.75 | 0.059762 | 0.00055896 | 2014-10-29 | B | 0.029881 | 0.00027948 | 2015 | 2014-10-29 | B | 183 | 0.059762 | 0.00055896
1 | 2869105 | 2014-10-29 12:45 | 2014-10-30 12:55 | 1450 | 1 | 1450 | 0.0044347 | 3.0584e-06 | Restore Supply on Device 4672 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses 4672 | Blown HV O/H cable - Open andTaged Fuses 4672 replaced x1DDO fuse and candle at pole 771246. Will need to go back in a couple of days to repair HV cable. Worked through control. Scott Bullock to arrange this with control. 30/10 Customer was advised 29/ | F2 | GILBERD ST | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1450 | 1447 | 1447 | 0.0044198 | 3.0544e-06 | 2014-10-29 | C | 0.0044198 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.0044198 | 3.0544e-06
1 | 2869854 | 2014-10-29 13:20 | 2014-10-29 14:11 | 50.25 | 162 | 8140.5 | 0.024897 | 0.00049546 | Restore Supply on Device WH803 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722940 | Emergency isolation to replace broken DDO's and Crossarm at pole 722940. 1 X DDO x-arm 1 X Full set DDO's. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 50.25 | 47.25 | 7654.5 | 0.02338 | 0.00049482 | 2014-10-29 | C | 0.02338 | 0.00049482 | 2015 | 2014-10-29 | C | 162 | 0.02338 | 0.00049482
1 | 2873280 | 2014-10-29 20:38 | 2014-10-29 22:46 | 127.1 | 59 | 7440.9667 | 0.022758 | 0.00018045 | Restore Supply on Device 5555 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuses 5555 | Fuses 5555 found blown as part of dispatch job - Fuses replaced after patrolling line, also 1 x fuse for Transformer P2040 blown, these were also replaced - suspect lightening strike. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 126.1181 | 123.1181 | 7263.9667 | 0.022187 | 0.00018021 | 2014-10-29 | C | 0.022187 | 0.00018021 | 2015 | 2014-10-29 | C | 59 | 0.022187 | 0.00018021
1 | 2873283 | 2014-10-29 21:05 | 2014-10-30 00:30 | 204.5167 | 277 | 21752.55 | 0.066528 | 0.00084718 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 746345 | RS 6610/2 Tripped - B Ph O/C L/O - Line down found while sectionalising at pole 746345 - Isolated at ABS's 355 & 347 - line repaired - used 10 mtrs Conducter & 3 x sleeves. Chris Viviers attended. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 78.5291 | 75.5291 | 20921.55 | 0.063903 | 0.00084608 | 2014-10-29 | C | 0.063903 | 0.00084607 | 2015 | 2014-10-29 | C | 277 | 0.063903 | 0.00084608
1 | 2874420 | 2014-10-29 21:10 | 2014-10-30 05:41 | 510.55 | 1 | 510.55 | 0.0015615 | 3.0584e-06 | Restore Supply on Device N1210 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses NG404 | Craig Brogden returned later in night replace fuse at NG404 & NG461 and for transformer N1195 - used 3x 6amp fuses, 2 x 2amp fuses and 2x15amp fuses. | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 510.55 | 507.55 | 507.55 | 0.0015503 | 3.0544e-06 | 2014-10-29 | C | 0.0015503 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.0015503 | 3.0544e-06
1 | 2874425 | 2014-10-29 21:12 | 2014-10-29 22:45 | 93.2167 | 511 | 41213.0833 | 0.12605 | 0.0015629 | Restore Supply on Device 2 | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | cloton rd sub | Job should of been tied to 2874937 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80.6518 | 77.6518 | 39680.0833 | 0.1212 | 0.0015608 | 2014-10-29 | C | 0.1212 | 0.0015608 | 2015 | 2014-10-29 | C | 511 | 0.1212 | 0.0015608
1 | 2875260 | 2014-10-29 21:33 | 2014-10-29 23:41 | 127.6833 | 1 | 127.6833 | 0.00039051 | 3.0584e-06 | Restore Supply on Device 4725T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4275T | 2 AMP HT FUSE DUE TO LIGHTNING. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 127.6833 | 124.6833 | 124.6833 | 0.00038084 | 3.0544e-06 | 2014-10-29 | C | 0.00038084 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.00038084 | 3.0544e-06
1 | 2875681 | 2014-10-29 21:58 | 2014-10-29 23:20 | 81.9833 | 2 | 163.9667 | 0.00050148 | 6.1168e-06 | Restore Supply on Device 6942 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | RC 6942 | RS 6942 tripped L/O - Not Patrolled - held on reclose. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 81.9833 | 78.9833 | 157.9667 | 0.0004825 | 6.1088e-06 | 2014-10-29 | C | 0.0004825 | 6.109e-06 | 2015 | 2014-10-29 | C | 2 | 0.0004825 | 6.1088e-06
1 | 2876544 | 2014-10-29 22:10 | 2014-10-29 23:44 | 94.2 | 1 | 94.2 | 0.0002881 | 3.0584e-06 | Restore Supply on Device 3238T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3238T | 2 X 2 AMP LIGHTNING. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 94.2 | 91.2 | 91.2 | 0.00027856 | 3.0544e-06 | 2014-10-29 | C | 0.00027856 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.00027856 | 3.0544e-06
1 | 2876934 | 2014-10-29 22:23 | 2014-10-30 00:41 | 137.5333 | 1 | 137.5333 | 0.00042063 | 3.0584e-06 | Restore Supply on Device 819 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 819 | 2 X 3 amp ht fuses due to lightning. No other assets repaired or replaced. Adjacent assets ok. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 137.5333 | 134.5333 | 134.5333 | 0.00041092 | 3.0544e-06 | 2014-10-29 | C | 0.00041092 | 3.054e-06 | 2015 | 2014-10-29 | C | 1 | 0.00041092 | 3.0544e-06
1 | 2877977 | 2014-10-29 22:41 | 2014-10-30 13:27 | 886.1167 | 69 | 21705.1167 | 0.066383 | 0.00021103 | Restore Supply on Device 4288T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole 765152 | Trees found through lines during sectionlising after RS 6274 from dispatch job - Pole Number 765154 - Isolated at fuses 6643 - Repairs will need to be carried out in day light. 10 Maikaikatea Rd Customer run to say tree through lines only feeding woolshed | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 314.5669 | 311.5669 | 21498.1167 | 0.065664 | 0.00021076 | 2014-10-29 | C | 0.065664 | 0.00021075 | 2015 | 2014-10-29 | C | 69 | 0.065664 | 0.00021076
1 | 2877980 | 2014-10-29 22:44 | 2014-10-30 01:06 | 141.7333 | 462 | 38470.2 | 0.11766 | 0.001413 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 755604 | CB 6 Tripped E/F L/O - Possum found on lines while sectionlising - cleared using hot sticks. Brett Moratti attended. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 83.2688 | 80.2688 | 37084.2 | 0.11327 | 0.0014111 | 2014-10-29 | C | 0.11327 | 0.0014111 | 2015 | 2014-10-29 | C | 462 | 0.11327 | 0.0014111
1 | 2876548 | 2014-10-29 22:58 | 2014-10-29 23:14 | 16.1167 | 377 | 5742.9667 | 0.017564 | 0.001153 | Restore Supply on Device S31 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB S31 | Part of OMS 2874937, showing wrong sub station was not picked up until afterwards. Blown transformer caused outage | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15.2333 | 12.2333 | 4611.9667 | 0.014087 | 0.0011515 | 2014-10-29 | C | 0.014087 | 0.0011515 | 2015 | 2014-10-29 | C | 377 | 0.014087 | 0.0011515
1 | 2881214 | 2014-10-29 23:27 | 2014-11-05 15:31 | 9604.1 | 2 | 2258 | 0.0069059 | 6.1168e-06 | Restore Supply on Device N1209 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N1209 | Power may have been restored around 5 am will need to contact telecom - 6:35am Contacted Telecom they still hva no power at the site updated details 2.47pm one tx has been livened but another tx has blown including all the earths and cable and telecom | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1129 | 1126 | 2252 | 0.0068786 | 6.1088e-06 | 2014-10-29 | C | 0.0068786 | 6.109e-06 | 2015 | 2014-10-29 | C | 2 | 0.0068786 | 6.1088e-06
1 | 2879436 | 2014-10-30 00:22 | 2014-10-30 01:09 | 47.4833 | 669 | 31766.35 | 0.097155 | 0.0020461 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Rec 9641/2 | Unknown Fault, Line Patrolled. No fault Found, strong wind gusts at the time of tripping | F2/F3 | QUEEN ST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 47.4833 | 44.4833 | 29759.35 | 0.090898 | 0.0020434 | 2014-10-30 | C | 0.090898 | 0.0020434 | 2015 | 2014-10-30 | C | 669 | 0.090898 | 0.0020434
1 | 2875266 | 2014-10-30 02:00 | 2014-10-30 12:51 | 650.8667 | 2 | 764.5167 | 0.0023382 | 6.1168e-06 | Restore Supply on Device P1200 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P1200 | Transformer P1200 found to be faulty due to possible lightning strike, will require replacement in morning 10.33am paul Sullivan going to replace this now Replaced 30kva TX. Emailed Jo as appears could have SAIDI component. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 382.2583 | 379.2583 | 758.5167 | 0.0023168 | 6.1088e-06 | 2014-10-30 | C | 0.0023168 | 6.109e-06 | 2015 | 2014-10-30 | C | 2 | 0.0023168 | 6.1088e-06
1 | 2881186 | 2014-10-30 04:11 | 2014-10-30 10:05 | 354 | 3 | 1062 | 0.003248 | 9.1753e-06 | Restore Supply on Device TC1773 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1773 | 50 kVA transformer Blown from Lightning. Transformer replaced. Emailed Jo as appears could have SAIDI component. Outage reflected under OMS Job ID 2881946 | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 354 | 351 | 1053 | 0.0032163 | 9.1633e-06 | 2014-10-30 | C | 0.0032163 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.0032163 | 9.1633e-06
1 | 2881196 | 2014-10-30 04:50 | 2014-10-30 11:20 | 390 | 3 | 1170 | 0.0035784 | 9.1753e-06 | Restore Supply on Device TC4522 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T4522 | 07:00 Transformer T4522 30kVA. Blown by lightning Will need replacing. replaced 3a DDO fuse, transformer to be replaced Transformer replaced. Emailed Jo as appears could have SAIDI component. Outage reflected under Child Job 2885386 | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 390 | 387 | 1161 | 0.0035462 | 9.1633e-06 | 2014-10-30 | C | 0.0035462 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.0035462 | 9.1633e-06
1 | 2881205 | 2014-10-30 05:02 | 2014-10-30 13:50 | 528 | 3 | 1584 | 0.0048445 | 9.1753e-06 | Restore Supply on Device TC4523 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC5423 | 08:10 Transformer TC4523 Found blown by lightning. To be replaced. 1x 5a DDO replaced. Transformer to be replaced Transformer TC4523 Replaced by Greg Whyte. Outage reflected in OMS Job ID 2888559 | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 528 | 525 | 1575 | 0.0048107 | 9.1633e-06 | 2014-10-30 | C | 0.0048107 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.0048107 | 9.1633e-06
1 | 2881261 | 2014-10-30 06:19 | 2014-11-01 08:36 | 3017.1333 | 2 | 5972.3333 | 0.018266 | 6.1168e-06 | Restore Supply on Device 3431T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3431T | 2R request as have a blown TX 1/11 8.31AM PHONED DENNIS EMBLING HE CONFIRMED THIS TX HAS BEEN REPLACED BY BRUCE KERR. Emailed Jo, as could have SAIDI component. | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2986.1667 | 2983.1667 | 5966.3333 | 0.018224 | 6.1088e-06 | 2014-10-30 | C | 0.018224 | 6.109e-06 | 2015 | 2014-10-30 | C | 2 | 0.018224 | 6.1088e-06
1 | 2881279 | 2014-10-30 06:30 | 2014-10-30 09:34 | 184.1167 | 1 | 184.1167 | 0.00056311 | 3.0584e-06 | Restore Supply on Device TC3200 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Tx T3200 | replaced 2x 3amp ddo fuse hv o/h. Tx T3200. Cause lightning. Full power restored nothing else repaired or replaced. Adjacent assets - ok. | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 184.1167 | 181.1167 | 181.1167 | 0.00055321 | 3.0544e-06 | 2014-10-30 | C | 0.00055321 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00055321 | 3.0544e-06
1 | 2881293 | 2014-10-30 06:40 | 2014-10-30 09:51 | 191.3167 | 3 | 472.8 | 0.001446 | 9.1753e-06 | Restore Supply on Device TC2854 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2854 | 1 x 5amp DDO fuse caused by lightning at TC2854. No other assets repaired or replaced, FM checked adjacent assets and up to PCO standard | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 157.6 | 154.6 | 463.8 | 0.0014166 | 9.1633e-06 | 2014-10-30 | C | 0.0014166 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.0014166 | 9.1633e-06
1 | 2881308 | 2014-10-30 06:52 | 2014-10-30 13:50 | 418 | 2 | 836 | 0.0025568 | 6.1168e-06 | Restore Supply on Device 2226T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2226T | blown tx 2228 2r another crew will replace Transformer 2226T Replaced by Ben Englebretsen Outage reflected under OMS Job ID 2888542 | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 418 | 415 | 830 | 0.0025352 | 6.1088e-06 | 2014-10-30 | C | 0.0025352 | 6.109e-06 | 2015 | 2014-10-30 | C | 2 | 0.0025352 | 6.1088e-06
1 | 2881337 | 2014-10-30 07:04 | 2014-10-30 11:30 | 266.4833 | 1 | 266.4833 | 0.00081502 | 3.0584e-06 | Restore Supply on Device 763 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 252320 | 2x 3amp hv fuses elements tx 763 pole 252320 due to lightening surrounding asett all good nothing else repaired or replaced | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 266.4833 | 263.4833 | 263.4833 | 0.00080479 | 3.0544e-06 | 2014-10-30 | C | 0.00080479 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00080479 | 3.0544e-06
1 | 2881429 | 2014-10-30 07:46 | 2014-10-30 09:36 | 110.2667 | 1 | 110.2667 | 0.00033724 | 3.0584e-06 | Restore Supply on Device TC4417 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Tc4417 | lightning hv oh 3x 3amp hv fuses in the oh tx tc4417 surrounding asset all good. | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 110.2667 | 107.2667 | 107.2667 | 0.00032764 | 3.0544e-06 | 2014-10-30 | C | 0.00032764 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00032764 | 3.0544e-06
1 | 2881841 | 2014-10-30 08:12 | 2014-10-30 12:02 | 230.2333 | 1 | 230.2333 | 0.00070415 | 3.0584e-06 | Restore Supply on Device 5106E | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5106E | replaced x3 2amp fuses DDO fuse blown due to lightning at TX 5106E No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok. Emailed Jo, as appears could have a SAIDI component. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 230.2333 | 227.2333 | 227.2333 | 0.00069407 | 3.0544e-06 | 2014-10-30 | C | 0.00069407 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00069407 | 3.0544e-06
1 | 2379612 | 2014-10-30 08:30 | 2014-10-30 15:30 | 420 | 8 | 3360 | 0.010276 | 2.4467e-05 | NAPA ID:02657 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 797741 | 11KV POLE REPLACEMENT. Works location: Yeronga Rd. WO 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 420 | 417 | 3336 | 0.01019 | 2.4435e-05 | 2014-10-30 | B | 0.0050948 | 1.2218e-05 | 2015 | 2014-10-30 | B | 8 | 0.01019 | 2.4435e-05
1 | 2881986 | 2014-10-30 08:43 | 2014-10-30 10:24 | 101.1333 | 1 | 101.1333 | 0.00030931 | 3.0584e-06 | Restore Supply on Device TC624 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5374 | 9.20am retailer requesting update hub advised Fm is on arapuni road now Check if this affects OMS : 2883233. replaced 2x 3a HV fuse links. nothing else repaired or replaced, adjacent assets up to powerco standard. | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 101.1333 | 98.1333 | 98.1333 | 0.00029974 | 3.0544e-06 | 2014-10-30 | C | 0.00029974 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00029974 | 3.0544e-06
1 | 2075986 | 2014-10-30 08:43 | 2014-10-30 15:38 | 414.5333 | 16 | 6552.7 | 0.020041 | 4.8935e-05 | NAPA ID:02697 TP_HINUERA GXP > WAHAROA SUB > FACTORY RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | H2325 | Install line break to replace poles and X-arms. Work Location: Landsdown Road, Waharoa W/O 10144381 | F3 | FACTORY RD | WAHAROA SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 409.5437 | 406.5437 | 6504.7 | 0.019868 | 4.8871e-05 | 2014-10-30 | B | 0.0099341 | 2.4435e-05 | 2015 | 2014-10-30 | B | 16 | 0.019868 | 4.8871e-05
1 | 2370989 | 2014-10-30 09:00 | 2014-10-30 12:44 | 224 | 29 | 6496 | 0.019868 | 8.8694e-05 | NAPA ID:02607 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-016 | Replace poles between ABS SD5-016 and ABS SD5-033. Works location: Kairua Rd WO IR6817 TA/2014/23 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 224 | 221 | 6409 | 0.019576 | 8.8578e-05 | 2014-10-30 | B | 0.0097879 | 4.4289e-05 | 2015 | 2014-10-30 | B | 29 | 0.019576 | 8.8578e-05
1 | 2335745 | 2014-10-30 09:00 | 2014-10-30 11:10 | 129.9333 | 13 | 1689.1333 | 0.0051661 | 3.9759e-05 | NAPA ID:02673 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP630 | To replace 11kV and LV cross arms. Works location: McNab Rd WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 129.9333 | 126.9333 | 1650.1333 | 0.0050402 | 3.9708e-05 | 2014-10-30 | B | 0.0025201 | 1.9854e-05 | 2015 | 2014-10-30 | B | 13 | 0.0050402 | 3.9708e-05
1 | 2400497 | 2014-10-30 09:15 | 2014-10-30 16:30 | 434.9667 | 10 | 4349.6667 | 0.013303 | 3.0584e-05 | NAPA ID:03422 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Recloser 6813/2 | 11kv pole and cross arm upgrade. Works location: Mohakau Rd WO IR1872 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 434.9667 | 431.9667 | 4319.6667 | 0.013194 | 3.0544e-05 | 2014-10-30 | B | 0.006597 | 1.5272e-05 | 2015 | 2014-10-30 | B | 10 | 0.013194 | 3.0544e-05
1 | 2371537 | 2014-10-30 09:30 | 2014-10-30 13:40 | 250 | 12 | 3000 | 0.0091753 | 3.6701e-05 | NAPA ID:02960 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-035 | REPLACE HV POLE AND ARMS FOR RECON WORK. Works location: Rangiuru Rd. WO 10154633 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 2964 | 0.0090533 | 3.6653e-05 | 2014-10-30 | B | 0.0045267 | 1.8327e-05 | 2015 | 2014-10-30 | B | 12 | 0.0090533 | 3.6653e-05
1 | 2379474 | 2014-10-30 09:33 | 2014-10-30 10:07 | 34 | 82 | 2788 | 0.0085269 | 0.00025079 | NAPA ID:03374 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/177 | Top up oil in the TX (Low oil Level). Works location: Amberley Ave, Palmerston North. WO 10149602 | F4 | TREMAINE AVE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 34 | 31 | 2542 | 0.0077643 | 0.00025046 | 2014-10-30 | B | 0.0038822 | 0.00012523 | 2015 | 2014-10-30 | B | 82 | 0.0077643 | 0.00025046
1 | 2882403 | 2014-10-30 09:34 | 2014-10-30 14:52 | 317.9833 | 1 | 317.9833 | 0.00097253 | 3.0584e-06 | Restore Supply on Device 3429T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3429T | blown TX 3429 T - Wanganui Guys are on there way to repair this Transformer 3429T Replaced by Ben Englegretsen | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 317.9833 | 314.9833 | 314.9833 | 0.00096209 | 3.0544e-06 | 2014-10-30 | C | 0.00096209 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00096209 | 3.0544e-06
1 | 2371600 | 2014-10-30 10:02 | 2014-10-30 12:30 | 148 | 22 | 3256 | 0.0099582 | 6.7285e-05 | NAPA ID:03326 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W14061 | Unbind & straighten pole W14061 & remove LL clamps. Works location: Purangi Rd WO TA-2014-22 | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 148 | 145 | 3190 | 0.0097436 | 6.7197e-05 | 2014-10-30 | B | 0.0048718 | 3.3599e-05 | 2015 | 2014-10-30 | B | 22 | 0.0097436 | 6.7197e-05
1 | 2333330 | 2014-10-30 10:03 | 2014-10-30 13:05 | 182 | 3 | 546 | 0.0016699 | 9.1753e-06 | NAPA ID:03096 TP_HAWERA GXP > CAMBRIA SUB > GLOVER RD EAST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C4005 | Replace 11kV groundmount Tx and HV cable at site C4005. Works location: Scott St WO 10148889 | F3 | ARGYLE ST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 537 | 0.0016402 | 9.1633e-06 | 2014-10-30 | B | 0.00082011 | 4.582e-06 | 2015 | 2014-10-30 | B | 3 | 0.0016402 | 9.1633e-06
1 | 2883593 | 2014-10-30 10:19 | 2014-10-30 11:30 | 70.9167 | 1 | 70.9167 | 0.00021689 | 3.0584e-06 | Restore Supply on Device TC5193 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5193 | replaced 4x 3a HV fuse links 2x at transformer and 2x at Section fuses not full set of fuses.nothing else repaired or replaced, adjacent assets up to powerco standard. also signed off child job on OMS#2881314, Did not realise it was a child job and it al | F3 | SMITH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 70.9167 | 67.9167 | 67.9167 | 0.00020745 | 3.0544e-06 | 2014-10-30 | C | 0.00020745 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00020745 | 3.0544e-06
1 | 2490518 | 2014-10-30 10:21 | 2014-10-30 11:38 | 77 | 4 | 308 | 0.00094199 | 1.2234e-05 | NAPA ID:03836 TP_MARTON GXP > PUKEPAPA SUB > BULLS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 801876 | replace hardwood 11kv pole 801876 | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 77 | 74 | 296 | 0.00090411 | 1.2218e-05 | 2014-10-30 | B | 0.00045205 | 6.109e-06 | 2015 | 2014-10-30 | B | 4 | 0.00090411 | 1.2218e-05
1 | 2883614 | 2014-10-30 10:29 | 2014-10-30 11:37 | 68 | 341 | 5902 | 0.018051 | 0.0010429 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | P27943 | Faulty jumper found at Pole P27943. Needed to offload feeder to operate ABS R52 safely. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 17.3079 | 14.3079 | 4879 | 0.014903 | 0.0010416 | 2014-10-30 | C | 0.014903 | 0.0010416 | 2015 | 2014-10-30 | C | 341 | 0.014903 | 0.0010416
1 | 2884273 | 2014-10-30 10:46 | 2014-10-30 13:08 | 142.0667 | 1 | 142.0667 | 0.0004345 | 3.0584e-06 | Restore Supply on Device TC624 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tx4680 and tx 624 | 60 amp hrc due to lightning tx 624 lv oh surrounding asset all good nothing else repaired or replaced and also affecting cowshed at. 430 has high tension fuses out don will advise the amp shortly 2x 2amp at tx 4680 hv oh due to lightning. | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 142.0667 | 139.0667 | 139.0667 | 0.00042477 | 3.0544e-06 | 2014-10-30 | C | 0.00042477 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00042477 | 3.0544e-06
1 | 2885359 | 2014-10-30 11:01 | 2014-10-30 12:11 | 70.25 | 1 | 70.25 | 0.00021485 | 3.0584e-06 | Restore Supply on Device 6642 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4789T | Change Transformer 4789T. Lightning damaged. Transformer changed by Ben Englebretsen | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 70.25 | 67.25 | 67.25 | 0.00020541 | 3.0544e-06 | 2014-10-30 | C | 0.00020541 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00020541 | 3.0544e-06
1 | 2886021 | 2014-10-30 12:01 | 2014-10-30 15:36 | 214.75 | 1 | 214.75 | 0.0006568 | 3.0584e-06 | Restore Supply on Device T2214 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx 2214, fuse 7398 | tx 2214, fuse 7398. replace 1 x 3 amp ht fuse element. cause: old age, deterioration. No other assets repaired or replaced on site. FM advise vine growing over tx which he is going to defect. | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 214.75 | 211.75 | 211.75 | 0.00064677 | 3.0544e-06 | 2014-10-30 | C | 0.00064677 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00064677 | 3.0544e-06
1 | 2886377 | 2014-10-30 12:18 | 2014-10-30 15:37 | 199.2167 | 3 | 537.05 | 0.0016425 | 9.1753e-06 | Restore Supply on Device TD2-023 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | TD2-023 | 11KV FUSE 6 AMP X 2 , DUE TO WIND AND POSSIBLY TREES. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 179.0167 | 176.0167 | 528.05 | 0.0016129 | 9.1633e-06 | 2014-10-30 | C | 0.0016129 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.0016129 | 9.1633e-06
1 | 2370832 | 2014-10-30 13:00 | 2014-10-30 14:50 | 110 | 5 | 520 | 0.0015904 | 1.5292e-05 | NAPA ID:03234 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 314603 | Replace 11kv crossarm. Works location: Tiki Quarry Rd, Coromandel. WO 10161990. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 104 | 101 | 505 | 0.0015425 | 1.5272e-05 | 2014-10-30 | B | 0.00077124 | 7.636e-06 | 2015 | 2014-10-30 | B | 5 | 0.0015425 | 1.5272e-05
1 | 2888575 | 2014-10-30 13:20 | 2014-10-30 18:49 | 328.7833 | 3 | 481.1 | 0.0014714 | 9.1753e-06 | Restore Supply on Device 4754T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4574T | blown tx 4754T. requesting 2R. | F4 | DUTHIE RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 160.3667 | 157.3667 | 472.1 | 0.001442 | 9.1633e-06 | 2014-10-30 | C | 0.001442 | 9.163e-06 | 2015 | 2014-10-30 | C | 3 | 0.001442 | 9.1633e-06
1 | 2890763 | 2014-10-30 15:10 | 2014-10-30 18:36 | 205.8 | 362 | 35959.8 | 0.10998 | 0.0011071 | Restore Supply on Device WH2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 600 Tangahoe Rd | 17 24 660 Tongahoe Valley Rd, tree blocking road, rung stdc to report Line Repaired # mtrs Poko & 3 Sleeves | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 99.3365 | 96.3365 | 34873.8 | 0.10652 | 0.0011057 | 2014-10-30 | C | 0.10652 | 0.0011057 | 2015 | 2014-10-30 | C | 362 | 0.10652 | 0.0011057
1 | 2891142 | 2014-10-30 15:26 | 2014-10-30 19:07 | 221.05 | 1 | 221.05 | 0.00067606 | 3.0584e-06 | Restore Supply on Device 3910T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4725t | replace 3 x 3 amp ht fuses. full set. 3 phases. tx 4725t. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 221.05 | 218.05 | 218.05 | 0.00066602 | 3.0544e-06 | 2014-10-30 | C | 0.00066602 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00066602 | 3.0544e-06
1 | 2891162 | 2014-10-30 15:33 | 2014-10-30 18:20 | 166.8333 | 1 | 166.8333 | 0.00051025 | 3.0584e-06 | Restore Supply on Device TC5627 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | pole mo874 fp 269 | 2 x ht 6 amp fuses due to lightning no other assets repaired or replaced adjacent assets ok Emailed Jo, as appears may have a SAIDI component. | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 166.8333 | 163.8333 | 163.8333 | 0.00050042 | 3.0544e-06 | 2014-10-30 | C | 0.00050042 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00050042 | 3.0544e-06
1 | 2891179 | 2014-10-30 15:40 | 2014-10-30 20:34 | 293.3333 | 1 | 293.3333 | 0.00089714 | 3.0584e-06 | Restore Supply on Device T148 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - SALT SPRAY | 365131 | repair 3 neutral joints. cause: age, salt. used 3 hv connectors. pole 365131. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 293.3333 | 290.3333 | 290.3333 | 0.0008868 | 3.0544e-06 | 2014-10-30 | C | 0.0008868 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.0008868 | 3.0544e-06
1 | 2891200 | 2014-10-30 15:52 | 2014-10-30 20:38 | 286.2333 | 1 | 286.2333 | 0.00087542 | 3.0584e-06 | Restore Supply on Device X1546 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x1546 | replaced 1 x ht 2 amp fuse at tx x1546. cause: lightning. 1 of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 286.2333 | 283.2333 | 283.2333 | 0.00086511 | 3.0544e-06 | 2014-10-30 | C | 0.00086511 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00086511 | 3.0544e-06
1 | 2380687 | 2014-10-30 16:17 | 2014-10-30 20:34 | 257.5667 | 3 | 772.7 | 0.0023632 | 9.1753e-06 | NAPA ID:03355 TP_WANGANUI GXP > BEACH RD SUB > BEACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | RMU 4209 | Replace RMU 4209 from CB3 Beach road Sub .Customers off transformers 4440W and X3097 will be advised of shutdown by Tenix. Rescheduled from NAPA ID 2325. Works location: Beach Rd. WO 10121204 | F2 | BEACH RD | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 257.5667 | 254.5667 | 763.7 | 0.0023327 | 9.1633e-06 | 2014-10-30 | B | 0.0011663 | 4.582e-06 | 2015 | 2014-10-30 | B | 3 | 0.0023327 | 9.1633e-06
1 | 2891305 | 2014-10-30 16:52 | 2014-10-30 19:21 | 148.9667 | 165 | 3156.1167 | 0.0096527 | 0.00050464 | Restore Supply on Device T260 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 359940 | Cross arm found twisted on Pole 359940 - Isolated at ABS's S194 & S369 - Crossarm straightened feeder returned to service | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 19.128 | 16.128 | 2661.1167 | 0.0081282 | 0.00050398 | 2014-10-30 | C | 0.0081282 | 0.00050398 | 2015 | 2014-10-30 | C | 165 | 0.0081282 | 0.00050398
1 | 2891314 | 2014-10-30 17:09 | 2014-10-30 20:21 | 192.1167 | 1 | 192.1167 | 0.00058757 | 3.0584e-06 | Restore Supply on Device T1380 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1380 | replaced 3 x 3 amp fuses on tx T1380. cause: lightning. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. Emailed Jo, as appears may have a SAIDI component. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 192.1167 | 189.1167 | 189.1167 | 0.00057764 | 3.0544e-06 | 2014-10-30 | C | 0.00057764 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00057764 | 3.0544e-06
1 | 2891415 | 2014-10-30 18:14 | 2014-10-30 20:47 | 153.1333 | 1 | 153.1333 | 0.00046835 | 3.0584e-06 | Restore Supply on Device T1480 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 714586 | replace 2 amp hv fuse. cause: lightning. pole 714586. 1 of 3 phases. replaced a nut as well. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 153.1333 | 150.1333 | 150.1333 | 0.00045857 | 3.0544e-06 | 2014-10-30 | C | 0.00045857 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00045857 | 3.0544e-06
1 | 2901843 | 2014-10-30 18:50 | 2014-10-30 19:12 | 22 | 131 | 2882 | 0.0088144 | 0.00040065 | Restore Supply on Device S369 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 359940 | Cross arm found twisted on Pole 359940 - Isolated at ABS's S194 & S369 - Crossarm straightened feeder returned to service | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 22 | 19 | 2489 | 0.0076025 | 0.00040013 | 2014-10-30 | C | 0.0076025 | 0.00040013 | 2015 | 2014-10-30 | C | 131 | 0.0076025 | 0.00040013
1 | 2891736 | 2014-10-30 19:37 | 2014-10-30 21:45 | 127.8833 | 1 | 127.8833 | 0.00039112 | 3.0584e-06 | Restore Supply on Device 2435T | 6600 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2354 | replace 2 amp hv fuse at tx 2354. cause: wind clashed lines. 1 out of 3 phases. No other assets repaired or replaced on site. network assets looks good. neighbour's lv lines needs re-sagging, does not want to pay for it but that is a customer side issue, | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 127.8833 | 124.8833 | 124.8833 | 0.00038145 | 3.0544e-06 | 2014-10-30 | C | 0.00038145 | 3.054e-06 | 2015 | 2014-10-30 | C | 1 | 0.00038145 | 3.0544e-06
1 | 2891789 | 2014-10-30 22:45 | 2014-10-31 02:02 | 196.9667 | 10 | 1969.6667 | 0.0060241 | 3.0584e-05 | Restore Supply on Device 5553 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2286T | Should have been a child job of 2879421. DDO's for transformer 2286T broke when trying to reliven after transformer replacement. 1 x 30 kVA Transformer and HV DDO's used. Kain MacKay attended. These transformers were isolated in an associated OMS Job | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 196.9667 | 193.9667 | 1939.6667 | 0.0059246 | 3.0544e-05 | 2014-10-30 | C | 0.0059246 | 3.0544e-05 | 2015 | 2014-10-30 | C | 10 | 0.0059246 | 3.0544e-05
1 | 2892153 | 2014-10-31 09:03 | 2014-10-31 13:50 | 286.75 | 1303 | 128231.1667 | 0.39219 | 0.0039851 | Restore Supply on Device CB2862 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | Kaponga and Cardiff Sub | 33kV CB 2862 at Stfd GXP Tripped. E/F. Neut Time O/C. L/O. Kaponga and Cardiff both off. Kaponga Sub Backfed from Eltham on the 33kV and power restored. Cardiff backfed via the 11kV to restore power. 33kV Lines patrolled. No fault found. lots of birds aro | F1, F2, F3 | CARDIFF NORTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 98.4123 | 95.4123 | 124322.1667 | 0.37973 | 0.0039799 | 2014-10-31 | C | 0.37973 | 0.0039799 | 2015 | 2014-10-31 | C | 1303 | 0.37973 | 0.0039799
1 | 2688916 | 2014-10-31 09:30 | 2014-10-31 16:51 | 441.05 | 32 | 10163.9 | 0.031085 | 9.787e-05 | NAPA ID:04014 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 460 | Replace poles and arms in shutdown area and reconductor 11kv. Works location: Henwood Rd WO 10145448 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 317.6219 | 314.6219 | 10067.9 | 0.030752 | 9.7742e-05 | 2014-10-31 | B | 0.015376 | 4.8871e-05 | 2015 | 2014-10-31 | B | 32 | 0.030752 | 9.7742e-05
1 | 2891150 | 2014-10-31 09:37 | 2014-10-31 14:10 | 273 | 1 | 273 | 0.00083495 | 3.0584e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Fuses 4672 | Repair cable termination at Fuses 4672. Original fault OMS 2869105 | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 273 | 270 | 270 | 0.00082469 | 3.0544e-06 | 2014-10-31 | B | 0.00041235 | 1.527e-06 | 2015 | 2014-10-31 | B | 1 | 0.00082469 | 3.0544e-06
1 | 2371880 | 2014-10-31 09:46 | 2014-10-31 14:16 | 270.1333 | 141 | 38088.8 | 0.11649 | 0.00043124 | NAPA ID:03331 TP_KOPU GXP > THAMES SUB > TOTARA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S12644 | Replace pole S12644 broken during storm. Works location: Kauaeranga Valley Rd. WO 10151793. | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 270.1333 | 267.1333 | 37665.8 | 0.11505 | 0.00043067 | 2014-10-31 | B | 0.057524 | 0.00021534 | 2015 | 2014-10-31 | B | 141 | 0.11505 | 0.00043067
1 | 2902053 | 2014-10-31 15:36 | 2014-10-31 18:05 | 149.25 | 447 | 41068.1833 | 0.1256 | 0.0013671 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole P33661 | CB11 tripped on E/F IDMT. Isolations made and lines down found at pole P33661. Rehang conductor. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 91.8751 | 88.8751 | 39727.1833 | 0.12134 | 0.0013653 | 2014-10-31 | C | 0.12134 | 0.0013653 | 2015 | 2014-10-31 | C | 447 | 0.12134 | 0.0013653
1 | 2903436 | 2014-10-31 16:45 | 2014-10-31 20:15 | 210.5167 | 31 | 6440.0167 | 0.019696 | 9.4811e-05 | Restore Supply on Device M56 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | fuse M56 | replace 2 x ht 10 amp fuses at fuse M56. cause: wind. 2 out of 3 phases. oh. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 207.7425 | 204.7425 | 6347.0167 | 0.019386 | 9.4687e-05 | 2014-10-31 | C | 0.019386 | 9.4687e-05 | 2015 | 2014-10-31 | C | 31 | 0.019386 | 9.4687e-05
1 | 2903751 | 2014-10-31 17:16 | 2014-11-01 12:42 | 1166.3833 | 7 | 8164.6833 | 0.024971 | 2.1409e-05 | Restore Supply on Device T9/37 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole P06672 | ***when FM signs job off, ask if oms 2904317 - #116 in same road - is part of this outage*** replaced 2 H/T Insulators with Clamp tops | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1166.3833 | 1163.3833 | 8143.6833 | 0.024874 | 2.1381e-05 | 2014-10-31 | C | 0.024874 | 2.1381e-05 | 2015 | 2014-10-31 | C | 7 | 0.024874 | 2.1381e-05
1 | 2904598 | 2014-11-01 05:19 | 2014-11-01 06:29 | 70.1 | 995 | 56574.3667 | 0.17303 | 0.0030431 | Restore Supply on Device CB14 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | pole P17686 | CB14 Tripped on Cph O/C and E/F. Found duck under lines @ pole P17686 | F3 | RESIDENTIAL | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56.8587 | 53.8587 | 53589.3667 | 0.16368 | 0.0030392 | 2014-11-01 | C | 0.16368 | 0.0030392 | 2015 | 2014-11-01 | C | 995 | 0.16368 | 0.0030392
1 | 2400484 | 2014-11-01 08:30 | 2014-11-01 13:23 | 293 | 76 | 22268 | 0.068105 | 0.00023244 | NAPA ID:02560 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 820907 | check open line breaks at poles 820907 & 820877 (breaks made 22/10/14), open s381 to isolate t1902 & t2304 so they can be replaced. Works location: High St Carterton WO 10140873 IR6938 | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 293 | 290 | 22040 | 0.067319 | 0.00023214 | 2014-11-01 | B | 0.03366 | 0.00011607 | 2015 | 2014-11-01 | B | 76 | 0.067319 | 0.00023214
1 | 2452019 | 2014-11-01 08:33 | 2014-11-01 16:52 | 499.0667 | 11 | 5489.7333 | 0.01679 | 3.3643e-05 | NAPA ID:03809 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole 216461 | Under live line permit cut jumpers on pole 216460. Under access permit terminate new 3core 185mm 11kv cable to 9439/3 and terminate other end to pole 216461. Under test permit test new cable between 9439/3 and pole 216461 , and then under live line permit | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 499.0667 | 496.0667 | 5456.7333 | 0.016667 | 3.3599e-05 | 2014-11-01 | B | 0.0083336 | 1.6799e-05 | 2015 | 2014-11-01 | B | 11 | 0.016667 | 3.3599e-05
1 | 2869098 | 2014-11-01 09:09 | 2014-11-01 10:10 | 60.0833 | 47 | 2823.9167 | 0.0086367 | 0.00014375 | NAPA ID:04140 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | pole 742474 | Isolation/permit/standover for safety for Crane to lift in concrete panels at entrance Sentry hill winery | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60.0833 | 57.0833 | 2682.9167 | 0.0081948 | 0.00014356 | 2014-11-01 | B | 0.0040974 | 7.1779e-05 | 2015 | 2014-11-01 | B | 47 | 0.0081948 | 0.00014356
1 | 2385554 | 2014-11-01 23:00 | 2014-11-02 04:12 | 312 | 8 | 2496 | 0.0076338 | 2.4467e-05 | NAPA ID:02068 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV Pole 226000 | Replace 33kV Poles and crossarms Between poles 226000 & 220985. Works location: Te Puke Pongakawa 33kV line WO 10153754 | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 312 | 309 | 2472 | 0.0075505 | 2.4435e-05 | 2014-11-01 | B | 0.0037753 | 1.2218e-05 | 2015 | 2014-11-01 | B | 8 | 0.0075505 | 2.4435e-05
1 | 2906839 | 2014-11-02 05:10 | 2014-11-02 06:31 | 81.4 | 2 | 81.4 | 0.00024896 | 6.1168e-06 | Restore Supply on Device X4208 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND |  | replaced 2X 20A HV Fuses | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 40.7 | 37.7 | 75.4 | 0.0002303 | 6.1088e-06 | 2014-11-02 | C | 0.0002303 | 6.109e-06 | 2015 | 2014-11-02 | C | 2 | 0.0002303 | 6.1088e-06
1 | 2906920 | 2014-11-02 09:01 | 2014-11-02 14:22 | 321.3333 | 31 | 7302.5167 | 0.022334 | 9.4811e-05 | Restore Supply on Device T470 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 811749 | Received initial auto-reclose on Hau nui CB C642 then reports of no power. patrol found sectionaliser CB C633/2 had tripped. Feeder further patrolled with floating conductor found at pole 811749. rebound, relivened OK. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 235.5651 | 232.5651 | 7209.5167 | 0.022021 | 9.4687e-05 | 2014-11-02 | C | 0.022021 | 9.4687e-05 | 2015 | 2014-11-02 | C | 31 | 0.022021 | 9.4687e-05
1 | 2906946 | 2014-11-02 09:31 | 2014-11-02 10:18 | 46.7667 | 50 | 2338.3333 | 0.0071516 | 0.00015292 | Restore Supply on Device 6285 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | bayley Rd p1135 | Isolation required from Fuses6285 to cahnge a broken DDO at Transformer P1135. NOTE: W.Botha was replacing this Transformer when he noticed this fault. (OMS 2906843). Relivened Rd OK at Contractor continued on Transformer change. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 46.7667 | 43.7667 | 2188.3333 | 0.0066841 | 0.00015272 | 2014-11-02 | C | 0.0066841 | 0.00015272 | 2015 | 2014-11-02 | C | 50 | 0.0066841 | 0.00015272
1 | 2861014 | 2014-11-02 09:44 | 2014-11-02 13:07 | 202.95 | 121 | 24556.95 | 0.075106 | 0.00037007 | NAPA ID:04029 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1118 | replace rotten crossarms. Works location: Wiltsdown Rd Putaruru WO 10165119 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 202.95 | 199.95 | 24193.95 | 0.073899 | 0.00036959 | 2014-11-02 | B | 0.036949 | 0.00018479 | 2015 | 2014-11-02 | B | 121 | 0.073899 | 0.00036959
1 | 2907185 | 2014-11-02 12:44 | 2014-11-02 16:17 | 212.2833 | 175 | 9495.7333 | 0.029042 | 0.00053522 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 832154 | Initial tripping on Recloser CB 7417 on E/F, Phase A O/C. Sub checked and found CB C948 had also tripped (Reclosed OK). Patrol found 2 broken conductors beyond fuses 7848. (Relivened up to there). Conductors re-jointed OK and relivened. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 54.2613 | 51.2613 | 8970.7333 | 0.0274 | 0.00053452 | 2014-11-02 | C | 0.0274 | 0.00053452 | 2015 | 2014-11-02 | C | 175 | 0.0274 | 0.00053452
1 | 2907607 | 2014-11-02 14:00 | 2014-11-03 17:10 | 1629.3833 | 9 | 6898.75 | 0.021099 | 2.7526e-05 | Restore Supply on Device T9/390 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole p10765 | Reports of no power found conductor wound up beyond fuses I26. (Alfredton, Brooklands feeder. Isolation made but will require reconductoring to repair damage. A temp line break made at Pole p10765 andall but 2 transformers relivened. repairs will be carri | F4 | BROOKLANDS | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 766.5278 | 763.5278 | 6871.75 | 0.020989 | 2.749e-05 | 2014-11-02 | C | 0.020989 | 2.749e-05 | 2015 | 2014-11-02 | C | 9 | 0.020989 | 2.749e-05
1 | 2907632 | 2014-11-02 14:52 | 2014-11-02 17:25 | 153.2333 | 1 | 153.2333 | 0.00046865 | 3.0584e-06 | Restore Supply on Device 5133E | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5133E Pole 715448 | Customer had tripped fuses on transformer 5133E. (Earlier lightning strike). 2 HT fuses reloaded / relivened OK. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 153.2333 | 150.2333 | 150.2333 | 0.00045888 | 3.0544e-06 | 2014-11-02 | C | 0.00045888 | 3.054e-06 | 2015 | 2014-11-02 | C | 1 | 0.00045888 | 3.0544e-06
1 | 2907615 | 2014-11-02 17:16 | 2014-11-02 17:45 | 28.3667 | 2 | 56.7333 | 0.00017351 | 6.1168e-06 | Restore Supply on Device T7/473 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P28050 | Reports of part found a broken 11kV jumper beyond fuses Q48 at Pole P28050. Isolation made with jumper repaired / relivened. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 28.3667 | 25.3667 | 50.7333 | 0.00015496 | 6.1088e-06 | 2014-11-02 | C | 0.00015496 | 6.109e-06 | 2015 | 2014-11-02 | C | 2 | 0.00015496 | 6.1088e-06
1 | 2910310 | 2014-11-03 06:23 | 2014-11-03 08:27 | 124.15 | 293 | 13873.6167 | 0.042431 | 0.00089612 | Restore Supply on Device 1011 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB1011 | Tripping on Recloser 1011 on O/C B, C Phase. Feeder backfed via VS688 to CB083 and from ABS1487 to CB4491. Remainder patrolled / sectionalised but all restored OK. Cause unknown at this stage. Jeremy HIll attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 47.3502 | 44.3502 | 12994.6167 | 0.039691 | 0.00089495 | 2014-11-03 | C | 0.039691 | 0.00089495 | 2015 | 2014-11-03 | C | 293 | 0.039691 | 0.00089495
1 | 2911268 | 2014-11-03 07:18 | 2014-11-03 10:03 | 165.2 | 4 | 660.8 | 0.002021 | 1.2234e-05 | Restore Supply on Device 3948T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764857 | replaced x2 HV 2amp element fuses at pole 764857 at TX 4872 cause unknown. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 165.2 | 162.2 | 648.8 | 0.0019817 | 1.2218e-05 | 2014-11-03 | C | 0.0019817 | 1.2218e-05 | 2015 | 2014-11-03 | C | 4 | 0.0019817 | 1.2218e-05
1 | 2379457 | 2014-11-03 09:11 | 2014-11-03 12:11 | 179.7333 | 1 | 179.7333 | 0.0005497 | 3.0584e-06 | NAPA ID:02779 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1627 | To replace 11kV and LV cross arms beyond FP1627. Works location: Rangitanuku Rd WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 179.7333 | 176.7333 | 176.7333 | 0.00053982 | 3.0544e-06 | 2014-11-03 | B | 0.00026991 | 1.527e-06 | 2015 | 2014-11-03 | B | 1 | 0.00053982 | 3.0544e-06
1 | 2912343 | 2014-11-03 11:52 | 2014-11-03 13:53 | 121.5667 | 2 | 144.4167 | 0.00044169 | 6.1168e-06 | Restore Supply on Device T7/37 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | T7/202 | Outage required on transformer T7/202 to repair a broken jumper at the DDO base. Relivened OK. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72.2083 | 69.2083 | 138.4167 | 0.00042278 | 6.1088e-06 | 2014-11-03 | C | 0.00042278 | 6.109e-06 | 2015 | 2014-11-03 | C | 2 | 0.00042278 | 6.1088e-06
1 | 2912470 | 2014-11-03 12:16 | 2014-11-03 18:31 | 374.8167 | 1 | 374.8167 | 0.0011463 | 3.0584e-06 | Restore Supply on Device 3436T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3436T | replace 2 x 2 amp ht fuses. cause: weather. tx 3436T. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 374.8167 | 371.8167 | 371.8167 | 0.0011357 | 3.0544e-06 | 2014-11-03 | C | 0.0011357 | 3.054e-06 | 2015 | 2014-11-03 | C | 1 | 0.0011357 | 3.0544e-06
1 | 2913375 | 2014-11-03 18:40 | 2014-11-03 21:44 | 183.85 | 10 | 1006.45 | 0.0030781 | 3.0584e-05 | Restore Supply on Device W2255 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 725833 | 6:49pm advised Tarn at HUB that probable cause is tree on lines outside 1277 Tangahoe Valley Rd. Hv line down in forestry block. isolated line and will now deal with control. requesting 2R. Used 25 M 16mm Copper | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 100.645 | 97.645 | 976.45 | 0.0029825 | 3.0544e-05 | 2014-11-03 | C | 0.0029825 | 3.0544e-05 | 2015 | 2014-11-03 | C | 10 | 0.0029825 | 3.0544e-05
1 | 2913524 | 2014-11-03 20:20 | 2014-11-03 21:09 | 49.4 | 1 | 49.4 | 0.00015109 | 3.0584e-06 | Restore Supply on Device X2887 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 789574 | replace 2 amp ht fuse. 1 out of 3 phases. cause: old age, deterioration. pole 789574. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 49.4 | 46.4 | 46.4 | 0.00014173 | 3.0544e-06 | 2014-11-03 | C | 0.00014172 | 3.054e-06 | 2015 | 2014-11-03 | C | 1 | 0.00014173 | 3.0544e-06
1 | 2542001 | 2014-11-04 08:42 | 2014-11-04 17:26 | 524 | 1 | 124 | 0.00037924 | 3.0584e-06 | NAPA ID:03774 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV ABS 3276 | 845-945:Access Permit: Remove aerial earth between Mckee Structure and pole 760695. Break jumpers on pole 760695 945-1615:Install new 33kV Pole and ABS 3276,remove overhead earth and change crossarms 1615-1715: Reconnect jumpers Pole 760695 Works loca | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 124 | 121 | 121 | 0.00036959 | 3.0544e-06 | 2014-11-04 | B | 0.00018479 | 1.527e-06 | 2015 | 2014-11-04 | B | 1 | 0.00036959 | 3.0544e-06
1 | 2385574 | 2014-11-04 08:45 | 2014-11-04 14:06 | 321.1 | 4 | 1255.6667 | 0.0038404 | 1.2234e-05 | NAPA ID:02659 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 797712 | 11KV POLE REPLACEMENT. Works location: Humes Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 313.9167 | 310.9167 | 1243.6667 | 0.0037987 | 1.2218e-05 | 2014-11-04 | B | 0.0018993 | 6.109e-06 | 2015 | 2014-11-04 | B | 4 | 0.0037987 | 1.2218e-05
1 | 2392856 | 2014-11-04 09:01 | 2014-11-04 13:05 | 244.3333 | 12 | 2932 | 0.0089673 | 3.6701e-05 | NAPA ID:02961 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF6-035 | REPLACE HV POLE AND ARMS FOR RECON WORK. Works location: Rangiuru Rd WO 10154633 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 244.3333 | 241.3333 | 2896 | 0.0088456 | 3.6653e-05 | 2014-11-04 | B | 0.0044228 | 1.8327e-05 | 2015 | 2014-11-04 | B | 12 | 0.0088456 | 3.6653e-05
1 | 2380071 | 2014-11-04 09:15 | 2014-11-04 14:51 | 335.2333 | 15 | 5028.5 | 0.015379 | 4.5876e-05 | NAPA ID:03206 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6604 | 11kv poles and overhead lines upgrade of Pheney Road. Works location: Pheney Rd New Plymouth WO IR7213 | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 335.2333 | 332.2333 | 4983.5 | 0.015222 | 4.5816e-05 | 2014-11-04 | B | 0.0076109 | 2.2908e-05 | 2015 | 2014-11-04 | B | 15 | 0.015222 | 4.5816e-05
1 | 2388212 | 2014-11-04 09:30 | 2014-11-04 15:26 | 355.6333 | 45 | 16003.5 | 0.048945 | 0.00013763 | NAPA ID:02736 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS pole 460 | replace abs pole 460 and other poles and arms in shutdown area. Works location: Egmont Rd WO 10145448 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 355.6333 | 352.6333 | 15868.5 | 0.048469 | 0.00013745 | 2014-11-04 | B | 0.024235 | 6.8725e-05 | 2015 | 2014-11-04 | B | 45 | 0.048469 | 0.00013745
1 | 2452863 | 2014-11-04 09:32 | 2014-11-04 14:34 | 301.8667 | 143 | 43166.9333 | 0.13202 | 0.00043735 | NAPA ID:03408 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS C21 | Replace x arms and TX arms. Works location: Cole Rd WO 10154056 | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 301.8667 | 298.8667 | 42737.9333 | 0.13054 | 0.00043678 | 2014-11-04 | B | 0.06527 | 0.00021839 | 2015 | 2014-11-04 | B | 143 | 0.13054 | 0.00043678
1 | 2357018 | 2014-11-04 10:16 | 2014-11-04 14:43 | 267.0833 | 14 | 3739.1667 | 0.011436 | 4.2818e-05 | NAPA ID:03143 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 722680 | Wire run Manawapou rd. Works location: Manawapou Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 267.0833 | 264.0833 | 3697.1667 | 0.011293 | 4.2762e-05 | 2014-11-04 | B | 0.0056464 | 2.1381e-05 | 2015 | 2014-11-04 | B | 14 | 0.011293 | 4.2762e-05
1 | 2357005 | 2014-11-04 11:00 | 2014-11-04 14:02 | 181.75 | 68 | 12359 | 0.037799 | 0.00020797 | NAPA ID:03441 TP_HUIRANGI GXP > WAITARA WEST SUB > BROWNE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer 4307T | Replace 4307T with micro type tx. Works location: Cracroft St WO 10154760 | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 181.75 | 178.75 | 12155 | 0.037127 | 0.0002077 | 2014-11-04 | B | 0.018563 | 0.00010385 | 2015 | 2014-11-04 | B | 68 | 0.037127 | 0.0002077
1 | 2914447 | 2014-11-04 11:54 | 2014-11-04 15:19 | 204.6667 | 1 | 204.6667 | 0.00062596 | 3.0584e-06 | Restore Supply on Device T3762 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 842289 | replace 11kv/oh fuse 15 amp cause: high wind. pole 842289. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 204.6667 | 201.6667 | 201.6667 | 0.00061598 | 3.0544e-06 | 2014-11-04 | C | 0.00061598 | 3.054e-06 | 2015 | 2014-11-04 | C | 1 | 0.00061598 | 3.0544e-06
1 | 2915051 | 2014-11-04 13:35 | 2014-11-04 14:58 | 82.3333 | 27 | 975.4 | 0.0029832 | 8.2577e-05 | Restore Supply on Device 5001E | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | Fuses CA799 | HV Fuse CA799 1 Phase blown. Incorrect fuse size installed due to increased load. approximately 450 kVA of transformers with 15Amp line fuses. Fuses are being upgraded to 30Amp. | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 36.1259 | 33.1259 | 894.4 | 0.0027319 | 8.2469e-05 | 2014-11-04 | C | 0.0027319 | 8.2469e-05 | 2015 | 2014-11-04 | C | 27 | 0.0027319 | 8.2469e-05
1 | 2915348 | 2014-11-05 02:06 | 2014-11-05 02:21 | 15 | 94 | 1410 | 0.0043124 | 0.00028749 | Restore Supply on Device RC25 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RC25 ( WLN 4 ) | Recloser RC25 tripped E/F, L/O. After 15 min RC25 was closed & held, not patrolled, unknown cause | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 1128 | 0.0034454 | 0.00028712 | 2014-11-05 | C | 0.0034454 | 0.00028712 | 2015 | 2014-11-05 | C | 94 | 0.0034454 | 0.00028712
1 | 2916932 | 2014-11-05 05:11 | 2014-11-05 07:47 | 155.55 | 416 | 59101.15 | 0.18076 | 0.0012723 | Restore Supply on Device C937 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Transformer T2647 | Tripping on Tinui CB C937 on Phase A-C O/C, E/F. (NOTE: This feeder A/R earlier but no reports of faults 0 Refer OMS 2916932). Branch found on lines while sectionlising near Transformer T2647 - Cleared using hot sticks | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 142.0701 | 139.0701 | 57853.15 | 0.17671 | 0.0012706 | 2014-11-05 | C | 0.17671 | 0.0012706 | 2015 | 2014-11-05 | C | 416 | 0.17671 | 0.0012706
1 | 2491065 | 2014-11-05 08:40 | 2014-11-05 15:17 | 397.35 | 162 | 64370.7 | 0.19687 | 0.00049546 | NAPA ID:03292 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC441 | Replace HV arms and straighten poles. Works location: SH25 and Pipiroa Rd WO TA-2014-36 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 397.35 | 394.35 | 63884.7 | 0.19513 | 0.00049482 | 2014-11-05 | B | 0.097565 | 0.00024741 | 2015 | 2014-11-05 | B | 162 | 0.19513 | 0.00049482
1 | 2400485 | 2014-11-05 08:45 | 2014-11-05 15:27 | 401.9667 | 105 | 41853.7 | 0.12801 | 0.00032113 | NAPA ID:02670 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 792821 | Replace 11kv poles and X arms between 792821 and ABS 1066. Works location: Ruatangata Rd Whanganehu WO 10141993 | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 398.6067 | 395.6067 | 41538.7 | 0.12688 | 0.00032071 | 2014-11-05 | B | 0.063438 | 0.00016036 | 2015 | 2014-11-05 | B | 105 | 0.12688 | 0.00032071
1 | 2918600 | 2014-11-05 08:48 | 2014-11-05 14:40 | 351.6333 | 908 | 6956.5333 | 0.021276 | 0.002777 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 20419 | CB 6 Tripped E/F O/L - Transformer T1/402 found to be faulty during sectionlising - Isolated at transformer fuses - Transformer replaced and when closing on of the HV fuse carriers broke - Isolated at Fuses L43 & DDo's all replaced - used 1 x 30 kVA Trans | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 7.6614 | 4.6614 | 4232.5333 | 0.012928 | 0.0027734 | 2014-11-05 | C | 0.012928 | 0.0027734 | 2015 | 2014-11-05 | C | 908 | 0.012928 | 0.0027734
1 | 2400506 | 2014-11-05 09:31 | 2014-11-05 14:48 | 317.65 | 15 | 4764.75 | 0.014573 | 4.5876e-05 | NAPA ID:03397 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 572 | Replace ABS 535 under DNO # 140721. Works location: Whakahoro Rd WO 10151972 | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 317.65 | 314.65 | 4719.75 | 0.014416 | 4.5816e-05 | 2014-11-05 | B | 0.0072081 | 2.2908e-05 | 2015 | 2014-11-05 | B | 15 | 0.014416 | 4.5816e-05
1 | 2403265 | 2014-11-05 09:34 | 2014-11-05 16:38 | 424.4667 | 1 | 424.4667 | 0.0012982 | 3.0584e-06 | NAPA ID:03410 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P11578 | Replace crossarms from pole P11578 through to pole P07812. Works location: Mangomako Rd WO 10160678 | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 424.4667 | 421.4667 | 421.4667 | 0.0012873 | 3.0544e-06 | 2014-11-05 | B | 0.00064367 | 1.527e-06 | 2015 | 2014-11-05 | B | 1 | 0.0012873 | 3.0544e-06
1 | 2920083 | 2014-11-05 10:57 | 2014-11-05 13:27 | 149.1667 | 1 | 149.1667 | 0.00045621 | 3.0584e-06 | Restore Supply on Device TP2378 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | tp2378 9657-2 | Tripping on fuse switch 9657-2 a new person in the business turned everything on at once which is not the process this caused the tripping. He has now been trained on the process of starting up the plant fm just needed to reset transformer tp 2378 switch | F3 | FLYOVER | OMANU SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 149.1667 | 146.1667 | 146.1667 | 0.00044645 | 3.0544e-06 | 2014-11-05 | C | 0.00044646 | 3.054e-06 | 2015 | 2014-11-05 | C | 1 | 0.00044645 | 3.0544e-06
1 | 2951372 | 2014-11-05 14:43 | 2014-11-05 16:58 | 134.3667 | 1 | 134.3667 | 0.00041095 | 3.0584e-06 | Restore Supply on Device T7/50 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p44746 | PUMP P44749 PART POWER. replace 3 amp ht fuse and holder. cause: unknown. 1 out of 3 phases. pole p44746. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 134.3667 | 131.3667 | 131.3667 | 0.00040125 | 3.0544e-06 | 2014-11-05 | C | 0.00040125 | 3.054e-06 | 2015 | 2014-11-05 | C | 1 | 0.00040125 | 3.0544e-06
1 | 2951787 | 2014-11-05 16:33 | 2014-11-05 21:38 | 304.8 | 1 | 304.8 | 0.00093221 | 3.0584e-06 | Restore Supply on Device 1174 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TX 1662 | 5/11 4.35PM ADVISED SVS HUB AND CONTROL 5:25pm faulty TX - Blown 2R request to replace TX Chris is waiting for Brett to arrive to check if we are able to install this tx tonight, needs rigging system using pullys to put tx up, wont be able to get truc | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 304.8 | 301.8 | 301.8 | 0.00092183 | 3.0544e-06 | 2014-11-05 | C | 0.00092183 | 3.054e-06 | 2015 | 2014-11-05 | C | 1 | 0.00092183 | 3.0544e-06
1 | 2951798 | 2014-11-05 16:36 | 2014-11-05 18:29 | 112.6 | 3 | 228.8667 | 0.00069997 | 9.1753e-06 | Restore Supply on Device 870 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 870 | replaced - 3amp Fuse x2 out of 3 HV fuses -due to lightning at TX 870. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standards. Email sent to Jo, as appears could have SAIDI component. \ | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 76.2889 | 73.2889 | 219.8667 | 0.00067157 | 9.1633e-06 | 2014-11-05 | C | 0.00067157 | 9.163e-06 | 2015 | 2014-11-05 | C | 3 | 0.00067157 | 9.1633e-06
1 | 2951833 | 2014-11-05 17:16 | 2014-11-05 19:24 | 128.4333 | 106 | 9558.9167 | 0.029235 | 0.00032419 | Restore Supply on Device 4848 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB 4848 Bird Rd | FM requesting help with switching and another set of eyes. Feeder patrolled and sectionalised, all restored OK. Lightning in area. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 90.1785 | 87.1785 | 9240.9167 | 0.028226 | 0.00032377 | 2014-11-05 | C | 0.028226 | 0.00032377 | 2015 | 2014-11-05 | C | 106 | 0.028226 | 0.00032377
1 | 2952382 | 2014-11-05 18:11 | 2014-11-05 21:41 | 209.1667 | 4 | 615.5667 | 0.0018827 | 1.2234e-05 | Restore Supply on Device TC1037 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc1037 | replace 3 amp fuse link. cause: unknown. 1 out of 3 phases. tx tc1037. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | PAPANUI ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 153.8917 | 150.8917 | 603.5667 | 0.0018435 | 1.2218e-05 | 2014-11-05 | C | 0.0018435 | 1.2218e-05 | 2015 | 2014-11-05 | C | 4 | 0.0018435 | 1.2218e-05
1 | 2952393 | 2014-11-05 18:15 | 2014-11-06 00:08 | 352.95 | 2 | 687.6833 | 0.0021032 | 6.1168e-06 | Restore Supply on Device TP1707 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TP 1707 | *** please check if # 1301 Jack Henry Road is part of this outage - oms 2953540 - off tx TP1708 *** 2 X 3A HV Transformer DDO Fuses. ! DDO 15A Line Fuse | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 343.8417 | 340.8417 | 681.6833 | 0.0020821 | 6.1088e-06 | 2014-11-05 | C | 0.0020822 | 6.109e-06 | 2015 | 2014-11-05 | C | 2 | 0.0020821 | 6.1088e-06
1 | 2952532 | 2014-11-05 19:01 | 2014-11-06 22:01 | 1620 | 335 | 13700 | 0.0419 | 0.0010246 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Pole P29642 | Tripping on Recloser CB 10050 on E/F. Area patrolled / sectionalised with lines found down feeding transformer T2/59. Suspect wind had caused a conductor to come unbound and burnt through pole (P29642) and then brought down 2 conductors. temp line break m | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 40.8955 | 37.8955 | 12695 | 0.038776 | 0.0010232 | 2014-11-05 | C | 0.038776 | 0.0010232 | 2015 | 2014-11-05 | C | 335 | 0.038776 | 0.0010232
1 | 2952868 | 2014-11-05 19:02 | 2014-11-06 11:41 | 999.2833 | 335 | 19602.7833 | 0.059954 | 0.0010246 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P29642 | part of outage 2952532 | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 58.5158 | 55.5158 | 18597.7833 | 0.056806 | 0.0010232 | 2014-11-05 | C | 0.056806 | 0.0010232 | 2015 | 2014-11-05 | C | 335 | 0.056806 | 0.0010232
1 | 2953540 | 2014-11-05 21:46 | 2014-11-06 11:33 | 827.4833 | 1 | 827.4833 | 0.0025308 | 3.0584e-06 | Restore Supply on Device TP1708 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Transformer TP1708 | *** possibly related to oms 2952393 - please check. else, send crew request to Tenix Hub *** Transformer found to be damaged by lightning will need to be replaced. Single phase / 15kVa | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 827.4833 | 824.4833 | 824.4833 | 0.0025183 | 3.0544e-06 | 2014-11-05 | C | 0.0025183 | 3.054e-06 | 2015 | 2014-11-05 | C | 1 | 0.0025183 | 3.0544e-06
1 | 2963689 | 2014-11-06 05:03 | 2014-11-06 06:32 | 89 | 53 | 4297 | 0.013142 | 0.0001621 | Restore Supply on Device 7074 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C844 | CB C844 tripped, no flags. Line patrolled, no fault found. Relivened OK Outage reflected under OMS Job ID 2953575. | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 81.0755 | 78.0755 | 4138 | 0.012639 | 0.00016188 | 2014-11-06 | C | 0.012639 | 0.00016188 | 2015 | 2014-11-06 | C | 53 | 0.012639 | 0.00016188
1 | 2963714 | 2014-11-06 07:13 | 2014-11-06 14:55 | 462.4333 | 24 | 11098.4 | 0.033944 | 7.3402e-05 | Restore Supply on Device TC4449 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | TC4449 | could not do a locate on this job as OMS crashed tested at TX x2 blown at TX poss blown at TX - will need to get mega test done on TX TC4449 and may need to replace TX Need to get Techs to do testing. 2x hv fuses blown, isolated with control, coli | F4 | PAPANUI ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 462.4333 | 459.4333 | 11026.4 | 0.033679 | 7.3306e-05 | 2014-11-06 | C | 0.033679 | 7.3306e-05 | 2015 | 2014-11-06 | C | 24 | 0.033679 | 7.3306e-05
1 | 2491081 | 2014-11-06 08:45 | 2014-11-06 14:53 | 367.9333 | 84 | 28911.9 | 0.088425 | 0.00025691 | NAPA ID:03215 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 383420 | REPLACE HV POLES AND HV ARMS ALONG ROAD AS PER SCOPE OF PACK. Works location: Beach Rd WO 10145667 IR7221 | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 344.1893 | 341.1893 | 28659.9 | 0.087539 | 0.00025657 | 2014-11-06 | B | 0.04377 | 0.00012829 | 2015 | 2014-11-06 | B | 84 | 0.087539 | 0.00025657
1 | 2402379 | 2014-11-06 08:46 | 2014-11-06 15:18 | 392 | 10 | 3920 | 0.011989 | 3.0584e-05 | NAPA ID:03545 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P07060 | Replace crossarms from pole P07060 to pole P49955 as per plans. Works location: Waipuru Rd WO 10160678 | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 392 | 389 | 3890 | 0.011882 | 3.0544e-05 | 2014-11-06 | B | 0.0059409 | 1.5272e-05 | 2015 | 2014-11-06 | B | 10 | 0.011882 | 3.0544e-05
1 | 2973911 | 2014-11-06 08:58 | 2014-11-06 10:40 | 102 | 303 | 30906 | 0.094524 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Pole 300356 | CB Xt40 tripped, no flags. Sectionalised lines and found fault between Parkville & Alfredton Sub's. Helicopter required to patrol lines. Line patrol found two magpies in the lines at Pole P300356. Birds removed with hot sticks. Relivened and restored netw | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 102 | 99 | 29997 | 0.091624 | 0.00092549 | 2014-11-06 | C | 0.091624 | 0.00092549 | 2015 | 2014-11-06 | C | 303 | 0.091624 | 0.00092549
1 | 2372002 | 2014-11-06 09:00 | 2014-11-06 14:56 | 355.65 | 15 | 5334.75 | 0.016316 | 4.5876e-05 | NAPA ID:03207 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6604 | 11kv poles and overhead lines upgrade of Pheney Road. Works location: Pheney Rd New Plymouth WO IR7213 | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 355.65 | 352.65 | 5289.75 | 0.016157 | 4.5816e-05 | 2014-11-06 | B | 0.0080786 | 2.2908e-05 | 2015 | 2014-11-06 | B | 15 | 0.016157 | 4.5816e-05
1 | 2379552 | 2014-11-06 09:02 | 2014-11-06 14:01 | 299 | 26 | 7774 | 0.023776 | 7.9519e-05 | NAPA ID:03213 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 378 | to remove two pole structure and old 100 kva trany and replace with new single pole with a new 100kva trany. Works location: Smart Rd WO 10149207 | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 299 | 296 | 7696 | 0.023507 | 7.9415e-05 | 2014-11-06 | B | 0.011753 | 3.9708e-05 | 2015 | 2014-11-06 | B | 26 | 0.023507 | 7.9415e-05
1 | 2384908 | 2014-11-06 09:16 | 2014-11-06 15:31 | 375.3 | 43 | 16137.9 | 0.049357 | 0.00013151 | NAPA ID:03443 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV ABS 154 | 33/6.6kV Pole & Crossarm replacement. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 375.3 | 372.3 | 16008.9 | 0.048898 | 0.00013134 | 2014-11-06 | B | 0.024449 | 6.567e-05 | 2015 | 2014-11-06 | B | 43 | 0.048898 | 0.00013134
1 | 2402986 | 2014-11-06 09:38 | 2014-11-06 13:51 | 253.3833 | 54 | 13682.7 | 0.041847 | 0.00016515 | NAPA ID:03543 TP_HUIRANGI GXP > WAITARA EAST SUB > PRINCESS ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer 3507T | Replace 3507T tx like-for-like. Works location: Mace Tce. WO 10154760 | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 253.3833 | 250.3833 | 13520.7 | 0.041298 | 0.00016494 | 2014-11-06 | B | 0.020649 | 8.2469e-05 | 2015 | 2014-11-06 | B | 54 | 0.041298 | 0.00016494
1 | 2974455 | 2014-11-06 09:48 | 2014-11-06 21:43 | 714.5728 | 46 | 32074.7 | 0.098098 | 0.00014069 | Restore Supply on Device 2811 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 843643 | Broken pole suspected car V pole - Isolated at Fuses 883 - Pole 843643 replaced, circuit returned to service - used 1xpole 1x footing block 1x crossarm complete | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 697.2761 | 694.2761 | 31936.7 | 0.097548 | 0.0001405 | 2014-11-06 | C | 0.097548 | 0.0001405 | 2015 | 2014-11-06 | C | 46 | 0.097548 | 0.0001405
1 | 2986702 | 2014-11-06 14:38 | 2014-11-06 17:38 | 180.3333 | 137 | 21730.4833 | 0.066461 | 0.000419 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 855996 | RS 9402 Trip, E/F. Patrolled & found blown insulator. Replaced insulator, pin, & binder | F3/F4 | ASHWORTH ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 158.6167 | 155.6167 | 21319.4833 | 0.065119 | 0.00041846 | 2014-11-06 | C | 0.065119 | 0.00041846 | 2015 | 2014-11-06 | C | 137 | 0.065119 | 0.00041846
1 | 2986686 | 2014-11-06 15:00 | 2014-11-06 18:15 | 194.6167 | 1 | 194.6167 | 0.00059522 | 3.0584e-06 | Restore Supply on Device TD5-020 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | td5-020 | replace 2amp ddo fuse. cause: lightning. 1 out of 2 phases. tx td5-020. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 194.6167 | 191.6167 | 191.6167 | 0.00058528 | 3.0544e-06 | 2014-11-06 | C | 0.00058528 | 3.054e-06 | 2015 | 2014-11-06 | C | 1 | 0.00058528 | 3.0544e-06
1 | 2987167 | 2014-11-06 15:29 | 2014-11-06 15:56 | 27.8167 | 149 | 4144.6833 | 0.012676 | 0.0004557 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | RS 9707 | RS 9707 Trip, O/C. Hot Line Tag was enabled on Recloser due to Tree Cutters working but they were not working near lines at the time. Feeder relivened and patrolled and faultman found blown HV fuse at Pole K12429. Farmer saw lightning strike lines. | F1 | TATUANUI | FARMER ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 27.8167 | 24.8167 | 3697.6833 | 0.011294 | 0.00045511 | 2014-11-06 | C | 0.011294 | 0.00045511 | 2015 | 2014-11-06 | C | 149 | 0.011294 | 0.00045511
1 | 2988304 | 2014-11-06 17:04 | 2014-11-06 19:59 | 174.8333 | 1 | 174.8333 | 0.00053471 | 3.0584e-06 | Restore Supply on Device TD5-017 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | td 5-023 | Lightening struck transformer located close to 165 Rocky Cutting Road Advised Tarns svs hub of this job. replace 2 amp ddo fuse at tx td 5-023. cause: lightning. 1 of 2 phases. No other assets repaired or replaced on site. Adjacent assets are checked a | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 174.8333 | 171.8333 | 171.8333 | 0.00052485 | 3.0544e-06 | 2014-11-06 | C | 0.00052485 | 3.054e-06 | 2015 | 2014-11-06 | C | 1 | 0.00052485 | 3.0544e-06
1 | 2988321 | 2014-11-06 17:39 | 2014-11-06 20:25 | 165.6667 | 1 | 165.6667 | 0.00050668 | 3.0584e-06 | Restore Supply on Device X1000 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1000 | replace 3 amp ht fuse at tx x1000. cause: unknown. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | PUTORINO | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 165.6667 | 162.6667 | 162.6667 | 0.00049685 | 3.0544e-06 | 2014-11-06 | C | 0.00049685 | 3.054e-06 | 2015 | 2014-11-06 | C | 1 | 0.00049685 | 3.0544e-06
1 | 2988788 | 2014-11-07 03:05 | 2014-11-07 05:39 | 153.5 | 460 | 26691.5667 | 0.081634 | 0.0014069 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747233 | CB 5 Tripped E/F L/O - Lines down found at Pole 747233 during sectionlising - Isolated at Fuses 8196 - line repaired & feeder returned to serviceused 5m conductor , 3 x sleeves | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 58.0251 | 55.0251 | 25311.5667 | 0.077312 | 0.001405 | 2014-11-07 | C | 0.077312 | 0.001405 | 2015 | 2014-11-07 | C | 460 | 0.077312 | 0.001405
1 | 2989732 | 2014-11-07 05:39 | 2014-11-07 07:29 | 109.5667 | 446 | 22156.9 | 0.067765 | 0.0013641 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 11 | Kairanga CB11 tripped. A,B,C Oh O/C. Feeder sectionalised, patrolled and no apparent fault found. Relevened OK. Les Robinson attended. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 49.6791 | 46.6791 | 20818.9 | 0.06359 | 0.0013623 | 2014-11-07 | C | 0.06359 | 0.0013623 | 2015 | 2014-11-07 | C | 446 | 0.06359 | 0.0013623
1 | 2990187 | 2014-11-07 06:05 | 2014-11-07 11:18 | 313.75 | 107 | 13993.9 | 0.042799 | 0.00032725 | Restore Supply on Device 4848 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | RS 4848 | RS4848, A/R, L/O, E/F. Patrolled with No Fault Found | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 130.7841 | 127.7841 | 13672.9 | 0.041763 | 0.00032682 | 2014-11-07 | C | 0.041763 | 0.00032682 | 2015 | 2014-11-07 | C | 107 | 0.041763 | 0.00032682
1 | 2992401 | 2014-11-07 07:36 | 2014-11-07 07:49 | 12.5333 | 29 | 363.4667 | 0.0011116 | 8.8694e-05 | Restore Supply on Device 4848 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | recloser 4848/2 | A/R of recloser 4848/2 E/F line not patrolled | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 12.5333 | 9.5333 | 276.4667 | 0.00084445 | 8.8578e-05 | 2014-11-07 | C | 0.00084445 | 8.8578e-05 | 2015 | 2014-11-07 | C | 29 | 0.00084445 | 8.8578e-05
1 | 2403212 | 2014-11-07 08:15 | 2014-11-07 14:30 | 375 | 132 | 23796 | 0.072778 | 0.00040371 | NAPA ID:03594 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T738 | Isolate T738 so a line break can be made at pole 831613 so T738 and pole can be replaced. Works location: Caverthen St Masterton WO 10140873 IR6938 | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 180.2727 | 177.2727 | 23400 | 0.071474 | 0.00040318 | 2014-11-07 | B | 0.035737 | 0.00020159 | 2015 | 2014-11-07 | B | 132 | 0.071474 | 0.00040318
1 | 2399040 | 2014-11-07 08:39 | 2014-11-07 12:37 | 238 | 1 | 238 | 0.0007279 | 3.0584e-06 | NAPA ID:02666 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 797762 | 11kV Pole Replacement. Works location: Lake Ferry Rd. WO 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 238 | 235 | 235 | 0.00071779 | 3.0544e-06 | 2014-11-07 | B | 0.0003589 | 1.527e-06 | 2015 | 2014-11-07 | B | 1 | 0.00071779 | 3.0544e-06
1 | 2402933 | 2014-11-07 09:05 | 2014-11-07 14:58 | 353 | 39 | 13767 | 0.042105 | 0.00011928 | NAPA ID:03144 TP_HINUERA GXP > WAHAROA SUB > FACTORY RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole H12481 | TO REPLACE POLES AND HARDWARE POLES 325801, H12481, 324801. | F3 | FACTORY RD | WAHAROA SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 353 | 350 | 13650 | 0.041693 | 0.00011912 | 2014-11-07 | B | 0.020846 | 5.9561e-05 | 2015 | 2014-11-07 | B | 39 | 0.041693 | 0.00011912
1 | 2993678 | 2014-11-07 09:15 | 2014-11-07 14:57 | 341.9333 | 43 | 14703.1333 | 0.044968 | 0.00013151 | Restore Supply on Device 5423 | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5423 | Parent 2384949 to replace 33kV and 6.6kV Poles and Cross Arms. | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 341.9333 | 338.9333 | 14574.1333 | 0.044516 | 0.00013134 | 2014-11-07 | C | 0.044516 | 0.00013134 | 2015 | 2014-11-07 | C | 43 | 0.044516 | 0.00013134
1 | 2541973 | 2014-11-07 09:15 | 2014-11-07 15:58 | 402.6667 | 56 | 20857.6333 | 0.063791 | 0.00017127 | NAPA ID:03730 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Recloser 6813 | 11kv pole and cross arm upgrade. Works location: Mohkau Rd WO IR1872 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 372.4577 | 369.4577 | 20689.6333 | 0.063195 | 0.00017105 | 2014-11-07 | B | 0.031597 | 8.5524e-05 | 2015 | 2014-11-07 | B | 56 | 0.063195 | 0.00017105
1 | 2994268 | 2014-11-07 12:10 | 2014-11-07 13:05 | 55 | 14 | 770 | 0.002355 | 4.2818e-05 | Restore Supply on Device X3233 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | X3233 | Transformer had been replaced under OMS 2688937 with a Powerco temporary transformer. An outgae is required to install new Transformer X3233 in order to return temporary transformer to spares. | F4 | MISSION RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 728 | 0.0022236 | 4.2762e-05 | 2014-11-07 | C | 0.0022236 | 4.2762e-05 | 2015 | 2014-11-07 | C | 14 | 0.0022236 | 4.2762e-05
1 | 2996671 | 2014-11-07 15:40 | 2014-11-11 03:37 | 5037.1833 | 4404 | 270811 | 0.82825 | 0.013469 | Restore Supply on Device 38 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 1 | Fire asking for ETA 09 486 7948. F1722376 Contractor cutting trees brought down lines Cameron Rd. This caused TGA sub to operate a BZ protection on T2. Once transpower had inspected site we relivened the CB's except CB 15 which tripped when closed when fa | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 61.4921 | 58.4921 | 257599 | 0.78682 | 0.013452 | 2014-11-07 | C | 0.78682 | 0.013452 | 2015 | 2014-11-07 | C | 4404 | 0.78682 | 0.013452
1 | 2999746 | 2014-11-07 18:30 | 2014-11-07 20:07 | 97.8333 | 1 | 97.8333 | 0.00029922 | 3.0584e-06 | Restore Supply on Device T1757 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t1757 | replace 2 amp ht fuse. cause: unknown. tx t1757. 1 of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 97.8333 | 94.8333 | 94.8333 | 0.00028966 | 3.0544e-06 | 2014-11-07 | C | 0.00028966 | 3.054e-06 | 2015 | 2014-11-07 | C | 1 | 0.00028966 | 3.0544e-06
1 | 3000229 | 2014-11-08 02:12 | 2014-11-08 04:29 | 136.65 | 1336 | 54054.2 | 0.16532 | 0.0040861 | Restore Supply on Device 8800/9 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 702967 | CB 9 Tripped A,B,C Ph O/C L/O - Fire services reported lines down at Rimu St - Isolated at ABS 4806 - Duck found near lines, lines Repair - Used 17 mtrs Conductor & 17 x Sleeves. Phil Webby and Henry Hood attended. | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40.4597 | 37.4597 | 50046.2 | 0.15286 | 0.0040807 | 2014-11-08 | C | 0.15286 | 0.0040807 | 2015 | 2014-11-08 | C | 1336 | 0.15286 | 0.0040807
1 | 3011622 | 2014-11-08 06:10 | 2014-11-08 07:18 | 68 | 120 | 8160 | 0.024957 | 0.00036701 | Restore Supply on Device 97 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Sw/Gear 97 | Repair and maintain O/S 531,532 (defected for partial discharge). Works location: Kaimanawa St Palmerston North. WO 10147942. | F3 | KARAMEA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 7800 | 0.023825 | 0.00036653 | 2014-11-08 | C | 0.023825 | 0.00036653 | 2015 | 2014-11-08 | C | 120 | 0.023825 | 0.00036653
1 | 2452782 | 2014-11-08 06:11 | 2014-11-08 07:19 | 68.3667 | 121 | 8272.3667 | 0.0253 | 0.00037007 | NAPA ID:03375 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Sw/Gear 97 | Repair and maintain O/S 531,532 (defected for partial discharge). Works location: Kaimanawa St Palmerston North WO 10147942 | F3 | KARAMEA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 68.3667 | 65.3667 | 7909.3667 | 0.024159 | 0.00036959 | 2014-11-08 | B | 0.012079 | 0.00018479 | 2015 | 2014-11-08 | B | 121 | 0.024159 | 0.00036959
1 | 3002604 | 2014-11-08 07:32 | 2014-11-08 09:29 | 116.4333 | 1 | 116.4333 | 0.0003561 | 3.0584e-06 | Restore Supply on Device X1729 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 795032 | 2X 2 AMP HT FUSES DUE TO DUCK NO OTHER ASSEST REPAIRED OR REPLACED ADJACENT ASSETS OK. Emailed Jo, as appears could have SAIDI component. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 116.4333 | 113.4333 | 113.4333 | 0.00034647 | 3.0544e-06 | 2014-11-08 | C | 0.00034647 | 3.054e-06 | 2015 | 2014-11-08 | C | 1 | 0.00034647 | 3.0544e-06
1 | 2403505 | 2014-11-08 08:04 | 2014-11-08 15:01 | 417.2833 | 75 | 28898.9167 | 0.088385 | 0.00022938 | NAPA ID:03445 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 144 | Replace 33/11kV poles and Crossarms. Remove aerial earth. Install 33kV ABS144 on pole pole 760783, Between poles 760792 -754728. Works location: Ngatimaru-Otaraoa WO 10151691 | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 385.3189 | 382.3189 | 28673.9167 | 0.087582 | 0.00022908 | 2014-11-08 | B | 0.043791 | 0.00011454 | 2015 | 2014-11-08 | B | 75 | 0.087582 | 0.00022908
1 | 2452182 | 2014-11-08 09:05 | 2014-11-08 12:08 | 182.8167 | 10 | 1828.1667 | 0.0055913 | 3.0584e-05 | NAPA ID:03701 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | U10 | To Replace burnt of 11kv pole. Works location: Bright St Eketahuna. WO 10193474. | F3 | EKETAHUNA | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 182.8167 | 179.8167 | 1798.1667 | 0.0054924 | 3.0544e-05 | 2014-11-08 | B | 0.0027462 | 1.5272e-05 | 2015 | 2014-11-08 | B | 10 | 0.0054924 | 3.0544e-05
1 | 2452160 | 2014-11-08 09:15 | 2014-11-08 10:11 | 55.6 | 25 | 1390 | 0.0042512 | 7.6461e-05 | NAPA ID:03705 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S38 | To replace badly burnt 11kv x-arm. Works location: State Hwy 2 Mt Bruce. WO 10144704 | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55.6 | 52.6 | 1315 | 0.0040166 | 7.6361e-05 | 2014-11-08 | B | 0.0020083 | 3.818e-05 | 2015 | 2014-11-08 | B | 25 | 0.0040166 | 7.6361e-05
1 | 3004289 | 2014-11-08 10:23 | 2014-11-08 12:26 | 123.3167 | 1 | 123.3167 | 0.00037715 | 3.0584e-06 | Restore Supply on Device 4748W | 22000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuse 4578 | 2 X 10 Amp Fuse | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 123.3167 | 120.3167 | 120.3167 | 0.0003675 | 3.0544e-06 | 2014-11-08 | C | 0.0003675 | 3.054e-06 | 2015 | 2014-11-08 | C | 1 | 0.0003675 | 3.0544e-06
1 | 3004883 | 2014-11-09 03:53 | 2014-11-09 05:49 | 115.8667 | 1 | 115.8667 | 0.00035437 | 3.0584e-06 | Restore Supply on Device T1769 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Fuses 7203 | Replaced 2X HV Fuses. Emailed Jo, as appears could have SAIDI component. | F4 | TAWAHA | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 115.8667 | 112.8667 | 112.8667 | 0.00034474 | 3.0544e-06 | 2014-11-09 | C | 0.00034474 | 3.054e-06 | 2015 | 2014-11-09 | C | 1 | 0.00034474 | 3.0544e-06
1 | 3004889 | 2014-11-09 06:12 | 2014-11-09 07:55 | 102.9667 | 2 | 157.35 | 0.00048124 | 6.1168e-06 | Restore Supply on Device TC3436 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3436 | Replace faulty 1 x 5A H/V fuse link. No other assets repaired or replaced on site. FM checked adjacent assets and up to Powerco Standard. | F1/F4 | MCCABE ROAD | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 78.675 | 75.675 | 151.35 | 0.00046229 | 6.1088e-06 | 2014-11-09 | C | 0.00046229 | 6.109e-06 | 2015 | 2014-11-09 | C | 2 | 0.00046229 | 6.1088e-06
1 | 3005491 | 2014-11-09 08:22 | 2014-11-09 10:28 | 125.9333 | 9 | 460.35 | 0.0014079 | 2.7526e-05 | Restore Supply on Device TE4-016 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SE4-020 | REPLACED 2 X 10 AMP FUSES AT SE4 -020 SUSPECT BIRD STRIKE NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK Emailed Jo, as appears could have SAIDI component. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 51.15 | 48.15 | 433.35 | 0.0013236 | 2.749e-05 | 2014-11-09 | C | 0.0013236 | 2.749e-05 | 2015 | 2014-11-09 | C | 9 | 0.0013236 | 2.749e-05
1 | 2913652 | 2014-11-09 09:02 | 2014-11-09 10:14 | 71.8 | 31 | 2225.8 | 0.0068074 | 9.4811e-05 | NAPA ID:04326 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F1312 | Replace crossarms at pole F1312. Works location: Te Poi South Rd. | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 71.8 | 68.8 | 2132.8 | 0.0065145 | 9.4687e-05 | 2014-11-09 | B | 0.0032572 | 4.7344e-05 | 2015 | 2014-11-09 | B | 31 | 0.0065145 | 9.4687e-05
1 | 3012024 | 2014-11-10 05:21 | 2014-11-10 06:03 | 42 | 454 | 19068 | 0.058318 | 0.0013885 | Restore Supply on Device S322 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 820907 | Remove line breaks at poles 820907 & 820877 which were installed 22/10/14. Works location: High St Carterton. WO 10140873 IR6938. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 17706 | 0.054082 | 0.0013867 | 2014-11-10 | C | 0.054082 | 0.0013867 | 2015 | 2014-11-10 | C | 454 | 0.054082 | 0.0013867
1 | 3006089 | 2014-11-10 07:44 | 2014-11-10 09:41 | 116.9833 | 5424 | 326847.6 | 0.99964 | 0.016589 | Restore Supply on Device Z200 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Kelvin Grove Sub | Tripping on 33kV BPE CB2252, KEG CBZ200 and TWP CB Z226 causing loss of supply to Kelvin Grove Sub. (11kv CB F26 and 10083 also tripped on undervolts). Flaggings CB2252 Neutral Time O/C and CB Z200 A.B,C O/C, Zone 1, Dir E/F. Lines patrolled and BPE-KEG | F1, F2, F3 | KEITH-MAIN 2 33KV | TP_BUNNYTHORPE | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 60.2595 | 57.2595 | 310575.6 | 0.94863 | 0.016567 | 2014-11-10 | C | 0.94863 | 0.016567 | 2015 | 2014-11-10 | C | 5424 | 0.94863 | 0.016567
1 | 2452868 | 2014-11-10 08:37 | 2014-11-10 14:25 | 347.7333 | 5 | 1738.6667 | 0.0053176 | 1.5292e-05 | NAPA ID:03738 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH856 | Wire run Paora East Road. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 347.7333 | 344.7333 | 1723.6667 | 0.0052648 | 1.5272e-05 | 2014-11-10 | B | 0.0026324 | 7.636e-06 | 2015 | 2014-11-10 | B | 5 | 0.0052648 | 1.5272e-05
1 | 2403508 | 2014-11-10 09:01 | 2014-11-10 16:06 | 425.1667 | 7 | 2976.1667 | 0.0091024 | 2.1409e-05 | NAPA ID:03476 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 760721 | Replace 33/11kV poles and Crossarms. Remove aerial earth. Between poles 760721-760730. Works location: Otaraoa Rd. WO 1015169. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 425.1667 | 422.1667 | 2955.1667 | 0.0090263 | 2.1381e-05 | 2014-11-10 | B | 0.0045132 | 1.069e-05 | 2015 | 2014-11-10 | B | 7 | 0.0090263 | 2.1381e-05
1 | 2633877 | 2014-11-10 09:30 | 2014-11-10 11:51 | 141 | 29 | 4089 | 0.012506 | 8.8694e-05 | NAPA ID:03749 TP_KOPU GXP > WHITIANGA SUB > COOK DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W12956 | Repair O/H span between W12956 + W12957. Works location: Bryce St, Whitianga. WO 10161114. | F3 | COOK DRIVE | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 141 | 138 | 4002 | 0.012224 | 8.8578e-05 | 2014-11-10 | B | 0.0061119 | 4.4289e-05 | 2015 | 2014-11-10 | B | 29 | 0.012224 | 8.8578e-05
1 | 3011818 | 2014-11-10 09:47 | 2014-11-11 16:11 | 1824.2667 | 76 | 36901.9667 | 0.11286 | 0.00023244 | Restore Supply on Device 1406 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | Pole 780775 | Tripping on Recloser CB1406. Feeder patrolled & sectionalised with Broken Pole / Hardware and conductors down feeding spur line to Transformer X2654. Temp line break installed at takeoff Pole 780635 with isolation from Fuses 195. Relivened OK. Pole replac | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 485.5522 | 482.5522 | 36673.9667 | 0.11202 | 0.00023214 | 2014-11-10 | C | 0.11202 | 0.00023214 | 2015 | 2014-11-10 | C | 76 | 0.11202 | 0.00023214
1 | 2453049 | 2014-11-10 10:01 | 2014-11-10 12:17 | 135.95 | 1 | 135.95 | 0.00041579 | 3.0584e-06 | NAPA ID:03645 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2113 | Replace 11 kV crossarms. Works location: Waghorn Rd. WO 10145424. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 135.95 | 132.95 | 132.95 | 0.00040609 | 3.0544e-06 | 2014-11-10 | B | 0.00020304 | 1.527e-06 | 2015 | 2014-11-10 | B | 1 | 0.00040609 | 3.0544e-06
1 | 2885045 | 2014-11-10 11:34 | 2014-11-10 15:59 | 264.8333 | 37 | 9798.8333 | 0.029969 | 0.00011316 | NAPA ID:02443 TP_BUNNYTHORPE GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Bunnythorpe GXP | Shutdown # 2 Changing 33kv and 11kv xarm fitting new insulators | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 264.8333 | 261.8333 | 9687.8333 | 0.029591 | 0.00011301 | 2014-11-10 | B | 0.014795 | 5.6507e-05 | 2015 | 2014-11-10 | B | 37 | 0.029591 | 0.00011301
1 | 3013301 | 2014-11-10 13:01 | 2014-11-10 17:19 | 258.4167 | 1 | 258.4167 | 0.00079035 | 3.0584e-06 | Restore Supply on Device T4/206 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | p14400 | bucket truck required to remove branch off 11kv line at pole P14400 Jeff leaving site now has requested a 2R 1R bucket truck required to remove branch from line. 2nd 1R request may turn into 2R depending if work carried out live line. FM advise: remov | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 258.4167 | 255.4167 | 255.4167 | 0.00078015 | 3.0544e-06 | 2014-11-10 | C | 0.00078015 | 3.054e-06 | 2015 | 2014-11-10 | C | 1 | 0.00078015 | 3.0544e-06
1 | 3014223 | 2014-11-10 19:16 | 2014-11-10 21:50 | 154.1833 | 253 | 23986.0833 | 0.07336 | 0.00077378 | Restore Supply on Device C927 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 799392 | No Back feed put in at ABS S525 as it would have taken longer to do this than do the job. Line Down At Pole 799392 Isolated at ABS S588 & ABS S512. Bulls in paddock rubbing on Stay Wire shaking pole. Faultman thinks this could be the reason wire came d | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 94.8067 | 91.8067 | 23227.0833 | 0.070945 | 0.00077277 | 2014-11-10 | C | 0.070945 | 0.00077277 | 2015 | 2014-11-10 | C | 253 | 0.070945 | 0.00077277
1 | 3017048 | 2014-11-11 07:37 | 2014-11-11 10:49 | 191.8 | 1 | 191.8 | 0.00058661 | 3.0584e-06 | Restore Supply on Device X2641 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | FUSES4564 | Area patrolled - one HT fuse out at 4564, reclosed OK. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 191.8 | 188.8 | 188.8 | 0.00057668 | 3.0544e-06 | 2014-11-11 | C | 0.00057668 | 3.054e-06 | 2015 | 2014-11-11 | C | 1 | 0.00057668 | 3.0544e-06
1 | 2490949 | 2014-11-11 08:30 | 2014-11-11 15:23 | 412.5667 | 497 | 204598.3333 | 0.62575 | 0.00152 | NAPA ID:02674 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS S529 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 411.6667 | 408.6667 | 203107.3333 | 0.62038 | 0.001518 | 2014-11-11 | B | 0.31019 | 0.00075902 | 2015 | 2014-11-11 | B | 497 | 0.62038 | 0.001518
1 | 2689401 | 2014-11-11 08:45 | 2014-11-11 15:00 | 375.1333 | 47 | 16747.1333 | 0.05122 | 0.00014375 | NAPA ID:03489 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Hauraki Rd | Replace ABS436 and X-arms, and Various other X-arms within vicinity | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 356.322 | 353.322 | 16606.1333 | 0.050722 | 0.00014356 | 2014-11-11 | B | 0.025361 | 7.1779e-05 | 2015 | 2014-11-11 | B | 47 | 0.050722 | 0.00014356
1 | 3017653 | 2014-11-11 08:59 | 2014-11-11 09:32 | 32.8833 | 48 | 1534.4 | 0.0046928 | 0.0001468 | Restore Supply on Device 4848 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Recloser 4848/2 | Recloser 4848/2 Trip. Flags E/F Line Patrolled & Sectionalized no fault found. Suspect Insuator fault | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 31.9667 | 28.9667 | 1390.4 | 0.0042469 | 0.00014661 | 2014-11-11 | C | 0.0042469 | 0.00014661 | 2015 | 2014-11-11 | C | 48 | 0.0042469 | 0.00014661
1 | 2689389 | 2014-11-11 09:01 | 2014-11-11 11:55 | 174.5333 | 15 | 2618 | 0.0080069 | 4.5876e-05 | NAPA ID:03295 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP768 | Replace HV arms and straighten poles. Works location: Rawerawe Rd West WO TA-2104-36 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 174.5333 | 171.5333 | 2573 | 0.007859 | 4.5816e-05 | 2014-11-11 | B | 0.0039295 | 2.2908e-05 | 2015 | 2014-11-11 | B | 15 | 0.007859 | 4.5816e-05
1 | 2453078 | 2014-11-11 09:16 | 2014-11-11 10:16 | 60.8667 | 1 | 60.8667 | 0.00018616 | 3.0584e-06 | NAPA ID:03649 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2286 | replace 11 kV crossarms. Works location: Waghorn Rd WO 10145424 | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 60.8667 | 57.8667 | 57.8667 | 0.00017675 | 3.0544e-06 | 2014-11-11 | B | 8.8375e-05 | 1.527e-06 | 2015 | 2014-11-11 | B | 1 | 0.00017675 | 3.0544e-06
1 | 2690089 | 2014-11-11 09:20 | 2014-11-11 15:39 | 378.1833 | 94 | 17106.8 | 0.05232 | 0.00028749 | NAPA ID:03546 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer TB2-013 | INSTALL NEW RMU 9856 , TEST AND LIVEN [ STAGE 1 ] 1 - ISOLATE LINK BOX AT TB2-013 AND REMOVE 25MM CABLES TO TB2-068 [L2] [ AP 0915 TO 10.00] 2- RE-LIVEN 11KV LINK BOX AT TB2-013. 3- REMOVE 25MM AND 185MM CABLE AT NEW RMU 9856 -3 Works location: Fairv | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 181.9872 | 178.9872 | 16824.8 | 0.05139 | 0.00028712 | 2014-11-11 | B | 0.025695 | 0.00014356 | 2015 | 2014-11-11 | B | 94 | 0.05139 | 0.00028712
1 | 2690098 | 2014-11-11 09:34 | 2014-11-11 14:53 | 318.95 | 8 | 2551.6 | 0.0078039 | 2.4467e-05 | NAPA ID:03348 TP_TAURANGA 33 GXP > OMOKOROA SUB > WHAKAMARAMA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 210143 | REPLACE TX POLE TD2-022. Works location: Leyland Rd WO 10155241 10161772 | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 318.95 | 315.95 | 2527.6 | 0.0077204 | 2.4435e-05 | 2014-11-11 | B | 0.0038602 | 1.2218e-05 | 2015 | 2014-11-11 | B | 8 | 0.0077204 | 2.4435e-05
1 | 2453089 | 2014-11-11 10:00 | 2014-11-11 12:31 | 151.0333 | 73 | 11023.2333 | 0.033714 | 0.00022326 | NAPA ID:03678 TP_HUIRANGI GXP > WAITARA WEST SUB > BLAKE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 3567T | Replace piggyback Tx 3567T like-for-like with short outageto HV circuit. LV on Tx 3567T to remain isolated for a further hour. Works location: Mould St WO 10154760 | F1 | BLAKE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 151.0032 | 148.0032 | 10804.2333 | 0.033001 | 0.00022297 | 2014-11-11 | B | 0.0165 | 0.00011149 | 2015 | 2014-11-11 | B | 73 | 0.033001 | 0.00022297
1 | 2453227 | 2014-11-11 10:57 | 2014-11-11 11:52 | 54.7833 | 2 | 109.5667 | 0.0003351 | 6.1168e-06 | NAPA ID:03651 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC4201 | Replace 11 kV crossarms. Works location: Waghorn Rd WO 10145424 | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 54.7833 | 51.7833 | 103.5667 | 0.00031634 | 6.1088e-06 | 2014-11-11 | B | 0.00015817 | 3.054e-06 | 2015 | 2014-11-11 | B | 2 | 0.00031634 | 6.1088e-06
1 | 2689390 | 2014-11-11 12:02 | 2014-11-11 14:35 | 152.8333 | 10 | 1528.3333 | 0.0046743 | 3.0584e-05 | NAPA ID:03296 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP769 | Replace HV arms and straighten poles. Works location: Rawerawe Rd East WO TA-2104-36 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 152.8333 | 149.8333 | 1498.3333 | 0.0045765 | 3.0544e-05 | 2014-11-11 | B | 0.0022883 | 1.5272e-05 | 2015 | 2014-11-11 | B | 10 | 0.0045765 | 3.0544e-05
1 | 2453250 | 2014-11-11 12:46 | 2014-11-11 13:49 | 63.3667 | 4 | 253.4667 | 0.00077521 | 1.2234e-05 | NAPA ID:03654 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2130 | Replace 11 kV crossarms. Works location: Waghorn Rd WO 10145424 | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 63.3667 | 60.3667 | 241.4667 | 0.00073754 | 1.2218e-05 | 2014-11-11 | B | 0.00036877 | 6.109e-06 | 2015 | 2014-11-11 | B | 4 | 0.00073754 | 1.2218e-05
1 | 3018903 | 2014-11-11 15:59 | 2014-11-11 19:27 | 208.7333 | 40 | 4279.0333 | 0.013087 | 0.00012234 | Restore Supply on Device T1/94 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer T1/94 | broken ht fuse, bernie adv will need to do shutdown Outage required between ABS L18 and L20 (SH1 Sanson) to replace a broken HT Fuse at Transformer T1/94. (Backfeeds at ABS L23 and VS4278). Fuse replaced and livened OK. Used 1x DDO fuse carrier and Base 1 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 106.9758 | 103.9758 | 4159.0333 | 0.012703 | 0.00012218 | 2014-11-11 | C | 0.012703 | 0.00012218 | 2015 | 2014-11-11 | C | 40 | 0.012703 | 0.00012218
1 | 3019166 | 2014-11-11 19:30 | 2014-11-11 23:26 | 235.6167 | 3 | 706.85 | 0.0021618 | 9.1753e-06 | Restore Supply on Device 2216N | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P746954 | Access : big radio mast in paddock on seaward side of road, access off Pohutukawa Place, Bell Block. 2R requested to replace full hv fuse unit & double LV cross arm. Also replacing 3x LV fuses. Isolated at Fuses 6707 HV DDO's and LV cross arm replaced - | F1 | BELL BLOCK 4 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.6167 | 232.6167 | 697.85 | 0.0021315 | 9.1633e-06 | 2014-11-11 | C | 0.0021315 | 9.163e-06 | 2015 | 2014-11-11 | C | 3 | 0.0021315 | 9.1633e-06
1 | 3019244 | 2014-11-11 21:21 | 2014-11-12 09:57 | 756.4167 | 1 | 756.4167 | 0.0023134 | 3.0584e-06 | Restore Supply on Device T4/216 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx t4-216 | FM requesting 2R for tomorrow 12/11 for replacing 2 x 11kv ddo's fuse holders that are broken, replacing the full set. tx t4-216. also requesting the bucket truck and another faultman to help onsite. cause: old age. FM could not complete the job tonight, | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 756.4167 | 753.4167 | 753.4167 | 0.0023013 | 3.0544e-06 | 2014-11-11 | C | 0.0023013 | 3.054e-06 | 2015 | 2014-11-11 | C | 1 | 0.0023013 | 3.0544e-06
1 | 3019354 | 2014-11-12 05:49 | 2014-11-12 10:16 | 267.7833 | 7 | 823.2167 | 0.0025177 | 2.1409e-05 | Restore Supply on Device P1015 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | fuses 6293 & tx t1015 | Links out at fuses 6293 & issue further up road as well at Tx. replaced 3x 10amp ddo fuse links at fuses 6293 replaced 3x3amp ddo fuse links at tx t1015 Replaced 1x 3amp fuse & barrel at Tx P1030 cause lightning full power restored nothing else rep | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 117.6024 | 114.6024 | 802.2167 | 0.0024503 | 2.1381e-05 | 2014-11-12 | C | 0.0024503 | 2.1381e-05 | 2015 | 2014-11-12 | C | 7 | 0.0024503 | 2.1381e-05
1 | 3019684 | 2014-11-12 05:49 | 2014-11-12 09:24 | 215.0833 | 12 | 2581 | 0.0078938 | 3.6701e-05 | Restore Supply on Device 6293 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | fuses 6293 | Fuses 6293 Blown from possible lightning strike 3 HV Fuses Links replaced full power restored nothing else repaired or replaced adjacent assets - ok | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 215.0833 | 212.0833 | 2545 | 0.0077735 | 3.6653e-05 | 2014-11-12 | C | 0.0077735 | 3.6653e-05 | 2015 | 2014-11-12 | C | 12 | 0.0077735 | 3.6653e-05
1 | 3019372 | 2014-11-12 06:06 | 2014-11-12 10:08 | 241.6 | 1 | 241.6 | 0.00073891 | 3.0584e-06 | Restore Supply on Device 4030T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Tx 4030T | Tx 4030T Replaced 3 of 3 3amp ddo fuse links hv o/h cause lightning full power restored nothing else repaired or replaced adjacent assets - ok - Email sent to JO | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 241.6 | 238.6 | 238.6 | 0.00072879 | 3.0544e-06 | 2014-11-12 | C | 0.00072879 | 3.054e-06 | 2015 | 2014-11-12 | C | 1 | 0.00072879 | 3.0544e-06
1 | 3019375 | 2014-11-12 06:08 | 2014-11-12 09:36 | 208.0167 | 35 | 1857.6167 | 0.0056814 | 0.00010704 | Restore Supply on Device 3976T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Fuse 5256 at pole 764217 & Fuse 6035 | Check if this affects OMS 3019425, OMS 3019397, OMS3019378, OMS3019433, OMS3019456 All 3 road links out at: Fuse 5256 - Replaced 3x 10amp links at pole 764217 & Fuse 6035 - Replaced 3x 3amp links. Cause lightning Full power restored nothing else repa | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 53.0748 | 50.0748 | 1752.6167 | 0.0053532 | 0.0001069 | 2014-11-12 | C | 0.0053532 | 0.0001069 | 2015 | 2014-11-12 | C | 35 | 0.0053532 | 0.0001069
1 | 3019524 | 2014-11-12 08:29 | 2014-11-12 09:59 | 90.7667 | 5 | 104.7 | 0.00032022 | 1.5292e-05 | Restore Supply on Device 3468T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3468T | 3X 3 AMP HV FUSES POLE 744831 DUE TO LIGHTEINIG TX 3468T SURROUNDING ASETT ALL GODD NOTHING ELSE REPAIRED OR REPLACED ALSO WORKED THROUGH CONTROL | F4 | WAITARA EAST TOWN | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 20.94 | 17.94 | 89.7 | 0.00027398 | 1.5272e-05 | 2014-11-12 | C | 0.00027398 | 1.5272e-05 | 2015 | 2014-11-12 | C | 5 | 0.00027398 | 1.5272e-05
1 | 2491117 | 2014-11-12 08:54 | 2014-11-12 14:28 | 334 | 4 | 1336 | 0.0040861 | 1.2234e-05 | NAPA ID:02708 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1kV pole 797550 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 334 | 331 | 1324 | 0.0040441 | 1.2218e-05 | 2014-11-12 | B | 0.002022 | 6.109e-06 | 2015 | 2014-11-12 | B | 4 | 0.0040441 | 1.2218e-05
1 | 2885366 | 2014-11-12 09:00 | 2014-11-12 16:45 | 465 | 37 | 17205 | 0.05262 | 0.00011316 | NAPA ID:02444 TP_BUNNYTHORPE GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sangsters Road | Shutdown # 3 Changing 33kv and 11kv xarm fitting new insulators Job had an over run due to contractors vehicals getting stuck on the wet ground. | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 465 | 462 | 17094 | 0.052212 | 0.00011301 | 2014-11-12 | B | 0.026106 | 5.6507e-05 | 2015 | 2014-11-12 | B | 37 | 0.052212 | 0.00011301
1 | 2861377 | 2014-11-12 09:01 | 2014-11-12 13:26 | 265.2833 | 135 | 35813.25 | 0.10953 | 0.00041289 | NAPA ID:03217 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 316923 | REPLACE HV POLES AND HV ARMS ALONG ROAD AS PER SCOPE OF PACK. Works location: Levley Lane WO 10145667 IR7221 | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 265.2833 | 262.2833 | 35408.25 | 0.10815 | 0.00041235 | 2014-11-12 | B | 0.054076 | 0.00020617 | 2015 | 2014-11-12 | B | 135 | 0.10815 | 0.00041235
1 | 2690056 | 2014-11-12 09:16 | 2014-11-13 04:05 | 1129.25 | 75 | 46569.7167 | 0.14243 | 0.00022938 | NAPA ID:02677 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 792852 | Replace 11kv poles and x arms between 792852 and ABS 1066. Works location: Ruatangata Rd Whangaehu WO 10141993 | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 620.9296 | 617.9296 | 46344.7167 | 0.14156 | 0.00022908 | 2014-11-12 | B | 0.070778 | 0.00011454 | 2015 | 2014-11-12 | B | 75 | 0.14156 | 0.00022908
1 | 2861362 | 2014-11-12 09:24 | 2014-11-12 14:11 | 286.65 | 20 | 5733 | 0.017534 | 6.1168e-05 | NAPA ID:03664 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC368 | Replace 11kv arms and pole at various sites. Works location: Thames Coast, Thames WO 10162255 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 286.65 | 283.65 | 5673 | 0.017328 | 6.1088e-05 | 2014-11-12 | B | 0.0086639 | 3.0544e-05 | 2015 | 2014-11-12 | B | 20 | 0.017328 | 6.1088e-05
1 | 2453285 | 2014-11-12 09:55 | 2014-11-12 14:15 | 260 | 3 | 780 | 0.0023856 | 9.1753e-06 | NAPA ID:02760 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 2513 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd Tariki Inglewood WO 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 260 | 257 | 771 | 0.002355 | 9.1633e-06 | 2014-11-12 | B | 0.0011775 | 4.582e-06 | 2015 | 2014-11-12 | B | 3 | 0.002355 | 9.1633e-06
1 | 2490931 | 2014-11-12 10:19 | 2014-11-13 13:18 | 1619.0667 | 46 | 74477.0667 | 0.22778 | 0.00014069 | NAPA ID:03798 TP_MANGAMAIRE GXP > ALFREDTON SUB > BROOKLANDS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS I27 | To Change 11Kv x-arms and ABS I27. Works location: Route 52 WO 10144449 | F4 | BROOKLANDS | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1619.0667 | 1616.0667 | 74339.0667 | 0.22706 | 0.0001405 | 2014-11-12 | B | 0.11353 | 7.0252e-05 | 2015 | 2014-11-12 | B | 46 | 0.22706 | 0.0001405
1 | 2453259 | 2014-11-12 10:21 | 2014-11-12 12:15 | 114.55 | 1 | 114.55 | 0.00035034 | 3.0584e-06 | NAPA ID:03657 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC767 | Replace 11 kV crossarms. Works location: Waghorn Rd WO 10145424 | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 114.55 | 111.55 | 111.55 | 0.00034072 | 3.0544e-06 | 2014-11-12 | B | 0.00017036 | 1.527e-06 | 2015 | 2014-11-12 | B | 1 | 0.00034072 | 3.0544e-06
1 | 3021557 | 2014-11-12 11:51 | 2014-11-12 13:41 | 109.4333 | 1 | 109.4333 | 0.00033469 | 3.0584e-06 | Restore Supply on Device 3523T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Tx 3523T | replaced 2x 2amp ddo fuses at Tx 3523T hv o/h. Cause lightning. full power restored. nothing else repaired or replaced. adjacent assets ok. | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.4333 | 106.4333 | 106.4333 | 0.00032509 | 3.0544e-06 | 2014-11-12 | C | 0.00032509 | 3.054e-06 | 2015 | 2014-11-12 | C | 1 | 0.00032509 | 3.0544e-06
1 | 3019469 | 2014-11-12 12:02 | 2014-11-12 14:35 | 153 | 10 | 1530 | 0.0046794 | 3.0584e-05 | Restore Supply on Device FP769 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP769 | Replace HV arms and straighten poles. Works location: Rawerawe Rd East WO TA-2104-36 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 153 | 150 | 1500 | 0.0045816 | 3.0544e-05 | 2014-11-12 | C | 0.0045816 | 3.0544e-05 | 2015 | 2014-11-12 | C | 10 | 0.0045816 | 3.0544e-05
1 | 3021565 | 2014-11-12 12:08 | 2014-11-12 16:30 | 261.9 | 1 | 261.9 | 0.000801 | 3.0584e-06 | Restore Supply on Device X1037 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 809101 | replace 3 amp hv fuse and candle at pole 809101. cause: lightning. 1 out of 2 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 261.9 | 258.9 | 258.9 | 0.00079079 | 3.0544e-06 | 2014-11-12 | C | 0.00079079 | 3.054e-06 | 2015 | 2014-11-12 | C | 1 | 0.00079079 | 3.0544e-06
1 | 3037489 | 2014-11-12 15:29 | 2014-11-12 15:47 | 18 | 1097 | 19743 | 0.060382 | 0.0033551 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 1251 | CB 5 tripped on neutral flags,suspect tripping was when back feed at ABS 1251 was opened under switching on ( Napa 3750 , OMS No: 2534551). Supect all 3 phases did not open at the same time. | F2 | KINGS AVENUE | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 17.9973 | 14.9973 | 16452 | 0.050251 | 0.0033507 | 2014-11-12 | C | 0.050251 | 0.0033507 | 2015 | 2014-11-12 | C | 1097 | 0.050251 | 0.0033507
1 | 3024724 | 2014-11-12 15:37 | 2014-11-12 17:00 | 83.2333 | 41 | 3380.5833 | 0.010339 | 0.0001254 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Recloser 9454 | Recloser 9454 found tripped. (No SCADA indication on this breaker). Recloser was on single shot for tree work to be carried out. This had finished and faultman was on his way to restore Recloser to 3 shots at the time of tripping. Patrolled, no fault foun | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 82.4533 | 79.4533 | 3257.5833 | 0.00995 | 0.00012523 | 2014-11-12 | C | 0.00995 | 0.00012523 | 2015 | 2014-11-12 | C | 41 | 0.00995 | 0.00012523
1 | 2653746 | 2014-11-13 08:30 | 2014-11-13 14:13 | 343 | 8 | 2744 | 0.0083923 | 2.4467e-05 | NAPA ID:02713 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 7442 | 11KV POLE REPLACEMENT. Works location: Warrens Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 343 | 340 | 2720 | 0.008308 | 2.4435e-05 | 2014-11-13 | B | 0.004154 | 1.2218e-05 | 2015 | 2014-11-13 | B | 8 | 0.008308 | 2.4435e-05
1 | 2453271 | 2014-11-13 08:31 | 2014-11-13 15:15 | 404.4833 | 32 | 12943.4667 | 0.039587 | 9.787e-05 | NAPA ID:03739 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6525 | Change poles. Works location: Whenuku Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 404.4833 | 401.4833 | 12847.4667 | 0.039242 | 9.7742e-05 | 2014-11-13 | B | 0.019621 | 4.8871e-05 | 2015 | 2014-11-13 | B | 32 | 0.039242 | 9.7742e-05
1 | 2914210 | 2014-11-13 08:53 | 2014-11-13 15:08 | 375 | 54 | 20250 | 0.061933 | 0.00016515 | NAPA ID:04342 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SB2-028 | UPGRADE 11KV CABLES TO 185MM FROM SB2-028 TO TB2-013 TO 9856-1 [STAGE 2] 1/ ISOLATE 11KV LINK BOX AT TB2-013 REMOVE 25MM CABLE HV, RUN IN AND TERMINATE NEW 185 CABLES. REMOVE 25MM HV CABLES FROM LINKS SB2-028 , RUN IN AND TERMINATE NEW 185MM CABLES. TERM | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 375 | 372 | 20088 | 0.061357 | 0.00016494 | 2014-11-13 | B | 0.030679 | 8.2469e-05 | 2015 | 2014-11-13 | B | 54 | 0.061357 | 0.00016494
1 | 2913703 | 2014-11-13 08:58 | 2014-11-13 15:59 | 420.85 | 110 | 46293.5 | 0.14159 | 0.00033643 | NAPA ID:04307 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC2572 | Replace HV arms and straighten poles. Works location: Pipiroa Rd WO TA/2014/36. Email sent to Andrew who will follow up why this outage went an hour over planned restoration time. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 420.85 | 417.85 | 45963.5 | 0.14039 | 0.00033599 | 2014-11-13 | B | 0.070196 | 0.00016799 | 2015 | 2014-11-13 | B | 110 | 0.14039 | 0.00033599
1 | 2385695 | 2014-11-13 09:00 | 2014-11-13 14:58 | 357.85 | 24 | 8588.4 | 0.026267 | 7.3402e-05 | NAPA ID:03485 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV Pole 760330 | 33/6.6kV pole and crossarm replacement between poles #760330 & 760629. Works location: Rimutauteka and Bristol Rd Waitara WO 10151691 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 357.85 | 354.85 | 8516.4 | 0.026013 | 7.3306e-05 | 2014-11-13 | B | 0.013006 | 3.6653e-05 | 2015 | 2014-11-13 | B | 24 | 0.026013 | 7.3306e-05
1 | 3035655 | 2014-11-13 09:01 | 2014-11-13 09:42 | 41.5167 | 80 | 3321.3333 | 0.010158 | 0.00024467 | Restore Supply on Device TC4164 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole M13126 Tx C6128 | 11kv lead off drop out at pole M13126 Tx C6128 Emergency outage notified on outage board Worked through control cause lead had been pulled too tight - unknown cut & refitted existing lead full power restored nothing else repaired or replaced adj | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 41.5167 | 38.5167 | 3081.3333 | 0.0094117 | 0.00024435 | 2014-11-13 | C | 0.0094117 | 0.00024435 | 2015 | 2014-11-13 | C | 80 | 0.0094117 | 0.00024435
1 | 2861404 | 2014-11-13 09:30 | 2014-11-13 15:15 | 345 | 22 | 7590 | 0.023213 | 6.7285e-05 | NAPA ID:02737 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 460 | Replace various arms and poles in work area. Works location; Egmont Rd WO 10145448 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 7524 | 0.022981 | 6.7197e-05 | 2014-11-13 | B | 0.011491 | 3.3599e-05 | 2015 | 2014-11-13 | B | 22 | 0.022981 | 6.7197e-05
1 | 3038784 | 2014-11-13 14:41 | 2014-11-13 16:54 | 132.9167 | 1 | 132.9167 | 0.00040652 | 3.0584e-06 | Restore Supply on Device T7/390 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | t7-390 | SEE IF THIS IS RELATED TO 3038722 4.23pm shannon called and advised she put trevor onsite by mistake, i have moved trevor back to assigned replace 1 x 3 amp ddo fuse. 1 out of 3 phases at tx t7-390. cause: lightning. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 132.9167 | 129.9167 | 129.9167 | 0.00039682 | 3.0544e-06 | 2014-11-13 | C | 0.00039682 | 3.054e-06 | 2015 | 2014-11-13 | C | 1 | 0.00039682 | 3.0544e-06
1 | 3038905 | 2014-11-13 19:36 | 2014-11-14 15:45 | 1209.45 | 5 | 6047.25 | 0.018495 | 1.5292e-05 | Restore Supply on Device A60 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | P44215 | Related to Site Inspection job 3038895 DNO 141102 to replace u/g cable from Pole P44215 to Transformer T6/189 Cable replaced and relivened OK. | F3 | AWAPUNI | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 1209.45 | 1206.45 | 6032.25 | 0.018425 | 1.5272e-05 | 2014-11-13 | C | 0.018425 | 1.5272e-05 | 2015 | 2014-11-13 | C | 5 | 0.018425 | 1.5272e-05
1 | 2690071 | 2014-11-14 08:30 | 2014-11-14 14:35 | 365 | 42 | 15330 | 0.046886 | 0.00012845 | NAPA ID:02679 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1903 | Open temp links #79 (installed 10/11/14) so that T1903 and pole can be replaced. Works location: Brooklyn Rd Carterton. WO 10140873 IR6938. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 365 | 362 | 15204 | 0.046439 | 0.00012829 | 2014-11-14 | B | 0.02322 | 6.4143e-05 | 2015 | 2014-11-14 | B | 42 | 0.046439 | 0.00012829
1 | 2881441 | 2014-11-14 08:30 | 2014-11-14 14:08 | 338.1167 | 32 | 10819.7333 | 0.033091 | 9.787e-05 | NAPA ID:03748 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6525 | Change poles on Whenuku rd. Works location: Whenuku Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 338.1167 | 335.1167 | 10723.7333 | 0.032755 | 9.7742e-05 | 2014-11-14 | B | 0.016377 | 4.8871e-05 | 2015 | 2014-11-14 | B | 32 | 0.032755 | 9.7742e-05
1 | 2689232 | 2014-11-14 08:49 | 2014-11-14 11:18 | 148.7167 | 32 | 4758.9333 | 0.014555 | 9.787e-05 | NAPA ID:03901 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | ABS 664 | isolation of 11 kv line for treescape for tree removal. Works location: Hibbards Rd, Taihape PPPD 43078 | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 148.7167 | 145.7167 | 4662.9333 | 0.014243 | 9.7742e-05 | 2014-11-14 | B | 0.0071213 | 4.8871e-05 | 2015 | 2014-11-14 | B | 32 | 0.014243 | 9.7742e-05
1 | 3039590 | 2014-11-14 09:15 | 2014-11-14 11:55 | 159.9167 | 4 | 639.6667 | 0.0019564 | 1.2234e-05 | Restore Supply on Device TE5-250 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE5-250 | HV problems at transformer, switching done to isolate transformer, tapped transformer down and voltage all good. cause unknown. customer had electrician onsite sorting internal issues. nothing else repaired or replaced, adjacent assets up to powerco stand | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 159.9167 | 156.9167 | 627.6667 | 0.0019172 | 1.2218e-05 | 2014-11-14 | C | 0.0019172 | 1.2218e-05 | 2015 | 2014-11-14 | C | 4 | 0.0019172 | 1.2218e-05
1 | 3012017 | 2014-11-14 09:25 | 2014-11-14 11:20 | 115 | 2 | 230 | 0.00070344 | 6.1168e-06 | NAPA ID:04491 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 2136 | To upgrade thev transformer due to Power Quility Issues. Works location: Endowment Rd WO 30000573 | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 115 | 112 | 224 | 0.00068419 | 6.1088e-06 | 2014-11-14 | B | 0.00034209 | 3.054e-06 | 2015 | 2014-11-14 | B | 2 | 0.00068419 | 6.1088e-06
1 | 3039597 | 2014-11-14 09:31 | 2014-11-14 11:53 | 142 | 3 | 5335.9 | 0.016319 | 9.1753e-06 | Restore Supply on Device T1832 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1832 | Pole 1832 LV/O/H F/man has requested 2R to replace LV 400amp Tx fuse & base (full fuse unit) at Tx T1832 also to replace the lead at the back of the Tx to the rear as is burnt out - other leads are loose too. Shutdown is required on this Tx to be worke | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1778.6333 | 1775.6333 | 5326.9 | 0.016271 | 9.1633e-06 | 2014-11-14 | C | 0.016271 | 9.163e-06 | 2015 | 2014-11-14 | C | 3 | 0.016271 | 9.1633e-06
1 | 2861380 | 2014-11-14 10:00 | 2014-11-14 13:15 | 195.05 | 19 | 3702.95 | 0.011325 | 5.811e-05 | NAPA ID:03963 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 63 | Replace 11Kv ABS 63 and x-arms and upgrade earths. Works location: Manutahi Rd Lepperton WO 10164710 | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 194.8921 | 191.8921 | 3645.95 | 0.011136 | 5.8034e-05 | 2014-11-14 | B | 0.0055681 | 2.9017e-05 | 2015 | 2014-11-14 | B | 19 | 0.011136 | 5.8034e-05
1 | 3039955 | 2014-11-14 17:50 | 2014-11-14 19:37 | 107.1333 | 63 | 1950.9 | 0.0059667 | 0.00019268 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 737 Rapanui Road | Faultman found a broken jumper on pole 769366, line was isolated at ABS's 807 and 2517 to repair the jumper. Ben Englebretsen attended. 1 X PG clamp used. | F3 | WESTMERE PEAT ST | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 30.9667 | 27.9667 | 1761.9 | 0.0053816 | 0.00019243 | 2014-11-14 | B | 0.0026908 | 9.6214e-05 | 2015 | 2014-11-14 | B | 63 | 0.0053816 | 0.00019243
1 | 3043051 | 2014-11-14 18:07 | 2014-11-15 10:33 | 985.9667 | 64 | 42182.7 | 0.12901 | 0.00019574 | Restore Supply on Device V5 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | recloser v5 | replace 2 x 10 amp fuses. 2 out of 3 phases. cause: wind. recloser v5. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 659.1047 | 656.1047 | 41990.7 | 0.12826 | 0.00019548 | 2014-11-14 | C | 0.12826 | 0.00019548 | 2015 | 2014-11-14 | C | 64 | 0.12826 | 0.00019548
1 | 3040155 | 2014-11-15 02:49 | 2014-11-15 06:15 | 206 | 53 | 9028 | 0.027611 | 0.0001621 | Restore Supply on Device C844 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C844 | CB C844 tripped no flags line was isolated and patrolled and fault was found , high wind in area. | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 170.3396 | 167.3396 | 8869 | 0.02709 | 0.00016188 | 2014-11-15 | C | 0.02709 | 0.00016188 | 2015 | 2014-11-15 | C | 53 | 0.02709 | 0.00016188
1 | 3045808 | 2014-11-15 05:33 | 2014-11-15 09:17 | 223.35 | 630 | 29808.8333 | 0.091168 | 0.0019268 | Restore Supply on Device C638 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 808912 | CB C890 autro reclosed. Recloser C638 tripped A,B,C phase O/C. Line patrolled and branch located burning on line at pole 808912. Fuses 7385 found blown. Sectionalised and repairs made. Adam Whale and Jason Hall attended. Outage steps recorded under OMS J | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 47.3156 | 44.3156 | 27918.8333 | 0.085276 | 0.0019243 | 2014-11-15 | C | 0.085276 | 0.0019243 | 2015 | 2014-11-15 | C | 630 | 0.085276 | 0.0019243
1 | 3040852 | 2014-11-15 05:41 | 2014-11-15 07:16 | 95.15 | 303 | 28689.05 | 0.087743 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Alfredton | CB XT 40 tripped, L/O no flags. Fault bypassed but not repaired | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 94.6833 | 91.6833 | 27780.05 | 0.084852 | 0.00092549 | 2014-11-15 | C | 0.084852 | 0.00092549 | 2015 | 2014-11-15 | C | 303 | 0.084852 | 0.00092549
1 | 3043118 | 2014-11-15 06:16 | 2014-11-15 12:00 | 343.7333 | 29 | 9968.2667 | 0.030487 | 8.8694e-05 | Restore Supply on Device T473 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN |  | HauNui C633 found open. Line patrolled and no fault found. Breaker closed on load. Jason Hall attended. Email sent to JO, as appears could have a SAIDI component. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 343.7333 | 340.7333 | 9881.2667 | 0.030182 | 8.8578e-05 | 2014-11-15 | C | 0.030182 | 8.8578e-05 | 2015 | 2014-11-15 | C | 29 | 0.030182 | 8.8578e-05
1 | 3047218 | 2014-11-15 07:06 | 2014-11-15 11:57 | 290.8667 | 192 | 8582.0667 | 0.026248 | 0.00058722 | Restore Supply on Device U22 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN |  | ARC | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 44.6983 | 41.6983 | 8006.0667 | 0.024454 | 0.00058645 | 2014-11-15 | C | 0.024454 | 0.00058645 | 2015 | 2014-11-15 | C | 192 | 0.024454 | 0.00058645
1 | 3043445 | 2014-11-15 07:11 | 2014-11-15 09:55 | 164.8333 | 116 | 19120.6667 | 0.058479 | 0.00035478 | Restore Supply on Device T42/2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND |  | Closed on load with no patrol or fault found | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 164.8333 | 161.8333 | 18772.6667 | 0.05734 | 0.00035431 | 2014-11-15 | C | 0.05734 | 0.00035431 | 2015 | 2014-11-15 | C | 116 | 0.05734 | 0.00035431
1 | 3045519 | 2014-11-15 08:23 | 2014-11-15 12:30 | 247.0667 | 178 | 21222.8667 | 0.064908 | 0.0005444 | Restore Supply on Device 2 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 811170 | CB C885 tripped O/C E/F. Line patrolled and 33kV insulator replaced at pole 811170. Gavin Gray attended. Refer to OMS Job ID 3046108 for remainder of outage. | F1, F2, F3 | FEATHERSTON 33KV | TP_GREYTOWN | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 119.2296 | 116.2296 | 20688.8667 | 0.063193 | 0.00054369 | 2014-11-15 | C | 0.063193 | 0.00054369 | 2015 | 2014-11-15 | C | 178 | 0.063193 | 0.00054369
1 | 3101617 | 2014-11-15 08:47 | 2014-11-15 13:09 | 262 | 3 | 786 | 0.0024039 | 9.1753e-06 | Restore Supply on Device T930 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 819230 | Broken pole 819230 on 11kV Spur Line. Held up by truck to stop pole from falling onto main road. Isolated at Links 7151. Adrian Marshall & Darrell Rothery attended. | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 262 | 259 | 777 | 0.0023733 | 9.1633e-06 | 2014-11-15 | C | 0.0023733 | 9.163e-06 | 2015 | 2014-11-15 | C | 3 | 0.0023733 | 9.1633e-06
1 | 3046103 | 2014-11-15 08:53 | 2014-11-15 13:32 | 278.6667 | 47 | 3060.9 | 0.0093615 | 0.00014375 | Restore Supply on Device 3873T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | transformer 3873T | repair jumper on pole 734962 to transformer 3873T Drop out fuse. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 65.1255 | 62.1255 | 2919.9 | 0.0089186 | 0.00014356 | 2014-11-15 | C | 0.0089186 | 0.00014356 | 2015 | 2014-11-15 | C | 47 | 0.0089186 | 0.00014356
1 | 3099455 | 2014-11-15 09:11 | 2014-11-15 16:14 | 423 | 196 | 65742 | 0.20107 | 0.00059945 | Restore Supply on Device C422 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | C422 | Clareville CB C422 tripped. Line patrolled and floating conductor loacted at pole 823068. Repaired undertaken and restoration completed. No Materials Noted. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 335.4184 | 332.4184 | 65154 | 0.19901 | 0.00059867 | 2014-11-15 | C | 0.19901 | 0.00059867 | 2015 | 2014-11-15 | C | 196 | 0.19901 | 0.00059867
1 | 3046365 | 2014-11-15 09:20 | 2014-11-15 17:21 | 481.7667 | 176 | 84790.9333 | 0.25933 | 0.00053828 | Restore Supply on Device CB3 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P04322, P04308 | Replaced stay wire on pole P04322 and Jumper on pole P04308. Phil Barnes attended. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 481.7667 | 478.7667 | 84262.9333 | 0.25737 | 0.00053758 | 2014-11-15 | C | 0.25737 | 0.00053758 | 2015 | 2014-11-15 | C | 176 | 0.25737 | 0.00053758
1 | 3095411 | 2014-11-15 09:31 | 2014-11-15 15:49 | 378 | 251 | 94878 | 0.29018 | 0.00076766 | Restore Supply on Device C639 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C639/2 | Tuhitarata C627 Auto Reclosed. Line patrolled and C639/2 was found open. Jason Hall attended. No materials noted on switching sheet. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 378 | 375 | 94125 | 0.2875 | 0.00076666 | 2014-11-15 | C | 0.2875 | 0.00076666 | 2015 | 2014-11-15 | C | 251 | 0.2875 | 0.00076666
1 | 2885033 | 2014-11-15 09:33 | 2014-11-15 10:32 | 59 | 243 | 14337 | 0.043849 | 0.0007432 | NAPA ID:04049 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/636 | Phasing must be completed first then connect new cable replaced under switching 4048 back up to T6/636. Repair termination at T6/651. Restore feeder to normal and remove DNO 140913. Works location: Rhodes Drive. WO 10159492. | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 59 | 56 | 13608 | 0.041565 | 0.00074222 | 2014-11-15 | B | 0.020782 | 0.00037111 | 2015 | 2014-11-15 | B | 243 | 0.041565 | 0.00074222
1 | 3099708 | 2014-11-15 09:34 | 2014-11-15 15:54 | 380 | 75 | 27914 | 0.085373 | 0.00022938 | Restore Supply on Device I4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P28796 | No Power - Line patrolled. Faultman found 2 floating wires at pole P28796, line was isolated at ABS I6 and Links I5 to rebinder the conductors in. 2 X Binders used. transitioning to Check if 3045066 is part of this before signing off. Faultman found 2 flo | F4 | IHURAUA | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 372.1867 | 369.1867 | 27689 | 0.084574 | 0.00022908 | 2014-11-15 | C | 0.084574 | 0.00022908 | 2015 | 2014-11-15 | C | 75 | 0.084574 | 0.00022908
1 | 3047178 | 2014-11-15 09:34 | 2014-11-17 10:48 | 2953.6167 | 1 | 2953.6167 | 0.0090334 | 3.0584e-06 | Restore Supply on Device T2004 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 246 longbush road, wairarapa | check if this affects OMS 3048793 signed off the same as OMS 3048793 | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 2953.6167 | 2950.6167 | 2950.6167 | 0.0090124 | 3.0544e-06 | 2014-11-15 | C | 0.0090124 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.0090124 | 3.0544e-06
1 | 3046108 | 2014-11-15 09:56 | 2014-11-15 12:06 | 129.6 | 148 | 19177.9333 | 0.058654 | 0.00045265 | Restore Supply on Device C885 | 33000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 811170 | Replaced 33kV insulator on pole 811170. Attended by Gavin Grey and Lee Wilton. Initial tripping outage recorded under OMS Job ID 3045519 | F1, F2, F3 | PAHAUTEA 33KV TIE | TP_GREYTOWN | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 129.5806 | 126.5806 | 18733.9333 | 0.057221 | 0.00045205 | 2014-11-15 | C | 0.057221 | 0.00045205 | 2015 | 2014-11-15 | C | 148 | 0.057221 | 0.00045205
1 | 3047689 | 2014-11-15 09:59 | 2014-11-15 10:18 | 19.1 | 132 | 2521.2 | 0.0077109 | 0.00040371 | Restore Supply on Device CB4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P04385 | replaced pole P04385 and repaired lines | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 19.1 | 16.1 | 2125.2 | 0.0064913 | 0.00040318 | 2014-11-15 | C | 0.0064913 | 0.00040318 | 2015 | 2014-11-15 | C | 132 | 0.0064913 | 0.00040318
1 | 3048693 | 2014-11-15 10:54 | 2014-11-15 17:34 | 400.5333 | 399 | 39198.3667 | 0.11989 | 0.0012203 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C224 | CB C937 Tripped 10:54 on O/C. Refer Outage OMS Job ID 3048390. Recloser C224 tripped - line patrolled, no fault located. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98.2415 | 95.2415 | 38001.3667 | 0.11607 | 0.0012187 | 2014-11-15 | C | 0.11607 | 0.0012187 | 2015 | 2014-11-15 | C | 399 | 0.11607 | 0.0012187
1 | 3048862 | 2014-11-15 11:23 | 2014-11-15 18:30 | 427.25 | 584 | 49992.8 | 0.1529 | 0.0017861 | Restore Supply on Device 9 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 249832 | Police report of milk tanker v pole - Police onsite carrying out traffic management. P019232477. Outside Tirohia School, SH26, TIROHIA. Isolated between ABS IP191, 547, 552 & 1041. Backfeed rest of area NDR 17944. James Kennerly attending not James Bri | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 85.6041 | 82.6041 | 48240.8 | 0.14735 | 0.0017838 | 2014-11-15 | C | 0.14735 | 0.0017838 | 2015 | 2014-11-15 | C | 584 | 0.14735 | 0.0017838
1 | 3099393 | 2014-11-15 11:27 | 2014-11-15 14:45 | 198 | 32 | 6336 | 0.019378 | 9.787e-05 | Restore Supply on Device 7255 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 7255 | Replaced 2x Hv fuses @ 7255 and 1x Hv Fuse @ 7257. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. Email sent to JO, as appears could have a SAIDI component. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 198 | 195 | 6240 | 0.01906 | 9.7742e-05 | 2014-11-15 | C | 0.01906 | 9.7742e-05 | 2015 | 2014-11-15 | C | 32 | 0.01906 | 9.7742e-05
1 | 3095060 | 2014-11-15 12:03 | 2014-11-15 20:52 | 529 | 33 | 17457 | 0.053391 | 0.00010093 | Restore Supply on Device 7383 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Fuses 7383 | No Power. Line patrolled. Fuses 7383 found open and trees located through lines at pole 817097. NDR 34881 & NDR 34882. Gavin Grey attended. Materials used: 3 Metres of 16mm Copper and 6 sleeves. Also 30 metres of 16mm copper and 12 binders. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 529 | 526 | 17358 | 0.053019 | 0.0001008 | 2014-11-15 | C | 0.053019 | 0.0001008 | 2015 | 2014-11-15 | C | 33 | 0.053019 | 0.0001008
1 | 3050774 | 2014-11-15 12:26 | 2014-11-15 15:21 | 174.8 | 528 | 67781.0833 | 0.2073 | 0.0016148 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D1454 | Recloser 9773 Locked out. O/C Sectionalised and found floating wire at pole D1454. Isolated at ABS 854. Rebound wire and re livened. Paul Cooper attended. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 128.3733 | 125.3733 | 66197.0833 | 0.20219 | 0.0016127 | 2014-11-15 | C | 0.20219 | 0.0016127 | 2015 | 2014-11-15 | C | 528 | 0.20219 | 0.0016127
1 | 3051327 | 2014-11-15 12:45 | 2014-11-15 21:03 | 497.9667 | 1 | 497.9667 | 0.001523 | 3.0584e-06 | Restore Supply on Device T1351 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 822512 | Faultman found a floating wires and a broken 11KV insualtor on pole 822512, line was isolated at Fuses 7635 to replace the insulator and rebind in conductor at 2 other poles. This job any be a 2 R. 1 X 11KV insulator replaced and 4 X binders used. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 497.9667 | 494.9667 | 494.9667 | 0.0015118 | 3.0544e-06 | 2014-11-15 | C | 0.0015118 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.0015118 | 3.0544e-06
1 | 3051416 | 2014-11-15 13:37 | 2014-11-15 15:18 | 100.9333 | 229 | 23113.7333 | 0.070692 | 0.00070038 | Restore Supply on Device T21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P47104 | NOC opened CB T21. Lines repaired at pole P47104. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100.9333 | 97.9333 | 22426.7333 | 0.068501 | 0.00069946 | 2014-11-15 | C | 0.068501 | 0.00069946 | 2015 | 2014-11-15 | C | 229 | 0.068501 | 0.00069946
1 | 3052039 | 2014-11-15 13:59 | 2014-11-15 19:22 | 323.5 | 1 | 323.5 | 0.0009894 | 3.0584e-06 | Restore Supply on Device T442 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | links # 7318 | replace 10 amp ddo fuse. 1 out of 2 phases. links # 7318. cause: wind. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 323.5 | 320.5 | 320.5 | 0.00097894 | 3.0544e-06 | 2014-11-15 | C | 0.00097894 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.00097894 | 3.0544e-06
1 | 3052287 | 2014-11-15 14:28 | 2014-11-15 16:38 | 130.0667 | 67 | 652.5667 | 0.0019958 | 0.00020491 | Restore Supply on Device C223 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 327277 | No Power. Line patrolled and CB C223 found open. CB C223 closed and tripped. Repaired binders at pole 327277. Brian Butler attended. Materials used: 2 x Binders. Refer to OMS Job ID 3052645 for restoration post tripping. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 9.7398 | 6.7398 | 451.5667 | 0.0013793 | 0.00020465 | 2014-11-15 | C | 0.0013793 | 0.00020465 | 2015 | 2014-11-15 | C | 67 | 0.0013793 | 0.00020465
1 | 3052529 | 2014-11-15 16:25 | 2014-11-15 20:48 | 262.6833 | 1 | 262.6833 | 0.0008034 | 3.0584e-06 | Restore Supply on Device X2462 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4189 | Replaced 2 x 6A HV fuses. All other assets appear okay; nothing else replaced. email to Jo to check SAIDI component | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 262.6833 | 259.6833 | 259.6833 | 0.00079318 | 3.0544e-06 | 2014-11-15 | C | 0.00079318 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.00079318 | 3.0544e-06
1 | 3052645 | 2014-11-15 16:38 | 2014-11-15 18:34 | 116 | 40 | 4640 | 0.014191 | 0.00012234 | Restore Supply on Device 7029 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 327277 | 18/11 SAM SIGNING OFF JOBS AS BEN HAS LEFT THE COMPANY AND NOT SIGNED OFF SOME OF HIS JOBS POWER RESTORED WHEN BEN ARRIVED SAM WILL TRY AND GET MORE INFORMATION SAM ADVISED THIS WAS PART OF FEEDER FAULT SO I AGREED TO SIGN THIS OFF SAM IS TRYING TO | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 116 | 113 | 4520 | 0.013806 | 0.00012218 | 2014-11-15 | C | 0.013806 | 0.00012218 | 2015 | 2014-11-15 | C | 40 | 0.013806 | 0.00012218
1 | 3053246 | 2014-11-15 17:51 | 2014-11-15 21:18 | 206.6667 | 176 | 34615.1667 | 0.10587 | 0.00053828 | Restore Supply on Device CB3 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P04331 | CB 3 tripped on B & C phase O/C flags, line was sectionalised and patrolled and a branch was found on the lines at pole P04331, branch was removed with hot line sticks. Les Robinson and Phil Barnes attended. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 196.6771 | 193.6771 | 34087.1667 | 0.10412 | 0.00053758 | 2014-11-15 | C | 0.10412 | 0.00053758 | 2015 | 2014-11-15 | C | 176 | 0.10412 | 0.00053758
1 | 3095032 | 2014-11-15 18:06 | 2014-11-15 19:18 | 72 | 26 | 1872 | 0.0057254 | 7.9519e-05 | Restore Supply on Device I41 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P08551 | Replace Dead End and Repair Jumper at Pole P08551. Materials Used: 1 x Gopher dead end and 1 x jumper. Robin Smith and Andrew Tahura attended. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 1794 | 0.0054796 | 7.9415e-05 | 2014-11-15 | C | 0.0054796 | 7.9415e-05 | 2015 | 2014-11-15 | C | 26 | 0.0054796 | 7.9415e-05
1 | 3053567 | 2014-11-15 18:07 | 2014-11-15 22:41 | 273.9833 | 431 | 59877.4 | 0.18313 | 0.0013182 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | Pole 200451 | CB 2 tripped to L/O - line sectionalised & patrolled - tree found through line at pole ---- with broken HV & LV conductors - isolation points for repairs were ABS SD3-014, SD3-148, SD3-118 - report of burning switchboard reported at 164 Crawford Rd soon a | F4 | WAIROA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 138.9267 | 135.9267 | 58584.4 | 0.17894 | 0.0013165 | 2014-11-15 | C | 0.17894 | 0.0013165 | 2015 | 2014-11-15 | C | 431 | 0.17894 | 0.0013165
1 | 3055010 | 2014-11-15 20:18 | 2014-11-15 22:36 | 138.0333 | 658 | 35647.9333 | 0.10903 | 0.0020124 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Omokoroa Sub | CB 1 tripped to L/O - report of explosion at substation being heard by neighbour at time of tripping - backfeed established from recloser 9805/2 to ABS SD3-002 while thorough checks were made at cable termination etc at sub - nothing found and all supply | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 54.1762 | 51.1762 | 33673.9333 | 0.10285 | 0.0020098 | 2014-11-15 | C | 0.10285 | 0.0020098 | 2015 | 2014-11-15 | C | 658 | 0.10285 | 0.0020098
1 | 3055678 | 2014-11-15 20:24 | 2014-11-15 23:17 | 172.6667 | 1 | 172.6667 | 0.00052809 | 3.0584e-06 | Restore Supply on Device X1186 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | X1186 | Faultman replaced fuse on X1186. 1 X 2 amp HV rewirable fuse used. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 172.6667 | 169.6667 | 169.6667 | 0.00051823 | 3.0544e-06 | 2014-11-15 | C | 0.00051823 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.00051823 | 3.0544e-06
1 | 3056200 | 2014-11-15 20:57 | 2014-11-16 16:39 | 1181.9667 | 1 | 1181.9667 | 0.003615 | 3.0584e-06 | Restore Supply on Device TC2-094 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2-094 | 11:15am 1R Line Crew required to help As HV jumper off ABS 10/12 emailed svs hub to get faultman to call to clear job repaired ABS - Took photos ( ABS is around the back of the Aongatete Sub Station ) Photos have been sent through on job card on th | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 1181.9667 | 1178.9667 | 1178.9667 | 0.0036011 | 3.0544e-06 | 2014-11-15 | C | 0.0036011 | 3.054e-06 | 2015 | 2014-11-15 | C | 1 | 0.0036011 | 3.0544e-06
1 | 3056211 | 2014-11-15 21:03 | 2014-11-16 13:57 | 1014.05 | 3 | 3042.15 | 0.0093042 | 9.1753e-06 | Restore Supply on Device T2931 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2931 | 10:15am 2R request Transformer Replacement replaced transformer and. nothing else repaired or replaced, adjacent assets up to powerco standard. NDR#37805 | F2 | HOLDSWORTH | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1014.05 | 1011.05 | 3033.15 | 0.0092645 | 9.1633e-06 | 2014-11-15 | C | 0.0092645 | 9.163e-06 | 2015 | 2014-11-15 | C | 3 | 0.0092645 | 9.1633e-06
1 | 3056623 | 2014-11-16 06:55 | 2014-11-16 15:56 | 541.3333 | 4 | 1903.7833 | 0.0058226 | 1.2234e-05 | Restore Supply on Device T9/130 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | p01430 | all related 2x 10 amp ddo p01430 hv oh due to wind line clash nothing else surrounding all good. Email sent to JO, as appears could have a SAIDI component. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 475.9458 | 472.9458 | 1891.7833 | 0.0057783 | 1.2218e-05 | 2014-11-16 | C | 0.0057783 | 1.2218e-05 | 2015 | 2014-11-16 | C | 4 | 0.0057783 | 1.2218e-05
1 | 3056711 | 2014-11-16 08:55 | 2014-11-16 15:21 | 386.1833 | 228 | 36377.35 | 0.11126 | 0.00069732 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 859494 | Recloser 9636 L/O. Sectionalised and found broken insulator on pole 859494. Isolated at fuses FP894. Replaced & re livened | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 159.5498 | 156.5498 | 35693.35 | 0.10902 | 0.00069641 | 2014-11-16 | C | 0.10902 | 0.00069641 | 2015 | 2014-11-16 | C | 228 | 0.10902 | 0.00069641
1 | 2867727 | 2014-11-16 10:05 | 2014-11-16 10:39 | 34.8 | 1 | 34.8 | 0.00010643 | 3.0584e-06 | NAPA ID:03679 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/593 | Make a gap at T6/593 then liven so more work can be done on isolated cable. Works location: Malden St WO 10139616 | F2 | ARMSTRONG ST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 34.8 | 31.8 | 31.8 | 9.7131e-05 | 3.0544e-06 | 2014-11-16 | B | 4.8565e-05 | 1.527e-06 | 2015 | 2014-11-16 | B | 1 | 9.7131e-05 | 3.0544e-06
1 | 3057819 | 2014-11-16 13:11 | 2014-11-16 16:02 | 170.7833 | 85 | 14487.8 | 0.04431 | 0.00025997 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC2-029 | Found centre phase burning on ABS SC2-029. Isolated between ABS SC2-013 & CB 5. Backfeed rest of area. Repaired connection and replaced faulty insulators, re livened | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 170.4447 | 167.4447 | 14232.8 | 0.043473 | 0.00025963 | 2014-11-16 | C | 0.043473 | 0.00025963 | 2015 | 2014-11-16 | C | 85 | 0.043473 | 0.00025963
1 | 3058639 | 2014-11-16 18:21 | 2014-11-16 19:23 | 61.5833 | 11 | 677.4167 | 0.0020718 | 3.3643e-05 | Restore Supply on Device T9/201 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | pole 857970 | replaced 2x Pin Insulators & 2X Binders. No other assets repaired or replaced on site. FM checked adjacent and all up to Powerco Standard. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 61.5833 | 58.5833 | 644.4167 | 0.0019683 | 3.3599e-05 | 2014-11-16 | C | 0.0019683 | 3.3599e-05 | 2015 | 2014-11-16 | C | 11 | 0.0019683 | 3.3599e-05
1 | 3058826 | 2014-11-16 21:00 | 2014-11-16 23:18 | 138 | 84 | 11592 | 0.035453 | 0.00025691 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | cb 10 | part of napa 3898 | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 138 | 135 | 11340 | 0.034637 | 0.00025657 | 2014-11-16 | C | 0.034637 | 0.00025657 | 2015 | 2014-11-16 | C | 84 | 0.034637 | 0.00025657
1 | 3058797 | 2014-11-17 06:20 | 2014-11-17 09:23 | 182.5833 | 1 | 182.5833 | 0.00055842 | 3.0584e-06 | Restore Supply on Device L4115 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole # 727055 | replace 2 amp ddo fuse at pole # 727055. 1 out of 3 phases. cause: unknown. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. FM advise oms 3059775 is related. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 182.5833 | 179.5833 | 179.5833 | 0.00054852 | 3.0544e-06 | 2014-11-17 | C | 0.00054852 | 3.054e-06 | 2015 | 2014-11-17 | C | 1 | 0.00054852 | 3.0544e-06
1 | 2861476 | 2014-11-17 08:31 | 2014-11-17 12:26 | 235.1667 | 32 | 7525.3333 | 0.023016 | 9.787e-05 | NAPA ID:03837 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6525 | Change poles or Wire run. Works location: Whenuku Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.1667 | 232.1667 | 7429.3333 | 0.022692 | 9.7742e-05 | 2014-11-17 | B | 0.011346 | 4.8871e-05 | 2015 | 2014-11-17 | B | 32 | 0.022692 | 9.7742e-05
1 | 2867226 | 2014-11-17 09:00 | 2014-11-17 15:20 | 379.65 | 91 | 34548.15 | 0.10566 | 0.00027832 | NAPA ID:03846 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF3-005 | REPLACE POLE AND ARMS AS PER SCOPE. Works location: Pyes Pa Rd Taumata Rd WO 10138318 | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 379.65 | 376.65 | 34275.15 | 0.10469 | 0.00027795 | 2014-11-17 | B | 0.052345 | 0.00013898 | 2015 | 2014-11-17 | B | 91 | 0.10469 | 0.00027795
1 | 2861531 | 2014-11-17 09:16 | 2014-11-17 13:45 | 269.4333 | 26 | 7005.2667 | 0.021425 | 7.9519e-05 | NAPA ID:02488 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 875 | Replace 11kv arms. Works location: Hildreth Rd Putaruru WO 468783 | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 269.4333 | 266.4333 | 6927.2667 | 0.021159 | 7.9415e-05 | 2014-11-17 | B | 0.010579 | 3.9708e-05 | 2015 | 2014-11-17 | B | 26 | 0.021159 | 7.9415e-05
1 | 2872816 | 2014-11-17 09:17 | 2014-11-17 12:46 | 209.0833 | 14 | 2927.1667 | 0.0089525 | 4.2818e-05 | NAPA ID:04005 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV SC3-027 | Maintenance on 11kv Linkbox. Works location: Bruntwood Drive WO 10151195 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 209.0833 | 206.0833 | 2885.1667 | 0.0088125 | 4.2762e-05 | 2014-11-17 | B | 0.0044063 | 2.1381e-05 | 2015 | 2014-11-17 | B | 14 | 0.0088125 | 4.2762e-05
1 | 3065579 | 2014-11-17 09:22 | 2014-11-17 12:10 | 168 | 235 | 16922 | 0.051755 | 0.00071873 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 727383 | LIV CB LI 1 tripped E/F, L/O. Feeder sectionalised & fault found beyound Fuses LI 192 ( no back feeds ), all service restored to remainder of feeder. 11kV insulator at pole 727383 x 1 replaced all service restored, P Webby & C Katene attended | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 72.0085 | 69.0085 | 16217 | 0.049534 | 0.00071779 | 2014-11-17 | C | 0.049534 | 0.00071779 | 2015 | 2014-11-17 | C | 235 | 0.049534 | 0.00071779
1 | 2690182 | 2014-11-17 09:40 | 2014-11-17 13:54 | 254.4 | 17 | 4324.8 | 0.013227 | 5.1993e-05 | NAPA ID:03902 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS M38 | DNO 141021. NDR 046502 Replace ABs handle onM38 can only happen on Mondays and upgrade T3/224 Structure as well.M38 is wedged shut. Works location: Halcombe/Kakariki Rd NDR 046502 | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 254.4 | 251.4 | 4273.8 | 0.013054 | 5.1925e-05 | 2014-11-17 | B | 0.006527 | 2.5963e-05 | 2015 | 2014-11-17 | B | 17 | 0.013054 | 5.1925e-05
1 | 3076063 | 2014-11-17 10:50 | 2014-11-17 15:52 | 302.3667 | 478 | 48908.9167 | 0.14958 | 0.0014619 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 757442 | OAK CB6 tripped E/F, L/O Feeder sectionalised & faulty insulator found at pole 757442 between ABS's 414 & 382 with back feed via ABS 52. Insulator replaced all service restored Neil Woodhead & Jade Williams attended. Materials 1 x h/v pin insulatoe & 1 x | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 102.3199 | 99.3199 | 47474.9167 | 0.14501 | 0.00146 | 2014-11-17 | C | 0.14501 | 0.00146 | 2015 | 2014-11-17 | C | 478 | 0.14501 | 0.00146
1 | 3076531 | 2014-11-17 10:56 | 2014-11-17 11:52 | 55.8 | 15 | 837 | 0.0025599 | 4.5876e-05 | Restore Supply on Device V77 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole P04220 | Bit of Tree on line Removed with Hot Stick isolated for saftey due to Conductor being No 8 Wire | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55.8 | 52.8 | 792 | 0.0024191 | 4.5816e-05 | 2014-11-17 | C | 0.0024191 | 4.5816e-05 | 2015 | 2014-11-17 | C | 15 | 0.0024191 | 4.5816e-05
1 | 3082018 | 2014-11-17 11:23 | 2014-11-17 16:04 | 281.4167 | 56 | 2529.3333 | 0.0077358 | 0.00017127 | Restore Supply on Device U31 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole P30078 | Close up Temp Line break at Pole P28872 after carrying out repairs. | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 45.1667 | 42.1667 | 2361.3333 | 0.0072125 | 0.00017105 | 2014-11-17 | C | 0.0072125 | 0.00017105 | 2015 | 2014-11-17 | C | 56 | 0.0072125 | 0.00017105
1 | 3081529 | 2014-11-17 13:54 | 2014-11-17 23:00 | 546.2 | 19 | 10377.8 | 0.03174 | 5.811e-05 | Restore Supply on Device 8734 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | tx L3020. | possible hv u/g fault to tx L3020. Chris going home. Hub advise Blair Greg calling Chris to deal with this fault. Chris has isolated HV u/g - I advised him that he should be working through control for that & he said he has a lot to do. Chris wanted a | F4 | PATEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 546.2 | 543.2 | 10320.8 | 0.031524 | 5.8034e-05 | 2014-11-17 | C | 0.031524 | 5.8034e-05 | 2015 | 2014-11-17 | C | 19 | 0.031524 | 5.8034e-05
1 | 3082003 | 2014-11-17 15:09 | 2014-11-18 01:25 | 615.6 | 1 | 615.6 | 0.0018828 | 3.0584e-06 | Restore Supply on Device T154 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 309 Homewood Road, Matapapa, Masterton | 17/11 4.45pm - Customer advise: This is a woolshed in 309 Homewood Road. He noticed a "lever" down at the pole next to the pumpshed that is by this woolshed. There is also 2 silos by the woolshed. Incorrect address provided by Nova. Customer advise he has | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 615.6 | 612.6 | 612.6 | 0.0018711 | 3.0544e-06 | 2014-11-17 | C | 0.0018711 | 3.054e-06 | 2015 | 2014-11-17 | C | 1 | 0.0018711 | 3.0544e-06
1 | 3088707 | 2014-11-17 17:14 | 2014-11-17 20:58 | 224.1833 | 1 | 224.1833 | 0.00068565 | 3.0584e-06 | Restore Supply on Device 908 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | tx 908 | replace 8 amp link. cause: deterioration, broken. tx 908. 1 out of 3 phases. | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 224.1833 | 221.1833 | 221.1833 | 0.00067559 | 3.0544e-06 | 2014-11-17 | C | 0.00067559 | 3.054e-06 | 2015 | 2014-11-17 | C | 1 | 0.00067559 | 3.0544e-06
1 | 3091580 | 2014-11-17 19:58 | 2014-11-17 22:04 | 126 | 31 | 3906 | 0.011946 | 9.4811e-05 | Restore Supply on Device 407 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 645 dover rd | repair line @ pole 758083 | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 126 | 123 | 3813 | 0.011647 | 9.4687e-05 | 2014-11-17 | C | 0.011647 | 9.4687e-05 | 2015 | 2014-11-17 | C | 31 | 0.011647 | 9.4687e-05
1 | 3090444 | 2014-11-18 04:46 | 2014-11-18 09:10 | 264.7667 | 416 | 18532.0833 | 0.056679 | 0.0012723 | Restore Supply on Device C937 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 378918 | RS C224 A/R, L/O, E/F, O/C B & C Phase. Sectionalised & Patrolled. Fault found to be tree through lines. REPLACED 30 METRES CONDUCTOR ON ONE SPAN AND RESAGGED 2 SPANS. BETWEEN POLE 378918 AND 378919 AND 2 JOINTS. WORKED THROUGH CONTROL | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 44.5483 | 41.5483 | 17284.0833 | 0.052793 | 0.0012706 | 2014-11-18 | C | 0.052793 | 0.0012706 | 2015 | 2014-11-18 | C | 416 | 0.052793 | 0.0012706
1 | 2881756 | 2014-11-18 08:15 | 2014-11-18 11:40 | 205 | 43 | 8815 | 0.02696 | 0.00013151 | NAPA ID:04032 TP_MATAROA GXP > WAIOURU SUB > IRIRANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1718 | Install new ABS 4718 on pole 358165 Turakina Valley Road Taihape. Works location: Turakina Valley Rd/Waiaruhe Rd. WO 10141785 | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 205 | 202 | 8686 | 0.026531 | 0.00013134 | 2014-11-18 | B | 0.013265 | 6.567e-05 | 2015 | 2014-11-18 | B | 43 | 0.026531 | 0.00013134
1 | 2914340 | 2014-11-18 08:20 | 2014-11-18 13:32 | 311.75 | 103 | 32110.25 | 0.098207 | 0.00031502 | NAPA ID:03964 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4301 | Upgrade customer transformer to 3 phase add new DDO into line @ TC4301 and utilise shut to Replace insulators on delta line from pole #03932. Works location: Back Miranda Rd WO 10156514 | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 311.75 | 308.75 | 31801.25 | 0.097134 | 0.00031461 | 2014-11-18 | B | 0.048567 | 0.0001573 | 2015 | 2014-11-18 | B | 103 | 0.097134 | 0.00031461
1 | 3092215 | 2014-11-18 08:56 | 2014-11-18 10:26 | 89.8833 | 231 | 11423.1333 | 0.034937 | 0.0007065 | Restore Supply on Device T21 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Transformer T7/334 | Tripping on Recloser T21 on EF1. Area patrolled with blown jumper found at Transformer T7/334. Isolation from Fuses T26 with remainder of freeder restored. Broken jumper repaired / relivened OK. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 49.4508 | 46.4508 | 10730.1333 | 0.032774 | 0.00070557 | 2014-11-18 | C | 0.032774 | 0.00070557 | 2015 | 2014-11-18 | C | 231 | 0.032774 | 0.00070557
1 | 2913164 | 2014-11-18 08:58 | 2014-11-18 16:26 | 448.5333 | 48 | 21529.6 | 0.065847 | 0.0001468 | NAPA ID:03839 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 201410 | REMOVE 11KV CABLES FROM POLE 201410 GB JOINT CABLE OFF POLE TO NEW CABLE FROM SAFE LINK CFCC9858/4 AP REMOVE CABLE FROM TX TB2-017 FROM DDO OFF POLE 201460 AND TERMINATE INTO SWICT 9858/2. TEST CABLES TP LIVEN FROM 9765/1 TEMP [BACK FEED FOR THE NIGHT | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 448.5333 | 445.5333 | 21385.6 | 0.065321 | 0.00014661 | 2014-11-18 | B | 0.03266 | 7.3306e-05 | 2015 | 2014-11-18 | B | 48 | 0.065321 | 0.00014661
1 | 2911523 | 2014-11-18 09:01 | 2014-11-18 15:10 | 369.5667 | 29 | 10717.4333 | 0.032778 | 8.8694e-05 | NAPA ID:02610 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD5-016 | Replace poles between ABS SD5-016 and ABS SD5-033. Works location: Kairua Rd WO TA/2014/23 IR6817 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 369.5667 | 366.5667 | 10630.4333 | 0.03247 | 8.8578e-05 | 2014-11-18 | B | 0.016235 | 4.4289e-05 | 2015 | 2014-11-18 | B | 29 | 0.03247 | 8.8578e-05
1 | 3091234 | 2014-11-18 09:09 | 2014-11-18 09:51 | 41.85 | 631 | 26407.35 | 0.080765 | 0.0019299 | Restore Supply on Device TC1977 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Transformer TC1977 | at 09:06 Whitianga Sub, CB 4 Coroglen Feeder. Faultman dispatched to no power job. Found blown jump at Transformer TC1977, Pole W13653. Isolated lines at ABS IP449 & 340. Permit issued and repairs carried out. All power restored on completion. No Material | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 41.85 | 38.85 | 24514.35 | 0.074877 | 0.0019273 | 2014-11-18 | C | 0.074877 | 0.0019273 | 2015 | 2014-11-18 | C | 631 | 0.074877 | 0.0019273
1 | 2911528 | 2014-11-18 09:18 | 2014-11-18 10:00 | 42.2833 | 7 | 295.9833 | 0.00090524 | 2.1409e-05 | NAPA ID:03903 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1501 | Replace Transformer TC1501. Works location: Thames Coast WO 10162275 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 42.2833 | 39.2833 | 274.9833 | 0.00083992 | 2.1381e-05 | 2014-11-18 | B | 0.00041996 | 1.069e-05 | 2015 | 2014-11-18 | B | 7 | 0.00083992 | 2.1381e-05
1 | 2861511 | 2014-11-18 09:30 | 2014-11-18 14:00 | 270 | 4 | 1080 | 0.0033031 | 1.2234e-05 | NAPA ID:02764 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6.6kV Fuses 2510 | Replace all HV and LV crossarms on surrey rd inglewood 6.6kv lines. Works location: Surrey Rd Tariki Inglewood WO 10150398 | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 270 | 267 | 1068 | 0.0032621 | 1.2218e-05 | 2014-11-18 | B | 0.0016311 | 6.109e-06 | 2015 | 2014-11-18 | B | 4 | 0.0032621 | 1.2218e-05
1 | 1855744 | 2014-11-18 09:54 | 2014-11-18 13:50 | 236.7833 | 41 | 9708.1167 | 0.029692 | 0.0001254 | NAPA ID:02304 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 378 | Replace 33kv xarms and broken 33kv insulators on carrington no. 2 line. Works location: Smart Rd WO 10144419 Switching commenced on SIS 2304 resulting in sub trip at item 6 - refer OMS number 2064214 & safety manager number 403002 - pre arranged work | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 236.7833 | 233.7833 | 9585.1167 | 0.029277 | 0.00012523 | 2014-11-18 | B | 0.014639 | 6.2616e-05 | 2015 | 2014-11-18 | B | 41 | 0.029277 | 0.00012523
1 | 2861584 | 2014-11-18 09:57 | 2014-11-18 14:31 | 273.6333 | 40 | 10945.3333 | 0.033475 | 0.00012234 | NAPA ID:03810 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS WH217 | Install x arms & replace DNO 140703 11Kv Abs WH217. Works location: Ohangai Rd WO 10159746 | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 273.6333 | 270.6333 | 10825.3333 | 0.033065 | 0.00012218 | 2014-11-18 | B | 0.016533 | 6.1088e-05 | 2015 | 2014-11-18 | B | 40 | 0.033065 | 0.00012218
1 | 3095363 | 2014-11-18 11:58 | 2014-11-18 16:11 | 253.3667 | 7 | 1089.95 | 0.0033335 | 2.1409e-05 | Restore Supply on Device W5075 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 843469 | 2R REQUESTED POLE 843469 HV REQUIRED X ARM REPLACEMENT FM NOW LEAVING SITE AND ANOTHER CREW WILL ATTEND. Arm replaced all service restored, Kane McKay attended. Materials 1 X double term arm & 2 x h/v insulators. Emailed Jo, as appears could have SAIDI | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 155.7071 | 152.7071 | 1068.95 | 0.003265 | 2.1381e-05 | 2014-11-18 | C | 0.003265 | 2.1381e-05 | 2015 | 2014-11-18 | C | 7 | 0.003265 | 2.1381e-05
1 | 3095369 | 2014-11-18 12:09 | 2014-11-19 07:29 | 1160.6667 | 3 | 1748.6833 | 0.0053482 | 9.1753e-06 | Restore Supply on Device T2/938 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TX2/938 | TREES IN LINE AFFECTING SETTER LINE AND NEWBURY LINE FM PHONING TREESCAPE AS TREES ON THREE PROPERTIES NEED TO BE TRIMMED BEFORE POWER CAN GO BACK ON TX2/938. 1.55 TREE SCAPE ON WAY TO TRIM TREES FM LEAVING SITE FM GAVE HIS PHONE NUMBER. Transformer back | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 582.8944 | 579.8944 | 1739.6833 | 0.0053137 | 9.1633e-06 | 2014-11-18 | C | 0.0053137 | 9.163e-06 | 2015 | 2014-11-18 | C | 3 | 0.0053137 | 9.1633e-06
1 | 3095379 | 2014-11-18 12:19 | 2014-11-18 14:40 | 141.65 | 8 | 1133.2 | 0.0034658 | 2.4467e-05 | Restore Supply on Device TD2-083 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses SD2-021 | head loud explosion from pole opposite 60A Ross Road, suspect breaker blown - customer still has power opp - advised Joanne at svs hub Clint Johnstone Attended. Found 2x Blown HV Fuses at SD2-021. Reloaded, Relivened - All Power Restored OK. 2x HV Fuses | F4 | WHAKAMARAMA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 141.65 | 138.65 | 1109.2 | 0.003388 | 2.4435e-05 | 2014-11-18 | C | 0.003388 | 2.4435e-05 | 2015 | 2014-11-18 | C | 8 | 0.003388 | 2.4435e-05
1 | 1926773 | 2014-11-18 12:57 | 2014-11-18 13:53 | 56 | 233 | 13048 | 0.039906 | 0.00071261 | Restore Supply on Device 254 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB14 | Replace Switchgear 383,384 & 385. | F3 | RESIDENTIAL | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56 | 53 | 12349 | 0.037719 | 0.00071168 | 2014-11-18 | C | 0.037719 | 0.00071168 | 2015 | 2014-11-18 | C | 233 | 0.037719 | 0.00071168
1 | 3092846 | 2014-11-18 14:52 | 2014-11-18 17:40 | 167.8 | 16 | 2114.2167 | 0.0064662 | 4.8935e-05 | Restore Supply on Device T1989 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 798672 | pole number 798672 BROKEN POLE 11KV POLE NEEDS BUCKET TRUCK AN EQUIPMENT BOUGHT TO SITE REQUESTED 2R FM LEAVING SITE AND ANOTHER CREW WILL REPLACE THE POLE WHAT CAUSED THIS POLE TO BREAK AGE HOW MANY CUSTOMERS 9 11KV LINK 7292. 11kV Outage require | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 132.1385 | 129.1385 | 2066.2167 | 0.0063111 | 4.8871e-05 | 2014-11-18 | C | 0.0063111 | 4.8871e-05 | 2015 | 2014-11-18 | C | 16 | 0.0063111 | 4.8871e-05
1 | 3096604 | 2014-11-18 15:37 | 2014-11-18 15:56 | 18.5833 | 207 | 3846.75 | 0.011765 | 0.00063309 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Rec 9198 | Recloser 9198 tripped, L/O ( BRD 5 ) ( no flags ) Recloser closed after 20 min patrolled no fault found, Don Masters attended. | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 18.5833 | 15.5833 | 3225.75 | 0.0098528 | 0.00063227 | 2014-11-18 | C | 0.0098528 | 0.00063227 | 2015 | 2014-11-18 | C | 207 | 0.0098528 | 0.00063227
1 | 3096823 | 2014-11-18 15:51 | 2014-11-18 18:32 | 161.0333 | 941 | 33297.2667 | 0.10184 | 0.002878 | Restore Supply on Device 22 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | Pole P42377 | CB 22 A/R, L/O, E/F. Partial Backfeed installed by opening RS 10183 & closing VS 10182. Started sectionalising until call came in of Line Down and a shock recieved by consumer off of Meterboard (See OMS 3097953). This was due to broken tree branch fallin | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 35.385 | 32.385 | 30474.2667 | 0.093081 | 0.0028742 | 2014-11-18 | C | 0.093081 | 0.0028742 | 2015 | 2014-11-18 | C | 941 | 0.093081 | 0.0028742
1 | 3096436 | 2014-11-18 16:41 | 2014-11-18 17:14 | 32.9167 | 19 | 625.4167 | 0.0019128 | 5.811e-05 | Restore Supply on Device T7/32 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Fuses R15 | 2 HT Fuses found tripped at R15. Patrolled, reclosed OK. Suspect line clash. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32.9167 | 29.9167 | 568.4167 | 0.0017362 | 5.8034e-05 | 2014-11-18 | C | 0.0017362 | 5.8034e-05 | 2015 | 2014-11-18 | C | 19 | 0.0017362 | 5.8034e-05
1 | 3098467 | 2014-11-18 17:55 | 2014-11-18 21:29 | 213.4833 | 111 | 11745.1333 | 0.035922 | 0.00033948 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 798386 | Used 10 m Conductor & 4 Selvees Isolation points ABS S526 ABS S505 & Fused ABS 8043 | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 105.812 | 102.812 | 11412.1333 | 0.034857 | 0.00033904 | 2014-11-18 | C | 0.034857 | 0.00033904 | 2015 | 2014-11-18 | C | 111 | 0.034857 | 0.00033904
1 | 3096482 | 2014-11-18 18:34 | 2014-11-18 19:38 | 64.5167 | 26 | 1677.4333 | 0.0051303 | 7.9519e-05 | Restore Supply on Device 3706T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer 3706T | Used 1 X DDO at transformer3706T | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 64.5167 | 61.5167 | 1599.4333 | 0.0048853 | 7.9415e-05 | 2014-11-18 | C | 0.0048853 | 7.9415e-05 | 2015 | 2014-11-18 | C | 26 | 0.0048853 | 7.9415e-05
1 | 2912250 | 2014-11-18 20:01 | 2014-11-18 21:57 | 116.3167 | 1 | 116.3167 | 0.00035575 | 3.0584e-06 | NAPA ID:04036 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > OMANU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4-324 | Isolation 11kv cables-clean Terms & HV bushings of TC4-324. Works location: Bayfair Shopping Centre WO 10162469 | F3 | OMANU | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 116.3167 | 113.3167 | 113.3167 | 0.00034612 | 3.0544e-06 | 2014-11-18 | B | 0.00017306 | 1.527e-06 | 2015 | 2014-11-18 | B | 1 | 0.00034612 | 3.0544e-06
1 | 3098976 | 2014-11-19 04:59 | 2014-11-19 06:14 | 74.6333 | 1 | 74.6333 | 0.00022826 | 3.0584e-06 | Restore Supply on Device 4323T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Fuses 6203 | 2 X 6 amp H/t Fuses. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 74.6333 | 71.6333 | 71.6333 | 0.0002188 | 3.0544e-06 | 2014-11-19 | C | 0.0002188 | 3.054e-06 | 2015 | 2014-11-19 | C | 1 | 0.0002188 | 3.0544e-06
1 | 2869101 | 2014-11-19 05:30 | 2014-11-19 06:01 | 31.0667 | 1 | 31.0667 | 9.5015e-05 | 3.0584e-06 | NAPA ID:03685 TP_BUNNYTHORPE GXP > MILSON SUB > FAIRS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | nT6/593 | Close line break at T6/593 then liven SG 10224. Works location: Malden St. WO 10139616 | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 31.0667 | 28.0667 | 28.0667 | 8.5727e-05 | 3.0544e-06 | 2014-11-19 | B | 4.2864e-05 | 1.527e-06 | 2015 | 2014-11-19 | B | 1 | 8.5727e-05 | 3.0544e-06
1 | 3098983 | 2014-11-19 06:16 | 2014-11-19 11:32 | 316.1667 | 121 | 21326.9667 | 0.065227 | 0.00037007 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P00465 | Auto-reclose on Recloser V27 on E/F A Phase. Line patrolled, reclosed OK. High winds. please check if contact attached has power restored found at p00465, replaced 6x binders and 1x insulator on this pole which is 15km away from next pole p007 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 176.2559 | 173.2559 | 20963.9667 | 0.064033 | 0.00036959 | 2014-11-19 | C | 0.064033 | 0.00036959 | 2015 | 2014-11-19 | C | 121 | 0.064033 | 0.00036959
1 | 3100221 | 2014-11-19 07:01 | 2014-11-19 10:06 | 185.0333 | 292 | 61438.05 | 0.1879 | 0.00089306 | Restore Supply on Device T321 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | as per | possibly related to OMS#3100203 Line patrolled, no fault found. Suspect line clash in high winds | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 210.4043 | 207.4043 | 60562.05 | 0.18498 | 0.00089189 | 2014-11-19 | C | 0.18498 | 0.00089189 | 2015 | 2014-11-19 | C | 292 | 0.18498 | 0.00089189
1 | 3100209 | 2014-11-19 08:27 | 2014-11-19 11:58 | 210.5167 | 69 | 2036.5167 | 0.0062285 | 0.00021103 | Restore Supply on Device T516 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Akura C223 | Akura CB C223 tripped. No flags. Line not patrolled - Line clash suspected. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 29.5147 | 26.5147 | 1829.5167 | 0.0055881 | 0.00021076 | 2014-11-19 | C | 0.0055881 | 0.00021075 | 2015 | 2014-11-19 | C | 69 | 0.0055881 | 0.00021076
1 | 2894508 | 2014-11-19 08:40 | 2014-11-19 14:48 | 367.5833 | 57 | 5261.7833 | 0.016093 | 0.00017433 | NAPA ID:04008 TP_HAWERA GXP > CAMBRIA SUB > GLOVER RD WEST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV transformer W5345 | Replace two pole structure W5345 with a single pole 100kva transformer. Works location: Glover Rd Hawera WO 10151961 | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 92.312 | 89.312 | 5090.7833 | 0.015549 | 0.0001741 | 2014-11-19 | B | 0.0077747 | 8.7051e-05 | 2015 | 2014-11-19 | B | 57 | 0.015549 | 0.0001741
1 | 2872792 | 2014-11-19 08:45 | 2014-11-19 14:59 | 373.9833 | 12 | 4487.8 | 0.013726 | 3.6701e-05 | NAPA ID:03742 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12175 | Replace crossarms between poles P12175 and P23226. Replace TX T5/214 with a new one. Works location: Beaconsfield Valley Rd WO 10160678 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 373.9833 | 370.9833 | 4451.8 | 0.013598 | 3.6653e-05 | 2014-11-19 | B | 0.0067988 | 1.8327e-05 | 2015 | 2014-11-19 | B | 12 | 0.013598 | 3.6653e-05
1 | 2894351 | 2014-11-19 08:46 | 2014-11-19 13:14 | 267.8667 | 32 | 8571.7333 | 0.026216 | 9.787e-05 | NAPA ID:03841 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6525 | Change poles or Wire run. Works location: Whenuku Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 267.8667 | 264.8667 | 8475.7333 | 0.025888 | 9.7742e-05 | 2014-11-19 | B | 0.012944 | 4.8871e-05 | 2015 | 2014-11-19 | B | 32 | 0.025888 | 9.7742e-05
1 | 2912303 | 2014-11-19 09:00 | 2014-11-19 15:30 | 390 | 22 | 8580 | 0.026241 | 6.7285e-05 | NAPA ID:03665 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 221455 | REPLACE RC POLE 221455 REPLACE POLES AND ARMS AS PER SCOPE REMOVE TEMP LINKS 19 IN THIS SHUT. Works location: Te Matai Rd WO 10154633 IR5996 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 390 | 387 | 8514 | 0.026005 | 6.7197e-05 | 2014-11-19 | B | 0.013003 | 3.3599e-05 | 2015 | 2014-11-19 | B | 22 | 0.026005 | 6.7197e-05
1 | 2915191 | 2014-11-19 09:09 | 2014-11-19 17:43 | 513.6833 | 1 | 513.6833 | 0.0015711 | 3.0584e-06 | NAPA ID:04122 TP_HUIRANGI GXP > MCKEE SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Mckee Sub | 3/6 Yearly 33kV & 11kV ABS maint. Moving new TR5 onto newly constructed pad, on location where TR6 used to be, wire secondary system,test and commission. Install lightening arrestors & carry out repairs to new 33kV ABS 3276 .Outage affecting McKee product | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 513.6833 | 510.6833 | 510.6833 | 0.0015598 | 3.0544e-06 | 2014-11-19 | B | 0.00077992 | 1.527e-06 | 2015 | 2014-11-19 | B | 1 | 0.0015598 | 3.0544e-06
1 | 2912953 | 2014-11-19 09:20 | 2014-11-19 14:45 | 325 | 2 | 650 | 0.001988 | 6.1168e-06 | NAPA ID:03905 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1499 | reposition Transformer TC1499. Works location: Thames Coast WO 10162266 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 325 | 322 | 644 | 0.001967 | 6.1088e-06 | 2014-11-19 | B | 0.00098352 | 3.054e-06 | 2015 | 2014-11-19 | B | 2 | 0.001967 | 6.1088e-06
1 | 3103617 | 2014-11-19 10:00 | 2014-11-19 11:48 | 108.25 | 3 | 189.05 | 0.00057819 | 9.1753e-06 | Restore Supply on Device X2916 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2916 | found 2x hv ddo links out replaced 2x10a due to bird strike. Steve advised he thinks this was 2R as he had to do line patrol to find fault | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 63.0167 | 60.0167 | 180.05 | 0.00054995 | 9.1633e-06 | 2014-11-19 | C | 0.00054995 | 9.163e-06 | 2015 | 2014-11-19 | C | 3 | 0.00054995 | 9.1633e-06
1 | 3102706 | 2014-11-19 10:44 | 2014-11-19 16:52 | 367.5833 | 1 | 367.5833 | 0.0011242 | 3.0584e-06 | Restore Supply on Device T8/396 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | T8/396 | 19/11 4.50pm - Part of oms 3106019 - can't get job to unlock or parented up, sign it off as part of feeder fault. Email sent to Alicia | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 367.5833 | 364.5833 | 364.5833 | 0.0011136 | 3.0544e-06 | 2014-11-19 | C | 0.0011136 | 3.054e-06 | 2015 | 2014-11-19 | C | 1 | 0.0011136 | 3.0544e-06
1 | 3106019 | 2014-11-19 10:44 | 2014-11-19 16:51 | 367.4333 | 24 | 8818.4 | 0.02697 | 7.3402e-05 | Restore Supply on Device S38 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | S38 | Tripping on Fuses S38 - Area patrolled/nothing found. Reclosed OK. Suspect line clash in high winds. T Pocock attended. | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 367.4333 | 364.4333 | 8746.4 | 0.026715 | 7.3306e-05 | 2014-11-19 | C | 0.026715 | 7.3306e-05 | 2015 | 2014-11-19 | C | 24 | 0.026715 | 7.3306e-05
1 | 3103360 | 2014-11-19 11:40 | 2014-11-19 13:06 | 86 | 238 | 19042 | 0.058238 | 0.0007279 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Livingston Sub | Cb LI 01 Tripped A,B ph O/C L/O - No Fault found during sectionlising | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80.0084 | 77.0084 | 18328 | 0.055981 | 0.00072695 | 2014-11-19 | C | 0.055981 | 0.00072695 | 2015 | 2014-11-19 | C | 238 | 0.055981 | 0.00072695
1 | 3103630 | 2014-11-19 11:48 | 2014-11-19 15:11 | 202.15 | 4 | 516.85 | 0.0015807 | 1.2234e-05 | Restore Supply on Device T1158 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 797491 | 11kV Tripping on fuses 7443 - tree had fallen through lines (High winds) and broken 2 conductors. Rejoined Ok and tree cut away. Relivened. Jason Hall attended. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 129.2125 | 126.2125 | 504.85 | 0.001542 | 1.2218e-05 | 2014-11-19 | C | 0.001542 | 1.2218e-05 | 2015 | 2014-11-19 | C | 4 | 0.001542 | 1.2218e-05
1 | 3103640 | 2014-11-19 11:55 | 2014-11-19 17:42 | 347.0333 | 19 | 4435.8667 | 0.013567 | 5.811e-05 | Restore Supply on Device T8/45 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | U15 | 11kV Fuses U15 found tripped. High winds, suspect clash. Area patrolled and reclosed OK. Trevor Pocock attended. | F3 | EKETAHUNA | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 233.4667 | 230.4667 | 4378.8667 | 0.013375 | 5.8034e-05 | 2014-11-19 | C | 0.013375 | 5.8034e-05 | 2015 | 2014-11-19 | C | 19 | 0.013375 | 5.8034e-05
1 | 3103665 | 2014-11-19 12:06 | 2014-11-19 14:24 | 138.0333 | 1 | 138.0333 | 0.00042216 | 3.0584e-06 | Restore Supply on Device T7/32 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P18233 | affecting cowshed, pump & house. Closed R15 - replaced 2 x 10amp fuses. Defecting pole P18233 has too saggy and causing line to clash. Emailed Jo, as appears could have a SAIDI component. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 138.0333 | 135.0333 | 135.0333 | 0.00041245 | 3.0544e-06 | 2014-11-19 | C | 0.00041245 | 3.054e-06 | 2015 | 2014-11-19 | C | 1 | 0.00041245 | 3.0544e-06
1 | 3104031 | 2014-11-19 13:40 | 2014-11-19 18:52 | 312.0833 | 69 | 4384.2833 | 0.013409 | 0.00021103 | Restore Supply on Device C223 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7028 | No Power - Line patrolled and blown Jumper located at fuses 7028. Sam Stuart, Paul Keating and Lucas Grant attended. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 63.5403 | 60.5403 | 4177.2833 | 0.012759 | 0.00021076 | 2014-11-19 | C | 0.012759 | 0.00021075 | 2015 | 2014-11-19 | C | 69 | 0.012759 | 0.00021076
1 | 3102580 | 2014-11-19 13:59 | 2014-11-19 15:35 | 95.8 | 1 | 95.8 | 0.000293 | 3.0584e-06 | Restore Supply on Device X432 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | Pole 806372 | Transformer X432 OK - fault with Broken 11kV jumper on Overhead feeding 4683W. Isolation from Fuse/Sw 4490/2, jumper repaired / relivened OK. | F4 | WAVERLEY | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 95.8 | 92.8 | 92.8 | 0.00028345 | 3.0544e-06 | 2014-11-19 | C | 0.00028345 | 3.054e-06 | 2015 | 2014-11-19 | C | 1 | 0.00028345 | 3.0544e-06
1 | 3106420 | 2014-11-19 16:17 | 2014-11-19 19:34 | 196.8833 | 238 | 10948 | 0.033484 | 0.0007279 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB LI1 | Not Patrolled | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 46 | 43 | 10234 | 0.031259 | 0.00072695 | 2014-11-19 | C | 0.031259 | 0.00072695 | 2015 | 2014-11-19 | C | 238 | 0.031259 | 0.00072695
1 | 3107625 | 2014-11-19 16:31 | 2014-11-19 21:28 | 297.1833 | 9 | 2182.9333 | 0.0066763 | 2.7526e-05 | Restore Supply on Device 10148 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V33 | Chris Naylor was assigned & onsite on OMS 3106051 (but this somehow cancelled out - mid job) so completed on this OMS 3107625 as needed signing off. Emailed Fiona & Stephanie. 2x 6amp ddo 11kv o/h fuses V33 11kv fuse wind full power restored adjac | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 242.5481 | 239.5481 | 2155.9333 | 0.0065851 | 2.749e-05 | 2014-11-19 | C | 0.0065851 | 2.749e-05 | 2015 | 2014-11-19 | C | 9 | 0.0065851 | 2.749e-05
1 | 3103671 | 2014-11-19 18:32 | 2014-11-19 19:38 | 66.15 | 37 | 2447.55 | 0.0074856 | 0.00011316 | Restore Supply on Device T9/64 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | Fuse V11 | Patrolled Nothing Found | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 66.15 | 63.15 | 2336.55 | 0.0071368 | 0.00011301 | 2014-11-19 | C | 0.0071368 | 0.00011301 | 2015 | 2014-11-19 | C | 37 | 0.0071368 | 0.00011301
1 | 3107627 | 2014-11-19 18:53 | 2014-11-19 19:26 | 33.3833 | 14 | 467.3667 | 0.0014294 | 4.2818e-05 | Restore Supply on Device 7028 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 834300 | Floating Conductor at Pole 834300. Isolated beyond Fuses 7028. No materials noted on the outage record. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 33.3833 | 30.3833 | 425.3667 | 0.0012993 | 4.2762e-05 | 2014-11-19 | C | 0.0012993 | 4.2762e-05 | 2015 | 2014-11-19 | C | 14 | 0.0012993 | 4.2762e-05
1 | 3108180 | 2014-11-19 20:53 | 2014-11-20 00:56 | 242.75 | 8 | 483.65 | 0.0014792 | 2.4467e-05 | Restore Supply on Device TC661 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses FP1170 | Grant Jordan Attended. Replaced 2x HV Fuses at FP1170. All Power Restored on completion. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 60.4562 | 57.4562 | 459.65 | 0.001404 | 2.4435e-05 | 2014-11-19 | C | 0.001404 | 2.4435e-05 | 2015 | 2014-11-19 | C | 8 | 0.001404 | 2.4435e-05
1 | 3108215 | 2014-11-19 22:03 | 2014-11-20 01:27 | 204.4 | 444 | 49441.6667 | 0.15121 | 0.0013579 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | Pole B12376, Transformer TC3564 | at 22:02, Baird Rd Sub, CB 6 Papanui St Feeder, Tripped, E/F, L/O. Faultmen dispatched and investigation began. Feeder sectionalised. Found possum on lines at Pole B12376, Transformer TC3564. Removed with hot stick. All Power Restored on completion. Denni | F4 | PAPANUI ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 111.3551 | 108.3551 | 48109.6667 | 0.14695 | 0.0013562 | 2014-11-19 | C | 0.14695 | 0.0013562 | 2015 | 2014-11-19 | C | 444 | 0.14695 | 0.0013562
1 | 3108710 | 2014-11-20 02:37 | 2014-11-20 04:27 | 109.7833 | 42 | 4610.9 | 0.014102 | 0.00012845 | Restore Supply on Device 1029 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer 1026 | Replaced 1 Set of DDO 2 Phase At Transformer 1026 | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.7833 | 106.7833 | 4484.9 | 0.013699 | 0.00012829 | 2014-11-20 | C | 0.013699 | 0.00012829 | 2015 | 2014-11-20 | C | 42 | 0.013699 | 0.00012829
1 | 3108703 | 2014-11-20 03:10 | 2014-11-20 03:45 | 35.0167 | 19 | 665.3167 | 0.0020348 | 5.811e-05 | Restore Supply on Device TE7-110 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | Pole 218335 | at 03:10, Pongakawa Sub, CB 1 Tainui Feeder. Found blown jumper at Pole 218335 caused by possum on the line. Isolated at fuses SE7-032. Permit issued & repairs carried out. All power restored on completion. Dave Ngatai attended. 1x Link Replaced. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 35.0167 | 32.0167 | 608.3167 | 0.0018581 | 5.8034e-05 | 2014-11-20 | C | 0.0018581 | 5.8034e-05 | 2015 | 2014-11-20 | C | 19 | 0.0018581 | 5.8034e-05
1 | 3110404 | 2014-11-20 07:58 | 2014-11-20 12:46 | 288.0167 | 24 | 1714.0167 | 0.0052422 | 7.3402e-05 | Restore Supply on Device T4/194 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p17341 | hv fuse at t4/194 fuse holder is burnt off this requires a road shut down to replace hv fuse holder this will require 2 more staff jeff leaving site they will need to bring hv fuse holder and do switching will work through control 2r requested repla | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.4174 | 68.4174 | 1642.0167 | 0.0050154 | 7.3306e-05 | 2014-11-20 | C | 0.0050154 | 7.3306e-05 | 2015 | 2014-11-20 | C | 24 | 0.0050154 | 7.3306e-05
1 | 2914456 | 2014-11-20 08:28 | 2014-11-20 13:53 | 325 | 2 | 650 | 0.001988 | 6.1168e-06 | NAPA ID:03909 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1498 | Replace lightning arrestors, DDO's and Transformer at TC1498. Works location: Thames Coast WO 10162265 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 325 | 322 | 644 | 0.001967 | 6.1088e-06 | 2014-11-20 | B | 0.00098352 | 3.054e-06 | 2015 | 2014-11-20 | B | 2 | 0.001967 | 6.1088e-06
1 | 2894520 | 2014-11-20 08:30 | 2014-11-20 15:35 | 425 | 39 | 16575 | 0.050693 | 0.00011928 | NAPA ID:02718 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S538 | 11KV POLE REPLACEMENT. Works location: Whakatomotomo Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 425 | 422 | 16458 | 0.05027 | 0.00011912 | 2014-11-20 | B | 0.025135 | 5.9561e-05 | 2015 | 2014-11-20 | B | 39 | 0.05027 | 0.00011912
1 | 2893479 | 2014-11-20 08:42 | 2014-11-20 15:34 | 412 | 15 | 6180 | 0.018901 | 4.5876e-05 | NAPA ID:03784 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P36463 | Replace crossarms from pole P36463 to P36878 as per plans. Install 11kV TEMP fuses on pole P36884. Works location: Forest Rd WO 10160678 | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 412 | 409 | 6135 | 0.018739 | 4.5816e-05 | 2014-11-20 | B | 0.0093694 | 2.2908e-05 | 2015 | 2014-11-20 | B | 15 | 0.018739 | 4.5816e-05
1 | 2920150 | 2014-11-20 08:54 | 2014-11-20 14:49 | 355.0833 | 646 | 229383.8333 | 0.70155 | 0.0019757 | NAPA ID:03842 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 201410 | REMOVE EXISTING POLE 201410 AND 201460 ALSO OH SPANS BEWTEEN ABS SB2-032 AP. INSATLL NEW TERM POLES AND TERMINATE NEW HV CABLES FROM NEW SAFE LINK 9858/1/3. TEST CABLES LIVEN AND PHASE CHECK ACROSS NEW SAFE LINK 9858 Works location: Park Rd Beach Rd | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 355.0833 | 352.0833 | 227445.8333 | 0.69472 | 0.0019732 | 2014-11-20 | B | 0.34736 | 0.00098658 | 2015 | 2014-11-20 | B | 646 | 0.69472 | 0.0019732
1 | 2902025 | 2014-11-20 09:01 | 2014-11-20 14:01 | 300.2 | 6 | 1801.2 | 0.0055088 | 1.8351e-05 | NAPA ID:02146 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole K13544 | To replaces arms and hardware beyond IC1106. Install a set of 11kV Fuses on pole C2221. Works location: No 9 Rd Springdale WO 476789 | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 300.2 | 297.2 | 1783.2 | 0.0054466 | 1.8327e-05 | 2014-11-20 | B | 0.0027233 | 9.163e-06 | 2015 | 2014-11-20 | B | 6 | 0.0054466 | 1.8327e-05
1 | 2914433 | 2014-11-20 09:01 | 2014-11-20 14:47 | 346.25 | 29 | 10041.25 | 0.03071 | 8.8694e-05 | NAPA ID:02611 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD5-016 | Replace poles between ABS SD5-016 and ABS SD5-033. Works location: Kairua Rd WO TA/2014/23 IR6817 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 346.25 | 343.25 | 9954.25 | 0.030404 | 8.8578e-05 | 2014-11-20 | B | 0.015202 | 4.4289e-05 | 2015 | 2014-11-20 | B | 29 | 0.030404 | 8.8578e-05
1 | 3119708 | 2014-11-20 09:49 | 2014-11-21 03:45 | 1076.45 | 224 | 6020 | 0.018412 | 0.00068509 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 779695 | CB 4695 tripped on A & C phase O/C flags. Back feed was installed from Recloser 4621/2 to Recloser 142. Line was patrolled and sectionalised and a floating wire was found at pole 779695. Line was isolated at ABS's 1065 & 1428 to rebind in the conductor & | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 26.875 | 23.875 | 5348 | 0.016335 | 0.00068419 | 2014-11-20 | C | 0.016335 | 0.00068419 | 2015 | 2014-11-20 | C | 224 | 0.016335 | 0.00068419
1 | 3110465 | 2014-11-20 10:25 | 2014-11-20 10:55 | 30 | 31 | 930 | 0.0028443 | 9.4811e-05 | Restore Supply on Device T177 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | pole824379 | 11 kv ddo needs to be replaced 2 other crew attending to isolate t177 remainig at site to assist with repairs will work though control requesting 2r and more crew to assist 11am Tallia called to advise needing to deassign James as neil butler is onsite | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 837 | 0.0025566 | 9.4687e-05 | 2014-11-20 | C | 0.0025566 | 9.4687e-05 | 2015 | 2014-11-20 | C | 31 | 0.0025566 | 9.4687e-05
1 | 2901986 | 2014-11-20 10:59 | 2014-11-20 14:55 | 235.9167 | 7 | 1651.4167 | 0.0050507 | 2.1409e-05 | NAPA ID:04124 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 721339 | Replace pole 721339 and transformer pole C6230. Works location: Katene Rd Hawera WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.9167 | 232.9167 | 1630.4167 | 0.00498 | 2.1381e-05 | 2014-11-20 | B | 0.00249 | 1.069e-05 | 2015 | 2014-11-20 | B | 7 | 0.00498 | 2.1381e-05
1 | 3104111 | 2014-11-20 11:22 | 2014-11-20 11:51 | 29.1667 | 39 | 1137.5 | 0.003479 | 0.00011928 | NAPA ID:04925 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 724784 | Repair 11Kv 7.064 cu conductor @ pole 724784 1 stand unraveling & maybe whats tripping recloser 6561. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 29.1667 | 26.1667 | 1020.5 | 0.003117 | 0.00011912 | 2014-11-20 | B | 0.0015585 | 5.9561e-05 | 2015 | 2014-11-20 | B | 39 | 0.003117 | 0.00011912
1 | 3112798 | 2014-11-20 19:35 | 2014-11-20 19:56 | 20.7667 | 90 | 1869 | 0.0057162 | 0.00027526 | Restore Supply on Device TC1029 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer Fuses TC1029 | at 19:35, Tirau Sub, CB 5 Cambridge Rd Feeder. Found broken DDO & blown jumper at Transformer Fuses TC1029. Isolated Lines at ABS 858. Permit issued & repairs carried out. All Power Restored on Completion. Marty Keenan Attended. 1x HV Fuse Holder & 1x HV | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 20.7667 | 17.7667 | 1599 | 0.004884 | 0.0002749 | 2014-11-20 | C | 0.004884 | 0.0002749 | 2015 | 2014-11-20 | C | 90 | 0.004884 | 0.0002749
1 | 3114519 | 2014-11-21 00:36 | 2014-11-21 07:52 | 435.5667 | 1184 | 163465.2167 | 0.49995 | 0.0036212 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 4419T | Trippings on both recloser CB6224 asnd CB4949 on Phase A-B O/C. Car vs Pole at 442 Inland north Rd (Double circuit 11kV). Transformer Pole 4419T broken, 11kv / 400V clash caused damage also. Isolations from ABS 5207, 5128, 5192, Links 4949/6, ABS 4949/1 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 138.0618 | 135.0618 | 159913.2167 | 0.48844 | 0.0036164 | 2014-11-21 | C | 0.48844 | 0.0036164 | 2015 | 2014-11-21 | C | 1184 | 0.48844 | 0.0036164
1 | 3115567 | 2014-11-21 03:05 | 2014-11-21 08:01 | 296.0333 | 121 | 29542.9333 | 0.090355 | 0.00037007 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P00400 | Recloser V27 tripped on B & C phase E/F flags, line was patrolled and a floating wire and broken insulator was found at pole P00400, line was isolated at ABS V29 and Links V28 to carry out the repairs. 1 X 11KV insulator replaced, 5 x Binders used. | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 244.1565 | 241.1565 | 29179.9333 | 0.089128 | 0.00036959 | 2014-11-21 | C | 0.089128 | 0.00036959 | 2015 | 2014-11-21 | C | 121 | 0.089128 | 0.00036959
1 | 3116039 | 2014-11-21 06:14 | 2014-11-21 13:00 | 405.6667 | 2 | 811.3333 | 0.0024814 | 6.1168e-06 | Restore Supply on Device 4571 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4743W | Blown cable - cause unknown. Replaced cable to transformer 4743W used 15 metres of 35mm HV cable and 2x termination kits. Nothing else repaired or replaced, adjacent assets up to Powerco standard. Karl Rogers and Brent Singleton attended. | F3 | CORNFOOT ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 405.6667 | 402.6667 | 805.3333 | 0.0024598 | 6.1088e-06 | 2014-11-21 | C | 0.0024598 | 6.109e-06 | 2015 | 2014-11-21 | C | 2 | 0.0024598 | 6.1088e-06
1 | 2912333 | 2014-11-21 08:31 | 2014-11-21 15:16 | 404.2833 | 32 | 12937.0667 | 0.039567 | 9.787e-05 | NAPA ID:03843 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6525 | Replace 11kV poles & conductor. Works location: Whenuku Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 404.2833 | 401.2833 | 12841.0667 | 0.039222 | 9.7742e-05 | 2014-11-21 | B | 0.019611 | 4.8871e-05 | 2015 | 2014-11-21 | B | 32 | 0.039222 | 9.7742e-05
1 | 2914955 | 2014-11-21 09:01 | 2014-11-21 13:59 | 298.0333 | 3 | 894.1 | 0.0027345 | 9.1753e-06 | NAPA ID:02801 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228957, 228956 | To replace transformer Structure pole 228957 and cross arm Pole 228956. Works location: Johnson Rd. WO 477863 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 298.0333 | 295.0333 | 885.1 | 0.0027035 | 9.1633e-06 | 2014-11-21 | B | 0.0013517 | 4.582e-06 | 2015 | 2014-11-21 | B | 3 | 0.0027035 | 9.1633e-06
1 | 3117000 | 2014-11-21 09:16 | 2014-11-21 13:33 | 256.85 | 1 | 256.85 | 0.00078556 | 3.0584e-06 | Restore Supply on Device 7061P | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p36340 | Replaced 2x 5amp hv fuses due to unknown. nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 256.85 | 253.85 | 253.85 | 0.00077537 | 3.0544e-06 | 2014-11-21 | C | 0.00077536 | 3.054e-06 | 2015 | 2014-11-21 | C | 1 | 0.00077537 | 3.0544e-06
1 | 2986276 | 2014-11-21 09:28 | 2014-11-21 14:24 | 296.15 | 7 | 2073.05 | 0.0063403 | 2.1409e-05 | NAPA ID:04398 TP_WAIKINO GXP > WAIHI SUB > WAIHI BEACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2074 | Replace the Transformer and LV Tx arm due to age. Works location: Mathers Rd Waihi. WO 10148378. | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 296.15 | 293.15 | 2052.05 | 0.0062678 | 2.1381e-05 | 2014-11-21 | B | 0.0031339 | 1.069e-05 | 2015 | 2014-11-21 | B | 7 | 0.0062678 | 2.1381e-05
1 | 3112648 | 2014-11-21 09:51 | 2014-11-21 15:04 | 312.8833 | 89 | 27846.6167 | 0.085167 | 0.0002722 | NAPA ID:04034 TP_TE MATAI GXP > TE PUKE SUB > PAPAMOA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE6-099 | Replace 11kV Termination at TE6-099. Works location: Harris St, Papamoa. WO 10148986 | F3 | PAPAMOA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 312.8833 | 309.8833 | 27579.6167 | 0.08424 | 0.00027184 | 2014-11-21 | B | 0.04212 | 0.00013592 | 2015 | 2014-11-21 | B | 89 | 0.08424 | 0.00027184
1 | 3120629 | 2014-11-21 12:12 | 2014-11-21 14:12 | 119.9167 | 1 | 119.9167 | 0.00036676 | 3.0584e-06 | Restore Supply on Device Y250 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 782511 | 2x 2amp hv fuse re-tightened and rewired fuses using copper wire and done live at pole 782511 due to age this is amber defected as the fuses need to be replaced nothing else repaired or replaced very bad rt reception. | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 119.9167 | 116.9167 | 116.9167 | 0.00035711 | 3.0544e-06 | 2014-11-21 | C | 0.00035711 | 3.054e-06 | 2015 | 2014-11-21 | C | 1 | 0.00035711 | 3.0544e-06
1 | 3120661 | 2014-11-21 12:34 | 2014-11-21 12:39 | 5 | 599 | 2995 | 0.00916 | 0.001832 | Restore Supply on Device C928 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C928 | CB C928 tripped on A & C phase O/C flags, at time of tripping a Live Line Permit 4783-01 was in force on the line so the feeder could not auto reclose. Live Line applicant confirmed that they were not doing any work at time of tripping. Hot Line Tag was d | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 5 | 2 | 1198 | 0.0036592 | 0.0018296 | 2014-11-21 | C | 0.0036592 | 0.0018296 | 2015 | 2014-11-21 | C | 599 | 0.0036592 | 0.0018296
1 | 3121692 | 2014-11-21 17:16 | 2014-11-21 20:11 | 174.4333 | 2 | 229 | 0.00070038 | 6.1168e-06 | Restore Supply on Device T8/286 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P12763 | Repaired existing 11kv jumper at pole P12763. Deteriorated / wind. Full power restored nothing else repaired or replaced. Adjacent assets - faultman advises there is already a defect in system for ddo fuses & crossarm. Trevor Pocock attended. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 114.5 | 111.5 | 223 | 0.00068114 | 6.1088e-06 | 2014-11-21 | C | 0.00068114 | 6.109e-06 | 2015 | 2014-11-21 | C | 2 | 0.00068114 | 6.1088e-06
1 | 3133430 | 2014-11-22 07:30 | 2014-11-22 11:22 | 232 | 1 | 232 | 0.00070955 | 3.0584e-06 | Restore Supply on Device 10113 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10113 | Repair Leaking 11kV transformer 7171P. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 232 | 229 | 229 | 0.00069946 | 3.0544e-06 | 2014-11-22 | C | 0.00069946 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00069946 | 3.0544e-06
1 | 3116114 | 2014-11-22 07:46 | 2014-11-22 12:12 | 266 | 1 | 266 | 0.00081354 | 3.0584e-06 | NAPA ID:04988 TP_MT MAUNGANUI 33 GXP > TRITON SUB > WHARF | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-167 | Repair Oil Leak on LV Bushings of TX. Works location: Port of Tauranga. WO 103313. | F1 | WHARF | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 266 | 263 | 263 | 0.00080331 | 3.0544e-06 | 2014-11-22 | B | 0.00040166 | 1.527e-06 | 2015 | 2014-11-22 | B | 1 | 0.00080331 | 3.0544e-06
1 | 3121815 | 2014-11-22 07:50 | 2014-11-22 11:59 | 249 | 438 | 86613.7833 | 0.2649 | 0.0013396 | Restore Supply on Device C850 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C850 | Line sectionalised and patrolled supply restored with no apparent fault found. Recloser CB 8097 defected by Tenix suspected tripping on inrush current protection settings to be investigated. Gavun Gray and Adam Whale attended. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 197.7484 | 194.7484 | 85299.7833 | 0.26054 | 0.0013378 | 2014-11-22 | C | 0.26054 | 0.0013378 | 2015 | 2014-11-22 | C | 438 | 0.26054 | 0.0013378
1 | 3134001 | 2014-11-22 09:00 | 2014-11-22 10:40 | 100 | 61 | 6100 | 0.018656 | 0.00018656 | Restore Supply on Device OS385 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | J41 | Close Live Line Breaks and Liven New Switch Gear - Return Feeder back to normal. | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 5917 | 0.018073 | 0.00018632 | 2014-11-22 | C | 0.018073 | 0.00018632 | 2015 | 2014-11-22 | C | 61 | 0.018073 | 0.00018632
1 | 3134066 | 2014-11-22 09:00 | 2014-11-22 10:20 | 80 | 172 | 13760 | 0.042084 | 0.00052605 | Restore Supply on Device 254 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/Gear 254 | Close Temp Line Breaks and Liven New Switch Gear - Return Feeder back to normal | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 13244 | 0.040453 | 0.00052536 | 2014-11-22 | C | 0.040453 | 0.00052536 | 2015 | 2014-11-22 | C | 172 | 0.040453 | 0.00052536
1 | 3134251 | 2014-11-22 09:08 | 2014-11-22 10:20 | 72 | 70 | 5040 | 0.015414 | 0.00021409 | Restore Supply on Device T3/469 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sw/Gear 222 | Close Temp Line Breaks and Liven New Switch Gear - Return Feeder back to normal | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 72 | 69 | 4830 | 0.014753 | 0.00021381 | 2014-11-22 | C | 0.014753 | 0.00021381 | 2015 | 2014-11-22 | C | 70 | 0.014753 | 0.00021381
1 | 3122346 | 2014-11-22 09:08 | 2014-11-22 12:53 | 224.55 | 7 | 1281.45 | 0.0039192 | 2.1409e-05 | Restore Supply on Device S25 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P12646 | 11 kv wires held up by 3rd one. All ladder work. Need to replace more than 3m of conductor. FM advise: NDR # 19185. Tree through 11kV line. Materials used: 6 x no.8 steel compressions and 6m of no.8 wire. Pole P12646. It was 2 wires in one span. Trev | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 183.0643 | 180.0643 | 1260.45 | 0.0038499 | 2.1381e-05 | 2014-11-22 | C | 0.0038499 | 2.1381e-05 | 2015 | 2014-11-22 | C | 7 | 0.0038499 | 2.1381e-05
1 | 3122374 | 2014-11-22 09:35 | 2014-11-22 14:38 | 303.0833 | 1 | 303.0833 | 0.00092696 | 3.0584e-06 | Restore Supply on Device T135 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | tx T135 | FM did not have coverage. advise: onsite 1.30pm, offsite 2pm. replace 11kv fuse at start of road. cause: wind. 10 amp fuse. 1 out 3 phases. tx T135. pole where the fuses were replaced is about 20km up the road. FM did not get pole number and already lef | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 303.0833 | 300.0833 | 300.0833 | 0.00091658 | 3.0544e-06 | 2014-11-22 | C | 0.00091658 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00091658 | 3.0544e-06
1 | 3124212 | 2014-11-22 10:28 | 2014-11-22 17:21 | 413.2833 | 238 | 33366.1333 | 0.10205 | 0.0007279 | Restore Supply on Device LI1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 727700 | Replaced burnt crossarm on pole 727700. Bevan Hughes and Kaine MacKay attended. | F4 | OTAUTU | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 140.1938 | 137.1938 | 32652.1333 | 0.099733 | 0.00072695 | 2014-11-22 | C | 0.099733 | 0.00072695 | 2015 | 2014-11-22 | C | 238 | 0.099733 | 0.00072695
1 | 3121803 | 2014-11-22 11:05 | 2014-11-22 11:20 | 15 | 7 | 105 | 0.00032113 | 2.1409e-05 | Restore Supply on Device TC812 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC812 | This is a quality supply issue previously dealt with under OMS number 3121673 - transformer TC812 isolated to alter tap position as temporary attempted voltage correction until supply issue remedied | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 84 | 0.00025657 | 2.1381e-05 | 2014-11-22 | C | 0.00025657 | 2.1381e-05 | 2015 | 2014-11-22 | C | 7 | 0.00025657 | 2.1381e-05
1 | 3123012 | 2014-11-22 11:17 | 2014-11-22 14:43 | 205.7 | 6 | 726.65 | 0.0022224 | 1.8351e-05 | Restore Supply on Device T8/242 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | fuse S 11 | fuse S 11. trees interfering further up the line. it is in the hands of treescape. replace 2 x 10 amp ddo fuses. 2 out 3 phases. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 121.1083 | 118.1083 | 708.65 | 0.0021645 | 1.8327e-05 | 2014-11-22 | C | 0.0021645 | 1.8327e-05 | 2015 | 2014-11-22 | C | 6 | 0.0021645 | 1.8327e-05
1 | 3123016 | 2014-11-22 11:18 | 2014-11-22 16:10 | 292.0667 | 113 | 18104 | 0.05537 | 0.0003456 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 838763 | Recloser C224 Auto Reclosed. No Flags. Subsequent call received regarding fire beneath lines. Isolation beyond 11kV Links 7366 to replace burnt cross arm and hardware at pole 838763. Lucas Grant attended. Refer to OMS Job ID 3123564 for restoration foll | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 160.2124 | 157.2124 | 17765 | 0.054262 | 0.00034515 | 2014-11-22 | C | 0.054262 | 0.00034515 | 2015 | 2014-11-22 | C | 113 | 0.054262 | 0.00034515
1 | 3124472 | 2014-11-22 13:07 | 2014-11-22 17:52 | 284.2 | 1 | 284.2 | 0.0008692 | 3.0584e-06 | Restore Supply on Device T9/150 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | b44 | section b44 blown. 2x 6amp hv fuses cause - needs line patrol done on this line, possible ducks/birds/trees | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 284.2 | 281.2 | 281.2 | 0.0008589 | 3.0544e-06 | 2014-11-22 | C | 0.0008589 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.0008589 | 3.0544e-06
1 | 3124517 | 2014-11-22 14:01 | 2014-11-22 15:15 | 74.3833 | 1 | 74.3833 | 0.0002275 | 3.0584e-06 | Restore Supply on Device S11 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | Device S11, PUTARA ROAD, EKETAHUNA | related to oms 3123012. fuse S 11. trees interfering further up the line. it is in the hands of treescape. replace 2 x 10 amp ddo fuses. 2 out 3 phases. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 74.3833 | 71.3833 | 71.3833 | 0.00021803 | 3.0544e-06 | 2014-11-22 | C | 0.00021803 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00021803 | 3.0544e-06
1 | 3125930 | 2014-11-22 14:31 | 2014-11-22 16:58 | 146.7333 | 1 | 146.7333 | 0.00044877 | 3.0584e-06 | Restore Supply on Device X537 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | fuses 840 | replaced 2x 8amp ht fuses at fuses 840 cause wind nothing repaired or replaced onsite, all adjacent assets ok | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 146.7333 | 143.7333 | 143.7333 | 0.00043902 | 3.0544e-06 | 2014-11-22 | C | 0.00043902 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00043902 | 3.0544e-06
1 | 3127155 | 2014-11-22 15:45 | 2014-11-22 19:00 | 195.25 | 75 | 14643.75 | 0.044787 | 0.00022938 | Restore Supply on Device T3160 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 817584 | possibly part of oms 3127165 | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 195.25 | 192.25 | 14418.75 | 0.044041 | 0.00022908 | 2014-11-22 | C | 0.044041 | 0.00022908 | 2015 | 2014-11-22 | C | 75 | 0.044041 | 0.00022908
1 | 3127165 | 2014-11-22 15:48 | 2014-11-23 00:31 | 523.1167 | 4 | 1660.2667 | 0.0050778 | 1.2234e-05 | Restore Supply on Device T1566 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 817584 | Faultman found Recloser C416/2 open, line was patrolled and a floating wire was found at pole 817584, line was isolated at Link C416/6 and ABS C416/1 to rebind in the conductor. Email sent to Jo, as appears could have SAIDI component. | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 415.0667 | 412.0667 | 1648.2667 | 0.0050345 | 1.2218e-05 | 2014-11-22 | C | 0.0050345 | 1.2218e-05 | 2015 | 2014-11-22 | C | 4 | 0.0050345 | 1.2218e-05
1 | 4130756 | 2014-11-22 16:48 | 2014-11-22 20:14 | 206 | 90 | 18540 | 0.056703 | 0.00027526 | Restore Supply on Device C632 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C632 | Sectionaliser C632 tripped. Line patrolled and no fault found. Gavin has defected several sites with trees close to lines. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 206 | 203 | 18270 | 0.055804 | 0.0002749 | 2014-11-22 | C | 0.055804 | 0.0002749 | 2015 | 2014-11-22 | C | 90 | 0.055804 | 0.0002749
1 | 3127377 | 2014-11-22 17:31 | 2014-11-23 14:27 | 1256.3167 | 46 | 18805.2667 | 0.057514 | 0.00014069 | Restore Supply on Device T9/407 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P28467 | 13667 State Highway 52, Eketahuna. CB I23 tripped no flags. Line was sectionalised and patrolled and lines down was found at pole P28467. Line was isolated at Fuses I26 to replace broken conductor. Replaced 10m Squirell conductor @ pole P28467. Email s | F4 | BROOKLANDS | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 408.8101 | 405.8101 | 18667.2667 | 0.057018 | 0.0001405 | 2014-11-22 | C | 0.057018 | 0.0001405 | 2015 | 2014-11-22 | C | 46 | 0.057018 | 0.0001405
1 | 3127405 | 2014-11-22 17:49 | 2014-11-22 21:59 | 250.0333 | 1 | 250.0333 | 0.00076471 | 3.0584e-06 | Restore Supply on Device T442 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses 7318 | Faultman replaced HV fuse at Fuses 7318. 1 X 10Amp HV rewirable fuse. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 250.0333 | 247.0333 | 247.0333 | 0.00075454 | 3.0544e-06 | 2014-11-22 | C | 0.00075454 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00075454 | 3.0544e-06
1 | 3127466 | 2014-11-22 18:14 | 2014-11-22 18:31 | 16.6833 | 904 | 14015.7333 | 0.042866 | 0.0027648 | Restore Supply on Device CB2762 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 332 | CB 2762 tripped on O/C flags, line was sectionalised and patrolled and a broken jumper was found at ABS 332, line was isolated at ABS's 332 & 311 to repair the jumper. Douglas Sub was back fed from VS 6289. Dennis Embling and Kane MacKay attended. | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15.5041 | 12.5041 | 11303.7333 | 0.034526 | 0.0027612 | 2014-11-22 | C | 0.034526 | 0.0027612 | 2015 | 2014-11-22 | C | 904 | 0.034526 | 0.0027612
1 | 3127397 | 2014-11-22 18:15 | 2014-11-22 19:15 | 60 | 12 | 720 | 0.0022021 | 3.6701e-05 | Restore Supply on Device T2903 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 838337 | This was related to OMS 3127346. Also refer to OMS Job ID 3123718. Isolated beyond Fuses 7889. Line patrolled and floating conductors rebound at pole 838337. Materials Used: 2 x Binders. Adam Whale attended. | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 684 | 0.0020892 | 3.6653e-05 | 2014-11-22 | C | 0.0020892 | 3.6653e-05 | 2015 | 2014-11-22 | C | 12 | 0.0020892 | 3.6653e-05
1 | 3128378 | 2014-11-22 18:16 | 2014-11-22 22:40 | 264.5667 | 1 | 264.5667 | 0.00080916 | 3.0584e-06 | Restore Supply on Device T436 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 7149 | Faultman replaced HV fuses at Fuses 7149.Suspect line clash high winds in area. 2 X 8Amp HV rewirable fusesn used. Email sent to Jo, as appears could have SAIDI component. | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 264.5667 | 261.5667 | 261.5667 | 0.00079894 | 3.0544e-06 | 2014-11-22 | C | 0.00079893 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00079894 | 3.0544e-06
1 | 3128660 | 2014-11-22 20:27 | 2014-11-22 21:50 | 83.2333 | 1 | 83.2333 | 0.00025456 | 3.0584e-06 | Restore Supply on Device X1186 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - PATROLLED - CAUSE UNKNOWN | X1186 | Faultman replaced blown HV fuse. 1 X 3Amp HV rewirable fuse No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 83.2333 | 80.2333 | 80.2333 | 0.00024507 | 3.0544e-06 | 2014-11-22 | C | 0.00024507 | 3.054e-06 | 2015 | 2014-11-22 | C | 1 | 0.00024507 | 3.0544e-06
1 | 2920063 | 2014-11-23 09:00 | 2014-11-23 14:53 | 353 | 79 | 27887 | 0.08529 | 0.00024162 | NAPA ID:03897 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 114 | 11kV Line re-configuration and automation between Junction Rd & Kaipi Rd feeders. All switching requirements and info was done under NAPA 2460 which could not be completed due to ABS failures during switching. Works location: Junction Rd and Egmont Rd W | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 353 | 350 | 27650 | 0.084455 | 0.0002413 | 2014-11-23 | B | 0.042227 | 0.00012065 | 2015 | 2014-11-23 | B | 79 | 0.084455 | 0.0002413
1 | 3131153 | 2014-11-23 10:43 | 2014-11-23 14:07 | 204 | 60 | 12240 | 0.037435 | 0.00018351 | Restore Supply on Device S539 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 810632 | related to 3130312 Replaced damaged pole - caused by trees. Gavin Grey and Adam Whale attended. NDR 24048. | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 204 | 201 | 12060 | 0.036836 | 0.00018327 | 2014-11-23 | C | 0.036836 | 0.00018327 | 2015 | 2014-11-23 | C | 60 | 0.036836 | 0.00018327
1 | 3131306 | 2014-11-23 14:05 | 2014-11-23 14:11 | 6 | 904 | 4698.5 | 0.01437 | 0.0027648 | Restore Supply on Device CB2762 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 2762 | 33kV CB2762 tripped O/C. Line sectionalised and patrolled . No apparent fault found and supply restored. Dennis Embling and Paul Fitzpatrick attended. Note - this is followed by OMS Job ID 3127466 which was patrolled and jumper at ABS332 was repaired. | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 5.1975 | 2.1975 | 1986.5 | 0.0060676 | 0.0027612 | 2014-11-23 | C | 0.0060676 | 0.0027612 | 2015 | 2014-11-23 | C | 904 | 0.0060676 | 0.0027612
1 | 3132212 | 2014-11-23 14:23 | 2014-11-23 16:41 | 137.7167 | 1 | 137.7167 | 0.0004212 | 3.0584e-06 | Restore Supply on Device 2669T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 7592 OHURA ROAD, WHANGAMOMONA, STRATFORD | 23/11 3.27pm left voice message on customer's phone. power should be restored (control has back fed). asked customer to call on 0800 200 904 if power has not been restored. provided oms job number 3132212 as reference for the customer. control advised tha | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 137.7167 | 134.7167 | 134.7167 | 0.00041148 | 3.0544e-06 | 2014-11-23 | C | 0.00041148 | 3.054e-06 | 2015 | 2014-11-23 | C | 1 | 0.00041148 | 3.0544e-06
1 | 3132401 | 2014-11-23 17:58 | 2014-11-23 18:44 | 46.45 | 68 | 3158.6 | 0.0096603 | 0.00020797 | Restore Supply on Device G295B | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | g302 | Swgear g302 damaged jumper attached to stop inferencing swgear been DNO 141105. No Paper work is able to be located. Restoration time taken from associated job OMS 3131249 and 3132313 | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 46.45 | 43.45 | 2954.6 | 0.0090246 | 0.0002077 | 2014-11-23 | C | 0.0090246 | 0.0002077 | 2015 | 2014-11-23 | C | 68 | 0.0090246 | 0.0002077
1 | 3132501 | 2014-11-24 05:24 | 2014-11-24 07:18 | 113.5 | 1 | 113.5 | 0.00034713 | 3.0584e-06 | Restore Supply on Device TE7-130 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 846174 | 2x 6amp ddo fuses feeding cowshed due to bird strike at pole 846174 surrounding asset up to standard patrolled line nothing else repaired or replaced. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 113.5 | 110.5 | 110.5 | 0.00033751 | 3.0544e-06 | 2014-11-24 | C | 0.00033751 | 3.054e-06 | 2015 | 2014-11-24 | C | 1 | 0.00033751 | 3.0544e-06
1 | 2912270 | 2014-11-24 09:03 | 2014-11-24 14:10 | 306.8167 | 6 | 1840.9 | 0.0056302 | 1.8351e-05 | NAPA ID:03387 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P22150 | Replace 11kv crossarms from p22150 to p20251, note these arms under Feilding Sanson 33kv. Works location: Kawakawa Rd Feilding. WO 10140843 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 306.8167 | 303.8167 | 1822.9 | 0.0055679 | 1.8327e-05 | 2014-11-24 | B | 0.002784 | 9.163e-06 | 2015 | 2014-11-24 | B | 6 | 0.0055679 | 1.8327e-05
1 | 3132720 | 2014-11-24 09:40 | 2014-11-24 10:51 | 71 | 178 | 10415.1667 | 0.031854 | 0.0005444 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB6 | CB 6 L/O on E/F & O/C. Sectionalised and line patrolled. No fault located. Dave Ngatai attended. | F1/F4 | TE PUKE QUARRY RD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 58.5122 | 55.5122 | 9881.1667 | 0.030181 | 0.00054369 | 2014-11-24 | C | 0.030181 | 0.00054369 | 2015 | 2014-11-24 | C | 178 | 0.030181 | 0.00054369
1 | 3133450 | 2014-11-24 11:16 | 2014-11-24 11:37 | 20.5833 | 376 | 7739.3333 | 0.02367 | 0.00115 | Restore Supply on Device PU2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 20/01/15, ASW, Feeder outage, unknown details. trip waited 20 closed back in all ok | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 20.5833 | 17.5833 | 6611.3333 | 0.020194 | 0.0011485 | 2014-11-24 | C | 0.020194 | 0.0011485 | 2015 | 2014-11-24 | C | 376 | 0.020194 | 0.0011485
1 | 3133938 | 2014-11-24 11:41 | 2014-11-24 12:29 | 48 | 8 | 384 | 0.0011744 | 2.4467e-05 | Restore Supply on Device 7149 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 841814 | Floating Conductor at Pole 841814. Isolated beyond Fuses 7149. James Matthews attended. | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 48 | 45 | 360 | 0.0010996 | 2.4435e-05 | 2014-11-24 | C | 0.0010996 | 2.4435e-05 | 2015 | 2014-11-24 | C | 8 | 0.0010996 | 2.4435e-05
1 | 3133860 | 2014-11-24 12:00 | 2014-11-24 14:45 | 165.4 | 16 | 2646.4 | 0.0080938 | 4.8935e-05 | Restore Supply on Device T27 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P46913 | Faultman found burnt out HV pole. Required 2R for assistance to reinstate. plz check oms 3133996 115 Hinemoa Valley road, plz also check 3133992 2094 Mangaone Valley Road, 3134334 300 Hinemoa Valley Road | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 165.4 | 162.4 | 2598.4 | 0.0079366 | 4.8871e-05 | 2014-11-24 | C | 0.0079366 | 4.8871e-05 | 2015 | 2014-11-24 | C | 16 | 0.0079366 | 4.8871e-05
1 | 3136370 | 2014-11-24 19:59 | 2014-11-25 01:00 | 300.9833 | 40 | 12025.7333 | 0.03678 | 0.00012234 | Restore Supply on Device 744 | 6600 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Y199 | Found transformer Y199 faulty and replaced. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 300.6433 | 297.6433 | 11905.7333 | 0.036365 | 0.00012218 | 2014-11-24 | C | 0.036365 | 0.00012218 | 2015 | 2014-11-24 | C | 40 | 0.036365 | 0.00012218
1 | 3136509 | 2014-11-24 21:25 | 2014-11-24 22:43 | 77.85 | 16 | 1245.6 | 0.0038096 | 4.8935e-05 | Restore Supply on Device 7856 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 824542 | Replaced 2x 10a hv fuse links due to bird strike. nothing else repaired or replaced, adjacent assets up to Powerco standard. Unalbe to locate paperwork. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 77.85 | 74.85 | 1197.6 | 0.003658 | 4.8871e-05 | 2014-11-24 | C | 0.003658 | 4.8871e-05 | 2015 | 2014-11-24 | C | 16 | 0.003658 | 4.8871e-05
1 | 2974552 | 2014-11-24 23:01 | 2014-11-25 02:57 | 236.1833 | 30 | 7085.5 | 0.02167 | 9.1753e-05 | NAPA ID:04257 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > WAIHI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD4-238 | Maintenance on 11kv Linkbox SD4-238 and replace LV frame at TX TD4-209. Works location: Waihi Rd WO 10162239 | F2 | WAIHI RD | WAIHI ROAD SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 236.1833 | 233.1833 | 6995.5 | 0.021367 | 9.1633e-05 | 2014-11-24 | B | 0.010684 | 4.5816e-05 | 2015 | 2014-11-24 | B | 30 | 0.021367 | 9.1633e-05
1 | 2912354 | 2014-11-24 23:13 | 2014-11-25 00:05 | 52.4333 | 40 | 2097.3333 | 0.0064145 | 0.00012234 | NAPA ID:03395 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P22104 | Break 11kV jumpers on 4 pole structure P22104 note 33kV on same structure. Works location: Stewart Rd. WO 10140843 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 52.4333 | 49.4333 | 1977.3333 | 0.0060396 | 0.00012218 | 2014-11-24 | B | 0.0030198 | 6.1088e-05 | 2015 | 2014-11-24 | B | 40 | 0.0060396 | 0.00012218
1 | 3136698 | 2014-11-25 05:14 | 2014-11-25 07:45 | 151 | 1139 | 114308.6667 | 0.3496 | 0.0034835 | Restore Supply on Device 13 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | G96 | Magnefix G96 Blown up. 4 Back feeds in Place. Back Feed at G120A, Back Feed at G292B, Back Feed at G243C, Back Feed at G107B. Dno Done for G96 141108, DNO Done For G243 141107, DNO Done For CB 13 141106. Shazil Khan attended. | F3 | KEITH ST 13 | KEITH ST SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100.3588 | 97.3588 | 110891.6667 | 0.33871 | 0.003479 | 2014-11-25 | C | 0.33871 | 0.003479 | 2015 | 2014-11-25 | C | 1139 | 0.33871 | 0.003479
1 | 3137840 | 2014-11-25 05:17 | 2014-11-25 07:05 | 107.8667 | 1 | 107.8667 | 0.0003299 | 3.0584e-06 | Restore Supply on Device TC415 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | fc1461 | 2x hv 3amp hv oh at pole fc 1461 due bird strike surrounding asset good nothing else repaired or replaced. | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 107.8667 | 104.8667 | 104.8667 | 0.00032031 | 3.0544e-06 | 2014-11-25 | C | 0.00032031 | 3.054e-06 | 2015 | 2014-11-25 | C | 1 | 0.00032031 | 3.0544e-06
1 | 3139591 | 2014-11-25 08:30 | 2014-11-25 14:47 | 377 | 39 | 14703 | 0.044968 | 0.00011928 | Restore Supply on Device S538 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S538 | napa 2914417 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 377 | 374 | 14586 | 0.044552 | 0.00011912 | 2014-11-25 | C | 0.044552 | 0.00011912 | 2015 | 2014-11-25 | C | 39 | 0.044552 | 0.00011912
1 | 2973754 | 2014-11-25 08:39 | 2014-11-25 15:10 | 390.6333 | 14 | 5468.8667 | 0.016726 | 4.2818e-05 | NAPA ID:04292 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 722680 | Replace pole or wire on Manawapou Road. Works location: Manawapou Rd. WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 390.6333 | 387.6333 | 5426.8667 | 0.016576 | 4.2762e-05 | 2014-11-25 | B | 0.008288 | 2.1381e-05 | 2015 | 2014-11-25 | B | 14 | 0.016576 | 4.2762e-05
1 | 3146935 | 2014-11-25 09:00 | 2014-11-25 14:16 | 316 | 7 | 2212 | 0.0067652 | 2.1409e-05 | Restore Supply on Device T1/451 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P22105 | Replace 11kV cross arms and hardware. Work location: Stewart Road, Sanson. Les Robinson attended. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 316 | 313 | 2191 | 0.0066922 | 2.1381e-05 | 2014-11-25 | C | 0.0066922 | 2.1381e-05 | 2015 | 2014-11-25 | C | 7 | 0.0066922 | 2.1381e-05
1 | 3023394 | 2014-11-25 09:00 | 2014-11-25 13:05 | 244.8333 | 72 | 17628 | 0.053914 | 0.00022021 | NAPA ID:04702 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC732 | Replace 11 kV crossarms and ABS IC732. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 244.8333 | 241.8333 | 17412 | 0.053184 | 0.00021992 | 2014-11-25 | B | 0.026592 | 0.00010996 | 2015 | 2014-11-25 | B | 72 | 0.053184 | 0.00021992
1 | 2985439 | 2014-11-25 09:00 | 2014-11-25 14:57 | 357.4167 | 38 | 13581.8333 | 0.041539 | 0.00011622 | NAPA ID:02957 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-032 | Replace poles between ABS SD5-033 and SD5-032. Works location: Kairua Rd. WO TA/2014/23 IR6817 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 357.4167 | 354.4167 | 13467.8333 | 0.041136 | 0.00011607 | 2014-11-25 | B | 0.020568 | 5.8034e-05 | 2015 | 2014-11-25 | B | 38 | 0.041136 | 0.00011607
1 | 2973743 | 2014-11-25 09:31 | 2014-11-25 15:30 | 359.25 | 27 | 9699.75 | 0.029666 | 8.2577e-05 | NAPA ID:03415 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB5 | Replace various arms and poles in work area. Works location: Egmont Rd. WO 10145448. | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 359.25 | 356.25 | 9618.75 | 0.02938 | 8.2469e-05 | 2014-11-25 | B | 0.01469 | 4.1235e-05 | 2015 | 2014-11-25 | B | 27 | 0.02938 | 8.2469e-05
1 | 3141059 | 2014-11-25 09:48 | 2014-11-25 13:28 | 219.7333 | 28 | 6152.5333 | 0.018817 | 8.5636e-05 | Restore Supply on Device LI775 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L7147, 726730 | Replace existing Fuse L1747 and cross arms on pole 726730 as per NAPA OMS Job ID 2963719/ NAPA4315. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 219.7333 | 216.7333 | 6068.5333 | 0.018536 | 8.5524e-05 | 2014-11-25 | C | 0.018536 | 8.5524e-05 | 2015 | 2014-11-25 | C | 28 | 0.018536 | 8.5524e-05
1 | 3139756 | 2014-11-25 10:03 | 2014-11-25 10:19 | 16 | 904 | 15527.8 | 0.047491 | 0.0027648 | Restore Supply on Device CB2762 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 737393, 737394, 737448 | Initial tripping on Stratford GXP CB2762 on O/C causing loss of supply to Douglas Sub. Sub backfed on 11kV Via CB6298 OK. Extensive faults were found on this circuit. First Patrol found a broken 33kV Line down at pole 737393 which had also fallen onto 11k | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 17.1768 | 14.1768 | 12815.8 | 0.039145 | 0.0027612 | 2014-11-25 | C | 0.039145 | 0.0027612 | 2015 | 2014-11-25 | C | 904 | 0.039145 | 0.0027612
1 | 3140836 | 2014-11-25 12:27 | 2014-11-25 15:01 | 154.25 | 163 | 25142.75 | 0.076897 | 0.00049852 | Restore Supply on Device S561 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 797283 | Re bolted cross arm to pole 797283. Faultman could not climb pole so waited for truck to arrive. Materials used: 1 x 63 Amp Pole Fuse. James Matthews attended. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 154.25 | 151.25 | 24653.75 | 0.075303 | 0.00049787 | 2014-11-25 | C | 0.075303 | 0.00049787 | 2015 | 2014-11-25 | C | 163 | 0.075303 | 0.00049787
1 | 2973741 | 2014-11-25 13:01 | 2014-11-25 15:51 | 170.45 | 4 | 681.8 | 0.0020852 | 1.2234e-05 | NAPA ID:04320 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1747 | 11kv pole and cross arm replacement at Powerhouse Road. Works location: Powerhouse Rd Kakaramea. WO 60914PE. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 170.45 | 167.45 | 669.8 | 0.0020459 | 1.2218e-05 | 2014-11-25 | B | 0.0010229 | 6.109e-06 | 2015 | 2014-11-25 | B | 4 | 0.0020459 | 1.2218e-05
1 | 3142527 | 2014-11-25 19:09 | 2014-11-25 20:38 | 89.3167 | 303 | 27062.95 | 0.08277 | 0.0009267 | Restore Supply on Device XT45 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | XT45 | Parkville CB XT40 tripped - no flags. Line patrolled. Sectionalised and supply restored with no apparent fault. Andrew Tuhura attended. | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 89.3167 | 86.3167 | 26153.95 | 0.079885 | 0.00092549 | 2014-11-25 | C | 0.079885 | 0.00092549 | 2015 | 2014-11-25 | C | 303 | 0.079885 | 0.00092549
1 | 3142837 | 2014-11-25 20:13 | 2014-11-25 22:24 | 131 | 61 | 7991 | 0.02444 | 0.00018656 | Restore Supply on Device TA720 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 713334 | Replaced burnt crossarm and associated gear as well as 3x drop out units. Kaine MacKay and Craig Brogden attended. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 131 | 128 | 7808 | 0.023849 | 0.00018632 | 2014-11-25 | C | 0.023849 | 0.00018632 | 2015 | 2014-11-25 | C | 61 | 0.023849 | 0.00018632
1 | 3142920 | 2014-11-25 22:58 | 2014-11-26 01:04 | 126.2333 | 1 | 126.2333 | 0.00038607 | 3.0584e-06 | Restore Supply on Device 1550 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 897 | removed Oppossum and replaced 2X 2a HV Fuses. | F2 | KATERE 7 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 126.2333 | 123.2333 | 123.2333 | 0.00037641 | 3.0544e-06 | 2014-11-25 | C | 0.00037641 | 3.054e-06 | 2015 | 2014-11-25 | C | 1 | 0.00037641 | 3.0544e-06
1 | 3157502 | 2014-11-26 01:11 | 2014-11-26 16:38 | 926.9167 | 96 | 18930.2 | 0.057897 | 0.00029361 | Restore Supply on Device CB1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V15 | CB 1 Tripped B Ph O/C E/F - Lines Down Found during Sectionalising - Isolated at ABS's V2, V3,& V15 and Fuses V16 - Unable to install any back feed due to Line Break at Pole P068079 - Lines Repaired and Feeder returned to service - Used 2x sleeves, 2 x B | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 197.1896 | 194.1896 | 18642.2 | 0.056941 | 0.00029322 | 2014-11-26 | C | 0.056941 | 0.00029322 | 2015 | 2014-11-26 | C | 96 | 0.056941 | 0.00029322
1 | 3142927 | 2014-11-26 02:40 | 2014-11-26 03:54 | 74 | 53 | 3922 | 0.011995 | 0.0001621 | Restore Supply on Device C844 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C844 | Line patrolled and restored with nothing definite found but some suspect areas will be defected by faultman | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 74 | 71 | 3763 | 0.011494 | 0.00016188 | 2014-11-26 | C | 0.011494 | 0.00016188 | 2015 | 2014-11-26 | C | 53 | 0.011494 | 0.00016188
1 | 3143216 | 2014-11-26 04:44 | 2014-11-26 12:22 | 458.4167 | 237 | 25423.0833 | 0.077755 | 0.00072485 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 790853 | CB10 A/R, L/O, E/F. Sectionalised & Patrolled and lines down found at Pole 790853. Temp Line Break made at Pole 790853 and feeder livened beyond ABS177. Lines down were repaired and then another shutdown required from ABS 177 to close temp line break. Ma | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 107.2704 | 104.2704 | 24712.0833 | 0.075481 | 0.0007239 | 2014-11-26 | C | 0.075481 | 0.0007239 | 2015 | 2014-11-26 | C | 237 | 0.075481 | 0.0007239
1 | 3143940 | 2014-11-26 06:04 | 2014-11-26 09:47 | 223.2 | 23 | 1636.3333 | 0.0050046 | 7.0344e-05 | Restore Supply on Device T8/211 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Pole P11367 | 6.45 MERCURY PHONED TO ADVISE CUSTOMER PHONED TO SAY ARCING LINES ADVISED JOANNE AT SVS HUB net work line is down one phase on 2 spans requesting 2r for assistance to repair these lines | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.1449 | 68.1449 | 1567.3333 | 0.0047873 | 7.0252e-05 | 2014-11-26 | C | 0.0047873 | 7.0252e-05 | 2015 | 2014-11-26 | C | 23 | 0.0047873 | 7.0252e-05
1 | 3173687 | 2014-11-26 07:53 | 2014-11-26 11:44 | 231 | 679 | 51063 | 0.15617 | 0.0020767 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | UNKNOWN - SUSPECT TREE CONTACT | CB7 | CB 7 Tripped A,B,C Ph O/C - No Fault Found during Sectionlising - Suspect Tree contact. Nick Lake attended. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 75.2032 | 72.2032 | 49026 | 0.14975 | 0.002074 | 2014-11-26 | C | 0.14975 | 0.002074 | 2015 | 2014-11-26 | C | 679 | 0.14975 | 0.002074
1 | 3174261 | 2014-11-26 07:59 | 2014-11-26 10:55 | 176 | 510 | 44847 | 0.13716 | 0.0015598 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | UNKNOWN - NO FAULT FOUND | 4242 | Recloser 4242 Tripped E/F L/O - Line patrolled with no fault found during sectionalising. Paul Osbourne and James Prime attended. | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 87.9353 | 84.9353 | 43317 | 0.13231 | 0.0015578 | 2014-11-26 | C | 0.13231 | 0.0015578 | 2015 | 2014-11-26 | C | 510 | 0.13231 | 0.0015578
1 | 2986268 | 2014-11-26 08:11 | 2014-11-26 15:07 | 416 | 5 | 1780 | 0.005444 | 1.5292e-05 | NAPA ID:04261 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4056 | 2 shuts morning and Arvo to replace X-arms. Works location: Awaiti Rd Awaiti WO 10145432 | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 356 | 353 | 1765 | 0.0053911 | 1.5272e-05 | 2014-11-26 | B | 0.0026955 | 7.636e-06 | 2015 | 2014-11-26 | B | 5 | 0.0053911 | 1.5272e-05
1 | 3019459 | 2014-11-26 08:59 | 2014-11-26 10:41 | 101.5667 | 293 | 29759.0333 | 0.091016 | 0.00089612 | NAPA ID:04152 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 341 | Install new high tension cross arm and 11kv fuse carriers with solid links12045 to supply new RMU 12046 and 300kva transformer 2244N. NOTE: Only fuses 12045 installed at this stage. | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 101.5667 | 98.5667 | 28880.0333 | 0.088212 | 0.00089495 | 2014-11-26 | B | 0.044106 | 0.00044747 | 2015 | 2014-11-26 | B | 293 | 0.088212 | 0.00089495
1 | 3013406 | 2014-11-26 09:15 | 2014-11-26 14:57 | 341.6167 | 272 | 92919.7333 | 0.28419 | 0.00083189 | NAPA ID:04051 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9632 | Replace poles. Works location: Kuaotunu, Whitianga. WO 10150350 | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 341.6167 | 338.6167 | 92103.7333 | 0.28132 | 0.0008308 | 2014-11-26 | B | 0.14066 | 0.0004154 | 2015 | 2014-11-26 | B | 272 | 0.28132 | 0.0008308
1 | 2951376 | 2014-11-26 09:16 | 2014-11-26 13:13 | 236.5833 | 4 | 946.3333 | 0.0028943 | 1.2234e-05 | NAPA ID:02721 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 7443 | 11KV POLE REPLACEMENT. Works location: Lake Ferry Rd WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 236.5833 | 233.5833 | 934.3333 | 0.0028538 | 1.2218e-05 | 2014-11-26 | B | 0.0014269 | 6.109e-06 | 2015 | 2014-11-26 | B | 4 | 0.0028538 | 1.2218e-05
1 | 3121381 | 2014-11-26 09:20 | 2014-11-26 16:36 | 435.4333 | 398 | 152452.05 | 0.46626 | 0.0012173 | NAPA ID:05040 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R12692 | Replace pole R12692 and install 11 meter pole and RC. IP93 becomes 9815/1, Fuselinks = 9815/4 & RC=9815 | F3 | ACHILLES AVE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 383.0454 | 380.0454 | 151258.05 | 0.46201 | 0.0012157 | 2014-11-26 | B | 0.231 | 0.00060783 | 2015 | 2014-11-26 | B | 398 | 0.46201 | 0.0012157
1 | 2951360 | 2014-11-26 09:32 | 2014-11-26 15:02 | 330.1667 | 37 | 12216.1667 | 0.037362 | 0.00011316 | NAPA ID:04167 TP_BUNNYTHORPE GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Z140 | Shutdown # 1 Changing 33kv and 11kV xarm fitting new insulators. Works location: Bunnythorpe. WO 10147202 | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 330.1667 | 327.1667 | 12105.1667 | 0.036974 | 0.00011301 | 2014-11-26 | B | 0.018487 | 5.6507e-05 | 2015 | 2014-11-26 | B | 37 | 0.036974 | 0.00011301
1 | 3019546 | 2014-11-26 10:30 | 2014-11-26 12:00 | 90 | 8 | 720 | 0.0022021 | 2.4467e-05 | NAPA ID:04624 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/332 | Replace rusted leaking transformer T1/332. Works location: SHW 3. WO 10150629 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 696 | 0.0021259 | 2.4435e-05 | 2014-11-26 | B | 0.0010629 | 1.2218e-05 | 2015 | 2014-11-26 | B | 8 | 0.0021259 | 2.4435e-05
1 | 3157147 | 2014-11-26 12:38 | 2014-11-26 13:50 | 72.2833 | 11 | 432.85 | 0.0013238 | 3.3643e-05 | Restore Supply on Device T893 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 324224 | Floating Conductor. Work area isolated at Fuse Links 7164. Materials used 2x Cu. binders and 1x 10 Amp HV Fuse Link . Email sent to Jo | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 39.35 | 36.35 | 399.85 | 0.0012213 | 3.3599e-05 | 2014-11-26 | C | 0.0012213 | 3.3599e-05 | 2015 | 2014-11-26 | C | 11 | 0.0012213 | 3.3599e-05
1 | 3139737 | 2014-11-26 13:02 | 2014-11-26 13:42 | 39.7167 | 8 | 317.7333 | 0.00097176 | 2.4467e-05 | NAPA ID:05101 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 765152 | Replace Broken pole and repair lines down. Works location: Maikaikatea Rd, Pehu. WO 10166119. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 39.7167 | 36.7167 | 293.7333 | 0.00089719 | 2.4435e-05 | 2014-11-26 | B | 0.00044859 | 1.2218e-05 | 2015 | 2014-11-26 | B | 8 | 0.00089719 | 2.4435e-05
1 | 3157866 | 2014-11-26 14:01 | 2014-11-26 15:15 | 74.5 | 1 | 74.5 | 0.00022785 | 3.0584e-06 | Restore Supply on Device N2165 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712087 | replace 3 amp ddo fuse at pole 712087. cause: unknown. 1 out 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 74.5 | 71.5 | 71.5 | 0.00021839 | 3.0544e-06 | 2014-11-26 | C | 0.00021839 | 3.054e-06 | 2015 | 2014-11-26 | C | 1 | 0.00021839 | 3.0544e-06
1 | 3158271 | 2014-11-26 16:36 | 2014-11-26 19:40 | 183.4333 | 1759 | 84281.95 | 0.25777 | 0.0053798 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | S5453 | cable fault between swgear S5453& sc4500 Faulty indication on Swgear sc4-807. At 16:36, Triton Sub, CB 3 Central Triton Feeder, Tripped, No Flags, L/O. Faultmen were dispatched and investigation began. Feeder sectionalised. During sectionalising, it wa | F2 | CENTRAL TRITON | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 47.9147 | 44.9147 | 79004.95 | 0.24131 | 0.0053727 | 2014-11-26 | C | 0.24131 | 0.0053727 | 2015 | 2014-11-26 | C | 1759 | 0.24131 | 0.0053727
1 | 3161423 | 2014-11-26 18:47 | 2014-11-26 21:48 | 180.2667 | 2 | 360.5333 | 0.0011027 | 6.1168e-06 | Restore Supply on Device 7480 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 839113 | No Power. Floating conductor has burnt through crossarm and burnt top off wooden pole. Temp repairs carried out. 1 x arm and 3 x insulators. Fuses opened at 7480 for isolation. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 180.2667 | 177.2667 | 354.5333 | 0.0010829 | 6.1088e-06 | 2014-11-26 | C | 0.0010829 | 6.109e-06 | 2015 | 2014-11-26 | C | 2 | 0.0010829 | 6.1088e-06
1 | 3171647 | 2014-11-26 19:24 | 2014-11-27 01:45 | 381.25 | 5 | 1492 | 0.0045632 | 1.5292e-05 | Restore Supply on Device 1130 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 782018 | Used 50 M conductor 4 x Joiner. Re slagged Span at Pole 782018. Karl Roger attended. | F4 | MISSION RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 298.4 | 295.4 | 1477 | 0.0045114 | 1.5272e-05 | 2014-11-26 | C | 0.0045114 | 1.5272e-05 | 2015 | 2014-11-26 | C | 5 | 0.0045114 | 1.5272e-05
1 | 3171680 | 2014-11-27 05:33 | 2014-11-27 07:23 | 110.1 | 1 | 110.1 | 0.00033673 | 3.0584e-06 | Restore Supply on Device TC2831 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1316 H2365 | 2 x 8amp DDO FUSE DUE TO BIRD STRIKE NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | WAIRERE RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 110.1 | 107.1 | 107.1 | 0.00032713 | 3.0544e-06 | 2014-11-27 | C | 0.00032713 | 3.054e-06 | 2015 | 2014-11-27 | C | 1 | 0.00032713 | 3.0544e-06
1 | 3171684 | 2014-11-27 05:44 | 2014-11-27 10:09 | 265.55 | 1 | 265.55 | 0.00081216 | 3.0584e-06 | Restore Supply on Device P1150 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | ddo fuse # 6299 | Replace 2 x ht 2amp ddo fuses at ddo fuse # 6299. 2 out 3 phases. paradise duck hit lines. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 265.55 | 262.55 | 262.55 | 0.00080194 | 3.0544e-06 | 2014-11-27 | C | 0.00080194 | 3.054e-06 | 2015 | 2014-11-27 | C | 1 | 0.00080194 | 3.0544e-06
1 | 3011587 | 2014-11-27 08:15 | 2014-11-27 14:58 | 402.6333 | 58 | 23352.7333 | 0.071423 | 0.00017739 | NAPA ID:03595 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11KV pole 818232 | isolate T1844, so that live line break can be made 818232. Works location: East St WO 10140873 IR6938 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 402.6333 | 399.6333 | 23178.7333 | 0.070798 | 0.00017716 | 2014-11-27 | B | 0.035399 | 8.8578e-05 | 2015 | 2014-11-27 | B | 58 | 0.070798 | 0.00017716
1 | 3021603 | 2014-11-27 08:15 | 2014-11-27 12:58 | 283.2667 | 24 | 6798.4 | 0.020792 | 7.3402e-05 | NAPA ID:04352 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS 2106 | Shut and standover for Asplundh Asplundh P.O 135035. Works location: Wentworth Valley WO 10165405 | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 283.2667 | 280.2667 | 6726.4 | 0.020545 | 7.3306e-05 | 2014-11-27 | B | 0.010273 | 3.6653e-05 | 2015 | 2014-11-27 | B | 24 | 0.020545 | 7.3306e-05
1 | 2986661 | 2014-11-27 08:30 | 2014-11-27 14:42 | 371.2667 | 32 | 11880.5333 | 0.036336 | 9.787e-05 | NAPA ID:04299 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6525 | Change poles or Wire run. Works location: Whenuku Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 371.2667 | 368.2667 | 11784.5333 | 0.035995 | 9.7742e-05 | 2014-11-27 | B | 0.017997 | 4.8871e-05 | 2015 | 2014-11-27 | B | 32 | 0.035995 | 9.7742e-05
1 | 3116962 | 2014-11-27 09:15 | 2014-11-27 14:05 | 290 | 3 | 870 | 0.0026608 | 9.1753e-06 | NAPA ID:04965 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TB2-085 | SITE 1 -REPLACE TX TB2-085 ALL ARMS DUE TO POOR CONDITION . SITE 2 - CHECK AND REPAIR DDO UNIT SITE TB2-026 Works location: Beach RD Pukakura Rd WO 10148382 IR7221 | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 290 | 287 | 861 | 0.0026299 | 9.1633e-06 | 2014-11-27 | B | 0.0013149 | 4.582e-06 | 2015 | 2014-11-27 | B | 3 | 0.0026299 | 9.1633e-06
1 | 3012895 | 2014-11-27 09:30 | 2014-11-27 14:52 | 322 | 25 | 914 | 0.0027954 | 7.6461e-05 | NAPA ID:03680 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 748160 | Replace various arms and poles in work area. Works location: Egmont Rd WO 10145448 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 36.56 | 33.56 | 839 | 0.0025627 | 7.6361e-05 | 2014-11-27 | B | 0.0012813 | 3.818e-05 | 2015 | 2014-11-27 | B | 25 | 0.0025627 | 7.6361e-05
1 | 3139634 | 2014-11-27 09:33 | 2014-11-27 12:48 | 195 | 1 | 195 | 0.00059639 | 3.0584e-06 | NAPA ID:05104 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TF6-097 | REPLACE TRANSFORMER TF6-097. Works location: Rangiuri Rd WO 10165124 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 195 | 192 | 192 | 0.00058645 | 3.0544e-06 | 2014-11-27 | B | 0.00029322 | 1.527e-06 | 2015 | 2014-11-27 | B | 1 | 0.00058645 | 3.0544e-06
1 | 3023393 | 2014-11-27 09:46 | 2014-11-27 14:20 | 274.75 | 38 | 10440.5 | 0.031931 | 0.00011622 | NAPA ID:02962 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 383448 | Open switch SD5-032, Then LLP required to disconect 11kv jumpers at pole 383448 (G&B). once completed cancel LLP and take out A/P to replace poles and conductor between Live Line gap at pole 383448 and SD5-033.Then LLP required to re-connect jumpers at po | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 274.75 | 271.75 | 10326.5 | 0.031542 | 0.00011607 | 2014-11-27 | B | 0.015771 | 5.8034e-05 | 2015 | 2014-11-27 | B | 38 | 0.031542 | 0.00011607
1 | 3013428 | 2014-11-27 10:12 | 2014-11-27 11:24 | 71.2167 | 16 | 1139.4667 | 0.003485 | 4.8935e-05 | NAPA ID:04313 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Linkbox SA2-037 | Maintanence on Linkbox SA2-037. Works location: Canon Rd WO 10142547 | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 71.2167 | 68.2167 | 1091.4667 | 0.0033338 | 4.8871e-05 | 2014-11-27 | B | 0.0016669 | 2.4435e-05 | 2015 | 2014-11-27 | B | 16 | 0.0033338 | 4.8871e-05
1 | 3172371 | 2014-11-27 11:37 | 2014-11-27 13:38 | 121.6667 | 5 | 608.3333 | 0.0018605 | 1.5292e-05 | Restore Supply on Device 7317 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 372025 | Faultman found broken polymers which had caused line clash & blown fuses 7317. Shutdown at Fuses 7317 & Polymer strains & deadend replaced. 2x HV fuses replaced & work area relivened ok | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 121.6667 | 118.6667 | 593.3333 | 0.0018123 | 1.5272e-05 | 2014-11-27 | C | 0.0018123 | 1.5272e-05 | 2015 | 2014-11-27 | C | 5 | 0.0018123 | 1.5272e-05
1 | 3091722 | 2014-11-27 11:59 | 2014-11-27 13:52 | 113 | 1 | 113 | 0.0003456 | 3.0584e-06 | NAPA ID:04835 KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole T13164 | Change pole T13164. Works location: Thames Coast WO 10162264 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 113 | 110 | 110 | 0.00033599 | 3.0544e-06 | 2014-11-27 | B | 0.00016799 | 1.527e-06 | 2015 | 2014-11-27 | B | 1 | 0.00033599 | 3.0544e-06
1 | 3018898 | 2014-11-27 12:08 | 2014-11-27 13:23 | 75.1333 | 59 | 4432.8667 | 0.013558 | 0.00018045 | NAPA ID:04318 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer TA2-029 | Maintanence on Linkbox TA2-029. Works location: Moana Dr WO 10142547 | F4 | BOWENTOWN | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 75.1333 | 72.1333 | 4255.8667 | 0.012999 | 0.00018021 | 2014-11-27 | B | 0.0064996 | 9.0105e-05 | 2015 | 2014-11-27 | B | 59 | 0.012999 | 0.00018021
1 | 3172696 | 2014-11-27 12:27 | 2014-11-27 13:57 | 89.6167 | 465 | 4533.3 | 0.013865 | 0.0014222 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 207500 | Blown 11kV Jumper at Pole 207500. Feeder isolated Between Recloser 9225 and ABS SA2-003. Backfeed put in via Recloser 9405. Jumper rejoined | F3 | ATHENREE | WAIHI BEACH SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 9.749 | 6.749 | 3138.3 | 0.0095857 | 0.0014203 | 2014-11-27 | C | 0.0095857 | 0.0014203 | 2015 | 2014-11-27 | C | 465 | 0.0095857 | 0.0014203
1 | 3175673 | 2014-11-27 13:10 | 2014-11-27 18:02 | 292 | 126 | 29086.9167 | 0.08896 | 0.00038536 | Restore Supply on Device C948 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 827995 | Trip, O/C, Non Scadarised breaker so NOC not aware of tripping for awhile. Feeder had autorecloser disabled due to Tree Workers on line. Feeder sectionalised and relivened ok. Patrol carried out and crossarm had twisted over on pole and required re attach | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 230.8485 | 227.8485 | 28708.9167 | 0.087689 | 0.00038486 | 2014-11-27 | C | 0.087689 | 0.00038486 | 2015 | 2014-11-27 | C | 126 | 0.087689 | 0.00038486
1 | 3173624 | 2014-11-27 13:11 | 2014-11-27 17:28 | 257.6333 | 1 | 257.6333 | 0.00078795 | 3.0584e-06 | Restore Supply on Device T1882 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | TX T1882, Bruce Rd, Masterton | tx replaced Tx T1882 cause : tx blown due to trees touching tx on pole 839133 cust owned trees within growth zone NDR # 23452 Full power restored Nothing else repaired or replaced Adjacent assets - ok | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 257.6333 | 254.6333 | 254.6333 | 0.00077776 | 3.0544e-06 | 2014-11-27 | C | 0.00077776 | 3.054e-06 | 2015 | 2014-11-27 | C | 1 | 0.00077776 | 3.0544e-06
1 | 3176154 | 2014-11-27 16:00 | 2014-11-27 17:51 | 111.6 | 16 | 1369.9 | 0.0041897 | 4.8935e-05 | Restore Supply on Device X2044 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803730 | replaced 2x 10a hv fuse links at fuses 458 . nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 85.6188 | 82.6188 | 1321.9 | 0.0040376 | 4.8871e-05 | 2014-11-27 | C | 0.0040376 | 4.8871e-05 | 2015 | 2014-11-27 | C | 16 | 0.0040376 | 4.8871e-05
1 | 3176022 | 2014-11-27 16:07 | 2014-11-27 17:09 | 62.1 | 1 | 62.1 | 0.00018993 | 3.0584e-06 | Restore Supply on Device T8/265 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 362870 | wire off insulator 11kv, worked through control and rebound wire onto 11kv insulator, used 3x binder. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | HUKANUI | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 62.1 | 59.1 | 59.1 | 0.00018052 | 3.0544e-06 | 2014-11-27 | C | 0.00018052 | 3.054e-06 | 2015 | 2014-11-27 | C | 1 | 0.00018052 | 3.0544e-06
1 | 3177551 | 2014-11-27 17:33 | 2014-11-27 20:46 | 192.3167 | 417 | 79826.6167 | 0.24414 | 0.0012754 | Restore Supply on Device C937 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 838529 | Tree in lines at pole 838529 | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 191.4307 | 188.4307 | 78575.6167 | 0.24 | 0.0012737 | 2014-11-27 | C | 0.24 | 0.0012737 | 2015 | 2014-11-27 | C | 417 | 0.24 | 0.0012737
1 | 3177995 | 2014-11-27 18:07 | 2014-11-27 19:35 | 88.1667 | 1 | 88.1667 | 0.00026965 | 3.0584e-06 | Restore Supply on Device T2/637 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p29800 | Replaced replaced 2x 6a hv fuses links fuses D99 due to bird strike. nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88.1667 | 85.1667 | 85.1667 | 0.00026014 | 3.0544e-06 | 2014-11-27 | C | 0.00026013 | 3.054e-06 | 2015 | 2014-11-27 | C | 1 | 0.00026014 | 3.0544e-06
1 | 3178112 | 2014-11-28 01:13 | 2014-11-28 05:40 | 267 | 104 | 19704 | 0.060263 | 0.00031808 | Restore Supply on Device 180 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 745861 | Car V Pole Pole Number 745861 NDR Number 43958 Isolation Points ABS 180 & ABS 408 Back Feed in at ABS 115 used 1x Pole 1 X H/T crossarm & Hardware 1 X L/V Crossarm & Hardware 1 X Tap Off L/V Crossarm & Hardware . Outage reflected under OMS Job ID 317 | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 189.4615 | 186.4615 | 19392 | 0.059231 | 0.00031766 | 2014-11-28 | C | 0.059231 | 0.00031766 | 2015 | 2014-11-28 | C | 104 | 0.059231 | 0.00031766
1 | 3178454 | 2014-11-28 02:52 | 2014-11-28 03:07 | 15 | 268 | 4020 | 0.012295 | 0.00081966 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 7131 | CB 7131 tripped. No flags. Not patrolled. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 3216 | 0.009823 | 0.00081859 | 2014-11-28 | C | 0.009823 | 0.00081859 | 2015 | 2014-11-28 | C | 268 | 0.009823 | 0.00081859
1 | 3180364 | 2014-11-28 04:50 | 2014-11-28 10:59 | 369.5 | 408 | 86706.25 | 0.26518 | 0.0012478 | Restore Supply on Device D11 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 3182134 | Initial tripping on Strahmore CB7131 at 02:52. Reclosed OK (Refer OMS 3180364). CB 7131 tripped again at 04:50. A reclose attempt caused Douglas D11 tripping causing loss of supply to Strathmore. CB D11 restored OK. CB 7131 patrolled and sectionalised wi | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 212.5153 | 209.5153 | 85482.25 | 0.2611 | 0.0012462 | 2014-11-28 | C | 0.2611 | 0.0012462 | 2015 | 2014-11-28 | C | 408 | 0.2611 | 0.0012462
1 | 3013358 | 2014-11-28 08:42 | 2014-11-28 10:16 | 93.8833 | 6 | 563.3 | 0.0017228 | 1.8351e-05 | NAPA ID:04420 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 461 | Isolation of 11kV line for Treescape. Works location: Mangakukeke Rd, Mangaweka. PPPD 46537. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 93.8833 | 90.8833 | 545.3 | 0.0016656 | 1.8327e-05 | 2014-11-28 | B | 0.00083279 | 9.163e-06 | 2015 | 2014-11-28 | B | 6 | 0.0016656 | 1.8327e-05
1 | 3019724 | 2014-11-28 09:00 | 2014-11-28 13:36 | 276 | 15 | 4140 | 0.012662 | 4.5876e-05 | NAPA ID:03677 TP_CARRINGTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1032 | Replace 33kV Faultman found broken 11kV jumper. Backfeed installed by closing ABS S176. Work area isolated at ABS S161 and S10. Jumper 2x joints replaced & network restored to normal. Lucas Grant and Neville Pope attended. Cross arms and broken 33kvV insu | F2 | BELL BLOCK 5 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 276 | 273 | 4095 | 0.012508 | 4.5816e-05 | 2014-11-28 | B | 0.0062539 | 2.2908e-05 | 2015 | 2014-11-28 | B | 15 | 0.012508 | 4.5816e-05
1 | 2986691 | 2014-11-28 09:15 | 2014-11-28 14:36 | 320.45 | 4 | 1281.8 | 0.0039203 | 1.2234e-05 | NAPA ID:04324 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1747 | 11kV pole and cross arm replacement. Works location: Powerhouse Rd Kakaramea. WO 60914PE | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 320.45 | 317.45 | 1269.8 | 0.0038785 | 1.2218e-05 | 2014-11-28 | B | 0.0019393 | 6.109e-06 | 2015 | 2014-11-28 | B | 4 | 0.0038785 | 1.2218e-05
1 | 3018910 | 2014-11-28 09:45 | 2014-11-28 14:15 | 270 | 4 | 1080 | 0.0033031 | 1.2234e-05 | NAPA ID:02808 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF8-009 | To remove the transformer, replace 400V Arms on TF8-009 & install 400V Fuses. Works location: Otamarahau Rd. WO 477863 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 270 | 267 | 1068 | 0.0032621 | 1.2218e-05 | 2014-11-28 | B | 0.0016311 | 6.109e-06 | 2015 | 2014-11-28 | B | 4 | 0.0032621 | 1.2218e-05
1 | 3184224 | 2014-11-28 12:35 | 2014-11-28 15:39 | 183.1333 | 1 | 183.1333 | 0.0005601 | 3.0584e-06 | Restore Supply on Device T9/485 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P29036 | Replaced 2 x 6A HV fuses; unknown cause. All other assets okay; nothing else replaced. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 183.1333 | 180.1333 | 180.1333 | 0.0005502 | 3.0544e-06 | 2014-11-28 | C | 0.0005502 | 3.054e-06 | 2015 | 2014-11-28 | C | 1 | 0.0005502 | 3.0544e-06
1 | 3184242 | 2014-11-28 12:52 | 2014-11-28 14:26 | 94.2 | 38 | 3579.6 | 0.010948 | 0.00011622 | Restore Supply on Device IC420 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | O3022 | Isolation between ABS IC420 and ABS 456 to repair broken Jumper at Pole O3022. Stu Simpson attended. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 94.2 | 91.2 | 3465.6 | 0.010585 | 0.00011607 | 2014-11-28 | C | 0.010585 | 0.00011607 | 2015 | 2014-11-28 | C | 38 | 0.010585 | 0.00011607
1 | 3191431 | 2014-11-28 15:31 | 2014-11-28 16:52 | 81.8667 | 344 | 21576.65 | 0.065991 | 0.0010521 | Restore Supply on Device RC5 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | E12873 | Tripping on Recloser CB RC05 on O/C. Feeder patrolled and tree branch found lying across 2 phases at Pole E12873. Removed OK with fuse stick and relivened. 2 Poplar trees within notice zone, Paul Cooper will advise Colin Winch (Photos taken). Perry Hicks | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 62.7228 | 59.7228 | 20544.65 | 0.062752 | 0.0010507 | 2014-11-28 | C | 0.062752 | 0.0010507 | 2015 | 2014-11-28 | C | 344 | 0.062752 | 0.0010507
1 | 3191937 | 2014-11-28 16:10 | 2014-11-28 18:47 | 157 | 6 | 611.6667 | 0.0018707 | 1.8351e-05 | Restore Supply on Device T9/24 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 373750 | Faultman found a floating wire at pole 373750 while attending a fault call, line was isolated at Fuses V18 to rebind in the conductor. Materials ued 2 clamp tops 2 armourguards. Andrew Tuhura attended. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 101.9444 | 98.9444 | 593.6667 | 0.0018133 | 1.8327e-05 | 2014-11-28 | C | 0.0018133 | 1.8327e-05 | 2015 | 2014-11-28 | C | 6 | 0.0018133 | 1.8327e-05
1 | 3192009 | 2014-11-28 18:39 | 2014-11-28 19:42 | 63 | 31 | 1953 | 0.0059731 | 9.4811e-05 | Restore Supply on Device WH105 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 728374 | found blown jumper at pole 728374 isolated at fuses WH105 materials 1 jumper 1 sleave 1epo bevan hughes attended | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 1860 | 0.0056812 | 9.4687e-05 | 2014-11-28 | C | 0.0056812 | 9.4687e-05 | 2015 | 2014-11-28 | C | 31 | 0.0056812 | 9.4687e-05
1 | 3192377 | 2014-11-28 19:38 | 2014-11-28 20:33 | 55 | 4 | 220 | 0.00067285 | 1.2234e-05 | Restore Supply on Device TF8-009 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF8-009 | at 19:38, Pongakawa Sub, CB 3 Rotoehu Feeder. Found transformer TF8-009 to be faulty. Own Isolation & AP and repairs carried out. All Power Restored on completion. T J Tanoa Attended. 1x Transformer Replaced. See Below for more details of this fault from | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 208 | 0.00063532 | 1.2218e-05 | 2014-11-28 | C | 0.00063532 | 1.2218e-05 | 2015 | 2014-11-28 | C | 4 | 0.00063532 | 1.2218e-05
1 | 3192083 | 2014-11-28 20:50 | 2014-11-28 21:29 | 39.35 | 118 | 4643.3 | 0.014201 | 0.00036089 | Restore Supply on Device 4870 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 3565T | 20:35 - Created 2R request as further investigation has shown that cable needs to be reterminated inside the transformer, requiring TX to be offloaded. Work can not reasonably be completed by one faultman under 1R. Reterminated cable joint failed due to | F1 | BLAKE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 39.35 | 36.35 | 4289.3 | 0.013101 | 0.00036042 | 2014-11-28 | C | 0.013101 | 0.00036042 | 2015 | 2014-11-28 | C | 118 | 0.013101 | 0.00036042
1 | 3013386 | 2014-11-28 22:30 | 2014-11-29 00:48 | 138 | 117 | 16146 | 0.049381 | 0.00035784 | NAPA ID:04273 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/62 | Repair Oil Leak on HV Bushing @ Tx T3/62. Works location: Awahuri Rd Feilding. WO 10155441 | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 138 | 135 | 15795 | 0.048245 | 0.00035737 | 2014-11-28 | B | 0.024122 | 0.00017868 | 2015 | 2014-11-28 | B | 117 | 0.048245 | 0.00035737
1 | 3193090 | 2014-11-29 05:51 | 2014-11-29 08:15 | 144.2667 | 510 | 28179.7 | 0.086185 | 0.0015598 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4242 | Recloser 4242 tripped on O/C and E/F flags, line was sectionalised and patrolled and no fault was found. Alan Cox and Gary Fisher attended. | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 55.2543 | 52.2543 | 26649.7 | 0.081399 | 0.0015578 | 2014-11-29 | C | 0.081399 | 0.0015578 | 2015 | 2014-11-29 | C | 510 | 0.081399 | 0.0015578
1 | 2912302 | 2014-11-29 08:34 | 2014-11-29 15:19 | 405 | 42 | 17010 | 0.052024 | 0.00012845 | NAPA ID:03806 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12741 | To make live line break at pole p12741 and replace ABS poles Q37 & Q34. Works location: Tiraumea Rd Pahiatua. WO 10144449. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 405 | 402 | 16884 | 0.051571 | 0.00012829 | 2014-11-29 | B | 0.025785 | 6.4143e-05 | 2015 | 2014-11-29 | B | 42 | 0.051571 | 0.00012829
1 | 3013175 | 2014-11-29 09:01 | 2014-11-29 12:25 | 203.65 | 29 | 5905.85 | 0.018063 | 8.8694e-05 | NAPA ID:03684 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1106 | To remove ABS IC1106. Replace arms on poles K2185 & K13544. Works location: No 9 Rd Springdale. WO 476789. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 203.65 | 200.65 | 5818.85 | 0.017773 | 8.8578e-05 | 2014-11-29 | B | 0.0088866 | 4.4289e-05 | 2015 | 2014-11-29 | B | 29 | 0.017773 | 8.8578e-05
1 | 3194408 | 2014-11-29 12:55 | 2014-11-29 15:08 | 133.3667 | 1 | 133.3667 | 0.00040789 | 3.0584e-06 | Restore Supply on Device W2265 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 725883 | HV 2 FUSE , SUSPECT DUE TO LIGHTNING STORM 2 MONTHS AGO NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. Email sent to Alicia to check for SAIDI component. | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 133.3667 | 130.3667 | 130.3667 | 0.0003982 | 3.0544e-06 | 2014-11-29 | C | 0.0003982 | 3.054e-06 | 2015 | 2014-11-29 | C | 1 | 0.0003982 | 3.0544e-06
1 | 3194695 | 2014-11-29 14:17 | 2014-11-29 16:14 | 116.9667 | 1 | 116.9667 | 0.00035773 | 3.0584e-06 | Restore Supply on Device T2286 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Fuses 7298 | Faultman found a blown fuse at Fuses 7298, line patrolled no fault found. 1 X 10 Amp HV rewirable replaced. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 116.9667 | 113.9667 | 113.9667 | 0.0003481 | 3.0544e-06 | 2014-11-29 | C | 0.0003481 | 3.054e-06 | 2015 | 2014-11-29 | C | 1 | 0.0003481 | 3.0544e-06
1 | 3194716 | 2014-11-29 15:03 | 2014-11-29 16:17 | 74.2333 | 682 | 28728.7 | 0.087864 | 0.0020858 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7 | CB 7 tripped on A, B & C ,O/C flags, line patrolled and sectionalised and no fault was found. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 42.1242 | 39.1242 | 26682.7 | 0.0815 | 0.0020831 | 2014-11-29 | C | 0.0815 | 0.0020831 | 2015 | 2014-11-29 | C | 682 | 0.0815 | 0.0020831
1 | 3196556 | 2014-11-29 15:35 | 2014-11-29 17:36 | 120.55 | 127 | 13680.95 | 0.041842 | 0.00038842 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4200/2 | Recloser 4200 tripped on B & C phase O/C flags. Line was patrolled and sectionalised and no fault was found. Alan Cox and Gary Fisher attended. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 107.724 | 104.724 | 13299.95 | 0.040624 | 0.00038791 | 2014-11-29 | C | 0.040624 | 0.00038791 | 2015 | 2014-11-29 | C | 127 | 0.040624 | 0.00038791
1 | 3196949 | 2014-11-29 16:29 | 2014-11-29 18:23 | 113.65 | 1 | 113.65 | 0.00034759 | 3.0584e-06 | Restore Supply on Device TC206 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses FC2170 | Faultman replace blown fuse at Fuses FC2170, suspect bird strike. 1 x 3 Amp HV rewirable fuse replaced. No other assets repaired or replaced on site. FM checked adjacent assets and all up to Powerco Standard. | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 113.65 | 110.65 | 110.65 | 0.00033797 | 3.0544e-06 | 2014-11-29 | C | 0.00033797 | 3.054e-06 | 2015 | 2014-11-29 | C | 1 | 0.00033797 | 3.0544e-06
1 | 3197292 | 2014-11-29 18:20 | 2014-11-29 21:04 | 164.5667 | 2 | 233.7667 | 0.00071496 | 6.1168e-06 | Restore Supply on Device X2044 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 458 | Replaced 2x 10Amp HV Fuse Links at Fuses 458 Email sent to Alicia to check for SAIDI component. | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 116.8833 | 113.8833 | 227.7667 | 0.0006957 | 6.1088e-06 | 2014-11-29 | C | 0.0006957 | 6.109e-06 | 2015 | 2014-11-29 | C | 2 | 0.0006957 | 6.1088e-06
1 | 3197328 | 2014-11-29 18:43 | 2014-11-29 22:57 | 254 | 13 | 884 | 0.0027036 | 3.9759e-05 | Restore Supply on Device C935 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | Faultman found broken 11kV jumper. Backfeed installed by closing ABS S176. Work area isolated at ABS S161 and S10. Jumper 2x joints replaced & network restored to normal. Lucas Grant and Neville Pope attended. | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 68 | 65 | 845 | 0.002581 | 3.9708e-05 | 2014-11-29 | C | 0.002581 | 3.9708e-05 | 2015 | 2014-11-29 | C | 13 | 0.002581 | 3.9708e-05
1 | 3197431 | 2014-11-29 22:36 | 2014-11-30 02:20 | 224 | 88 | 14132 | 0.043222 | 0.00026914 | Restore Supply on Device C926 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 845050 | CB C926 A/R, L/O, O/C A & B Phase. Fault locators beyond ABS S571 flashing, so feeder livened up to ABS 571 & then remainder of line patrolled. Found line down & floating conductor, repaired & relivened. Materials used: 3mtrs conductor, conductor joints | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 160.5909 | 157.5909 | 13868 | 0.042359 | 0.00026879 | 2014-11-29 | C | 0.042359 | 0.00026879 | 2015 | 2014-11-29 | C | 88 | 0.042359 | 0.00026879
1 | 3198768 | 2014-11-30 04:34 | 2014-11-30 08:00 | 206.2833 | 510 | 37804 | 0.11562 | 0.0015598 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 802555 | RS 4242/2 Tripped L/O - Faulty HV Insulator found during sectionlising - Isolated at ABS's 1090 & 4242/1 plus Links 4242/6 -backfeed installed via VS 4661/2 - HV Insulator replaces at Pole 802555, feeder restored to normal config - Used 1 x HV insulator, | F4 | TURAKINA | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 74.1255 | 71.1255 | 36274 | 0.1108 | 0.0015578 | 2014-11-30 | C | 0.1108 | 0.0015578 | 2015 | 2014-11-30 | C | 510 | 0.1108 | 0.0015578
1 | 3199981 | 2014-11-30 08:40 | 2014-11-30 10:36 | 116.1833 | 1 | 116.1833 | 0.00035534 | 3.0584e-06 | Restore Supply on Device T9/172 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | v53 | replace 2 x 6 amp ht fuses. 2 out 3 phases. cause: wind. fuse v53. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 116.1833 | 113.1833 | 113.1833 | 0.00034571 | 3.0544e-06 | 2014-11-30 | C | 0.00034571 | 3.054e-06 | 2015 | 2014-11-30 | C | 1 | 0.00034571 | 3.0544e-06
1 | 3203884 | 2014-11-30 09:32 | 2014-11-30 10:25 | 53 | 2 | 106 | 0.00032419 | 6.1168e-06 | Restore Supply on Device 2435T | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2435 |  | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 100 | 0.00030544 | 6.1088e-06 | 2014-11-30 | C | 0.00030544 | 6.109e-06 | 2015 | 2014-11-30 | C | 2 | 0.00030544 | 6.1088e-06
1 | 3200624 | 2014-11-30 11:15 | 2014-11-30 14:31 | 195.95 | 248 | 18739.4667 | 0.057313 | 0.00075849 | Restore Supply on Device KA7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 720282 | CB & Tripped E/F O/C L/O - Arcing Pole Reported by Public - Isolated at ABS's KA774, 6690, & KA743 - Back feed installed via ABS MA 482 - Damaged DDO's replaced - Used 3 Complete DDO's, 3 mtrs of HV and LV conduct, Sleeves of different sizes and 2 connec | F1/F4 | MATAPU | KAPUNI SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 75.5624 | 72.5624 | 17995.4667 | 0.054966 | 0.0007575 | 2014-11-30 | C | 0.054966 | 0.0007575 | 2015 | 2014-11-30 | C | 248 | 0.054966 | 0.0007575
1 | 3200880 | 2014-11-30 11:28 | 2014-11-30 20:49 | 561 | 17 | 9537 | 0.029168 | 5.1993e-05 | Restore Supply on Device V17 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V17 | 12.42 T 9/7 WILL BE OFF OVER NIGHT CANNOT GET TO THE POLE WHICH IS BROKEN FM WANTS TO LEAVE 9 CUSTOMER OFF TO NIGHT AND MAY BE TOMORROW I ADVISED WE WILL NEED TO ORGANISE GENERATORS AND SPOKE TO DAVE COOPER IN CONTROL WHO IS GOING TO TALK TO FM ABOUT A PO | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 561 | 558 | 9486 | 0.028974 | 5.1925e-05 | 2014-11-30 | C | 0.028974 | 5.1925e-05 | 2015 | 2014-11-30 | C | 17 | 0.028974 | 5.1925e-05
1 | 3200929 | 2014-11-30 12:00 | 2014-12-03 11:35 | 4295 | 6 | 5167.7833 | 0.015805 | 1.8351e-05 | Restore Supply on Device X1625 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 803871 | 2 x 10 amp HV fuses at Links 458. Isolated lines that have clashed at Fuses1354. The pole is leaning and lines are low and clashing everyone has power except 1x transformer (X2456) which is feeding a pump. No stock in the paddock and now trying to find t | F4 | RACECOURSE | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 861.2972 | 858.2972 | 5149.7833 | 0.01573 | 1.8327e-05 | 2014-11-30 | C | 0.01573 | 1.8327e-05 | 2015 | 2014-11-30 | C | 6 | 0.01573 | 1.8327e-05
1 | 3201339 | 2014-11-30 13:51 | 2014-11-30 15:42 | 111.35 | 6 | 668.1 | 0.0020433 | 1.8351e-05 | Restore Supply on Device FP1630 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TP2699 | Emergency shutdown to change transformer TP2699 - Transformer was installed approx. 3 weeks ago and load transferred from TE6-054 after it was decommissioned yesterday (OMS 3139700). The new transformer TP2699 has proved to be not compatible with motors | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 111.35 | 108.35 | 650.1 | 0.0019857 | 1.8327e-05 | 2014-11-30 | C | 0.0019857 | 1.8327e-05 | 2015 | 2014-11-30 | C | 6 | 0.0019857 | 1.8327e-05
1 | 3201824 | 2014-11-30 17:06 | 2014-11-30 19:15 | 129.45 | 569 | 4920.5 | 0.015049 | 0.0017402 | Restore Supply on Device K29 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P19892 | CB 7 auto reclosed on B & C phase O/C flags, line had tripped the night before and no fault was found, so after auto reclose got faultman to carry out line patrol again and and floating wire and broken insulator was found at pole P19892, line was isolated | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 8.6476 | 5.6476 | 3213.5 | 0.0098154 | 0.001738 | 2014-11-30 | C | 0.0098154 | 0.001738 | 2015 | 2014-11-30 | C | 569 | 0.0098154 | 0.001738
1 | 3202273 | 2014-11-30 20:41 | 2014-11-30 23:19 | 158 | 248 | 24834 | 0.075953 | 0.00075849 | Restore Supply on Device TA9 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 715982 | CB TA9 tripped on E/F flags, recieved a call from customer at 402 Watino Rd of line down in paddock, faultman found a dead Duck under the line at pole 715982, line was isolated at ABS's TA 914, TA 916 & ABS TA 876. 6 metres of 35mm Ali conductor was used | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 100.1371 | 97.1371 | 24090 | 0.073581 | 0.0007575 | 2014-11-30 | C | 0.073581 | 0.0007575 | 2015 | 2014-11-30 | C | 248 | 0.073581 | 0.0007575
1 | 3095308 | 2014-12-01 05:30 | 2014-12-01 19:12 | 822 | 410 | 17220 | 0.052666 | 0.001254 | NAPA ID:03597 GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 814892 | Close line break at pole 814892 which was made for a shutdown on 06/10/14. Works location: East St Greytown. WO 10140873 IR6938 | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 42 | 39 | 15990 | 0.04884 | 0.0012523 | 2014-12-01 | B | 0.02442 | 0.00062616 | 2015 | 2014-12-01 | B | 410 | 0.04884 | 0.0012523
1 | 3203887 | 2014-12-01 08:32 | 2014-12-01 12:38 | 246.5167 | 105 | 25824.75 | 0.078983 | 0.00032113 | Restore Supply on Device C828 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 833789 | CB C828 Tripped C Ph E/F L/O - Tree contact lines and on fire near pole 833789 - Isolated at ABS's S157 & S193 and CB C828 - Tree Removed, no repairs required to lines. James Matthews attended. | F4 | TAUWERU | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 245.95 | 242.95 | 25509.75 | 0.077918 | 0.00032071 | 2014-12-01 | C | 0.077918 | 0.00032071 | 2015 | 2014-12-01 | C | 105 | 0.077918 | 0.00032071
1 | 3017808 | 2014-12-01 08:37 | 2014-12-04 09:50 | 4392.95 | 161 | 74209.3333 | 0.22696 | 0.00049241 | NAPA ID:03802 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/251 | Replace transformer T6/251 with new city pad. All LV will be back fed during transformer change only. Works location: Carter Crescent. WO 10152197. | F4 | TREMAINE AVE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 460.9275 | 457.9275 | 73726.3333 | 0.22519 | 0.00049176 | 2014-12-01 | B | 0.1126 | 0.00024588 | 2015 | 2014-12-01 | B | 161 | 0.22519 | 0.00049176
1 | 3013399 | 2014-12-01 09:00 | 2014-12-01 15:32 | 391.8667 | 67 | 26255.0667 | 0.080299 | 0.00020491 | NAPA ID:03849 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP558 | REPLACE POLE AND ARMS AS PER SCOPE. Works location: Pyes Pa Rd Taumata Rd. WO 10138318 | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 391.8667 | 388.8667 | 26054.0667 | 0.07958 | 0.00020465 | 2014-12-01 | B | 0.03979 | 0.00010232 | 2015 | 2014-12-01 | B | 67 | 0.07958 | 0.00020465
1 | 3013398 | 2014-12-01 09:15 | 2014-12-01 15:30 | 375 | 134 | 8164 | 0.024969 | 0.00040983 | NAPA ID:04421 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6533 | Replace pole & wire Ohawe. Works location: Ohawe Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60.9254 | 57.9254 | 7762 | 0.023708 | 0.00040929 | 2014-12-01 | B | 0.011854 | 0.00020465 | 2015 | 2014-12-01 | B | 134 | 0.023708 | 0.00040929
1 | 3019512 | 2014-12-01 09:15 | 2014-12-01 15:33 | 378 | 35 | 13230 | 0.040463 | 0.00010704 | NAPA ID:04526 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 449 | 11kv poles and overhead lines upgrade of Pheney Road connect recloser ready for commissioning and remove 11kv fuses 6604 from the network. Works location: Pheney Rd New Plymouth WO IR7213 | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 378 | 375 | 13125 | 0.040089 | 0.0001069 | 2014-12-01 | B | 0.020045 | 5.3452e-05 | 2015 | 2014-12-01 | B | 35 | 0.040089 | 0.0001069
1 | 3036351 | 2014-12-01 09:16 | 2014-12-01 11:29 | 133.8833 | 11 | 1472.7167 | 0.0045042 | 3.3643e-05 | NAPA ID:04509 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC469 | Re-sag lines and repair corroded jumper. Works location: Piako Rd Pipiroa. WO 10149782 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 133.8833 | 130.8833 | 1439.7167 | 0.0043975 | 3.3599e-05 | 2014-12-01 | B | 0.0021988 | 1.6799e-05 | 2015 | 2014-12-01 | B | 11 | 0.0043975 | 3.3599e-05
1 | 3039848 | 2014-12-01 09:42 | 2014-12-01 14:26 | 283.85 | 14 | 3973.9 | 0.012154 | 4.2818e-05 | NAPA ID:04284 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-032 | Replace cross arms on 33kV between 3102 and 66, Papamoa 2. Works location: SHWY 2. WO 10148262. | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 283.85 | 280.85 | 3931.9 | 0.01201 | 4.2762e-05 | 2014-12-01 | B | 0.0060048 | 2.1381e-05 | 2015 | 2014-12-01 | B | 14 | 0.01201 | 4.2762e-05
1 | 3018861 | 2014-12-01 09:51 | 2014-12-01 12:58 | 187.35 | 26 | 4871.1 | 0.014898 | 7.9519e-05 | NAPA ID:03977 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B6 | Replace 11KV ABS B6. Works location: Lockwood Rd, Palmerston North. WO 10160819 | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 187.35 | 184.35 | 4793.1 | 0.01464 | 7.9415e-05 | 2014-12-01 | B | 0.0073201 | 3.9708e-05 | 2015 | 2014-12-01 | B | 26 | 0.01464 | 7.9415e-05
1 | 3204647 | 2014-12-01 11:41 | 2014-12-01 14:00 | 138.9333 | 1 | 138.9333 | 0.00042492 | 3.0584e-06 | Restore Supply on Device X3020 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | X3020 | 2 X 6 AMP FUSES TRESS WITHIN GROWTH ZONE. NDR 23206. TREES TO BE TRIMMED NEXT WEEK. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 138.9333 | 135.9333 | 135.9333 | 0.0004152 | 3.0544e-06 | 2014-12-01 | C | 0.0004152 | 3.054e-06 | 2015 | 2014-12-01 | C | 1 | 0.0004152 | 3.0544e-06
1 | 3210192 | 2014-12-01 13:40 | 2014-12-01 15:38 | 118.0333 | 4 | 384.7667 | 0.0011768 | 1.2234e-05 | Restore Supply on Device X1420 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773975 | Replaced 2x 8a HV Fuses due to unknown at Fuses 774. Email sent to Alicia to check for SAIDI component. | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 96.1917 | 93.1917 | 372.7667 | 0.0011386 | 1.2218e-05 | 2014-12-01 | C | 0.0011386 | 1.2218e-05 | 2015 | 2014-12-01 | C | 4 | 0.0011386 | 1.2218e-05
1 | 3038672 | 2014-12-01 19:02 | 2014-12-02 01:01 | 359.2 | 78 | 28017.6 | 0.08569 | 0.00023856 | NAPA ID:04429 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME EXPRESS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SD4-310 | Maintenance on 11kV Linkbox and RMU. Works location: Maleme St. WO 10142547 | F2 | POOLES RD | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 359.2 | 356.2 | 27783.6 | 0.084863 | 0.00023825 | 2014-12-01 | B | 0.042431 | 0.00011912 | 2015 | 2014-12-01 | B | 78 | 0.084863 | 0.00023825
1 | 3210813 | 2014-12-01 20:18 | 2014-12-01 21:31 | 73.1333 | 19 | 1389.5333 | 0.0042498 | 5.811e-05 | Restore Supply on Device SG7-001 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231017 | Line isolated at fuses SG7-001 to repair broken conductor (16mm galv) at pole 231017 - 10 metres conductor & 6 sleeves only material required. T J Tanoa attended. | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 73.1333 | 70.1333 | 1332.5333 | 0.0040701 | 5.8034e-05 | 2014-12-01 | C | 0.0040701 | 5.8034e-05 | 2015 | 2014-12-01 | C | 19 | 0.0040701 | 5.8034e-05
1 | 3210515 | 2014-12-01 21:00 | 2014-12-01 22:00 | 60 | 5 | 300 | 0.00091753 | 1.5292e-05 | Restore Supply on Device 5475 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 761660 | Worked through control needs to replace TX 3002T requesting 2R and another faultman to help replace to the transformer. Replaced TX 3002T due to lightning HV O/H. Surrounding asset good except will amber defect the crossarm on 764660 as it is a bit sha | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 285 | 0.00087051 | 1.5272e-05 | 2014-12-01 | C | 0.00087051 | 1.5272e-05 | 2015 | 2014-12-01 | C | 5 | 0.00087051 | 1.5272e-05
1 | 3018695 | 2014-12-01 23:01 | 2014-12-01 23:40 | 39.0833 | 32 | 1250.6667 | 0.0038251 | 9.787e-05 | NAPA ID:03405 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P22104 | Close 11kv jumpers on 4 pole structure P22104 note 33kv on same structure. Work slocation: Stewart Rd. WO 10140843 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39.0833 | 36.0833 | 1154.6667 | 0.0035268 | 9.7742e-05 | 2014-12-01 | B | 0.0017634 | 4.8871e-05 | 2015 | 2014-12-01 | B | 32 | 0.0035268 | 9.7742e-05
1 | 3211465 | 2014-12-02 03:14 | 2014-12-02 03:57 | 43.45 | 331 | 7408.5333 | 0.022658 | 0.0010123 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2281 | 7.15am Hilton called to get cleared off job.. located fault which was line down, sectionailised feeder and worked his way along it. 1 transformer off (TC1150) at the moment. Feeds quarry but they have a generator (not included in outage). Isolated at Fu | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 22.3823 | 19.3823 | 6415.5333 | 0.019596 | 0.001011 | 2014-12-02 | C | 0.019596 | 0.001011 | 2015 | 2014-12-02 | C | 331 | 0.019596 | 0.001011
1 | 3212412 | 2014-12-02 05:33 | 2014-12-02 05:52 | 19.3833 | 678 | 13141.9 | 0.040193 | 0.0020736 | Restore Supply on Device 60 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 1 | 1 x A/R on CB 402 @ Waihou GXP along with L/O on CB 60 @ Waitoa sub - O/C flag at Waihou along with 19.3% DTF flag - also 90.1% DTF flag operated on CB 332 at Waihou - CB 60 reclosed - 2 x 1 r requested to carry out line patrol between Waihou/Waitoa/Farme | F1, F2, F3 | PC199-WAITOA 33KV | TP_WAIHOU | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 19.3833 | 16.3833 | 11107.9 | 0.033928 | 0.0020709 | 2014-12-02 | C | 0.033928 | 0.0020709 | 2015 | 2014-12-02 | C | 678 | 0.033928 | 0.0020709
1 | 3213096 | 2014-12-02 06:13 | 2014-12-02 21:45 | 931.6333 | 19 | 17701.0333 | 0.054137 | 5.811e-05 | Restore Supply on Device V16 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | V16 | 16/12 email sent to hub for fault man to clear this job | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 931.6333 | 928.6333 | 17644.0333 | 0.053892 | 5.8034e-05 | 2014-12-02 | C | 0.053892 | 5.8034e-05 | 2015 | 2014-12-02 | C | 19 | 0.053892 | 5.8034e-05
1 | 3213152 | 2014-12-02 07:02 | 2014-12-02 09:14 | 132.1667 | 1 | 132.1667 | 0.00040422 | 3.0584e-06 | Restore Supply on Device X4167 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4132, X4167 | Pole fuse smoking opposite driveway - part power cows on platform 7.03 advised Tallia at svs hub Replace 2 x HT 3 amp fuses and holders at fuse 4132 at TX X4167 replace fuse holder and base and 80 Amp HRC fuse. Cause unknown. No other assets repaired o | F4 | CROFTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 132.1667 | 129.1667 | 129.1667 | 0.00039453 | 3.0544e-06 | 2014-12-02 | C | 0.00039453 | 3.054e-06 | 2015 | 2014-12-02 | C | 1 | 0.00039453 | 3.0544e-06
1 | 3036231 | 2014-12-02 08:42 | 2014-12-02 11:23 | 161.2167 | 90 | 14509.5 | 0.044376 | 0.00027526 | NAPA ID:02725 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S527 | 11KV POLE REPLACEMENT. Works location: Lake Ferry. WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 161.2167 | 158.2167 | 14239.5 | 0.043493 | 0.0002749 | 2014-12-02 | B | 0.021747 | 0.00013745 | 2015 | 2014-12-02 | B | 90 | 0.043493 | 0.0002749
1 | 3059778 | 2014-12-02 08:46 | 2014-12-02 15:11 | 384.7333 | 144 | 55401.6 | 0.16944 | 0.00044041 | NAPA ID:03910 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 207890 | REPLACE HV POLES AND ARMS AS PER SCOPE. Works location: Plummer Point Rd. WO 10148295 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 384.7333 | 381.7333 | 54969.6 | 0.1679 | 0.00043984 | 2014-12-02 | B | 0.08395 | 0.00021992 | 2015 | 2014-12-02 | B | 144 | 0.1679 | 0.00043984
1 | 3059820 | 2014-12-02 09:00 | 2014-12-02 11:35 | 155 | 23 | 3565 | 0.010903 | 7.0344e-05 | NAPA ID:04541 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | SP09 | Tree cutting (Asplundh) Standover required. Works location: Purangi Whitianga WO 10167928 | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 155 | 152 | 3496 | 0.010678 | 7.0252e-05 | 2014-12-02 | B | 0.0053391 | 3.5126e-05 | 2015 | 2014-12-02 | B | 23 | 0.010678 | 7.0252e-05
1 | 3035814 | 2014-12-02 09:16 | 2014-12-02 14:10 | 293.9333 | 293 | 86122.4667 | 0.2634 | 0.00089612 | NAPA ID:03921 TP_BUNNYTHORPE GXP > MILSON SUB > MILSON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/535 | Change Tx T6/535. Works location: Pinadale Pde WO 10158153 | F1 | RUAHINE | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 293.9333 | 290.9333 | 85243.4667 | 0.26037 | 0.00089495 | 2014-12-02 | B | 0.13018 | 0.00044747 | 2015 | 2014-12-02 | B | 293 | 0.26037 | 0.00089495
1 | 3214419 | 2014-12-02 09:20 | 2014-12-02 09:41 | 20.7 | 6 | 124.2 | 0.00037986 | 1.8351e-05 | Restore Supply on Device SE7-053 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SE7-053 | No Power. Line Patrolled. Bird Strike - Dead Swan found. Replaced 2 x 8Amp HV Fuse links. Dave Ngatai attended. | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 20.7 | 17.7 | 106.2 | 0.00032438 | 1.8327e-05 | 2014-12-02 | C | 0.00032438 | 1.8327e-05 | 2015 | 2014-12-02 | C | 6 | 0.00032438 | 1.8327e-05
1 | 3135197 | 2014-12-02 09:30 | 2014-12-02 14:30 | 300 | 27 | 8100 | 0.024773 | 8.2577e-05 | NAPA ID:05096 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | Replace various arms and poles in work area | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 300 | 297 | 8019 | 0.024493 | 8.2469e-05 | 2014-12-02 | B | 0.012247 | 4.1235e-05 | 2015 | 2014-12-02 | B | 27 | 0.024493 | 8.2469e-05
1 | 3024692 | 2014-12-02 09:35 | 2014-12-02 14:40 | 305 | 31 | 9455 | 0.028917 | 9.4811e-05 | NAPA ID:04136 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/177 | Replace 11kv 400v TX cross arms. Works location: Lower Pakihura Rd. WO 10142182. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 305 | 302 | 9362 | 0.028596 | 9.4687e-05 | 2014-12-02 | B | 0.014298 | 4.7344e-05 | 2015 | 2014-12-02 | B | 31 | 0.028596 | 9.4687e-05
1 | 3017059 | 2014-12-02 10:20 | 2014-12-02 15:15 | 295 | 4 | 1180 | 0.0036089 | 1.2234e-05 | NAPA ID:04481 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1852 | Live Line to replace the 11kV D.O.Fuses and Arm. AP to replace the transformer & LV Arms. Works location: Piakoiti Rd Walton. WO IR5140. | F4 | PIAKOITI RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 295 | 292 | 1168 | 0.0035676 | 1.2218e-05 | 2014-12-02 | B | 0.0017838 | 6.109e-06 | 2015 | 2014-12-02 | B | 4 | 0.0035676 | 1.2218e-05
1 | 3013448 | 2014-12-02 12:30 | 2014-12-02 14:22 | 112 | 3 | 336 | 0.0010276 | 9.1753e-06 | NAPA ID:04483 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3156 | To replace the transformer. WOrks location: Te Poi Rd North, Matamata. WO IR5140 | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 112 | 109 | 327 | 0.0009988 | 9.1633e-06 | 2014-12-02 | B | 0.0004994 | 4.582e-06 | 2015 | 2014-12-02 | B | 3 | 0.0009988 | 9.1633e-06
1 | 3059827 | 2014-12-02 12:30 | 2014-12-02 15:18 | 167.65 | 22 | 3688.3 | 0.01128 | 6.7285e-05 | NAPA ID:04572 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 222 | Tree cutting (Asplundh) standover required. Works location: Purangi Whitianga. WO 10167928 | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 167.65 | 164.65 | 3622.3 | 0.011064 | 6.7197e-05 | 2014-12-02 | B | 0.005532 | 3.3599e-05 | 2015 | 2014-12-02 | B | 22 | 0.011064 | 6.7197e-05
1 | 3215251 | 2014-12-02 14:19 | 2014-12-02 16:49 | 150.3 | 1 | 150.3 | 0.00045968 | 3.0584e-06 | Restore Supply on Device TD3-246 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210575, TD3246 | 2 x 3 Amp DDO Fuse at pole 210575. Tx TD3246 - unknown cause HV O/H Full power restored. Nothing else repaired or replaced. Email sent to Alicia Adjacent assets - ok - email sent to Alicia to check for SAIDI component. | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 150.3 | 147.3 | 147.3 | 0.00044992 | 3.0544e-06 | 2014-12-02 | C | 0.00044992 | 3.054e-06 | 2015 | 2014-12-02 | C | 1 | 0.00044992 | 3.0544e-06
1 | 3216888 | 2014-12-02 18:34 | 2014-12-02 19:31 | 57.2667 | 1276 | 10182.7 | 0.031143 | 0.0039025 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P01372 | CB 10 Tripped. No Flags. Auto Backfeed system activated closing RS 10082 and Opening RS 10083. Reported by public that tree feller had dropped tree into lines - Isolated at ABS E70 & ABS E71. Power restored up to both points. Branch found across all 3 lin | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 7.9802 | 4.9802 | 6354.7 | 0.01941 | 0.0038974 | 2014-12-02 | C | 0.01941 | 0.0038974 | 2015 | 2014-12-02 | C | 1276 | 0.01941 | 0.0038974
1 | 3218267 | 2014-12-02 20:52 | 2014-12-02 23:06 | 134.7 | 1 | 134.7 | 0.00041197 | 3.0584e-06 | Restore Supply on Device TC592 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC592 | 8 amp HV fuse replaced, no other assets repaired or replaced on site. | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 134.7 | 131.7 | 131.7 | 0.00040227 | 3.0544e-06 | 2014-12-02 | C | 0.00040227 | 3.054e-06 | 2015 | 2014-12-02 | C | 1 | 0.00040227 | 3.0544e-06
1 | 3024710 | 2014-12-03 05:30 | 2014-12-03 06:22 | 52 | 233 | 12116 | 0.037056 | 0.00071261 | NAPA ID:04070 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 848461 | Isolate 11kV line between C954, S304, S375 and S344 so that inline breaks can be made at poles 848461 & 818020 for use in shutdown the following day. Works location: East St Greytown. WO 10140873 / IR6938. | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 11417 | 0.034872 | 0.00071168 | 2014-12-03 | B | 0.017436 | 0.00035584 | 2015 | 2014-12-03 | B | 233 | 0.034872 | 0.00071168
1 | 3218885 | 2014-12-03 06:48 | 2014-12-10 08:03 | 10154.7 | 3 | 1360.8 | 0.0041619 | 9.1753e-06 | Restore Supply on Device 7856 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuses 7637 | No other assets repaired or replaced on site, FM checked adjacent assets and all up to Powerco Standard. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 453.6 | 450.6 | 1351.8 | 0.004129 | 9.1633e-06 | 2014-12-03 | C | 0.004129 | 9.163e-06 | 2015 | 2014-12-03 | C | 3 | 0.004129 | 9.1633e-06
1 | 3024742 | 2014-12-03 08:30 | 2014-12-03 14:29 | 359 | 97 | 34726 | 0.10621 | 0.00029667 | NAPA ID:04071 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 818465 | isolate T332, T1270 and T567 so that a live line break can be made at pole 818465 so that transformer poles T3323, T1270 and T567 can be replaced. Works location: East St Greytown. WO 10140873 / IR6938. | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 358 | 355 | 34435 | 0.10518 | 0.00029628 | 2014-12-03 | B | 0.05259 | 0.00014814 | 2015 | 2014-12-03 | B | 97 | 0.10518 | 0.00029628
1 | 3093790 | 2014-12-03 08:31 | 2014-12-03 13:53 | 322.3833 | 14 | 4513.3667 | 0.013804 | 4.2818e-05 | NAPA ID:04451 TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-151 | Maintanence on 11kv Linkbox and Switch Unit. Works location: Casuarina Dr. WO 10143066 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 322.3833 | 319.3833 | 4471.3667 | 0.013657 | 4.2762e-05 | 2014-12-03 | B | 0.0068287 | 2.1381e-05 | 2015 | 2014-12-03 | B | 14 | 0.013657 | 4.2762e-05
1 | 3013426 | 2014-12-03 09:02 | 2014-12-03 15:13 | 371 | 134 | 8868 | 0.027122 | 0.00040983 | NAPA ID:04495 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6533 | Replace 11kV poles and reconductor. Works location: Ohawe Rd. WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 66.1791 | 63.1791 | 8466 | 0.025859 | 0.00040929 | 2014-12-03 | B | 0.012929 | 0.00020465 | 2015 | 2014-12-03 | B | 134 | 0.025859 | 0.00040929
1 | 3017070 | 2014-12-03 09:17 | 2014-12-03 14:56 | 339 | 67 | 22713 | 0.069466 | 0.00020491 | NAPA ID:03956 TP_HUIRANGI GXP > INGLEWOOD SUB > BROOKES ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4160T | Relocate and replace transformer 4160T with same size unit. Replace HV cable between 4160T and Fuse 6365 and reterminate HV cable to 4153T. Works location: Maire St. WO 10154760 | F3 | BROOKES ST | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 339 | 336 | 22512 | 0.068761 | 0.00020465 | 2014-12-03 | B | 0.034381 | 0.00010232 | 2015 | 2014-12-03 | B | 67 | 0.068761 | 0.00020465
1 | 3226853 | 2014-12-03 09:20 | 2014-12-03 15:08 | 348 | 6 | 2088 | 0.006386 | 1.8351e-05 | Restore Supply on Device TF8-020 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF8-020 | Replace 4 x 11kV hardwood poles. Wok Location: Hereford Park Road , Pongakawa. Work Order: 477863 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 348 | 345 | 2070 | 0.0063227 | 1.8327e-05 | 2014-12-03 | C | 0.0063227 | 1.8327e-05 | 2015 | 2014-12-03 | C | 6 | 0.0063227 | 1.8327e-05
1 | 3036289 | 2014-12-03 09:24 | 2014-12-03 13:30 | 245.9833 | 38 | 9329.25 | 0.028533 | 0.00011622 | NAPA ID:03850 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1534 | REPLACE POLE AND ARMS AS PER SCOPE. Works location: Pyes Pa Rd Taumata Rd WO 10138318 | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 245.5066 | 242.5066 | 9215.25 | 0.028147 | 0.00011607 | 2014-12-03 | B | 0.014074 | 5.8034e-05 | 2015 | 2014-12-03 | B | 38 | 0.028147 | 0.00011607
1 | 3095306 | 2014-12-03 09:30 | 2014-12-03 15:16 | 345.5333 | 272 | 93985.0667 | 0.28745 | 0.00083189 | NAPA ID:04557 KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9632 | Replace 11kV poles and arms. Works location: Kuaotunu Whitianga. WO 10150350 | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 345.5333 | 342.5333 | 93169.0667 | 0.28458 | 0.0008308 | 2014-12-03 | B | 0.14229 | 0.0004154 | 2015 | 2014-12-03 | B | 272 | 0.28458 | 0.0008308
1 | 3018473 | 2014-12-03 09:40 | 2014-12-03 16:15 | 395 | 77 | 30415 | 0.093022 | 0.0002355 | NAPA ID:04473 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C1040 | Replace 11kV transformer structure with new pad mount transformer. Install new pole and Fuses CA196. Works location: Argyle Rd Hawera. WO 10151961. | F3 | ARGYLE ST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 395 | 392 | 30184 | 0.092195 | 0.00023519 | 2014-12-03 | B | 0.046097 | 0.0001176 | 2015 | 2014-12-03 | B | 77 | 0.092195 | 0.00023519
1 | 3221330 | 2014-12-03 13:07 | 2014-12-03 13:21 | 13.8667 | 72 | 998.4 | 0.0030535 | 0.00022021 | Restore Supply on Device C613 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 812327 | Crossarm needs bolting back to arm brace at pole 812327. Neville Pope attended. | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 13.8667 | 10.8667 | 782.4 | 0.0023898 | 0.00021992 | 2014-12-03 | C | 0.0023898 | 0.00021992 | 2015 | 2014-12-03 | C | 72 | 0.0023898 | 0.00021992
1 | 3220759 | 2014-12-03 13:10 | 2014-12-03 15:00 | 109.7167 | 1 | 109.7167 | 0.00033556 | 3.0584e-06 | Restore Supply on Device 4384W | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 840966 | 2 x 6 amp HT fuses due to bird strike. Awaiting pole number. No other assets repaired or replaced. Adjacent assets ok. Email to Alicia sent out. Amended from single phase outage to 2 or more phases. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 109.7167 | 106.7167 | 106.7167 | 0.00032596 | 3.0544e-06 | 2014-12-03 | C | 0.00032596 | 3.054e-06 | 2015 | 2014-12-03 | C | 1 | 0.00032596 | 3.0544e-06
1 | 3222221 | 2014-12-03 15:45 | 2014-12-03 17:40 | 114.9833 | 1 | 114.9833 | 0.00035167 | 3.0584e-06 | Restore Supply on Device TC4418 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | FC2361 | Replaced 3 10amp fuses. No other assets repaired or replaced on site. FM checked adjacent assets and up to Powerco standard. Email sent to Alicia to check for SAIDI component. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 114.9833 | 111.9833 | 111.9833 | 0.00034204 | 3.0544e-06 | 2014-12-03 | C | 0.00034205 | 3.054e-06 | 2015 | 2014-12-03 | C | 1 | 0.00034204 | 3.0544e-06
1 | 3222250 | 2014-12-03 16:28 | 2014-12-03 18:11 | 102.6833 | 83 | 8507.6333 | 0.02602 | 0.00025385 | Restore Supply on Device 475 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2890 | At 16:07, Kerepehi Sub, CB 3 Hauraki Rd Feeder. After Tenix had completed LV Shutdown Job; went to close in LV Fuses at Transformer TC2890 & HV Jumper in top of DDO Fuse Came out. Isolated Line at ABS 475, IC454, 9724/1 & Links 9724/4. Permit issued & rep | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 102.5016 | 99.5016 | 8258.6333 | 0.025225 | 0.00025352 | 2014-12-03 | C | 0.025225 | 0.00025352 | 2015 | 2014-12-03 | C | 83 | 0.025225 | 0.00025352
1 | 3222861 | 2014-12-03 20:27 | 2014-12-03 23:13 | 166.4333 | 8 | 141.3333 | 0.00043226 | 2.4467e-05 | Restore Supply on Device SC3-043 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | SC3-048 | Replace 2x11kV HRC Fuse Links. Unknown Cause. T J Tanoa attended. | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 17.6667 | 14.6667 | 117.3333 | 0.00035839 | 2.4435e-05 | 2014-12-03 | C | 0.00035839 | 2.4435e-05 | 2015 | 2014-12-03 | C | 8 | 0.00035839 | 2.4435e-05
1 | 3222874 | 2014-12-03 23:32 | 2014-12-04 00:38 | 65.3 | 2639 | 136828.7167 | 0.41848 | 0.0080712 | Restore Supply on Device 60 | 66000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 60 | At 23:32, Tairua Sub CB 60 Tripped, A & B Fault, DIR E/F, Ground Fault, Zone 1 Prot Trip. Whitianga CB 50 Tripped A & B Fault, DIR E/F, Ground Fault, Zone 1 Prot Trip. Loss of Supply to Coromandel Sub. Partial Backfeed COR 5 from THS 4, Opened Sectiona | F1, F2, F3 | TAISUB-CGLEN 66KV | TP_KOPU | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.8487 | 48.8487 | 128911.7167 | 0.39375 | 0.0080606 | 2014-12-03 | C | 0.39375 | 0.0080606 | 2015 | 2014-12-03 | C | 2639 | 0.39375 | 0.0080606
1 | 3035745 | 2014-12-04 05:31 | 2014-12-04 06:27 | 56.4333 | 233 | 13148.9667 | 0.040215 | 0.00071261 | NAPA ID:04072 TP_GREYTOWN GXP > KEMPTON SUB > EAST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 848461 | Close inline line breaks at poles 848461 and 818020 (NAPA 04071). Works location: East St Greytown. WO 10140873 IR6938. | F3 | EAST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 56.4333 | 53.4333 | 12449.9667 | 0.038027 | 0.00071168 | 2014-12-04 | B | 0.019014 | 0.00035584 | 2015 | 2014-12-04 | B | 233 | 0.038027 | 0.00071168
1 | 3228395 | 2014-12-04 08:00 | 2014-12-04 16:25 | 505.2 | 8 | 4041.6 | 0.012361 | 2.4467e-05 | Restore Supply on Device FC2361 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | 2361 | Dis connect for safety, 11kV fuses FC2361 ( TIR 5 ) supplying transformers TC4418 & TP2656 opened & tagged, 1 customer involved. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 505.2 | 502.2 | 4017.6 | 0.012271 | 2.4435e-05 | 2014-12-04 | C | 0.012271 | 2.4435e-05 | 2015 | 2014-12-04 | C | 8 | 0.012271 | 2.4435e-05
1 | 3074754 | 2014-12-04 08:01 | 2014-12-04 15:12 | 430.8167 | 2 | 861.6333 | 0.0026352 | 6.1168e-06 | NAPA ID:04718 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P08371 | Replace cross arms from pole P08371 to P13418 as per plans. Works location: Beaconsfield Valley Rd. WO 10160678. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 430.8167 | 427.8167 | 855.6333 | 0.0026135 | 6.1088e-06 | 2014-12-04 | B | 0.0013067 | 3.054e-06 | 2015 | 2014-12-04 | B | 2 | 0.0026135 | 6.1088e-06
1 | 3226356 | 2014-12-04 08:01 | 2014-12-04 09:22 | 80.9167 | 1 | 80.9167 | 0.00024748 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P13193 | REPLACED 2 X 3 AMP FUSES, BIRD STRIKE NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 80.9167 | 77.9167 | 77.9167 | 0.00023799 | 3.0544e-06 | 2014-12-04 | C | 0.00023799 | 3.054e-06 | 2015 | 2014-12-04 | C | 1 | 0.00023799 | 3.0544e-06
1 | 3081532 | 2014-12-04 08:02 | 2014-12-04 14:52 | 410 | 22 | 9020 | 0.027587 | 6.7285e-05 | NAPA ID:03686 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 76 | Reconductor 11kV between temp fuses 76 and abs 460. Works location: Egmont Rd. WO 10145448. | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 410 | 407 | 8954 | 0.027349 | 6.7197e-05 | 2014-12-04 | B | 0.013675 | 3.3599e-05 | 2015 | 2014-12-04 | B | 22 | 0.027349 | 6.7197e-05
1 | 3101624 | 2014-12-04 08:46 | 2014-12-04 14:36 | 350.2 | 144 | 50428.8 | 0.15423 | 0.00044041 | NAPA ID:03916 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3-029 | REPLACE HV POLES AND ARMS AS PER SCOPE. Works location: Plummer Point Rd. WO 10148295 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 350.2 | 347.2 | 49996.8 | 0.15271 | 0.00043984 | 2014-12-04 | B | 0.076356 | 0.00021992 | 2015 | 2014-12-04 | B | 144 | 0.15271 | 0.00043984
1 | 3074774 | 2014-12-04 09:15 | 2014-12-04 16:05 | 409.7667 | 40 | 16390.6667 | 0.05013 | 0.00012234 | NAPA ID:04143 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K54 | Replace 11kV 400V transformer cross arms. Works location: Lower Pakihikura Rd WO 10142182. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 409.7667 | 406.7667 | 16270.6667 | 0.049698 | 0.00012218 | 2014-12-04 | B | 0.024849 | 6.1088e-05 | 2015 | 2014-12-04 | B | 40 | 0.049698 | 0.00012218
1 | 3116113 | 2014-12-04 09:15 | 2014-12-04 13:49 | 273.9167 | 118 | 32322.1667 | 0.098855 | 0.00036089 | NAPA ID:04527 TP_NEW PLYMOUTH GXP > MOTUROA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12007 | Connect 3x185mm under ground 11kV cable to ABS 12007 and phase in on pole 752890. NOTE: Hurford Rd left on MRA 3 until Recloser 12000/2 ( MRA 9 ) commissioned. | F3 | PAPAMOA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 273.9167 | 270.9167 | 31968.1667 | 0.097644 | 0.00036042 | 2014-12-04 | B | 0.048822 | 0.00018021 | 2015 | 2014-12-04 | B | 118 | 0.097644 | 0.00036042
1 | 3095366 | 2014-12-04 09:21 | 2014-12-04 13:27 | 246 | 33 | 8118 | 0.024828 | 0.00010093 | NAPA ID:04679 WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 248 | Drop wires for tree cutting and standover for Asplundh - P.O for C.I.W to come. Works location: Waitekauri Rd Waitawheta. WO 10165405. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 246 | 243 | 8019 | 0.024493 | 0.0001008 | 2014-12-04 | B | 0.012247 | 5.0398e-05 | 2015 | 2014-12-04 | B | 33 | 0.024493 | 0.0001008
1 | 3091540 | 2014-12-04 09:28 | 2014-12-04 14:44 | 316.4833 | 34 | 10760.4333 | 0.03291 | 0.00010399 | NAPA ID:04453 HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CA413 | Replacing 8 X 11kV poles. Works location: Austin Rd Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 316.4833 | 313.4833 | 10658.4333 | 0.032555 | 0.00010385 | 2014-12-04 | B | 0.016278 | 5.1925e-05 | 2015 | 2014-12-04 | B | 34 | 0.032555 | 0.00010385
1 | 3102578 | 2014-12-04 09:31 | 2014-12-04 14:37 | 306.65 | 29 | 8892.85 | 0.027198 | 8.8694e-05 | NAPA ID:04719 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 219744 | Replace 11kv conductor between poles 219744 and 380367. Works location: Kairua Rd. WO TA/2014/23 IR6817 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 306.65 | 303.65 | 8805.85 | 0.026897 | 8.8578e-05 | 2014-12-04 | B | 0.013448 | 4.4289e-05 | 2015 | 2014-12-04 | B | 29 | 0.026897 | 8.8578e-05
1 | 3227124 | 2014-12-04 09:47 | 2014-12-04 11:44 | 116.9167 | 21 | 2455.25 | 0.0075092 | 6.4227e-05 | Restore Supply on Device V66 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE |  | Outage was caused due to planned switching under SIS 4638 (OMS #3070868) | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 116.9167 | 113.9167 | 2392.25 | 0.0073069 | 6.4143e-05 | 2014-12-04 | C | 0.0073069 | 6.4143e-05 | 2015 | 2014-12-04 | C | 21 | 0.0073069 | 6.4143e-05
1 | 3228406 | 2014-12-04 13:36 | 2014-12-04 16:33 | 176.2667 | 2 | 334.55 | 0.0010232 | 6.1168e-06 | Restore Supply on Device TC1-014 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 201651 and fuse sc2-032 | FM advise: ht ddo fuse holder hanging down, just pushed it back in. 1 out of 3 phases. pole 201651. fuse: sc2-032. cause: unknown. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 167.275 | 164.275 | 328.55 | 0.0010035 | 6.1088e-06 | 2014-12-04 | C | 0.0010035 | 6.109e-06 | 2015 | 2014-12-04 | C | 2 | 0.0010035 | 6.1088e-06
1 | 3228601 | 2014-12-04 17:05 | 2014-12-04 20:49 | 224.5 | 7 | 434.5 | 0.0013289 | 2.1409e-05 | Restore Supply on Device V19 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T9/21 | Broken Jumper at Transformer T9/21. Materials Used: 1 x m10 Connector. Robin Smith attended. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 62.0714 | 59.0714 | 413.5 | 0.001263 | 2.1381e-05 | 2014-12-04 | C | 0.001263 | 2.1381e-05 | 2015 | 2014-12-04 | C | 7 | 0.001263 | 2.1381e-05
1 | 3229078 | 2014-12-05 05:05 | 2014-12-05 08:00 | 174.7667 | 4 | 353.3333 | 0.0010806 | 1.2234e-05 | Restore Supply on Device H116 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P03952 | Repaired 11kV jumper at pole P03952. Used 2 x 10 amp fuses when trying to locate the fault and tape to fix the cable. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. Fault was on 1 phase. 1 out of | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88.3333 | 85.3333 | 341.3333 | 0.0010426 | 1.2218e-05 | 2014-12-05 | C | 0.0010426 | 1.2218e-05 | 2015 | 2014-12-05 | C | 4 | 0.0010426 | 1.2218e-05
1 | 3229064 | 2014-12-05 07:00 | 2014-12-05 10:03 | 183.3667 | 2 | 474.6167 | 0.0014516 | 6.1168e-06 | Restore Supply on Device X1258 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 851809 | is 3229090 linked 2 X 15 AMP FUSES DUE TO BIRD STRIKE NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. Email sent to Alicia | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 237.3083 | 234.3083 | 468.6167 | 0.0014314 | 6.1088e-06 | 2014-12-05 | C | 0.0014314 | 6.109e-06 | 2015 | 2014-12-05 | C | 2 | 0.0014314 | 6.1088e-06
1 | 3102588 | 2014-12-05 08:45 | 2014-12-05 13:25 | 280 | 76 | 21280 | 0.065083 | 0.00023244 | NAPA ID:04761 TP_KOPU GXP > MATATOKI SUB > KOPU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6177 | Level up Transformer and install LV and HV boots. Works location: Teretiu Dr, Totara. WO 10165349. | F1/F4 | KOPU | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 280 | 277 | 21052 | 0.064302 | 0.00023214 | 2014-12-05 | B | 0.032151 | 0.00011607 | 2015 | 2014-12-05 | B | 76 | 0.064302 | 0.00023214
1 | 3099664 | 2014-12-05 08:50 | 2014-12-05 13:27 | 277.7833 | 153 | 42500.85 | 0.12999 | 0.00046794 | NAPA ID:04496 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH890 | Replace poles & wire Ohawe. Works location: Ohawe Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 277.7833 | 274.7833 | 42041.85 | 0.12841 | 0.00046733 | 2014-12-05 | B | 0.064207 | 0.00023366 | 2015 | 2014-12-05 | B | 153 | 0.12841 | 0.00046733
1 | 3093930 | 2014-12-05 09:06 | 2014-12-05 14:30 | 324.0167 | 3 | 972.05 | 0.0029729 | 9.1753e-06 | NAPA ID:04489 WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 792880 | Replace five 11kv poles 792880,792932,792933,792934, 792935. Works location: Ruatangata Rd Whangaehu. WO 10141993. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 324.0167 | 321.0167 | 963.05 | 0.0029416 | 9.1633e-06 | 2014-12-05 | B | 0.0014708 | 4.582e-06 | 2015 | 2014-12-05 | B | 3 | 0.0029416 | 9.1633e-06
1 | 3102530 | 2014-12-05 09:15 | 2014-12-05 11:20 | 125 | 9 | 1125 | 0.0034407 | 2.7526e-05 | NAPA ID:04485 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC354 | Replace TC354. Works location: Piakoiti Rd Walton. WO IR5140. | F4 | PIAKOITI RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 125 | 122 | 1098 | 0.0033538 | 2.749e-05 | 2014-12-05 | B | 0.0016769 | 1.3745e-05 | 2015 | 2014-12-05 | B | 9 | 0.0033538 | 2.749e-05
1 | 3102703 | 2014-12-05 09:15 | 2014-12-05 14:01 | 285.6167 | 22 | 6283.5667 | 0.019218 | 6.7285e-05 | NAPA ID:04444 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-191 | Maintenance on 11kv Linkbox. Works location: Gridley Road and Lismore Lane. WO 10143066. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 285.6167 | 282.6167 | 6217.5667 | 0.018991 | 6.7197e-05 | 2014-12-05 | B | 0.0094955 | 3.3599e-05 | 2015 | 2014-12-05 | B | 22 | 0.018991 | 6.7197e-05
1 | 3096349 | 2014-12-05 09:15 | 2014-12-05 14:10 | 294.65 | 4 | 1178.6 | 0.0036047 | 1.2234e-05 | NAPA ID:04647 PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I13247 | To Isolate TC3249. Remove the 11kV Fuses on pole I13247. Replace Pole I0662. Relocate TC3249 to the new pole. Connect the new set of HV Fuses on pole I0662. Liven and test transformer. Works location: SH26 Morrinsville. WO 10162110. | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 294.65 | 291.65 | 1166.6 | 0.0035633 | 1.2218e-05 | 2014-12-05 | B | 0.0017816 | 6.109e-06 | 2015 | 2014-12-05 | B | 4 | 0.0035633 | 1.2218e-05
1 | 3082011 | 2014-12-05 09:49 | 2014-12-05 15:30 | 340.5833 | 37 | 12601.5833 | 0.038541 | 0.00011316 | NAPA ID:04747 TP_BUNNYTHORPE GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D45 | This is to complete 4 x unfinished xarms from Shutdown # 3 Changing 33kv and 11kv xarm fitting new insulators. Works location: Bunnythorpe 33kV West Feeder WO 10147202 | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 340.5833 | 337.5833 | 12490.5833 | 0.038152 | 0.00011301 | 2014-12-05 | B | 0.019076 | 5.6507e-05 | 2015 | 2014-12-05 | B | 37 | 0.038152 | 0.00011301
1 | 3095010 | 2014-12-05 10:10 | 2014-12-05 15:31 | 320.6833 | 28 | 8979.1333 | 0.027462 | 8.5636e-05 | NAPA ID:04777 MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P06802 | Replace 11kv conductor , restrain conductor and close line breaks at poles P06802 and P06879. Works location: Range Rd Pongaroa. WO 10163075. | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 320.6833 | 317.6833 | 8895.1333 | 0.02717 | 8.5524e-05 | 2014-12-05 | B | 0.013585 | 4.2762e-05 | 2015 | 2014-12-05 | B | 28 | 0.02717 | 8.5524e-05
1 | 3229837 | 2014-12-05 11:44 | 2014-12-05 12:21 | 37 | 3 | 111 | 0.00033948 | 9.1753e-06 | Restore Supply on Device 6761 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 737587 | CHANGED 63 AMP FUSE , AND 100 BASE AND CARRIER DUE TO DETERIORATION TIGHTENED LV JUMPER AT POLE NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. NOTE HV Fuses 6761 open for isolation - Refer OMS 329733 already closed of. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 37 | 34 | 102 | 0.00031155 | 9.1633e-06 | 2014-12-05 | C | 0.00031155 | 9.163e-06 | 2015 | 2014-12-05 | C | 3 | 0.00031155 | 9.1633e-06
1 | 3229330 | 2014-12-05 12:13 | 2014-12-05 13:15 | 62 | 29 | 1798 | 0.005499 | 8.8694e-05 | Restore Supply on Device 2453W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719472 | 9.24am Tallia called to have Garry's status put back to Assigned as she has diverted him to a sparking lines job Shutdown to repair termination to one phase at Fuses 1007. Isolation between ABS 604 and ABS2671 whilst repairs were undertaken. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 62 | 59 | 1711 | 0.0052261 | 8.8578e-05 | 2014-12-05 | C | 0.0052261 | 8.8578e-05 | 2015 | 2014-12-05 | C | 29 | 0.0052261 | 8.8578e-05
1 | 3099654 | 2014-12-05 12:30 | 2014-12-05 14:00 | 90 | 3 | 270 | 0.00082577 | 9.1753e-06 | NAPA ID:04487 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3245 | Replace Transformer TC3245. Works location: Piakoiti Rd Walton. WO IR5140. | F4 | PIAKOITI RD | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 261 | 0.0007972 | 9.1633e-06 | 2014-12-05 | B | 0.0003986 | 4.582e-06 | 2015 | 2014-12-05 | B | 3 | 0.0007972 | 9.1633e-06
1 | 3227320 | 2014-12-05 13:01 | 2014-12-05 13:56 | 54.8167 | 46 | 2521.5667 | 0.007712 | 0.00014069 | NAPA ID:05411 TP_OPUNAKE GXP > PUNGAREHU SUB > PARIHAKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 704967 | 11kV pole 704967 HV crossarm kingbolt nut loose. Tighten and secure with doublenut. Works location: Warea Rd. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 54.8167 | 51.8167 | 2383.5667 | 0.0072804 | 0.0001405 | 2014-12-05 | B | 0.0036402 | 7.0252e-05 | 2015 | 2014-12-05 | B | 46 | 0.0072804 | 0.0001405
1 | 3230950 | 2014-12-05 18:10 | 2014-12-05 19:30 | 80 | 20 | 1600 | 0.0048935 | 6.1168e-05 | Restore Supply on Device 3854T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 740139, 3854T | 11kV cross arm rotten and insulator hanging down opposite 435 Standish Road, Midhurst. This is also the transformer pole for 3854T. Burnt cross arm located at pole 740139. Used 1 X H/T Crossarm & Full Set Of 3 DDOs at pole 740139. Bruce Kerr attended. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 1540 | 0.0047038 | 6.1088e-05 | 2014-12-05 | C | 0.0047038 | 6.1088e-05 | 2015 | 2014-12-05 | C | 20 | 0.0047038 | 6.1088e-05
1 | 3232917 | 2014-12-05 22:16 | 2014-12-05 23:28 | 71.9833 | 11 | 197.9333 | 0.00060536 | 3.3643e-05 | Restore Supply on Device M29 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M29 | 2 X Fuses hanging down reloaded all Ok | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 17.9939 | 14.9939 | 164.9333 | 0.00050378 | 3.3599e-05 | 2014-12-05 | C | 0.00050378 | 3.3599e-05 | 2015 | 2014-12-05 | C | 11 | 0.00050378 | 3.3599e-05
1 | 3232989 | 2014-12-06 07:14 | 2014-12-06 07:25 | 11.85 | 1 | 11.85 | 3.6242e-05 | 3.0584e-06 | Restore Supply on Device T7/440 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Q27 | Faultman found blown fuses at Fuses Q27 caused by a bird found dead on the fuses. 2 X 20 Amp HV rewirable Fuses replaced. Email sent to Alicia to check for SAIDI content. NB: No Paper Work Created - Closed by Dispatch. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 11.85 | 8.85 | 8.85 | 2.7032e-05 | 3.0544e-06 | 2014-12-06 | C | 2.7032e-05 | 3.054e-06 | 2015 | 2014-12-06 | C | 1 | 2.7032e-05 | 3.0544e-06
1 | 3119478 | 2014-12-06 07:15 | 2014-12-06 11:20 | 245 | 45 | 11025 | 0.033719 | 0.00013763 | NAPA ID:04970 TP_MASTERTON GXP > AKURA SUB > NGAUMUTAWA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 172 | REPLACE DNO ABS 172. Works location: Ngaumutawa Rd. WO 10153517. | F2 | NGAUMUTAWA RD | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 245 | 242 | 10890 | 0.033263 | 0.00013745 | 2014-12-06 | B | 0.016631 | 6.8725e-05 | 2015 | 2014-12-06 | B | 45 | 0.033263 | 0.00013745
1 | 2920039 | 2014-12-06 08:22 | 2014-12-06 13:08 | 286 | 6 | 1716 | 0.0052483 | 1.8351e-05 | NAPA ID:04332 TP_MASTERTON GXP > AKURA SUB > RENALL ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 831439 | Replacing red tag transformer pole T298. Works location: Ngamutawa Rd. WO 10136314 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 286 | 283 | 1698 | 0.0051864 | 1.8327e-05 | 2014-12-06 | B | 0.0025932 | 9.163e-06 | 2015 | 2014-12-06 | B | 6 | 0.0051864 | 1.8327e-05
1 | 3233242 | 2014-12-06 09:22 | 2014-12-06 17:03 | 460.9333 | 1044 | 41132.6333 | 0.1258 | 0.003193 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 2054 | CB 8 tripped on B phase O/C flags, line was patrolled and sectionalised and fault found at Sw/Gear 2054, line was isolated at ABS 2640.Found a whole in Sw/Gear 2054 and had to replace 1 of the bus bar bushings. Fill Sw/Gear 2054 with oil. 1 X Bus bar bush | F3 | PURIRI ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 39.3991 | 36.3991 | 38000.6333 | 0.11607 | 0.0031888 | 2014-12-06 | C | 0.11607 | 0.0031888 | 2015 | 2014-12-06 | C | 1044 | 0.11607 | 0.0031888
1 | 3234548 | 2014-12-06 12:44 | 2014-12-06 15:06 | 141.6833 | 36 | 2101.6833 | 0.0064278 | 0.0001101 | Restore Supply on Device M1200 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | MA117 | Faultman found broken fuse holder at Fuses MA117, line was isolated at ABS's MA 106 & MA 128 to replaced the fuse holder and fuse. 1 X 6Amp HV fuse replaced. 1 X Fuse holder replaced. Email sent to Alicia to check for SAIDI component. axk: Outage also | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 58.3801 | 55.3801 | 1993.6833 | 0.0060896 | 0.00010996 | 2014-12-06 | C | 0.0060896 | 0.00010996 | 2015 | 2014-12-06 | C | 36 | 0.0060896 | 0.00010996
1 | 3219750 | 2014-12-06 16:21 | 2014-12-06 18:20 | 119 | 1 | 119 | 0.00036395 | 3.0584e-06 | NAPA ID:05339 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8177/3 | 11kV fuse 8177-3 switch inspect operation and test operate. Works location: Moreton Rd, Carton - Premier Beehive Bacon Factory. WO 30001403 | F4 | RENALL ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 119 | 116 | 116 | 0.00035431 | 3.0544e-06 | 2014-12-06 | B | 0.00017716 | 1.527e-06 | 2015 | 2014-12-06 | B | 1 | 0.00035431 | 3.0544e-06
1 | 3235354 | 2014-12-07 05:42 | 2014-12-07 07:27 | 105.35 | 3 | 453 | 0.0013855 | 9.1753e-06 | Restore Supply on Device 2612T | 6600 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 4850, 5528 | Faultman found fuses blown at Fuses 4850 and Fuses 5528, line was patrolled and no fault was found suspect bird strike as a lot of birds flying around the lines, fuses reloaded supply restored. 2 X 25 Amp HV rewirable fuses replaced. 2 X 20 Amp HV rewir | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 151 | 148 | 444 | 0.0013562 | 9.1633e-06 | 2014-12-07 | C | 0.0013562 | 9.163e-06 | 2015 | 2014-12-07 | C | 3 | 0.0013562 | 9.1633e-06
1 | 3133955 | 2014-12-07 08:30 | 2014-12-07 15:11 | 401 | 87 | 34887 | 0.1067 | 0.00026608 | NAPA ID:04722 TP_HAWERA GXP > CAMBRIA SUB > GLOVER RD WEST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 703654 | Replace 4 x 11kV poles no's 703654 /5 /6 /7. Works location: Glover Rd. WO 10157155. | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 401 | 398 | 34626 | 0.10576 | 0.00026573 | 2014-12-07 | B | 0.052881 | 0.00013287 | 2015 | 2014-12-07 | B | 87 | 0.10576 | 0.00026573
1 | 3236988 | 2014-12-07 14:11 | 2014-12-07 15:07 | 56.2667 | 179 | 10024 | 0.030658 | 0.00054746 | Restore Supply on Device RC18 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | F1661 | 2 x A/R on recloser RC18 @ 14:07 was followed by trip to L/O @ 14:11 - report received from member of public that some balloons had been set off near Te Poi church that flew into line - site checked out by Paul Cooper - all ok - recloser closed & all supp | F4 | BANKS ST | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 56 | 53 | 9487 | 0.028977 | 0.00054674 | 2014-12-07 | C | 0.028977 | 0.00054674 | 2015 | 2014-12-07 | C | 179 | 0.028977 | 0.00054674
1 | 3237623 | 2014-12-07 15:21 | 2014-12-07 20:44 | 323.1667 | 462 | 51372.45 | 0.15712 | 0.001413 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | IC1825 | Cable Fault found between Sw/gear IC1825 and T/Blade TC3832 To be repaired at a later date. DNO 141206. Colin P attended. | F2 | POLLEN ST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 111.1958 | 108.1958 | 49986.45 | 0.15268 | 0.0014111 | 2014-12-07 | C | 0.15268 | 0.0014111 | 2015 | 2014-12-07 | C | 462 | 0.15268 | 0.0014111
1 | 3238582 | 2014-12-08 07:11 | 2014-12-08 07:46 | 35 | 303 | 10605 | 0.032435 | 0.0009267 | Restore Supply on Device XT40 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P26650 | Lines sectionalised at Alfredton Sub and fault isolated to lines between Parkville & Alfredton Subs. Alfredton Sub relivened from Pongaroa. Lines flown with helicopter and found two dead magpies at Pole P26650. Removed with hot sticks. Restored OK. Trevor | F1, F2, F3 | PARKVILLE-ALFREDTON 33KV | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 9696 | 0.029616 | 0.00092549 | 2014-12-08 | C | 0.029616 | 0.00092549 | 2015 | 2014-12-08 | C | 303 | 0.029616 | 0.00092549
1 | 3239025 | 2014-12-08 07:53 | 2014-12-08 11:15 | 202 | 175 | 14926.8333 | 0.045653 | 0.00053522 | Restore Supply on Device T2800 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 848797 | Lines bought down by tree contractors, Harvard Logging NDR 37971. Recloser 7417 A/R at 07:53 and Gladstone Sub CB C948 tripped. At the time we had other tree contractors working on the feeder and had a Hot Line Tag applied to CB C948 under CAC 5136-01, th | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 85.2962 | 82.2962 | 14401.8333 | 0.043989 | 0.00053452 | 2014-12-08 | C | 0.043989 | 0.00053452 | 2015 | 2014-12-08 | C | 175 | 0.043989 | 0.00053452
1 | 3102721 | 2014-12-08 08:17 | 2014-12-08 09:42 | 85.1167 | 3 | 255.35 | 0.00078097 | 9.1753e-06 | NAPA ID:04459 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-030 | Maintanence on 11kv Linkboxe SE6-178. Works location: Rangiuru Rd. WO 10143066. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 85.1167 | 82.1167 | 246.35 | 0.00075246 | 9.1633e-06 | 2014-12-08 | B | 0.00037623 | 4.582e-06 | 2015 | 2014-12-08 | B | 3 | 0.00075246 | 9.1633e-06
1 | 3229772 | 2014-12-08 08:46 | 2014-12-08 15:09 | 382.8833 | 14 | 5360.3667 | 0.016394 | 4.2818e-05 | NAPA ID:05453 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC907 | Isolate DDO fuses on Transformer TC907 for safety while replacing 400V poles. Works location: Cambridge Rd Waihi. WO 10148315. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 382.8833 | 379.8833 | 5318.3667 | 0.016245 | 4.2762e-05 | 2014-12-08 | B | 0.0081223 | 2.1381e-05 | 2015 | 2014-12-08 | B | 14 | 0.016245 | 4.2762e-05
1 | 3102627 | 2014-12-08 09:00 | 2014-12-08 13:50 | 290 | 15 | 4350 | 0.013304 | 4.5876e-05 | NAPA ID:04470 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CA407 | Replace 17 x 11kV poles. Works location: Boylan Rd, Hawera. WO 1014179. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 290 | 287 | 4305 | 0.013149 | 4.5816e-05 | 2014-12-08 | B | 0.0065746 | 2.2908e-05 | 2015 | 2014-12-08 | B | 15 | 0.013149 | 4.5816e-05
1 | 3158140 | 2014-12-08 09:00 | 2014-12-08 12:02 | 182 | 35 | 6370 | 0.019482 | 0.00010704 | NAPA ID:05169 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1073 | Replace cracked pole at ground level, cannot get sufficent ground clearance on service line. Works location: Tauhei Rd. WO 30001109. | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 6265 | 0.019136 | 0.0001069 | 2014-12-08 | B | 0.009568 | 5.3452e-05 | 2015 | 2014-12-08 | B | 35 | 0.019136 | 0.0001069
1 | 3110428 | 2014-12-08 09:05 | 2014-12-08 14:48 | 343 | 134 | 45962 | 0.14057 | 0.00040983 | NAPA ID:04497 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6533 | Replace pole & wire. Works location: Ohawe Rd. WO 10141948. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 343 | 340 | 45560 | 0.13916 | 0.00040929 | 2014-12-08 | B | 0.06958 | 0.00020465 | 2015 | 2014-12-08 | B | 134 | 0.13916 | 0.00040929
1 | 3096350 | 2014-12-08 09:18 | 2014-12-08 11:39 | 141 | 369 | 49077 | 0.1501 | 0.0011286 | NAPA ID:04488 BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/245 | Replace 12m of faulty cable between T3/245 and pole P20315. First AP is to remove old cable and connect new cable to transformer T3/245. We will then need to liven and phase out at pole P20315. Then secon AP will be to make the conection to overhead line | F3 | DENBIGH | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 133 | 130 | 47970 | 0.14652 | 0.0011271 | 2014-12-08 | B | 0.07326 | 0.00056354 | 2015 | 2014-12-08 | B | 369 | 0.14652 | 0.0011271
1 | 3103636 | 2014-12-08 09:22 | 2014-12-08 10:54 | 91.55 | 9 | 823.95 | 0.00252 | 2.7526e-05 | NAPA ID:03917 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC3-050 | REPLACE HV POLES AND ARMS AS PER SCOPE. Works location: Anderson Lane. WO 10142895. | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 91.55 | 88.55 | 796.95 | 0.0024342 | 2.749e-05 | 2014-12-08 | B | 0.0012171 | 1.3745e-05 | 2015 | 2014-12-08 | B | 9 | 0.0024342 | 2.749e-05
1 | 3240299 | 2014-12-08 09:31 | 2014-12-08 12:29 | 178.1833 | 1 | 178.1833 | 0.00054496 | 3.0584e-06 | Restore Supply on Device N3225 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713210 | replace 2 amp ht fuse element. cause: deterioration. pole # 713210. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4/F1 | SOUTH RD NGARIKI | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 178.1833 | 175.1833 | 175.1833 | 0.00053508 | 3.0544e-06 | 2014-12-08 | C | 0.00053508 | 3.054e-06 | 2015 | 2014-12-08 | C | 1 | 0.00053508 | 3.0544e-06
1 | 3184221 | 2014-12-08 10:00 | 2014-12-08 12:16 | 136.3667 | 6 | 818.2 | 0.0025024 | 1.8351e-05 | NAPA ID:05220 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > GREEN PARK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TE4-010 | UPGRADE TX TE4-010 DUE TO LOW POWER [PQI JOB] | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 136.3667 | 133.3667 | 800.2 | 0.0024441 | 1.8327e-05 | 2014-12-08 | B | 0.0012221 | 9.163e-06 | 2015 | 2014-12-08 | B | 6 | 0.0024441 | 1.8327e-05
1 | 3103696 | 2014-12-08 10:11 | 2014-12-08 11:30 | 79.0333 | 14 | 1106.4667 | 0.003384 | 4.2818e-05 | NAPA ID:04461 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-084 | Maintenance on 11kv Linkbox SE6-187. Works location: Karner Rd Te Puke. WO 10143066. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 79.0333 | 76.0333 | 1064.4667 | 0.0032513 | 4.2762e-05 | 2014-12-08 | B | 0.0016257 | 2.1381e-05 | 2015 | 2014-12-08 | B | 14 | 0.0032513 | 4.2762e-05
1 | 3240969 | 2014-12-08 12:49 | 2014-12-08 17:15 | 266 | 109 | 28954.1333 | 0.088554 | 0.00033337 | Restore Supply on Device TC4030 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | FC711 | *** check if part of oms 3240957 ***Contractor hit U/G cable. Fuse/Sw FC711 tripped. Isolated at fuse/sw and repaired cable. Relivened. NDR 048155. Initial site inspection OMS Job 3240957 logs advise that 1R Contractors onsite have exposed a cable that wa | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 265.6343 | 262.6343 | 28627.1333 | 0.087439 | 0.00033293 | 2014-12-08 | C | 0.087439 | 0.00033293 | 2015 | 2014-12-08 | C | 109 | 0.087439 | 0.00033293
1 | 3110486 | 2014-12-08 13:00 | 2014-12-08 14:56 | 115.7667 | 3 | 347.3 | 0.0010622 | 9.1753e-06 | NAPA ID:04465 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-215 | Maintanence on 11kV Linkboxes SE6-216 and SE6-217. Works location: Huse Lane Te Puke. WO 10143066. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 115.7667 | 112.7667 | 338.3 | 0.0010333 | 9.1633e-06 | 2014-12-08 | B | 0.00051666 | 4.582e-06 | 2015 | 2014-12-08 | B | 3 | 0.0010333 | 9.1633e-06
1 | 3241528 | 2014-12-08 17:43 | 2014-12-08 18:26 | 42.65 | 271 | 5338.8667 | 0.016329 | 0.00082883 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 362859 | Lines down at pole 362859. Materials used: 5 metres of 70mm Copper, H18 6 x line taps and 4 x 70mm Links. Wes Botha attended. | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 19.7006 | 16.7006 | 4525.8667 | 0.013824 | 0.00082775 | 2014-12-08 | C | 0.013824 | 0.00082775 | 2015 | 2014-12-08 | C | 271 | 0.013824 | 0.00082775
1 | 3244528 | 2014-12-09 01:13 | 2014-12-09 02:20 | 66.8167 | 3 | 200.45 | 0.00061306 | 9.1753e-06 | Restore Supply on Device 4845 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1726N | Faultman saw a blown fuse at Fuses 4845 while carrying out switching after a feeder fault on CB 11(OMS 3241528, after completing the switching faultman went to investigate the blown fuse and found that on transformer 1726N there was a broken white phase b | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 66.8167 | 63.8167 | 191.45 | 0.00058477 | 9.1633e-06 | 2014-12-09 | C | 0.00058477 | 9.163e-06 | 2015 | 2014-12-09 | C | 3 | 0.00058477 | 9.1633e-06
1 | 3121316 | 2014-12-09 09:00 | 2014-12-09 12:11 | 191 | 6 | 1146 | 0.003505 | 1.8351e-05 | NAPA ID:02893 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I1898 | To replace pole I1898 and crossarms on poles I1899 to I1904. Works location: Kereone Rd Morrinsville. WO 480110. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 191 | 188 | 1128 | 0.0034454 | 1.8327e-05 | 2014-12-09 | B | 0.0017227 | 9.163e-06 | 2015 | 2014-12-09 | B | 6 | 0.0034454 | 1.8327e-05
1 | 3110283 | 2014-12-09 09:02 | 2014-12-09 10:44 | 102 | 5 | 510 | 0.0015598 | 1.5292e-05 | NAPA ID:04593 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WH856 | Replace wire. Works location: Paora Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 102 | 99 | 495 | 0.0015119 | 1.5272e-05 | 2014-12-09 | B | 0.00075597 | 7.636e-06 | 2015 | 2014-12-09 | B | 5 | 0.0015119 | 1.5272e-05
1 | 3133935 | 2014-12-09 09:04 | 2014-12-09 15:43 | 399.1 | 247 | 98577.7 | 0.30149 | 0.00075543 | NAPA ID:04310 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4-231 | Replace series one switchgear with automated CFCF Safelink2 at SC4-524/526. Works location: Maunganui Rd WO 10136679 | F3 | TOTARA ST NORTH | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 399.1 | 396.1 | 97836.7 | 0.29883 | 0.00075444 | 2014-12-09 | B | 0.14942 | 0.00037722 | 2015 | 2014-12-09 | B | 247 | 0.29883 | 0.00075444
1 | 2385749 | 2014-12-09 09:15 | 2014-12-09 15:08 | 353 | 35 | 12355 | 0.037787 | 0.00010704 | NAPA ID:03491 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 759892 | 33/11kV pole and crossarm replacement between poles #759892 & 760694. Works location: Otaraora Rd Waitara. WO 10151691. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 353 | 350 | 12250 | 0.037417 | 0.0001069 | 2014-12-09 | B | 0.018708 | 5.3452e-05 | 2015 | 2014-12-09 | B | 35 | 0.037417 | 0.0001069
1 | 3103638 | 2014-12-09 09:20 | 2014-12-09 13:51 | 270.9333 | 2 | 541.8667 | 0.0016573 | 6.1168e-06 | NAPA ID:04558 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1418 | Replace 11kV crossarms poles 792881, 792882 & Transformer X1418. Works location: Ruatangata Rd, Whangaehu. WO 10141993 | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 270.9333 | 267.9333 | 535.8667 | 0.0016368 | 6.1088e-06 | 2014-12-09 | B | 0.00081838 | 3.054e-06 | 2015 | 2014-12-09 | B | 2 | 0.0016368 | 6.1088e-06
1 | 3135185 | 2014-12-09 09:31 | 2014-12-09 14:49 | 318.5167 | 22 | 7007.3667 | 0.021431 | 6.7285e-05 | NAPA ID:03926 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse SC3-034 | REPLACE 33 AND 11KV HV POLES AND ARMS AS PER SCOPE. Works location: Plummer Point Rd and Emeny Rd WO 10148295 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 318.5167 | 315.5167 | 6941.3667 | 0.021202 | 6.7197e-05 | 2014-12-09 | B | 0.010601 | 3.3599e-05 | 2015 | 2014-12-09 | B | 22 | 0.021202 | 6.7197e-05
1 | 3103661 | 2014-12-09 09:32 | 2014-12-09 15:58 | 386.05 | 15 | 5790.75 | 0.017711 | 4.5876e-05 | NAPA ID:04155 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K59 | Replace 11kv 400v TX crossarms. Works location: Lower Pakihikura Rd. WO 10142182. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 386.05 | 383.05 | 5745.75 | 0.01755 | 4.5816e-05 | 2014-12-09 | B | 0.008775 | 2.2908e-05 | 2015 | 2014-12-09 | B | 15 | 0.01755 | 4.5816e-05
1 | 3245125 | 2014-12-09 13:15 | 2014-12-09 13:47 | 32 | 6 | 192 | 0.00058722 | 1.8351e-05 | Restore Supply on Device T1/506 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P06527 | Replace jumper on Fuses L80. Replace 1 joiner, 1m cable. Jeff Roberts attended. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32 | 29 | 174 | 0.00053147 | 1.8327e-05 | 2014-12-09 | C | 0.00053147 | 1.8327e-05 | 2015 | 2014-12-09 | C | 6 | 0.00053147 | 1.8327e-05
1 | 3245318 | 2014-12-09 13:22 | 2014-12-09 14:17 | 55 | 1 | 55 | 0.00016821 | 3.0584e-06 | Restore Supply on Device V80 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06527 | Repair lines of insulator. Replace 2 x binder. Trevor Pocock attended. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55 | 52 | 52 | 0.00015883 | 3.0544e-06 | 2014-12-09 | C | 0.00015883 | 3.054e-06 | 2015 | 2014-12-09 | C | 1 | 0.00015883 | 3.0544e-06
1 | 3245414 | 2014-12-09 15:49 | 2014-12-09 20:34 | 284.3667 | 528 | 75004.65 | 0.2294 | 0.0016148 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | Recloser 9773/2 | Recloser 9773/2 tripped to L/O - E/F flag - line sectionalised & patrolled with trips during sectionalising indicating fault between ABS 2518 & 821, 843 - all supply eventually restored with line patrols failing to locate any fault - some foreign object e | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 142.0543 | 139.0543 | 73420.65 | 0.22426 | 0.0016127 | 2014-12-09 | C | 0.22426 | 0.0016127 | 2015 | 2014-12-09 | C | 528 | 0.22426 | 0.0016127
1 | 3248095 | 2014-12-09 18:25 | 2014-12-09 18:55 | 30 | 2 | 60 | 0.00018351 | 6.1168e-06 | Restore Supply on Device 7572 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 817626 | While attending a LV fault Lee Wilton found a conductor resting on a cross arm. He requires a bucket truck to repair. 2 BROKEN BINDERS REPAIRED. TIGHTENED INSULATOR , TIGHTENED CROSSARM. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. Isolated | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 54 | 0.00016494 | 6.1088e-06 | 2014-12-09 | C | 0.00016494 | 6.109e-06 | 2015 | 2014-12-09 | C | 2 | 0.00016494 | 6.1088e-06
1 | 3244675 | 2014-12-09 18:53 | 2014-12-09 21:55 | 182 | 3 | 546 | 0.0016699 | 9.1753e-06 | NAPA ID:05539 TP_CARRINGTON GXP > KATERE SUB > KATERE 11 | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 1726N | Change transformer 1726N (Toops - Devon Road). Urgent Shutdown. | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 537 | 0.0016402 | 9.1633e-06 | 2014-12-09 | B | 0.00082011 | 4.582e-06 | 2015 | 2014-12-09 | B | 3 | 0.0016402 | 9.1633e-06
1 | 3249324 | 2014-12-09 21:19 | 2014-12-10 00:15 | 176.0833 | 197 | 14030.85 | 0.042912 | 0.00060251 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole 798520 | Recloser C634 tripped on E/F flags, line was patrolled and sectionalised and a floating wire was found on pole 798520, line was isolated at ABS's S505, C634/1 and Links C634/6 to rebind in the conductor. Back feed was closed at Recloser 11035. 3 X Binders | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 71.2226 | 68.2226 | 13439.85 | 0.041051 | 0.00060172 | 2014-12-09 | C | 0.041051 | 0.00060172 | 2015 | 2014-12-09 | C | 197 | 0.041051 | 0.00060172
1 | 3272024 | 2014-12-10 04:58 | 2014-12-10 10:00 | 302 | 1 | 302 | 0.00092364 | 3.0584e-06 | Restore Supply on Device T2/776 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2/776 | Fault at metering unit - removed/relivened. Note: T2/420 put on a generator. (T2/776 had to be used for outage steps as this holds the ICP). | F2 | WORKS | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 302 | 299 | 299 | 0.00091327 | 3.0544e-06 | 2014-12-10 | C | 0.00091327 | 3.054e-06 | 2015 | 2014-12-10 | C | 1 | 0.00091327 | 3.0544e-06
1 | 3260189 | 2014-12-10 08:15 | 2014-12-10 08:25 | 9.4 | 1 | 9.4 | 2.8749e-05 | 3.0584e-06 | Restore Supply on Device FC4238 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | FC4238 | Fuses FC4238 Blown. Unknown Cause Line Patrolled. Faultman: Shane Walker. Paper work not required. | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 9.4 | 6.4 | 6.4 | 1.9548e-05 | 3.0544e-06 | 2014-12-10 | C | 1.9548e-05 | 3.054e-06 | 2015 | 2014-12-10 | C | 1 | 1.9548e-05 | 3.0544e-06
1 | 3260145 | 2014-12-10 08:40 | 2014-12-10 11:04 | 143.8667 | 1 | 143.8667 | 0.00044 | 3.0584e-06 | Restore Supply on Device 429 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | X429 | removed bail of hay from Transformer No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | BELL BLOCK 8 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 143.8667 | 140.8667 | 140.8667 | 0.00043027 | 3.0544e-06 | 2014-12-10 | C | 0.00043027 | 3.054e-06 | 2015 | 2014-12-10 | C | 1 | 0.00043027 | 3.0544e-06
1 | 3111298 | 2014-12-10 08:41 | 2014-12-10 11:36 | 175 | 40 | 7000 | 0.021409 | 0.00012234 | NAPA ID:04887 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 844644 | Isolation of 11kV line and remove one span of wire at pole 844642 for Treescape. Works location: Tiriaukawa Rd. PPPD 42735. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 175 | 172 | 6880 | 0.021014 | 0.00012218 | 2014-12-10 | B | 0.010507 | 6.1088e-05 | 2015 | 2014-12-10 | B | 40 | 0.021014 | 0.00012218
1 | 3104200 | 2014-12-10 08:49 | 2014-12-10 13:35 | 286 | 1 | 286 | 0.00087471 | 3.0584e-06 | NAPA ID:04564 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2784 | Replace 3 x 11kv poles & cross arms at transformer X2784. Works location: Ruatangata Rd Whangaehu. WO 10141993. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 286 | 283 | 283 | 0.0008644 | 3.0544e-06 | 2014-12-10 | B | 0.0004322 | 1.527e-06 | 2015 | 2014-12-10 | B | 1 | 0.0008644 | 3.0544e-06
1 | 3124498 | 2014-12-10 08:59 | 2014-12-10 11:37 | 158.15 | 13 | 2055.95 | 0.006288 | 3.9759e-05 | NAPA ID:03552 TP_HINUERA GXP > PUTARURU SUB > HORAHORA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M0224 | To replace rotten 11kV termination arm at Pole # M0224. Works location: Arapuni Rd WO 10158134 | F2 | HORAHORA | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 158.15 | 155.15 | 2016.95 | 0.0061606 | 3.9708e-05 | 2014-12-10 | B | 0.0030803 | 1.9854e-05 | 2015 | 2014-12-10 | B | 13 | 0.0061606 | 3.9708e-05
1 | 3121608 | 2014-12-10 09:05 | 2014-12-10 14:13 | 307.2333 | 134 | 41169.2667 | 0.12591 | 0.00040983 | NAPA ID:04498 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6533 | Replace pole & wire. Works location: Ohawe Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 307.2333 | 304.2333 | 40767.2667 | 0.12452 | 0.00040929 | 2014-12-10 | B | 0.06226 | 0.00020465 | 2015 | 2014-12-10 | B | 134 | 0.12452 | 0.00040929
1 | 3141177 | 2014-12-10 09:15 | 2014-12-10 14:07 | 291.2167 | 273 | 79502.15 | 0.24315 | 0.00083495 | NAPA ID:04561 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9632/4 | Reconductoring 11kV lines. Works location: Kuaotunu Whitianga. WO 10150350. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 291.2167 | 288.2167 | 78683.15 | 0.24033 | 0.00083386 | 2014-12-10 | B | 0.12017 | 0.00041693 | 2015 | 2014-12-10 | B | 273 | 0.24033 | 0.00083386
1 | 3172510 | 2014-12-10 09:16 | 2014-12-10 15:04 | 347.7833 | 35 | 12172.4167 | 0.037228 | 0.00010704 | NAPA ID:05206 TP_HUIRANGI GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 211 | NORTHPOWER: 33/11kV pole and crossarm replacement between poles #759892 & 760694. WO number 10151691 TENIX: 3 Yearly Maintenance 33kV CB 210. WO number 10143214. Works location: Northpower Otaraora Rd Waitara, Tenix Motukawa Sub WO 10151691 | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 347.7833 | 344.7833 | 12067.4167 | 0.036859 | 0.0001069 | 2014-12-10 | B | 0.01843 | 5.3452e-05 | 2015 | 2014-12-10 | B | 35 | 0.036859 | 0.0001069
1 | 3140816 | 2014-12-10 09:30 | 2014-12-10 12:32 | 182.0333 | 35 | 6371.1667 | 0.019486 | 0.00010704 | NAPA ID:04891 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC802 | Unbind and straighten poles. Works location: Buchanan Rd, Pipiroa. WO 10140919. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 182.0333 | 179.0333 | 6266.1667 | 0.01914 | 0.0001069 | 2014-12-10 | B | 0.0095698 | 5.3452e-05 | 2015 | 2014-12-10 | B | 35 | 0.01914 | 0.0001069
1 | 3104207 | 2014-12-10 09:33 | 2014-12-10 16:00 | 387.0667 | 50 | 19353.3333 | 0.059191 | 0.00015292 | NAPA ID:04772 TP_MASTERTON GXP > AWATOITOI SUB > BLAIRLOGIE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2915 | T2915 Replace LV Frame. Works location: Tamarisk Dr Riversdale Masterton. WO 10150963. | F5 | BLAIRLOGIE | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 387.0667 | 384.0667 | 19203.3333 | 0.058655 | 0.00015272 | 2014-12-10 | B | 0.029328 | 7.6361e-05 | 2015 | 2014-12-10 | B | 50 | 0.058655 | 0.00015272
1 | 3104238 | 2014-12-10 09:49 | 2014-12-10 13:47 | 238 | 52 | 12376 | 0.037851 | 0.00015904 | NAPA ID:04737 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ROBERTS LINE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/647 | Relocate transformer T6/647 from 2 pole structure 2 new 1 pole structure. Treescape to cut trees in shutdown area. Refer to switching no 3411. Works location: Napier Rd, Palmerston North. WO 10154051. | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 238 | 235 | 12220 | 0.037325 | 0.00015883 | 2014-12-10 | B | 0.018663 | 7.9415e-05 | 2015 | 2014-12-10 | B | 52 | 0.037325 | 0.00015883
1 | 3191266 | 2014-12-10 09:49 | 2014-12-10 14:22 | 272.7 | 2 | 545.4 | 0.0016681 | 6.1168e-06 | NAPA ID:05217 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF7-015 | REPLACE 16MM CU WIRE ON THIS SPURLINE ONE CUST ONLY AT POWERCO REQUEST AS A URGENT JOB. Works location: Pongakawa Bush Rd. WO 10163170. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 272.7 | 269.7 | 539.4 | 0.0016476 | 6.1088e-06 | 2014-12-10 | B | 0.00082378 | 3.054e-06 | 2015 | 2014-12-10 | B | 2 | 0.0016476 | 6.1088e-06
1 | 3271355 | 2014-12-10 15:56 | 2014-12-11 13:07 | 1271.2667 | 66 | 53856 | 0.16471 | 0.00020186 | Restore Supply on Device C5335 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C5335 | Check to see if 3271359 3272017 is related to this . 6.47pm emailed svs hub for follow up. 21:49 PHIL ENROUTE NOW. Inspection on Transformer C5335 found centre HV fuse blown. Inspection found HV cable fault, All 3 fuses opened for safety. TENIX Unable t | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 816 | 813 | 53658 | 0.16389 | 0.00020159 | 2014-12-10 | C | 0.16389 | 0.00020159 | 2015 | 2014-12-10 | C | 66 | 0.16389 | 0.00020159
1 | 3271488 | 2014-12-10 18:29 | 2014-12-10 19:22 | 53 | 6 | 318 | 0.00097258 | 1.8351e-05 | Restore Supply on Device T4/104 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses E39 | 5.09pm retailer now advising there is a line down down across the customers driveway, check for safety required. hub has been advised. Isolation required from Fuses E40 to repair broken jumper at Fuses E39. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 300 | 0.00091633 | 1.8327e-05 | 2014-12-10 | C | 0.00091633 | 1.8327e-05 | 2015 | 2014-12-10 | C | 6 | 0.00091633 | 1.8327e-05
1 | 3271901 | 2014-12-10 18:46 | 2014-12-10 22:42 | 235.7 | 31 | 7306.7 | 0.022347 | 9.4811e-05 | Restore Supply on Device MA408 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 721366 | Car / Pole on Mawhiti Rd area. isolation required between ABS MA408 and ABS MA411. Pole change required including fitting new crossarms (HV, LV) and associated hardware. Relivened OK. NDR 43462 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 235.7 | 232.7 | 7213.7 | 0.022034 | 9.4687e-05 | 2014-12-10 | C | 0.022034 | 9.4687e-05 | 2015 | 2014-12-10 | C | 31 | 0.022034 | 9.4687e-05
1 | 3271950 | 2014-12-10 19:14 | 2014-12-10 19:56 | 41.5167 | 12 | 498.2 | 0.0015237 | 3.6701e-05 | Restore Supply on Device 6720 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720443 | Outage required between ABS KA780 and 6720 to replace 2 faulty DDO holders at Trasnformer K4230. Relivened Ok. | F1/F4 | MATAPU | KAPUNI SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 41.5167 | 38.5167 | 462.2 | 0.0014118 | 3.6653e-05 | 2014-12-10 | C | 0.0014118 | 3.6653e-05 | 2015 | 2014-12-10 | C | 12 | 0.0014118 | 3.6653e-05
1 | 3272007 | 2014-12-10 20:11 | 2014-12-10 21:00 | 49 | 2 | 98 | 0.00029973 | 6.1168e-06 | Restore Supply on Device L1130 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L1130 | Defective Transformer Changed (L1130) on Ball rd. Isolation From HT Fuses. Relivened OK. | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 49 | 46 | 92 | 0.00028101 | 6.1088e-06 | 2014-12-10 | C | 0.00028101 | 6.109e-06 | 2015 | 2014-12-10 | C | 2 | 0.00028101 | 6.1088e-06
1 | 3272045 | 2014-12-10 20:30 | 2014-12-10 20:53 | 23 | 38 | 874 | 0.0026731 | 0.00011622 | Restore Supply on Device T1/189 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/189 | Ohakea Fuse T1/189 opened and blown fuses replaced. 1 phase only reloaded and relivened. | F2 | SANSON LS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 23 | 20 | 760 | 0.0023214 | 0.00011607 | 2014-12-10 | C | 0.0023214 | 0.00011607 | 2015 | 2014-12-10 | C | 38 | 0.0023214 | 0.00011607
1 | 3272798 | 2014-12-10 21:18 | 2014-12-10 23:56 | 158.4333 | 8 | 298.4333 | 0.00091274 | 2.4467e-05 | Restore Supply on Device 1101 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 742120 | Transformer 1101 isolated & self AP issued to repair HV jumper onto transformer bushing | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 37.3042 | 34.3042 | 274.4333 | 0.00083824 | 2.4435e-05 | 2014-12-10 | C | 0.00083824 | 2.4435e-05 | 2015 | 2014-12-10 | C | 8 | 0.00083824 | 2.4435e-05
1 | 3272102 | 2014-12-10 22:35 | 2014-12-11 01:50 | 195.4 | 109 | 18108.6 | 0.055384 | 0.00033337 | Restore Supply on Device T42/2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P46620 | RS T42 Tripped - Fault located between Links T31 & T34 - Backfeed installed Via ABS V19 - cause of fault unable to be located in the dark, as no ICP's affected inspection left to be done in day light - Possium found on lines at Pole P46620 the next day - | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 166.1339 | 163.1339 | 17781.6 | 0.054313 | 0.00033293 | 2014-12-10 | C | 0.054313 | 0.00033293 | 2015 | 2014-12-10 | C | 109 | 0.054313 | 0.00033293
1 | 3272491 | 2014-12-10 22:48 | 2014-12-11 01:20 | 151.5667 | 271 | 16021.05 | 0.048999 | 0.00082883 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 746899 | Tripping on Katere CB11 on O/C. Fault caused by tree branch falling into conductors on Devon Rd. Isolation required between ABS 256 and Sw/Gear 563/4 with backfeed at Sw/Gear 563/1. Tree branch cut away and relivened OK. No damage to Powerco Assets. T Kas | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 59.1183 | 56.1183 | 15208.05 | 0.046452 | 0.00082775 | 2014-12-10 | C | 0.046452 | 0.00082775 | 2015 | 2014-12-10 | C | 271 | 0.046452 | 0.00082775
1 | 3272937 | 2014-12-11 00:47 | 2014-12-11 06:14 | 326.9167 | 197 | 64402.5833 | 0.19697 | 0.00060251 | Restore Supply on Device RC28 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R13047 | Recloser RC28 tripped to L/O - E/F flag -line sectionalised & patrolled - broken strain insulator located & replaced on pole # R13046 - problems in locating fault due to being in 1st section of isolation with no backfeeds available - LFI's also didn't ope | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 326.9167 | 323.9167 | 63811.5833 | 0.19491 | 0.00060172 | 2014-12-11 | C | 0.19491 | 0.00060172 | 2015 | 2014-12-11 | C | 197 | 0.19491 | 0.00060172
1 | 3273278 | 2014-12-11 05:51 | 2014-12-11 08:56 | 185.0667 | 5 | 569.6333 | 0.0017422 | 1.5292e-05 | Restore Supply on Device T348 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7637, 7024 | plz check 3273306 565 Te Kopi Road, Masterton, 32703316 45 Te Kopi Road. 7am faultman onsite no one answering the door, tried customers landline and went straight to voicemail. Called cellphone that was on voicemail and customer will go out and meet faul | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 113.9267 | 110.9267 | 554.6333 | 0.0016941 | 1.5272e-05 | 2014-12-11 | C | 0.0016941 | 1.5272e-05 | 2015 | 2014-12-11 | C | 5 | 0.0016941 | 1.5272e-05
1 | 3273285 | 2014-12-11 06:16 | 2014-12-11 10:50 | 273.7833 | 3 | 355.6333 | 0.0010877 | 9.1753e-06 | Restore Supply on Device T2563 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7054 | *** please check if oms 3277387 is part of this outage *** FM advise: Palmer Road would have been affected. Replace 2 x 10 amp fuses. Reason: Unknown, possible tree interfering with line, faultman will defect the tree. Fuse #7054. No other assets repaire | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 118.5444 | 115.5444 | 346.6333 | 0.0010588 | 9.1633e-06 | 2014-12-11 | C | 0.0010588 | 9.163e-06 | 2015 | 2014-12-11 | C | 3 | 0.0010588 | 9.1633e-06
1 | 3276196 | 2014-12-11 07:02 | 2014-12-11 09:42 | 160 | 1151 | 178682.5 | 0.54649 | 0.0035202 | Restore Supply on Device X22 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | X20 | 11 kV feeder fault. Patrolled line, no fault found. Power back on. Dave Thompson and shazil Khan attended. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 155.2411 | 152.2411 | 175229.5 | 0.53523 | 0.0035156 | 2014-12-11 | C | 0.53523 | 0.0035156 | 2015 | 2014-12-11 | C | 1151 | 0.53523 | 0.0035156
1 | 3132538 | 2014-12-11 08:30 | 2014-12-11 15:54 | 444 | 1 | 444 | 0.0013579 | 3.0584e-06 | NAPA ID:04227 TP_MASTERTON GXP > CLAREVILLE SUB > SOMERSET RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 823856 | Open Line Break at pole 823856 and construciton of site for installation of new 11kV voltage Regulators 11050/2 on Somerset Feeder. Work Location: Gladstone Road. Work Order 10153767. | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 444 | 441 | 441 | 0.001347 | 3.0544e-06 | 2014-12-11 | B | 0.0006735 | 1.527e-06 | 2015 | 2014-12-11 | B | 1 | 0.001347 | 3.0544e-06
1 | 3133433 | 2014-12-11 08:35 | 2014-12-11 15:55 | 439.5167 | 281 | 79279.4667 | 0.24247 | 0.00085942 | NAPA ID:04766 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS J42 | replace old fibreglass kiosk with new 300KVA citypad. Works location: Wild St WO 10158157 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 282.1333 | 279.1333 | 78436.4667 | 0.23958 | 0.00085829 | 2014-12-11 | B | 0.11979 | 0.00042915 | 2015 | 2014-12-11 | B | 281 | 0.23958 | 0.00085829
1 | 3121325 | 2014-12-11 08:46 | 2014-12-11 13:43 | 296.9667 | 63 | 18708.9 | 0.05722 | 0.00019268 | NAPA ID:04618 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 790743 | Replace 11kV pole 790743 and ABS 177. Works location: Longacre Valley Rd. WO 10141785 | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 296.9667 | 293.9667 | 18519.9 | 0.056568 | 0.00019243 | 2014-12-11 | B | 0.028284 | 9.6214e-05 | 2015 | 2014-12-11 | B | 63 | 0.056568 | 0.00019243
1 | 2491037 | 2014-12-11 08:46 | 2014-12-11 14:39 | 353 | 16 | 5648 | 0.017274 | 4.8935e-05 | NAPA ID:03627 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 154 | 33/6.6kV Pole & Crossarm replacement Install TEMP66. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 353 | 350 | 5600 | 0.017105 | 4.8871e-05 | 2014-12-11 | B | 0.0085524 | 2.4435e-05 | 2015 | 2014-12-11 | B | 16 | 0.017105 | 4.8871e-05
1 | 3157088 | 2014-12-11 09:08 | 2014-12-11 14:39 | 331 | 4 | 1324 | 0.0040494 | 1.2234e-05 | NAPA ID:05128 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 797712 | 11KV POLE REPLACEMENT. Works location: Humes Rd. WO 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 331 | 328 | 1312 | 0.0040074 | 1.2218e-05 | 2014-12-11 | B | 0.0020037 | 6.109e-06 | 2015 | 2014-12-11 | B | 4 | 0.0040074 | 1.2218e-05
1 | 3158186 | 2014-12-11 09:30 | 2014-12-11 10:50 | 80.1333 | 10 | 801.3333 | 0.0024508 | 3.0584e-05 | NAPA ID:03933 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 208689 | REPLACE HV ARMS AS PER SCOPE. Works location: Plummer Point Rd. WO 10148295. | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 80.1333 | 77.1333 | 771.3333 | 0.002356 | 3.0544e-05 | 2014-12-11 | B | 0.001178 | 1.5272e-05 | 2015 | 2014-12-11 | B | 10 | 0.002356 | 3.0544e-05
1 | 3141212 | 2014-12-11 09:30 | 2014-12-11 10:30 | 60 | 14 | 840 | 0.0025691 | 4.2818e-05 | NAPA ID:04840 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC353 | Replace DDO's and lightning arrestors. Works location: Marae Rd Manaia Coromandel WO 10166961. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 798 | 0.0024374 | 4.2762e-05 | 2014-12-11 | B | 0.0012187 | 2.1381e-05 | 2015 | 2014-12-11 | B | 14 | 0.0024374 | 4.2762e-05
1 | 3135181 | 2014-12-11 09:30 | 2014-12-11 14:47 | 317 | 27 | 8559 | 0.026177 | 8.2577e-05 | NAPA ID:03687 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 748139, 748160 | Reconductor between 748139 and 748160. Works location: Egmont Rd. WO 10145448 | F4 | KATERE 5 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 317 | 314 | 8478 | 0.025895 | 8.2469e-05 | 2014-12-11 | B | 0.012948 | 4.1235e-05 | 2015 | 2014-12-11 | B | 27 | 0.025895 | 8.2469e-05
1 | 3135161 | 2014-12-11 09:35 | 2014-12-11 14:51 | 315.9833 | 18 | 5687.7 | 0.017395 | 5.5052e-05 | NAPA ID:04854 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 810224 | Tree trimming, Felling between poles 810224, 810225. Works location: James Rd Turakina Valley Rd. PPPD 44026 | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 315.9833 | 312.9833 | 5633.7 | 0.017208 | 5.498e-05 | 2014-12-11 | B | 0.0086039 | 2.749e-05 | 2015 | 2014-12-11 | B | 18 | 0.017208 | 5.498e-05
1 | 3120647 | 2014-12-11 09:51 | 2014-12-11 12:33 | 162.2833 | 180 | 25331.9 | 0.077476 | 0.00055052 | NAPA ID:04929 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 788721 | Replace red tag pole 788721 with digger. Works location: Rongoiti Rd. WO 10159785 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140.7328 | 137.7328 | 24791.9 | 0.075725 | 0.0005498 | 2014-12-11 | B | 0.037862 | 0.0002749 | 2015 | 2014-12-11 | B | 180 | 0.075725 | 0.0005498
1 | 3280998 | 2014-12-11 10:00 | 2014-12-11 14:48 | 288 | 65 | 3900 | 0.011928 | 0.0001988 | Restore Supply on Device B16 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B16 | Greg from Meridian called to advise that property at 20 Tollbridge Road advised that they have a blown pole fuse. Damaged jumper found at pole P36019 - Isolated at ABS B16 - Jumper Repaired and, feeder restored to service - used 1 X Lug. Anjay Prasad atte | F4 | TAIKOREA | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 3705 | 0.011317 | 0.00019854 | 2014-12-11 | C | 0.011317 | 0.00019854 | 2015 | 2014-12-11 | C | 65 | 0.011317 | 0.00019854
1 | 3135168 | 2014-12-11 10:00 | 2014-12-11 14:25 | 265 | 29 | 7685 | 0.023504 | 8.8694e-05 | NAPA ID:04936 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L1030 | replace existing transformer structure KL1030 and transformer, cross arms to poles 726880, 726877, 726876 and 726868. Works location: Wilson Rd Wood St Kakaramea. WO 60914PE | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 265 | 262 | 7598 | 0.023208 | 8.8578e-05 | 2014-12-11 | B | 0.011604 | 4.4289e-05 | 2015 | 2014-12-11 | B | 29 | 0.023208 | 8.8578e-05
1 | 3278231 | 2014-12-11 10:05 | 2014-12-11 12:57 | 172.2 | 1 | 172.2 | 0.00052666 | 3.0584e-06 | Restore Supply on Device T5/278 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 154 BARROW ROAD, CHELTENHAM, FEILDING | 1137hrs tried to call customer to see if power back on but call went to voicemail. F/man (Shaz) thought it might be part of area fault from this morning. Svs hub sending f/man to check this out now. part of feeder fualt - Kimbolton OMS 3271619 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 172.2 | 169.2 | 169.2 | 0.00051681 | 3.0544e-06 | 2014-12-11 | C | 0.00051681 | 3.054e-06 | 2015 | 2014-12-11 | C | 1 | 0.00051681 | 3.0544e-06
1 | 3121340 | 2014-12-11 10:41 | 2014-12-11 16:08 | 327.8167 | 10 | 3278.1667 | 0.010026 | 3.0584e-05 | NAPA ID:04156 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K58 | Replace 11kV 400v transformer cross arms. Works location: Lower Pakihikura Rd. WO 10142182. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 327.8167 | 324.8167 | 3248.1667 | 0.0099213 | 3.0544e-05 | 2014-12-11 | B | 0.0049606 | 1.5272e-05 | 2015 | 2014-12-11 | B | 10 | 0.0099213 | 3.0544e-05
1 | 3141189 | 2014-12-11 10:55 | 2014-12-11 11:30 | 35 | 1 | 35 | 0.00010704 | 3.0584e-06 | NAPA ID:04841 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IP428 | replace DDO's and crossarm. Works location: Manaia Rd Manaia Coromandel WO 10166961 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 35 | 32 | 32 | 9.7742e-05 | 3.0544e-06 | 2014-12-11 | B | 4.8871e-05 | 1.527e-06 | 2015 | 2014-12-11 | B | 1 | 9.7742e-05 | 3.0544e-06
1 | 3279008 | 2014-12-11 12:00 | 2014-12-11 14:02 | 122.1 | 7 | 497.4667 | 0.0015215 | 2.1409e-05 | Restore Supply on Device T5/65 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | recloser N21 | ecloser N21. cause: unknown. possible related to kimbolton feeder fault this morning (oms 3271619). oh/hv. FM advise peka road, mangamako road and marshall road all affected. NB: No Paper Work Created - Closed by Dispatch. | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 71.0667 | 68.0667 | 476.4667 | 0.0014553 | 2.1381e-05 | 2014-12-11 | C | 0.0014553 | 2.1381e-05 | 2015 | 2014-12-11 | C | 7 | 0.0014553 | 2.1381e-05
1 | 3281106 | 2014-12-11 13:30 | 2014-12-11 14:16 | 46 | 6 | 276 | 0.00084412 | 1.8351e-05 | Restore Supply on Device FC799 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole D1381 | Replaced Crossam at Pole D1381 Used 1 X H/T Crossarm 3X H/T Insulators | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 46 | 43 | 258 | 0.00078804 | 1.8327e-05 | 2014-12-11 | C | 0.00078804 | 1.8327e-05 | 2015 | 2014-12-11 | C | 6 | 0.00078804 | 1.8327e-05
1 | 3280917 | 2014-12-11 13:55 | 2014-12-11 16:29 | 154.2167 | 1 | 154.2167 | 0.00047166 | 3.0584e-06 | Restore Supply on Device T2/239 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 1304 HIGHWAY 56 , PALMERSTON NORTH | part of HV fault - full power to property | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 154.2167 | 151.2167 | 151.2167 | 0.00046188 | 3.0544e-06 | 2014-12-11 | C | 0.00046188 | 3.054e-06 | 2015 | 2014-12-11 | C | 1 | 0.00046188 | 3.0544e-06
1 | 3158222 | 2014-12-11 14:01 | 2014-12-11 14:27 | 26.1667 | 2 | 52.3333 | 0.00016006 | 6.1168e-06 | NAPA ID:03934 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 208687 | RESTRAIN 11KV OH LINES ONLY. Works location: Plummer Point Rd. WO 10148295. | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 26.1667 | 23.1667 | 46.3333 | 0.00014152 | 6.1088e-06 | 2014-12-11 | B | 7.0761e-05 | 3.054e-06 | 2015 | 2014-12-11 | B | 2 | 0.00014152 | 6.1088e-06
1 | 3280516 | 2014-12-11 14:03 | 2014-12-11 15:44 | 100.8 | 8 | 806.4 | 0.0024663 | 2.4467e-05 | Restore Supply on Device TC860 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 14098 | 12.48pm advised Tallia at svs hub of job. 3385 State Highway 2, Mangatarata. Stewart requesting another faultman in bucket truck to attend to help to rehang the line. PULLED UP 1 WIRE, RE SAGGED OTHER THREE. LESS THAN ONE SPAN ONE PHASE. NO OTHER ASSETS R | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.8 | 97.8 | 782.4 | 0.0023898 | 2.4435e-05 | 2014-12-11 | C | 0.0023898 | 2.4435e-05 | 2015 | 2014-12-11 | C | 8 | 0.0023898 | 2.4435e-05
1 | 3281619 | 2014-12-11 17:54 | 2014-12-12 00:38 | 404.6833 | 379 | 51723.3833 | 0.15819 | 0.0011591 | Restore Supply on Device 4812 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 758537 | Pole replaced after car accident. Isolation at ABS's 5591 & 5343 no back feeds available. Materials used: 2x concrete poles, crane was used to place poles as Tenix Hiab trucks can not lift a double pole. NDR to follow. Phil Webby attended. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 136.4733 | 133.4733 | 50586.3833 | 0.15451 | 0.0011576 | 2014-12-11 | C | 0.15451 | 0.0011576 | 2015 | 2014-12-11 | C | 379 | 0.15451 | 0.0011576
1 | 3303232 | 2014-12-12 07:45 | 2014-12-12 10:45 | 180 | 10 | 1779.9833 | 0.0054439 | 3.0584e-05 | Restore Supply on Device TEMP30 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22914 | Top burnt off of Softwood Pole. Faultman replaced crossarm and all associated hardware to restore power temporarily. Pole to be defected for replacement. Trevor Pocock attended. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 177.9983 | 174.9983 | 1749.9833 | 0.0053452 | 3.0544e-05 | 2014-12-12 | C | 0.0053452 | 3.0544e-05 | 2015 | 2014-12-12 | C | 10 | 0.0053452 | 3.0544e-05
1 | 3351288 | 2014-12-12 08:02 | 2014-12-12 15:10 | 428 | 1 | 428 | 0.001309 | 3.0584e-06 | Restore Supply on Device T4254 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S363 | Install new voltage regulators on the somerset fdr. Parent 3132717. | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 428 | 425 | 425 | 0.0012981 | 3.0544e-06 | 2014-12-12 | C | 0.0012981 | 3.054e-06 | 2015 | 2014-12-12 | C | 1 | 0.0012981 | 3.0544e-06
1 | 3147041 | 2014-12-12 08:43 | 2014-12-12 13:55 | 312.6333 | 134 | 41892.8667 | 0.12813 | 0.00040983 | NAPA ID:04499 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 6533 | Replace pole & wire. Works location: Ohawe Rd WO 10141948 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 312.6333 | 309.6333 | 41490.8667 | 0.12673 | 0.00040929 | 2014-12-12 | B | 0.063365 | 0.00020465 | 2015 | 2014-12-12 | B | 134 | 0.12673 | 0.00040929
1 | 3135188 | 2014-12-12 08:49 | 2014-12-12 13:28 | 278.5167 | 7 | 1949.6167 | 0.0059628 | 2.1409e-05 | NAPA ID:04888 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 4015 | isolation of 11 kv line for Treescape to fell trees. Works location: State Hwy 1 Mangaweka. PPPD 42819. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 278.5167 | 275.5167 | 1928.6167 | 0.0058908 | 2.1381e-05 | 2014-12-12 | B | 0.0029454 | 1.069e-05 | 2015 | 2014-12-12 | B | 7 | 0.0058908 | 2.1381e-05
1 | 3240335 | 2014-12-12 09:00 | 2014-12-12 14:04 | 304 | 13 | 3952 | 0.012087 | 3.9759e-05 | NAPA ID:02640 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC978 | To replace 11kV and LV cross arms. Works location: SH29 Hinuera WO 10160662 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 304 | 301 | 3913 | 0.011952 | 3.9708e-05 | 2014-12-12 | B | 0.005976 | 1.9854e-05 | 2015 | 2014-12-12 | B | 13 | 0.011952 | 3.9708e-05
1 | 3174789 | 2014-12-12 09:00 | 2014-12-12 13:53 | 292.3333 | 130 | 38003.3333 | 0.11623 | 0.00039759 | NAPA ID:04838 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 349 | Stand over for tree cutting (Asplundh). Works location: Te Kouma Rd Coromandel. WO 10168630. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 292.3333 | 289.3333 | 37613.3333 | 0.11489 | 0.00039708 | 2014-12-12 | B | 0.057444 | 0.00019854 | 2015 | 2014-12-12 | B | 130 | 0.11489 | 0.00039708
1 | 2385925 | 2014-12-12 09:19 | 2014-12-12 14:24 | 304.75 | 43 | 13104.25 | 0.040078 | 0.00013151 | NAPA ID:03499 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 5423 | 33/6.6kV Pole & Crossarm replacement. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 304.75 | 301.75 | 12975.25 | 0.039632 | 0.00013134 | 2014-12-12 | B | 0.019816 | 6.567e-05 | 2015 | 2014-12-12 | B | 43 | 0.039632 | 0.00013134
1 | 3141050 | 2014-12-12 10:15 | 2014-12-12 14:08 | 233 | 10 | 2330 | 0.0071261 | 3.0584e-05 | NAPA ID:04934 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 505 | to replace two spans of low tension for new service. Works location: Atkinson Rd WO 10151249 See OMS 3141050 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 233 | 230 | 2300 | 0.0070252 | 3.0544e-05 | 2014-12-12 | B | 0.0035126 | 1.5272e-05 | 2015 | 2014-12-12 | B | 10 | 0.0070252 | 3.0544e-05
1 | 3303256 | 2014-12-12 10:34 | 2014-12-12 10:55 | 21 | 98 | 2058 | 0.0062942 | 0.00029973 | Restore Supply on Device TD4-042 | 11000 | UNPLANNED | Distribution Equip. | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-042 | During planned L/V job at transformer TD4 042 it was noticed the live L/V panel bus had dropped close to metal frame ( broken mounts ) Transformer H/V fuses opened to repair L/V frame, repairs carried out all service restored. Denis Ngatai attended. Mater | F3 | CAMERON RD | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 21 | 18 | 1764 | 0.005388 | 0.00029933 | 2014-12-12 | C | 0.005388 | 0.00029933 | 2015 | 2014-12-12 | C | 98 | 0.005388 | 0.00029933
1 | 3303363 | 2014-12-12 11:10 | 2014-12-12 13:14 | 123.8667 | 1 | 123.8667 | 0.00037884 | 3.0584e-06 | Restore Supply on Device TP1311 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12755 | Fuse FP1404 open and tagged for isolation to repair broken xarm. Used 2 X H/T Crossarms 1 X H/T Insulator 3 X Polymas | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 123.8667 | 120.8667 | 120.8667 | 0.00036918 | 3.0544e-06 | 2014-12-12 | C | 0.00036918 | 3.054e-06 | 2015 | 2014-12-12 | C | 1 | 0.00036918 | 3.0544e-06
1 | 3260143 | 2014-12-12 13:00 | 2014-12-12 14:41 | 101 | 1 | 101 | 0.0003089 | 3.0584e-06 | NAPA ID:04441 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Pole E0169 | To install new pole between Poles E0169 and E0170 to improve ground clearances. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 101 | 98 | 98 | 0.00029933 | 3.0544e-06 | 2014-12-12 | B | 0.00014967 | 1.527e-06 | 2015 | 2014-12-12 | B | 1 | 0.00029933 | 3.0544e-06
1 | 3304301 | 2014-12-12 18:50 | 2014-12-12 19:40 | 50 | 1 | 50 | 0.00015292 | 3.0584e-06 | Restore Supply on Device 2257T | 6600 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 758785 | 6.02pm advised Glo of lines down & advised control 226 Mana Road, Inglewood 100 M 6MM PVC , ONE SPAN TW0 PHASES 6 CONNECTORS NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | RATAPIKO | MOTUKAWA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 47 | 0.00014356 | 3.0544e-06 | 2014-12-12 | C | 0.00014356 | 3.054e-06 | 2015 | 2014-12-12 | C | 1 | 0.00014356 | 3.0544e-06
1 | 3304197 | 2014-12-12 19:04 | 2014-12-12 19:17 | 12.9833 | 2 | 21 | 6.4227e-05 | 6.1168e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/347 | DN 5595, TX NEEDS TO BE TAPPED DOWN READINGS 46 , 248 249.2 phase to neutral, to be attended after 5pm Anjay attended original OMS 330370. TX T2/347 Chris called as needing access to property, called customer and they will meet faultman onsite. Tapped | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 10.5 | 7.5 | 15 | 4.5816e-05 | 6.1088e-06 | 2014-12-12 | B | 2.2908e-05 | 3.054e-06 | 2015 | 2014-12-12 | B | 2 | 4.5816e-05 | 6.1088e-06
1 | 3141200 | 2014-12-13 08:30 | 2014-12-13 12:18 | 228.15 | 50 | 11407.5 | 0.034889 | 0.00015292 | NAPA ID:04073 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 841268 | isolate T1682 and make a live line break at pole 841268 so that 11kV at T1682 can be moved on to new transformer pole which is to be installed behind existing pole on 17/09/14. Works location: High St Carterton. WO 10140873 IR6938. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 228.15 | 225.15 | 11257.5 | 0.034385 | 0.00015272 | 2014-12-13 | B | 0.017193 | 7.6361e-05 | 2015 | 2014-12-13 | B | 50 | 0.034385 | 0.00015272
1 | 3351627 | 2014-12-13 09:01 | 2014-12-13 14:57 | 356 | 46 | 16376 | 0.050085 | 0.00014069 | Restore Supply on Device cut side 1 temp line [1294,0,100,0] | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp 66 | planned work Napa 3625 - Parent 2491070 33/6.6kV Pole & Crossarm replacement. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 356 | 353 | 16238 | 0.049598 | 0.0001405 | 2014-12-13 | C | 0.049598 | 0.0001405 | 2015 | 2014-12-13 | C | 46 | 0.049598 | 0.0001405
1 | 3304528 | 2014-12-13 10:09 | 2014-12-13 21:45 | 695.7833 | 1 | 695.7833 | 0.002128 | 3.0584e-06 | Restore Supply on Device T2321 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Transformer T2321 | No Power, part of Planned outage | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 695.7833 | 692.7833 | 692.7833 | 0.0021161 | 3.0544e-06 | 2014-12-13 | C | 0.0021161 | 3.054e-06 | 2015 | 2014-12-13 | C | 1 | 0.0021161 | 3.0544e-06
1 | 3304594 | 2014-12-13 13:03 | 2014-12-13 15:08 | 124.4167 | 1 | 124.4167 | 0.00038052 | 3.0584e-06 | Restore Supply on Device TD3-350 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TD3-098. | part of shutdown 4601 as advised by f/man - checking what tx ppty is fed from as is not listed on the spreadsheet. ppty is feed from Tx TD3-098 Bad Data Email sent to Kasey :0000965173TU, 22 Orange Lane, Bethlehem, Tauranga. feeding out of TD3-350 on | F3 | MOFFAT RD | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 124.4167 | 121.4167 | 121.4167 | 0.00037086 | 3.0544e-06 | 2014-12-13 | C | 0.00037086 | 3.054e-06 | 2015 | 2014-12-13 | C | 1 | 0.00037086 | 3.0544e-06
1 | 3184035 | 2014-12-13 13:16 | 2014-12-13 14:47 | 90.4833 | 1 | 90.4833 | 0.00027674 | 3.0584e-06 | NAPA ID:05166 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 6 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G202 | Replace oil @ TX G202 T High Moisture & Acidity Content. International Fine Foods Factory (Outage for Factory Maintenance). Works location: Highbury Ave, Palmerston North. WO 10162325 | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 90.4833 | 87.4833 | 87.4833 | 0.00026721 | 3.0544e-06 | 2014-12-13 | B | 0.00013361 | 1.527e-06 | 2015 | 2014-12-13 | B | 1 | 0.00026721 | 3.0544e-06
1 | 3306039 | 2014-12-14 07:24 | 2014-12-14 10:21 | 176.6833 | 987 | 83427.4 | 0.25516 | 0.0030187 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | C2346 | Tree through lines at Pole C2346. Tree removed from lines. no damage to lines. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 84.5262 | 81.5262 | 80466.4 | 0.24578 | 0.0030147 | 2014-12-14 | C | 0.24578 | 0.0030147 | 2015 | 2014-12-14 | C | 987 | 0.24578 | 0.0030147
1 | 3308416 | 2014-12-14 09:15 | 2014-12-14 15:16 | 360.8667 | 359 | 65255.7 | 0.19958 | 0.001098 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I1792 | CB 5 tripped and L/O on E/F and O/C. Line down found at pole I1792. 6 mtrs Squirrel conductor and 6 sleeves | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 181.7708 | 178.7708 | 64178.7 | 0.19603 | 0.0010965 | 2014-12-14 | C | 0.19603 | 0.0010965 | 2015 | 2014-12-14 | C | 359 | 0.19603 | 0.0010965
1 | 3151972 | 2014-12-14 09:25 | 2014-12-14 17:36 | 491 | 93 | 45663 | 0.13966 | 0.00028443 | NAPA ID:04802 TP_HAWERA GXP > CAMBRIA SUB > GLOVER RD WEST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 8608 | Run new new Kyrpton conductor connect new Hv cable close LL break. Works location: Glover Rd Hawera WO 10155221 Job had an over run due to still had live LV in work area they had to find before they could start work. | F3 | GLOVER RD WEST | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 491 | 488 | 45384 | 0.13862 | 0.00028406 | 2014-12-14 | B | 0.069311 | 0.00014203 | 2015 | 2014-12-14 | B | 93 | 0.13862 | 0.00028406
1 | 3309539 | 2014-12-14 10:46 | 2014-12-14 13:15 | 148.3667 | 867 | 38570.3167 | 0.11796 | 0.0026517 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12593 | CB5 tripped on E/F, and O/C and L/O. Loose jumper at pole V12593 resting on x-arm. Jumper re-attached | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 44.4871 | 41.4871 | 35969.3167 | 0.10987 | 0.0026482 | 2014-12-14 | C | 0.10987 | 0.0026482 | 2015 | 2014-12-14 | C | 867 | 0.10987 | 0.0026482
1 | 3311928 | 2014-12-14 13:46 | 2014-12-14 15:04 | 78.1333 | 18 | 1406.4 | 0.0043014 | 5.5052e-05 | Restore Supply on Device 1123 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 8905 | Customer heard a loud explosion from outside of the premise. She thinks it may have been the Tx - no no power. 217 Brown Road, Waitara. Check if affects OMS 3311925. 1427hrs advised svs hub. Faultman found 2 blown fuses at Fuses 8905, line was patrolled | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 78.1333 | 75.1333 | 1352.4 | 0.0041308 | 5.498e-05 | 2014-12-14 | C | 0.0041308 | 5.498e-05 | 2015 | 2014-12-14 | C | 18 | 0.0041308 | 5.498e-05
1 | 3311959 | 2014-12-14 14:14 | 2014-12-14 15:37 | 82.9667 | 685 | 22460.6333 | 0.068694 | 0.002095 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V13147 | CB3 tripped on E/F, O/C and L/O. Report of line down at TC4702 (Pole V13147). 10 mtrs 25mm conductor & 4 Sleeves. | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 32.7892 | 29.7892 | 20405.6333 | 0.062327 | 0.0020923 | 2014-12-14 | C | 0.062327 | 0.0020923 | 2015 | 2014-12-14 | C | 685 | 0.062327 | 0.0020923
1 | 3313323 | 2014-12-14 14:28 | 2014-12-14 17:39 | 190.45 | 307 | 56174.4167 | 0.17181 | 0.00093894 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9736 | Feeder Sectionalised no fault found. Suspect Recloser 9736 faulty. Recloser bypassed. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 182.9786 | 179.9786 | 55253.4167 | 0.16877 | 0.00093771 | 2014-12-14 | C | 0.16877 | 0.00093771 | 2015 | 2014-12-14 | C | 307 | 0.16877 | 0.00093771
1 | 3314720 | 2014-12-14 15:35 | 2014-12-15 10:59 | 1163.2 | 6 | 5422.7833 | 0.016585 | 1.8351e-05 | Restore Supply on Device TC4504 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4504 | Removed trees from LV Lines, restrained LV Lines. When closing in HV fuses after repairs, HV fuses did not hold in. Transformer TC4504 is blown. Will be left off overnight until tomorrow morning. Transformer replaced all service restored . | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 903.7972 | 900.7972 | 5404.7833 | 0.016508 | 1.8327e-05 | 2014-12-14 | C | 0.016508 | 1.8327e-05 | 2015 | 2014-12-14 | C | 6 | 0.016508 | 1.8327e-05
1 | 3315123 | 2014-12-14 16:15 | 2014-12-14 16:30 | 15.8833 | 685 | 10880.0833 | 0.033276 | 0.002095 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 3 | Trip O/C. L/O. Reclosed after 15 mins OK. Suspect Line Clash | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15.8833 | 12.8833 | 8825.0833 | 0.026956 | 0.0020923 | 2014-12-14 | C | 0.026956 | 0.0020923 | 2015 | 2014-12-14 | C | 685 | 0.026956 | 0.0020923
1 | 3315826 | 2014-12-14 16:29 | 2014-12-14 18:06 | 97.45 | 854 | 55567.4667 | 0.16995 | 0.0026119 | Restore Supply on Device TC1180 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V0321 | job rolled up into feeder. lines repaired at 505 TIKI ROAD, used 2x 25m crimp sleeve and 6 meters of conductor | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 65.0673 | 62.0673 | 53005.4667 | 0.1619 | 0.0026085 | 2014-12-14 | C | 0.1619 | 0.0026085 | 2015 | 2014-12-14 | C | 854 | 0.1619 | 0.0026085
1 | 3315833 | 2014-12-14 16:35 | 2014-12-14 21:19 | 283.6 | 359 | 44871.9 | 0.13724 | 0.001098 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I1792 | at 16:35 Piako Sub, CB 5 Kiwitahi Feeder, Tripped, L/O. Report came in of lines down at Pole I1792. Lines had already come down here earlier in the day. Isolated Lines at ABS IC779. Permit Issued & Repairs carried out. All Power Restored on completion. De | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 124.9914 | 121.9914 | 43794.9 | 0.13377 | 0.0010965 | 2014-12-14 | C | 0.13377 | 0.0010965 | 2015 | 2014-12-14 | C | 359 | 0.13377 | 0.0010965
1 | 3316202 | 2014-12-14 16:51 | 2014-12-14 21:58 | 307.6 | 645 | 182841.65 | 0.55921 | 0.0019727 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | T1318 | 31 Trotter Ave report of Transformer Sparking. James Kennerley was actually the faultman that attended this job. It was 2R a job. Unsure what has gone on with the crew requests for this job. Time Onsite: 19:20. Offsite: 22:25. 6x HV Sleeves, 6m of conduct | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 283.4754 | 280.4754 | 180906.65 | 0.55257 | 0.0019701 | 2014-12-14 | C | 0.55257 | 0.0019701 | 2015 | 2014-12-14 | C | 645 | 0.55257 | 0.0019701
1 | 3314729 | 2014-12-14 17:01 | 2014-12-14 17:24 | 23.3333 | 35 | 816.6667 | 0.0024977 | 0.00010704 | Restore Supply on Device TC4009 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C13045 | HV Jumper off at Pole C13045. Re-attached | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 23.3333 | 20.3333 | 711.6667 | 0.0021737 | 0.0001069 | 2014-12-14 | C | 0.0021737 | 0.0001069 | 2015 | 2014-12-14 | C | 35 | 0.0021737 | 0.0001069
1 | 3318890 | 2014-12-14 19:03 | 2014-12-14 21:08 | 124.6167 | 779 | 76203.7167 | 0.23306 | 0.0023825 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T0968 | at 19:04 Thames Sub, CB 4 Thames Coast Feeder Tripped, L/O. Investigation began. Found lines down at Pole T0968. Isolated Lines at ABS 2722 & ABS 9426. Permit issued & repairs carried out. All Power Restored on completion. Steve McKinney actually attended | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 97.8225 | 94.8225 | 73866.7167 | 0.22562 | 0.0023794 | 2014-12-14 | C | 0.22562 | 0.0023794 | 2015 | 2014-12-14 | C | 779 | 0.22562 | 0.0023794
1 | 3319737 | 2014-12-14 20:03 | 2014-12-14 20:33 | 30.2833 | 7 | 211.9833 | 0.00064833 | 2.1409e-05 | Restore Supply on Device FP1148 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1148 | Replaced 2x HV Fuses & 1x HV Fuse Carrier. Stu Beaver Attended. | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 30.2833 | 27.2833 | 190.9833 | 0.00058334 | 2.1381e-05 | 2014-12-14 | C | 0.00058334 | 2.1381e-05 | 2015 | 2014-12-14 | C | 7 | 0.00058334 | 2.1381e-05
1 | 4222522 | 2014-12-14 21:53 | 2014-12-14 23:10 | 77.35 | 5 | 386.75 | 0.0011828 | 1.5292e-05 | Restore Supply on Device TC1249 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Transformer TC1249 | Fuses blown. Replaced and relivened. Restaged Outage | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 77.35 | 74.35 | 371.75 | 0.0011355 | 1.5272e-05 | 2014-12-14 | C | 0.0011355 | 1.5272e-05 | 2015 | 2014-12-14 | C | 5 | 0.0011355 | 1.5272e-05
1 | 3321736 | 2014-12-14 21:53 | 2014-12-15 10:11 | 738.6833 | 3183 | 146121.75 | 0.4469 | 0.009735 | Restore Supply on Device 17 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB1 | Kerepehi CB17 and CB19 tripped on E/F and L/O. Fault on CB1 - CB1 did not clear fault. Feeder sectionalised. No fault found. Need to check cable between switchgear 9459/3 and 9054/1. NOC to instigate protection review. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 45.9069 | 42.9069 | 136572.75 | 0.41715 | 0.0097222 | 2014-12-14 | C | 0.41715 | 0.0097222 | 2015 | 2014-12-14 | C | 3183 | 0.41715 | 0.0097222
1 | 3319766 | 2014-12-14 23:48 | 2014-12-15 12:29 | 761.4833 | 1 | 1522.1333 | 0.0046553 | 3.0584e-06 | Restore Supply on Device TC5114 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5114 | Broken DDO at TC5114. FC4076 open. needs 2nd response. Fuse holder x 1 & fuse link x 1 ( H/V ) replaced, all service restored. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1522.1333 | 1519.1333 | 1519.1333 | 0.0046401 | 3.0544e-06 | 2014-12-14 | C | 0.0046401 | 3.054e-06 | 2015 | 2014-12-14 | C | 1 | 0.0046401 | 3.0544e-06
1 | 3327253 | 2014-12-15 00:10 | 2014-12-15 00:27 | 17 | 535 | 9095 | 0.027816 | 0.0016363 | Restore Supply on Device RP15 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | at 00:10, Coromandel Sub, CB 1 Colville, Recloser RP15 Tripped, E/F, L/O. Auto Reclose was disabled on this feeder due to a previous fault on this feeder. Waited 15 minutes, tried manual reclose and feeder held in at 00:26. at 00:31, Recloser RP15 Trip | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 7490 | 0.022878 | 0.0016341 | 2014-12-15 | C | 0.022878 | 0.0016341 | 2015 | 2014-12-15 | C | 535 | 0.022878 | 0.0016341
1 | 3328331 | 2014-12-15 00:11 | 2014-12-15 01:38 | 87.4833 | 535 | 34519.9167 | 0.10558 | 0.0016363 | Restore Supply on Device RP15 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser RP15 | at 00:10, Coromandel Sub, CB 1 Colville, Recloser RP15 Tripped, E/F, L/O. Auto Reclose was disabled on this feeder due to a previous fault on this feeder. Waited 15 minutes, tried manual reclose and feeder held in at 00:26. at 00:31, Recloser RP15 Trip | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 64.5232 | 61.5232 | 32914.9167 | 0.10054 | 0.0016341 | 2014-12-15 | C | 0.10054 | 0.0016341 | 2015 | 2014-12-15 | C | 535 | 0.10054 | 0.0016341
1 | 3358099 | 2014-12-15 05:36 | 2014-12-15 07:09 | 93 | 711 | 65121 | 0.19917 | 0.0021745 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | 9226 | Recloser 9226 tripped on E/F, O/C and L/O. Line patrolled and no fault found. Suspect wind blown debris (trees) | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 91.5907 | 88.5907 | 62988 | 0.19239 | 0.0021717 | 2014-12-15 | C | 0.19239 | 0.0021717 | 2015 | 2014-12-15 | C | 711 | 0.19239 | 0.0021717
1 | 3364148 | 2014-12-15 06:07 | 2014-12-15 15:41 | 574 | 1 | 574 | 0.0017555 | 3.0584e-06 | Restore Supply on Device 6910 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TX5369 | Planned work Napa 3281128. Job did not create a child at time of working. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 574 | 571 | 571 | 0.0017441 | 3.0544e-06 | 2014-12-15 | C | 0.0017441 | 3.054e-06 | 2015 | 2014-12-15 | C | 1 | 0.0017441 | 3.0544e-06
1 | 3347834 | 2014-12-15 07:18 | 2014-12-15 17:45 | 626.2 | 64 | 17200.45 | 0.052606 | 0.00019574 | Restore Supply on Device TC1359 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC1359 | *** check if part of lines down job oms 3347821 *** - 15/12 11.52 advised hub of lines down 2.50 retailer following up again elderly people starting to get distressed spoke to Talia and she is trying to find someone this job had already been attend | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 268.757 | 265.757 | 17008.45 | 0.051951 | 0.00019548 | 2014-12-15 | C | 0.051951 | 0.00019548 | 2015 | 2014-12-15 | C | 64 | 0.051951 | 0.00019548
1 | 3347851 | 2014-12-15 07:29 | 2014-12-15 17:09 | 580.3167 | 3 | 851.5667 | 0.0026045 | 9.1753e-06 | Restore Supply on Device TC6065 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | 7:31am called through to Joanne at the hub (tree resting on the lines) called customer, power is back on part of feeder fault, thames coast feeder fault. | F3/F4 | THAMES COAST | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 283.8556 | 280.8556 | 842.5667 | 0.0025736 | 9.1633e-06 | 2014-12-15 | C | 0.0025736 | 9.163e-06 | 2015 | 2014-12-15 | C | 3 | 0.0025736 | 9.1633e-06
1 | 3348006 | 2014-12-15 07:40 | 2014-12-15 10:09 | 149.15 | 3 | 444.75 | 0.0013602 | 9.1753e-06 | Restore Supply on Device TC5798 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | ST10 | patrolled line and closed links at ST10. nothing repaired or replaced, adjacent assets up to powerco standard. | F3/F4 | PURANGI | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 148.25 | 145.25 | 435.75 | 0.001331 | 9.1633e-06 | 2014-12-15 | C | 0.001331 | 9.163e-06 | 2015 | 2014-12-15 | C | 3 | 0.001331 | 9.1633e-06
1 | 3132571 | 2014-12-15 08:12 | 2014-12-15 15:32 | 440 | 1 | 440 | 0.0013457 | 3.0584e-06 | NAPA ID:04211 TP_MASTERTON GXP > CLAREVILLE SUB > SOMERSET RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | New Regulators 11050/2 | Construction work for installing new voltage regulators on the somerset fdr | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 440 | 437 | 437 | 0.0013348 | 3.0544e-06 | 2014-12-15 | B | 0.00066739 | 1.527e-06 | 2015 | 2014-12-15 | B | 1 | 0.0013348 | 3.0544e-06
1 | 3357385 | 2014-12-15 08:46 | 2014-12-15 14:01 | 314.9 | 27 | 3046.6333 | 0.0093179 | 8.2577e-05 | Restore Supply on Device TA718 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3015 | Line isolated at fuses TA718 to replace faulty transformer T3015. | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 112.8383 | 109.8383 | 2965.6333 | 0.0090583 | 8.2469e-05 | 2014-12-15 | C | 0.0090583 | 8.2469e-05 | 2015 | 2014-12-15 | C | 27 | 0.0090583 | 8.2469e-05
1 | 3141185 | 2014-12-15 08:50 | 2014-12-15 09:53 | 63 | 9 | 567 | 0.0017341 | 2.7526e-05 | NAPA ID:04907 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 425 | resag 11 kv lines at pole 795396 due to low clearence. Works location: Pukenaua Rd WO 10150853 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 540 | 0.0016494 | 2.749e-05 | 2014-12-15 | B | 0.00082469 | 1.3745e-05 | 2015 | 2014-12-15 | B | 9 | 0.0016494 | 2.749e-05
1 | 3351315 | 2014-12-15 08:54 | 2014-12-16 11:25 | 1590.6667 | 2 | 3161.9 | 0.0096704 | 6.1168e-06 | Restore Supply on Device TC5856 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4018 | cut trees affecting lines, replaced 2x 8a HV fuse links due trees. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1580.95 | 1577.95 | 3155.9 | 0.0096395 | 6.1088e-06 | 2014-12-15 | C | 0.0096395 | 6.109e-06 | 2015 | 2014-12-15 | C | 2 | 0.0096395 | 6.1088e-06
1 | 3175683 | 2014-12-15 08:55 | 2014-12-15 15:13 | 377.3167 | 133 | 50183.1167 | 0.15348 | 0.00040677 | NAPA ID:04824 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 722543 | Replace 11, 11kv poles between poles 722543 (ABS CA464) and 772473. Works location: Wallscourt Place, Egmont St Hawera WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 377.3167 | 374.3167 | 49784.1167 | 0.15206 | 0.00040624 | 2014-12-15 | B | 0.076031 | 0.00020312 | 2015 | 2014-12-15 | B | 133 | 0.15206 | 0.00040624
1 | 2403244 | 2014-12-15 09:00 | 2014-12-15 15:06 | 365.85 | 3 | 1097.55 | 0.0033568 | 9.1753e-06 | NAPA ID:03486 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP5165 | 33/11kV pole and crossarm replacement between poles #760682 & 760654. Works location: Otaraora Rd Waitara. WO 10151691. | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 365.85 | 362.85 | 1088.55 | 0.0033249 | 9.1633e-06 | 2014-12-15 | B | 0.0016624 | 4.582e-06 | 2015 | 2014-12-15 | B | 3 | 0.0033249 | 9.1633e-06
1 | 3148051 | 2014-12-15 09:26 | 2014-12-15 12:34 | 187.7667 | 9 | 1689.9 | 0.0051684 | 2.7526e-05 | NAPA ID:04516 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4327 | To replace the 11kV Transformer Fuses on TC4327 & Replace TC4327. Works location: Kakahu Rd Tirau WO IR5140 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 187.7667 | 184.7667 | 1662.9 | 0.0050792 | 2.749e-05 | 2014-12-15 | B | 0.0025396 | 1.3745e-05 | 2015 | 2014-12-15 | B | 9 | 0.0050792 | 2.749e-05
1 | 3175491 | 2014-12-15 09:38 | 2014-12-15 14:09 | 271.0333 | 9 | 2439.3 | 0.0074604 | 2.7526e-05 | NAPA ID:04519 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2498 | To replace the 11kV Transformer Fuses, Replace the transformer, replace the 400V Arm & Install 400V Fuses. Works location: Te Miro Rd WO IR5140 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 271.0333 | 268.0333 | 2412.3 | 0.0073682 | 2.749e-05 | 2014-12-15 | B | 0.0036841 | 1.3745e-05 | 2015 | 2014-12-15 | B | 9 | 0.0073682 | 2.749e-05
1 | 3351625 | 2014-12-15 10:10 | 2014-12-15 13:07 | 177.0667 | 1 | 177.0667 | 0.00054154 | 3.0584e-06 | Restore Supply on Device T8/63 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p12472 | replace ht 3 amp ddo fuse. pole p12472. cause: unknown. 1 out 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. . | F4 | MAURICEVILLE | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 177.0667 | 174.0667 | 174.0667 | 0.00053167 | 3.0544e-06 | 2014-12-15 | C | 0.00053167 | 3.054e-06 | 2015 | 2014-12-15 | C | 1 | 0.00053167 | 3.0544e-06
1 | 3351688 | 2014-12-15 10:22 | 2014-12-15 12:23 | 120.8167 | 1 | 120.8167 | 0.00036951 | 3.0584e-06 | Restore Supply on Device T2/926 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t2/926 | 11kv lines are low. FM advise customer to stop all work and also apply for a close approach permit for future work. FM sent e-mail to Greg Turner about the low lines which possibly may be private as there are no pole numbers. FM Greg Turner to look into i | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 120.8167 | 117.8167 | 117.8167 | 0.00035986 | 3.0544e-06 | 2014-12-15 | C | 0.00035986 | 3.054e-06 | 2015 | 2014-12-15 | C | 1 | 0.00035986 | 3.0544e-06
1 | 3351765 | 2014-12-15 11:07 | 2014-12-15 12:09 | 62.5333 | 1 | 62.5333 | 0.00019125 | 3.0584e-06 | Restore Supply on Device TC1209 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1209 | EMAP UPDATE - cannot do a map locate Replaced 2x 3amp DDO Fuse links due to weather. Nothing else repaired or replaced. Adjacent assets up to Powerco standard. Email sent to Jo to check for SAIDI. NB: No Paper Work Created - Closed by Dispatch. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 62.5333 | 59.5333 | 59.5333 | 0.00018184 | 3.0544e-06 | 2014-12-15 | C | 0.00018184 | 3.054e-06 | 2015 | 2014-12-15 | C | 1 | 0.00018184 | 3.0544e-06
1 | 3140773 | 2014-12-15 12:31 | 2014-12-15 13:42 | 70.8833 | 27 | 1913.85 | 0.0058534 | 8.2577e-05 | NAPA ID:04908 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 813 | resag 11 kv line due to lines lashing in high winds pole 795468. Works location: Ridge Rd Taihape WO 10149595 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 70.8833 | 67.8833 | 1832.85 | 0.0055983 | 8.2469e-05 | 2014-12-15 | B | 0.0027991 | 4.1235e-05 | 2015 | 2014-12-15 | B | 27 | 0.0055983 | 8.2469e-05
1 | 3360582 | 2014-12-15 13:00 | 2014-12-15 15:00 | 120 | 7 | 840 | 0.0025691 | 2.1409e-05 | Restore Supply on Device TC2305 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Tc2305 | Planned work replace tx | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 819 | 0.0025016 | 2.1381e-05 | 2014-12-15 | C | 0.0025016 | 2.1381e-05 | 2015 | 2014-12-15 | C | 7 | 0.0025016 | 2.1381e-05
1 | 3176020 | 2014-12-15 13:37 | 2014-12-15 15:18 | 100.9333 | 2 | 201.8667 | 0.00061739 | 6.1168e-06 | NAPA ID:04522 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4663 | Replace Transformer TC4663. Works location: Te Miro Rd Te Miro WO IR5140 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.9333 | 97.9333 | 195.8667 | 0.00059826 | 6.1088e-06 | 2014-12-15 | B | 0.00029913 | 3.054e-06 | 2015 | 2014-12-15 | B | 2 | 0.00059826 | 6.1088e-06
1 | 3357556 | 2014-12-15 13:42 | 2014-12-15 16:01 | 139.1333 | 1 | 139.1333 | 0.00042553 | 3.0584e-06 | Restore Supply on Device TE6-180 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 221575 | Replaced 2x 20a HV DDO fuse links due to unknown. Nothing else repaired or replaced. Adjacent assets up to Powerco standard. Email sent to Jo to check for SAIDI component. NB: No Paper Work Created - Closed by Dispatch. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 139.1333 | 136.1333 | 136.1333 | 0.00041581 | 3.0544e-06 | 2014-12-15 | C | 0.00041581 | 3.054e-06 | 2015 | 2014-12-15 | C | 1 | 0.00041581 | 3.0544e-06
1 | 3358950 | 2014-12-15 14:34 | 2014-12-15 17:11 | 156.7333 | 5 | 629.9333 | 0.0019266 | 1.5292e-05 | Restore Supply on Device FC:V1500/1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1552 | COR 5 Fuses FP1552 blown on arrival. Floating conductor found at pole V1504. Conductor rebound all service restored. S Walker attended. No Materials Used. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 125.9867 | 122.9867 | 614.9333 | 0.0018783 | 1.5272e-05 | 2014-12-15 | C | 0.0018783 | 1.5272e-05 | 2015 | 2014-12-15 | C | 5 | 0.0018783 | 1.5272e-05
1 | 3359434 | 2014-12-15 18:24 | 2014-12-15 21:20 | 176.1 | 2 | 203.6833 | 0.00062295 | 6.1168e-06 | Restore Supply on Device C6805 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 724975 | check 3359529 568 Morea Road if related 9.14pm called customer to see if their power has been restored, customer advised no ans on customers home phone replaced 2x 8amp hv ddo fuses 724975 cause unknown No other assets repaired or replaced and all ad | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 101.8417 | 98.8417 | 197.6833 | 0.00060381 | 6.1088e-06 | 2014-12-15 | C | 0.00060381 | 6.109e-06 | 2015 | 2014-12-15 | C | 2 | 0.00060381 | 6.1088e-06
1 | 3359579 | 2014-12-15 23:42 | 2014-12-16 01:36 | 114.15 | 99 | 7035.9833 | 0.021519 | 0.00030278 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9464 | Kerepehi CB2. REcloser 9464 TRipped L/O E/F. Feeder sectionalised beyond Recloser 9464 no fault found. Suspect Opossum. Grant Jordan attended. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 71.0705 | 68.0705 | 6738.9833 | 0.020584 | 0.00030239 | 2014-12-15 | C | 0.020584 | 0.00030239 | 2015 | 2014-12-15 | C | 99 | 0.020584 | 0.00030239
1 | 3359899 | 2014-12-16 03:34 | 2014-12-16 03:44 | 10 | 423 | 4230 | 0.012937 | 0.0012937 | Restore Supply on Device CB2742 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | O/C Trip, Sectionalised with no fault found. Padlocked replaced on ABS 528 | F1, F2, F3 | MOTUKAWA SOUTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 2961 | 0.0090441 | 0.001292 | 2014-12-16 | C | 0.0090441 | 0.001292 | 2015 | 2014-12-16 | C | 423 | 0.0090441 | 0.001292
1 | 3360326 | 2014-12-16 04:16 | 2014-12-16 08:02 | 225.9833 | 111 | 11966.3167 | 0.036598 | 0.00033948 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 798317 | Lines bought down by large swan. Backfeed from TUH C927 via Sectionaliser 11035. Lines repaired, relivened OK. Materials Used: 2 x Joints. Lee Wilton and Jason Hall attended. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 107.8047 | 104.8047 | 11633.3167 | 0.035533 | 0.00033904 | 2014-12-16 | C | 0.035533 | 0.00033904 | 2015 | 2014-12-16 | C | 111 | 0.035533 | 0.00033904
1 | 3374138 | 2014-12-16 04:18 | 2014-12-16 19:18 | 899.85 | 107 | 18134.8667 | 0.055464 | 0.00032725 | Restore Supply on Device E33 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P20976 | Recloser E33 tripped on B & C phase O/C. Line was sectionalised and a floating wire was found at Pole P20976. Line was isolated at ABS's E34, E35 & E41. 1 X Binder was used. Jeff Roberts and Peter Marshall attended. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 169.4847 | 166.4847 | 17813.8667 | 0.054411 | 0.00032682 | 2014-12-16 | C | 0.054411 | 0.00032682 | 2015 | 2014-12-16 | C | 107 | 0.054411 | 0.00032682
1 | 3360548 | 2014-12-16 06:01 | 2014-12-16 09:33 | 211.9667 | 1 | 211.9667 | 0.00064828 | 3.0584e-06 | Restore Supply on Device TC2589 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | t2589 | Replace 2 amp ht fuse at tx t2589. 1 out two phases. cause: wind. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 211.9667 | 208.9667 | 208.9667 | 0.00063827 | 3.0544e-06 | 2014-12-16 | C | 0.00063827 | 3.054e-06 | 2015 | 2014-12-16 | C | 1 | 0.00063827 | 3.0544e-06
1 | 3132713 | 2014-12-16 08:00 | 2014-12-16 12:55 | 295 | 130 | 38306 | 0.11716 | 0.00039759 | NAPA ID:04212 TP_MASTERTON GXP > CLAREVILLE SUB > SOMERSET RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 823856 | Install new 11kV Regulators 11050/2 and associated equipment. Close Temporary Line Break at Pole 823856. | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 294.6615 | 291.6615 | 37916 | 0.11581 | 0.00039708 | 2014-12-16 | B | 0.057906 | 0.00019854 | 2015 | 2014-12-16 | B | 130 | 0.11581 | 0.00039708
1 | 3184066 | 2014-12-16 08:15 | 2014-12-16 14:57 | 402.3 | 3 | 1206.9 | 0.0036912 | 9.1753e-06 | NAPA ID:05137 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8160 | UPGRADING CONDUCTOR POLE REPLACEMENT CROSSARMS. Works location: Te Rata Rd. WO 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 402.3 | 399.3 | 1197.9 | 0.0036589 | 9.1633e-06 | 2014-12-16 | B | 0.0018294 | 4.582e-06 | 2015 | 2014-12-16 | B | 3 | 0.0036589 | 9.1633e-06
1 | 3157177 | 2014-12-16 08:30 | 2014-12-16 12:00 | 210 | 3 | 630 | 0.0019268 | 9.1753e-06 | NAPA ID:04912 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2218 | Replace transformer X2218. Isolation required for 11kV line. Works location: State Hwy 1 Taihape. WO 10141784 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 210 | 207 | 621 | 0.0018968 | 9.1633e-06 | 2014-12-16 | B | 0.0009484 | 4.582e-06 | 2015 | 2014-12-16 | B | 3 | 0.0018968 | 9.1633e-06
1 | 3209276 | 2014-12-16 08:46 | 2014-12-16 16:03 | 436.7667 | 97 | 21438.0333 | 0.065567 | 0.00029667 | NAPA ID:04610 TP_TAURANGA 33 GXP > MATUA SUB > BELLEVUE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-532 | Due to land slide at the existing site work is to relocate TD4-532 to the other side of the road and joint a section of 11kV HV cables in. Connect a Gen set to supply TD4-578 while the shutdown is on. Work Order# 10152627. | F3 | BELLEVUE RD | MATUA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 221.0107 | 218.0107 | 21147.0333 | 0.064592 | 0.00029628 | 2014-12-16 | B | 0.032296 | 0.00014814 | 2015 | 2014-12-16 | B | 97 | 0.064592 | 0.00029628
1 | 3204269 | 2014-12-16 09:09 | 2014-12-16 14:07 | 298.1167 | 10 | 2974.2833 | 0.0090966 | 3.0584e-05 | NAPA ID:03212 TP_HINUERA GXP > TIRAU SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole D0532 | To install 11kv line brack at pole # D0352 and replace 11kv and LV cross arms as per attached plan Works Location: SH1 Tirtau WO 101-48278 | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 297.4283 | 294.4283 | 2944.2833 | 0.0089931 | 3.0544e-05 | 2014-12-16 | B | 0.0044965 | 1.5272e-05 | 2015 | 2014-12-16 | B | 10 | 0.0089931 | 3.0544e-05
1 | 3181893 | 2014-12-16 09:15 | 2014-12-16 13:24 | 249 | 7 | 1743 | 0.0053308 | 2.1409e-05 | NAPA ID:03935 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 208698 | REPLACE POLE 208698. Works location: Albert Lane. WO 10148295. | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 249 | 246 | 1722 | 0.0052597 | 2.1381e-05 | 2014-12-16 | B | 0.0026299 | 1.069e-05 | 2015 | 2014-12-16 | B | 7 | 0.0052597 | 2.1381e-05
1 | 3158142 | 2014-12-16 09:30 | 2014-12-16 15:02 | 331.5333 | 15 | 4973 | 0.01521 | 4.5876e-05 | NAPA ID:04160 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K59 | Replace 11kV 400v transformer cross arms. Works location: Lower Pakihikura Rd WO 10142182 | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 331.5333 | 328.5333 | 4928 | 0.015052 | 4.5816e-05 | 2014-12-16 | B | 0.0075261 | 2.2908e-05 | 2015 | 2014-12-16 | B | 15 | 0.015052 | 4.5816e-05
1 | 3372913 | 2014-12-16 10:46 | 2014-12-16 11:53 | 67.2333 | 1 | 67.2333 | 0.00020563 | 3.0584e-06 | Restore Supply on Device T4196 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 812513 | 10.48am advised shan at hub pole 812513 fires were out on arrival, magpie caused fault between 33kv conductor which went into pole, caused tripping on feeder which James was already investigating on line patrol - oms 3372292. nothing repaired or replaced | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 67.2333 | 64.2333 | 64.2333 | 0.0001962 | 3.0544e-06 | 2014-12-16 | C | 0.0001962 | 3.054e-06 | 2015 | 2014-12-16 | C | 1 | 0.0001962 | 3.0544e-06
1 | 3373167 | 2014-12-16 14:04 | 2014-12-16 16:00 | 115.6667 | 1 | 115.6667 | 0.00035376 | 3.0584e-06 | Restore Supply on Device T1568 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuses 7262 | Replaced 2x links through control - links where missing, not sure where they have gone, no debris by pole at fuses 7262 x 10amp fuses and replaced 2x links. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco stand | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 115.6667 | 112.6667 | 112.6667 | 0.00034413 | 3.0544e-06 | 2014-12-16 | C | 0.00034413 | 3.054e-06 | 2015 | 2014-12-16 | C | 1 | 0.00034413 | 3.0544e-06
1 | 3372311 | 2014-12-16 15:00 | 2014-12-16 15:11 | 10.8 | 215 | 2322 | 0.0071017 | 0.00065756 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 207858 | OMO 6 Plummers Point feeder. During planned switching Ted Glasgow noticed conductor x 1 at pole 207858 damaged & requiring immediate repair. CB6 isolated ( no back feeds ) conductor repaired all service restored. Materials 1 x H/V sleeve | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 10.8 | 7.8 | 1677 | 0.0051223 | 0.0006567 | 2014-12-16 | C | 0.0051223 | 0.0006567 | 2015 | 2014-12-16 | C | 215 | 0.0051223 | 0.0006567
1 | 3374572 | 2014-12-16 16:09 | 2014-12-16 19:47 | 217.9667 | 45 | 9808.5 | 0.029999 | 0.00013763 | Restore Supply on Device MA158 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | MA192 | plz check oms 3374021 as may be related 865 Auroa Road, Manaia, 3374026, 3374252, 3374427 4.25pm spoke to Maurice in control and he advised to suggest faultman to go to MA192 - advised Shannon at svs hub of this Chris advising needing 2nd response, need | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 217.9667 | 214.9667 | 9673.5 | 0.029547 | 0.00013745 | 2014-12-16 | C | 0.029547 | 0.00013745 | 2015 | 2014-12-16 | C | 45 | 0.029547 | 0.00013745
1 | 3374640 | 2014-12-16 20:02 | 2014-12-16 20:17 | 15.0667 | 86 | 1295.7333 | 0.0039629 | 0.00026302 | Restore Supply on Device C8 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T2/489 | Faultman found a broken service line, customers reported that a vehicle had hit it 15/12/14, line had flicked over 11kV line, line was isolated at ABS's C8 & D90 so faultman could remove the service line with hot line sticks. LV line hit by something and | F4 | KOPANE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 15.0667 | 12.0667 | 1037.7333 | 0.0031697 | 0.00026268 | 2014-12-16 | C | 0.0031697 | 0.00026268 | 2015 | 2014-12-16 | C | 86 | 0.0031697 | 0.00026268
1 | 3375004 | 2014-12-17 01:10 | 2014-12-17 12:59 | 709.1333 | 685 | 48318.4667 | 0.14778 | 0.002095 | Restore Supply on Device 335 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2376 | 11kV conductor came down pole V12644, repaired & relivened, feeder tripped again, then found king bolt on xarm had come out at pole V12696 with 11kV conductor down on LV neutral. this affected 20-30 ICP's, these will require elect inspection, Shane has o | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 70.5379 | 67.5379 | 46263.4667 | 0.14131 | 0.0020923 | 2014-12-17 | C | 0.14131 | 0.0020923 | 2015 | 2014-12-17 | C | 685 | 0.14131 | 0.0020923
1 | 3375658 | 2014-12-17 01:36 | 2014-12-17 05:15 | 218.6667 | 48 | 10496 | 0.032101 | 0.0001468 | Restore Supply on Device SE3-017 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 380617 | Lines Found Down At Pole 380617. Tree branch through lines. NDR # 44155. 10 mtrs Namu and 4 sleeves. Jayden attended. | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 218.6667 | 215.6667 | 10352 | 0.031619 | 0.00014661 | 2014-12-17 | C | 0.031619 | 0.00014661 | 2015 | 2014-12-17 | C | 48 | 0.031619 | 0.00014661
1 | 3376365 | 2014-12-17 04:56 | 2014-12-17 06:36 | 100.7 | 1 | 100.7 | 0.00030798 | 3.0584e-06 | Restore Supply on Device 2419T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2419 | Replace 2 x 8 amp HT 735586. Cause: Possibly a bird. Email sent to Jo to check for SAIDI. NB: No Paper Work Created - Closed by Dispatch. | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 100.7 | 97.7 | 97.7 | 0.00029842 | 3.0544e-06 | 2014-12-17 | C | 0.00029842 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00029842 | 3.0544e-06
1 | 3376619 | 2014-12-17 05:23 | 2014-12-17 12:13 | 409.9667 | 94 | 10713.0667 | 0.032765 | 0.00028749 | Restore Supply on Device RC25 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 324123 | 1 R To be decided at invoicing if going to 2R Recloser RC25 tripped to L/O - Lines down reported & located on Tower Rd - isolation points ABS ic963, IC1330, Links IP576 - lines repaired all supply restored - Marty Keenan initially attended - AP taken b | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 113.9688 | 110.9688 | 10431.0667 | 0.031861 | 0.00028712 | 2014-12-17 | C | 0.031861 | 0.00028712 | 2015 | 2014-12-17 | C | 94 | 0.031861 | 0.00028712
1 | 3376723 | 2014-12-17 05:43 | 2014-12-17 05:59 | 16.0833 | 436 | 7012.3333 | 0.021447 | 0.0013335 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | 3 | Trip. O/C. L/O. Closed back in after 15 min. | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 16.0833 | 13.0833 | 5704.3333 | 0.017423 | 0.0013317 | 2014-12-17 | C | 0.017423 | 0.0013317 | 2015 | 2014-12-17 | C | 436 | 0.017423 | 0.0013317
1 | 3377581 | 2014-12-17 06:00 | 2014-12-17 08:49 | 168.95 | 1 | 168.95 | 0.00051672 | 3.0584e-06 | Restore Supply on Device T2/690 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D88 | Replaced 2x 10amp fuse links due to possible bird strike. Nothing else repaired or replaced, Adjacent assets up to Powerco standard. Email sent to Jo to check for SAIDI. NB: No Paper Work Created - Closed by Dispatch. | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 168.95 | 165.95 | 165.95 | 0.00050688 | 3.0544e-06 | 2014-12-17 | C | 0.00050688 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00050688 | 3.0544e-06
1 | 3377584 | 2014-12-17 06:06 | 2014-12-17 06:27 | 21.0167 | 1281 | 26922.35 | 0.08234 | 0.0039178 | Restore Supply on Device 19 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | 19 | CB19 tripped O/C L/O. Line not patrolled. High winds in area. | F3 | BETHLEHEM | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 21.0167 | 18.0167 | 23079.35 | 0.070494 | 0.0039127 | 2014-12-17 | C | 0.070494 | 0.0039127 | 2015 | 2014-12-17 | C | 1281 | 0.070494 | 0.0039127
1 | 3378867 | 2014-12-17 06:13 | 2014-12-17 10:54 | 281.2333 | 120 | 28320.25 | 0.086615 | 0.00036701 | Restore Supply on Device SP15 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole E0996 | Retailer advise of Line down outsied 297 Pakaraka Road, Te Poi across the road - they are sending the job through and have advised control room Lines down reported & located between poles E0997 & E0998 - isolation at ABS 1145 - 6 metres squirrell condu | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 236.0021 | 233.0021 | 27960.25 | 0.085402 | 0.00036653 | 2014-12-17 | C | 0.085402 | 0.00036653 | 2015 | 2014-12-17 | C | 120 | 0.085402 | 0.00036653
1 | 3379579 | 2014-12-17 06:31 | 2014-12-17 09:50 | 199.2 | 436 | 53569.1333 | 0.16384 | 0.0013335 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | CB 3 | CB 3 tripped to L/O - O/C flag - initial backfeed establised by opening recloser RC18 & closing 9663/2 - line sectionalised & patrolled - no fault found - all supply restored in area - very high winds in area - backfeed left in for interim in case of furt | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 122.865 | 119.865 | 52261.1333 | 0.15963 | 0.0013317 | 2014-12-17 | C | 0.15963 | 0.0013317 | 2015 | 2014-12-17 | C | 436 | 0.15963 | 0.0013317
1 | 3380089 | 2014-12-17 06:51 | 2014-12-17 10:32 | 220.65 | 1 | 220.65 | 0.00067484 | 3.0584e-06 | Restore Supply on Device TC4688 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4688 | Mandhir with James for safety reasons. FM has requested another 1R crew request as he is taking Mandhir with for safety. Request has been declined. Advise FM that he has to tell SMC that he is taking Mandhir with and that they need to sort it out. ***Also | F4 | PURIRI | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 220.65 | 217.65 | 217.65 | 0.0006648 | 3.0544e-06 | 2014-12-17 | C | 0.0006648 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.0006648 | 3.0544e-06
1 | 3380101 | 2014-12-17 07:01 | 2014-12-17 11:40 | 278.9 | 5 | 1394.5 | 0.004265 | 1.5292e-05 | Restore Supply on Device V70 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P00783 | replace 6 amp ht fuse at v70. worked through control. it only held for 2 minutes and then it blew again. FM advise he needs to do a line patrol and needs someone to come to site with a quad bike. Fiona advise that if the line patrol takes longer than 1 ho | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 278.9 | 275.9 | 1379.5 | 0.0042136 | 1.5272e-05 | 2014-12-17 | C | 0.0042136 | 1.5272e-05 | 2015 | 2014-12-17 | C | 5 | 0.0042136 | 1.5272e-05
1 | 3380114 | 2014-12-17 07:12 | 2014-12-17 17:19 | 606.8333 | 348 | 61022.45 | 0.18663 | 0.0010643 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | H3106 | switching completed to make safe - isolated and made safe, someone else coming to do repairs CB 4 tripped to L/O - lines down & broken pole reported & identified on Waghorn Rd - tree through line at pole H3106 - fault isolated at ABS IC732 - 1 x 11m bu | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 175.3519 | 172.3519 | 59978.45 | 0.1832 | 0.0010629 | 2014-12-17 | C | 0.1832 | 0.0010629 | 2015 | 2014-12-17 | C | 348 | 0.1832 | 0.0010629
1 | 3380488 | 2014-12-17 07:28 | 2014-12-17 10:25 | 176.7 | 224 | 30862.3333 | 0.09439 | 0.00068509 | Restore Supply on Device 1428 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 785639 | CB7 tripped. tree branch on line at pole 785639 removed by hot stick Cb 7 Trip No flags. | F2 | WAIOURU LS | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 137.7783 | 134.7783 | 30190.3333 | 0.092214 | 0.00068419 | 2014-12-17 | C | 0.092214 | 0.00068419 | 2015 | 2014-12-17 | C | 224 | 0.092214 | 0.00068419
1 | 3204367 | 2014-12-17 09:15 | 2014-12-17 12:10 | 174.85 | 116 | 20282.6 | 0.062033 | 0.00035478 | NAPA ID:05021 TP_CARRINGTON GXP > KATERE SUB > KATERE 11 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 746930 | Replace pole 746930 with new pole and 100kva pole mounted transformer Works Location: Pohutukawa Place Bell Block WO10162664 | F2 | KATERE 11 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 174.85 | 171.85 | 19934.6 | 0.060889 | 0.00035431 | 2014-12-17 | B | 0.030444 | 0.00017716 | 2015 | 2014-12-17 | B | 116 | 0.060889 | 0.00035431
1 | 3239086 | 2014-12-17 09:31 | 2014-12-17 15:48 | 377.3167 | 224 | 84518.9333 | 0.25849 | 0.00068509 | NAPA ID:05492 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 544 | replace poles xarms and run new wire. Install new TEMP 09 fuses to reduce SAIDI on future outages. Works location: Wairau Rd and Messanger Tce. WO 10154759. NOTE: Delay in restoration, Water pipe beneath area of pole replacement / required some "redesig | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 377.3167 | 374.3167 | 83846.9333 | 0.2561 | 0.00068419 | 2014-12-17 | B | 0.12805 | 0.00034209 | 2015 | 2014-12-17 | B | 224 | 0.2561 | 0.00068419
1 | 3158203 | 2014-12-17 09:34 | 2014-12-17 12:26 | 172 | 90 | 15480 | 0.047344 | 0.00027526 | NAPA ID:04424 TP_GREYTOWN GXP > HAU NUI SUB > TUTURUMURI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 838928 | reconductor one span of 11kv between poles 838928 & 855621. Works location: Tora Rd WO 10121855 | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 172 | 169 | 15210 | 0.046458 | 0.0002749 | 2014-12-17 | B | 0.023229 | 0.00013745 | 2015 | 2014-12-17 | B | 90 | 0.046458 | 0.0002749
1 | 3385800 | 2014-12-17 09:41 | 2014-12-17 14:49 | 308.25 | 3 | 742.95 | 0.0022723 | 9.1753e-06 | Restore Supply on Device PU402 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 704125 | Initial auto-reclose on CB PU4. Isolation later required on Fuses PU402 to clear away a tree branch hitting the outside conductor. The Neutral Conductor was also broken (repaired) at Transformer 5385E. Relivened. Jade attended. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 247.65 | 244.65 | 733.95 | 0.0022418 | 9.1633e-06 | 2014-12-17 | C | 0.0022418 | 9.163e-06 | 2015 | 2014-12-17 | C | 3 | 0.0022418 | 9.1633e-06
1 | 3384734 | 2014-12-17 09:44 | 2014-12-17 10:35 | 50.4333 | 179 | 5955.6167 | 0.018215 | 0.00054746 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9663/2 | Sectionaliser 9663/2 tripped to L/O - had been getting used for temp backfeed up to recloser RC18 & ABS 720 - line sectionalised & patrolled - no fault found although trees suspected - all supply restored | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 33.2716 | 30.2716 | 5418.6167 | 0.016551 | 0.00054674 | 2014-12-17 | C | 0.016551 | 0.00054674 | 2015 | 2014-12-17 | C | 179 | 0.016551 | 0.00054674
1 | 3385506 | 2014-12-17 10:11 | 2014-12-17 14:30 | 258.9833 | 50 | 2683.1 | 0.0082061 | 0.00015292 | Restore Supply on Device T3705 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | Pole 845392 | *** check if 3385782 and 3385814 are part of this outage *** Removed branch from the lines at Pole 845392 with hot sticks. Reliven OK | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 53.662 | 50.662 | 2533.1 | 0.0077372 | 0.00015272 | 2014-12-17 | C | 0.0077372 | 0.00015272 | 2015 | 2014-12-17 | C | 50 | 0.0077372 | 0.00015272
1 | 3214134 | 2014-12-17 10:14 | 2014-12-17 15:17 | 303 | 1 | 303 | 0.0009267 | 3.0584e-06 | NAPA ID:05253 TP_MARTON GXP > PUKEPAPA SUB > TURAKINA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 802414 | Replace 11kv pole and Transformer X1656 | F4 | RENALL ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 303 | 300 | 300 | 0.00091633 | 3.0544e-06 | 2014-12-17 | B | 0.00045816 | 1.527e-06 | 2015 | 2014-12-17 | B | 1 | 0.00091633 | 3.0544e-06
1 | 3385521 | 2014-12-17 10:16 | 2014-12-17 12:33 | 137.2167 | 1 | 137.2167 | 0.00041967 | 3.0584e-06 | Restore Supply on Device T2424 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 812824 | joints and connectors at tx t2424 inspected. trees touching 11kv line at pole 812824. defect into spa. | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 137.2167 | 134.2167 | 134.2167 | 0.00040995 | 3.0544e-06 | 2014-12-17 | C | 0.00040995 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00040995 | 3.0544e-06
1 | 3385533 | 2014-12-17 10:24 | 2014-12-17 12:03 | 99.1333 | 1 | 99.1333 | 0.00030319 | 3.0584e-06 | Restore Supply on Device X1410 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 795845 | replace 2 amp ht fuse. 1 out 3 phases. cause: wind. pole # 795845. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 99.1333 | 96.1333 | 96.1333 | 0.00029363 | 3.0544e-06 | 2014-12-17 | C | 0.00029363 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00029363 | 3.0544e-06
1 | 3385536 | 2014-12-17 10:25 | 2014-12-17 11:16 | 51.3167 | 1 | 51.3167 | 0.00015695 | 3.0584e-06 | Restore Supply on Device TC1718 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 802 KAKAHU ROAD - Tirau | part of earlier feeder fault on OCB3 Lake Road - full power restored. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.3167 | 48.3167 | 48.3167 | 0.00014758 | 3.0544e-06 | 2014-12-17 | C | 0.00014758 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00014758 | 3.0544e-06
1 | 3374430 | 2014-12-17 10:35 | 2014-12-17 11:31 | 56 | 53 | 2968 | 0.0090774 | 0.0001621 | Restore Supply on Device 4357T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole NUmber 761311 | Unplanned short notice shut to replace a rotten 6.6kV Crossarm at Pole 761311, Isolation via Fuses 5525. Neil Woodhead to Attend. Shut down to run from 17/12/ 10:30am to 12:30pm. ICP's to be advertised by NOC Please note there may be additional equipme | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 56 | 53 | 2809 | 0.0085799 | 0.00016188 | 2014-12-17 | C | 0.0085799 | 0.00016188 | 2015 | 2014-12-17 | C | 53 | 0.0085799 | 0.00016188
1 | 3172713 | 2014-12-17 11:23 | 2014-12-17 15:33 | 250 | 3 | 750 | 0.0022938 | 9.1753e-06 | NAPA ID:05018 TP_MANGAMAIRE GXP > ALFREDTON SUB > ALFREDTON LS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS I2 | To Change ABS I2 and Pole. Works location; Route 52 Alfredton Sub WO 10144449 | F5 | CASTLEHILL | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 741 | 0.0022633 | 9.1633e-06 | 2014-12-17 | B | 0.0011317 | 4.582e-06 | 2015 | 2014-12-17 | B | 3 | 0.0022633 | 9.1633e-06
1 | 3385859 | 2014-12-17 11:41 | 2014-12-17 18:09 | 387.8667 | 250 | 17573.1667 | 0.053746 | 0.00076461 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | W13399 | Feeder fault. Recloser 9170 Trip E/F. Back feed from Whitianga CB 4 Sectionalizer 9721/2, recloser RC20 opened/ Sectionalizer 9721/2 Closed. Line sectionalized & patrolled from recloser 9170/2. Fault found to be lines down at pole W13399 past ABS 323. n | F3/F4 | TAIRUA NORTH | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 70.2927 | 67.2927 | 16823.1667 | 0.051385 | 0.00076361 | 2014-12-17 | C | 0.051385 | 0.00076361 | 2015 | 2014-12-17 | C | 250 | 0.051385 | 0.00076361
1 | 3386123 | 2014-12-17 11:47 | 2014-12-18 05:31 | 1064.3667 | 1 | 1064.3667 | 0.0032553 | 3.0584e-06 | Restore Supply on Device TC4248 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | fc2297 | possibly related to OMS#3383180 fm advised not related request made 18/12 9.40am - smc advise: the rejection of the crew request was made in error. Perry Hicks actually did attend and smc will ask him to sign the job off this morning as they will only st | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1064.3667 | 1061.3667 | 1061.3667 | 0.0032419 | 3.0544e-06 | 2014-12-17 | C | 0.0032419 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.0032419 | 3.0544e-06
1 | 3386229 | 2014-12-17 12:20 | 2014-12-17 19:26 | 425.7667 | 27 | 11495.7 | 0.035159 | 8.2577e-05 | Restore Supply on Device 5193 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5193 | 5.36pm emailed svs hub for update replaced 2x 15amp hv road links at fuses 5193 No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 425.7667 | 422.7667 | 11414.7 | 0.034865 | 8.2469e-05 | 2014-12-17 | C | 0.034865 | 8.2469e-05 | 2015 | 2014-12-17 | C | 27 | 0.034865 | 8.2469e-05
1 | 3386286 | 2014-12-17 12:44 | 2014-12-17 13:21 | 36.55 | 44 | 1608.2 | 0.0049186 | 0.00013457 | Restore Supply on Device SD3-012 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 386759 | Remove Bamboo from the overhead lines at pole 386759. No Bucket truck available. NDR 44808. Andy Wreaks attended. | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 36.55 | 33.55 | 1476.2 | 0.0045089 | 0.00013439 | 2014-12-17 | C | 0.0045089 | 0.00013439 | 2015 | 2014-12-17 | C | 44 | 0.0045089 | 0.00013439
1 | 3241154 | 2014-12-17 13:08 | 2014-12-17 14:59 | 110.9667 | 7 | 776.7667 | 0.0023757 | 2.1409e-05 | NAPA ID:05469 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4457T | Replace Blown Lightning Arrestors at Tx 4457T. Work Location: 377 Makuri Road, Huiroa, Stratford. Work Order:10153039 | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 110.9667 | 107.9667 | 755.7667 | 0.0023084 | 2.1381e-05 | 2014-12-17 | B | 0.0011542 | 1.069e-05 | 2015 | 2014-12-17 | B | 7 | 0.0023084 | 2.1381e-05
1 | 3442334 | 2014-12-17 13:13 | 2014-12-17 17:55 | 282 | 179 | 23120 | 0.070711 | 0.00054746 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | as per | Recreation of fault on TWR3 Recloser 9663/2 | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 129.162 | 126.162 | 22583 | 0.068978 | 0.00054674 | 2014-12-17 | C | 0.068978 | 0.00054674 | 2015 | 2014-12-17 | C | 179 | 0.068978 | 0.00054674
1 | 3392172 | 2014-12-17 13:44 | 2014-12-18 07:17 | 1052.5667 | 839 | 69902.65 | 0.21379 | 0.002566 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | pole 791424 | CB 4 tripped on A phase O/C & E/F flags and Recloser 1087 also tripped on A & b phase O/C, at time of tripping CB 4 was backfeeding Wanganui East Sub CB 10 via ANS 702, line was sectionalised and patrolled, line down was found at pole 791424, line was iso | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 83.3166 | 80.3166 | 67385.65 | 0.20582 | 0.0025627 | 2014-12-17 | C | 0.20582 | 0.0025627 | 2015 | 2014-12-17 | C | 839 | 0.20582 | 0.0025627
1 | 3386907 | 2014-12-17 14:27 | 2014-12-17 22:50 | 502.8333 | 519 | 35853.9333 | 0.10966 | 0.0015873 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole E0228 | LAK CB3 tripped L/O. Tree through line between poles E0228 & E12661. Isolation between CB3, ABS 890 & ABS 2657 with back feed via Secionaliser 9663. Lines & hardware replaced/repaired all service ( 2 customers remain off due to poor readings, inspector ) | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 69.0827 | 66.0827 | 34296.9333 | 0.10476 | 0.0015852 | 2014-12-17 | C | 0.10476 | 0.0015852 | 2015 | 2014-12-17 | C | 519 | 0.10476 | 0.0015852
1 | 3388574 | 2014-12-17 14:54 | 2014-12-17 15:55 | 61.4333 | 1 | 61.4333 | 0.00018789 | 3.0584e-06 | Restore Supply on Device 7059 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3654 | Outage required for LV repairs on Transformer T3654. Replaced LV connection from LV bushing to fuse, Fuse and holder | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 61.4333 | 58.4333 | 58.4333 | 0.00017848 | 3.0544e-06 | 2014-12-17 | C | 0.00017848 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00017848 | 3.0544e-06
1 | 3388582 | 2014-12-17 14:57 | 2014-12-17 17:05 | 128.15 | 3 | 201.0167 | 0.00061479 | 9.1753e-06 | Restore Supply on Device 665 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X665 | Transformer 665 found with 2 HT Fuses blown. Reloaded, relivened OK. Lightning in area. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 67.0056 | 64.0056 | 192.0167 | 0.0005865 | 9.1633e-06 | 2014-12-17 | C | 0.0005865 | 9.163e-06 | 2015 | 2014-12-17 | C | 3 | 0.0005865 | 9.1633e-06
1 | 3388962 | 2014-12-17 15:49 | 2014-12-17 17:16 | 86.8333 | 185 | 16064.1667 | 0.049131 | 0.00056581 | Restore Supply on Device RP02 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | RP02 | Recloser RP02 tripped to L/O - line patrolled & branch found over line at pole D1898 - branch remove all supply restored - Denis Ngatai attended | F4 | OKOROIRE | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 86.8333 | 83.8333 | 15509.1667 | 0.047372 | 0.00056507 | 2014-12-17 | C | 0.047372 | 0.00056507 | 2015 | 2014-12-17 | C | 185 | 0.047372 | 0.00056507
1 | 3390765 | 2014-12-17 16:21 | 2014-12-17 22:52 | 390.8167 | 2 | 720.0167 | 0.0022021 | 6.1168e-06 | Restore Supply on Device 3761T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3761T 736335 | plz check if oms 3390922 2761 Rawhitiroa Road, Eltham related. 9.06pm retailer calling for eta. called Margaret at the svs hub for eta, she was unable to give eta. 2x 3amp hv fuse tx. No other assets repaired or replaced and all adjacent assets checked | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 360.0083 | 357.0083 | 714.0167 | 0.0021809 | 6.1088e-06 | 2014-12-17 | C | 0.0021809 | 6.109e-06 | 2015 | 2014-12-17 | C | 2 | 0.0021809 | 6.1088e-06
1 | 3390785 | 2014-12-17 16:27 | 2014-12-17 20:56 | 269.2167 | 1 | 269.2167 | 0.00082338 | 3.0584e-06 | Restore Supply on Device P1255 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4680 | deassigned to put blair gregg onsite 2x 3amp hv fuses & candle stick No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard - Blair advised that the whole road is not up to standard, I asked him if he was g | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 269.2167 | 266.2167 | 266.2167 | 0.00081314 | 3.0544e-06 | 2014-12-17 | C | 0.00081314 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00081314 | 3.0544e-06
1 | 3390812 | 2014-12-17 16:45 | 2014-12-17 21:32 | 286.45 | 1 | 286.45 | 0.00087608 | 3.0584e-06 | Restore Supply on Device 2715T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2715T | possibly related to oms 3388729 8.22pm Paul advised that this is not related to the above oms number 2X HV 2AMP TX 2715T DUE TO LIGHTENING SURROUNDING ASETT GOOD NOTHING ELSE. Email sent to JO. NB: No Paper Work Created - Closed by Dispatch. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 286.45 | 283.45 | 283.45 | 0.00086578 | 3.0544e-06 | 2014-12-17 | C | 0.00086578 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00086578 | 3.0544e-06
1 | 3390916 | 2014-12-17 17:21 | 2014-12-18 03:16 | 595.15 | 1 | 595.15 | 0.0018202 | 3.0584e-06 | Restore Supply on Device 3577T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3577T | 10.19pm emailed svs hub for update, Faultman found blown fuse on transformer. 2 X 2 Amp HV rewirable. | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 595.15 | 592.15 | 592.15 | 0.0018087 | 3.0544e-06 | 2014-12-17 | C | 0.0018087 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.0018087 | 3.0544e-06
1 | 3390974 | 2014-12-17 18:06 | 2014-12-18 00:58 | 411.8 | 1 | 411.8 | 0.0012595 | 3.0584e-06 | Restore Supply on Device 2449T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2449T | Faultman found blown fuse on transformer 2449T. 3x 2Amp HV rewirable fuses replaced, suspect lightning. | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 411.8 | 408.8 | 408.8 | 0.0012486 | 3.0544e-06 | 2014-12-17 | C | 0.0012486 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.0012486 | 3.0544e-06
1 | 3391078 | 2014-12-17 19:25 | 2014-12-17 22:11 | 165.9667 | 1 | 165.9667 | 0.0005076 | 3.0584e-06 | Restore Supply on Device TP1146 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1146 | Replaced 2x HV 6amp OH HV at tx TP1146 due to weather surrounding asset all good nothing else. Email sent to Jo to check for SAIDI component. NB: No Paper Work Created - Closed by Dispatch. | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 165.9667 | 162.9667 | 162.9667 | 0.00049777 | 3.0544e-06 | 2014-12-17 | C | 0.00049777 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.00049777 | 3.0544e-06
1 | 3175475 | 2014-12-17 20:30 | 2014-12-17 22:25 | 114.9 | 5 | 574.5 | 0.0017571 | 1.5292e-05 | NAPA ID:04603 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 12 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer G30T | Replace oil on 11 Kv Tx G30 T (high Moisture & Acitdy Content in the oil). Works location: Park Rd Palmerston North WO 10157370 | F2 | PASCAL ST LS | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 114.9 | 111.9 | 559.5 | 0.001709 | 1.5272e-05 | 2014-12-17 | B | 0.00085448 | 7.636e-06 | 2015 | 2014-12-17 | B | 5 | 0.001709 | 1.5272e-05
1 | 3391470 | 2014-12-17 21:23 | 2014-12-18 06:36 | 552.8167 | 1 | 552.8167 | 0.0016907 | 3.0584e-06 | Restore Supply on Device X2582 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 796072 | replace main line fuse with 5 amp ht fuse. cause: wind. pole 796072. 1 out 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 552.8167 | 549.8167 | 549.8167 | 0.0016794 | 3.0544e-06 | 2014-12-17 | C | 0.0016794 | 3.054e-06 | 2015 | 2014-12-17 | C | 1 | 0.0016794 | 3.0544e-06
1 | 3391761 | 2014-12-18 01:33 | 2014-12-18 05:09 | 216.4667 | 123 | 17943.8667 | 0.05488 | 0.00037619 | Restore Supply on Device RC18 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | F1879 | TWR 3 Recloser RC18 tripped B Ph O/C, L/O. Feeder sectionalised, floating conductor & faulty insulators found at pole F1879. Isolations between ABS's 715, IC2611 & 789 ( no back feeds ). Section of TWR 3 being back feed between ABS IC796 & 715 via 9756 ( | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 145.8851 | 142.8851 | 17574.8667 | 0.053681 | 0.00037569 | 2014-12-18 | C | 0.053681 | 0.00037569 | 2015 | 2014-12-18 | C | 123 | 0.053681 | 0.00037569
1 | 3394980 | 2014-12-18 07:52 | 2014-12-18 15:41 | 468.8333 | 7 | 932.35 | 0.0028515 | 2.1409e-05 | Restore Supply on Device TC2732 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2732 | 10:33am - Retailer called as Customers going to work and requires if f/man requires access to property called for ETA from Shannon. advised Retailer 30mins made safe, transformer T2732 HV fuses open and tagged. load has hit lines and taken them down, | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 133.1929 | 130.1929 | 911.35 | 0.0027836 | 2.1381e-05 | 2014-12-18 | C | 0.0027836 | 2.1381e-05 | 2015 | 2014-12-18 | C | 7 | 0.0027836 | 2.1381e-05
1 | 3230946 | 2014-12-18 09:00 | 2014-12-18 13:45 | 284.9333 | 24 | 6838.4 | 0.020915 | 7.3402e-05 | NAPA ID:05431 TP_HUIRANGI GXP | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Fuses 5402 | 33/6.6kV pole and crossarm replacement between poles #760622& 760659. | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 284.9333 | 281.9333 | 6766.4 | 0.020667 | 7.3306e-05 | 2014-12-18 | B | 0.010334 | 3.6653e-05 | 2015 | 2014-12-18 | B | 24 | 0.020667 | 7.3306e-05
1 | 3395892 | 2014-12-18 09:05 | 2014-12-18 10:45 | 100 | 3 | 300 | 0.00091753 | 9.1753e-06 | Restore Supply on Device TC297 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer TC297 |  | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100 | 97 | 291 | 0.00088884 | 9.1633e-06 | 2014-12-18 | C | 0.00088884 | 9.163e-06 | 2015 | 2014-12-18 | C | 3 | 0.00088884 | 9.1633e-06
1 | 3395076 | 2014-12-18 09:09 | 2014-12-18 10:56 | 106.6 | 1 | 106.6 | 0.00032603 | 3.0584e-06 | Restore Supply on Device T973 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 7510 | Two Fuses at fuses 7510 found blown due to branch on lines - removed using hot sticks - hedge being trimmed below lines - NDR # 21906. Email sent to Jo. NB: No Paper Work Created - Closed by Dispatch. | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106.6 | 103.6 | 103.6 | 0.00031644 | 3.0544e-06 | 2014-12-18 | C | 0.00031644 | 3.054e-06 | 2015 | 2014-12-18 | C | 1 | 0.00031644 | 3.0544e-06
1 | 3395088 | 2014-12-18 09:17 | 2014-12-18 10:21 | 63.7667 | 527 | 22067.3833 | 0.067491 | 0.0016118 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 219983 | Feeder trip OC. back feed from Welcome bay CB 3 via Recloser 9462. Recloser RP09 NOC Open Recloser 9462 Closed Locally due to SCADA issues. Line Patrolled report from Public about a flash, site check pukeko's found in area. CB closed power restored. back | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 41.8736 | 38.8736 | 20486.3833 | 0.062574 | 0.0016097 | 2014-12-18 | C | 0.062574 | 0.0016097 | 2015 | 2014-12-18 | C | 527 | 0.062574 | 0.0016097
1 | 3230933 | 2014-12-18 09:51 | 2014-12-18 12:40 | 169.0167 | 16 | 2704.2667 | 0.0082708 | 4.8935e-05 | NAPA ID:05178 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 752746 | replace existing network pole 752746 with new pole cross arm pins and insulators. Works location: Pheney Rd New Plymouth WO NA | F3 | MOTUROA 9 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 169.0167 | 166.0167 | 2656.2667 | 0.0081134 | 4.8871e-05 | 2014-12-18 | B | 0.0040567 | 2.4435e-05 | 2015 | 2014-12-18 | B | 16 | 0.0081134 | 4.8871e-05
1 | 3191293 | 2014-12-18 09:55 | 2014-12-18 14:45 | 290 | 12 | 3480 | 0.010643 | 3.6701e-05 | NAPA ID:05038 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/549 | Using live line to change hv top arm then hv fuse arm.then cancel live line permit and issue AP to change rest of hardware from the bottom of the hv fuses. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 290 | 287 | 3444 | 0.010519 | 3.6653e-05 | 2014-12-18 | B | 0.0052597 | 1.8327e-05 | 2015 | 2014-12-18 | B | 12 | 0.010519 | 3.6653e-05
1 | 3395970 | 2014-12-18 12:51 | 2014-12-18 14:23 | 91.8333 | 3 | 236.9667 | 0.00072474 | 9.1753e-06 | Restore Supply on Device 2280T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 736257, 2280T | replace 2 x 3amp HT fuses at pole 736257 and transformer 2280T. Cause: Lightning last night. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. Email sent to Jo NB: No Paper Work Created - Closed by | F5 | RAWHITIROA | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 78.9889 | 75.9889 | 227.9667 | 0.00069631 | 9.1633e-06 | 2014-12-18 | C | 0.00069631 | 9.163e-06 | 2015 | 2014-12-18 | C | 3 | 0.00069631 | 9.1633e-06
1 | 3397334 | 2014-12-18 14:51 | 2014-12-18 15:58 | 67.3833 | 650 | 27458.1667 | 0.083979 | 0.001988 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 9467/1 | Cable Fault Between Sw/Gear 9467/1 & Sw/Gear IC1890 2 R has been done to Find Fault Paul Cooper Knows about This | F3 | RAWHITI AVE | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 42.2433 | 39.2433 | 25508.1667 | 0.077913 | 0.0019854 | 2014-12-18 | C | 0.077913 | 0.0019854 | 2015 | 2014-12-18 | C | 650 | 0.077913 | 0.0019854
1 | 3398810 | 2014-12-18 16:08 | 2014-12-18 17:07 | 58.4333 | 1 | 58.4333 | 0.00017871 | 3.0584e-06 | Restore Supply on Device TC1680 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4049 | 2 X 3 AMP DDO FUSES . REASON UNKNOWN WORKED THROUGH CONTROL TO RELIVEN NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. Email sent to Jo. NB: No Paper Work Created - Closed by Dispatch. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 58.4333 | 55.4333 | 55.4333 | 0.00016932 | 3.0544e-06 | 2014-12-18 | C | 0.00016932 | 3.054e-06 | 2015 | 2014-12-18 | C | 1 | 0.00016932 | 3.0544e-06
1 | 3401925 | 2014-12-18 17:39 | 2014-12-18 21:48 | 249.2333 | 51 | 8062.8333 | 0.02466 | 0.00015598 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11939 | KIM 7 Recloser 4443/2 tripped E/F, L/O Feeder sectionalised & floating conductor found at pole 11939 between ABS K40 & ABS K41 with back feed via ABS N12. Conductor re bound all service restored, Jeff Roberts & Nev Morris attended. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 158.0948 | 155.0948 | 7909.8333 | 0.02416 | 0.00015578 | 2014-12-18 | C | 0.02416 | 0.00015578 | 2015 | 2014-12-18 | C | 51 | 0.02416 | 0.00015578
1 | 3403519 | 2014-12-18 18:08 | 2014-12-18 18:19 | 11.3333 | 49 | 539 | 0.0016485 | 0.00014986 | Restore Supply on Device IC2611 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | F13100 | Repairs to jumper burning up at Transformer TC318. Isolation at ABS 715 & IC2611 no back feeds available. No material used. Hilton Gardiner attended. | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 11 | 8 | 392 | 0.0011973 | 0.00014967 | 2014-12-18 | C | 0.0011973 | 0.00014967 | 2015 | 2014-12-18 | C | 49 | 0.0011973 | 0.00014967
1 | 3403715 | 2014-12-18 19:15 | 2014-12-18 21:11 | 116.4333 | 99 | 2993.7 | 0.009156 | 0.00030278 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 013413 | Tripping on Recloser CB 9464 on EF 1. Feeder sectionalised / patrolled with a broken conductor found down. (Isolation from Fuses IC1226). Cause unknown but suspeect clash during storm yesterday (Conductor burnt). Rejointed, 3 sleeves required & 2 metres c | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 30.2394 | 27.2394 | 2696.7 | 0.0082369 | 0.00030239 | 2014-12-18 | C | 0.0082369 | 0.00030239 | 2015 | 2014-12-18 | C | 99 | 0.0082369 | 0.00030239
1 | 3404131 | 2014-12-19 06:06 | 2014-12-19 10:57 | 291.2833 | 23 | 6557.25 | 0.020055 | 7.0344e-05 | Restore Supply on Device 825 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847766 | HV line Down Roger working through control - Isolated at Fuses 825 - Line repaired at pole 847766 - used 4 sleeves & 10 mtrs of Conductor | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 285.0978 | 282.0978 | 6488.25 | 0.019818 | 7.0252e-05 | 2014-12-19 | C | 0.019818 | 7.0252e-05 | 2015 | 2014-12-19 | C | 23 | 0.019818 | 7.0252e-05
1 | 3410024 | 2014-12-19 08:00 | 2014-12-19 10:33 | 153.1667 | 2 | 205.9167 | 0.00062978 | 6.1168e-06 | Restore Supply on Device T2/419 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | p01332 | replaced 1 x 3amp ht fuse. pole p01332. cause: line clash. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. FM advise: 518 Te Matai Road was also affected by this outage as it is fed off the same tx | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 102.9583 | 99.9583 | 199.9167 | 0.00061063 | 6.1088e-06 | 2014-12-19 | C | 0.00061063 | 6.109e-06 | 2015 | 2014-12-19 | C | 2 | 0.00061063 | 6.1088e-06
1 | 3220124 | 2014-12-19 09:00 | 2014-12-19 11:39 | 158.4667 | 33 | 5229.4 | 0.015994 | 0.00010093 | NAPA ID:05347 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > TE AROHA BOROUGH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4037 | Replace leaking transformer TC4037. Works location: Whitaker St Te Aroha WO 10161148 | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 158.4667 | 155.4667 | 5130.4 | 0.01567 | 0.0001008 | 2014-12-19 | B | 0.0078352 | 5.0398e-05 | 2015 | 2014-12-19 | B | 33 | 0.01567 | 0.0001008
1 | 3410285 | 2014-12-19 09:10 | 2014-12-19 10:17 | 67 | 5 | 335 | 0.0010246 | 1.5292e-05 | Restore Supply on Device TC2944 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer TC2944 | Replaced Transformer TC2944 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 67 | 64 | 320 | 0.00097742 | 1.5272e-05 | 2014-12-19 | C | 0.00097742 | 1.5272e-05 | 2015 | 2014-12-19 | C | 5 | 0.00097742 | 1.5272e-05
1 | 3204606 | 2014-12-19 10:02 | 2014-12-19 14:28 | 266.45 | 81 | 21582.45 | 0.066008 | 0.00024773 | NAPA ID:05197 TP_BUNNYTHORPE GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS D75 | Changing 33kv and 11kv xarm Works Location: Raymond St Bunnythorpe WO10147202 | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 266.45 | 263.45 | 21339.45 | 0.06518 | 0.00024741 | 2014-12-19 | B | 0.03259 | 0.0001237 | 2015 | 2014-12-19 | B | 81 | 0.06518 | 0.00024741
1 | 3410567 | 2014-12-19 16:23 | 2014-12-19 18:33 | 130.5333 | 1 | 130.5333 | 0.00039923 | 3.0584e-06 | Restore Supply on Device TC2690 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2690 | replaced 2x 2amp ddo fuses at tx - full set replaced only 2 phase. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 130.5333 | 127.5333 | 127.5333 | 0.00038954 | 3.0544e-06 | 2014-12-19 | C | 0.00038954 | 3.054e-06 | 2015 | 2014-12-19 | C | 1 | 0.00038954 | 3.0544e-06
1 | 3410660 | 2014-12-19 19:25 | 2014-12-20 01:40 | 374.2667 | 50 | 5457.5667 | 0.016692 | 0.00015292 | Restore Supply on Device 3295T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Transformer 3295T | 11kV Fuse Holders faulty & need replacing. 11/400V transformer 3295T also needs to be replaced. Shut down to replace DDO's first OMS 3410706 then second AP to replace transformer 3295T OMS 3410660 1100/400V Transfomer, 3 x 11kV HV Fuse assemblies | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.1513 | 106.1513 | 5307.5667 | 0.016212 | 0.00015272 | 2014-12-19 | C | 0.016212 | 0.00015272 | 2015 | 2014-12-19 | C | 50 | 0.016212 | 0.00015272
1 | 3215031 | 2014-12-20 05:04 | 2014-12-20 06:11 | 66.95 | 98 | 6561.1 | 0.020067 | 0.00029973 | NAPA ID:05064 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/547 | repair 11 kv cable crutch and clear partial electrical discharge@ tx T3/547. Works location: Monmouth St Feilding WO 10155775 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 66.95 | 63.95 | 6267.1 | 0.019142 | 0.00029933 | 2014-12-20 | B | 0.0095712 | 0.00014967 | 2015 | 2014-12-20 | B | 98 | 0.019142 | 0.00029933
1 | 3411999 | 2014-12-20 11:26 | 2014-12-20 13:18 | 112.7833 | 10 | 1127.8333 | 0.0034494 | 3.0584e-05 | Restore Supply on Device M9 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | M9 | Fuses M9 Opened to Isolate to cut trees near lines. See OMS 3410579 | F2 | SANSON LS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 112.7833 | 109.7833 | 1097.8333 | 0.0033532 | 3.0544e-05 | 2014-12-20 | C | 0.0033532 | 3.0544e-05 | 2015 | 2014-12-20 | C | 10 | 0.0033532 | 3.0544e-05
1 | 3412132 | 2014-12-20 15:18 | 2014-12-20 19:51 | 273.3167 | 175 | 6865.5667 | 0.020998 | 0.00053522 | Restore Supply on Device T459 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8094 | Repaired jumper. No other assets repaired or replaced on site. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 39.2318 | 36.2318 | 6340.5667 | 0.019367 | 0.00053452 | 2014-12-20 | C | 0.019367 | 0.00053452 | 2015 | 2014-12-20 | C | 175 | 0.019367 | 0.00053452
1 | 3412493 | 2014-12-20 19:53 | 2014-12-20 21:36 | 102.6167 | 1 | 102.6167 | 0.00031385 | 3.0584e-06 | Restore Supply on Device T1658 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | CB C947 found open - CB closed after line partly patrolled - no Fault found | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 102.6167 | 99.6167 | 99.6167 | 0.00030427 | 3.0544e-06 | 2014-12-20 | C | 0.00030427 | 3.054e-06 | 2015 | 2014-12-20 | C | 1 | 0.00030427 | 3.0544e-06
1 | 3413766 | 2014-12-20 23:06 | 2014-12-20 23:29 | 22.35 | 120 | 2682 | 0.0082027 | 0.00036701 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 9539/2 | Recloser 9539/2 Trip. Unknown fault line not patrolled | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 22.35 | 19.35 | 2322 | 0.0070924 | 0.00036653 | 2014-12-20 | C | 0.0070924 | 0.00036653 | 2015 | 2014-12-20 | C | 120 | 0.0070924 | 0.00036653
1 | 3414401 | 2014-12-21 05:04 | 2014-12-21 06:50 | 106.3 | 24 | 106.3 | 0.00032511 | 7.3402e-05 | Restore Supply on Device X2173 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2173 | 2 Fuses found bown at Fuses 144 - line patrolled with no fault found 2x 15Amp Links | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 4.4292 | 1.4292 | 34.3 | 0.00010477 | 7.3306e-05 | 2014-12-21 | C | 0.00010477 | 7.3306e-05 | 2015 | 2014-12-21 | C | 24 | 0.00010477 | 7.3306e-05
1 | 3414564 | 2014-12-21 09:50 | 2014-12-21 10:52 | 62 | 3 | 113.55 | 0.00034728 | 9.1753e-06 | Restore Supply on Device T7/457 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7-456. p16214 | replaced 16a hv fuse link due to deterioration. nothing else repaired or replaced, adjacent assets up to powerco standard. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 37.85 | 34.85 | 104.55 | 0.00031934 | 9.1633e-06 | 2014-12-21 | C | 0.00031934 | 9.163e-06 | 2015 | 2014-12-21 | C | 3 | 0.00031934 | 9.1633e-06
1 | 3215034 | 2014-12-21 10:06 | 2014-12-21 11:06 | 60.0833 | 71 | 4265.9167 | 0.013047 | 0.00021715 | NAPA ID:05074 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/453 | Repair HV cable T3/453 (Failed Partial Discharge Test). Works location: North St Feilding. WO 10155775 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 60.0833 | 57.0833 | 4052.9167 | 0.012379 | 0.00021686 | 2014-12-21 | B | 0.0061897 | 0.00010843 | 2015 | 2014-12-21 | B | 71 | 0.012379 | 0.00021686
1 | 3214103 | 2014-12-21 12:38 | 2014-12-21 13:29 | 51.3 | 32 | 1641.6 | 0.0050207 | 9.787e-05 | NAPA ID:05245 TP_HUIRANGI GXP > WAITARA EAST SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Waitara East Sub | Removing 33kV bypass line outside Waitara East sub. This is shut 2 of 2 on the day. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 51.3 | 48.3 | 1545.6 | 0.0047209 | 9.7742e-05 | 2014-12-21 | B | 0.0023605 | 4.8871e-05 | 2015 | 2014-12-21 | B | 32 | 0.0047209 | 9.7742e-05
1 | 3414846 | 2014-12-21 20:17 | 2014-12-21 21:03 | 46 | 2857 | 128489 | 0.39297 | 0.0087379 | Restore Supply on Device X60 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | X60 | 33Kv CB X60 at Fielding tripped taking out Sanson Sub - Line patrolled with no fault found feeder restore then load restored to sub in sections. | F1, F2, F3 | FEILDING-SANSON 33KV | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 44.9734 | 41.9734 | 119918 | 0.36628 | 0.0087265 | 2014-12-21 | C | 0.36628 | 0.0087265 | 2015 | 2014-12-21 | C | 2857 | 0.36628 | 0.0087265
1 | 3417885 | 2014-12-22 05:25 | 2014-12-22 08:18 | 172.75 | 1 | 2501.6 | 0.0076509 | 3.0584e-06 | Restore Supply on Device 5208E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 846202 | repaired HV line down due to Deterioration - at pole 846202 used 064 sleeve and 3 meters of copper band to repair, 1phase only No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2501.6 | 2498.6 | 2498.6 | 0.0076318 | 3.0544e-06 | 2014-12-22 | C | 0.0076318 | 3.054e-06 | 2015 | 2014-12-22 | C | 1 | 0.0076318 | 3.0544e-06
1 | 3417896 | 2014-12-22 06:12 | 2014-12-22 06:28 | 15.8667 | 2 | 31.7333 | 9.7054e-05 | 6.1168e-06 | Restore Supply on Device 6942 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6942 | Recloser 6942 Tripped A,C Ph E/F - Contacted Cheal to see if they had any issues - Recloser closed. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 15.8667 | 12.8667 | 25.7333 | 7.8601e-05 | 6.1088e-06 | 2014-12-22 | C | 7.8601e-05 | 6.109e-06 | 2015 | 2014-12-22 | C | 2 | 7.8601e-05 | 6.1088e-06
1 | 3417900 | 2014-12-22 06:25 | 2014-12-22 08:45 | 140.4167 | 32 | 4493.3333 | 0.013743 | 9.787e-05 | Restore Supply on Device 1346 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X1654 | 8:32am Gary advised working through control blown TX 1654 have back fed at 0845 so all customers have power. Faultman advised that the transformer X1654 will be replaced in January 2015 (have no 200KVA transformer available). This transformer has been DN | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140.4167 | 137.4167 | 4397.3333 | 0.013431 | 9.7742e-05 | 2014-12-22 | C | 0.013431 | 9.7742e-05 | 2015 | 2014-12-22 | C | 32 | 0.013431 | 9.7742e-05
1 | 3417908 | 2014-12-22 06:53 | 2014-12-22 10:06 | 193.2333 | 10 | 822.65 | 0.002516 | 3.0584e-05 | Restore Supply on Device 949 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 949 | replaced x2 15amp fuse links at fuse link - did a line patrol and possible cause was bird strike. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 82.265 | 79.265 | 792.65 | 0.0024211 | 3.0544e-05 | 2014-12-22 | C | 0.0024211 | 3.0544e-05 | 2015 | 2014-12-22 | C | 10 | 0.0024211 | 3.0544e-05
1 | 3441563 | 2014-12-22 09:30 | 2014-12-22 14:53 | 323 | 47 | 15181 | 0.04643 | 0.00014375 | Restore Supply on Device 7366 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7366 | planned outage 5778 | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 323 | 320 | 15040 | 0.045939 | 0.00014356 | 2014-12-22 | C | 0.045939 | 0.00014356 | 2015 | 2014-12-22 | C | 47 | 0.045939 | 0.00014356
1 | 3422523 | 2014-12-22 12:13 | 2014-12-22 13:52 | 98.5833 | 292 | 17782.2 | 0.054385 | 0.00089306 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/gear 8573/1 & 6563/4 | CB 8 tripped to L/O - E/F & O/C flags - circuit sectionalised with a faulty HV cable identified between Sw/gear 8573/1 & 6563/4 - some delays in sectionalising due to heavy traffic volumes in inner City - Tony Julien & Nick Patton initially attended - iso | F2 | CITY 8 | CITY SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60.8979 | 57.8979 | 16906.2 | 0.051639 | 0.00089189 | 2014-12-22 | C | 0.051639 | 0.00089189 | 2015 | 2014-12-22 | C | 292 | 0.051639 | 0.00089189
1 | 3422983 | 2014-12-22 13:00 | 2014-12-23 10:40 | 1299.7828 | 1 | 1299.7833 | 0.0039753 | 3.0584e-06 | Restore Supply on Device TC3009 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | F12773 | FM could not find dairy shed number. FM can't get hold of customer to verify address or dairy shed number. FM therefore can't see the tx, don't want to re-liven as a line may have come down. signed FM off and put through crew request for a FM to attend fi | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1299.7833 | 1296.7833 | 1296.7833 | 0.0039609 | 3.0544e-06 | 2014-12-22 | C | 0.0039609 | 3.054e-06 | 2015 | 2014-12-22 | C | 1 | 0.0039609 | 3.0544e-06
1 | 3425393 | 2014-12-22 18:12 | 2014-12-22 22:04 | 232.5833 | 1758 | 119245.3333 | 0.3647 | 0.0053767 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/457 & T6/488 | 59 gemini avenue, palmerston north. Powerbox made a big bang, smoking. Tripped CB4 E/F. Tripped CB 5 when backfeeding due to U/G cable fault. Tenix oms system not working. 6.26pm - shazil onsite. 2R request. Underground 11kV cable has blown up as well as | F3 | GEMINI | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 67.8301 | 64.8301 | 113971.3333 | 0.34812 | 0.0053697 | 2014-12-22 | C | 0.34812 | 0.0053697 | 2015 | 2014-12-22 | C | 1758 | 0.34812 | 0.0053697
1 | 3437408 | 2014-12-22 19:07 | 2014-12-22 19:54 | 46.95 | 26 | 1216.5333 | 0.0037207 | 7.9519e-05 | Restore Supply on Device 4992 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE |  | Jumper off fuse. 3 amp fuses. 1 out 3 phases. pole # 738387. bird - next 738388. oil company. Isolated at Fuses 4992 and 8861 to make repairs. Materials: 3A fuse link, conductor joint and 1 metre of 16mm Cu conductor. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 46.7897 | 43.7897 | 1138.5333 | 0.0034776 | 7.9415e-05 | 2014-12-22 | C | 0.0034776 | 7.9415e-05 | 2015 | 2014-12-22 | C | 26 | 0.0034776 | 7.9415e-05
1 | 3437913 | 2014-12-22 19:25 | 2014-12-22 21:19 | 114 | 2983 | 246362.6 | 0.75348 | 0.0091233 | Restore Supply on Device 2092 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2092 | Wanganui GXP CB 2092 Trip, O/C, E/F causing loss of supply to Wanganui East Sub. Wanganui East Sub backfed and then CB 2092 feeder patrolled with no fault found. Suspect Bird Strike. Garry Fisher and Karl Rodgers attended. | F1, F2, F3 | WANGANUI EAST 33KV | TP_WANGANUI | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 82.5889 | 79.5889 | 237413.6 | 0.72516 | 0.0091113 | 2014-12-22 | C | 0.72516 | 0.0091113 | 2015 | 2014-12-22 | C | 2983 | 0.72516 | 0.0091113
1 | 3441045 | 2014-12-23 05:22 | 2014-12-23 06:38 | 76 | 2 | 152 | 0.00046488 | 6.1168e-06 | Restore Supply on Device W40 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | W40 | CB W40, CB Z200 & CB Z226 tripped on O/C & E/F flags, line was patrolled and no fault was found, suspect bird strike. Anjay & Shazil attended. | F2 | FAIRS RD | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 76 | 73 | 146 | 0.00044595 | 6.1088e-06 | 2014-12-23 | C | 0.00044595 | 6.109e-06 | 2015 | 2014-12-23 | C | 2 | 0.00044595 | 6.1088e-06
1 | 3441555 | 2014-12-23 13:35 | 2014-12-23 14:05 | 30 | 132 | 3960 | 0.012111 | 0.00040371 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | Transformer T6/488 | Test and locate cable fault between transformers T6/455 & T6/488 after feeder fault. Dave Thomson to attend. Cable fault has been repaired. | F3 | GEMINI | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 30 | 27 | 3564 | 0.010886 | 0.00040318 | 2014-12-23 | B | 0.005443 | 0.00020159 | 2015 | 2014-12-23 | B | 132 | 0.010886 | 0.00040318
1 | 3445211 | 2014-12-23 14:52 | 2014-12-23 16:24 | 92.1333 | 1 | 92.1333 | 0.00028178 | 3.0584e-06 | Restore Supply on Device 2363T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738556 | replaced 2x 10amp hv fuses, replaced fuse link as was burnt - cause possible bird strike - customer advised Nick of low line, Nick has amber defected this line, customer advised this line has been like this for 20 years. No other assets repaired or repla | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 92.1333 | 89.1333 | 89.1333 | 0.00027225 | 3.0544e-06 | 2014-12-23 | C | 0.00027225 | 3.054e-06 | 2015 | 2014-12-23 | C | 1 | 0.00027225 | 3.0544e-06
1 | 3445358 | 2014-12-23 19:07 | 2014-12-23 20:42 | 95.1667 | 3 | 285.5 | 0.00087318 | 9.1753e-06 | Restore Supply on Device FC2735 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2735 | 2 X 6A HV DDOs. Possible Bird Strike | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 95.1667 | 92.1667 | 276.5 | 0.00084455 | 9.1633e-06 | 2014-12-23 | C | 0.00084455 | 9.163e-06 | 2015 | 2014-12-23 | C | 3 | 0.00084455 | 9.1633e-06
1 | 3449898 | 2014-12-24 12:38 | 2014-12-24 14:20 | 101.1167 | 1 | 101.1167 | 0.00030926 | 3.0584e-06 | Restore Supply on Device X1424 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x87 773844 | 3x 2amp tx at tx x87 fuses cause bird strike. Verified HV job created to replace fuses oms 3449921 - James advised that he had to drive around to find this fault retailer has given wrong address and customer advised pole fuses hanging not low line. No ot | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 101.1167 | 98.1167 | 98.1167 | 0.00029969 | 3.0544e-06 | 2014-12-24 | C | 0.00029969 | 3.054e-06 | 2015 | 2014-12-24 | C | 1 | 0.00029969 | 3.0544e-06
1 | 3450819 | 2014-12-25 04:17 | 2014-12-25 05:38 | 81.2667 | 22 | 1787.8667 | 0.0054681 | 6.7285e-05 | Restore Supply on Device X755 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | pole 388897 | Faultman found a line down at pole 388897 while attending a fault call, line was isolated at Fuses 825 to replace a span of conductor, conductor was all burnt. 65 meters of 16mm copper used. 2 x sleeves. 1 x 20 Amp rewirable fuse replaced. This Job wi | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 81.2667 | 78.2667 | 1721.8667 | 0.0052593 | 6.7197e-05 | 2014-12-25 | C | 0.0052593 | 6.7197e-05 | 2015 | 2014-12-25 | C | 22 | 0.0052593 | 6.7197e-05
1 | 3450894 | 2014-12-25 12:26 | 2014-12-25 16:50 | 264.75 | 2 | 529.5 | 0.0016194 | 6.1168e-06 | Restore Supply on Device TC2367 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4266 | replaced 3x 30kVA 1100/400V transformer due to old age. Had blown to 2x3Amp HCV Fuses | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 264.75 | 261.75 | 523.5 | 0.001599 | 6.1088e-06 | 2014-12-25 | C | 0.001599 | 6.109e-06 | 2015 | 2014-12-25 | C | 2 | 0.001599 | 6.1088e-06
1 | 3452842 | 2014-12-26 11:23 | 2014-12-26 16:55 | 332.3667 | 463 | 47387.4833 | 0.14493 | 0.001416 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 755735 | CB 6 Tripped E/F - Car V Pole reported to Dispatch - Isolated at ABS 69 - Pole and Conplete Cross arm replaced and lines Repaired - Used 1 x Pole, 2x Complete HV Cross arms, 1 x donut Block, 1 X upper block NDR # 38195 | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 102.3488 | 99.3488 | 45998.4833 | 0.1405 | 0.0014142 | 2014-12-26 | C | 0.1405 | 0.0014142 | 2015 | 2014-12-26 | C | 463 | 0.1405 | 0.0014142
1 | 3454504 | 2014-12-26 15:56 | 2014-12-26 21:23 | 326.5833 | 399 | 31992.1 | 0.097845 | 0.0012203 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 357735 | HOUSE 45 TINUI VALLEY ROAD - tree on lines .Recloser C224/2 tripped B & C Ph O/C, L/O. Tree on line between pole structures 837821 - 837824. tree resting on lines no damage to network equipment. isolation at ABS C224/1 & Links C224/6 ( no back feeds ) T | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 80.1807 | 77.1807 | 30795.1 | 0.094061 | 0.0012187 | 2014-12-26 | C | 0.094061 | 0.0012187 | 2015 | 2014-12-26 | C | 399 | 0.094061 | 0.0012187
1 | 3454880 | 2014-12-26 18:21 | 2014-12-26 19:32 | 71.0667 | 331 | 19574.6667 | 0.059868 | 0.0010123 | Restore Supply on Device R51 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | R51 | ELT CB R51ipped O/C, L/O. Feeder sectionalised but no fault found. All service restored, no materials | F1/F4 | MANGATOKI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 59.138 | 56.138 | 18581.6667 | 0.056756 | 0.001011 | 2014-12-26 | C | 0.056756 | 0.001011 | 2015 | 2014-12-26 | C | 331 | 0.056756 | 0.001011
1 | 3455522 | 2014-12-27 06:46 | 2014-12-27 10:27 | 221.1667 | 2 | 441.5833 | 0.0013505 | 6.1168e-06 | Restore Supply on Device X2018 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x2018 | 2x 8am DDO worked through control due to unknown surrounding asset good hv oh tx x2018. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 220.7917 | 217.7917 | 435.5833 | 0.0013305 | 6.1088e-06 | 2014-12-27 | C | 0.0013305 | 6.109e-06 | 2015 | 2014-12-27 | C | 2 | 0.0013305 | 6.1088e-06
1 | 3455642 | 2014-12-27 12:12 | 2014-12-27 15:48 | 215.65 | 5 | 863.6167 | 0.0026413 | 1.5292e-05 | Restore Supply on Device T3/156 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | C19364 | ADVISED CONTROL AND HUB. Line down, on berm next to road, caused by tree. check for safety,TREES ON LINE NOW CUT AWAY REPLACED 5 METER OF CONDUCTOR 8 SLEEVES AND 2 X 6AMP FUSES AND 1X 100 AMP HRC FUSES AT POLE C 19364 NDR N300014. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 172.7233 | 169.7233 | 848.6167 | 0.002592 | 1.5272e-05 | 2014-12-27 | C | 0.002592 | 1.5272e-05 | 2015 | 2014-12-27 | C | 5 | 0.002592 | 1.5272e-05
1 | 3455791 | 2014-12-27 22:09 | 2014-12-28 02:53 | 284.5833 | 318 | 35302.9167 | 0.10797 | 0.00097258 | Restore Supply on Device C830 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 826997 | CB C830 Trip. B C E/F Line Patrolled & sectionalized. Fault found to be tree accross line past ABS S164 at pole 826997. branches cut clear line repaired. No Back feeds used NDR 37918. Material 4 Fargo Sleeves 10m conductor | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 111.0155 | 108.0155 | 34348.9167 | 0.10492 | 0.00097131 | 2014-12-27 | C | 0.10492 | 0.00097131 | 2015 | 2014-12-27 | C | 318 | 0.10492 | 0.00097131
1 | 3214653 | 2014-12-28 05:30 | 2014-12-28 06:59 | 88.8167 | 24 | 2131.6 | 0.0065193 | 7.3402e-05 | NAPA ID:04964 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS J40 | Repair HV cable ( Failed Partial Discharge Test). Works location: Nancy Ave Feilding WO 10155775 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 88.8167 | 85.8167 | 2059.6 | 0.0062909 | 7.3306e-05 | 2014-12-28 | B | 0.0031454 | 3.6653e-05 | 2015 | 2014-12-28 | B | 24 | 0.0062909 | 7.3306e-05
1 | 3458365 | 2014-12-28 07:05 | 2014-12-28 09:11 | 125.45 | 1 | 125.45 | 0.00038368 | 3.0584e-06 | Restore Supply on Device T2419 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 817075 | 817075 LINKS 7377 2 AMP FUSES DUE TO LINE CLASH SURROUNDING ASSET GOOD NOTHIING ELSE REPAIRED OR REPLACED | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 125.45 | 122.45 | 122.45 | 0.00037401 | 3.0544e-06 | 2014-12-28 | C | 0.00037401 | 3.054e-06 | 2015 | 2014-12-28 | C | 1 | 0.00037401 | 3.0544e-06
1 | 3458424 | 2014-12-28 10:40 | 2014-12-28 12:10 | 90 | 2984 | 120955.9667 | 0.36993 | 0.0091263 | Restore Supply on Device 2092 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 366923 | CB 2092 Trip E/F, O/C. Caused total outage of Wanganui East Sub. Sub backfed via 11kV. pole 366923 33kv hv Patrolled with cause of trip being magpie hit line. nothng repaired or replaced. Faultman found blown lightning arrestor which will be defected. Not | F1, F2, F3 | WANGANUI EAST 33KV | TP_WANGANUI | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 40.5348 | 37.5348 | 112003.9667 | 0.34211 | 0.0091144 | 2014-12-28 | C | 0.34211 | 0.0091144 | 2015 | 2014-12-28 | C | 2984 | 0.34211 | 0.0091144
1 | 3461418 | 2014-12-28 11:08 | 2014-12-28 14:55 | 227.2167 | 7 | 1590.5167 | 0.0048645 | 2.1409e-05 | Restore Supply on Device TC193 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC193 | 11.11AM 2R REQUESTED TO REPLACE TC 193 REQUESTED AT 10.45 AS THOUGHT HAD TO TAP TX DOWN MY NOTES DID NOT SAVE AT 10.45 AT 10.45 ANDY ALSO ADVISED HE REPLACED A 60 AMP FUSE WHICH RESTORED POWER BUY THEN HAD HIGH VOLTAGE SO REQUESTED 2 R TO TAP THE TX DOWN | F4 | TOWNSHIP & LS | FARMER ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 227.2167 | 224.2167 | 1569.5167 | 0.004794 | 2.1381e-05 | 2014-12-28 | C | 0.004794 | 2.1381e-05 | 2015 | 2014-12-28 | C | 7 | 0.004794 | 2.1381e-05
1 | 3214630 | 2014-12-29 05:00 | 2014-12-29 06:21 | 80.4167 | 15 | 1206.25 | 0.0036892 | 4.5876e-05 | NAPA ID:04967 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/550 | Repair HV cable ( Failed Partial Discharge Test). Works location: Nancy Ave Feilding WO 10155775 | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 80.4167 | 77.4167 | 1161.25 | 0.0035469 | 4.5816e-05 | 2014-12-29 | B | 0.0017735 | 2.2908e-05 | 2015 | 2014-12-29 | B | 15 | 0.0035469 | 4.5816e-05
1 | 3461918 | 2014-12-29 05:43 | 2014-12-29 06:47 | 64 | 839 | 12953 | 0.039616 | 0.002566 | Restore Supply on Device 9278 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9278 | Recloser 9512 tripped. Feeder sectionalised. No fault found. | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15.4386 | 12.4386 | 10436 | 0.031876 | 0.0025627 | 2014-12-29 | C | 0.031876 | 0.0025627 | 2015 | 2014-12-29 | C | 839 | 0.031876 | 0.0025627
1 | 3462769 | 2014-12-29 06:39 | 2014-12-29 08:33 | 113.7667 | 215 | 14317.4833 | 0.043789 | 0.00065756 | Restore Supply on Device R11 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 738497 | CB R11 Trip, O/C, Sectionalised & Patrolled. Dead bird found at base of Pole 738497, as this was confirmed to be the cause by a farmer onsite | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 66.5929 | 63.5929 | 13672.4833 | 0.041762 | 0.0006567 | 2014-12-29 | C | 0.041762 | 0.0006567 | 2015 | 2014-12-29 | C | 215 | 0.041762 | 0.0006567
1 | 3464341 | 2014-12-29 18:08 | 2014-12-29 22:05 | 236.7667 | 1 | 236.7667 | 0.00072413 | 3.0584e-06 | Restore Supply on Device X1592 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 858 | Two HV fuse found Blown at Fuses 858 - Replaced 2x 8amp fuses & 1x carrier - suspect lightning. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 236.7667 | 233.7667 | 233.7667 | 0.00071402 | 3.0544e-06 | 2014-12-29 | C | 0.00071402 | 3.054e-06 | 2015 | 2014-12-29 | C | 1 | 0.00071402 | 3.0544e-06
1 | 3464306 | 2014-12-29 18:11 | 2014-12-29 19:38 | 87.2167 | 10 | 849.7333 | 0.0025988 | 3.0584e-05 | Restore Supply on Device 3598T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 708945 | 2 DDO AND FUSE 2 AMP 2 OF 2 DUE TO LIGHTNING WORKED THROUGH CONTROL NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 84.9733 | 81.9733 | 819.7333 | 0.0025038 | 3.0544e-05 | 2014-12-29 | C | 0.0025038 | 3.0544e-05 | 2015 | 2014-12-29 | C | 10 | 0.0025038 | 3.0544e-05
1 | 3464349 | 2014-12-29 18:14 | 2014-12-29 19:39 | 85.3667 | 1 | 85.3667 | 0.00026109 | 3.0584e-06 | Restore Supply on Device 2357T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 738551 | is this linked to 3464202. 2 X 3 AMP FUSES DUE TO LIGHTNING. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK. | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 85.3667 | 82.3667 | 82.3667 | 0.00025158 | 3.0544e-06 | 2014-12-29 | C | 0.00025158 | 3.054e-06 | 2015 | 2014-12-29 | C | 1 | 0.00025158 | 3.0544e-06
1 | 3464403 | 2014-12-29 18:58 | 2014-12-30 07:12 | 733.9833 | 87 | 43759.55 | 0.13384 | 0.00026608 | Restore Supply on Device FC5060 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC5700 | Replaced transformer TC5700 200kVa. Isolated at transformer TC4978. OMS 3464506 IS LINKED | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 502.9833 | 499.9833 | 43498.55 | 0.13286 | 0.00026573 | 2014-12-29 | C | 0.13286 | 0.00026574 | 2015 | 2014-12-29 | C | 87 | 0.13286 | 0.00026573
1 | 3464516 | 2014-12-29 19:20 | 2014-12-29 20:27 | 66.9333 | 1 | 66.9333 | 0.00020471 | 3.0584e-06 | Restore Supply on Device X1324 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1324 | 3 X 3 AMP HV FUSES DUE TO LIGHTNING ,WORKED THROUGH CONTROL NO OTHER ASSETS REPAIRED OR REPLACED ADJACENT ASSETS OK. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 66.9333 | 63.9333 | 63.9333 | 0.00019528 | 3.0544e-06 | 2014-12-29 | C | 0.00019528 | 3.054e-06 | 2015 | 2014-12-29 | C | 1 | 0.00019528 | 3.0544e-06
1 | 3464522 | 2014-12-29 19:30 | 2014-12-29 21:45 | 135.1333 | 1 | 135.1333 | 0.00041329 | 3.0584e-06 | Restore Supply on Device X592 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 783828 | 2 X 2amp HV fuses found blown at Pole 783828 - Suspected Lightning. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 135.1333 | 132.1333 | 132.1333 | 0.00040359 | 3.0544e-06 | 2014-12-29 | C | 0.00040359 | 3.054e-06 | 2015 | 2014-12-29 | C | 1 | 0.00040359 | 3.0544e-06
1 | 3464647 | 2014-12-29 20:58 | 2014-12-30 00:42 | 223.5667 | 32 | 6309.9 | 0.019298 | 9.787e-05 | Restore Supply on Device 1500 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1500 | Replaced 2 X 15 amp HV fuses at Fuses 1500 - lightning strike | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 197.1844 | 194.1844 | 6213.9 | 0.01898 | 9.7742e-05 | 2014-12-29 | C | 0.01898 | 9.7742e-05 | 2015 | 2014-12-29 | C | 32 | 0.01898 | 9.7742e-05
1 | 3464657 | 2014-12-29 21:14 | 2014-12-29 23:25 | 130.8333 | 1 | 130.8333 | 0.00040014 | 3.0584e-06 | Restore Supply on Device 4483W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4483 | 2 X HV fuse found blown at Transformer X4483 - Suspected lightning | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 130.8333 | 127.8333 | 127.8333 | 0.00039046 | 3.0544e-06 | 2014-12-29 | C | 0.00039046 | 3.054e-06 | 2015 | 2014-12-29 | C | 1 | 0.00039046 | 3.0544e-06
1 | 3465018 | 2014-12-30 06:56 | 2014-12-30 10:43 | 226.7667 | 3 | 508.4667 | 0.0015551 | 9.1753e-06 | Restore Supply on Device X783 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx x783 | Check if affects OMS 3465464. 2x 3amp ddo fuses. tx x783. hv o/h. Cause lightning Full power restored. Nothing else repaired or replaced . Adjacent assets - ok | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 169.4889 | 166.4889 | 499.4667 | 0.0015256 | 9.1633e-06 | 2014-12-30 | C | 0.0015256 | 9.163e-06 | 2015 | 2014-12-30 | C | 3 | 0.0015256 | 9.1633e-06
1 | 3465122 | 2014-12-30 07:43 | 2014-12-30 09:15 | 91.8333 | 1 | 91.8333 | 0.00028087 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 13193 | goose hit line at pole 267388. 2x 6amp ddo fuses at pole 13193. hv o/h. Full power restored. nothing else repaired or replaced adjacent assets | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 91.8333 | 88.8333 | 88.8333 | 0.00027133 | 3.0544e-06 | 2014-12-30 | C | 0.00027133 | 3.054e-06 | 2015 | 2014-12-30 | C | 1 | 0.00027133 | 3.0544e-06
1 | 3465995 | 2014-12-30 10:12 | 2014-12-30 15:09 | 296.6 | 1 | 296.6 | 0.00090713 | 3.0584e-06 | Restore Supply on Device TF5-107 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF5-107 | 08/01 Emailed svs hub : Hilton Gardiner completed from site. f/man to call dispatch so we can close job off. 12/01 Emailed svs hub : Please get Hilton to call dispatch to close this job off. 13/01 Svs hub advised : We have no record of this oms can you p | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 296.6 | 293.6 | 293.6 | 0.00089678 | 3.0544e-06 | 2014-12-30 | C | 0.00089678 | 3.054e-06 | 2015 | 2014-12-30 | C | 1 | 0.00089678 | 3.0544e-06
1 | 3465577 | 2014-12-30 10:22 | 2014-12-30 14:50 | 268 | 2 | 536 | 0.0016393 | 6.1168e-06 | Restore Supply on Device T4530 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223878 | Transformer T4530 faulty on Pole 223878. Replaced 2 phase 15kVa transformer. Own A/P issued. Ted Glasgow attended. | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 268 | 265 | 530 | 0.0016188 | 6.1088e-06 | 2014-12-30 | C | 0.0016188 | 6.109e-06 | 2015 | 2014-12-30 | C | 2 | 0.0016188 | 6.1088e-06
1 | 3465572 | 2014-12-30 12:18 | 2014-12-30 15:15 | 177.0333 | 1 | 177.0333 | 0.00054144 | 3.0584e-06 | Restore Supply on Device X2711 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tx X2711 POLE # 791351 | BLOWN HV FUSE DROPPER ON POLE # 791351, AT RAPID NUMBER 454 WHANGAEHU VALLEY ROAD. SHEEP STATION CALLED MOUNT VIEW. FRED FROM TRANSFIELD PHONED TO ADVISE 027 223 7450. 3x 2amp ddo 11kv fuse links due to lightning. Tx X2711 HV O/H. Full power restored. Not | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 177.0333 | 174.0333 | 174.0333 | 0.00053157 | 3.0544e-06 | 2014-12-30 | C | 0.00053157 | 3.054e-06 | 2015 | 2014-12-30 | C | 1 | 0.00053157 | 3.0544e-06
1 | 3465601 | 2014-12-30 13:00 | 2014-12-30 15:10 | 130.2333 | 1 | 130.2333 | 0.00039831 | 3.0584e-06 | Restore Supply on Device T1480 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 826046 | 2x 10amp ddo fuses. Cause unknown. Pole 826046. hv o/h. Full power restored. Nothing else repaired or replaced. adjacent assets - ok | F4 | CHESTER RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 130.2333 | 127.2333 | 127.2333 | 0.00038862 | 3.0544e-06 | 2014-12-30 | C | 0.00038862 | 3.054e-06 | 2015 | 2014-12-30 | C | 1 | 0.00038862 | 3.0544e-06
1 | 3466019 | 2014-12-30 16:23 | 2014-12-30 18:05 | 102.4667 | 294 | 13015.1 | 0.039806 | 0.00089918 | Restore Supply on Device 1011 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 1011 | Recloser 1011 tripped on A phase O/C & E/F flags, line was patrolled and sectionalised and fault was found with Recloser 1011, Recloser 1011 has been bypassed and DNO'ed DNO Tag 141221. Roger Bland and Jeremy Hill attended. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 44.269 | 41.269 | 12133.1 | 0.03706 | 0.000898 | 2014-12-30 | C | 0.03706 | 0.000898 | 2015 | 2014-12-30 | C | 294 | 0.03706 | 0.000898
1 | 3467085 | 2014-12-30 21:54 | 2014-12-31 00:06 | 131.6167 | 1 | 131.6167 | 0.00040254 | 3.0584e-06 | Restore Supply on Device TC4395 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4395 | Changed 2 X 10Amp fuses at FP1472 & 2 X 8 Amp fuses at FC2330. | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 131.6167 | 128.6167 | 128.6167 | 0.00039285 | 3.0544e-06 | 2014-12-30 | C | 0.00039285 | 3.054e-06 | 2015 | 2014-12-30 | C | 1 | 0.00039285 | 3.0544e-06
1 | 3468612 | 2014-12-31 07:30 | 2014-12-31 12:20 | 290.2333 | 1 | 290.2333 | 0.00088766 | 3.0584e-06 | Restore Supply on Device TB2-012 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 201761 and fuse sb3004 | replace 10 amp ddo fuse. cause: unknown. 1 out 3 phases. pole 201761. fuse # sb3004. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 290.2333 | 287.2333 | 287.2333 | 0.00087733 | 3.0544e-06 | 2014-12-31 | C | 0.00087733 | 3.054e-06 | 2015 | 2014-12-31 | C | 1 | 0.00087733 | 3.0544e-06
1 | 3468652 | 2014-12-31 08:00 | 2014-12-31 12:36 | 275.6833 | 4 | 965.1667 | 0.0029519 | 1.2234e-05 | Restore Supply on Device TC985 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M12578 | replaced 2x 15a hv fuse links due to unknown, nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 241.2917 | 238.2917 | 953.1667 | 0.0029114 | 1.2218e-05 | 2014-12-31 | C | 0.0029114 | 1.2218e-05 | 2015 | 2014-12-31 | C | 4 | 0.0029114 | 1.2218e-05
1 | 3245107 | 2014-12-31 08:55 | 2014-12-31 11:58 | 183 | 1 | 330.15 | 0.0010097 | 3.0584e-06 | NAPA ID:05470 TP_MASTERTON GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 826394 | Replace Red Tag Pole 826394. Work Location: Norfolk Road, Carterton. Work Order 10132887 | F1 | UPPER MANAIA RD | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 330.15 | 327.15 | 327.15 | 0.00099925 | 3.0544e-06 | 2014-12-31 | B | 0.00049963 | 1.527e-06 | 2015 | 2014-12-31 | B | 1 | 0.00099925 | 3.0544e-06
1 | 3469023 | 2014-12-31 11:35 | 2014-12-31 16:00 | 264.6833 | 1 | 264.6833 | 0.00080951 | 3.0584e-06 | Restore Supply on Device X1769 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x1769 | replace distribution transformer. cause: lightning. tx x1769. lv and hv. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. Email sent to JO | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 264.6833 | 261.6833 | 261.6833 | 0.00079929 | 3.0544e-06 | 2014-12-31 | C | 0.00079929 | 3.054e-06 | 2015 | 2014-12-31 | C | 1 | 0.00079929 | 3.0544e-06
1 | 3469036 | 2014-12-31 11:51 | 2014-12-31 15:33 | 221.8 | 1 | 221.8 | 0.00067836 | 3.0584e-06 | Restore Supply on Device TD6-041 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD6 041 | Blown 50 kVA transformer TD6 041 replaced unknown cause, all service restored Tom Tanoa attended own isolation and AP. Materials 1 x transformer, 2 x fuse holders, 2 x fuse links. Transformer TD6 041 OFF - 12:58 - ON 15:33. Email sent to Jo to check | F4 | BLACK STUMP | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 221.8 | 218.8 | 218.8 | 0.00066831 | 3.0544e-06 | 2014-12-31 | C | 0.00066831 | 3.054e-06 | 2015 | 2014-12-31 | C | 1 | 0.00066831 | 3.0544e-06
1 | 3471213 | 2014-12-31 13:06 | 2014-12-31 15:15 | 128.2333 | 462 | 29223.9667 | 0.089379 | 0.001413 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 755604 | CB 6 tripped on E/F flags, line was patrolled and sectionalised and vegetation was found growing in the lines at pole 755604, line was isolated at ABS 412 so faultman could cut part of the vegetation away. Faultman has defected this part of the line so tr | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 63.2553 | 60.2553 | 27837.9667 | 0.085029 | 0.0014111 | 2014-12-31 | C | 0.085029 | 0.0014111 | 2015 | 2014-12-31 | C | 462 | 0.085029 | 0.0014111
1 | 3473288 | 2014-12-31 17:45 | 2014-12-31 18:13 | 27.6667 | 13 | 359.6667 | 0.0011 | 3.9759e-05 | Restore Supply on Device 986 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 986 | Faultman found a burnt jumper at Fuses 986, line was isolated at fuses 986 to repair the jumper. | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 27.6667 | 24.6667 | 320.6667 | 0.00097945 | 3.9708e-05 | 2014-12-31 | C | 0.00097945 | 3.9708e-05 | 2015 | 2014-12-31 | C | 13 | 0.00097945 | 3.9708e-05
1 | 3473356 | 2014-12-31 21:12 | 2014-12-31 23:38 | 145.55 | 237 | 21919.5333 | 0.067039 | 0.00072485 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773596 | CB6 A/R, L/O. E/F, O/C B Phase. Due to broken insulator. Materials used: 1x 11kV pin & insulator, 1x Tie wrap, 2mtrs of squirrel conductor, 2x conductor joints | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 92.4875 | 89.4875 | 21208.5333 | 0.06478 | 0.0007239 | 2014-12-31 | C | 0.06478 | 0.0007239 | 2015 | 2014-12-31 | C | 237 | 0.06478 | 0.0007239
1 | 3474012 | 2015-01-01 08:22 | 2015-01-01 10:25 | 122.7167 | 4 | 181.7833 | 0.00055597 | 1.2234e-05 | Restore Supply on Device T1161 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7043 | 2 HT Fuses found tripped at Fuses 7043. Patrolled, suspect bird strike. Reloaded OK with 3A. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 45.4458 | 42.4458 | 169.7833 | 0.00051859 | 1.2218e-05 | 2015-01-01 | C | 0.00051859 | 1.2218e-05 | 2015 | 2015-01-01 | C | 4 | 0.00051859 | 1.2218e-05
1 | 3474119 | 2015-01-01 11:07 | 2015-01-01 14:12 | 185.0667 | 1 | 185.0667 | 0.00056601 | 3.0584e-06 | Restore Supply on Device 8322 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuses 8322 | 11kV fuses 8322 found tripped by member of Public. Open, Tagged, suspect 11kV cable fault. B.Moratti on site. DNO 150101 raised. 05/01/15. Fault still being repaired, powerr is still off to the industrial site. It is the former Tenix engineering workshop | F3 | BROOKLANDS 7 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 185.0667 | 182.0667 | 182.0667 | 0.00055611 | 3.0544e-06 | 2015-01-01 | C | 0.00055611 | 3.054e-06 | 2015 | 2015-01-01 | C | 1 | 0.00055611 | 3.0544e-06
1 | 3474216 | 2015-01-01 17:28 | 2015-01-01 19:44 | 135.8 | 2 | 271.6 | 0.00083067 | 6.1168e-06 | Restore Supply on Device 3239T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2699T | Replaced 2 x blown 2A HV tx fuses. All other assets okay; nothing else replaced. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 135.8 | 132.8 | 265.6 | 0.00081125 | 6.1088e-06 | 2015-01-01 | C | 0.00081125 | 6.109e-06 | 2015 | 2015-01-01 | C | 2 | 0.00081125 | 6.1088e-06
1 | 3474232 | 2015-01-01 18:54 | 2015-01-01 23:04 | 250.2333 | 666 | 85954.5833 | 0.26289 | 0.0020369 | Restore Supply on Device 9278 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2703 | Sectionalised and found no fault. SCADA drawing total wrong Needs verified. Suspect recloser 9278 O/L settings wrong | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 129.0609 | 126.0609 | 83956.5833 | 0.25644 | 0.0020342 | 2015-01-01 | C | 0.25644 | 0.0020342 | 2015 | 2015-01-01 | C | 666 | 0.25644 | 0.0020342
1 | 3478153 | 2015-01-02 05:36 | 2015-01-02 07:54 | 138.3667 | 1 | 138.3667 | 0.00042318 | 3.0584e-06 | Restore Supply on Device TP1975 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1075 | Replaced 2x 8a ddo fuse links due to bird strike. nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | OLD CAMBRIDGE RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 138.3667 | 135.3667 | 135.3667 | 0.00041347 | 3.0544e-06 | 2015-01-02 | C | 0.00041347 | 3.054e-06 | 2015 | 2015-01-02 | C | 1 | 0.00041347 | 3.0544e-06
1 | 3478159 | 2015-01-02 05:36 | 2015-01-02 09:19 | 222.5667 | 15 | 398.3 | 0.0012182 | 4.5876e-05 | Restore Supply on Device TC3582 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | TC2146 | Replace 2 x 11 kV fuse at transformer TC2146. 10 Amps. 2 out of 2 phases. Restored at 08.26am and patrolled. Worked through control. Cause: possum (?). No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standar | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 26.5533 | 23.5533 | 353.3 | 0.0010791 | 4.5816e-05 | 2015-01-02 | C | 0.0010791 | 4.5816e-05 | 2015 | 2015-01-02 | C | 15 | 0.0010791 | 4.5816e-05
1 | 3478169 | 2015-01-02 06:35 | 2015-01-02 10:15 | 220.4 | 268 | 51177.3167 | 0.15652 | 0.00081966 | Restore Supply on Device 7131 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB7131 | Tripping on Starthmore CB7131. Feeder sectionalised / patrolled but nothing found. Restored OK. Phil Webby and Bruce attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 190.9601 | 187.9601 | 50373.3167 | 0.15386 | 0.00081859 | 2015-01-02 | C | 0.15386 | 0.00081859 | 2015 | 2015-01-02 | C | 268 | 0.15386 | 0.00081859
1 | 3478166 | 2015-01-02 07:01 | 2015-01-02 09:27 | 146.1833 | 33 | 4824.05 | 0.014754 | 0.00010093 | Restore Supply on Device TE8-045 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227646 |  | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 146.1833 | 143.1833 | 4725.05 | 0.014432 | 0.0001008 | 2015-01-02 | C | 0.014432 | 0.0001008 | 2015 | 2015-01-02 | C | 33 | 0.014432 | 0.0001008
1 | 3478493 | 2015-01-02 07:32 | 2015-01-02 09:32 | 119.9 | 1 | 119.9 | 0.0003667 | 3.0584e-06 | Restore Supply on Device T2419 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 7377 | replace 2 x 10 amp fuses at link 7377. cause: bull rubbing up the stay wire/pole. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 119.9 | 116.9 | 116.9 | 0.00035706 | 3.0544e-06 | 2015-01-02 | C | 0.00035706 | 3.054e-06 | 2015 | 2015-01-02 | C | 1 | 0.00035706 | 3.0544e-06
1 | 3479221 | 2015-01-02 08:53 | 2015-01-02 10:26 | 92.7333 | 2 | 113.35 | 0.00034667 | 6.1168e-06 | Restore Supply on Device T4207 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 11001 | Follow track to the ponds. 11kV Fuses 11001 found tripped. Patrolled / suspect bird strike / reloaded OK. Adrian Marshall attended. | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 56.675 | 53.675 | 107.35 | 0.00032789 | 6.1088e-06 | 2015-01-02 | C | 0.00032789 | 6.109e-06 | 2015 | 2015-01-02 | C | 2 | 0.00032789 | 6.1088e-06
1 | 3480468 | 2015-01-02 17:48 | 2015-01-02 20:10 | 142.0667 | 333 | 18307.4 | 0.055992 | 0.0010185 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P26058 | Recloser 10050 auto reclosed on E/F flags, line was not patrolled. This was related to OMS 3480440. Car vs Pole. Pole hit was double circuit line and affected Turitea, TWP Kelvin Grove and Keith St substations. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54.9772 | 51.9772 | 17308.4 | 0.052867 | 0.0010171 | 2015-01-02 | C | 0.052867 | 0.0010171 | 2015 | 2015-01-02 | C | 333 | 0.052867 | 0.0010171
1 | 3480895 | 2015-01-03 01:53 | 2015-01-03 02:58 | 64.2167 | 2817 | 175778.7833 | 0.53761 | 0.0086156 | Restore Supply on Device 60 | 66000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Unknown | Tai CB 60 tripped Dir E/F, C & B Ph O/C (Loss of COR sub). 66kV line patrolled between COR & WHT. No fault found. Backfeed via WHT CB50 with TAI - COR isolated at ABS 3602. Andrew King and Steve Johnstone attended. | F1, F2, F3 | TAISUB-CGLEN 66KV | TP_KOPU | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 62.3993 | 59.3993 | 167327.7833 | 0.51109 | 0.0086043 | 2015-01-03 | C | 0.51109 | 0.0086043 | 2015 | 2015-01-03 | C | 2817 | 0.51109 | 0.0086043
1 | 3483726 | 2015-01-03 06:26 | 2015-01-03 07:20 | 54.55 | 1 | 54.55 | 0.00016684 | 3.0584e-06 | Restore Supply on Device T7/440 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses Q27 | Fuse found blown at Fuses Q27 -Dead bird found under lines at Q27- used 2X 6 amp fuses. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54.55 | 51.55 | 51.55 | 0.00015746 | 3.0544e-06 | 2015-01-03 | C | 0.00015746 | 3.054e-06 | 2015 | 2015-01-03 | C | 1 | 0.00015746 | 3.0544e-06
1 | 3484324 | 2015-01-03 14:24 | 2015-01-03 17:03 | 158.95 | 1 | 158.95 | 0.00048614 | 3.0584e-06 | Restore Supply on Device 2981T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3949T | HV fuses feeding Transformer 3949T - Used 1x 3amp & 1 X 6amp HV fuses | F5 | OTARAOA RD | MCKEE SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 158.95 | 155.95 | 155.95 | 0.00047634 | 3.0544e-06 | 2015-01-03 | C | 0.00047634 | 3.054e-06 | 2015 | 2015-01-03 | C | 1 | 0.00047634 | 3.0544e-06
1 | 3484375 | 2015-01-03 16:53 | 2015-01-03 19:11 | 138.5167 | 1 | 138.5167 | 0.00042364 | 3.0584e-06 | Restore Supply on Device TC4939 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T4939 | Replace 2 x 100A fuse links o/h. Email sent to Jo to check for possible SAIDI component. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 138.5167 | 135.5167 | 135.5167 | 0.00041393 | 3.0544e-06 | 2015-01-03 | C | 0.00041392 | 3.054e-06 | 2015 | 2015-01-03 | C | 1 | 0.00041393 | 3.0544e-06
1 | 3484421 | 2015-01-03 21:40 | 2015-01-03 22:10 | 29.7833 | 33 | 982.85 | 0.003006 | 0.00010093 | Restore Supply on Device TC4037 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4037 | Isolate transformer TC4037 to replace burnt out 200A base & fuse U/G. P Hicks attended. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 29.7833 | 26.7833 | 883.85 | 0.0026997 | 0.0001008 | 2015-01-03 | C | 0.0026997 | 0.0001008 | 2015 | 2015-01-03 | C | 33 | 0.0026997 | 0.0001008
1 | 3484635 | 2015-01-03 22:24 | 2015-01-04 01:26 | 182.7167 | 157 | 16339.7833 | 0.049974 | 0.00048017 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C313 | MIK CB5 tripped C & B Ph O/C, E/F L/O feeder sectionalised & line x 1 found at pole C313. Isolations between ABS's 675, 704, IC672 & IC1270 ( no back feeds ). Line repaired all service restored. Materials 2 meters conductor 3 x H/V comp sleeves. | F4 | NGARUA | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 104.0751 | 101.0751 | 15868.7833 | 0.04847 | 0.00047954 | 2015-01-03 | C | 0.04847 | 0.00047955 | 2015 | 2015-01-03 | C | 157 | 0.04847 | 0.00047954
1 | 3485731 | 2015-01-04 07:24 | 2015-01-04 09:54 | 149.6833 | 1 | 149.6833 | 0.00045779 | 3.0584e-06 | Restore Supply on Device T1581 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7495 | Two HV Fuses found Blown at Fuses 7495 - Line Patrolled with no fault found - Used 2 X 10 fuses. email sent to jo | F4 | MOROA | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 149.6833 | 146.6833 | 146.6833 | 0.00044803 | 3.0544e-06 | 2015-01-04 | C | 0.00044803 | 3.054e-06 | 2015 | 2015-01-04 | C | 1 | 0.00044803 | 3.0544e-06
1 | 3485748 | 2015-01-04 08:11 | 2015-01-04 10:15 | 123.6167 | 2 | 206.7333 | 0.00063228 | 6.1168e-06 | Restore Supply on Device TC1-004 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | TC1/004 | Replaced 2x 3a HV Fuses. email sent to Jo | F4 | KATIKATI | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 103.3667 | 100.3667 | 200.7333 | 0.00061312 | 6.1088e-06 | 2015-01-04 | C | 0.00061312 | 6.109e-06 | 2015 | 2015-01-04 | C | 2 | 0.00061312 | 6.1088e-06
1 | 3486318 | 2015-01-04 16:28 | 2015-01-04 18:55 | 147.3833 | 16 | 2096.1333 | 0.0064109 | 4.8935e-05 | Restore Supply on Device 7856 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7856 | 2 x 10Amp llkV Fuses blown at fuses 7856. Line Patrolled, unknown cause | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 131.0083 | 128.0083 | 2048.1333 | 0.0062559 | 4.8871e-05 | 2015-01-04 | C | 0.0062559 | 4.8871e-05 | 2015 | 2015-01-04 | C | 16 | 0.0062559 | 4.8871e-05
1 | 3486807 | 2015-01-05 06:49 | 2015-01-05 10:01 | 191.8 | 7 | 1315.4 | 0.004023 | 2.1409e-05 | Restore Supply on Device 7667 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 824665 | Replaced 2 X 10A HV Fuses at Fuses 7667. Bird Strike at Pole 824665 | F3 | SOMERSET RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 187.9143 | 184.9143 | 1294.4 | 0.0039536 | 2.1381e-05 | 2015-01-05 | C | 0.0039536 | 2.1381e-05 | 2015 | 2015-01-05 | C | 7 | 0.0039536 | 2.1381e-05
1 | 3487007 | 2015-01-05 08:12 | 2015-01-05 09:30 | 77.5833 | 1 | 77.5833 | 0.00023728 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13193 | 2x 6 amp DDO HV oh did not work through control P13193 caused by bird nothing else repaired or replaced surrounding asset up to standard. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 77.5833 | 74.5833 | 74.5833 | 0.00022781 | 3.0544e-06 | 2015-01-05 | C | 0.00022781 | 3.054e-06 | 2015 | 2015-01-05 | C | 1 | 0.00022781 | 3.0544e-06
1 | 3487335 | 2015-01-05 19:30 | 2015-01-05 19:31 | 0.8 | 243 | 8942.4 | 0.02735 | 0.0007432 | Restore Supply on Device SE7-020 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 227130 | Tenix reported a broken cross arm at pole 227130, unplanned shut to replace. PKW Sub, CB 2, Iso via ABS SE7-020 ans Rs site 7960. Cross arm replaced, structure amber defected for later replacement. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 36.8 | 33.8 | 8213.4 | 0.025087 | 0.00074222 | 2015-01-05 | C | 0.025087 | 0.00074223 | 2015 | 2015-01-05 | C | 243 | 0.025087 | 0.00074222
1 | 3487684 | 2015-01-05 22:27 | 2015-01-05 23:23 | 56 | 168 | 9408 | 0.028774 | 0.00051381 | Restore Supply on Device C927 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C927 | CB C927 Tripped A & B ph O/ C A/R & RS C630 Tripped A & C Ph O/C E/F A/R - Not Patrolled | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 56 | 53 | 8904 | 0.027197 | 0.00051314 | 2015-01-05 | C | 0.027197 | 0.00051314 | 2015 | 2015-01-05 | C | 168 | 0.027197 | 0.00051314
1 | 3487855 | 2015-01-05 22:44 | 2015-01-06 00:27 | 103.15 | 436 | 20909.2333 | 0.063949 | 0.0013335 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | CB3 | CB 3 tripped. No Flags. Back feed put in from Lake Rd Cb 3 via Recloser 9663/2 up to Recloser RC18. Line Patrolled & Sectionalized possible possum, one found dead up Taihoa South Rd | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 47.957 | 44.957 | 19601.2333 | 0.05987 | 0.0013317 | 2015-01-05 | C | 0.05987 | 0.0013317 | 2015 | 2015-01-05 | C | 436 | 0.05987 | 0.0013317
1 | 3488633 | 2015-01-06 06:13 | 2015-01-06 06:59 | 46.3167 | 3016 | 79016.8833 | 0.24167 | 0.0092242 | Restore Supply on Device 2212 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | KINBRD094 | CB 2212 Tripped, N time O/C. Backfed BRD6 & BRD8 via Recloser 9083. Backfeed past BRD5 Recloser 9198 via Recloser 9595. Fault found to be Magpie on the line. Fault had cleared, relivened OK. | F1, F2, F3 | KINLEITH2212-BAIRD RD 33KV | TP_KINLEITH | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 26.1992 | 23.1992 | 69968.8833 | 0.21371 | 0.0092121 | 2015-01-06 | C | 0.21371 | 0.0092121 | 2015 | 2015-01-06 | C | 3016 | 0.21371 | 0.0092121
1 | 3419650 | 2015-01-06 09:00 | 2015-01-06 16:14 | 434 | 13 | 5642 | 0.017256 | 3.9759e-05 | NAPA ID:05818 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M1461 | To Break Jumpers on Pole M1461 Isolating Lines To Stringers Rd. Works location: Waotu South Rd WO 10153771 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 434 | 431 | 5603 | 0.017114 | 3.9708e-05 | 2015-01-06 | B | 0.008557 | 1.9854e-05 | 2015 | 2015-01-06 | B | 13 | 0.017114 | 3.9708e-05
1 | 3245354 | 2015-01-06 09:15 | 2015-01-06 15:05 | 350 | 5 | 1750 | 0.0053522 | 1.5292e-05 | NAPA ID:05480 TP_KINLEITH GXP > BAIRD ROAD SUB > PAPANUI ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3363 | Replacing LV fusing in Transformer TC3363. Work Location: Baird Road, Tokoroa. Work Order 10162951 | F4 | PAPANUI ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 350 | 347 | 1735 | 0.0052994 | 1.5272e-05 | 2015-01-06 | B | 0.0026497 | 7.636e-06 | 2015 | 2015-01-06 | B | 5 | 0.0052994 | 1.5272e-05
1 | 3220701 | 2015-01-06 09:16 | 2015-01-15 11:29 | 13093.6167 | 404 | 100980.75 | 0.30884 | 0.0012356 | NAPA ID:04987 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/631 | Make gap at transformers T6/631 and T6/636, remove old tin shed and install new city pad transformer. Works location: Karamea St. WO 10158152 | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 249.9524 | 246.9524 | 99768.75 | 0.30474 | 0.001234 | 2015-01-06 | B | 0.15237 | 0.00061699 | 2015 | 2015-01-06 | B | 404 | 0.30474 | 0.001234
1 | 3487230 | 2015-01-06 10:00 | 2015-01-06 15:58 | 357.4167 | 107 | 38243.5833 | 0.11697 | 0.00032725 | NAPA ID:05900 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11000 | PLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole P26056 | Replace 33Kv 11KV pole hit by car NDR no 30876 | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 357.4167 | 354.4167 | 37922.5833 | 0.11583 | 0.00032682 | 2015-01-06 | B | 0.057916 | 0.00016341 | 2015 | 2015-01-06 | B | 107 | 0.11583 | 0.00032682
1 | 3494945 | 2015-01-06 10:39 | 2015-01-06 17:56 | 436.95 | 10 | 3893.6833 | 0.011909 | 3.0584e-05 | Restore Supply on Device 7768 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 373702 | 10.46am - called through to svs Hub 1 MANGAREI ROAD off Te Ore Ore Bideford road. Mangarei road is opposite Mount Clyde Road. 15:20 Joe advises helicopter needed to re-string conductor. NDR 37973. Child job 3493920. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 389.3683 | 386.3683 | 3863.6833 | 0.011801 | 3.0544e-05 | 2015-01-06 | C | 0.011801 | 3.0544e-05 | 2015 | 2015-01-06 | C | 10 | 0.011801 | 3.0544e-05
1 | 3495010 | 2015-01-06 15:30 | 2015-01-06 18:03 | 152.3833 | 1 | 152.3833 | 0.00046605 | 3.0584e-06 | Restore Supply on Device TE6-190 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 221542 | Part power on 3 phase supply. Go down the drive for 1km to the Transformer. Customer own Sparky attended details following Bob 0274 973 453 please call bob when fm arrives Rplace 2 HT fuse links | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 152.3833 | 149.3833 | 149.3833 | 0.00045628 | 3.0544e-06 | 2015-01-06 | C | 0.00045628 | 3.054e-06 | 2015 | 2015-01-06 | C | 1 | 0.00045628 | 3.0544e-06
1 | 3229378 | 2015-01-07 08:45 | 2015-01-07 16:02 | 437 | 385 | 168245 | 0.51456 | 0.0011775 | NAPA ID:05385 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ROBERTS LINE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E77 | Replace 11KV poles and install new recloser. Works location: Roberts Line. WO 10157271. | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 437 | 434 | 167090 | 0.51036 | 0.001176 | 2015-01-07 | B | 0.25518 | 0.00058798 | 2015 | 2015-01-07 | B | 385 | 0.51036 | 0.001176
1 | 3245329 | 2015-01-07 09:45 | 2015-01-07 11:47 | 122 | 95 | 11590 | 0.035447 | 0.00029055 | NAPA ID:05516 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TB2-013, TB2-068 | 11kV Switchgear 9856 installed at fence line is over boundary by 80mm so unit has to be excavated around and pulled forward that 80mm. Work Location: Blundell Place, Katikati. Work Order: 10148375 | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 122 | 119 | 11305 | 0.03453 | 0.00029017 | 2015-01-07 | B | 0.017265 | 0.00014509 | 2015 | 2015-01-07 | B | 95 | 0.03453 | 0.00029017
1 | 3214672 | 2015-01-07 10:00 | 2015-01-07 14:08 | 248 | 25 | 6200 | 0.018962 | 7.6461e-05 | NAPA ID:04830 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 266 | Replace ABS 266 DNO140915 upgrade Earths replce xarms. Works location: Lepper Rd Inglewood WO 10160584 | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 248 | 245 | 6125 | 0.018708 | 7.6361e-05 | 2015-01-07 | B | 0.0093542 | 3.818e-05 | 2015 | 2015-01-07 | B | 25 | 0.018708 | 7.6361e-05
1 | 3498097 | 2015-01-07 14:34 | 2015-01-07 15:17 | 43.2167 | 184 | 20057 | 0.061343 | 0.00056275 | Restore Supply on Device F55 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/351, P14224 | This Job & Job 3498810 are one & the same 4:40pm Jeff advised Blown TX (T4/351 Bruce Mehrtens assisting Transformer T4/351 Replaced. 30kVA 3 phase Pole mount. Cannot close job off due to OMS 3498810 Stuck in verified. | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 109.0054 | 106.0054 | 19505 | 0.059577 | 0.00056201 | 2015-01-07 | C | 0.059577 | 0.00056201 | 2015 | 2015-01-07 | C | 184 | 0.059577 | 0.00056201
1 | 3499649 | 2015-01-07 20:33 | 2015-01-07 23:27 | 173.95 | 1 | 173.95 | 0.00053201 | 3.0584e-06 | Restore Supply on Device TE7-069 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T7-069 | Replaced 2X 3a HV Fuses. Email sent to Jo to check for SAIDI component. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 173.95 | 170.95 | 170.95 | 0.00052215 | 3.0544e-06 | 2015-01-07 | C | 0.00052215 | 3.054e-06 | 2015 | 2015-01-07 | C | 1 | 0.00052215 | 3.0544e-06
1 | 3499653 | 2015-01-07 21:12 | 2015-01-07 22:11 | 58.6833 | 12 | 704.2 | 0.0021537 | 3.6701e-05 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 799260 | Recloser C640 Trip. E/F. L/O. Line patrolled. A twig was found across conductor and pole brace. Knocked off with fuse stick. Wind Blown Debris from outside the notice zone. Jason Hall attended. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 58.6833 | 55.6833 | 668.2 | 0.002041 | 3.6653e-05 | 2015-01-07 | C | 0.002041 | 3.6653e-05 | 2015 | 2015-01-07 | C | 12 | 0.002041 | 3.6653e-05
1 | 3499676 | 2015-01-07 21:30 | 2015-01-07 22:53 | 82.6333 | 1 | 82.6333 | 0.00025273 | 3.0584e-06 | Restore Supply on Device TE4-169 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 316908 | CUST ADVISES HAS SPOKEN TO NEIGHBOUR AT 158 CORNER OF HEREFORD & WARNER ROAD HAS HEARD A LOUD BANG & SIGHTED BLOWN POLE FUSES X 2 replaced x2 10amp HV fuses at pole 316908 cause clash of line due to poss bird strike No other assets repaired or repla | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 82.6333 | 79.6333 | 79.6333 | 0.00024323 | 3.0544e-06 | 2015-01-07 | C | 0.00024323 | 3.054e-06 | 2015 | 2015-01-07 | C | 1 | 0.00024323 | 3.0544e-06
1 | 3499742 | 2015-01-08 06:05 | 2015-01-08 10:34 | 269.3333 | 6 | 1127.75 | 0.0034491 | 1.8351e-05 | Restore Supply on Device 637 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 849539 | Replaced 2x 6a HV Fuses Links and 2x 2a HV Fuse Links at transformer X2015 on pole#804296. Nothing else repaired or replaced, adjacent assets up to Powerco standard. Allen Cox attended. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 187.9583 | 184.9583 | 1109.75 | 0.0033896 | 1.8327e-05 | 2015-01-08 | C | 0.0033896 | 1.8327e-05 | 2015 | 2015-01-08 | C | 6 | 0.0033896 | 1.8327e-05
1 | 3303725 | 2015-01-08 08:24 | 2015-01-08 14:12 | 347.0167 | 29 | 10063.4833 | 0.030778 | 8.8694e-05 | NAPA ID:05701 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V73 | To change 11kV poles , and to remove Temp Fuse Links 69 and remove Temp ABS 58. Works location; Route 52 Pongaroa. WO 10130597. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 347.0167 | 344.0167 | 9976.4833 | 0.030472 | 8.8578e-05 | 2015-01-08 | B | 0.015236 | 4.4289e-05 | 2015 | 2015-01-08 | B | 29 | 0.030472 | 8.8578e-05
1 | 3228392 | 2015-01-08 08:30 | 2015-01-08 12:49 | 259.0833 | 68 | 17617.6667 | 0.053882 | 0.00020797 | NAPA ID:04898 TP_MASTERTON GXP > CHAPEL SUB > ESSEX ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 830908 | Isolate T779 so 11kV jumpers at pole 830908 can be cut so that old t/x and structure can be removed and 11kV can be connected to new pole which will be installed prior to this date. Works location: Cole St Masterton. WO 10133440. | F3 | ESSEX ST | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 259.0833 | 256.0833 | 17413.6667 | 0.053189 | 0.0002077 | 2015-01-08 | B | 0.026594 | 0.00010385 | 2015 | 2015-01-08 | B | 68 | 0.053189 | 0.0002077
1 | 3244970 | 2015-01-08 08:45 | 2015-01-08 10:24 | 98.95 | 62 | 6134.9 | 0.018763 | 0.00018962 | NAPA ID:05398 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 810623 | Replace defective pole 810623. Work Location: Lake Ferry Road. Work Order 10150842 | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98.95 | 95.95 | 5948.9 | 0.01817 | 0.00018937 | 2015-01-08 | B | 0.0090852 | 9.4687e-05 | 2015 | 2015-01-08 | B | 62 | 0.01817 | 0.00018937
1 | 3229866 | 2015-01-08 09:02 | 2015-01-08 15:21 | 379 | 3 | 1137 | 0.0034774 | 9.1753e-06 | NAPA ID:02823 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 228909 | To replace pole 228909. Works location: Billing Rd Pukehina Te Puke WO 10161617 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 379 | 376 | 1128 | 0.0034454 | 9.1633e-06 | 2015-01-08 | B | 0.0017227 | 4.582e-06 | 2015 | 2015-01-08 | B | 3 | 0.0034454 | 9.1633e-06
1 | 3232895 | 2015-01-08 09:07 | 2015-01-08 15:29 | 382 | 48 | 18336 | 0.056079 | 0.0001468 | NAPA ID:05330 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CA413 | Replacing 14, 11kV defect poles. Works location: Austin Rd East, Normanby. WO 10141791. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 382 | 379 | 18192 | 0.055566 | 0.00014661 | 2015-01-08 | B | 0.027783 | 7.3306e-05 | 2015 | 2015-01-08 | B | 48 | 0.055566 | 0.00014661
1 | 3500293 | 2015-01-08 09:37 | 2015-01-08 13:54 | 257.1833 | 8 | 2057.4667 | 0.0062926 | 2.4467e-05 | Restore Supply on Device T1/313 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1/313 | This is part of SIS 3227498. Replace 11kV transformer T1/313 crossarms. | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 257.1833 | 254.1833 | 2033.4667 | 0.0062111 | 2.4435e-05 | 2015-01-08 | C | 0.0062111 | 2.4435e-05 | 2015 | 2015-01-08 | C | 8 | 0.0062111 | 2.4435e-05
1 | 3245081 | 2015-01-08 09:39 | 2015-01-08 14:43 | 304.1 | 32 | 9731.2 | 0.029762 | 9.787e-05 | NAPA ID:05447 TP_BRUNSWICK GXP > CASTLECLIFF SUB > HEADS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X259 | Replace 400v board for transformer X259 for new type. No backfeed available. Work Location: Montgomery Road, Wanganui. PPPD 10172145 | F2 | HEADS RD | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 304.1 | 301.1 | 9635.2 | 0.02943 | 9.7742e-05 | 2015-01-08 | B | 0.014715 | 4.8871e-05 | 2015 | 2015-01-08 | B | 32 | 0.02943 | 9.7742e-05
1 | 3500345 | 2015-01-08 10:10 | 2015-01-08 11:00 | 50 | 27 | 1350 | 0.0041289 | 8.2577e-05 | Restore Supply on Device 6435 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 317084 | Faultman was informed by electrician working for New Plymouth Electrical that a cross arm on pole 317084 was only just been held in place by king bolt, the nut was missing, Line was isolated at Fuses 6435 to replace the king bolt nut & washers. 1 x Kingpi | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 50 | 47 | 1269 | 0.0038761 | 8.2469e-05 | 2015-01-08 | C | 0.0038761 | 8.2469e-05 | 2015 | 2015-01-08 | C | 27 | 0.0038761 | 8.2469e-05
1 | 3500503 | 2015-01-08 12:05 | 2015-01-08 17:29 | 324.5667 | 242 | 25273.05 | 0.077296 | 0.00074014 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | W13378 | Call from Maria at Akld Fire Comms 12:14hrs Ref : F1761919 Lines down & pole broken due to vehicle accident 823 Tairua Whitianga Road, Whenuakite. Control have been advised. | F3/F4 | TAIRUA NORTH | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 104.4341 | 101.4341 | 24547.05 | 0.074977 | 0.00073917 | 2015-01-08 | C | 0.074977 | 0.00073917 | 2015 | 2015-01-08 | C | 242 | 0.074977 | 0.00073917
1 | 3505095 | 2015-01-08 18:51 | 2015-01-08 23:04 | 252.7167 | 194 | 3721.1333 | 0.011381 | 0.00059333 | Restore Supply on Device 8764 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Recloser 6942 | Recloser 8764 & 6942 Both Tripped. Flaggings on 6942 E/F. O/C. L/O. Suspect a bird strike beyond 6942. 8764 closed back in OK but 6942 would not close. it was found that the backup battery had a broken terminal. This was repaired and power restored to Ch | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 19.1811 | 16.1811 | 3139.1333 | 0.0095882 | 0.00059256 | 2015-01-08 | C | 0.0095882 | 0.00059256 | 2015 | 2015-01-08 | C | 194 | 0.0095882 | 0.00059256
1 | 3505354 | 2015-01-08 21:56 | 2015-01-09 12:05 | 848.7833 | 436 | 78249.5667 | 0.23932 | 0.0013335 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F1619 | CB 3 L/O on O/C & E/F. Sectionalised and found strain insulator at pole F1619 faulty Isoalted between ASB IC793, 9757/1 & 9757/4 Backfeed rest of area. During switching Steve left to do a saftey disconnect then returned to carry out fault finding. Maybe t | F4 | TE POI | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 179.4715 | 176.4715 | 76941.5667 | 0.23501 | 0.0013317 | 2015-01-08 | C | 0.23501 | 0.0013317 | 2015 | 2015-01-08 | C | 436 | 0.23501 | 0.0013317
1 | 3228451 | 2015-01-09 08:35 | 2015-01-09 13:58 | 322.55 | 154 | 49672.7 | 0.15192 | 0.000471 | NAPA ID:05133 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole P13054 | Replace poles P13054 and P2255. Works location: Old Waitekauri Rd Waikino WO 10162904 | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 322.55 | 319.55 | 49210.7 | 0.15031 | 0.00047038 | 2015-01-09 | B | 0.075155 | 0.00023519 | 2015 | 2015-01-09 | B | 154 | 0.15031 | 0.00047038
1 | 3271245 | 2015-01-09 09:15 | 2015-01-09 14:38 | 323 | 27 | 8721 | 0.026672 | 8.2577e-05 | NAPA ID:05396 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 713569 | Replace 11kV poles. Work Location: Namu Road. Work Order 10162610 | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 323 | 320 | 8640 | 0.02639 | 8.2469e-05 | 2015-01-09 | B | 0.013195 | 4.1235e-05 | 2015 | 2015-01-09 | B | 27 | 0.02639 | 8.2469e-05
1 | 3228424 | 2015-01-09 09:37 | 2015-01-09 16:17 | 400.35 | 2 | 800.7 | 0.0024489 | 6.1168e-06 | NAPA ID:05334 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P37539 | Replace crossarms from pole P37539 to P19773. Transformer structure T5/162 is currently a 2-pole structure (P19773 & P19774), this will be changed to a single pole structure using existing pole P19773. TX T5/162 will be replaced with a new pole mount TX. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 400.35 | 397.35 | 794.7 | 0.0024274 | 6.1088e-06 | 2015-01-09 | B | 0.0012137 | 3.054e-06 | 2015 | 2015-01-09 | B | 2 | 0.0024274 | 6.1088e-06
1 | 3510302 | 2015-01-09 10:15 | 2015-01-09 12:22 | 127.4333 | 1 | 127.4333 | 0.00038974 | 3.0584e-06 | Restore Supply on Device TC634 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC634 | Replaced 2 x 6 DDO amp fuses, this also affected 3513172. Adjacent assets checked, all good. Email sent to Jo to check for possible SAIDI component. | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 127.4333 | 124.4333 | 124.4333 | 0.00038007 | 3.0544e-06 | 2015-01-09 | C | 0.00038007 | 3.054e-06 | 2015 | 2015-01-09 | C | 1 | 0.00038007 | 3.0544e-06
1 | 3518787 | 2015-01-09 15:21 | 2015-01-09 16:40 | 78.95 | 1 | 78.95 | 0.00024146 | 3.0584e-06 | Restore Supply on Device TC836 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | IC765 | 11kV switch dropped opened slightly, causing arcing, green light. FM did switching through control. No outage occurred. Pushed switch back. Switch # IC765. cause: unknown. control room has defected this switch. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 78.95 | 75.95 | 75.95 | 0.00023198 | 3.0544e-06 | 2015-01-09 | C | 0.00023198 | 3.054e-06 | 2015 | 2015-01-09 | C | 1 | 0.00023198 | 3.0544e-06
1 | 3518817 | 2015-01-09 16:21 | 2015-01-09 18:05 | 104.95 | 1 | 104.95 | 0.00032098 | 3.0584e-06 | Restore Supply on Device TC2810 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2810 | replace distribution transformer. 15 kva, 11kv, 3 phase. tx 2810. cause: unknown. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 104.95 | 101.95 | 101.95 | 0.0003114 | 3.0544e-06 | 2015-01-09 | C | 0.0003114 | 3.054e-06 | 2015 | 2015-01-09 | C | 1 | 0.0003114 | 3.0544e-06
1 | 3518898 | 2015-01-09 19:39 | 2015-01-09 19:48 | 9 | 3 | 27 | 8.2577e-05 | 9.1753e-06 | Restore Supply on Device SF3-002 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 212258 | Replace faulty kidney at pole 212258. Isolated at fuses SF3-002 1 strain Insulator & 1 deadend | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 18 | 5.498e-05 | 9.1633e-06 | 2015-01-09 | C | 5.498e-05 | 9.163e-06 | 2015 | 2015-01-09 | C | 3 | 5.498e-05 | 9.1633e-06
1 | 3229728 | 2015-01-10 05:01 | 2015-01-10 06:18 | 77.3167 | 281 | 21725.9833 | 0.066447 | 0.00085942 | NAPA ID:05066 TP_BUNNYTHORPE GXP > FEILDING SUB > RESIDENTIAL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | J42 | Repair 11 kv cable crutch and clear partial electrical discharge @ transformer T3/306. Works location: Wild St, Feilding. WO 10155775. | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 77.3167 | 74.3167 | 20882.9833 | 0.063785 | 0.00085829 | 2015-01-10 | B | 0.031893 | 0.00042915 | 2015 | 2015-01-10 | B | 281 | 0.063785 | 0.00085829
1 | 3519369 | 2015-01-10 06:34 | 2015-01-10 08:12 | 97.9167 | 1 | 97.9167 | 0.00029947 | 3.0584e-06 | Restore Supply on Device X1834 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 495 | check if oms 3519373 switch 243 2 jobs Taraketi Road Replaced 2X HV fuses - Email sent to Jo to check for possible SAIDI component. | F4 | PUTORINO | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 97.9167 | 94.9167 | 94.9167 | 0.00028992 | 3.0544e-06 | 2015-01-10 | C | 0.00028992 | 3.054e-06 | 2015 | 2015-01-10 | C | 1 | 0.00028992 | 3.0544e-06
1 | 3303096 | 2015-01-10 09:45 | 2015-01-10 12:47 | 182 | 90 | 16380 | 0.050097 | 0.00027526 | NAPA ID:05644 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P10472 | To replace 11kV ABS S34 plus 11kV cross arms. Work Location: South Road No 2. Work Order 10147863 | F4 | RONGOKOKAKO | PARKVILLE SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 182 | 179 | 16110 | 0.049207 | 0.0002749 | 2015-01-10 | B | 0.024603 | 0.00013745 | 2015 | 2015-01-10 | B | 90 | 0.049207 | 0.0002749
1 | 3520381 | 2015-01-11 07:13 | 2015-01-11 09:21 | 127.4667 | 1 | 127.4667 | 0.00038985 | 3.0584e-06 | Restore Supply on Device X2500 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F4709 | address was stantoft 2x 6amp hv f4709 cause birdstrike No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 127.4667 | 124.4667 | 124.4667 | 0.00038017 | 3.0544e-06 | 2015-01-11 | C | 0.00038017 | 3.054e-06 | 2015 | 2015-01-11 | C | 1 | 0.00038017 | 3.0544e-06
1 | 3520397 | 2015-01-11 08:26 | 2015-01-11 11:14 | 168.0667 | 1 | 168.0667 | 0.00051402 | 3.0584e-06 | Restore Supply on Device Z147 | 22000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2756 805393 | 2x 6amp ht fuse links 2756- cause unknown possible birds No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | LEEDSTOWN 22KV | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 168.0667 | 165.0667 | 165.0667 | 0.00050418 | 3.0544e-06 | 2015-01-11 | C | 0.00050418 | 3.054e-06 | 2015 | 2015-01-11 | C | 1 | 0.00050418 | 3.0544e-06
1 | 3520441 | 2015-01-11 09:55 | 2015-01-11 12:24 | 148.65 | 1 | 148.65 | 0.00045463 | 3.0584e-06 | Restore Supply on Device T77 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7077 | Two Fuse found blown at Fuses 7077 - Line Patrolled with no Fault found - 2 x 10 fuses used. Email sent to Jo to check for SAIDI component. | F5 | MANGAPAKEHA | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 148.65 | 145.65 | 145.65 | 0.00044488 | 3.0544e-06 | 2015-01-11 | C | 0.00044488 | 3.054e-06 | 2015 | 2015-01-11 | C | 1 | 0.00044488 | 3.0544e-06
1 | 3531007 | 2015-01-12 07:17 | 2015-01-12 10:07 | 169.6167 | 3 | 365.8667 | 0.001119 | 9.1753e-06 | Restore Supply on Device T4/302 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p08731 | check if oms 3531080 is related replaced 2x 10a hv fuse due to unknown. nothing else repaired or replaced, adjacent assets up to powerco standard. Email sent to Jo to check for SAIDI component. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 121.9556 | 118.9556 | 356.8667 | 0.00109 | 9.1633e-06 | 2015-01-12 | C | 0.00109 | 9.163e-06 | 2015 | 2015-01-12 | C | 3 | 0.00109 | 9.1633e-06
1 | 3531046 | 2015-01-12 08:29 | 2015-01-12 09:51 | 82.4667 | 1 | 82.4667 | 0.00025222 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | TC5838 | 2X 6AMP DDO HV OH CAUSED BY BIRD STRIKE SURROUNDING ASSET GOOD NOTHING ELSE REPAIRED OR REPLACED. Email sent to JO to check for SAIDI component. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 82.4667 | 79.4667 | 79.4667 | 0.00024272 | 3.0544e-06 | 2015-01-12 | C | 0.00024273 | 3.054e-06 | 2015 | 2015-01-12 | C | 1 | 0.00024272 | 3.0544e-06
1 | 3240378 | 2015-01-12 08:43 | 2015-01-12 13:21 | 277.55 | 22 | 6106.1 | 0.018675 | 6.7285e-05 | NAPA ID:05351 TP_TAURANGA 33 GXP > OMOKOROA SUB > PLUMMERS POINT | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 208662 | REPLACE 33KV 11KV POLES 208662 & 208666. Works location: Jess Rd Omokoroa WO TA-2014-52 | F4 | PLUMMERS POINT | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 277.55 | 274.55 | 6040.1 | 0.018449 | 6.7197e-05 | 2015-01-12 | B | 0.0092245 | 3.3599e-05 | 2015 | 2015-01-12 | B | 22 | 0.018449 | 6.7197e-05
1 | 3245314 | 2015-01-12 08:55 | 2015-01-12 11:55 | 180 | 1 | 180 | 0.00055052 | 3.0584e-06 | NAPA ID:05433 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/247 | Replace Transformer and LV Cross arms on pole P36893 (T5/247). Existing Transformer to be reused. Work Location: Forest Road, Kimbolton. Work Order 10160678 off 08:55 on 11:55 | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 180 | 177 | 177 | 0.00054063 | 3.0544e-06 | 2015-01-12 | B | 0.00027032 | 1.527e-06 | 2015 | 2015-01-12 | B | 1 | 0.00054063 | 3.0544e-06
1 | 3423280 | 2015-01-12 09:15 | 2015-01-12 15:11 | 356 | 2 | 712 | 0.0021776 | 6.1168e-06 | NAPA ID:05822 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 792850 | Replace 11kv pole 792850. Works Location: Ruatagata Rd, Whangaehu. WO 10141993. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 356 | 353 | 706 | 0.0021564 | 6.1088e-06 | 2015-01-12 | B | 0.0010782 | 3.054e-06 | 2015 | 2015-01-12 | B | 2 | 0.0021564 | 6.1088e-06
1 | 3245335 | 2015-01-12 09:15 | 2015-01-12 14:37 | 321.4 | 27 | 8677.8 | 0.02654 | 8.2577e-05 | NAPA ID:05407 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 713562,713565, 713574, 713575, 713576, 713577, 713578, 713580, 713581, 713587, 713600, 713601, 713602, 713606 | Replace pole numbers 713562, 713565, 713574, 713575, 713576, 713577, 713578, 713580, 713581, 713587, 713600, 713601, 713602 and 713606. Work Location: Namu Road. Work Order 10162610 | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 321.4 | 318.4 | 8596.8 | 0.026258 | 8.2469e-05 | 2015-01-12 | B | 0.013129 | 4.1235e-05 | 2015 | 2015-01-12 | B | 27 | 0.026258 | 8.2469e-05
1 | 3239627 | 2015-01-12 09:44 | 2015-01-12 16:15 | 391.3333 | 1 | 391.3333 | 0.0011969 | 3.0584e-06 | NAPA ID:02824 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 229195 | To replace pole 229195 & ABS SF7-026. Works location: Old Coach Rd WO 477863 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 391.3333 | 388.3333 | 388.3333 | 0.0011861 | 3.0544e-06 | 2015-01-12 | B | 0.00059307 | 1.527e-06 | 2015 | 2015-01-12 | B | 1 | 0.0011861 | 3.0544e-06
1 | 3533602 | 2015-01-12 11:06 | 2015-01-12 12:07 | 61.5833 | 1 | 61.5833 | 0.00018835 | 3.0584e-06 | Restore Supply on Device L1235 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 858064 | at 11:05, Livingstone Sub, CB LI7 Kakaramea Feeder. Found low hanging 11kV conductor at Pole 858064. Isolated Lines at Fuses 8758. Permit Issued & Repairs Carried Out, Re-hung & Restrained conductor. All Power Restored on Completion. Chris Katene Attended | F4 | KAKARAMEA | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 61.5833 | 58.5833 | 58.5833 | 0.00017894 | 3.0544e-06 | 2015-01-12 | C | 0.00017894 | 3.054e-06 | 2015 | 2015-01-12 | C | 1 | 0.00017894 | 3.0544e-06
1 | 3533673 | 2015-01-12 11:18 | 2015-01-12 11:45 | 27 | 426 | 11502 | 0.035178 | 0.0013029 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717989 | at 11:18, Manaia Sub, CB 5 Auroa Feeder, Tripped, O/C, L/O. This was also backfeeding most of Manaia Sub, CB 8 Manaia Feeder, ABS 6817 was closed and CB 8 Open (up to ABS 6711: ABS 6711 Open & ABS WH844 Closed). Planned Switching was being carried out at | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 27 | 24 | 10224 | 0.031228 | 0.0013012 | 2015-01-12 | C | 0.031228 | 0.0013012 | 2015 | 2015-01-12 | C | 426 | 0.031228 | 0.0013012
1 | 4130243 | 2015-01-12 11:18 | 2015-01-12 15:06 | 228 | 358 | 42025 | 0.12853 | 0.0010949 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717988 | at 11:18, Manaia Sub, CB 5 Auroa Feeder, Tripped, O/C, L/O. This was also backfeeding most of Manaia Sub, CB 8 Manaia Feeder, ABS 6817 was closed and CB 8 Open (up to ABS 6711: ABS 6711 Open & ABS WH844 Closed). Planned Switching was being carried out at | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 117.3883 | 114.3883 | 40951 | 0.12508 | 0.0010935 | 2015-01-12 | C | 0.12508 | 0.0010935 | 2015 | 2015-01-12 | C | 358 | 0.12508 | 0.0010935
1 | 3245328 | 2015-01-12 12:30 | 2015-01-12 15:07 | 157 | 2 | 314 | 0.00096034 | 6.1168e-06 | NAPA ID:05508 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/161 | Replace transformer and LV cross arms on pole P36885 (T5/161). Existing transformer to be reused. Work Location: Forest Road, Kimbolton. Work Order 10160678 off 12:30 on 15:07 | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 157 | 154 | 308 | 0.00094076 | 6.1088e-06 | 2015-01-12 | B | 0.00047038 | 3.054e-06 | 2015 | 2015-01-12 | B | 2 | 0.00094076 | 6.1088e-06
1 | 4128655 | 2015-01-12 13:29 | 2015-01-12 16:04 | 155 | 92 | 10562 | 0.032303 | 0.00028137 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9380/2 | Sectionaliser 9380/2 on Paeroa CB5 feeder has locked out. 1 x A/R on recloser RC17 was followed by lockout on sectionaliser 9380/2. Line sectionalised & patrolled with no apparent fault found. All supply restored. No job was created by OMS from initial tr | F4 | BENNETT ST | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 114.8043 | 111.8043 | 10286 | 0.031418 | 0.00028101 | 2015-01-12 | C | 0.031418 | 0.00028101 | 2015 | 2015-01-12 | C | 92 | 0.031418 | 0.00028101
1 | 3614148 | 2015-01-13 04:41 | 2015-01-13 06:25 | 104.25 | 410 | 28092.1833 | 0.085918 | 0.001254 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT BIRD STRIKE | 380309 | CB 3 trip No Flags. Line Patrolled & Sectionalised. Lines twisted at pole 380309 - suspect bird strike. Recloser 9489 Batteries failed on Power off. Needs Batteries changed. Dave Ngatai attended. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 68.5175 | 65.5175 | 26862.1833 | 0.082048 | 0.0012523 | 2015-01-13 | C | 0.082048 | 0.0012523 | 2015 | 2015-01-13 | C | 410 | 0.082048 | 0.0012523
1 | 3240994 | 2015-01-13 08:21 | 2015-01-13 13:09 | 288.2333 | 39 | 11241.1 | 0.03438 | 0.00011928 | NAPA ID:05477 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C928 | 11kV Pole Replacement. Work Location: Whakatomotomo Road. Work Order 10141890 | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 288.2333 | 285.2333 | 11124.1 | 0.033978 | 0.00011912 | 2015-01-13 | B | 0.016989 | 5.9561e-05 | 2015 | 2015-01-13 | B | 39 | 0.033978 | 0.00011912
1 | 3383191 | 2015-01-13 08:31 | 2015-01-13 10:29 | 118.05 | 222 | 26207.1 | 0.080152 | 0.00067897 | NAPA ID:05723 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD4-727 | Isolate Switchgear - investigate & remedy source of discharge, Maintanence on Switchgear & 11kv Terms. Works Location: 235 Maungatapu Rd, Welcome Bay. WO 10162628. | F3 | MAUNGATAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 118.05 | 115.05 | 25541.1 | 0.078013 | 0.00067808 | 2015-01-13 | B | 0.039007 | 0.00033904 | 2015 | 2015-01-13 | B | 222 | 0.078013 | 0.00067808
1 | 3260891 | 2015-01-13 08:33 | 2015-01-13 14:06 | 332.7333 | 1 | 332.7333 | 0.0010176 | 3.0584e-06 | NAPA ID:05363 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P21019, P21016 | Replace cross arms from pole P21019 to P21016. Convert transformer structure T5/160 to a single pole structure. Replace transformer T5/160 with a new pole mount transformer. Work Location: Jens Road - located at the end of Beaconsfield Valley Road, Waitun | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 332.7333 | 329.7333 | 329.7333 | 0.0010071 | 3.0544e-06 | 2015-01-13 | B | 0.00050357 | 1.527e-06 | 2015 | 2015-01-13 | B | 1 | 0.0010071 | 3.0544e-06
1 | 3241059 | 2015-01-13 08:47 | 2015-01-13 12:58 | 250.7667 | 19 | 4764.5667 | 0.014572 | 5.811e-05 | NAPA ID:05403 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 796607 | Isolation of 11kV line for Treescape; Removal of trees around line. Work Location: Mangakukeke Road, Kahwatau Valley Road. PPPD 46537 | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 250.7667 | 247.7667 | 4707.5667 | 0.014379 | 5.8034e-05 | 2015-01-13 | B | 0.0071895 | 2.9017e-05 | 2015 | 2015-01-13 | B | 19 | 0.014379 | 5.8034e-05
1 | 3234680 | 2015-01-13 09:01 | 2015-01-13 15:16 | 375.6333 | 16 | 6010.1333 | 0.018382 | 4.8935e-05 | NAPA ID:05047 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV ABS 154 | 33/6.6kV Pole & Crossarm replacement Remove TEMP66. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 375.6333 | 372.6333 | 5962.1333 | 0.018211 | 4.8871e-05 | 2015-01-13 | B | 0.0091054 | 2.4435e-05 | 2015 | 2015-01-13 | B | 16 | 0.018211 | 4.8871e-05
1 | 3241168 | 2015-01-13 09:01 | 2015-01-13 13:25 | 264.1833 | 12 | 3170.2 | 0.0096958 | 3.6701e-05 | NAPA ID:05233 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE6-032 | CREATE LLWP GAP AT POLE 269466 [MAIN LINE POLE]. AP FOR HV ARMS AND POLE REPLACEMENT WORK ALSO RECONDUCTOR 9 SPANS. Work Location: State Highway 2, Te Tumu Road. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 264.1833 | 261.1833 | 3134.2 | 0.0095732 | 3.6653e-05 | 2015-01-13 | B | 0.0047866 | 1.8327e-05 | 2015 | 2015-01-13 | B | 12 | 0.0095732 | 3.6653e-05
1 | 3232923 | 2015-01-13 09:06 | 2015-01-13 15:05 | 358.8833 | 73 | 26198.4833 | 0.080126 | 0.00022326 | NAPA ID:05336 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS CA447 | Replace 11kv poles 720980, 720979, 720904, 720857, 720858, 720868, 720870, 720871, 720873, 720874, 720883. Works location: Austin Rd East and Turuturu Rd WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 358.8833 | 355.8833 | 25979.4833 | 0.079352 | 0.00022297 | 2015-01-13 | B | 0.039676 | 0.00011149 | 2015 | 2015-01-13 | B | 73 | 0.079352 | 0.00022297
1 | 3232914 | 2015-01-13 09:56 | 2015-01-13 14:19 | 262.65 | 18 | 4727.7 | 0.014459 | 5.5052e-05 | NAPA ID:05147 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole K1066 | Replace pole K1066. Works location: Reay and Watson Rd Tauhei Morrinsville WO 10161853 | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 262.65 | 259.65 | 4673.7 | 0.014275 | 5.498e-05 | 2015-01-13 | B | 0.0071377 | 2.749e-05 | 2015 | 2015-01-13 | B | 18 | 0.014275 | 5.498e-05
1 | 3241180 | 2015-01-13 10:30 | 2015-01-13 13:00 | 150 | 2 | 300 | 0.00091753 | 6.1168e-06 | NAPA ID:05263 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2439 | To replace the 11kV Leads to the top of Fuses TC2439. Replace TC2439 & LV Hardware. Work Location: 792 Kereone Road, Morrinsville. Work Order 10147832 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 150 | 147 | 294 | 0.000898 | 6.1088e-06 | 2015-01-13 | B | 0.000449 | 3.054e-06 | 2015 | 2015-01-13 | B | 2 | 0.000898 | 6.1088e-06
1 | 3619474 | 2015-01-14 | 2015-01-14 01:04 | 63.5667 | 11 | 652.2333 | 0.0019948 | 3.3643e-05 | Restore Supply on Device 7748 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T066 | Opussum found on lines at Pole - Cleared using hot sticks 3 HV fuses replaced at transformer T066 & two at Fuses 7748. | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 59.2939 | 56.2939 | 619.2333 | 0.0018914 | 3.3599e-05 | 2015-01-14 | C | 0.0018914 | 3.3599e-05 | 2015 | 2015-01-14 | C | 11 | 0.0018914 | 3.3599e-05
1 | 3619514 | 2015-01-14 06:43 | 2015-01-14 09:10 | 147.0333 | 84 | 5044.2 | 0.015427 | 0.00025691 | Restore Supply on Device IC3075 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LC2329 | at 08:10, Piako Sub, CB 1 Morrinsville North Feeder. Part power & no power calls coming in from customers. Found broken Jumper at Links LC2329. Isolated Lines at Links LC2329 & Sw/gear IC3075. Permit Issued & Repairs carried out. All power restored on com | F3 | MVILLE NORTH | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 60.05 | 57.05 | 4792.2 | 0.014637 | 0.00025657 | 2015-01-14 | C | 0.014637 | 0.00025657 | 2015 | 2015-01-14 | C | 84 | 0.014637 | 0.00025657
1 | 3358830 | 2015-01-14 08:01 | 2015-01-14 16:14 | 492.6833 | 14 | 6897.5667 | 0.021096 | 4.2818e-05 | NAPA ID:04423 TP_GREYTOWN GXP > KEMPTON SUB > WEST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T107, 818494 | Isolate T107 replace 11kV transformer and pole live line. Work Location: West Street, Greytown. Work Order 10140873 | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 492.6833 | 489.6833 | 6855.5667 | 0.02094 | 4.2762e-05 | 2015-01-14 | B | 0.01047 | 2.1381e-05 | 2015 | 2015-01-14 | B | 14 | 0.02094 | 4.2762e-05
1 | 3494933 | 2015-01-14 08:45 | 2015-01-14 12:36 | 230.8833 | 12 | 2770.6 | 0.0084737 | 3.6701e-05 | NAPA ID:05404 TP_GREYTOWN GXP > TUHITARATA SUB > PIRINOA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1321 | At transformer replace structure and transformer also. Works location: Raho Raho Rd, Pirinoa. WO 10151981 | F4 | PIRINOA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 230.8833 | 227.8833 | 2734.6 | 0.0083526 | 3.6653e-05 | 2015-01-14 | B | 0.0041763 | 1.8327e-05 | 2015 | 2015-01-14 | B | 12 | 0.0083526 | 3.6653e-05
1 | 3232903 | 2015-01-14 08:51 | 2015-01-14 14:59 | 368.2167 | 61 | 22461.2167 | 0.068696 | 0.00018656 | NAPA ID:03876 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC933 | Repole,rearm,& reconductor 11kV. Works location: Old Taupo Rd WO 10151890 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 368.2167 | 365.2167 | 22278.2167 | 0.068047 | 0.00018632 | 2015-01-14 | B | 0.034024 | 9.316e-05 | 2015 | 2015-01-14 | B | 61 | 0.068047 | 0.00018632
1 | 3245332 | 2015-01-14 09:00 | 2015-01-14 14:26 | 326 | 45 | 14670 | 0.044867 | 0.00013763 | NAPA ID:05235 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE6-166 | REPLACE HV POLES AND CROSS ARMS READY FOR RECONDUCTOR WORK. Work Location: State Highway 2 Te Tumu Road. | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 326 | 323 | 14535 | 0.044396 | 0.00013745 | 2015-01-14 | B | 0.022198 | 6.8725e-05 | 2015 | 2015-01-14 | B | 45 | 0.044396 | 0.00013745
1 | 3234681 | 2015-01-14 09:00 | 2015-01-14 15:40 | 399.95 | 16 | 6399.2 | 0.019571 | 4.8935e-05 | NAPA ID:05048 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV ABS 154 | 33/6.6kV Pole & Crossarm replacement. Works location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 399.95 | 396.95 | 6351.2 | 0.019399 | 4.8871e-05 | 2015-01-14 | B | 0.0096996 | 2.4435e-05 | 2015 | 2015-01-14 | B | 16 | 0.019399 | 4.8871e-05
1 | 3232908 | 2015-01-14 09:00 | 2015-01-14 15:48 | 407.6833 | 10 | 4076.8333 | 0.012469 | 3.0584e-05 | NAPA ID:03123 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2837, TC2467 | To replace poles and upgrade conductors. Work Location: Old Taupo Road. Work Order 10162189 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 407.6833 | 404.6833 | 4046.8333 | 0.012361 | 3.0544e-05 | 2015-01-14 | B | 0.0061804 | 1.5272e-05 | 2015 | 2015-01-14 | B | 10 | 0.012361 | 3.0544e-05
1 | 3260125 | 2015-01-14 09:15 | 2015-01-14 15:28 | 373.0167 | 3 | 1119.05 | 0.0034225 | 9.1753e-06 | NAPA ID:05489 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C928 | Reconductoring. Work Location: Te Rata Road. Work Order: 10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 373.0167 | 370.0167 | 1110.05 | 0.0033906 | 9.1633e-06 | 2015-01-14 | B | 0.0016953 | 4.582e-06 | 2015 | 2015-01-14 | B | 3 | 0.0033906 | 9.1633e-06
1 | 3245387 | 2015-01-14 09:31 | 2015-01-14 15:30 | 358.3167 | 18 | 6449.7 | 0.019726 | 5.5052e-05 | NAPA ID:05415 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P11576, P11577, P07812 | Replace 11kV X-Arms on 2-pole structure P11576 & P11577. This includes installing new DDO's for 11kV fuse N27. Remove existing stub pole and replace with deadman anchor. Replace LV and TX (T5/66) x-arms on pole P07812. Existing TX to be reused. Work Locat | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 358.3167 | 355.3167 | 6395.7 | 0.019535 | 5.498e-05 | 2015-01-14 | B | 0.0097676 | 2.749e-05 | 2015 | 2015-01-14 | B | 18 | 0.019535 | 5.498e-05
1 | 3620914 | 2015-01-14 12:04 | 2015-01-14 12:46 | 42 | 2309 | 92627 | 0.28329 | 0.0070619 | Restore Supply on Device 220 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 220 | at 12:04, Motukawa Sub, CB 220 Tripped, No Flags, L/O. Loss of Supply to Inglewood Sub as Inglewood was being supplied from Motukawa CB 220 due to Transpower Works at Huirangi and Also Northpower Working on the McKee - Inglewood 33kV Line. Faultmen dispat | F1, F2, F3 | INGLEWOOD SOUTH 33KV | MOTUKAWA 33 SW | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 40.1156 | 37.1156 | 85700 | 0.26176 | 0.0070527 | 2015-01-14 | C | 0.26176 | 0.0070527 | 2015 | 2015-01-14 | C | 2309 | 0.26176 | 0.0070527
1 | 3623491 | 2015-01-14 21:18 | 2015-01-14 23:38 | 140.4 | 235 | 11839.4667 | 0.03621 | 0.00071873 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 780041 | Nicole from Genesis refused to submit a job on behalf of her caller but advises that the lady (would not provide her name or contact ph number) witnessed a bird fly into the lines at 187 Marahau Road, Maxwell. Another unknown caller advised pole fuse dow | F4 | MAXWELL | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 50.3807 | 47.3807 | 11134.4667 | 0.034009 | 0.00071779 | 2015-01-14 | C | 0.034009 | 0.00071779 | 2015 | 2015-01-14 | C | 235 | 0.034009 | 0.00071779
1 | 3623766 | 2015-01-14 23:14 | 2015-01-15 00:56 | 101.8667 | 1 | 101.8667 | 0.00031155 | 3.0584e-06 | Restore Supply on Device G135 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Sub G152 | CB tripped at Sub G152 - rest and monitored for 10 min with no issues. | F2 | PASCAL ST 8 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 101.8667 | 98.8667 | 98.8667 | 0.00030198 | 3.0544e-06 | 2015-01-14 | C | 0.00030198 | 3.054e-06 | 2015 | 2015-01-14 | C | 1 | 0.00030198 | 3.0544e-06
1 | 3234682 | 2015-01-15 08:45 | 2015-01-15 15:27 | 402.2 | 42 | 16892.4 | 0.051664 | 0.00012845 | NAPA ID:05045 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 33kV ABS 154 | 33/6.6kV Pole & Crossarm replacement. WOrks location: Bristol Rd Waitara WO 10161253 | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 402.2 | 399.2 | 16766.4 | 0.051212 | 0.00012829 | 2015-01-15 | B | 0.025606 | 6.4143e-05 | 2015 | 2015-01-15 | B | 42 | 0.051212 | 0.00012829
1 | 3260901 | 2015-01-15 08:50 | 2015-01-15 13:34 | 284.3667 | 39 | 11090.3 | 0.033919 | 0.00011928 | NAPA ID:05478 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | ABS S538 | 11kV Pole Replacement. Work Location: Whakatomotomo Road. Work Order:10141890. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 284.3667 | 281.3667 | 10973.3 | 0.033517 | 0.00011912 | 2015-01-15 | B | 0.016759 | 5.9561e-05 | 2015 | 2015-01-15 | B | 39 | 0.033517 | 0.00011912
1 | 3232909 | 2015-01-15 09:00 | 2015-01-15 16:01 | 420.55 | 10 | 4205.5 | 0.012862 | 3.0584e-05 | NAPA ID:03125 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M1263, M12428 | To replace 11kV conductor Old Taupo Road Between Pole # M1263 and M12428. Work Order 10162189 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 420.55 | 417.55 | 4175.5 | 0.012754 | 3.0544e-05 | 2015-01-15 | B | 0.0063769 | 1.5272e-05 | 2015 | 2015-01-15 | B | 10 | 0.012754 | 3.0544e-05
1 | 3260127 | 2015-01-15 09:00 | 2015-01-15 12:35 | 215 | 45 | 9675 | 0.02959 | 0.00013763 | NAPA ID:05243 TP_TE MATAI GXP > TE PUKE SUB > MAKETU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SP-012 | REPLACE HV POLES AND CROSS ARMS READY FOR RECONDUCTOR WORK. Work Location: State Highway 2, Te Tumu Road. WO NA | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 215 | 212 | 9540 | 0.029139 | 0.00013745 | 2015-01-15 | B | 0.01457 | 6.8725e-05 | 2015 | 2015-01-15 | B | 45 | 0.029139 | 0.00013745
1 | 3493933 | 2015-01-15 09:02 | 2015-01-15 13:56 | 294 | 91 | 26754 | 0.081825 | 0.00027832 | NAPA ID:05573 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | Replace poles and hardware on poles 726648, 722656, 726614, 726615, 726617, 726619 and 726621 | F3 | PORTLAND QUAY | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 294 | 291 | 26481 | 0.080884 | 0.00027795 | 2015-01-15 | B | 0.040442 | 0.00013898 | 2015 | 2015-01-15 | B | 91 | 0.080884 | 0.00027795
1 | 3624467 | 2015-01-15 09:21 | 2015-01-15 11:57 | 155.7167 | 79 | 12301.6167 | 0.037624 | 0.00024162 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 9525/2 | This outage needs investigation as no customers should be affected but during planned switching CB7 operated and L/O. Labelling on switch 9524/1 and9524/3 were transposed on the SCADA tile. The 79 ICPs on this outage were not included in isolated work ar | F2 | PAPAMOA JUNCTION | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 155.7167 | 152.7167 | 12064.6167 | 0.03685 | 0.0002413 | 2015-01-15 | C | 0.03685 | 0.0002413 | 2015 | 2015-01-15 | C | 79 | 0.03685 | 0.0002413
1 | 3364159 | 2015-01-15 09:24 | 2015-01-15 13:54 | 270.0167 | 9 | 2430.15 | 0.0074324 | 2.7526e-05 | NAPA ID:05199 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/412 | Remove 1 pole of 2 pole structure replace Transformer T3/412. Works Location: Junction Rd, Halcombe. WO 10149420. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 270.0167 | 267.0167 | 2403.15 | 0.0073402 | 2.749e-05 | 2015-01-15 | B | 0.0036701 | 1.3745e-05 | 2015 | 2015-01-15 | B | 9 | 0.0073402 | 2.749e-05
1 | 3624769 | 2015-01-15 09:34 | 2015-01-15 10:14 | 40 | 773 | 30920 | 0.094566 | 0.0023642 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 9524/3 | Part of verified outage on oms 3624467, possibly feeder fault but no comms on feeder currently. 10.30am power now restored, control to deal with this job. CB 7 tripped on E/F while switching on NAPA 5725. Comms to sub out at tme due to changing radio freq | F2 | PAPAMOA JUNCTION | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 28601 | 0.08736 | 0.0023611 | 2015-01-15 | C | 0.08736 | 0.0023611 | 2015 | 2015-01-15 | C | 773 | 0.08736 | 0.0023611
1 | 3260871 | 2015-01-15 09:50 | 2015-01-15 15:00 | 310 | 3 | 930 | 0.0028443 | 9.1753e-06 | NAPA ID:05529 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/82, P49955 | Replace TX and LV X-Arms on pole P49955 (T5/82). Existing TX to be reused. Replace LV X-Arms on the following LV pole numbers: P07037, P07036, P07035, P07034 & P07033. Work Location: Waipuru Road, Rangiwahia. Work Order 10160678 | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 310 | 307 | 921 | 0.0028131 | 9.1633e-06 | 2015-01-15 | B | 0.0014066 | 4.582e-06 | 2015 | 2015-01-15 | B | 3 | 0.0028131 | 9.1633e-06
1 | 3626952 | 2015-01-15 17:51 | 2015-01-16 15:12 | 1280.3333 | 1 | 1280.3333 | 0.0039158 | 3.0584e-06 | Restore Supply on Device 4120T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4119T | Transformer 4119T blown and requires replacement tomorrow. Jade will follow this up this up with Dennis Embling tomorrow. Adjacent assets. Whole structure deteriorated including cross arms & earths require upgrading. One other property at the top of the | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1280.3333 | 1277.3333 | 1277.3333 | 0.0039015 | 3.0544e-06 | 2015-01-15 | C | 0.0039015 | 3.054e-06 | 2015 | 2015-01-15 | C | 1 | 0.0039015 | 3.0544e-06
1 | 3626975 | 2015-01-15 18:33 | 2015-01-15 20:11 | 98 | 1 | 19.4667 | 5.9537e-05 | 3.0584e-06 | Restore Supply on Device 5247E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5247E | Replace blown transformer 5247E as per details on OMS 3626963. Isolated via transformer fuses. Green box is leaking oil on the pole and smells burnt out - please check for safety -no power to Irrigation pump. 6:36 advised Leanne at the hub Tx on pole rel | F1 | MANAIA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 19.4667 | 16.4667 | 16.4667 | 5.0296e-05 | 3.0544e-06 | 2015-01-15 | C | 5.0296e-05 | 3.054e-06 | 2015 | 2015-01-15 | C | 1 | 5.0296e-05 | 3.0544e-06
1 | 3627026 | 2015-01-16 05:26 | 2015-01-16 06:48 | 81.7 | 761 | 54901.9 | 0.16791 | 0.0023275 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB8 | Line patrolled with no apparent fault found ... suspect bird strike | F3 | KATERE 8 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 72.1444 | 69.1444 | 52618.9 | 0.16072 | 0.0023244 | 2015-01-16 | C | 0.16072 | 0.0023244 | 2015 | 2015-01-16 | C | 761 | 0.16072 | 0.0023244
1 | 3384626 | 2015-01-16 09:18 | 2015-01-16 15:24 | 365.2167 | 39 | 14243.45 | 0.043562 | 0.00011928 | NAPA ID:05540 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | p04267, p04268, p02656 | To change 11kv poles and to install temp abs at H structure p04267 &p04268 and install temp fuses 69 at pole p02656. Works Location: Huia Rd and Waihoki Valley Rd, Pongaroa. WO 10134517 | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 365.2167 | 362.2167 | 14126.45 | 0.043148 | 0.00011912 | 2015-01-16 | B | 0.021574 | 5.9561e-05 | 2015 | 2015-01-16 | B | 39 | 0.043148 | 0.00011912
1 | 3650790 | 2015-01-16 09:50 | 2015-01-16 16:17 | 387 | 11 | 4257 | 0.01302 | 3.3643e-05 | Restore Supply on Device 5453 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 5453 | Part of planned job 6281 on OMS 3626838. Re-staged event duwe to SCADA dressing issue. Power off: 16/01/15 @ 0950. Power on: 16/01/15 @ 16:17 | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 387 | 384 | 4224 | 0.012902 | 3.3599e-05 | 2015-01-16 | C | 0.012902 | 3.3599e-05 | 2015 | 2015-01-16 | C | 11 | 0.012902 | 3.3599e-05
1 | 4241842 | 2015-01-16 10:52 | 2015-01-16 17:23 | 391 | 1020 | 179644 | 0.54943 | 0.0031196 | Restore Supply on Device 5032 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | V30 | Breaker tripped patrol required . Found faulty CT on Pole740908 which was then removed from Network | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 176.1216 | 173.1216 | 176584 | 0.53936 | 0.0031155 | 2015-01-16 | C | 0.53936 | 0.0031155 | 2015 | 2015-01-16 | C | 1020 | 0.53936 | 0.0031155
1 | 3630881 | 2015-01-16 12:09 | 2015-01-16 12:37 | 28 | 764 | 21392 | 0.065426 | 0.0023366 | Restore Supply on Device U20 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB U20 | Trippped due to GFN operation, no fault | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 19100 | 0.058339 | 0.0023336 | 2015-01-16 | C | 0.058339 | 0.0023336 | 2015 | 2015-01-16 | C | 764 | 0.058339 | 0.0023336
1 | 3396121 | 2015-01-16 22:19 | 2015-01-16 23:55 | 96.4333 | 74 | 7136.0667 | 0.021825 | 0.00022632 | NAPA ID:05721 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 12 | 6600 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G31 | Replace oil on 11 Kv Tx G31T (high Moisture & Acitdy Content in the oil) Shutdown. Required No LV backfeed. Works Location: 6 Henere St, Palmerston North. WO 10157370. | F2 | PASCAL ST LS | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 96.4333 | 93.4333 | 6914.0667 | 0.021118 | 0.00022603 | 2015-01-16 | B | 0.010559 | 0.00011301 | 2015 | 2015-01-16 | B | 74 | 0.021118 | 0.00022603
1 | 3638191 | 2015-01-17 05:56 | 2015-01-17 07:22 | 86 | 49 | 3998 | 0.012228 | 0.00014986 | Restore Supply on Device C843 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C843 | Trip on CB C843. Feeder patrolled and sectionalised but all restored OK. OMS job complete but CB tripped later (Refer OMS 3638271). | F5 | ROROKOKO | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 81.5918 | 78.5918 | 3851 | 0.011763 | 0.00014967 | 2015-01-17 | C | 0.011763 | 0.00014967 | 2015 | 2015-01-17 | C | 49 | 0.011763 | 0.00014967
1 | 3638271 | 2015-01-17 07:59 | 2015-01-17 08:47 | 48 | 49 | 2154 | 0.0065878 | 0.00014986 | Restore Supply on Device C843 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C843 | Tripping on CB C843 (2nd fault - refer OMS 3638191). patrolled / sectionailised but all restored. Ongoing problem, fault locators fitted by Gavin and Adam. | F5 | ROROKOKO | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 43.9592 | 40.9592 | 2007 | 0.0061302 | 0.00014967 | 2015-01-17 | C | 0.0061302 | 0.00014967 | 2015 | 2015-01-17 | C | 49 | 0.0061302 | 0.00014967
1 | 3638501 | 2015-01-17 09:59 | 2015-01-17 11:44 | 105 | 854 | 31241.5333 | 0.09555 | 0.0026119 | Restore Supply on Device S31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 734511 | Tripping on 11kV Cloton Rd CB S31. (Backfeed to CB6616 in place from NOC). Fault located on Flint Rd Upper with 2 blown insulators replaced. All relivened OK. (Isolation from ABS 5671) | F4 | CLOTON RD NORTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 36.5826 | 33.5826 | 28679.5333 | 0.087599 | 0.0026085 | 2015-01-17 | C | 0.087599 | 0.0026085 | 2015 | 2015-01-17 | C | 854 | 0.087599 | 0.0026085
1 | 3640010 | 2015-01-17 11:04 | 2015-01-17 11:54 | 50.1 | 9 | 103.8333 | 0.00031757 | 2.7526e-05 | Restore Supply on Device 716 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8295 | Tripping on Fuses 8295 caused by bird strike. 2 * 10A HV Fuses replaced. Relivened OK. Neil Woodhead attended. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 11.537 | 8.537 | 76.8333 | 0.00023468 | 2.749e-05 | 2015-01-17 | C | 0.00023468 | 2.749e-05 | 2015 | 2015-01-17 | C | 9 | 0.00023468 | 2.749e-05
1 | 3640024 | 2015-01-17 13:04 | 2015-01-17 14:25 | 80.7 | 4 | 322.8 | 0.00098726 | 1.2234e-05 | Restore Supply on Device 3163T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 762826 | Initially found one fuse tripped at 5206. Farmers tree branch in line required isolation from Fuses 5206 to cut away. Restored OK including replacement of 1 DDO. NDR 43769. Paul Sullivan attended. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80.7 | 77.7 | 310.8 | 0.00094931 | 1.2218e-05 | 2015-01-17 | C | 0.00094931 | 1.2218e-05 | 2015 | 2015-01-17 | C | 4 | 0.00094931 | 1.2218e-05
1 | 3640251 | 2015-01-17 18:17 | 2015-01-17 18:42 | 25.3 | 1 | 25.3 | 7.7378e-05 | 3.0584e-06 | Restore Supply on Device T1/187 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | L82 | Isolation required from Fuses L82 to repair a broken Jumper at those Fuses. Relivened OK. Anjay Prasad attended. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 25.3 | 22.3 | 22.3 | 6.8114e-05 | 3.0544e-06 | 2015-01-17 | C | 6.8114e-05 | 3.054e-06 | 2015 | 2015-01-17 | C | 1 | 6.8114e-05 | 3.0544e-06
1 | 3640288 | 2015-01-18 04:16 | 2015-01-18 04:31 | 15 | 163 | 2445 | 0.0074778 | 0.00049852 | Restore Supply on Device RC4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | RC04 | RC04 Tripped E/F - Not Patrolled | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 1956 | 0.0059745 | 0.00049787 | 2015-01-18 | C | 0.0059745 | 0.00049787 | 2015 | 2015-01-18 | C | 163 | 0.0059745 | 0.00049787
1 | 3640851 | 2015-01-18 08:31 | 2015-01-18 08:37 | 6 | 904 | 5424 | 0.016589 | 0.0027648 | Restore Supply on Device CB2762 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 737474 | Tripping on SFD 33kV CB2762 causing loss of supply to Douglas & Starathmore Subs. (backfed OK from NOC via VS6298). 33kV Broken Conductor found down outside 63 Douglas Rd caused by Bird strike (Dead Magpie under line). Isolation required from Douglas sub | F1, F2, F3 | DOUGLAS 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 6 | 3 | 2712 | 0.0082836 | 0.0027612 | 2015-01-18 | C | 0.0082836 | 0.0027612 | 2015 | 2015-01-18 | C | 904 | 0.0082836 | 0.0027612
1 | 3395798 | 2015-01-18 09:10 | 2015-01-18 16:04 | 413.7333 | 52 | 21446.2833 | 0.065592 | 0.00015904 | NAPA ID:02193 TP_OHAKUNE GXP > TP_OHAKUNE > RAETIHI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Y119 | Install new poles and re-sag conductors. Work Location: Ruatiti Road, Raetihi. Work Order 10160182 | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 412.4285 | 409.4285 | 21290.2833 | 0.06503 | 0.00015883 | 2015-01-18 | B | 0.032515 | 7.9415e-05 | 2015 | 2015-01-18 | B | 52 | 0.06503 | 0.00015883
1 | 3357571 | 2015-01-18 09:36 | 2015-01-18 12:23 | 167.0667 | 14 | 2338.9333 | 0.0071534 | 4.2818e-05 | NAPA ID:05505 TP_CARRINGTON GXP > CITY SUB > CITY 10 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 751801 | To change high voltage pole 751801 hit by car. Work Location: 99 Lemon Street. Work Order 10162739. | F3 | CITY 10 | CITY SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 167.0667 | 164.0667 | 2296.9333 | 0.0070158 | 4.2762e-05 | 2015-01-18 | B | 0.0035079 | 2.1381e-05 | 2015 | 2015-01-18 | B | 14 | 0.0070158 | 4.2762e-05
1 | 3395819 | 2015-01-18 10:20 | 2015-01-18 13:47 | 206.6 | 4 | 826.4 | 0.0025275 | 1.2234e-05 | NAPA ID:05727 TP_MT MAUNGANUI 33 GXP > TRITON SUB > HEWLETTS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Sc4-724 | Investigate possible faulty fuse sw SC4-724. Maint on Switch unit and 11kv Terms. Works Location: 124 Hewletts Rd, Mt Maunganui. WO 30001392. | F2 | HEWLETTS RD | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 206.6 | 203.6 | 814.4 | 0.0024875 | 1.2218e-05 | 2015-01-18 | B | 0.0012438 | 6.109e-06 | 2015 | 2015-01-18 | B | 4 | 0.0024875 | 1.2218e-05
1 | 3641895 | 2015-01-18 10:59 | 2015-01-18 12:45 | 106.5333 | 1 | 106.5333 | 0.00032582 | 3.0584e-06 | Restore Supply on Device T1339 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 797673 | replace 1 x 3 amp ddo fuse. 1 out of 2 phases. pole # 797673. cause: unknown. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106.5333 | 103.5333 | 103.5333 | 0.00031623 | 3.0544e-06 | 2015-01-18 | C | 0.00031623 | 3.054e-06 | 2015 | 2015-01-18 | C | 1 | 0.00031623 | 3.0544e-06
1 | 3642005 | 2015-01-18 17:40 | 2015-01-19 15:52 | 1331.7833 | 2 | 738.6 | 0.002259 | 6.1168e-06 | Restore Supply on Device TC5063 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | FC2459 | H/V fuse x 1 was replace & blew straight away. Suspect H/V cable fault ( singles ) customer happy to be left off over night. To be attended in morning. Cable isolated at fuses FC2459, Testing & repairs carried out. Materials Cable Joint kit & conductor. | F4 | PURIRI | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 369.3 | 366.3 | 732.6 | 0.0022377 | 6.1088e-06 | 2015-01-18 | C | 0.0022377 | 6.109e-06 | 2015 | 2015-01-18 | C | 2 | 0.0022377 | 6.1088e-06
1 | 3642168 | 2015-01-18 18:45 | 2015-01-19 14:45 | 1199.7667 | 855 | 39426.9167 | 0.12058 | 0.002615 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 783257 | Too Dark to carry on looking as line goes cross country Roger will back on Site at 6 am in morning. First we had O/C A & B Phase Trip Flag at Sectioniser 2713 But it did not open and CB 4 & Recloser 575 opened Traced the fault down to after Fuses 909 Af | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 46.1134 | 43.1134 | 36861.9167 | 0.11259 | 0.0026115 | 2015-01-18 | C | 0.11259 | 0.0026115 | 2015 | 2015-01-18 | C | 855 | 0.11259 | 0.0026115
1 | 3644654 | 2015-01-19 01:14 | 2015-01-19 05:06 | 231.1167 | 2465 | 116521.2833 | 0.35637 | 0.007539 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cable between Sw/gear SC4-500 & S5453, Blow jumpers at Pole 213672 | * CB3 tripped L/O ( no flags ) Feeder sectionalised. * When attempting a close of ABS SC4 069 noticed arcing jumper where U/G cable joins at ABS SC4 069 from Sw/gear S5834. Pole 213672. Suspected to be a secondary fault. * ABS SC4 069 left open & Tagge | F2 | CENTRAL TRITON | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 47.2703 | 44.2703 | 109126.2833 | 0.33332 | 0.0075292 | 2015-01-19 | C | 0.33332 | 0.0075292 | 2015 | 2015-01-19 | C | 2465 | 0.33332 | 0.0075292
1 | 3373200 | 2015-01-19 08:51 | 2015-01-19 15:36 | 404.7167 | 42 | 16998.1 | 0.051987 | 0.00012845 | NAPA ID:05606 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 12 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 751202 | Replace pole mount transformer to a ground mount transformer. Works Location: Mangorei Rd, New Plymouth. WO 10149207. | F3 | BROOKLANDS 12 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 404.7167 | 401.7167 | 16872.1 | 0.051535 | 0.00012829 | 2015-01-19 | B | 0.025767 | 6.4143e-05 | 2015 | 2015-01-19 | B | 42 | 0.051535 | 0.00012829
1 | 3397327 | 2015-01-19 09:05 | 2015-01-19 15:05 | 360 | 16 | 5760 | 0.017617 | 4.8935e-05 | NAPA ID:05049 TP_HUIRANGI GXP > INGLEWOOD SUB > BRISTOL RD | 6600 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 760444 | 33/6.6kV Pole & Cross arm replacement. Work Location: Bristol Road, Waitara. Work Order: 10161253. | F4 | BRISTOL RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 360 | 357 | 5712 | 0.017447 | 4.8871e-05 | 2015-01-19 | B | 0.0087234 | 2.4435e-05 | 2015 | 2015-01-19 | B | 16 | 0.017447 | 4.8871e-05
1 | 3373178 | 2015-01-19 09:30 | 2015-01-19 11:51 | 140.75 | 175 | 24631.25 | 0.075333 | 0.00053522 | NAPA ID:05604 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726195 | Replace crossarm and hardware on network pole 726195. Works Location: Cnr of Devon and Norfolk Streets, Patea. WO 10163052. | F3 | PORTLAND QUAY | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 140.75 | 137.75 | 24106.25 | 0.073631 | 0.00053452 | 2015-01-19 | B | 0.036815 | 0.00026726 | 2015 | 2015-01-19 | B | 175 | 0.073631 | 0.00053452
1 | 3358855 | 2015-01-19 09:33 | 2015-01-19 15:02 | 329.45 | 33 | 10459.05 | 0.031988 | 0.00010093 | NAPA ID:05597 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 716288 | Replace ABS TA803 & cross arms. Work Location: Skeet Road. Work Order 10163264 | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 316.9409 | 313.9409 | 10360.05 | 0.031644 | 0.0001008 | 2015-01-19 | B | 0.015822 | 5.0398e-05 | 2015 | 2015-01-19 | B | 33 | 0.031644 | 0.0001008
1 | 3650665 | 2015-01-19 13:48 | 2015-01-19 16:28 | 159.9833 | 2 | 270.25 | 0.00082654 | 6.1168e-06 | Restore Supply on Device X2606 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843675 | o/h hv 2x 20amp ddo fuses. pole 843675. Full power restored. Nothing else repaired or replaced. Adjacent assets - ok | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 135.125 | 132.125 | 264.25 | 0.00080713 | 6.1088e-06 | 2015-01-19 | C | 0.00080713 | 6.109e-06 | 2015 | 2015-01-19 | C | 2 | 0.00080713 | 6.1088e-06
1 | 3650719 | 2015-01-19 14:56 | 2015-01-19 18:44 | 227.9667 | 42 | 9574.6 | 0.029283 | 0.00012845 | Restore Supply on Device 443 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | O2974 | Car Versus Pole O2974. CB 6 A/R at 1354 A,B O/C E/F. Fire notify powerco of accident. Fire event number F1769047. Isolation at ABS's 443 & 472 Back feed from KPE CB 1Via Sw/Gear 9045/1. NDR# 31554. Material 11m concrete pole, single HV & LV crossarm + Ins | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 227.9667 | 224.9667 | 9448.6 | 0.02886 | 0.00012829 | 2015-01-19 | C | 0.02886 | 0.00012829 | 2015 | 2015-01-19 | C | 42 | 0.02886 | 0.00012829
1 | 3650865 | 2015-01-19 17:44 | 2015-01-19 18:26 | 42.7 | 1358 | 27237.9333 | 0.083305 | 0.0041533 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 215257 | CB 3 Trip. Recloser 9412 Opened Recloser 9462 closed. Back feed from CB8 Papamoa. Bird on pole 215257. Bird removed by hotstick and feeder relivened. David Joynt attended. | F3 | WELCOME BAY | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 20.0574 | 17.0574 | 23163.9333 | 0.070752 | 0.0041479 | 2015-01-19 | C | 0.070752 | 0.0041479 | 2015 | 2015-01-19 | C | 1358 | 0.070752 | 0.0041479
1 | 3410560 | 2015-01-20 00:02 | 2015-01-20 02:56 | 174.3833 | 136 | 23716.1333 | 0.072534 | 0.00041595 | NAPA ID:05759 TP_MT MAUNGANUI 33 GXP > TRITON SUB > CENTRAL TRITON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-197, TC4-192 | Isolate Switchgear SC4-803-807 and investigate faulty indication on switch SC4-803. Works Location: Cnr Maunganui Rd & Grove Ave, Mt Maunganui. WO 30001260. | F2 | CENTRAL TRITON | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 174.3833 | 171.3833 | 23308.1333 | 0.071193 | 0.0004154 | 2015-01-20 | B | 0.035596 | 0.0002077 | 2015 | 2015-01-20 | B | 136 | 0.071193 | 0.0004154
1 | 3652689 | 2015-01-20 00:44 | 2015-01-20 03:01 | 137 | 178 | 16168 | 0.049449 | 0.0005444 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND |  | ATU CB6 tripped Neut O/C, A Ph O/C, E/F, L/O. Feeder sectionalised ( no back feeds ). No fault found no rain or wind suspect Possum | F1/F4 | TE PUKE QUARRY RD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 90.8315 | 87.8315 | 15634 | 0.047753 | 0.00054369 | 2015-01-20 | C | 0.047753 | 0.00054369 | 2015 | 2015-01-20 | C | 178 | 0.047753 | 0.00054369
1 | 3232913 | 2015-01-20 08:45 | 2015-01-20 14:35 | 349.8333 | 61 | 20990 | 0.064196 | 0.00018656 | NAPA ID:03877 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC933 | Repole,rearm,& reconductor 11kV. Works location: Old Taupo Rd. WO 10151890. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 344.0984 | 341.0984 | 20807 | 0.063553 | 0.00018632 | 2015-01-20 | B | 0.031777 | 9.316e-05 | 2015 | 2015-01-20 | B | 61 | 0.063553 | 0.00018632
1 | 3232935 | 2015-01-20 08:54 | 2015-01-20 14:32 | 338.4333 | 38 | 12860.4667 | 0.039333 | 0.00011622 | NAPA ID:05376 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS CA421 | Replace 22, 11kv poles. Works location: Ohangai Rd Normanby WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 338.4333 | 335.4333 | 12746.4667 | 0.038933 | 0.00011607 | 2015-01-20 | B | 0.019467 | 5.8034e-05 | 2015 | 2015-01-20 | B | 38 | 0.038933 | 0.00011607
1 | 3398403 | 2015-01-20 08:58 | 2015-01-20 10:05 | 66.8 | 3 | 200.4 | 0.00061291 | 9.1753e-06 | NAPA ID:05733 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-032, SF6-033 | Maintanence on 11kv Linkbox - SF6-032 - SF6-033. Works Location: Penderel Rd, Rangiuru. WO 10143066. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 66.8 | 63.8 | 191.4 | 0.00058462 | 9.1633e-06 | 2015-01-20 | B | 0.00029231 | 4.582e-06 | 2015 | 2015-01-20 | B | 3 | 0.00058462 | 9.1633e-06
1 | 3360620 | 2015-01-20 09:09 | 2015-01-20 16:00 | 410.4333 | 165 | 66752.9333 | 0.20416 | 0.00050464 | NAPA ID:05497 TP_TAURANGA 33 GXP > MATUA SUB > BELLEVUE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 202388 | REPLACE MAIN LINE POLE AND ONE OTHER. RECONDUCTOR THE HV NETWORK. WOKR LCOATION: ANNE RD PPPD. IR4838 | F3 | BELLEVUE RD | MATUA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 404.5632 | 401.5632 | 66257.9333 | 0.20238 | 0.00050398 | 2015-01-20 | B | 0.10119 | 0.00025199 | 2015 | 2015-01-20 | B | 165 | 0.20238 | 0.00050398
1 | 3260726 | 2015-01-20 09:21 | 2015-01-20 12:57 | 216.3167 | 438 | 94111.1833 | 0.28783 | 0.0013396 | NAPA ID:03758 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D0907, IC871 | Replace Pole number D0907 and replace 11kV ABS IC871 complete with termination arms under shut down conditions. Work Location: Plantation Road. Work Order 484459 | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 214.8657 | 211.8657 | 92797.1833 | 0.28344 | 0.0013378 | 2015-01-20 | B | 0.14172 | 0.00066892 | 2015 | 2015-01-20 | B | 438 | 0.28344 | 0.0013378
1 | 3398045 | 2015-01-20 09:32 | 2015-01-20 13:21 | 229.0333 | 196 | 44890.5333 | 0.13729 | 0.00059945 | NAPA ID:05405 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 819870 | Replace cracked cross arms and replace ABS with new 600Amp switch. Works Location: Kokotau Road, Carterton. WO 10155779. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 229.0333 | 226.0333 | 44302.5333 | 0.13532 | 0.00059867 | 2015-01-20 | B | 0.067659 | 0.00029933 | 2015 | 2015-01-20 | B | 196 | 0.13532 | 0.00059867
1 | 3398409 | 2015-01-20 11:32 | 2015-01-20 12:16 | 43.9167 | 5 | 219.5833 | 0.00067158 | 1.5292e-05 | NAPA ID:05734 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-025 | Maintanence on 11kv Linkbox - SF6-025. Works Location: 76 Oak Drive, Rangiuru, Te Puke. WO 10143066 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 43.9167 | 40.9167 | 204.5833 | 0.00062488 | 1.5272e-05 | 2015-01-20 | B | 0.00031244 | 7.636e-06 | 2015 | 2015-01-20 | B | 5 | 0.00062488 | 1.5272e-05
1 | 3654930 | 2015-01-20 12:14 | 2015-01-20 12:40 | 26 | 17 | 442 | 0.0013518 | 5.1993e-05 | Restore Supply on Device cut side 1 temp line [1341,0,100,0] | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 1812N | Wayne and Andrew installed a temp gene set to transformer 1812N and a temp break, both on the emap to allow SCADA to be dressed correctly. Wayne and Andrew to remove on completion. OMS Job to be closed out once power restored, ASW. Part of DNO 150110 | F3 | BROOKLANDS 12 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 26 | 23 | 391 | 0.0011943 | 5.1925e-05 | 2015-01-20 | C | 0.0011943 | 5.1925e-05 | 2015 | 2015-01-20 | C | 17 | 0.0011943 | 5.1925e-05
1 | 3655561 | 2015-01-20 13:59 | 2015-01-20 16:26 | 147.6333 | 1 | 147.6333 | 0.00045153 | 3.0584e-06 | Restore Supply on Device X235 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 801903 | replaced 2x 2a HV fuse links due to unknown, nothing else repaired or replaced, adjacent assets up to powerco standard. Email sent to Jo to calculate SAIDI component. | F4 | BULLS | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 147.6333 | 144.6333 | 144.6333 | 0.00044177 | 3.0544e-06 | 2015-01-20 | C | 0.00044177 | 3.054e-06 | 2015 | 2015-01-20 | C | 1 | 0.00044177 | 3.0544e-06
1 | 3655679 | 2015-01-20 14:09 | 2015-01-20 16:43 | 153.2833 | 1 | 153.2833 | 0.00046881 | 3.0584e-06 | Restore Supply on Device TP2272 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TF7-148 | Very poor mobile reception. FM made safe. there was a blow up in back of tx. Irrigation pump only affected, not needed today, customer need it fix by Thursday, happy to be without power till then. FM has been working through control. Tx is TF7-148 and not | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 153.2833 | 150.2833 | 150.2833 | 0.00045903 | 3.0544e-06 | 2015-01-20 | C | 0.00045903 | 3.054e-06 | 2015 | 2015-01-20 | C | 1 | 0.00045903 | 3.0544e-06
1 | 3656236 | 2015-01-20 17:19 | 2015-01-21 16:21 | 1381.9333 | 1 | 1381.9333 | 0.0042265 | 3.0584e-06 | Restore Supply on Device TC2966 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | FC 2128 | 4KM Long SWER line to CHH Lokout post. All through Forestry. Due to time (early evening NOC NCTL contacted for direction. Leave off for the night. To be patrolled in detail in the morning to find the cause of the fault. NCTL to organise with SMC on the 21 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1381.9333 | 1378.9333 | 1378.9333 | 0.0042118 | 3.0544e-06 | 2015-01-20 | C | 0.0042118 | 3.054e-06 | 2015 | 2015-01-20 | C | 1 | 0.0042118 | 3.0544e-06
1 | 3666352 | 2015-01-21 06:05 | 2015-01-21 08:40 | 155.1 | 163 | 22425.3 | 0.068586 | 0.00049852 | Restore Supply on Device 4897 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | RS 4897 | RS 4897 A/R, L/O, O/C B & C Phase Line Patrolled & Sectionalised with no fault found. Kaine MacKay and Phil Webby attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 137.5785 | 134.5785 | 21936.3 | 0.067003 | 0.00049787 | 2015-01-21 | C | 0.067003 | 0.00049787 | 2015 | 2015-01-21 | C | 163 | 0.067003 | 0.00049787
1 | 3410376 | 2015-01-21 08:15 | 2015-01-21 14:49 | 394 | 47 | 18518 | 0.056636 | 0.00014375 | NAPA ID:05665 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 794495, X825 | Replace pole 794495 including new crossarms. Reuse existing pole mount TX X825. Works Location: Turakina Valley Rd, Turakina. Wo 10131465. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 394 | 391 | 18377 | 0.056131 | 0.00014356 | 2015-01-21 | B | 0.028066 | 7.1779e-05 | 2015 | 2015-01-21 | B | 47 | 0.056131 | 0.00014356
1 | 3666967 | 2015-01-21 08:29 | 2015-01-21 19:03 | 634.3833 | 170 | 30154.5667 | 0.092225 | 0.00051993 | Restore Supply on Device C946 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 822525 | 11kV CB C946 tripped locked out. Sectionalised, found lines down at pole 822525, Isolated via Fuses 7633. Replaced 3x jumpers and sleeves, all work complete. Fire in the area, suspected to be caused due to the lines down, Gavin Paget investigated and to p | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 177.3798 | 174.3798 | 29644.5667 | 0.090547 | 0.00051925 | 2015-01-21 | C | 0.090547 | 0.00051925 | 2015 | 2015-01-21 | C | 170 | 0.090547 | 0.00051925
1 | 3386190 | 2015-01-21 09:02 | 2015-01-21 15:08 | 365.85 | 26 | 9512.1 | 0.029092 | 7.9519e-05 | NAPA ID:02992 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 321074 | To rewire from pole 227478 To pole 227498. Works Location: Old Coach Rd, Pongakawa. WO 10162190. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 365.85 | 362.85 | 9434.1 | 0.028816 | 7.9415e-05 | 2015-01-21 | B | 0.014408 | 3.9708e-05 | 2015 | 2015-01-21 | B | 26 | 0.028816 | 7.9415e-05
1 | 3372965 | 2015-01-21 09:20 | 2015-01-21 14:35 | 314.75 | 2 | 629.5 | 0.0019253 | 6.1168e-06 | NAPA ID:05416 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1077 | Replace Transformer TC1077 with new 50Kva minisub. Works Location: Rifle Range Rd, Waihi. WO10148220. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 314.75 | 311.75 | 623.5 | 0.0019044 | 6.1088e-06 | 2015-01-21 | B | 0.00095222 | 3.054e-06 | 2015 | 2015-01-21 | B | 2 | 0.0019044 | 6.1088e-06
1 | 3410355 | 2015-01-21 09:45 | 2015-01-21 15:52 | 367 | 1 | 367 | 0.0011224 | 3.0584e-06 | NAPA ID:05567 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T9/252 | To replace 11kv poles and to replace 11kv x/arms. Work Location: Huia Road, Pongaroa. WO 10134517. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 367 | 364 | 364 | 0.0011118 | 3.0544e-06 | 2015-01-21 | B | 0.0005559 | 1.527e-06 | 2015 | 2015-01-21 | B | 1 | 0.0011118 | 3.0544e-06
1 | 3500035 | 2015-01-21 10:01 | 2015-01-21 14:22 | 260.4333 | 3 | 781.3 | 0.0023895 | 9.1753e-06 | NAPA ID:06001 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5026 | Replace defected TX TC5026. Works location: SH24 Matamata. WO 10148293 | F3 | FIRTH ST | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 260.4333 | 257.4333 | 772.3 | 0.0023589 | 9.1633e-06 | 2015-01-21 | B | 0.0011795 | 4.582e-06 | 2015 | 2015-01-21 | B | 3 | 0.0023589 | 9.1633e-06
1 | 3668595 | 2015-01-21 11:25 | 2015-01-21 12:45 | 80 | 1 | 80 | 0.00024467 | 3.0584e-06 | Restore Supply on Device 4672 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | 4672 | Cable isolated for safety whilst raising the cable for roadworks ... | F2 | GILBERD ST | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 77 | 0.00023519 | 3.0544e-06 | 2015-01-21 | C | 0.00023519 | 3.054e-06 | 2015 | 2015-01-21 | C | 1 | 0.00023519 | 3.0544e-06
1 | 3668642 | 2015-01-21 13:21 | 2015-01-21 16:15 | 174.5167 | 44 | 7244.3667 | 0.022156 | 0.00013457 | Restore Supply on Device I15 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Alfredton sub | CB I15 appears to have faulted and bypassed DNO 150113 applied | F5 | CASTLEHILL | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 164.6447 | 161.6447 | 7112.3667 | 0.021724 | 0.00013439 | 2015-01-21 | C | 0.021724 | 0.00013439 | 2015 | 2015-01-21 | C | 44 | 0.021724 | 0.00013439
1 | 3670669 | 2015-01-21 17:51 | 2015-01-21 21:33 | 221.9333 | 132 | 23085.6333 | 0.070606 | 0.00040371 | Restore Supply on Device CB4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | CB4 | at 17:50 Pongaroa Sub, CB 4 Tiraumea Feeder, Tripped, Ph B O/C, E/F, L/O. Faultmen dispatched and investigation began. Feeder sectionalised and patrolled by faultman, no fault found. All Power Restored on completion. Andrew Tuhura Attended. Faultman did s | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 174.8912 | 171.8912 | 22689.6333 | 0.069304 | 0.00040318 | 2015-01-21 | C | 0.069304 | 0.00040318 | 2015 | 2015-01-21 | C | 132 | 0.069304 | 0.00040318
1 | 3671334 | 2015-01-22 00:23 | 2015-01-22 11:00 | 637 | 22 | 14014 | 0.042861 | 6.7285e-05 | Restore Supply on Device 7875 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 837720 | Removed and trimmed trees at various points along the line | F5 | ANNEDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 637 | 634 | 13948 | 0.042603 | 6.7197e-05 | 2015-01-22 | C | 0.042603 | 6.7197e-05 | 2015 | 2015-01-22 | C | 22 | 0.042603 | 6.7197e-05
1 | 3671392 | 2015-01-22 04:11 | 2015-01-22 09:37 | 325.55 | 99 | 15436.8167 | 0.047212 | 0.00030278 | Restore Supply on Device TP1248 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | SD3-109 | 2 x 63Amp HV fuses blown in link box SD3-109. Cable to be tested. Cables tested & transformers checked, All OK. Re livened | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 155.9274 | 152.9274 | 15139.8167 | 0.046243 | 0.00030239 | 2015-01-22 | C | 0.046243 | 0.00030239 | 2015 | 2015-01-22 | C | 99 | 0.046243 | 0.00030239
1 | 3410249 | 2015-01-22 08:00 | 2015-01-22 15:30 | 450 | 2 | 1286 | 0.0039331 | 6.1168e-06 | NAPA ID:05625 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole P05778 | Replace TX and LV X-Arms on pole P05778 (T5/141). Existing TX is to be reused. Works location: Conspicuous Rd Apiti WO 10160678 | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 643 | 640 | 1280 | 0.0039097 | 6.1088e-06 | 2015-01-22 | B | 0.0019548 | 3.054e-06 | 2015 | 2015-01-22 | B | 2 | 0.0039097 | 6.1088e-06
1 | 3487126 | 2015-01-22 08:04 | 2015-01-22 15:03 | 419 | 38 | 15922 | 0.048696 | 0.00011622 | NAPA ID:05745 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 813708 | 11KV POLE REPLACEMENT / ISOLATION OF T1901 TO REMOVE 11KV SPUR FEEDING T1901 LIVE LINE /LIVE LINE POLE 813708. Works location: Jellicoe Rd Martinborough WO 10161174 | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 419 | 416 | 15808 | 0.048284 | 0.00011607 | 2015-01-22 | B | 0.024142 | 5.8034e-05 | 2015 | 2015-01-22 | B | 38 | 0.048284 | 0.00011607
1 | 3487086 | 2015-01-22 08:45 | 2015-01-22 10:01 | 76 | 12 | 912 | 0.0027893 | 3.6701e-05 | NAPA ID:05735 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Linkbox SE6-228 | Maintanence on 11kv Linkbox SE6-228. Works location: Gulliver Rd Paengaroa. WO 10143066 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 76 | 73 | 876 | 0.0026757 | 3.6653e-05 | 2015-01-22 | B | 0.0013378 | 1.8327e-05 | 2015 | 2015-01-22 | B | 12 | 0.0026757 | 3.6653e-05
1 | 3357969 | 2015-01-22 08:46 | 2015-01-22 13:44 | 298.4333 | 61 | 18204.4333 | 0.055677 | 0.00018656 | NAPA ID:03878 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4905 | Repole, rearm,& reconductor 11kV. Work Location: Old Taupo Road. Work Order 10151890. Powerco Project Reference IR4840 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 298.4333 | 295.4333 | 18021.4333 | 0.055045 | 0.00018632 | 2015-01-22 | B | 0.027523 | 9.316e-05 | 2015 | 2015-01-22 | B | 61 | 0.055045 | 0.00018632
1 | 3361302 | 2015-01-22 08:51 | 2015-01-22 15:10 | 379 | 159 | 60172.6333 | 0.18403 | 0.00048629 | NAPA ID:05337 TP_WAIKINO GXP > WAIHI BEACH SUB > WILSON RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Q0027, Q12383 | Replace Pole# Q0027 and repair cables at Q12383. Work Location: Seaforth Road, Waihi Beach. Work Order 10162903 | F3 | WILSON RD | WAIHI BEACH SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 378.4442 | 375.4442 | 59695.6333 | 0.18234 | 0.00048565 | 2015-01-22 | B | 0.091168 | 0.00024283 | 2015 | 2015-01-22 | B | 159 | 0.18234 | 0.00048565
1 | 3386193 | 2015-01-22 09:00 | 2015-01-22 14:29 | 329 | 26 | 8554 | 0.026162 | 7.9519e-05 | NAPA ID:02990 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 227478 | To replace poles and Cross arms. Works Location: Old Coach Rd, Pongakawa. WO 10162190. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 329 | 326 | 8476 | 0.025889 | 7.9415e-05 | 2015-01-22 | B | 0.012945 | 3.9708e-05 | 2015 | 2015-01-22 | B | 26 | 0.025889 | 7.9415e-05
1 | 3410353 | 2015-01-22 09:59 | 2015-01-22 17:08 | 429 | 1 | 429 | 0.0013121 | 3.0584e-06 | NAPA ID:05575 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole P02656 | To replace 11kv poles and x/ams. Works location: Huia Rd WO 10134517 | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 429 | 426 | 426 | 0.0013012 | 3.0544e-06 | 2015-01-22 | B | 0.00065059 | 1.527e-06 | 2015 | 2015-01-22 | B | 1 | 0.0013012 | 3.0544e-06
1 | 3487087 | 2015-01-22 11:30 | 2015-01-22 12:41 | 71 | 15 | 1065 | 0.0032572 | 4.5876e-05 | NAPA ID:05737 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-189 | Maintanence on 11kv Linkbox - SE6-189. Works location: SH 33 Paengaroa WO 10143066 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 71 | 68 | 1020 | 0.0031155 | 4.5816e-05 | 2015-01-22 | B | 0.0015578 | 2.2908e-05 | 2015 | 2015-01-22 | B | 15 | 0.0031155 | 4.5816e-05
1 | 3686386 | 2015-01-22 12:30 | 2015-01-22 15:15 | 165 | 3 | 495 | 0.0015139 | 9.1753e-06 | Restore Supply on Device T5/224 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/224 | Part of NAPA 5628. re-staged after the fact Note power off: 1230, back on: 1515 | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 165 | 162 | 486 | 0.0014844 | 9.1633e-06 | 2015-01-22 | C | 0.0014845 | 9.163e-06 | 2015 | 2015-01-22 | C | 3 | 0.0014844 | 9.1633e-06
1 | 3487092 | 2015-01-22 14:00 | 2015-01-22 14:52 | 52 | 103 | 5317 | 0.016262 | 0.00031502 | NAPA ID:05738 TP_TE MATAI GXP > TE PUKE SUB > PAENGAROA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | SE6-167 | Maintanence on 11kv Linkbox SE6-167. Works location: Maungarangi Rd. WO 10143066 | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 51.6214 | 48.6214 | 5008 | 0.015297 | 0.00031461 | 2015-01-22 | B | 0.0076483 | 0.0001573 | 2015 | 2015-01-22 | B | 103 | 0.015297 | 0.00031461
1 | 3487160 | 2015-01-23 08:54 | 2015-01-23 14:50 | 356 | 29 | 10324 | 0.031575 | 8.8694e-05 | NAPA ID:05314 TP_MT MAUNGANUI 33 GXP | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | 11kV pole 383830 | Check Open SD5-016. Create Live Line break at pole 383830. Replace 11kV conductor between poles 321691 and 383830. Close live Line break at pole 383830. Works location: Kairua Rd WO 10156589 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 356 | 353 | 10237 | 0.031268 | 8.8578e-05 | 2015-01-23 | B | 0.015634 | 4.4289e-05 | 2015 | 2015-01-23 | B | 29 | 0.031268 | 8.8578e-05
1 | 3614756 | 2015-01-23 09:34 | 2015-01-23 11:49 | 135.0667 | 58 | 7833.8667 | 0.023959 | 0.00017739 | NAPA ID:06177 TP_HUIRANGI GXP > WAITARA WEST SUB > BROWNE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3557T | Complete change over of O/H to U/G Transformer stucture 3557T with 11kV Fuses 12031 supplying new ground mount 200 KVA. Works location: Queens St High St West Waitara. WO 10149207 | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 135.0667 | 132.0667 | 7659.8667 | 0.023396 | 0.00017716 | 2015-01-23 | B | 0.011698 | 8.8578e-05 | 2015 | 2015-01-23 | B | 58 | 0.023396 | 0.00017716
1 | 3422514 | 2015-01-23 12:31 | 2015-01-23 14:02 | 91 | 1 | 91 | 0.00027832 | 3.0584e-06 | NAPA ID:05634 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P12145 | Replace transformer and LV cross arms on pole P12145 (T5/253). Existing transformer is to be reused. Works location: Beaconsfield Valley Rd, Waituna West. WO 10160678. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 91 | 88 | 88 | 0.00026879 | 3.0544e-06 | 2015-01-23 | B | 0.00013439 | 1.527e-06 | 2015 | 2015-01-23 | B | 1 | 0.00026879 | 3.0544e-06
1 | 3688909 | 2015-01-23 17:50 | 2015-01-23 18:47 | 57 | 1 | 57 | 0.00017433 | 3.0584e-06 | Restore Supply on Device FC4056 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | N0064 | Found bailer wrap across 11kV. Isolated at fuses FC4056. Removed wrap & relivened - NDR number 31410. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 57 | 54 | 54 | 0.00016494 | 3.0544e-06 | 2015-01-23 | C | 0.00016494 | 3.054e-06 | 2015 | 2015-01-23 | C | 1 | 0.00016494 | 3.0544e-06
1 | 3689021 | 2015-01-24 02:27 | 2015-01-24 04:03 | 95.9 | 1 | 95.9 | 0.0002933 | 3.0584e-06 | Restore Supply on Device Y10 | 33000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Turitea | Turitea 33kV CB Y10 tripped C phase O/C & Dir E/F Zone. Line Patrol carried out and nothing found. Supply restored. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 95.9 | 92.9 | 92.9 | 0.00028376 | 3.0544e-06 | 2015-01-24 | C | 0.00028376 | 3.054e-06 | 2015 | 2015-01-24 | C | 1 | 0.00028376 | 3.0544e-06
1 | 3441686 | 2015-01-24 08:31 | 2015-01-24 10:26 | 115.1333 | 89 | 10246.8667 | 0.031339 | 0.0002722 | NAPA ID:05656 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T7/424 & T7/425 | To install Lighting Arrestors to 11kV cables feeding new ground mount Switch Gear #10215. Works Location: Cabbridge St, Pahiatua. WO 10147880. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 115.1333 | 112.1333 | 9979.8667 | 0.030483 | 0.00027184 | 2015-01-24 | B | 0.015241 | 0.00013592 | 2015 | 2015-01-24 | B | 89 | 0.030483 | 0.00027184
1 | 3689338 | 2015-01-24 13:35 | 2015-01-24 13:50 | 15 | 26 | 390 | 0.0011928 | 7.9519e-05 | Restore Supply on Device TC3694 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC723 | Isolate transformer TC723 to repair L/V jumper. Jumper repaired, all service restored Materials 1 x quick lug. | F4 | TOWNSHIP & LS | FARMER ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 312 | 0.00095298 | 7.9415e-05 | 2015-01-24 | C | 0.00095298 | 7.9415e-05 | 2015 | 2015-01-24 | C | 26 | 0.00095298 | 7.9415e-05
1 | 3689456 | 2015-01-24 15:27 | 2015-01-24 21:00 | 333.05 | 73 | 12576.1333 | 0.038463 | 0.00022326 | Restore Supply on Device C613 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 812387 | Fire comms reporting line down INT Ashbys Road, South Featherston Road, Lake Reserve. ETA required. 04 801 0812. Line break cut at pole 812387 for tree removal and line repairs. Replaced 1 span 3 phases. NDR 37920. Safety Manager Incident #441135 | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 172.2758 | 169.2758 | 12357.1333 | 0.037744 | 0.00022297 | 2015-01-24 | C | 0.037744 | 0.00022297 | 2015 | 2015-01-24 | C | 73 | 0.037744 | 0.00022297
1 | 3690262 | 2015-01-25 13:17 | 2015-01-25 15:29 | 132.4 | 2 | 194.3167 | 0.0005943 | 6.1168e-06 | Restore Supply on Device X373 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 997 | Worked through control replaced 2x 20amp 11kv fuses. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. Check 556 Mangahoe Road tx x375 if would have been affected 3690322 | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 97.1583 | 94.1583 | 188.3167 | 0.0005752 | 6.1088e-06 | 2015-01-25 | C | 0.0005752 | 6.109e-06 | 2015 | 2015-01-25 | C | 2 | 0.0005752 | 6.1088e-06
1 | 3690312 | 2015-01-25 14:01 | 2015-01-25 16:21 | 140.1333 | 1 | 140.1333 | 0.00042859 | 3.0584e-06 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | Planned Metering checks at international Malting Company | Planned Job NAPA5666 - no OMS # to group job to. Scott Bullock on site. | F3 | NGATAWA | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140.1333 | 137.1333 | 137.1333 | 0.00041886 | 3.0544e-06 | 2015-01-25 | C | 0.00041886 | 3.054e-06 | 2015 | 2015-01-25 | C | 1 | 0.00041886 | 3.0544e-06
1 | 3690353 | 2015-01-25 16:42 | 2015-01-25 22:32 | 349.45 | 1 | 349.45 | 0.0010688 | 3.0584e-06 | Restore Supply on Device T3293 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T3046 | Transformer T3046 found to be faulty and in need of replacement - | F5 | LANGDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 349.45 | 346.45 | 346.45 | 0.0010582 | 3.0544e-06 | 2015-01-25 | C | 0.0010582 | 3.054e-06 | 2015 | 2015-01-25 | C | 1 | 0.0010582 | 3.0544e-06
1 | 3690369 | 2015-01-25 18:58 | 2015-01-26 04:45 | 587.1667 | 471 | 80795.5 | 0.24711 | 0.0014405 | Restore Supply on Device RC15 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC5718 | Recloser RC 15 L/O. No flags Sectionalised and found fault beyound fuses FC4237. Isolated at fuses. Requested generator to be organised and connected to Transformer TC5781. Generator connected at 04:45 hours. Testing and cable repairs to be done on NAPA | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 171.5403 | 168.5403 | 79382.5 | 0.24247 | 0.0014386 | 2015-01-25 | C | 0.24247 | 0.0014386 | 2015 | 2015-01-25 | C | 471 | 0.24247 | 0.0014386
1 | 3620861 | 2015-01-26 08:17 | 2015-01-26 15:41 | 444.2667 | 10 | 4442.6667 | 0.013588 | 3.0584e-05 | NAPA ID:06222 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV S794 | CLEARING BURNING TREES FROM 11KV NETWORK. Works location; Te Wharau Rd. PPPD 47295 | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 444.2667 | 441.2667 | 4412.6667 | 0.013478 | 3.0544e-05 | 2015-01-26 | B | 0.0067391 | 1.5272e-05 | 2015 | 2015-01-26 | B | 10 | 0.013478 | 3.0544e-05
1 | 3423312 | 2015-01-26 08:32 | 2015-01-26 11:58 | 206 | 5 | 1030 | 0.0031502 | 1.5292e-05 | NAPA ID:05703 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P08373 | Replace TX and LV X-Arms on pole P08373 (T5/131). Replace TX T5/131 with a new pole mount TX. Works Location: Beaconsfield Valley Rd, Waituna West. WO 10160678. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 206 | 203 | 1015 | 0.0031002 | 1.5272e-05 | 2015-01-26 | B | 0.0015501 | 7.636e-06 | 2015 | 2015-01-26 | B | 5 | 0.0031002 | 1.5272e-05
1 | 3410528 | 2015-01-26 08:42 | 2015-01-26 18:10 | 567.9333 | 1 | 567.9333 | 0.001737 | 3.0584e-06 | NAPA ID:05521 TP_MASTERTON GXP > CHAPEL SUB > HEAD OFFICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1942 | 11kv Transformer Replacement St Pat School. Works Location: 132 Chapel Street, Masterton. WO 10157264. | F2 | HEAD OFFICE | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 567.9333 | 564.9333 | 564.9333 | 0.0017255 | 3.0544e-06 | 2015-01-26 | B | 0.00086277 | 1.527e-06 | 2015 | 2015-01-26 | B | 1 | 0.0017255 | 3.0544e-06
1 | 3699837 | 2015-01-26 15:35 | 2015-01-26 16:17 | 42.25 | 2 | 63.7167 | 0.00019487 | 6.1168e-06 | Restore Supply on Device 58 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | South Road napa 5959 | This is part of planned outage 5959 Obertech advise fm they are having problems and spoke to Murray in control who said most of TX are back on now and the rest are going back on now 4.15 | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 31.8583 | 28.8583 | 57.7167 | 0.00017629 | 6.1088e-06 | 2015-01-26 | C | 0.00017629 | 6.109e-06 | 2015 | 2015-01-26 | C | 2 | 0.00017629 | 6.1088e-06
1 | 3703387 | 2015-01-26 17:18 | 2015-01-26 23:39 | 381 | 659 | 92697 | 0.28351 | 0.0020155 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 210327 | Fire comms reporting lines down and possible car v pole CNR Snodgrass road and State Highway 2. ETA required F1774401 09 486 7948. 5.53pm Fire Service advised car and caravan upside down. Fire under caravan, ammunition in caravan. Advised Shan at hub and | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 140.6631 | 137.6631 | 90720 | 0.2771 | 0.0020129 | 2015-01-26 | C | 0.2771 | 0.0020129 | 2015 | 2015-01-26 | C | 659 | 0.2771 | 0.0020129
1 | 3701171 | 2015-01-27 05:36 | 2015-01-27 09:24 | 228.0333 | 478 | 39197.6167 | 0.11988 | 0.0014619 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P05104 | 2 lines down due to deterioration. Materials used 30m of conductor. Les Robinson and Mike Thompson attended. Pole P05104. | F4 | APITI | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 82.0034 | 79.0034 | 37763.6167 | 0.11535 | 0.00146 | 2015-01-27 | C | 0.11535 | 0.00146 | 2015 | 2015-01-27 | C | 478 | 0.11535 | 0.00146
1 | 3701910 | 2015-01-27 08:03 | 2015-01-27 15:30 | 446.7 | 1 | 446.7 | 0.0013662 | 3.0584e-06 | Restore Supply on Device TE7-153 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7/153 | faultman attended yesterday and advised tx is broken and needs replacing - they completed this job at 3.30pm 27/1/14 , David Joynt attending today 28/1 to replace tx. TE7-153. Transformer replace, all power restored. New transformer and 2 x 15amp HV fus | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 446.7 | 443.7 | 443.7 | 0.0013552 | 3.0544e-06 | 2015-01-27 | C | 0.0013552 | 3.054e-06 | 2015 | 2015-01-27 | C | 1 | 0.0013552 | 3.0544e-06
1 | 3500839 | 2015-01-27 09:16 | 2015-01-27 13:49 | 273.2833 | 373 | 101934.6833 | 0.31176 | 0.0011408 | NAPA ID:05286 TP_BUNNYTHORPE GXP > MILSON SUB > GEMINI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/454 | Cut 11kV and add in 2 legs for T6/454. Works location: Apollo Parade. WO 10160016. | F3 | GEMINI | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 273.2833 | 270.2833 | 100815.6833 | 0.30793 | 0.0011393 | 2015-01-27 | B | 0.15397 | 0.00056965 | 2015 | 2015-01-27 | B | 373 | 0.30793 | 0.0011393
1 | 3617496 | 2015-01-27 09:25 | 2015-01-27 14:05 | 280.5 | 7 | 1963.5 | 0.0060052 | 2.1409e-05 | NAPA ID:06196 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole WHIWGM104 | Install Line break @ Pole# WHIWGM104 to replce pole and ABS IC250. REMOVE DNO 140603 ON COMPLETION. Works location: Waihi-Whangamata Rd Waihi. WO 10157335 | F4 | WAIHI NORTH | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 280.5 | 277.5 | 1942.5 | 0.0059332 | 2.1381e-05 | 2015-01-27 | B | 0.0029666 | 1.069e-05 | 2015 | 2015-01-27 | B | 7 | 0.0059332 | 2.1381e-05
1 | 3388576 | 2015-01-27 09:26 | 2015-01-27 13:30 | 243.65 | 47 | 11451.55 | 0.035024 | 0.00014375 | NAPA ID:05593 TP_OPUNAKE GXP > TASMAN SUB > IHAIA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6726 | replace pole on Ihaia rd opunake. Works Location: Ihaia Rd, Opunake. WO 10162610. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 243.65 | 240.65 | 11310.55 | 0.034547 | 0.00014356 | 2015-01-27 | B | 0.017274 | 7.1779e-05 | 2015 | 2015-01-27 | B | 47 | 0.034547 | 0.00014356
1 | 3500469 | 2015-01-27 09:30 | 2015-01-27 12:32 | 181.9167 | 66 | 12006.5 | 0.036721 | 0.00020186 | NAPA ID:05892 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5977 | Replace ABS 5977 & cross arms. Upgrade Earths [DNO141031]. Works location: Auroa Rd Kaponga. WO 10166827. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 181.9167 | 178.9167 | 11808.5 | 0.036068 | 0.00020159 | 2015-01-27 | B | 0.018034 | 0.0001008 | 2015 | 2015-01-27 | B | 66 | 0.036068 | 0.00020159
1 | 3494934 | 2015-01-27 09:30 | 2015-01-27 11:45 | 135.0167 | 16 | 2033.3833 | 0.0062189 | 4.8935e-05 | NAPA ID:05841 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP729 | Replace crossarms. Works location: Te Rerenga, Kuaotunu Rd Whitianga. WO 10148314 | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 127.0865 | 124.0865 | 1985.3833 | 0.0060642 | 4.8871e-05 | 2015-01-27 | B | 0.0030321 | 2.4435e-05 | 2015 | 2015-01-27 | B | 16 | 0.0060642 | 4.8871e-05
1 | 3497290 | 2015-01-27 09:46 | 2015-01-27 15:47 | 361.5167 | 8 | 2892.1333 | 0.0088454 | 2.4467e-05 | NAPA ID:05898 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-084 | Replace 11kV DDO's with fused ABS. Works location: No 3 Rd Bayly Rd Te Puke. WO 10148307 | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 361.5167 | 358.5167 | 2868.1333 | 0.0087605 | 2.4435e-05 | 2015-01-27 | B | 0.0043802 | 1.2218e-05 | 2015 | 2015-01-27 | B | 8 | 0.0087605 | 2.4435e-05
1 | 3668614 | 2015-01-27 09:54 | 2015-01-27 14:43 | 289.2333 | 75 | 20207.9833 | 0.061805 | 0.00022938 | NAPA ID:06384 TP_PIAKO GXP > WALTON SUB > WARDVILLE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1099 | CONNECT UP NEW HV TIE LINE OPEN POINT FROM PIAKO GXP - MIKELSEN RD CB2 McCABES RD to WAIHOU GXP - WALTON CB4 WARDVILLE ROAD. PHASE CHECK ACROSS NEW ABS IP584. If Phasing is incorrect a short shut on the WALTON CB4 feeder only will be required. Isolatio | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 269.4398 | 266.4398 | 19982.9833 | 0.061036 | 0.00022908 | 2015-01-27 | B | 0.030518 | 0.00011454 | 2015 | 2015-01-27 | B | 75 | 0.061036 | 0.00022908
1 | 3705343 | 2015-01-27 10:39 | 2015-01-28 00:15 | 816 | 6 | 3060 | 0.0093588 | 1.8351e-05 | Restore Supply on Device IP198 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC2 098 | Replace faulty transformer TC2 098 , burnt out gyro box & L/V joints. All repaired all service restored | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 510 | 507 | 3042 | 0.0092916 | 1.8327e-05 | 2015-01-27 | C | 0.0092916 | 1.8327e-05 | 2015 | 2015-01-27 | C | 6 | 0.0092916 | 1.8327e-05
1 | 3705142 | 2015-01-27 11:03 | 2015-01-27 11:18 | 14.8167 | 98 | 1452.0333 | 0.0044409 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C224 | Tinui CDB C224 tripped L/O. Closed successfully after 15 mins - not patrolled. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 14.8167 | 11.8167 | 1158.0333 | 0.0035371 | 0.00029933 | 2015-01-27 | C | 0.0035371 | 0.00029933 | 2015 | 2015-01-27 | C | 98 | 0.0035371 | 0.00029933
1 | 3494914 | 2015-01-27 13:15 | 2015-01-27 15:15 | 120 | 143 | 17160 | 0.052483 | 0.00043735 | NAPA ID:05843 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 337 | Restrain conductors for legal clearance. Works location: Bluff Rd Kuaotunu WO 10148314 | F4 | MOTUROA 3 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 16731 | 0.051104 | 0.00043678 | 2015-01-27 | B | 0.025552 | 0.00021839 | 2015 | 2015-01-27 | B | 143 | 0.051104 | 0.00043678
1 | 3706351 | 2015-01-27 16:16 | 2015-01-27 19:36 | 199.6833 | 953 | 153980.8167 | 0.47094 | 0.0029147 | Restore Supply on Device 9613 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw?Gear IC3089 | 11kV CB 9495/3 tripped ( no flags, no Comms ) feeder sectionalised & suspected cable fault isolated to between Sw/Gear IC3089 & T Blade TC3802 B Back feed in place via CB 9457/2. All service restored | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 161.5748 | 158.5748 | 151121.8167 | 0.46159 | 0.0029109 | 2015-01-27 | C | 0.46159 | 0.0029109 | 2015 | 2015-01-27 | C | 953 | 0.46159 | 0.0029109
1 | 3706358 | 2015-01-27 16:32 | 2015-01-27 18:58 | 146.4167 | 101 | 5033.6667 | 0.015395 | 0.0003089 | Restore Supply on Device IC3089 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | IC3089 |  | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 49.8383 | 46.8383 | 4730.6667 | 0.014449 | 0.0003085 | 2015-01-27 | C | 0.014449 | 0.0003085 | 2015 | 2015-01-27 | C | 101 | 0.014449 | 0.0003085
1 | 3706433 | 2015-01-27 16:41 | 2015-01-27 19:41 | 180.1667 | 64 | 5322.6 | 0.016279 | 0.00019574 | Restore Supply on Device IC3802A/B | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | IC3089 |  | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 83.1656 | 80.1656 | 5130.6 | 0.015671 | 0.00019548 | 2015-01-27 | C | 0.015671 | 0.00019548 | 2015 | 2015-01-27 | C | 64 | 0.015671 | 0.00019548
1 | 3707593 | 2015-01-27 20:19 | 2015-01-27 21:13 | 54 | 39 | 2106 | 0.006441 | 0.00011928 | Restore Supply on Device 13 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G67/B | CB 13 tripped on A & C phase O/C and E/F flags. Faultman found that Magnefix G67/B had the grease coming out of it. Magnefix was isolated at Magnefix G67/B and at Sw/Gear G265B. Faultman to return in the morning to check Magnefix G67/B and test cable to | F2 | MAIN ST 13 | MAIN ST SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 1989 | 0.0060752 | 0.00011912 | 2015-01-27 | C | 0.0060752 | 0.00011912 | 2015 | 2015-01-27 | C | 39 | 0.0060752 | 0.00011912
1 | 3708546 | 2015-01-28 06:37 | 2015-01-28 07:56 | 78.3 | 2 | 92.55 | 0.00028306 | 6.1168e-06 | Restore Supply on Device 4632T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 6393 | Suspect Bird Strike. 2 fuses blown. Line patrolled fuses replaced. Materials:- 2x 8 Amp HV Fuses. Brett Bensley attended. | F4 | MAHOE | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 46.275 | 43.275 | 86.55 | 0.00026436 | 6.1088e-06 | 2015-01-28 | C | 0.00026436 | 6.109e-06 | 2015 | 2015-01-28 | C | 2 | 0.00026436 | 6.1088e-06
1 | 3410058 | 2015-01-28 07:46 | 2015-01-28 16:31 | 525 | 112 | 33672 | 0.10298 | 0.00034254 | NAPA ID:05563 TP_HUIRANGI GXP > WAITARA WEST SUB > BLAKE ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3559T | Complete change over from O/H to U/G Transformer Structure 3559T;11kV with 33kV Overbuilt. Works Location: Parris St, Waitara. WO 10149207. | F1, F2, F3 | WAITARA WEST 33KV | TP_HUIRANGI | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 300.6429 | 297.6429 | 33336 | 0.10182 | 0.0003421 | 2015-01-28 | B | 0.050911 | 0.00017105 | 2015 | 2015-01-28 | B | 112 | 0.10182 | 0.0003421
1 | 3708773 | 2015-01-28 08:32 | 2015-01-28 10:21 | 108.45 | 1 | 108.45 | 0.00033169 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | p13193 | REPLACED 2 X 6 AMP HV FUSES, DUE TO BIRD STRIKE. NO OTHER ASSETS REPAIRED OR REPLACED. ADJACENT ASSETS OK | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 108.45 | 105.45 | 105.45 | 0.00032209 | 3.0544e-06 | 2015-01-28 | C | 0.00032209 | 3.054e-06 | 2015 | 2015-01-28 | C | 1 | 0.00032209 | 3.0544e-06
1 | 3498487 | 2015-01-28 08:45 | 2015-01-28 15:19 | 393.3333 | 61 | 23993.3333 | 0.073382 | 0.00018656 | NAPA ID:06033 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC933 | Repole,rearm,& reconductor 11kV. Connect new transformer TP2742 1 span from pole M12517. Works location: Old Taupo Rd. WO 10151890. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 393.3333 | 390.3333 | 23810.3333 | 0.072727 | 0.00018632 | 2015-01-28 | B | 0.036363 | 9.316e-05 | 2015 | 2015-01-28 | B | 61 | 0.072727 | 0.00018632
1 | 3496825 | 2015-01-28 09:09 | 2015-01-28 13:52 | 283.5167 | 91 | 25800.0167 | 0.078907 | 0.00027832 | NAPA ID:05910 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 726648 | Replace poles and hardware on poles 726648, 722656, 726614, 726615, 726617, 726619 and 726621. Works location: Cambridge St, Patea. WO 10163052. | F3 | PORTLAND QUAY | LIVINGSTONE SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 283.5167 | 280.5167 | 25527.0167 | 0.07797 | 0.00027795 | 2015-01-28 | B | 0.038985 | 0.00013898 | 2015 | 2015-01-28 | B | 91 | 0.07797 | 0.00027795
1 | 3497688 | 2015-01-28 09:17 | 2015-01-28 14:28 | 310.6 | 20 | 6212 | 0.018999 | 6.1168e-05 | NAPA ID:05424 TP_KOPU GXP > WHITIANGA SUB > COOK DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP723 | Replace Transformer TP723. Works location: Cook Drive Whitianga | F3 | COOK DRIVE | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 310.6 | 307.6 | 6152 | 0.018791 | 6.1088e-05 | 2015-01-28 | B | 0.0093954 | 3.0544e-05 | 2015 | 2015-01-28 | B | 20 | 0.018791 | 6.1088e-05
1 | 3497700 | 2015-01-28 09:41 | 2015-01-28 15:25 | 344.0167 | 274 | 94260.5667 | 0.28829 | 0.00083801 | NAPA ID:05835 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sectionaliser 9632/4 | Reconductoring. Works location: Black Jack Kuaotunu. WO 10148314 | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 344.0167 | 341.0167 | 93438.5667 | 0.2854 | 0.00083691 | 2015-01-28 | B | 0.1427 | 0.00041846 | 2015 | 2015-01-28 | B | 274 | 0.2854 | 0.00083691
1 | 3618878 | 2015-01-28 09:46 | 2015-01-28 14:17 | 270.85 | 1 | 270.85 | 0.00082837 | 3.0584e-06 | NAPA ID:06140 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F12626 | To replace 11kV cross arms complete with 11kV fuses and Lightning Arrestors at Pole # F12626. Works location; Springs Rd, Okauia. WO 10148256. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 270.85 | 267.85 | 267.85 | 0.00081813 | 3.0544e-06 | 2015-01-28 | B | 0.00040906 | 1.527e-06 | 2015 | 2015-01-28 | B | 1 | 0.00081813 | 3.0544e-06
1 | 3497711 | 2015-01-28 09:50 | 2015-01-28 14:24 | 273.8667 | 4 | 1095.4667 | 0.0033504 | 1.2234e-05 | NAPA ID:05915 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-131 | Replace 11kV DDO's with fused ABS. Works location: No 3 Rd Te Puke. WO 10148307 | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 273.8667 | 270.8667 | 1083.4667 | 0.0033094 | 1.2218e-05 | 2015-01-28 | B | 0.0016547 | 6.109e-06 | 2015 | 2015-01-28 | B | 4 | 0.0033094 | 1.2218e-05
1 | 3500480 | 2015-01-28 09:51 | 2015-01-28 12:30 | 159 | 17 | 2703 | 0.0082669 | 5.1993e-05 | NAPA ID:05960 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC6054 | Replace broken lightning arrestor, which is a combination DDO. Unsafe to do DDO live so fuses will be removed. 9 ICP's - Will be carded by Tenix staff. Will be replacing all 3 sets. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 159 | 156 | 2652 | 0.0081003 | 5.1925e-05 | 2015-01-28 | B | 0.0040502 | 2.5963e-05 | 2015 | 2015-01-28 | B | 17 | 0.0081003 | 5.1925e-05
1 | 3712949 | 2015-01-28 10:46 | 2015-01-28 11:05 | 19 | 64 | 1216 | 0.003719 | 0.00019574 | NAPA ID:06548 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | IC3089 | Remove cable from T-Switch TC3802-B. Test cable for fault. Locate & repair fault and test. Fault located & repaired on cable but marginal test results. To be discussed between Brent Williams & Chian Ho on 30/01/15. Decision to be made where to from her | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 19 | 16 | 1024 | 0.0031277 | 0.00019548 | 2015-01-28 | B | 0.0015639 | 9.7742e-05 | 2015 | 2015-01-28 | B | 64 | 0.0031277 | 0.00019548
1 | 3709918 | 2015-01-28 12:29 | 2015-01-28 14:06 | 96.6833 | 1 | 96.6833 | 0.0002957 | 3.0584e-06 | Restore Supply on Device T7/50 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x t7-50 and pole p44746 | worked through control. replaced 3 amp ddo fuse at tx t7-50 and pole p44746. 1 out of 3 phases. cause: faulty tx. FM will defect tx. No other assets repaired or replaced on site. | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 96.6833 | 93.6833 | 93.6833 | 0.00028615 | 3.0544e-06 | 2015-01-28 | C | 0.00028615 | 3.054e-06 | 2015 | 2015-01-28 | C | 1 | 0.00028615 | 3.0544e-06
1 | 3710273 | 2015-01-28 13:47 | 2015-01-28 17:37 | 229.7333 | 132 | 14173.0333 | 0.043347 | 0.00040371 | Restore Supply on Device CB4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p03205 | Phil Barnes and another attended. OMS down so put on child job for crew requests. Found broken insulator at pole P03205. Materials used: 1 insulator. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107.3715 | 104.3715 | 13777.0333 | 0.042081 | 0.00040318 | 2015-01-28 | C | 0.042081 | 0.00040318 | 2015 | 2015-01-28 | C | 132 | 0.042081 | 0.00040318
1 | 3710260 | 2015-01-28 14:00 | 2015-01-28 15:24 | 83.6 | 1 | 83.6 | 0.00025568 | 3.0584e-06 | Restore Supply on Device TC5369 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC4132 | Emap update, unable to locate replace 10 amp ht fuse. cause: bird strike (farmer advise: ducks in the area) 1 out 3 phases. Switch # FC4132. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 83.6 | 80.6 | 80.6 | 0.00024619 | 3.0544e-06 | 2015-01-28 | C | 0.00024619 | 3.054e-06 | 2015 | 2015-01-28 | C | 1 | 0.00024619 | 3.0544e-06
1 | 3712937 | 2015-01-28 15:45 | 2015-01-29 09:41 | 1076.4667 | 2 | 2152.9333 | 0.0065846 | 6.1168e-06 | Restore Supply on Device X69 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X70 | Working with control to replace transformer X70 and LV & HV cross arm at pole 781933(will replace tomorrow). Transformer isolated on HV fuses; customer is happy to have power restored tomorrow by lunch time. James Prime returned to site and has checked | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1076.4667 | 1073.4667 | 2146.9333 | 0.0065576 | 6.1088e-06 | 2015-01-28 | C | 0.0065576 | 6.109e-06 | 2015 | 2015-01-28 | C | 2 | 0.0065576 | 6.1088e-06
1 | 3714096 | 2015-01-28 21:41 | 2015-01-28 23:35 | 113.9 | 1 | 113.9 | 0.00034835 | 3.0584e-06 | Restore Supply on Device X1924 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer X1924 | Faultman replaced blown fuses on transformer X1924 suspect lightning. 2 x 2 Amp HV fuses replaced. | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 113.9 | 110.9 | 110.9 | 0.00033874 | 3.0544e-06 | 2015-01-28 | C | 0.00033874 | 3.054e-06 | 2015 | 2015-01-28 | C | 1 | 0.00033874 | 3.0544e-06
1 | 3487170 | 2015-01-29 08:37 | 2015-01-29 12:28 | 231 | 3 | 693 | 0.0021195 | 9.1753e-06 | NAPA ID:05639 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P12156 | Replace TX and LV Cross Arms on pole P12156 (T5/213). Existing Transformer to be reused. Works location: Beaconsfield Valley Rd, Waituna West. WO 10160678. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 231 | 228 | 684 | 0.0020892 | 9.1633e-06 | 2015-01-29 | B | 0.0010446 | 4.582e-06 | 2015 | 2015-01-29 | B | 3 | 0.0020892 | 9.1633e-06
1 | 3623269 | 2015-01-29 08:51 | 2015-01-29 15:20 | 389.7167 | 27 | 10522.35 | 0.032182 | 8.2577e-05 | NAPA ID:05948 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP549 | Replace 11kV DDO's with fused ABS. Works location: Dunlop Rd, Te Puke. WO#10148307. | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 389.7167 | 386.7167 | 10441.35 | 0.031892 | 8.2469e-05 | 2015-01-29 | B | 0.015946 | 4.1235e-05 | 2015 | 2015-01-29 | B | 27 | 0.031892 | 8.2469e-05
1 | 3535406 | 2015-01-29 09:25 | 2015-01-29 14:59 | 334 | 40 | 13360 | 0.040861 | 0.00012234 | NAPA ID:05731 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T5/284 | Replace 11kV 400V cross arms. Works location: Lower Pakihikura Rd. WO# 10142182. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 334 | 331 | 13240 | 0.040441 | 0.00012218 | 2015-01-29 | B | 0.02022 | 6.1088e-05 | 2015 | 2015-01-29 | B | 40 | 0.040441 | 0.00012218
1 | 3714940 | 2015-01-29 09:31 | 2015-01-29 10:08 | 37.2167 | 23 | 855.9833 | 0.002618 | 7.0344e-05 | Restore Supply on Device 014 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 778429 | Outage required to rebind single conductor at Pole 778429. Chris Winter attended. | F5 | PARAPARA | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 37.2167 | 34.2167 | 786.9833 | 0.0024038 | 7.0252e-05 | 2015-01-29 | C | 0.0024038 | 7.0252e-05 | 2015 | 2015-01-29 | C | 23 | 0.0024038 | 7.0252e-05
1 | 3720782 | 2015-01-29 11:20 | 2015-01-29 21:03 | 583.1833 | 6 | 2928.75 | 0.0089574 | 1.8351e-05 | Restore Supply on Device TC515 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | TC515 | Transformer TC515 Replaced. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 488.125 | 485.125 | 2910.75 | 0.0088907 | 1.8327e-05 | 2015-01-29 | C | 0.0088907 | 1.8327e-05 | 2015 | 2015-01-29 | C | 6 | 0.0088907 | 1.8327e-05
1 | 3715428 | 2015-01-29 12:28 | 2015-01-29 17:32 | 304.4167 | 428 | 38948.2833 | 0.11912 | 0.001309 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O1566 | Line backfed and section isolated to replace 3 x insulators on pole O1566 for commissioning tests on the GFN. Brian Fisher, Morgan Wells, Chris Malone and Steve M attended. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 91.0007 | 88.0007 | 37664.2833 | 0.11504 | 0.0013073 | 2015-01-29 | C | 0.11504 | 0.0013073 | 2015 | 2015-01-29 | C | 428 | 0.11504 | 0.0013073
1 | 3718321 | 2015-01-29 12:48 | 2015-01-29 14:21 | 93 | 1316 | 100637 | 0.30779 | 0.0040249 | Restore Supply on Device CB2862 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 2862 | Stratford CB 2862 Trip, O/C. Caused total outage to Kaponga & Cardiff Subs. Backfeeds installed via 33kV to reliven those Subs. Line Patrol carried out on Stratford Kaponga line with no fault found. Stratford Kaponga line relivened and network restored to | F1, F2, F3 | CARDIFF NORTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 76.4719 | 73.4719 | 96689 | 0.29533 | 0.0040196 | 2015-01-29 | C | 0.29533 | 0.0040196 | 2015 | 2015-01-29 | C | 1316 | 0.29533 | 0.0040196
1 | 3719954 | 2015-01-29 14:33 | 2015-01-29 15:08 | 34.6333 | 429 | 9906.8333 | 0.030299 | 0.0013121 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 4 | CB 4 Tripped on A Phase O/C & E/F. Line patrolled, no fault found. Relivened OK. James Prime attended. | F2 | POLSON ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 23.0929 | 20.0929 | 8619.8333 | 0.026329 | 0.0013103 | 2015-01-29 | C | 0.026329 | 0.0013103 | 2015 | 2015-01-29 | C | 429 | 0.026329 | 0.0013103
1 | 3720531 | 2015-01-29 15:18 | 2015-01-29 17:29 | 131.45 | 2 | 262.9 | 0.00080406 | 6.1168e-06 | Restore Supply on Device 1782N | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1782N | Distribution Transformer replaced due to lightning strike. Materials used 1x 3Phase/30kVa Transformer & seismic bracket. Darren Spademan and Bruce Meek attended. | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 131.45 | 128.45 | 256.9 | 0.00078468 | 6.1088e-06 | 2015-01-29 | C | 0.00078468 | 6.109e-06 | 2015 | 2015-01-29 | C | 2 | 0.00078468 | 6.1088e-06
1 | 3720593 | 2015-01-29 16:43 | 2015-01-30 03:40 | 656.9833 | 16 | 4169.3 | 0.012751 | 4.8935e-05 | Restore Supply on Device X1873 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1874 | Check if OMS 3720600 and OMS 3720641 is related. CONTROL ADVISED GO TO FUSES 612 ADVISED LEANNE AT SVS HUB AND SHE WILL LET ALAN KNOW. Replaced transformer as faulty. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 260.5813 | 257.5813 | 4121.3 | 0.012588 | 4.8871e-05 | 2015-01-29 | C | 0.012588 | 4.8871e-05 | 2015 | 2015-01-29 | C | 16 | 0.012588 | 4.8871e-05
1 | 3714671 | 2015-01-29 19:40 | 2015-01-29 20:23 | 43 | 1 | 43 | 0.00013151 | 3.0584e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE6-237 | Andy advised he is needing to attend tonight and resag 3 phase 11kV line as it is too low. Will need bucket truck to do this work. Please refer to original OMS 3714581. Andy Wreaks attended. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 43 | 40 | 40 | 0.00012218 | 3.0544e-06 | 2015-01-29 | B | 6.1088e-05 | 1.527e-06 | 2015 | 2015-01-29 | B | 1 | 0.00012218 | 3.0544e-06
1 | 3720983 | 2015-01-30 03:03 | 2015-01-30 03:17 | 14.3 | 98 | 1401.4 | 0.0042861 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9464 | Recloser 9464 Trip. No Flags. L/O. Reclosed Recloser after 15 min wait. Closed OK. Line not patrolled - cause of fault unknown. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 14.3 | 11.3 | 1107.4 | 0.0033825 | 0.00029933 | 2015-01-30 | C | 0.0033825 | 0.00029933 | 2015 | 2015-01-30 | C | 98 | 0.0033825 | 0.00029933
1 | 3721087 | 2015-01-30 04:51 | 2015-01-30 05:05 | 14.6667 | 98 | 1437.3333 | 0.004396 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9464 | Recloser 9464. Trip. E/F. L/O. Not Patrolled. Closed in after 15 mins. Cause of fault unknown. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 14.6667 | 11.6667 | 1143.3333 | 0.0034922 | 0.00029933 | 2015-01-30 | C | 0.0034922 | 0.00029933 | 2015 | 2015-01-30 | C | 98 | 0.0034922 | 0.00029933
1 | 3721220 | 2015-01-30 06:17 | 2015-01-30 07:43 | 86.0833 | 41 | 2287.3 | 0.0069955 | 0.0001254 | Restore Supply on Device T2/942 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | H134 | Turitea CB8 Linton. Fuses H134 tripped - no flags. Line patrolled, no fault found. Relivened OK. Bruce Mehrtens attended. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55.7878 | 52.7878 | 2164.3 | 0.0066107 | 0.00012523 | 2015-01-30 | C | 0.0066107 | 0.00012523 | 2015 | 2015-01-30 | C | 41 | 0.0066107 | 0.00012523
1 | 3721543 | 2015-01-30 09:15 | 2015-01-30 14:33 | 318 | 94 | 29892 | 0.091422 | 0.00028749 | Restore Supply on Device SD4-058 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 210862 | Found pole hit by vehicle. Isolated at ABS SD6-058. Replaced pole, reused transformer TD4-613. Josh Reid attended. | F3/F4 | WAIMAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 318 | 315 | 29610 | 0.090441 | 0.00028712 | 2015-01-30 | C | 0.090441 | 0.00028712 | 2015 | 2015-01-30 | C | 94 | 0.090441 | 0.00028712
1 | 3230717 | 2015-01-30 09:30 | 2015-01-30 14:58 | 328 | 24 | 7872 | 0.024076 | 7.3402e-05 | NAPA ID:05302 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > GREEN PARK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9884 | Liven new RMU 9884. Remove 11kV Switch 9059/1 associated cable jointing & testing. Works location: Inverness Drive, Pyes Pa, Tauranga. WO 10154255. | F3/F4 | GREEN PARK | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 328 | 325 | 7800 | 0.023825 | 7.3306e-05 | 2015-01-30 | B | 0.011912 | 3.6653e-05 | 2015 | 2015-01-30 | B | 24 | 0.023825 | 7.3306e-05
1 | 3419461 | 2015-01-30 10:00 | 2015-01-30 11:00 | 60 | 73 | 4380 | 0.013396 | 0.00022326 | NAPA ID:05583 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 582 | To change 11kV transformer fuses on transformer 582. Works Location: 44 Messenger Terrace, Oakura. WO 10146610. | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 4161 | 0.012709 | 0.00022297 | 2015-01-30 | B | 0.0063547 | 0.00011149 | 2015 | 2015-01-30 | B | 73 | 0.012709 | 0.00022297
1 | 3722326 | 2015-01-30 16:47 | 2015-01-30 20:28 | 220.5 | 1 | 220.5 | 0.00067438 | 3.0584e-06 | Restore Supply on Device X4022 | 11000 | UNPLANNED | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | X4022 | ADVISED SHAN AT SVS HUB. Isolated transformer to tap down to get better voltage. No materials. Karl Rodgers attended. | F4 | BULLS | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 220.5 | 217.5 | 217.5 | 0.00066434 | 3.0544e-06 | 2015-01-30 | C | 0.00066434 | 3.054e-06 | 2015 | 2015-01-30 | C | 1 | 0.00066434 | 3.0544e-06
1 | 3722431 | 2015-01-31 02:53 | 2015-01-31 05:24 | 151.05 | 123 | 17711.15 | 0.054168 | 0.00037619 | Restore Supply on Device C936 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 845780 | CB936 Tripped A and B Phase O/C. Line patrolled and branch located on line at pole 845780. Removed by hot stick. | F5 | ANNEDALE | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 143.9931 | 140.9931 | 17342.15 | 0.05297 | 0.00037569 | 2015-01-31 | C | 0.05297 | 0.00037569 | 2015 | 2015-01-31 | C | 123 | 0.05297 | 0.00037569
1 | 3722799 | 2015-01-31 04:36 | 2015-01-31 09:55 | 319.3 | 98 | 17413.2667 | 0.053257 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O1869 | Recloser RS9464 on Kerepehi CB 2 feeder tripped to L/O. Sectionalised and found fault between ABS IC1269 & IC1276. Replaced 1 faulty insulator at pole O1869. James Briar attended. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 177.6864 | 174.6864 | 17119.2667 | 0.052289 | 0.00029933 | 2015-01-31 | C | 0.052289 | 0.00029933 | 2015 | 2015-01-31 | C | 98 | 0.052289 | 0.00029933
1 | 3536397 | 2015-01-31 05:02 | 2015-01-31 06:24 | 82 | 1 | 82 | 0.00025079 | 3.0584e-06 | NAPA ID:06134 TP_LINTON GXP > TURITEA SUB > MASSEY | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/436 | Repair 11kv cable Crutch and clear transient earth voltages on Switch gear. Works location: Massey. WO 10155775. No outage job created due to 1 icp multiple transformers | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 82 | 79 | 79 | 0.0002413 | 3.0544e-06 | 2015-01-31 | B | 0.00012065 | 1.527e-06 | 2015 | 2015-01-31 | B | 1 | 0.0002413 | 3.0544e-06
1 | 3723135 | 2015-01-31 07:11 | 2015-01-31 09:08 | 117.3167 | 127 | 14420.3667 | 0.044104 | 0.00038842 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 840053 | Recloser 4200 tripped on A and B phase O/C. ABS 906 opened and branch removed from line at pole 840053. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 113.5462 | 110.5462 | 14039.3667 | 0.042882 | 0.00038791 | 2015-01-31 | C | 0.042882 | 0.00038791 | 2015 | 2015-01-31 | C | 127 | 0.042882 | 0.00038791
1 | 3723606 | 2015-01-31 07:45 | 2015-01-31 08:29 | 43.6 | 36 | 1569.6 | 0.0048005 | 0.0001101 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8393 | When doing planned NAPA job 6469 the top of one of the fuses at Fuse 8393 broke off. Isolation was made at 6406 and 8555 and repairs made. Replaced 1 X DDO. | F2 | KATERE 6 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 43.6 | 40.6 | 1461.6 | 0.0044643 | 0.00010996 | 2015-01-31 | C | 0.0044643 | 0.00010996 | 2015 | 2015-01-31 | C | 36 | 0.0044643 | 0.00010996
1 | 3628190 | 2015-01-31 08:15 | 2015-01-31 14:20 | 365 | 38 | 13870 | 0.04242 | 0.00011622 | NAPA ID:05311 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD5-033 | Replace conductor between ABS SD5-033 and SD5-032. Works location: Kairua Rd. WO# 10156589. | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 365 | 362 | 13756 | 0.042017 | 0.00011607 | 2015-01-31 | B | 0.021008 | 5.8034e-05 | 2015 | 2015-01-31 | B | 38 | 0.042017 | 0.00011607
1 | 3536405 | 2015-01-31 08:17 | 2015-01-31 09:49 | 92.1333 | 87 | 8015.6 | 0.024515 | 0.00026608 | NAPA ID:06135 TP_BUNNYTHORPE GXP > FEILDING SUB > WEST TOWN | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/308 | Repair HV cable T3/308 (Failed Partial Discharge Test). Works location: Wellesley St, Feilding. WO 10155775. | F3 | WEST TOWN | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 92.1333 | 89.1333 | 7754.6 | 0.023686 | 0.00026573 | 2015-01-31 | B | 0.011843 | 0.00013287 | 2015 | 2015-01-31 | B | 87 | 0.023686 | 0.00026573
1 | 3518750 | 2015-01-31 09:09 | 2015-01-31 14:56 | 347 | 1 | 347 | 0.0010613 | 3.0584e-06 | NAPA ID:06017 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4040 | Replace defected TX TC859. Works location: Hinuera Stone, SH 29, Hinuera. WO #10148293. | F4 | BUCKLAND RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 347 | 344 | 344 | 0.0010507 | 3.0544e-06 | 2015-01-31 | B | 0.00052536 | 1.527e-06 | 2015 | 2015-01-31 | B | 1 | 0.0010507 | 3.0544e-06
1 | 3724295 | 2015-01-31 15:12 | 2015-01-31 18:04 | 172.3 | 98 | 8609.1667 | 0.02633 | 0.00029973 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O1873 | Recloser 9464 L/O E/F. Sectionalised and found faulty insulator on pole O1873. Isolated between ABS IC1269 & IC1276. Replace insulator & re-livened. Colin Pepper and James Briar attended. | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 87.8486 | 84.8486 | 8315.1667 | 0.025398 | 0.00029933 | 2015-01-31 | C | 0.025398 | 0.00029933 | 2015 | 2015-01-31 | C | 98 | 0.025398 | 0.00029933
1 | 3724675 | 2015-01-31 17:13 | 2015-01-31 20:18 | 185 | 65 | 12025 | 0.036778 | 0.0001988 | Restore Supply on Device 6274 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6274 | Investigation found Recloser 6274 tripped (OMS No 3724675). Patrolled line and found transformer 4228T blown and requires replacement. Transformer replaced.See OMS 3724649 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 185 | 182 | 11830 | 0.036134 | 0.00019854 | 2015-01-31 | C | 0.036134 | 0.00019854 | 2015 | 2015-01-31 | C | 65 | 0.036134 | 0.00019854
1 | 3724922 | 2015-01-31 19:24 | 2015-02-01 00:11 | 287.0833 | 9 | 2713.1833 | 0.0082981 | 2.7526e-05 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44366 | Remove trees and repair lines at pole P44366. Repaired 2 conductors used +/- 5m conductor. Phil Barnes attended. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 301.4648 | 298.4648 | 2686.1833 | 0.0082047 | 2.749e-05 | 2015-01-31 | B | 0.0041024 | 1.3745e-05 | 2015 | 2015-01-31 | B | 9 | 0.0082047 | 2.749e-05
1 | 3725110 | 2015-01-31 21:51 | 2015-02-01 07:18 | 567.05 | 1 | 567.05 | 0.0017343 | 3.0584e-06 | Restore Supply on Device T1624 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7379 | Found 2 fuses blown at 7379 and reluctant to attempt restoration without a patrol because of the fire risk . Due to ground conditions unsafe to patrol in darkness and will be patrolled at first light . | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 567.05 | 564.05 | 564.05 | 0.0017228 | 3.0544e-06 | 2015-01-31 | C | 0.0017228 | 3.054e-06 | 2015 | 2015-01-31 | C | 1 | 0.0017228 | 3.0544e-06
1 | 3728220 | 2015-01-31 22:40 | 2015-02-01 16:50 | 1090.35 | 237 | 30220.5 | 0.092427 | 0.00072485 | Restore Supply on Device 10 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 790774 | CB10 Tripped B & C Phase O/C. Line patrolled and trees in lines located. Removed trees from in lines at pole 790774. Allen Cox attended. | F4 | NO 3 LINE | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 127.5127 | 124.5127 | 29509.5 | 0.090135 | 0.0007239 | 2015-01-31 | C | 0.090135 | 0.0007239 | 2015 | 2015-01-31 | C | 237 | 0.090135 | 0.0007239
1 | 3725121 | 2015-02-01 01:11 | 2015-02-01 03:50 | 159.2667 | 587 | 85209.4 | 0.26061 | 0.0017953 | Restore Supply on Device RP15 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | V13567 | Recloser RP15 tripped to L/O - E/F flag - line sectionalised & patrolled. Fault between Recloser and ABS IC383 - possom found & removed from pole V13567. Problem locating it due to off road sections of line - no back feeds were available while line patrol | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 145.1608 | 142.1608 | 83448.4 | 0.25489 | 0.0017929 | 2015-02-01 | C | 0.25489 | 0.0017929 | 2015 | 2015-02-01 | C | 587 | 0.25489 | 0.0017929
1 | 3725872 | 2015-02-01 07:18 | 2015-02-01 09:14 | 115.55 | 485 | 33339.3 | 0.10197 | 0.0014833 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755768 | CB6 tripped E/F. Auto Reclose disabled. Line patrolled and 1 phase of conductor found down at pole 755768. Rehang 1 Phase. Neil Woodhead & Wes Botha attended. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 68.7408 | 65.7408 | 31884.3 | 0.097388 | 0.0014814 | 2015-02-01 | C | 0.097388 | 0.0014814 | 2015 | 2015-02-01 | C | 485 | 0.097388 | 0.0014814
1 | 3726339 | 2015-02-01 07:19 | 2015-02-01 10:05 | 166.3167 | 52 | 1543.3167 | 0.0047201 | 0.00015904 | Restore Supply on Device X3143 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2550 | 9:04am 1R request for another faultman to assist to replace HV insulator at Fused ABS 2550. Replaced 1X Stand off Insulator & little bits and pieces. Allen Cox attended. | F2 | MARTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 29.6792 | 26.6792 | 1387.3167 | 0.0042375 | 0.00015883 | 2015-02-01 | C | 0.0042375 | 0.00015883 | 2015 | 2015-02-01 | C | 52 | 0.0042375 | 0.00015883
1 | 3620906 | 2015-02-01 08:06 | 2015-02-01 08:59 | 52.8333 | 106 | 5600.3333 | 0.017128 | 0.00032419 | NAPA ID:06137 TP_BUNNYTHORPE GXP > FEILDING SUB > WORKS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | T3-115 | Repair HV cable feeeding T3/115 ( Failed Partial Discharge Test). | F2 | WORKS | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 52.8333 | 49.8333 | 5282.3333 | 0.016134 | 0.00032377 | 2015-02-01 | B | 0.0080672 | 0.00016188 | 2015 | 2015-02-01 | B | 106 | 0.016134 | 0.00032377
1 | 3727115 | 2015-02-01 08:26 | 2015-02-01 09:30 | 63.7667 | 1 | 63.7667 | 0.00019503 | 3.0584e-06 | Restore Supply on Device 1357 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755765 | Neil advised same fault as OMS 3727115 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 63.7667 | 60.7667 | 60.7667 | 0.00018561 | 3.0544e-06 | 2015-02-01 | C | 0.00018561 | 3.054e-06 | 2015 | 2015-02-01 | C | 1 | 0.00018561 | 3.0544e-06
1 | 3727133 | 2015-02-01 09:12 | 2015-02-01 10:43 | 90.9667 | 1 | 90.9667 | 0.00027821 | 3.0584e-06 | Restore Supply on Device TC4958 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole O14398 | Replace 1 x 8 A H/V O/H Fuse link. | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90.9667 | 87.9667 | 87.9667 | 0.00026869 | 3.0544e-06 | 2015-02-01 | C | 0.00026869 | 3.054e-06 | 2015 | 2015-02-01 | C | 1 | 0.00026869 | 3.0544e-06
1 | 3727833 | 2015-02-01 09:38 | 2015-02-01 17:08 | 449.85 | 36 | 11742.0167 | 0.035912 | 0.0001101 | Restore Supply on Device 2792 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 792487 | Outage resulting from OMS Job 3727137 (CB3 A/R) line patrol. Line down located at pole 792487. Isolated beyond Fuses 2792. 1 x 25 Amp Fuse replaced and 5 metres of conductor. Karl Rogers attended. | F4 | UNION LINE | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 326.1671 | 323.1671 | 11634.0167 | 0.035535 | 0.00010996 | 2015-02-01 | C | 0.035535 | 0.00010996 | 2015 | 2015-02-01 | C | 36 | 0.035535 | 0.00010996
1 | 3727825 | 2015-02-01 09:52 | 2015-02-01 11:30 | 98.15 | 33 | 2183.7667 | 0.0066789 | 0.00010093 | Restore Supply on Device E27 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P14848 | Isolated beyond Fuses E27. Removed branch from lines using Hot Stick at pole P14848. NDR N300020. Shazil Khan attended. | F3/F4 | COLYTON | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 66.1747 | 63.1747 | 2084.7667 | 0.0063678 | 0.0001008 | 2015-02-01 | C | 0.0063678 | 0.0001008 | 2015 | 2015-02-01 | C | 33 | 0.0063678 | 0.0001008
1 | 3730579 | 2015-02-01 11:33 | 2015-02-01 14:33 | 179.8833 | 342 | 27054.5 | 0.082744 | 0.001046 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P15999 | CB 6 Tripped on E/F. Switching identified jumper resting on crossarm at pole P15999. Repairs made and feeder relivened. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 79.1067 | 76.1067 | 26028.5 | 0.079502 | 0.0010446 | 2015-02-01 | C | 0.079502 | 0.0010446 | 2015 | 2015-02-01 | C | 342 | 0.079502 | 0.0010446
1 | 3732433 | 2015-02-01 12:53 | 2015-02-01 15:45 | 172.5167 | 177 | 30535.45 | 0.09339 | 0.00054134 | Restore Supply on Device CB3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01001 | CB 3 Tripped B & C Phases O/C E/F. Auto reclose disabled - line patrol undertaken. Broken Polymer Strain located at pole P01001. Repaired and restored power. Phil Barnes attended. Used 1 x11kV Polymer. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 172.5167 | 169.5167 | 30004.45 | 0.091646 | 0.00054063 | 2015-02-01 | C | 0.091646 | 0.00054063 | 2015 | 2015-02-01 | C | 177 | 0.091646 | 0.00054063
1 | 3733267 | 2015-02-01 15:15 | 2015-02-01 17:04 | 109.4333 | 3 | 263.1167 | 0.00080472 | 9.1753e-06 | Restore Supply on Device T3630 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7095 | 2 X 10 Amp H/T Fuses at Fuses 7095 | F4 | LONGBUSH | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 87.7056 | 84.7056 | 254.1167 | 0.00077618 | 9.1633e-06 | 2015-02-01 | C | 0.00077618 | 9.163e-06 | 2015 | 2015-02-01 | C | 3 | 0.00077618 | 9.1633e-06
1 | 3744908 | 2015-02-01 18:54 | 2015-02-01 21:04 | 130 | 108 | 14040 | 0.04294 | 0.00033031 | Restore Supply on Device M79 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | M79 | Outage re-created to capture all ICP's effected by M79 Tripping. See 3733863. Found Recloser M79 Open. Closed on load and line patrol carried out with no apparent fault found. Jeff Roberts attended. Email to Jo to check SAIDI. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 130 | 127 | 13716 | 0.041894 | 0.00032988 | 2015-02-01 | C | 0.041894 | 0.00032988 | 2015 | 2015-02-01 | C | 108 | 0.041894 | 0.00032988
1 | 3733863 | 2015-02-01 18:55 | 2015-02-01 21:04 | 129.1667 | 1 | 129.1667 | 0.00039505 | 3.0584e-06 | Restore Supply on Device T3/30 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | M79 | Found recloser M79 Open , Closed on load and line patrol carried out with no apparent fault found. Jeff Roberts attended. Email to Jo to check SAIDI. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 129.1667 | 126.1667 | 126.1667 | 0.00038537 | 3.0544e-06 | 2015-02-01 | C | 0.00038537 | 3.054e-06 | 2015 | 2015-02-01 | C | 1 | 0.00038537 | 3.0544e-06
1 | 3738507 | 2015-02-01 22:07 | 2015-02-02 16:53 | 1126.3 | 108 | 83295.3333 | 0.25475 | 0.00033031 | Restore Supply on Device T3/30 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P02479 | 7.05am advised Tallia at svs hub that there are a few jobs in tikorangi road from last night 2.31pm Anjay called asking if we can call customer to see if they have power at 330 Pryces Line as he is unable to locate 330. called customers celphone twice no | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 771.2531 | 768.2531 | 82971.3333 | 0.25343 | 0.00032988 | 2015-02-01 | C | 0.25343 | 0.00032988 | 2015 | 2015-02-01 | C | 108 | 0.25343 | 0.00032988
1 | 3738492 | 2015-02-02 06:45 | 2015-02-03 07:41 | 1495.7845 | 1 | 1495.8 | 0.0045748 | 3.0584e-06 | Restore Supply on Device 7054P | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P02479 | Couldn't inference due to lost network details (see Job Summary). Originally grouped to parent 3738507. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 1495.8 | 1492.8 | 1492.8 | 0.0045596 | 3.0544e-06 | 2015-02-02 | C | 0.0045596 | 3.054e-06 | 2015 | 2015-02-02 | C | 1 | 0.0045596 | 3.0544e-06
1 | 3738527 | 2015-02-02 07:09 | 2015-02-02 09:32 | 143.1333 | 2 | 206.5833 | 0.00063182 | 6.1168e-06 | Restore Supply on Device TC2-145 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sc2129 | *** please check with FM if oms 3744076 is part of this job. water pump at same address *** replace 2 x 6 amp ht ddo fuse. cause: unknown. 2 out 3 phase. fuse sc2129. No other assets repaired or replaced on site. Adjacent assets are checked and are up to | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 103.2917 | 100.2917 | 200.5833 | 0.00061267 | 6.1088e-06 | 2015-02-02 | C | 0.00061267 | 6.109e-06 | 2015 | 2015-02-02 | C | 2 | 0.00061267 | 6.1088e-06
1 | 3738585 | 2015-02-02 09:30 | 2015-02-02 11:36 | 126 | 16 | 2016 | 0.0061658 | 4.8935e-05 | Restore Supply on Device TC2288 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G0170 | 8.00AM - advised smc that it is a low hanging line, still treating it as urgnet but it is not a lines down. broken main lv cross arm. pole # g0170 and tx # t2288. Transformer TC2288 Isolated to work on the LV as no LV isolators fitted to transformer Mat | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 126 | 123 | 1968 | 0.0060111 | 4.8871e-05 | 2015-02-02 | C | 0.0060111 | 4.8871e-05 | 2015 | 2015-02-02 | C | 16 | 0.0060111 | 4.8871e-05
1 | 3628287 | 2015-02-02 09:36 | 2015-02-02 11:16 | 100.3167 | 9 | 902.85 | 0.0027613 | 2.7526e-05 | NAPA ID:06120 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2104 | Replacing crossarms at various sites. Works location: Castle Rock Rd Manaia. WO 30000253 | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.3167 | 97.3167 | 875.85 | 0.0026752 | 2.749e-05 | 2015-02-02 | B | 0.0013376 | 1.3745e-05 | 2015 | 2015-02-02 | B | 9 | 0.0026752 | 2.749e-05
1 | 3738548 | 2015-02-02 11:25 | 2015-02-02 15:56 | 270.5 | 30 | 8107.25 | 0.024795 | 9.1753e-05 | Restore Supply on Device TC698 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 13398 | FM advise: broken double terminator cross arms on 11 kv. Broken x arm at pole 13398. Isolation at ABS 323 ( no back feeds ) . Arms replaced all service restored. Materials 2 x 11kV Arms complete , 4 x Polymers, 2 x dead ends. This has OMS child 3744845 wh | F4 | WARDVILLE | WALTON SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 270.2417 | 267.2417 | 8017.25 | 0.024488 | 9.1633e-05 | 2015-02-02 | C | 0.024488 | 9.1633e-05 | 2015 | 2015-02-02 | C | 30 | 0.024488 | 9.1633e-05
1 | 3745631 | 2015-02-02 18:53 | 2015-02-03 12:01 | 1027.8667 | 158 | 105429.45 | 0.32245 | 0.00048323 | Restore Supply on Device 5475 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 764733 | Pole down Not able to Change as it a River bank and may need a chopper to help get wire back up Tenix going out at First light to work on this fault. Large pine tree bought down lines snapping off the pole. Line runs across country at this point so access | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 667.275 | 664.275 | 104955.45 | 0.32058 | 0.0004826 | 2015-02-02 | C | 0.32058 | 0.0004826 | 2015 | 2015-02-02 | C | 158 | 0.32058 | 0.0004826
1 | 3748964 | 2015-02-02 23:19 | 2015-02-03 01:39 | 140.4167 | 714 | 59896.25 | 0.18319 | 0.0021837 | Restore Supply on Device C953 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 818569 | C953 tripped. Line patrolled and branch located on line. Cut Branch away from line. Adrian Marshall attended. | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 83.8883 | 80.8883 | 57754.25 | 0.17641 | 0.0021809 | 2015-02-02 | C | 0.17641 | 0.0021809 | 2015 | 2015-02-02 | C | 714 | 0.17641 | 0.0021809
1 | 3750096 | 2015-02-03 00:20 | 2015-02-03 00:33 | 13.0833 | 45 | 588.75 | 0.0018006 | 0.00013763 | Restore Supply on Device C625 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | C625 | Recloser C625 auto reclosed. Momentary Loss of Supply. Line not patrolled. Closed in After 15 Minutes. | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 13.0833 | 10.0833 | 453.75 | 0.0013859 | 0.00013745 | 2015-02-03 | C | 0.0013859 | 0.00013745 | 2015 | 2015-02-03 | C | 45 | 0.0013859 | 0.00013745
1 | 3761484 | 2015-02-03 05:41 | 2015-02-03 11:00 | 318.45 | 108 | 13603.6167 | 0.041606 | 0.00033031 | Restore Supply on Device T3/30 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01858 | Tripping on Recloser M79 (Ongoing fault). Area patrolled and sectionalised with a faulty insulator found (Isolation between ABS M72 and M73). 1 Insulator, pin replaced and relivened OK. N Lake attended. (Email has been sent to Systems & Performance Engine | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 125.9594 | 122.9594 | 13279.6167 | 0.040562 | 0.00032988 | 2015-02-03 | C | 0.040562 | 0.00032988 | 2015 | 2015-02-03 | C | 108 | 0.040562 | 0.00032988
1 | 3762388 | 2015-02-03 07:29 | 2015-02-03 08:59 | 89.8 | 1 | 89.8 | 0.00027465 | 3.0584e-06 | Restore Supply on Device TP1694 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 7.31am - advised smc. made safe, screwed lid back on and fuse mounting is needing replacement, has amber 3 defected. new subdivision no one fed from gyro box yet. NDR # 34190 No other assets repaired or replaced and all adjacent assets checked and are | F3 | GLOUCESTER RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 89.8 | 86.8 | 86.8 | 0.00026512 | 3.0544e-06 | 2015-02-03 | C | 0.00026512 | 3.054e-06 | 2015 | 2015-02-03 | C | 1 | 0.00026512 | 3.0544e-06
1 | 3494978 | 2015-02-03 08:18 | 2015-02-03 14:40 | 382.45 | 1 | 382.45 | 0.0011697 | 3.0584e-06 | NAPA ID:05714 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 832725 | At pole 832725 replace with new structure and transformer. Works location: Upper Plain Rd Masterton. WO 10170883. | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 382.45 | 379.45 | 379.45 | 0.001159 | 3.0544e-06 | 2015-02-03 | B | 0.0005795 | 1.527e-06 | 2015 | 2015-02-03 | B | 1 | 0.001159 | 3.0544e-06
1 | 3762582 | 2015-02-03 08:53 | 2015-02-03 11:11 | 137.9833 | 14 | 1266.6 | 0.0038738 | 4.2818e-05 | Restore Supply on Device Q62 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q62 | Fuses Q62 tripped - no flags. Line patrolled and Fuses Replaced. 2 x 6 amp HV Fuses at section Fuses Q62 HV OH. No other assets repaired or replaced and all adjacent assets checked and are ok / up to Powerco standard? T Pocock attended. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 90.4714 | 87.4714 | 1224.6 | 0.0037404 | 4.2762e-05 | 2015-02-03 | C | 0.0037404 | 4.2762e-05 | 2015 | 2015-02-03 | C | 14 | 0.0037404 | 4.2762e-05
1 | 3628308 | 2015-02-03 09:15 | 2015-02-03 13:32 | 256.75 | 110 | 28242.5 | 0.086377 | 0.00033643 | NAPA ID:05894 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-028 | REPLACE HV ARMS ALONG MANOEKA ROAD. Works location: Manoeka Rd. WO 10148383 | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 256.75 | 253.75 | 27912.5 | 0.085257 | 0.00033599 | 2015-02-03 | B | 0.042628 | 0.00016799 | 2015 | 2015-02-03 | B | 110 | 0.085257 | 0.00033599
1 | 3623227 | 2015-02-03 09:30 | 2015-02-03 11:14 | 103.75 | 3 | 311.25 | 0.00095193 | 9.1753e-06 | NAPA ID:06148 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 794025 | Straighten and reblock tap off pole 794025 and resag conductor. Works location; Whangaehu Beach Rd. WO 10141993. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 103.75 | 100.75 | 302.25 | 0.0009232 | 9.1633e-06 | 2015-02-03 | B | 0.0004616 | 4.582e-06 | 2015 | 2015-02-03 | B | 3 | 0.0009232 | 9.1633e-06
1 | 3623254 | 2015-02-03 09:47 | 2015-02-03 13:35 | 228.4333 | 44 | 10051.0667 | 0.03074 | 0.00013457 | NAPA ID:06147 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 688 | Isolation of 11kV line for tree cutting. Works location: SH4 Parapara Rd. PPPD 47008. | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 228.4333 | 225.4333 | 9919.0667 | 0.030297 | 0.00013439 | 2015-02-03 | B | 0.015149 | 6.7197e-05 | 2015 | 2015-02-03 | B | 44 | 0.030297 | 0.00013439
1 | 3487208 | 2015-02-03 09:51 | 2015-02-03 15:02 | 311.3333 | 25 | 7783.3333 | 0.023805 | 7.6461e-05 | NAPA ID:05106 TP_STRATFORD GXP > DOUGLAS SUB > TOKO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4459T | Replace 4459T Tx 10m pole & half structure with 11m pole + Add extra 11m pole to fix LV clearance issues across tanker track. Works location: Gordon Rd. WO 10160059. | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 311.3333 | 308.3333 | 7708.3333 | 0.023545 | 7.6361e-05 | 2015-02-03 | B | 0.011772 | 3.818e-05 | 2015 | 2015-02-03 | B | 25 | 0.023545 | 7.6361e-05
1 | 3764899 | 2015-02-03 10:46 | 2015-02-03 15:51 | 304.55 | 665 | 61306.2667 | 0.1875 | 0.0020339 | Restore Supply on Device 9 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P39269 | CB 9 A/R, L/O, O/C. Trees Contacting Lines between Poles P39267 & P39269. Area iaolated between ABS D76 & D77 & backfeed installed via ABS D75. Nick Lake also attend | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 92.1899 | 89.1899 | 59311.2667 | 0.18116 | 0.0020312 | 2015-02-03 | C | 0.18116 | 0.0020312 | 2015 | 2015-02-03 | C | 665 | 0.18116 | 0.0020312
1 | 3766184 | 2015-02-03 11:07 | 2015-02-03 13:02 | 115.0833 | 1 | 115.0833 | 0.00035197 | 3.0584e-06 | Restore Supply on Device T6/170 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | T6/170 | crn of Cascade Cres and Egmont place - Palmerston North - Door open on TX and wires exposed - please check for safety 11:10am Called Talia at the hub. FM advise: tx door was open, off completely. appears kids have been jumping on it. used banded to | F3 | PIONEER | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 115.0833 | 112.0833 | 112.0833 | 0.00034235 | 3.0544e-06 | 2015-02-03 | C | 0.00034235 | 3.054e-06 | 2015 | 2015-02-03 | C | 1 | 0.00034235 | 3.0544e-06
1 | 3768489 | 2015-02-03 13:39 | 2015-02-03 16:12 | 153.2167 | 1273 | 58460.5667 | 0.1788 | 0.0038934 | Restore Supply on Device C828 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3826 | Advised by Gavin Gray of Fire at Regulator site T3826 on Masterton-Castlepoint Rd. (This site was supplying both Awatoitoi and Tinui Subs due to planned 33kV outages). Urgent outage required, Teoreore CB828 open from NOC causing loss of supply to Tinui an | F4 | TAUWERU | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 45.9235 | 42.9235 | 54641.5667 | 0.1669 | 0.0038883 | 2015-02-03 | C | 0.1669 | 0.0038883 | 2015 | 2015-02-03 | C | 1273 | 0.1669 | 0.0038883
1 | 3768369 | 2015-02-03 14:28 | 2015-02-03 16:23 | 114.5667 | 109 | 11644.0333 | 0.035612 | 0.00033337 | Restore Supply on Device T42/2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46619, P46623 | Tripping on Recloser T42/2. Patrol found twisted crosarm between links T31 and T34. (Open for isolation - no transformers in this area). Supply restored with backfeed at ABS V19. Repairs to be carried out tomorrow - manpower shortage due to stormy condit | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 106.826 | 103.826 | 11317.0333 | 0.034567 | 0.00033293 | 2015-02-03 | C | 0.034567 | 0.00033293 | 2015 | 2015-02-03 | C | 109 | 0.034567 | 0.00033293
1 | 3770518 | 2015-02-03 17:14 | 2015-02-03 23:02 | 347.35 | 1 | 347.35 | 0.0010623 | 3.0584e-06 | Restore Supply on Device T4/114 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13213 | RETAILER ADVISES 216 ZIG ZAG RD NO POWER. Found a Floating conductor at Pole P13213 | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 347.35 | 344.35 | 344.35 | 0.0010518 | 3.0544e-06 | 2015-02-03 | C | 0.0010518 | 3.054e-06 | 2015 | 2015-02-03 | C | 1 | 0.0010518 | 3.0544e-06
1 | 3770329 | 2015-02-03 19:15 | 2015-02-03 20:35 | 80.25 | 47 | 3771.5 | 0.011535 | 0.00014375 | Restore Supply on Device X839 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | 794465 | Power pole on the paddock has fallen down, pole is about 0.5km from the property - go into the cattle yards and turn a hard left 1821 Turakina Valley Road, Wanganui 3:38pm advised hub replacing 11 kv pole pole 794465 ndr 41965 fm will stay at site requ | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 80.2447 | 77.2447 | 3630.5 | 0.011089 | 0.00014356 | 2015-02-03 | C | 0.011089 | 0.00014356 | 2015 | 2015-02-03 | C | 47 | 0.011089 | 0.00014356
1 | 3770890 | 2015-02-04 02:43 | 2015-02-04 06:02 | 199.1667 | 2 | 243.0667 | 0.0007434 | 6.1168e-06 | Restore Supply on Device 716 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8295 | 2 X 10 amp H/T Fuses. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 121.5333 | 118.5333 | 237.0667 | 0.0007241 | 6.1088e-06 | 2015-02-04 | C | 0.0007241 | 6.109e-06 | 2015 | 2015-02-04 | C | 2 | 0.0007241 | 6.1088e-06
1 | 3771157 | 2015-02-04 08:13 | 2015-02-04 09:48 | 95.0333 | 1 | 95.0333 | 0.00029065 | 3.0584e-06 | Restore Supply on Device T1109 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848261 | found 2 ht fuses blown 848261 - patrolled line, replaced and relivened 2x 8amp No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 95.0333 | 92.0333 | 92.0333 | 0.00028111 | 3.0544e-06 | 2015-02-04 | C | 0.00028111 | 3.054e-06 | 2015 | 2015-02-04 | C | 1 | 0.00028111 | 3.0544e-06
1 | 3721854 | 2015-02-04 08:30 | 2015-02-04 14:32 | 361.8167 | 171 | 24703.6 | 0.075554 | 0.00052299 | NAPA ID:06644 TP_WAIKINO GXP > WHANGAMATA SUB > HETHERINGTON RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6134 | Replace Transformer TC6143. Note this NAPA application replaces 5425 & was created to rewrite switching due to generation being supplied for shops fed from TX TC6134 - the advertising is still under 5425 which has been cancelled . | F3 | HETHERINGTON RD | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 144.4655 | 141.4655 | 24190.6 | 0.073888 | 0.00052231 | 2015-02-04 | B | 0.036944 | 0.00026115 | 2015 | 2015-02-04 | B | 171 | 0.073888 | 0.00052231
1 | 3487123 | 2015-02-04 08:35 | 2015-02-04 14:06 | 330.4 | 83 | 27423.2 | 0.083872 | 0.00025385 | NAPA ID:05401 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 721862 | Replacing 22, 11kv poles between poles 721862 and 721898. Works location: Ohangai Rd, Normanby. WO 10141791. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 330.4 | 327.4 | 27174.2 | 0.083002 | 0.00025352 | 2015-02-04 | B | 0.041501 | 0.00012676 | 2015 | 2015-02-04 | B | 83 | 0.083002 | 0.00025352
1 | 3634290 | 2015-02-04 09:16 | 2015-02-04 14:52 | 335.8833 | 274 | 92032.0333 | 0.28147 | 0.00083801 | NAPA ID:05935 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9632 | Replacing crossarms and hardware. Works location; Black Jack Rd, Kuaotunu. WO 10148314. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 335.8833 | 332.8833 | 91210.0333 | 0.27859 | 0.00083691 | 2015-02-04 | B | 0.1393 | 0.00041846 | 2015 | 2015-02-04 | B | 274 | 0.27859 | 0.00083691
1 | 3487155 | 2015-02-04 09:52 | 2015-02-04 12:42 | 170.6333 | 12 | 2047.6 | 0.0062624 | 3.6701e-05 | NAPA ID:05458 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 747458 | Replace Xarm on pole 747458. Works location: Hydro Rd. WO 10152599. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 170.6333 | 167.6333 | 2011.6 | 0.0061443 | 3.6653e-05 | 2015-02-04 | B | 0.0030721 | 1.8327e-05 | 2015 | 2015-02-04 | B | 12 | 0.0061443 | 3.6653e-05
1 | 3271272 | 2015-02-04 10:38 | 2015-02-05 15:08 | 1710.15 | 10 | 816.2833 | 0.0024965 | 3.0584e-05 | NAPA ID:05312 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Mikkelsen Rd Springdale feeder | Transfer of Mikkelsen Rd Substation, Springdale feeder from old switchboard to new. Existing connection to 9900/10, new connection to new CB8. This is being achieved by rerouting and jointing cable if necessary. Works location: Mikkelsen Rd Substation. WO | F4 | SPRINGDALE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 81.6283 | 78.6283 | 786.2833 | 0.0024016 | 3.0544e-05 | 2015-02-04 | B | 0.0012008 | 1.5272e-05 | 2015 | 2015-02-04 | B | 10 | 0.0024016 | 3.0544e-05
1 | 3773720 | 2015-02-04 10:46 | 2015-02-04 12:03 | 77.7 | 1 | 77.7 | 0.00023764 | 3.0584e-06 | Restore Supply on Device X2059 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | X2059 | Replace 3 amp HT fuse. 1 out 3 phases. Transformer X2059. Cause: Possum. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 77.7 | 74.7 | 74.7 | 0.00022817 | 3.0544e-06 | 2015-02-04 | C | 0.00022817 | 3.054e-06 | 2015 | 2015-02-04 | C | 1 | 0.00022817 | 3.0544e-06
1 | 3774352 | 2015-02-04 14:30 | 2015-02-04 19:08 | 277.5833 | 2 | 528.5 | 0.0016164 | 6.1168e-06 | Restore Supply on Device T4126 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 811438, 8158 | Please check if OMS 3774359 related & 3774368. 117 HAURANGI ROAD, MARTINBOROUGH. 2818 RUAKOKOPATUNA ROAD, - advised Tallia at svs hub of the other 2 jobs. 236 Haurangi Road advised Shannon at SVS hub of added job. Check line fuses 8179 - adv at Tallia SV | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 264.25 | 261.25 | 522.5 | 0.0015959 | 6.1088e-06 | 2015-02-04 | C | 0.0015959 | 6.109e-06 | 2015 | 2015-02-04 | C | 2 | 0.0015959 | 6.1088e-06
1 | 3774387 | 2015-02-04 15:02 | 2015-02-04 18:32 | 209.7833 | 1 | 209.7833 | 0.00064161 | 3.0584e-06 | Restore Supply on Device T436 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8158 | Please check if OMS 3774359 related & 3774368. 117 HAURANGI ROAD, MARTINBOROUGH. 2818 RUAKOKOPATUNA ROAD, - advised Tallia at svs hub of the other 2 jobs. 236 Haurangi Road advised Shannon at SVS hub of added job. Check line fuses 8179 - adv at Tallia SV | F3 | DYERVILLE | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 209.7833 | 206.7833 | 206.7833 | 0.0006316 | 3.0544e-06 | 2015-02-04 | C | 0.0006316 | 3.054e-06 | 2015 | 2015-02-04 | C | 1 | 0.0006316 | 3.0544e-06
1 | 3774710 | 2015-02-04 15:28 | 2015-02-04 17:56 | 148.8333 | 1 | 148.8333 | 0.0004552 | 3.0584e-06 | Restore Supply on Device X1641 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT TREE CONTACT | 810383 | 2 X HT FUSE BLOWN DUE TO TREES AND RE- LOADED LV SIDE FUSE TS CORRECT SIZE 30 AMP. TREES INSIDE GROWTH ZONE IS GOING TO CONTACT TREE TRIMMERS TOMORROW. | F4 | MANGAWEKA | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 148.8333 | 145.8333 | 145.8333 | 0.00044544 | 3.0544e-06 | 2015-02-04 | C | 0.00044544 | 3.054e-06 | 2015 | 2015-02-04 | C | 1 | 0.00044544 | 3.0544e-06
1 | 3775049 | 2015-02-04 17:14 | 2015-02-04 18:33 | 78.9833 | 1 | 78.9833 | 0.00024156 | 3.0584e-06 | Restore Supply on Device T9/416 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | I32 | Reports of no power found CB I32 tripped. Reclosed OK. Windy in area. Trevor Pocock attended. | F4 | RONGOMAI | ALFREDTON SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 78.9833 | 75.9833 | 75.9833 | 0.00023209 | 3.0544e-06 | 2015-02-04 | C | 0.00023209 | 3.054e-06 | 2015 | 2015-02-04 | C | 1 | 0.00023209 | 3.0544e-06
1 | 3775780 | 2015-02-04 20:42 | 2015-02-05 00:46 | 244.5 | 130 | 5066.75 | 0.015496 | 0.00039759 | Restore Supply on Device 5270 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762618 | Outage required from ABS 5720 and 5310 to repair a broken DDO at Transformer 3086T. All 3 DDO replaced as in poor condition (2 Amp rating). Brent Moratti attended. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 38.975 | 35.975 | 4676.75 | 0.014285 | 0.00039708 | 2015-02-04 | C | 0.014285 | 0.00039707 | 2015 | 2015-02-04 | C | 130 | 0.014285 | 0.00039708
1 | 3775911 | 2015-02-04 23:19 | 2015-02-05 02:05 | 166 | 107 | 3154 | 0.0096463 | 0.00032725 | Restore Supply on Device 2621 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 709806 | Auto-reclose on CB 4196/2 on E/F, C Phase O/C. Patrol carried out from fuses 2620 due to eatlier fault. Branch found on line at Pole 789806 which required an isolation at fuses 2620 to safely remove. Relivened OK. NOTE: CB4196 hat tripped earlie (note a | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 29.4766 | 26.4766 | 2833 | 0.0086532 | 0.00032682 | 2015-02-04 | C | 0.0086532 | 0.00032682 | 2015 | 2015-02-04 | C | 107 | 0.0086532 | 0.00032682
1 | 3776010 | 2015-02-05 01:45 | 2015-02-05 04:31 | 165.7167 | 56 | 8920.1833 | 0.027282 | 0.00017127 | Restore Supply on Device 4402T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 4915 | Reports of no power found Recloser CB4915 had tripped (E/F indication on site). Area sectionailsed and restored OK. Many Opossums in area. Patrolled, nothing found. Phil Webby attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 159.289 | 156.289 | 8752.1833 | 0.026733 | 0.00017105 | 2015-02-05 | C | 0.026733 | 0.00017105 | 2015 | 2015-02-05 | C | 56 | 0.026733 | 0.00017105
1 | 3776660 | 2015-02-05 07:19 | 2015-02-05 11:32 | 252.9167 | 35 | 2462.9167 | 0.0075326 | 0.00010704 | Restore Supply on Device C929 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810728 | 11kv joint failed due to old age. Used clamp, 1m of 16mm copper wire, 1 x 16mm sleeve. pole 810728. FM advise: provided full list to control, worked through control. | F4 | OTARAIA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 70.369 | 67.369 | 2357.9167 | 0.0072021 | 0.0001069 | 2015-02-05 | C | 0.0072021 | 0.0001069 | 2015 | 2015-02-05 | C | 35 | 0.0072021 | 0.0001069
1 | 3775637 | 2015-02-05 08:42 | 2015-02-05 15:22 | 400 | 3 | 1200 | 0.0036701 | 9.1753e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1495 | RADIO SITE, TX STRUCTURE BROKEN AT PRESENT HELD BY TRACTOR. OMS 2774785 PLEASE SEND JASON HALL. A TLB was made at pole 797194 to replace the transformer T1495 structure. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 400 | 397 | 1191 | 0.0036378 | 9.1633e-06 | 2015-02-05 | B | 0.0018189 | 4.582e-06 | 2015 | 2015-02-05 | B | 3 | 0.0036378 | 9.1633e-06
1 | 3668911 | 2015-02-05 08:43 | 2015-02-05 15:48 | 424.9 | 44 | 18695.6 | 0.057179 | 0.00013457 | NAPA ID:05899 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 222877 | REPLACE HV ARMS ALONG TE PUKE QUARRY ROAD. W/O 10148383 | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 424.9 | 421.9 | 18563.6 | 0.056701 | 0.00013439 | 2015-02-05 | B | 0.028351 | 6.7197e-05 | 2015 | 2015-02-05 | B | 44 | 0.056701 | 0.00013439
1 | 3617434 | 2015-02-05 08:45 | 2015-02-05 13:49 | 303.6 | 56 | 5180.9333 | 0.015845 | 0.00017127 | NAPA ID:05741 TP_HINUERA GXP > TIRAU SUB > PROSPECT ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3784/B | To relocate 4 11kV cable for new building in the Tirau substation | F4 | PROSPECT ST | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 92.5167 | 89.5167 | 5012.9333 | 0.015312 | 0.00017105 | 2015-02-05 | B | 0.0076558 | 8.5524e-05 | 2015 | 2015-02-05 | B | 56 | 0.015312 | 0.00017105
1 | 3535440 | 2015-02-05 09:10 | 2015-02-05 17:20 | 490 | 52 | 15391 | 0.047072 | 0.00015904 | NAPA ID:03667 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P32882 | Change 3 x poles, 1 x 11kv tap pole 1 x pole with links L30 and 1 x T1/293 new TX and pole. Works location: SH 1 Oroua Downs WO 10162444 This job could not be completed under the Live Line due to high winds and a shutdown was needed between ABS's L2 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 295.9808 | 292.9808 | 15235 | 0.046534 | 0.00015883 | 2015-02-05 | B | 0.023267 | 7.9415e-05 | 2015 | 2015-02-05 | B | 52 | 0.046534 | 0.00015883
1 | 3705796 | 2015-02-05 09:19 | 2015-02-05 14:53 | 333.7667 | 230 | 76639.5333 | 0.2344 | 0.00070344 | NAPA ID:05916 TP_WAIKINO GXP > PAEROA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 312 | Replace crossarms on 33kV 312 Waikino/Paeroa Line. Works location: Waikino/Paeroa. WO 300000074. | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 333.2154 | 330.2154 | 75949.5333 | 0.23198 | 0.00070252 | 2015-02-05 | B | 0.11599 | 0.00035126 | 2015 | 2015-02-05 | B | 230 | 0.23198 | 0.00070252
1 | 3536168 | 2015-02-05 09:20 | 2015-02-05 10:57 | 96.6167 | 4 | 386.4667 | 0.001182 | 1.2234e-05 | NAPA ID:06023 TP_PIAKO GXP > PIAKO SUB > MVILLE SOUTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I1118 | Replace x-arm at pole I1118. Works location: Snell St, Morrinsville. WO 10161855. | F3 | MVILLE SOUTH | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 96.6167 | 93.6167 | 374.4667 | 0.0011438 | 1.2218e-05 | 2015-02-05 | B | 0.00057189 | 6.109e-06 | 2015 | 2015-02-05 | B | 4 | 0.0011438 | 1.2218e-05
1 | 3776559 | 2015-02-05 09:26 | 2015-02-05 11:19 | 112.5667 | 1 | 112.5667 | 0.00034428 | 3.0584e-06 | Restore Supply on Device T3943 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | 848549 | re-terminate staywire at 11kv pole 848549. cause: bulls in paddock rubbing on it. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 112.5667 | 109.5667 | 109.5667 | 0.00033466 | 3.0544e-06 | 2015-02-05 | C | 0.00033466 | 3.054e-06 | 2015 | 2015-02-05 | C | 1 | 0.00033466 | 3.0544e-06
1 | 3623314 | 2015-02-05 10:45 | 2015-02-05 12:56 | 131 | 4 | 524 | 0.0016026 | 1.2234e-05 | NAPA ID:06175 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 788570 | Isolation of 11kV lines for tree cutting at poles 788570 /71. Works location: Mataroa Rd SH1 PPPD 53678. Job started late due to faultman in area were on standdown. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 131 | 128 | 512 | 0.0015639 | 1.2218e-05 | 2015-02-05 | B | 0.00078193 | 6.109e-06 | 2015 | 2015-02-05 | B | 4 | 0.0015639 | 1.2218e-05
1 | 3668926 | 2015-02-05 13:10 | 2015-02-05 14:58 | 108.1167 | 2 | 216.2333 | 0.00066133 | 6.1168e-06 | NAPA ID:02851 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228420 | To replace arms on poles 228420, 228421 & 228422. Works location; Pongakawa Bush Rd. WO 477863 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 108.1167 | 105.1167 | 210.2333 | 0.00064214 | 6.1088e-06 | 2015-02-05 | B | 0.00032107 | 3.054e-06 | 2015 | 2015-02-05 | B | 2 | 0.00064214 | 6.1088e-06
1 | 3778080 | 2015-02-05 17:13 | 2015-02-05 19:44 | 151.6 | 632 | 63547.3833 | 0.19435 | 0.0019329 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 9281 | Tree Branch fallen across Recloser 9281. Removed and feeder restored | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 100.5497 | 97.5497 | 61651.3833 | 0.18831 | 0.0019304 | 2015-02-05 | C | 0.18831 | 0.0019304 | 2015 | 2015-02-05 | C | 632 | 0.18831 | 0.0019304
1 | 3779840 | 2015-02-05 19:14 | 2015-02-06 00:36 | 322.3 | 1446 | 60780.0333 | 0.18589 | 0.0044225 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | P12998 | Report of Lines down at 2 Symons St Waihi.1 HV Line Down and 3 LV Lines down. Tree through lines at pole P12998. NDR # 15186. 6 7064 Sleeves and less than 1m 7064 wire used. Nick Hyland attended. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 42.0332 | 39.0332 | 56442.0333 | 0.1724 | 0.0044167 | 2015-02-05 | C | 0.1724 | 0.0044167 | 2015 | 2015-02-05 | C | 1446 | 0.1724 | 0.0044167
1 | 3780763 | 2015-02-05 23:01 | 2015-02-06 03:46 | 285.4333 | 309 | 43040.6833 | 0.13164 | 0.00094505 | Restore Supply on Device PU4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 704054 | Tripping on Pungarehu CB PU4 on O/C Phase A, B, C. Feeder patrolled ansd sectionalised. Wind blown tree branch found on Puniho Rd, removed OK but some conductor damage required repair (Several broken strands). Isolation between ABS PU413 and PU203. Repair | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 139.2902 | 136.2902 | 42113.6833 | 0.12863 | 0.00094382 | 2015-02-05 | C | 0.12863 | 0.00094382 | 2015 | 2015-02-05 | C | 309 | 0.12863 | 0.00094382
1 | 3780729 | 2015-02-05 23:11 | 2015-02-06 00:42 | 91 | 20 | 1820 | 0.0055663 | 6.1168e-05 | Restore Supply on Device 511 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 752504 | Outage required between ABS 6741, ABS 208 and Mangorie CB 6777/5 to repair a blown HT jumper at fuses 8278. (Back feed at Sw/Gear 12026/3). Repairs carried out and relivened OK. Arthur Botha attended. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 91 | 88 | 1760 | 0.0053758 | 6.1088e-05 | 2015-02-05 | C | 0.0053758 | 6.1088e-05 | 2015 | 2015-02-05 | C | 20 | 0.0053758 | 6.1088e-05
1 | 3782336 | 2015-02-06 02:33 | 2015-02-06 05:11 | 158.3167 | 417 | 65802.6 | 0.20125 | 0.0012754 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 766078 | Tripping on CB4 Aramoho Riverside feeder. Blown Insulator found on corner of Lowther and London St. Isolation required from ABS 1393 to CB4 to replace 2 blown insulators. Relivened OK. Roger Blan attended. | F3 | ARAMOHO RIVERSIDE | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 157.8 | 154.8 | 64551.6 | 0.19717 | 0.0012737 | 2015-02-06 | C | 0.19717 | 0.0012737 | 2015 | 2015-02-06 | C | 417 | 0.19717 | 0.0012737
1 | 3782756 | 2015-02-06 03:32 | 2015-02-06 06:28 | 176.0167 | 244 | 27526.55 | 0.084188 | 0.00074625 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9806 | Tauranga CB11 Recloser 9806 tripped O/C L/O. Lines past Recloser 9806 sectionalised and patrolled but no fault found. High Winds in the area. Steve Doran attended. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 112.8137 | 109.8137 | 26794.55 | 0.081842 | 0.00074528 | 2015-02-06 | C | 0.081842 | 0.00074528 | 2015 | 2015-02-06 | C | 244 | 0.081842 | 0.00074528
1 | 3783303 | 2015-02-06 04:57 | 2015-02-06 13:48 | 531 | 82 | 39122.3 | 0.11965 | 0.00025079 | Restore Supply on Device 7121 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 739159 | CB7121 Tripped - no flags. Line sectionalised and patrolled. During sectionalising and patrol found an oppossom on pole 739159 and removed using sticks . | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 477.1012 | 474.1012 | 38876.3 | 0.11874 | 0.00025046 | 2015-02-06 | C | 0.11874 | 0.00025046 | 2015 | 2015-02-06 | C | 82 | 0.11874 | 0.00025046
1 | 3783503 | 2015-02-06 05:29 | 2015-02-06 07:18 | 108.55 | 1 | 108.55 | 0.00033199 | 3.0584e-06 | Restore Supply on Device T2286 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7298 | replace 2 x 10 amp ddo fuses and carriers. cause: wind. fuses 7298. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 108.55 | 105.55 | 105.55 | 0.00032239 | 3.0544e-06 | 2015-02-06 | C | 0.00032239 | 3.054e-06 | 2015 | 2015-02-06 | C | 1 | 0.00032239 | 3.0544e-06
1 | 3783506 | 2015-02-06 05:30 | 2015-02-06 11:09 | 339.6833 | 3 | 919.0833 | 0.0028109 | 9.1753e-06 | Restore Supply on Device 4738W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuses @ 2719 and fuses @ 1322 | *** check if 27 Tuke Road - oms 3783517 and 163 Lower Okotuku Road - oms 3783511 are part of this outage *** Replaced 2X 15a fuses @ 2719 & 2 X 8a fuses @ 1322 | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 306.3611 | 303.3611 | 910.0833 | 0.0027798 | 9.1633e-06 | 2015-02-06 | C | 0.0027798 | 9.163e-06 | 2015 | 2015-02-06 | C | 3 | 0.0027798 | 9.1633e-06
1 | 3783621 | 2015-02-06 06:53 | 2015-02-06 12:30 | 336.5333 | 83 | 20415.4667 | 0.062439 | 0.00025385 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794459 | Found broken crossarm at pole 794459 Isolated from fuses O58 for repairs. Ben Wilson attended. | F4 | TUTAENUI | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 245.9695 | 242.9695 | 20166.4667 | 0.061597 | 0.00025352 | 2015-02-06 | C | 0.061597 | 0.00025352 | 2015 | 2015-02-06 | C | 83 | 0.061597 | 0.00025352
1 | 3784203 | 2015-02-06 07:23 | 2015-02-06 11:13 | 230.25 | 3 | 626.6667 | 0.0019166 | 9.1753e-06 | Restore Supply on Device 3410T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 765149 | 46 Puke Road, oms 3784484 - 310 Puke Rd are part of this outage *** 2x 6amp DD643 hv fuses - cause branch on line. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 208.8889 | 205.8889 | 617.6667 | 0.0018866 | 9.1633e-06 | 2015-02-06 | C | 0.0018866 | 9.163e-06 | 2015 | 2015-02-06 | C | 3 | 0.0018866 | 9.1633e-06
1 | 3784497 | 2015-02-06 07:52 | 2015-02-06 10:31 | 159 | 45 | 7155 | 0.021883 | 0.00013763 | Restore Supply on Device S566 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812432 | cut off burnt bit of pole and replaced crossarm related to 3783514 | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 159 | 156 | 7020 | 0.021442 | 0.00013745 | 2015-02-06 | C | 0.021442 | 0.00013745 | 2015 | 2015-02-06 | C | 45 | 0.021442 | 0.00013745
1 | 3784608 | 2015-02-06 09:00 | 2015-02-06 12:50 | 230.6167 | 177 | 30818.2833 | 0.094255 | 0.00054134 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844721 | Recloser 4659 ARC & Trip and sectionaliser 2924 open. Report received of lines down @ 1758 Parewanui Road. Lines brought down by digger. NDR No 23092. Line repaired at pole 844721. Steve Edwards attended. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 174.1146 | 171.1146 | 30287.2833 | 0.09251 | 0.00054063 | 2015-02-06 | C | 0.09251 | 0.00054063 | 2015 | 2015-02-06 | C | 177 | 0.09251 | 0.00054063
1 | 3785142 | 2015-02-06 10:41 | 2015-02-06 10:58 | 16.7 | 27 | 450.9 | 0.001379 | 8.2577e-05 | Restore Supply on Device SB1-047 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 268253 | Line isolated at Fuses SB1-047 to remove branch from line on pole 268253 - removed with hot stick - all supply restored. Denis Ngatai attended. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 16.7 | 13.7 | 369.9 | 0.0011298 | 8.2469e-05 | 2015-02-06 | C | 0.0011298 | 8.2469e-05 | 2015 | 2015-02-06 | C | 27 | 0.0011298 | 8.2469e-05
1 | 3785187 | 2015-02-06 10:50 | 2015-02-06 23:01 | 730.2833 | 3 | 1823.2 | 0.0055761 | 9.1753e-06 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | S5130 | Essie from Nova called to advise tree has taken down lines and damaged power pole 11.02am advised SVS hub of job & control. Pole Replaced 15kVA Transformer Replaced. Lines repaired. Sam Jones attended. | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 607.7333 | 604.7333 | 1814.2 | 0.0055413 | 9.1633e-06 | 2015-02-06 | B | 0.0027707 | 4.582e-06 | 2015 | 2015-02-06 | B | 3 | 0.0055413 | 9.1633e-06
1 | 3785200 | 2015-02-06 10:57 | 2015-02-06 15:25 | 267.7833 | 515 | 66284.9333 | 0.20273 | 0.0015751 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 217002 | Recloser 9220/2 tripped to L/O - line sectionalised & patrolled - LV line found at transformer TE4-001 to have contacted HV line - transformer isolated to have inspector check installation for Hi/Lo contact - sectionaliser 9208/2 tripped to L/O on restora | F2/F4 | MALEME ST | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 128.7086 | 125.7086 | 64739.9333 | 0.19774 | 0.001573 | 2015-02-06 | C | 0.19774 | 0.001573 | 2015 | 2015-02-06 | C | 515 | 0.19774 | 0.001573
1 | 3786038 | 2015-02-06 11:10 | 2015-02-06 15:07 | 236.9167 | 405 | 55609.4333 | 0.17008 | 0.0012387 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 21309 | dallas fire comms work road Aongatete Just of SH2 lines down - causing fire F1782095 eta required 09 486 7949 - 11.19am called Lucy svs hub and advised of job. & advised Control 12.53pm - FM (Ciaan) will go to site in bucket truck, has requested a 2R b | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 137.3072 | 134.3072 | 54394.4333 | 0.16614 | 0.001237 | 2015-02-06 | C | 0.16614 | 0.001237 | 2015 | 2015-02-06 | C | 405 | 0.16614 | 0.001237
1 | 3786987 | 2015-02-06 12:26 | 2015-02-06 20:06 | 460.15 | 1021 | 113500.8333 | 0.34713 | 0.0031226 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T13335 | Lauren Fire 2km north of Te Mata vegetation fire - possibly caused by power lines down.... F1782234 eta required 09 486 7949 - advised control. High winds caused line to come down. 100mtrs line replaced and 3 x tension sleeves used to repair. Andrew Kin | F4 | MANAIA COROMANDEL | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 111.1663 | 108.1663 | 110437.8333 | 0.33732 | 0.0031186 | 2015-02-06 | C | 0.33732 | 0.0031186 | 2015 | 2015-02-06 | C | 1021 | 0.33732 | 0.0031186
1 | 3788028 | 2015-02-06 12:48 | 2015-02-06 14:00 | 72.1667 | 52 | 3752.6667 | 0.011477 | 0.00015904 | Restore Supply on Device IC1385 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC863 | Line isolated beyond ABS IC1385 to replace broken 11kV fuse base at transformer TC863 11kV fuse base and holder only materials required | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 72.1667 | 69.1667 | 3596.6667 | 0.010986 | 0.00015883 | 2015-02-06 | C | 0.010986 | 0.00015883 | 2015 | 2015-02-06 | C | 52 | 0.010986 | 0.00015883
1 | 3788865 | 2015-02-06 13:42 | 2015-02-06 17:01 | 199 | 32 | 6368 | 0.019476 | 9.787e-05 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 374025 | Should be related to OMS 3786495 . Could not find when Opened sectionaliser | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 199 | 196 | 6272 | 0.019157 | 9.7742e-05 | 2015-02-06 | C | 0.019157 | 9.7742e-05 | 2015 | 2015-02-06 | C | 32 | 0.019157 | 9.7742e-05
1 | 3789367 | 2015-02-06 14:43 | 2015-02-06 17:53 | 189.3167 | 3 | 429.2 | 0.0013127 | 9.1753e-06 | Restore Supply on Device TC1937 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC1937 | Fuses FP637 opened to straighten crossarm. Reset 4 DDO fuses worked through control. No other assets repaired or replaced. Adjacent assets ok. Marty Keenan attended. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 143.0667 | 140.0667 | 420.2 | 0.0012835 | 9.1633e-06 | 2015-02-06 | C | 0.0012835 | 9.163e-06 | 2015 | 2015-02-06 | C | 3 | 0.0012835 | 9.1633e-06
1 | 3789719 | 2015-02-06 15:40 | 2015-02-06 16:20 | 40 | 5 | 200 | 0.00061168 | 1.5292e-05 | Restore Supply on Device TC5643 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 04072, TC5643 | 2x 3amp DDO fuses & cut some trees down to ground. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. Grant Jordan attended. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 185 | 0.00056507 | 1.5272e-05 | 2015-02-06 | C | 0.00056507 | 1.5272e-05 | 2015 | 2015-02-06 | C | 5 | 0.00056507 | 1.5272e-05
1 | 3790498 | 2015-02-06 21:19 | 2015-02-06 23:16 | 117.1167 | 48 | 4958.2167 | 0.015164 | 0.0001468 | Restore Supply on Device T3340 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7363 | possibly related to oms 3790482. Faultman found 2 HV fuses blown at Fuses 7363, line was patrolled and faultman found blown fuse on transformer T876, transformer was isolated and faultman will return in the morning to test it as it is raining heavily. 2 | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 103.2962 | 100.2962 | 4814.2167 | 0.014705 | 0.00014661 | 2015-02-06 | C | 0.014705 | 0.00014661 | 2015 | 2015-02-06 | C | 48 | 0.014705 | 0.00014661
1 | 3790565 | 2015-02-06 23:25 | 2015-02-07 12:34 | 789 | 1 | 789 | 0.0024131 | 3.0584e-06 | Restore Supply on Device T876 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T876 | Faultman isolated transformer T876 found 2 fuses blown will return in the morning to test transformer as it is raining very heavily and is to dangerous to get up and carry out tests. This was part of OMS 3790498.Transformer T876 only feeds an old cow shed | F4 | PONATAHI | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 789 | 786 | 786 | 0.0024008 | 3.0544e-06 | 2015-02-06 | C | 0.0024008 | 3.054e-06 | 2015 | 2015-02-06 | C | 1 | 0.0024008 | 3.0544e-06
1 | 3790594 | 2015-02-07 01:49 | 2015-02-07 05:45 | 236 | 46 | 10743.4 | 0.032858 | 0.00014069 | Restore Supply on Device P2290 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 6422 | Faultman found blown fuse at Fuses 6422, line was patrolled and no found was found suspect possible cause was a Opossum. 1 x 10 Amp HV fuse replaced. Blair Gregg attended. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 233.5522 | 230.5522 | 10605.4 | 0.032393 | 0.0001405 | 2015-02-07 | C | 0.032393 | 0.0001405 | 2015 | 2015-02-07 | C | 46 | 0.032393 | 0.0001405
1 | 3790728 | 2015-02-07 07:47 | 2015-02-07 10:51 | 184.45 | 1 | 184.45 | 0.00056413 | 3.0584e-06 | Restore Supply on Device Z195 | 22000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | z195 | 9.42am retailer calling for update.. called svs hub and they advised they are trying to dispatch faultman. 2x 6amp hv fuses at tx z195 cause seagull flying through lines No other assets repaired or replaced and all adjacent assets checked and are up to | F4 | LEEDSTOWN 22KV | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 184.45 | 181.45 | 181.45 | 0.00055423 | 3.0544e-06 | 2015-02-07 | C | 0.00055422 | 3.054e-06 | 2015 | 2015-02-07 | C | 1 | 0.00055423 | 3.0544e-06
1 | 3792063 | 2015-02-07 21:18 | 2015-02-08 02:06 | 287.7 | 327 | 52819.2333 | 0.16154 | 0.0010001 | Restore Supply on Device RP09 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TD5-221 | Recloser RP09 tripped to L/O - E/F flag - line sectionalised & patrolled - fault eventually identified to be a faulty transformer TD5-221 - transformer isolated & all other supply restored - 2 r requested to have transformer changed in morning | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 161.5267 | 158.5267 | 51838.2333 | 0.15834 | 0.0009988 | 2015-02-07 | C | 0.15834 | 0.0009988 | 2015 | 2015-02-07 | C | 327 | 0.15834 | 0.0009988
1 | 3792851 | 2015-02-08 00:31 | 2015-02-08 01:31 | 60 | 2 | 120 | 0.00036701 | 6.1168e-06 | Restore Supply on Device 11001 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 1101 | Faultman found 2 blown HV fuses at Fuses 1101, suspect bird strike as lines run by water treatment pond area. 2 X 10 Amp HV fuses replaced. Jason Hall attended. | F4 | SOUTH FEATHERSTON | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 114 | 0.0003482 | 6.1088e-06 | 2015-02-08 | C | 0.0003482 | 6.109e-06 | 2015 | 2015-02-08 | C | 2 | 0.0003482 | 6.1088e-06
1 | 3792872 | 2015-02-08 06:46 | 2015-02-08 08:09 | 82.8833 | 1 | 588.05 | 0.0017985 | 3.0584e-06 | Restore Supply on Device X1839 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 495 |  | F4 | PUTORINO | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 588.05 | 585.05 | 585.05 | 0.001787 | 3.0544e-06 | 2015-02-08 | C | 0.001787 | 3.054e-06 | 2015 | 2015-02-08 | C | 1 | 0.001787 | 3.0544e-06
1 | 3792882 | 2015-02-08 07:28 | 2015-02-08 09:15 | 107.15 | 1 | 107.15 | 0.00032771 | 3.0584e-06 | Restore Supply on Device T2/624 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FUSE D88, P3857 T2/20 | ADDRESS IS 1220 RANGITEKE LINE. 2 X 10 AMP DDOS RELOADED , LINE CLASH DUE TO BIRD STRIKE. No other assets repaired or replaced. Adjacent assets ok | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107.15 | 104.15 | 104.15 | 0.00031812 | 3.0544e-06 | 2015-02-08 | C | 0.00031812 | 3.054e-06 | 2015 | 2015-02-08 | C | 1 | 0.00031812 | 3.0544e-06
1 | 3792934 | 2015-02-08 08:38 | 2015-02-08 09:00 | 22 | 2987 | 53475 | 0.16355 | 0.0091355 | Restore Supply on Device 3043 | 33000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 365237 | Transpower called CB 2092 Tripped on E/F Yellow Blue Phase. Line patrolled. Found Bird at Pole 365237 on the Ground. Ben Wilson attended. | F1, F2, F3 | WANGANUI EAST 33KV | TP_WANGANUI | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 17.9026 | 14.9026 | 44514 | 0.13596 | 0.0091236 | 2015-02-08 | C | 0.13596 | 0.0091236 | 2015 | 2015-02-08 | C | 2987 | 0.13596 | 0.0091236
1 | 3536175 | 2015-02-09 09:15 | 2015-02-09 10:46 | 90.4167 | 2 | 180.8333 | 0.00055306 | 6.1168e-06 | NAPA ID:06051 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2262 | To replace 11kV and LV cross arms on existing line. Works location: Tower Rd Matamata WO 10148256 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90.4167 | 87.4167 | 174.8333 | 0.00053402 | 6.1088e-06 | 2015-02-09 | B | 0.00026701 | 3.054e-06 | 2015 | 2015-02-09 | B | 2 | 0.00053402 | 6.1088e-06
1 | 3704998 | 2015-02-09 09:15 | 2015-02-09 13:21 | 245.25 | 2 | 490.5 | 0.0015002 | 6.1168e-06 | NAPA ID:06390 TP_PIAKO GXP > PIAKO SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I1847 | LLP -Change 11kV arm on pole I1846 & cut droppers to transformer fuses FP1660 on pole I1847. AP - Change tap-off arm and DDO FP1660 on pole I1487. LLP replace droppers to fuses FP1660. NOTE There are two 11kV feeders on the poles (PKO CB5 and PKO CB8) | F4 | KIWITAHI | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 245.25 | 242.25 | 484.5 | 0.0014799 | 6.1088e-06 | 2015-02-09 | B | 0.00073993 | 3.054e-06 | 2015 | 2015-02-09 | B | 2 | 0.0014799 | 6.1088e-06
1 | 3500747 | 2015-02-09 09:31 | 2015-02-09 13:36 | 245.5333 | 9 | 2209.8 | 0.0067585 | 2.7526e-05 | NAPA ID:05647 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6003 | Replace ABS 6003 DNO 141030 & cross arms. Works location: Melville Rd, Kaponga. WO 10166830 | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 245.5333 | 242.5333 | 2182.8 | 0.0066672 | 2.749e-05 | 2015-02-09 | B | 0.0033336 | 1.3745e-05 | 2015 | 2015-02-09 | B | 9 | 0.0066672 | 2.749e-05
1 | 3799140 | 2015-02-09 11:36 | 2015-02-09 13:57 | 141.4333 | 1 | 141.4333 | 0.00043256 | 3.0584e-06 | Restore Supply on Device T7/36 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P29 | 12.50pm - FM advise: lv checked, this is a hv fault. it is a small spur line so FM is onsite and he can do the line patrol alone. FM did request a 2R, this being a hv fault. advise FM that once he has found the fault to give Dispatch a call and advise of | F4 | MANGATAINOKA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 141.4333 | 138.4333 | 138.4333 | 0.00042283 | 3.0544e-06 | 2015-02-09 | C | 0.00042283 | 3.054e-06 | 2015 | 2015-02-09 | C | 1 | 0.00042283 | 3.0544e-06
1 | 3799171 | 2015-02-09 12:04 | 2015-02-09 13:53 | 108.7333 | 1 | 108.7333 | 0.00033255 | 3.0584e-06 | Restore Supply on Device X2182 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tx 2182W and pole 809425 | replace 3 amp ht fuse. tx 2182W and pole 809425. cause: unknown. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 108.7333 | 105.7333 | 105.7333 | 0.00032295 | 3.0544e-06 | 2015-02-09 | C | 0.00032295 | 3.054e-06 | 2015 | 2015-02-09 | C | 1 | 0.00032295 | 3.0544e-06
1 | 3799641 | 2015-02-09 14:13 | 2015-02-09 14:31 | 18.3333 | 47 | 861.6667 | 0.0026353 | 0.00014375 | Restore Supply on Device 80 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742477 | Emergency switching to repair damaged conductor at pole 742477 ( BBK2 ). Isolations between ABS's 45, 82 & 80 with back feeds via ABS's 190 & 350. Conductor repaired, all service restored. Nick Patton & Jade Williams attended. Materials 2 x H/V sleeves, | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 18.3333 | 15.3333 | 720.6667 | 0.0022012 | 0.00014356 | 2015-02-09 | C | 0.0022012 | 0.00014356 | 2015 | 2015-02-09 | C | 47 | 0.0022012 | 0.00014356
1 | 3800109 | 2015-02-09 16:28 | 2015-02-09 16:43 | 15 | 212 | 3180 | 0.0097258 | 0.00064839 | Restore Supply on Device C881 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | C881 | CB C881 tripped - no flags. Line patrolled - no fault located. Sam Stuart attended. | F2 | HOLDSWORTH | NORFOLK SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 2544 | 0.0077705 | 0.00064754 | 2015-02-09 | C | 0.0077705 | 0.00064754 | 2015 | 2015-02-09 | C | 212 | 0.0077705 | 0.00064754
1 | 3800794 | 2015-02-09 20:01 | 2015-02-09 23:56 | 234.8167 | 824 | 100304.7833 | 0.30677 | 0.0025201 | Restore Supply on Device TA2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713895 | Explosion on power pole cnr Ihaia Road & Whitcome Road Opunake 027 244 1586 Wires hanging down on corner, due to magpies hitting lines On investigation no lines down but jumpers clashed on pole 713895 | F3 | OPUNAKE | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 121.7291 | 118.7291 | 97832.7833 | 0.29882 | 0.0025168 | 2015-02-09 | C | 0.29882 | 0.0025168 | 2015 | 2015-02-09 | C | 824 | 0.29882 | 0.0025168
1 | 3801870 | 2015-02-09 22:43 | 2015-02-10 03:07 | 264.1167 | 32 | 4819.6667 | 0.014741 | 9.787e-05 | Restore Supply on Device 396 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756237 | Line comes from the road across the garden and sparking over garden area (house just before the bridge). 10.56pm advise SVS hub of job. Found polymer insulator broken and 11kV contacted the 400v line. Isolated between ABS 484 and Recloser 6748 for repairs | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 150.6146 | 147.6146 | 4723.6667 | 0.014428 | 9.7742e-05 | 2015-02-09 | C | 0.014428 | 9.7742e-05 | 2015 | 2015-02-09 | C | 32 | 0.014428 | 9.7742e-05
1 | 3801981 | 2015-02-09 23:14 | 2015-02-10 01:01 | 106.2833 | 416 | 10371.6667 | 0.031721 | 0.0012723 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 837837 | CB C224 A/R and tripped on O/C. During patrol & sectionalising found a branch on the lines @ pole 837837 and removed using operating sticks. | F5 | CASTLEPOINT | TINUI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 24.9319 | 21.9319 | 9123.6667 | 0.027868 | 0.0012706 | 2015-02-09 | C | 0.027868 | 0.0012706 | 2015 | 2015-02-09 | C | 416 | 0.027868 | 0.0012706
1 | 3802625 | 2015-02-10 01:06 | 2015-02-10 12:25 | 679.25 | 86 | 24841.9167 | 0.075977 | 0.00026302 | Restore Supply on Device 5329 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 763934 | Brent didn't attend Craig Wellington did.( WAE U30 ) Recloser 5329 tripped, L/O. Feeder sectionalised & trees in line found at pole 763934. Spur line isolated at fuses 5193 with rest of feeder returned to service. Trees removed lines repaired all service | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 288.8595 | 285.8595 | 24583.9167 | 0.07509 | 0.00026268 | 2015-02-10 | C | 0.07509 | 0.00026268 | 2015 | 2015-02-10 | C | 86 | 0.07509 | 0.00026268
1 | 3803029 | 2015-02-10 02:35 | 2015-02-10 02:43 | 8.55 | 2 | 17.1 | 5.2299e-05 | 6.1168e-06 | Restore Supply on Device 6942 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6942 | no paperwork | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 8.55 | 5.55 | 11.1 | 3.3904e-05 | 6.1088e-06 | 2015-02-10 | C | 3.3904e-05 | 6.109e-06 | 2015 | 2015-02-10 | C | 2 | 3.3904e-05 | 6.1088e-06
1 | 3803227 | 2015-02-10 03:55 | 2015-02-11 12:01 | 1926.1667 | 855 | 202770.7 | 0.62016 | 0.002615 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 783267 | (NOTE: Please make this job second response). Tripping on Roberts CB4 on E/F. Feeder sectionalised / patrolled with 2 broken conductors found. Isolation required between ABS 818 and 985 with backfeed at VS4616. Repairs made with 40m conductor replaced an | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 237.1587 | 234.1587 | 200205.7 | 0.61151 | 0.0026115 | 2015-02-10 | C | 0.61151 | 0.0026115 | 2015 | 2015-02-10 | C | 855 | 0.61151 | 0.0026115
1 | 3805833 | 2015-02-10 07:23 | 2015-02-10 11:26 | 243.4667 | 40 | 9738.6667 | 0.029785 | 0.00012234 | Restore Supply on Device T5/181 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P07408 | Reports of "no power" found recloser CB K54 had tripped. Feeder sectionalised / patrolled with a tree branch (wind blown) found on line at Pole P07408. Removed with fuse stick. Relivened OK. | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 243.4667 | 240.4667 | 9618.6667 | 0.029379 | 0.00012218 | 2015-02-10 | C | 0.029379 | 0.00012218 | 2015 | 2015-02-10 | C | 40 | 0.029379 | 0.00012218
1 | 3626678 | 2015-02-10 08:35 | 2015-02-10 15:01 | 385.3167 | 32 | 12330.1333 | 0.037711 | 9.787e-05 | NAPA ID:04443 TP_GREYTOWN GXP > HAU NUI SUB > TUTURUMURI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 811557 | replace 11kv conductor between poles 811557 & 811569. Works location: White Rock Rd WO IR722 | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 385.3167 | 382.3167 | 12234.1333 | 0.037368 | 9.7742e-05 | 2015-02-10 | B | 0.018684 | 4.8871e-05 | 2015 | 2015-02-10 | B | 32 | 0.037368 | 9.7742e-05
1 | 3628218 | 2015-02-10 09:01 | 2015-02-10 15:30 | 389.0333 | 43 | 16728.4333 | 0.051163 | 0.00013151 | NAPA ID:05260 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1118 | To install new poles and TEMP switches TEMP88, 89, 90 and 91. In preparation for conductor upgrade Waotu Road. Works location: Waotu Rd. WO 10134042. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 389.0333 | 386.0333 | 16599.4333 | 0.050702 | 0.00013134 | 2015-02-10 | B | 0.025351 | 6.567e-05 | 2015 | 2015-02-10 | B | 43 | 0.050702 | 0.00013134
1 | 3626085 | 2015-02-10 09:11 | 2015-02-10 14:57 | 345.7 | 133 | 45978.1 | 0.14062 | 0.00040677 | NAPA ID:05716 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 831550 | at pole 831547 make live line break At pole 831550 replace structure S111 and new abs also make live line break and reconnect at pole 831547. Works location: Colville St Masterton. WO 10170883 | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 345.7 | 342.7 | 45579.1 | 0.13922 | 0.00040624 | 2015-02-10 | B | 0.069609 | 0.00020312 | 2015 | 2015-02-10 | B | 133 | 0.13922 | 0.00040624
1 | 3798920 | 2015-02-10 09:15 | 2015-02-10 15:57 | 402 | 14 | 5628 | 0.017213 | 4.2818e-05 | NAPA ID:06871 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS IP587 | Isolate 11kV OH and replace pole P13003 (TC907). Connect through new 11kV OH conductor to Newly installed ABS switch IC587. This site will be left in an Open state until phasing out has been done at pole P12683 to enable the paralleling of the 2 feeders. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 402 | 399 | 5586 | 0.017062 | 4.2762e-05 | 2015-02-10 | B | 0.008531 | 2.1381e-05 | 2015 | 2015-02-10 | B | 14 | 0.017062 | 4.2762e-05
1 | 3500812 | 2015-02-10 09:18 | 2015-02-10 14:05 | 287.55 | 41 | 11789.55 | 0.036057 | 0.0001254 | NAPA ID:05590 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > TE AROHA BOROUGH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TC4012 | Replace Transfomer like for like along with new LV frame and sw/gear. Install new Street light U/G Box. Works location: Puriri Rd Te Aroha. WO 10148293 | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 287.55 | 284.55 | 11666.55 | 0.035635 | 0.00012523 | 2015-02-10 | B | 0.017817 | 6.2616e-05 | 2015 | 2015-02-10 | B | 41 | 0.035635 | 0.00012523
1 | 3686593 | 2015-02-10 09:19 | 2015-02-10 14:07 | 287.35 | 11 | 3160.85 | 0.0096672 | 3.3643e-05 | NAPA ID:05907 TP_TE MATAI GXP > ATUAROA AVE SUB > TE PUKE QUARRY RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE5-057 | REPLACE HV ARMS ALONG ALLEY ROAD. Works location: Alley Rd. WO 10148383 | F2 | BROWNE ST | WAITARA WEST SUB | TP_HUIRANGI | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 287.35 | 284.35 | 3127.85 | 0.0095538 | 3.3599e-05 | 2015-02-10 | B | 0.0047769 | 1.6799e-05 | 2015 | 2015-02-10 | B | 11 | 0.0095538 | 3.3599e-05
1 | 3500820 | 2015-02-10 09:21 | 2015-02-10 14:41 | 319.9167 | 7 | 2239.4167 | 0.0068491 | 2.1409e-05 | NAPA ID:05422 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS CA421 | Replaceing 7, 11kv poles. Works location: Ohangai Rd Normanby WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 319.9167 | 316.9167 | 2218.4167 | 0.006776 | 2.1381e-05 | 2015-02-10 | B | 0.003388 | 1.069e-05 | 2015 | 2015-02-10 | B | 7 | 0.006776 | 2.1381e-05
1 | 3806180 | 2015-02-10 09:26 | 2015-02-10 10:35 | 68.9667 | 1 | 68.9667 | 0.00021093 | 3.0584e-06 | Restore Supply on Device 2800T | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 741665 | replace 3 amp ht fuse at pole 741665. cause: wind. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 68.9667 | 65.9667 | 65.9667 | 0.00020149 | 3.0544e-06 | 2015-02-10 | C | 0.00020149 | 3.054e-06 | 2015 | 2015-02-10 | C | 1 | 0.00020149 | 3.0544e-06
1 | 3806401 | 2015-02-10 12:50 | 2015-02-10 14:13 | 83.1167 | 2 | 84.7333 | 0.00025915 | 6.1168e-06 | Restore Supply on Device TC2874 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | TP2052 | 12.54pm - advised smc. Transformer TC2874 Not affected from this job. Wayne Seath Attended. Completed Tapchange from Tap 4 to Tap 2 on Transformer TP2052. Voltage After Tapchange: Single Phase: 235V. 3 Phase: 406V. | F3 | HETHERINGTON RD | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 42.3667 | 39.3667 | 78.7333 | 0.00024048 | 6.1088e-06 | 2015-02-10 | C | 0.00024048 | 6.109e-06 | 2015 | 2015-02-10 | C | 2 | 0.00024048 | 6.1088e-06
1 | 3806581 | 2015-02-10 16:09 | 2015-02-10 17:28 | 78.7833 | 1 | 78.7833 | 0.00024095 | 3.0584e-06 | Restore Supply on Device TD3-189 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | minden road | is 3806592 linked? fm advised cannot find an issue and the two phone number he phone don't direct to answer phone re paul cooper 5.19 paul advised he has found the problem these are water tanks and when this gets very windy this is causing the feeder | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 78.7833 | 75.7833 | 75.7833 | 0.00023147 | 3.0544e-06 | 2015-02-10 | C | 0.00023147 | 3.054e-06 | 2015 | 2015-02-10 | C | 1 | 0.00023147 | 3.0544e-06
1 | 3806592 | 2015-02-10 16:15 | 2015-02-10 17:29 | 73.3667 | 1 | 73.3667 | 0.00022439 | 3.0584e-06 | Restore Supply on Device TD3-122 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 125 b minden and 295 water tanks | is 3806851 linked? 5.12 paul is checking this address now spoke to richard 0274769374 on who manages libraries and outer offices he does not no anything about this said to try adrian 5.19 paul advised he has found the problem these are water tanks and | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 73.3667 | 70.3667 | 70.3667 | 0.00021493 | 3.0544e-06 | 2015-02-10 | C | 0.00021493 | 3.054e-06 | 2015 | 2015-02-10 | C | 1 | 0.00021493 | 3.0544e-06
1 | 3806668 | 2015-02-10 17:38 | 2015-02-10 18:35 | 57.8167 | 4638 | 268153.7 | 0.82013 | 0.014185 | Restore Supply on Device 1342 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 1342 | Huirangi CB 1342 and Motukawa 225 tripped causing LOS to Waitara East and Motukawa Substations. Cause was thought to be birds hitting the lines. Outage step shown in 3811307. | F1, F2, F3 | HUIRANGI FAULL ROAD 33KV | TP_HUIRANGI | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 57.8167 | 54.8167 | 254239.7 | 0.77656 | 0.014166 | 2015-02-10 | C | 0.77656 | 0.014166 | 2015 | 2015-02-10 | C | 4638 | 0.77656 | 0.014166
1 | 3813624 | 2015-02-10 17:41 | 2015-02-10 20:43 | 181.9167 | 2 | 282.2333 | 0.00086319 | 6.1168e-06 | Restore Supply on Device W5060 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722691 | Chris requesting bucket truck to attend needing to replace ht cross arm & assmbly | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 141.1167 | 138.1167 | 276.2333 | 0.00084373 | 6.1088e-06 | 2015-02-10 | C | 0.00084373 | 6.109e-06 | 2015 | 2015-02-10 | C | 2 | 0.00084373 | 6.1088e-06
1 | 3814957 | 2015-02-10 22:34 | 2015-02-11 00:25 | 111.2167 | 196 | 10584 | 0.03237 | 0.00059945 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P18040 | Broken jumper at Pole P18040. No Back feeder put in as it would have taken longer to do this than do job. Used 2X HD12A Connectors .5 M PVC Copper Wire | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 9996 | 0.030532 | 0.00059867 | 2015-02-10 | B | 0.015266 | 0.00029933 | 2015 | 2015-02-10 | B | 196 | 0.030532 | 0.00059867
1 | 3667707 | 2015-02-11 08:16 | 2015-02-11 15:06 | 410.05 | 14 | 2724.7 | 0.0083333 | 4.2818e-05 | NAPA ID:06042 TP_KOPU GXP > TAIRUA SUB > PAUANUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3595 | Connect generator at TC3595 then replace switch gear IC1999 then disconnect generator at TC3595. Works location: Pauanui Blvd. WO 10163296. | F3 | PAUANUI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 194.6214 | 191.6214 | 2682.7 | 0.0081941 | 4.2762e-05 | 2015-02-11 | B | 0.0040971 | 2.1381e-05 | 2015 | 2015-02-11 | B | 14 | 0.0081941 | 4.2762e-05
1 | 3815861 | 2015-02-11 08:23 | 2015-02-11 09:30 | 67.3833 | 1 | 67.3833 | 0.00020609 | 3.0584e-06 | Restore Supply on Device TC5838 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P1393 | Replace 2 x 6 amp HT fuses. Cause: possible bird strike. 2 out 3 phases. Pole P1393. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. Wayne Seaton attended. | F4 | WAITAWHETA | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 67.3833 | 64.3833 | 64.3833 | 0.00019665 | 3.0544e-06 | 2015-02-11 | C | 0.00019665 | 3.054e-06 | 2015 | 2015-02-11 | C | 1 | 0.00019665 | 3.0544e-06
1 | 3771145 | 2015-02-11 09:30 | 2015-02-11 15:49 | 378.7833 | 102 | 11917.75 | 0.03645 | 0.00031196 | NAPA ID:06321 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 404 | isolation to install 11kv temporary line breaks poles 701699 and pole 701696 remove ABS 404 and install new Entec EcoswitchDas switch onto pole 701698 number 12001/2 for recloser and 12001/4. Isolation to re install 11kv line poles 701699 and pole 701696 | F3 | BROOKLANDS 7 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 116.8407 | 113.8407 | 11611.75 | 0.035467 | 0.00031155 | 2015-02-11 | B | 0.017734 | 0.00015578 | 2015 | 2015-02-11 | B | 102 | 0.035467 | 0.00031155
1 | 3500796 | 2015-02-11 09:30 | 2015-02-11 13:49 | 258.35 | 50 | 12917.5 | 0.039507 | 0.00015292 | NAPA ID:05652 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6000 | Replace ABS 6000 DNO141028. Works location: Mangawhero Rd Kaponga. WO 10166877. NAPA 5936 completed in parallel with this job off & on times identical. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 258.35 | 255.35 | 12767.5 | 0.038997 | 0.00015272 | 2015-02-11 | B | 0.019499 | 7.6361e-05 | 2015 | 2015-02-11 | B | 50 | 0.038997 | 0.00015272
1 | 3634288 | 2015-02-12 08:15 | 2015-02-12 10:09 | 114 | 5 | 570 | 0.0017433 | 1.5292e-05 | NAPA ID:05719 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7716 | Hardware replacement at poles 836363/836380/836379. Works location: Cootes Rd, Masterton. WO 10170778. | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 114 | 111 | 555 | 0.0016952 | 1.5272e-05 | 2015-02-12 | B | 0.0008476 | 7.636e-06 | 2015 | 2015-02-12 | B | 5 | 0.0016952 | 1.5272e-05
1 | 3704861 | 2015-02-12 08:20 | 2015-02-12 12:00 | 220 | 5 | 1100 | 0.0033643 | 1.5292e-05 | NAPA ID:06525 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > PAPAMOA JUNCTION | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9107 | Investigate faulty interlock on switch unit. Works location: Tara Rd. WO 30001407 | F4 | HOE-O-TAINUI | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 220 | 217 | 1085 | 0.003314 | 1.5272e-05 | 2015-02-12 | B | 0.001657 | 7.636e-06 | 2015 | 2015-02-12 | B | 5 | 0.003314 | 1.5272e-05
1 | 3634291 | 2015-02-12 08:30 | 2015-02-12 16:00 | 450 | 32 | 14400 | 0.044041 | 9.787e-05 | NAPA ID:04450 TP_GREYTOWN GXP > HAU NUI SUB > TUTURUMURI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 811578 | Replace 11kV conductor between poles 811578 & 811597. Work Location: White Rock Road, Greytown. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 450 | 447 | 14304 | 0.04369 | 9.7742e-05 | 2015-02-12 | B | 0.021845 | 4.8871e-05 | 2015 | 2015-02-12 | B | 32 | 0.04369 | 9.7742e-05
1 | 3634317 | 2015-02-12 09:00 | 2015-02-12 15:30 | 390 | 27 | 10530 | 0.032205 | 8.2577e-05 | NAPA ID:03694 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/361 | Change 50 x HV xarms. 1 x new transformer T1/361. Works location: Lake Rd, Oroua Downs. WO 10162444. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 390 | 387 | 10449 | 0.031916 | 8.2469e-05 | 2015-02-12 | B | 0.015958 | 4.1235e-05 | 2015 | 2015-02-12 | B | 27 | 0.031916 | 8.2469e-05
1 | 3628302 | 2015-02-12 09:01 | 2015-02-12 14:43 | 342.7 | 4 | 1370.8 | 0.0041925 | 1.2234e-05 | NAPA ID:05565 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | To replace 11kV poles and cross arms in preparation for conductor upgrade. Works location: Waotu Rd. WO 10134042. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 342.7 | 339.7 | 1358.8 | 0.0041504 | 1.2218e-05 | 2015-02-12 | B | 0.0020752 | 6.109e-06 | 2015 | 2015-02-12 | B | 4 | 0.0041504 | 1.2218e-05
1 | 3618927 | 2015-02-12 09:09 | 2015-02-12 14:24 | 314.9667 | 39 | 12283.7 | 0.037569 | 0.00011928 | NAPA ID:05961 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 724755 | Replace 10 11kv poles 724755, 724760, 724761, 724786, 724781, 724780, 724778, 724775, 724771, 724770. Works location: Whakatau Rd Normanby. WO 10141791. Job Started late due to work load on control room desk, faultman unable to get through to desk. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 314.9667 | 311.9667 | 12166.7 | 0.037162 | 0.00011912 | 2015-02-12 | B | 0.018581 | 5.9561e-05 | 2015 | 2015-02-12 | B | 39 | 0.037162 | 0.00011912
1 | 3693609 | 2015-02-12 09:17 | 2015-02-12 09:37 | 19.75 | 62 | 1224.5 | 0.003745 | 0.00018962 | NAPA ID:06044 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > KOROMIKO ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TK5-019 | AP1: Replace existing series 1 SDAF3 with a Safelink CFC. During outage will also replace LV fusing on transformer TK5-019. TP1: Test 11kV cable connected to new Safelink Switch. AP2: Complete final cable connections onto new Safelink unit. Works locati | F2 | KOROMIKO ST | WAIHI ROAD SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 19.75 | 16.75 | 1038.5 | 0.003172 | 0.00018937 | 2015-02-12 | B | 0.001586 | 9.4687e-05 | 2015 | 2015-02-12 | B | 62 | 0.003172 | 0.00018937
1 | 3693605 | 2015-02-12 09:34 | 2015-02-12 15:20 | 345.6 | 274 | 94694.4 | 0.28962 | 0.00083801 | NAPA ID:06071 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9632 | Reconductoring and replacing poles. Works location: Otama Bay Rd. WO 10148314. | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 345.6 | 342.6 | 93872.4 | 0.28673 | 0.00083691 | 2015-02-12 | B | 0.14336 | 0.00041846 | 2015 | 2015-02-12 | B | 274 | 0.28673 | 0.00083691
1 | 3704530 | 2015-02-12 10:02 | 2015-02-12 12:27 | 145.7 | 6 | 874.2 | 0.0026737 | 1.8351e-05 | NAPA ID:05473 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF7-024 | To Check the Fuse Size SF7-024. Replace Fuses SF7-037 & Install Fixed Links. To Check Fuse Size SF7-037. Works location: Rotoehu Rd, Pongakawa. WO 10146569. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 145.7 | 142.7 | 856.2 | 0.0026152 | 1.8327e-05 | 2015-02-12 | B | 0.0013076 | 9.163e-06 | 2015 | 2015-02-12 | B | 6 | 0.0026152 | 1.8327e-05
1 | 3705784 | 2015-02-12 14:04 | 2015-02-12 14:13 | 9 | 16 | 144 | 0.00044041 | 4.8935e-05 | NAPA ID:05753 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse SF7-037 | To Check the Fuse Size SF7-024. Replace Fuses SF7-037 & Install Fixed Links. To Check Fuse Size SF7-037. Works location: Rotoehu Rd Pongakawa. WO 10146569. Power Off at 1404 and back on at 1413 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 96 | 0.00029322 | 4.8871e-05 | 2015-02-12 | B | 0.00014661 | 2.4435e-05 | 2015 | 2015-02-12 | B | 16 | 0.00029322 | 4.8871e-05
1 | 3856351 | 2015-02-13 02:31 | 2015-02-13 04:55 | 144.4167 | 4 | 460.3167 | 0.0014078 | 1.2234e-05 | Restore Supply on Device 2186T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2186T | Inspection carried out on Transformer 2018T and was found to have failed. Transformer replaced, relivened OK. (Not aged equipment / defective). | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 115.0792 | 112.0792 | 448.3167 | 0.0013693 | 1.2218e-05 | 2015-02-13 | C | 0.0013693 | 1.2218e-05 | 2015 | 2015-02-13 | C | 4 | 0.0013693 | 1.2218e-05
1 | 3856394 | 2015-02-13 07:38 | 2015-02-13 09:15 | 96.8667 | 33 | 585.9333 | 0.001792 | 0.00010093 | Restore Supply on Device 4738W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2719 | Possibly part of oms 3856390. Replace 2 x 15 amp fuses and candles at fuse 2719. one of the fuses has got defect at the top and FM will defect this. Cause: unknown, possibly magpies. No other assets repaired or replaced on site. Adjacent assets are check | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 17.7556 | 14.7556 | 486.9333 | 0.0014873 | 0.0001008 | 2015-02-13 | C | 0.0014873 | 0.0001008 | 2015 | 2015-02-13 | C | 33 | 0.0014873 | 0.0001008
1 | 3712706 | 2015-02-13 08:15 | 2015-02-13 13:55 | 340.15 | 29 | 9864.35 | 0.030169 | 8.8694e-05 | NAPA ID:05454 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > BRUCE RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 219724 | Replace pole 219724 and run new 11kv conductor. Work Location: Kairua Road. Work Order: 10156589. | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 340.15 | 337.15 | 9777.35 | 0.029864 | 8.8578e-05 | 2015-02-13 | B | 0.014932 | 4.4289e-05 | 2015 | 2015-02-13 | B | 29 | 0.029864 | 8.8578e-05
1 | 3686641 | 2015-02-13 08:34 | 2015-02-13 16:42 | 488.05 | 10 | 4880.5 | 0.014927 | 3.0584e-05 | NAPA ID:06401 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Regulator 4690/2 | Remove 11kV Regulator 4515 from service. Install conductor between poles 57 and 59 (top & bottom circuits). Top circuit to be livened at pole 81, 11kV ABS 4708 to be left in OPEN state. Remove 11kV Fuses TEMP52. At pole 9 separate top and bottom circuits, | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 488.05 | 485.05 | 4850.5 | 0.014815 | 3.0544e-05 | 2015-02-13 | B | 0.0074077 | 1.5272e-05 | 2015 | 2015-02-13 | B | 10 | 0.014815 | 3.0544e-05
1 | 3623263 | 2015-02-13 08:45 | 2015-02-13 14:02 | 316.8667 | 39 | 12357.8 | 0.037795 | 0.00011928 | NAPA ID:05972 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 6403 | Replace 9, 11kv poles. Works location: Aratata Rd Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 316.8667 | 313.8667 | 12240.8 | 0.037389 | 0.00011912 | 2015-02-13 | B | 0.018694 | 5.9561e-05 | 2015 | 2015-02-13 | B | 39 | 0.037389 | 0.00011912
1 | 3704062 | 2015-02-13 09:00 | 2015-02-13 09:26 | 25.4167 | 11 | 279.5833 | 0.00085508 | 3.3643e-05 | NAPA ID:05476 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE7-039 | To check/Replace Fuse Links. Works location: Pongakawa Area WO 10146569 | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 25.4167 | 22.4167 | 246.5833 | 0.00075317 | 3.3599e-05 | 2015-02-13 | B | 0.00037658 | 1.6799e-05 | 2015 | 2015-02-13 | B | 11 | 0.00075317 | 3.3599e-05
1 | 3623954 | 2015-02-13 09:01 | 2015-02-13 09:59 | 58.4667 | 7 | 409.2667 | 0.0012517 | 2.1409e-05 | NAPA ID:05364 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1511 | To lower 2 poles, Replace 1 Pole & replace cross arms. Works location: Te Miro Rd Te Miro WO 10162183 Due G-map not being drawn correctly on and Off times are recorded incorrectly. Off time 09:00 On Time 13:21 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 58.4667 | 55.4667 | 388.2667 | 0.0011859 | 2.1381e-05 | 2015-02-13 | B | 0.00059296 | 1.069e-05 | 2015 | 2015-02-13 | B | 7 | 0.0011859 | 2.1381e-05
1 | 3821069 | 2015-02-13 09:32 | 2015-02-13 15:31 | 359.1333 | 220 | 78778.9333 | 0.24094 | 0.00067285 | NAPA ID:06967 TP_WAIKINO GXP > PAEROA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB7 | Replace crossarms on 33kV 312 Waikino/Paeroa Line. Works location: Waikino/Paeroa. WO 30000074 | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 358.0861 | 355.0861 | 78118.9333 | 0.23861 | 0.00067197 | 2015-02-13 | B | 0.1193 | 0.00033599 | 2015 | 2015-02-13 | B | 220 | 0.23861 | 0.00067197
1 | 3705312 | 2015-02-13 09:58 | 2015-02-13 10:07 | 8.7333 | 17 | 148.4667 | 0.00045407 | 5.1993e-05 | NAPA ID:05775 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE8-002 | To check/Replace Fuse Links. Works location: Pongakawa Area. WO 10146569 | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 8.7333 | 5.7333 | 97.4667 | 0.0002977 | 5.1925e-05 | 2015-02-13 | B | 0.00014885 | 2.5963e-05 | 2015 | 2015-02-13 | B | 17 | 0.0002977 | 5.1925e-05
1 | 3705323 | 2015-02-13 11:00 | 2015-02-13 11:15 | 15.35 | 6 | 92.1 | 0.00028168 | 1.8351e-05 | NAPA ID:05773 TP_TE MATAI GXP > PONGAKAWA SUB > OTAMARAKAU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF8-007 | To check/Replace Fuse Links. Works location: Pongakawa Area. WO 10146569. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 15.35 | 12.35 | 74.1 | 0.00022633 | 1.8327e-05 | 2015-02-13 | B | 0.00011317 | 9.163e-06 | 2015 | 2015-02-13 | B | 6 | 0.00022633 | 1.8327e-05
1 | 3705772 | 2015-02-13 13:02 | 2015-02-13 13:53 | 50.6333 | 11 | 556.9667 | 0.0017034 | 3.3643e-05 | NAPA ID:05772 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF8-002 | To check/Replace Fuse Links. Works location: Pongakawa Area. WO 10146569. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 50.6333 | 47.6333 | 523.9667 | 0.0016004 | 3.3599e-05 | 2015-02-13 | B | 0.00080021 | 1.6799e-05 | 2015 | 2015-02-13 | B | 11 | 0.0016004 | 3.3599e-05
1 | 3857434 | 2015-02-13 13:15 | 2015-02-13 13:54 | 38.55 | 1 | 38.55 | 0.0001179 | 3.0584e-06 | Restore Supply on Device TC5934 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | planned outage 6029 | part of shutdown fed from tc5934 customer was notified for last week and this is a continuation of last weeks shut down but customer was not notified for this week referred to richard to look into | F4 | TIROHIA-KARANGAHAKE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 38.55 | 35.55 | 35.55 | 0.00010858 | 3.0544e-06 | 2015-02-13 | C | 0.00010859 | 3.054e-06 | 2015 | 2015-02-13 | C | 1 | 0.00010858 | 3.0544e-06
1 | 3705789 | 2015-02-13 14:17 | 2015-02-13 14:42 | 25.0833 | 16 | 401.3333 | 0.0012274 | 4.8935e-05 | NAPA ID:05771 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF7-023 | To check/Replace Fuse Links. Works location: Pongakawa Area. WO 10146569. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 25.0833 | 22.0833 | 353.3333 | 0.0010792 | 4.8871e-05 | 2015-02-13 | B | 0.00053962 | 2.4435e-05 | 2015 | 2015-02-13 | B | 16 | 0.0010792 | 4.8871e-05
1 | 3858648 | 2015-02-13 20:14 | 2015-02-14 04:01 | 466.5333 | 276 | 47570.7333 | 0.14549 | 0.00084412 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 391389 | Fire event numbers as received 2 seperate F1787187 09 486 7948 - Belinda from fire service confirmed it is 664 Maketu Road. 8.23pm advised Glo at svs hub Car V Pole Pole # 391389. This Pole also carries ABS SE7-028, a tie point between TPV CB3 and PKW CB1 | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 172.3577 | 169.3577 | 46742.7333 | 0.14277 | 0.00084302 | 2015-02-13 | C | 0.14277 | 0.00084302 | 2015 | 2015-02-13 | C | 276 | 0.14277 | 0.00084302
1 | 3858925 | 2015-02-13 20:14 | 2015-02-14 03:49 | 454.7833 | 678 | 215222.1667 | 0.65824 | 0.0020736 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 391389 | Fire event numbers as received 2 separate F1787187 09 486 7948 - Belinda from fire service confirmed it is 664 Maketu Road. 8.23pm advised Glo at svs hub Car V Pole Pole # 391389. This Pole also carries ABS SE7-028, a tie point between TPV CB3 and PKW CB1 | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 317.4368 | 314.4368 | 213188.1667 | 0.65117 | 0.0020709 | 2015-02-13 | C | 0.65117 | 0.0020709 | 2015 | 2015-02-13 | C | 678 | 0.65117 | 0.0020709
1 | 3654268 | 2015-02-14 06:11 | 2015-02-14 06:22 | 11.2167 | 49 | 549.6167 | 0.001681 | 0.00014986 | NAPA ID:05507 TP_MASTERTON GXP > CHAPEL SUB > HEAD OFFICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse Switch C1040 | 11kv live tank oil sampling in fuse switch. Works location: Chapel St Masterton. WO 10138661 | F2 | HEAD OFFICE | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 11.2167 | 8.2167 | 402.6167 | 0.0012298 | 0.00014967 | 2015-02-14 | B | 0.00061488 | 7.4833e-05 | 2015 | 2015-02-14 | B | 49 | 0.0012298 | 0.00014967
1 | 3860019 | 2015-02-14 06:43 | 2015-02-14 07:47 | 64.7333 | 3021 | 154685.9667 | 0.47309 | 0.0092395 | Restore Supply on Device 2212 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 2212 | CB 2212 Kinleith GXP tripped to L/O - Neutral O/C flag - back feeds on CB 5 & CB 6 feeders established while initial line patrol & checking of LFI's were carried out - LFI operations inconclusive & nothing identified on line patrol with problem suspected | F1, F2, F3 | KINLEITH2212-BAIRD RD 33KV | TP_KINLEITH | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.2036 | 48.2036 | 145622.9667 | 0.44479 | 0.0092274 | 2015-02-14 | C | 0.44479 | 0.0092274 | 2015 | 2015-02-14 | C | 3021 | 0.44479 | 0.0092274
1 | 3869159 | 2015-02-14 06:50 | 2015-02-14 14:01 | 431 | 2 | 862 | 0.0026364 | 6.1168e-06 | Restore Supply on Device 8393 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8393 | Planned job 6468. Isolation for main switch replacement. Parent OMS 3693590. | F2 | KATERE 6 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 431 | 428 | 856 | 0.0026146 | 6.1088e-06 | 2015-02-14 | C | 0.0026146 | 6.109e-06 | 2015 | 2015-02-14 | C | 2 | 0.0026146 | 6.1088e-06
1 | 3654288 | 2015-02-14 07:44 | 2015-02-14 08:05 | 20.6667 | 22 | 454.6667 | 0.0013906 | 6.7285e-05 | NAPA ID:05586 TP_MASTERTON GXP > CHAPEL SUB > HEAD OFFICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C270 | 11kV live tank oil sampling C270. Works location: Cricket St, Masterton. WO 10138661. | F2 | HEAD OFFICE | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 20.6667 | 17.6667 | 388.6667 | 0.0011872 | 6.7197e-05 | 2015-02-14 | B | 0.00059358 | 3.3599e-05 | 2015 | 2015-02-14 | B | 22 | 0.0011872 | 6.7197e-05
1 | 3863084 | 2015-02-14 08:52 | 2015-02-14 11:18 | 146.0167 | 2824 | 384235.3167 | 1.1752 | 0.008637 | Restore Supply on Device 50 | 66000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 50 | CB 50 Whitianga tripped losing supply to Coromandel sub - Zone 1 Gr, Ph A fault, Ground Fault relays operated - line patrols initiated from both Whitianga & Coromandel ends with patrols being inconclusive - reclose attempt successful and all supply restor | F1, F2, F3 | WHITIANGA-COROMANDEL 66KV | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 136.0607 | 133.0607 | 375763.3167 | 1.1477 | 0.0086257 | 2015-02-14 | C | 1.1477 | 0.0086257 | 2015 | 2015-02-14 | C | 2824 | 1.1477 | 0.0086257
1 | 3668904 | 2015-02-14 09:15 | 2015-02-14 12:30 | 195.3167 | 57 | 11133.05 | 0.03405 | 0.00017433 | NAPA ID:06302 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ASHHURST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CUSTOMER REQUEST | P01347 | Install new 11m pole to feed new Transformer not installed fuses left in open position. Commission new 11kV transformer 7301P. | F3 | ASHHURST | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 195.3167 | 192.3167 | 10962.05 | 0.033483 | 0.0001741 | 2015-02-14 | B | 0.016741 | 8.7051e-05 | 2015 | 2015-02-14 | B | 57 | 0.033483 | 0.0001741
1 | 3715426 | 2015-02-14 09:17 | 2015-02-14 15:24 | 367.25 | 16 | 5771.2 | 0.017651 | 4.8935e-05 | NAPA ID:06048 TP_TE MATAI GXP > TE PUKE SUB > TE MATAI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SF5-022 | Replace Series one SDAF3 RMU with a Safelink CFCF. Reconfigure 11kV cable connections so transformers TF5-074 and TF5-075 are fused from the additional fuse switch. All cable testing to be completed within the Access Permit area so no test permit is req | F4 | TE MATAI RD | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 360.7 | 357.7 | 5723.2 | 0.017481 | 4.8871e-05 | 2015-02-14 | B | 0.0087405 | 2.4435e-05 | 2015 | 2015-02-14 | B | 16 | 0.017481 | 4.8871e-05
1 | 3776765 | 2015-02-14 13:00 | 2015-02-14 15:16 | 135.55 | 1 | 135.55 | 0.00041457 | 3.0584e-06 | NAPA ID:06660 TP_BRUNSWICK GXP > PEAT ST SUB > ARAMOHO INLAND | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1259 | 10 yearly 11kV metering check for RMU 4228. Urgent app to fit in with Factory shutdown. Works location: Kelvin St, Wanganui. WO 10174412. | F2 | ARAMOHO INLAND | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 135.55 | 132.55 | 132.55 | 0.00040486 | 3.0544e-06 | 2015-02-14 | B | 0.00020243 | 1.527e-06 | 2015 | 2015-02-14 | B | 1 | 0.00040486 | 3.0544e-06
1 | 3776771 | 2015-02-14 17:00 | 2015-02-14 20:53 | 233 | 1 | 233 | 0.00071261 | 3.0584e-06 | NAPA ID:06775 TP_BRUNSWICK GXP > CASTLECLIFF SUB > PURIRI ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2045 | 10 yearly 11kV metering check for RMU 2045. Work Loction: Hinau Street, Wanganui. Work Order 10173585 | F3 | PURIRI ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 233 | 230 | 230 | 0.00070252 | 3.0544e-06 | 2015-02-14 | B | 0.00035126 | 1.527e-06 | 2015 | 2015-02-14 | B | 1 | 0.00070252 | 3.0544e-06
1 | 3868075 | 2015-02-14 20:00 | 2015-02-14 20:15 | 15 | 16 | 240 | 0.00073402 | 4.8935e-05 | Restore Supply on Device X5 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2951 | Faultman found 2 blown fuses at Fuses 2951, line was patrolled and suspect line was hit by ducks as it runs by a pond. 2 X 15 Amp HV rewirable fuses replaced. Tony Sinclair attended. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 15 | 12 | 192 | 0.00058645 | 4.8871e-05 | 2015-02-14 | C | 0.00058645 | 4.8871e-05 | 2015 | 2015-02-14 | C | 16 | 0.00058645 | 4.8871e-05
1 | 3868475 | 2015-02-14 23:33 | 2015-02-15 09:32 | 598.6667 | 10 | 5986.6667 | 0.01831 | 3.0584e-05 | Restore Supply on Device SF5-001 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 223810 | Fuse SF5-001 Blown. Will not hold in. Line needs patrolling in daylight. Found possum on pole 223810. Removed and re-livened. Tom Tanoa Jr and HaydenMilburn attended. | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 598.6667 | 595.6667 | 5956.6667 | 0.018194 | 3.0544e-05 | 2015-02-14 | C | 0.018194 | 3.0544e-05 | 2015 | 2015-02-14 | C | 10 | 0.018194 | 3.0544e-05
1 | 3869042 | 2015-02-15 15:28 | 2015-02-15 16:43 | 74.8833 | 1 | 74.8833 | 0.00022902 | 3.0584e-06 | Restore Supply on Device T2/624 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/624 | Replaced 2X hV fuses | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 74.8833 | 71.8833 | 71.8833 | 0.00021956 | 3.0544e-06 | 2015-02-15 | C | 0.00021956 | 3.054e-06 | 2015 | 2015-02-15 | C | 1 | 0.00021956 | 3.0544e-06
1 | 3869066 | 2015-02-15 18:14 | 2015-02-15 20:11 | 116.9833 | 1 | 116.9833 | 0.00035778 | 3.0584e-06 | Restore Supply on Device Y99 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole 806212 | faultman found blown fuse at transformer Y99 on pole 806212. 1 X 2 Amp HV rewirable fuse. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 116.9833 | 113.9833 | 113.9833 | 0.00034815 | 3.0544e-06 | 2015-02-15 | C | 0.00034815 | 3.054e-06 | 2015 | 2015-02-15 | C | 1 | 0.00034815 | 3.0544e-06
1 | 3715391 | 2015-02-16 09:30 | 2015-02-16 15:20 | 350 | 3 | 1050 | 0.0032113 | 9.1753e-06 | NAPA ID:05512 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228951 | To replace Arms on pole 228951. Replace fuses SF7-029 with Fused ABS. Replace fuse links SF7-059 with Solid Links. Works location: Johnson Rd & Hereford Park Rd. WO 10146569. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 350 | 347 | 1041 | 0.0031797 | 9.1633e-06 | 2015-02-16 | B | 0.0015898 | 4.582e-06 | 2015 | 2015-02-16 | B | 3 | 0.0031797 | 9.1633e-06
1 | 3869245 | 2015-02-16 11:45 | 2015-02-16 13:50 | 125 | 3 | 375 | 0.0011469 | 9.1753e-06 | Restore Supply on Device 5391E | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 721386 | advised Talia at hub. 10.43am fire comms at site requesting eta. Brett advised LV line wrapped around another line will need to isolate transformer M3335 to make repairs. Requires Bucket Truck. 12.20 Brett advised the lines down are on the corner of Norma | F4 | OKAIAWA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 125 | 122 | 366 | 0.0011179 | 9.1633e-06 | 2015-02-16 | C | 0.0011179 | 9.163e-06 | 2015 | 2015-02-16 | C | 3 | 0.0011179 | 9.1633e-06
1 | 3869651 | 2015-02-16 16:03 | 2015-02-16 21:20 | 317 | 30 | 9497.6 | 0.029048 | 9.1753e-05 | Restore Supply on Device TD4-244 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-244 | Ted requesting 2nd response - suspects underground cable fault, tried to reliven a 10amp u/g ht cable link, and it just popped and blew straight away. Will need to isolate TD4-244 - this is on wooden pole, pole is unsafe to climb to isolate and needs buck | F3 | TE MAUNGA | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 316.5867 | 313.5867 | 9407.6 | 0.028735 | 9.1633e-05 | 2015-02-16 | C | 0.028735 | 9.1633e-05 | 2015 | 2015-02-16 | C | 30 | 0.028735 | 9.1633e-05
1 | 3869848 | 2015-02-16 21:50 | 2015-02-16 23:51 | 121.2 | 147 | 11668.3167 | 0.035687 | 0.00044959 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 9463/2 | Recloser 9463/2 tripped to L/O - E/F flag - line sectionalised & patrolled - no apparent fault found - all supply restored - Ted Glasgow & Clint Johnstone attended | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 79.3763 | 76.3763 | 11227.3167 | 0.034293 | 0.000449 | 2015-02-16 | C | 0.034293 | 0.000449 | 2015 | 2015-02-16 | C | 147 | 0.034293 | 0.000449
1 | 3870862 | 2015-02-17 07:44 | 2015-02-17 07:58 | 14.2167 | 210 | 2985.5 | 0.0091309 | 0.00064227 | Restore Supply on Device 2 | 22000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 808216 | CB1350 tripped E/F O/C A Phase. Found some bark on line at Pole 808216. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 14.2167 | 11.2167 | 2355.5 | 0.0071947 | 0.00064143 | 2015-02-17 | C | 0.0071947 | 0.00064143 | 2015 | 2015-02-17 | C | 210 | 0.0071947 | 0.00064143
1 | 3871095 | 2015-02-17 08:18 | 2015-02-17 10:13 | 115.45 | 2826 | 71304.0167 | 0.21808 | 0.0086431 | Restore Supply on Device 1272 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | MAG Sub | 33kV CB's 1272 and CB 1292 at Mangamaire GXP tripped on over current inverse time resulting in a loss of supply to Mangamutu Substation. At the time of the trippings, planned switching was being conducted on NAPA 6357 to close 33kV ABS XT65 and Open ABS | F1, F2, F3 | MANGAMUTU 1 33KV | TP_MANGAMAIRE | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 25.2314 | 22.2314 | 62826.0167 | 0.1919 | 0.0086318 | 2015-02-17 | C | 0.1919 | 0.0086318 | 2015 | 2015-02-17 | C | 2826 | 0.1919 | 0.0086318
1 | 3685118 | 2015-02-17 08:59 | 2015-02-17 15:08 | 368.6 | 27 | 9952.2 | 0.030438 | 8.2577e-05 | NAPA ID:03696 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L30 | Change 7 x x-arms, fit 22 x sets of 11kV insulators, change 7 x poles. Works location: Lake Rd, Oroua Downs. WO 10162444. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 368.6 | 365.6 | 9871.2 | 0.030151 | 8.2469e-05 | 2015-02-17 | B | 0.015075 | 4.1235e-05 | 2015 | 2015-02-17 | B | 27 | 0.030151 | 8.2469e-05
1 | 3623323 | 2015-02-17 09:01 | 2015-02-17 13:32 | 271.4667 | 11 | 2986.1333 | 0.0091329 | 3.3643e-05 | NAPA ID:04500 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1406 | Replace 11kV crossarms. Works location: Rollet Rd, Tokorea. WO 10155882. | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 271.4667 | 268.4667 | 2953.1333 | 0.0090201 | 3.3599e-05 | 2015-02-17 | B | 0.0045101 | 1.6799e-05 | 2015 | 2015-02-17 | B | 11 | 0.0090201 | 3.3599e-05
1 | 3628286 | 2015-02-17 09:16 | 2015-02-17 15:46 | 390.2333 | 4 | 1560.9333 | 0.004774 | 1.2234e-05 | NAPA ID:05582 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M1159 | To replace 11kV conductor between Poles M1159 and M1177. Works location: Waotu Rd. WO 10134042. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 390.2333 | 387.2333 | 1548.9333 | 0.0047311 | 1.2218e-05 | 2015-02-17 | B | 0.0023655 | 6.109e-06 | 2015 | 2015-02-17 | B | 4 | 0.0047311 | 1.2218e-05
1 | 3674460 | 2015-02-17 09:17 | 2015-02-17 09:26 | 8.9167 | 5 | 44.5833 | 0.00013635 | 1.5292e-05 | NAPA ID:05692 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 11002 | 11kv Live Tank oil sampling CB's 11002 and 11005. Works location: Te Whiti Rd Masterton WO 10138661. This outage did not happen I opened the Fuse switch But the Men in the Field Did not as there was a funny sound coming from Fuse switch So outage did no | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 8.9167 | 5.9167 | 29.5833 | 9.036e-05 | 1.5272e-05 | 2015-02-17 | B | 4.518e-05 | 7.636e-06 | 2015 | 2015-02-17 | B | 5 | 9.036e-05 | 1.5272e-05
1 | 3815857 | 2015-02-17 09:49 | 2015-02-17 15:54 | 365 | 44 | 16024 | 0.049008 | 0.00013457 | NAPA ID:06357 TP_MANGAMAIRE GXP > MANGAMUTU SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | mangamutu sub | Replace 33Kv Pole P00340 & Twin circuit 11kV pole P00341 & Install new TX at pole P00341. Note transfer 11kV from R44 ( 4 TX's ) to Feeder 9 -pole P00386 ( to remain on feeder 9 for approximately 2 weeks ) | F1 | TMP | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 364.1818 | 361.1818 | 15892 | 0.048541 | 0.00013439 | 2015-02-17 | B | 0.02427 | 6.7197e-05 | 2015 | 2015-02-17 | B | 44 | 0.048541 | 0.00013439
1 | 3674448 | 2015-02-17 11:37 | 2015-02-17 11:50 | 13.7833 | 4 | 55.1333 | 0.00016862 | 1.2234e-05 | NAPA ID:05694 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8053-2 | 11kV Live Tank oil sampling CB 8053-2. Works location; Stuart Rd, Masterton. WO 10138661. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 13.7833 | 10.7833 | 43.1333 | 0.00013175 | 1.2218e-05 | 2015-02-17 | B | 6.5874e-05 | 6.109e-06 | 2015 | 2015-02-17 | B | 4 | 0.00013175 | 1.2218e-05
1 | 3876565 | 2015-02-17 15:50 | 2015-02-17 17:36 | 106.1833 | 5 | 530.9167 | 0.0016238 | 1.5292e-05 | Restore Supply on Device 11002 | 11000 | UNPLANNED | Distribution Equip. | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Fuse switch 11002 | Take oil samples and move Cable termation as it was rubbing on Switch gear | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106.1833 | 103.1833 | 515.9167 | 0.0015758 | 1.5272e-05 | 2015-02-17 | C | 0.0015758 | 1.5272e-05 | 2015 | 2015-02-17 | C | 5 | 0.0015758 | 1.5272e-05
1 | 3876775 | 2015-02-17 16:39 | 2015-02-17 18:33 | 114.7833 | 1 | 114.7833 | 0.00035106 | 3.0584e-06 | Restore Supply on Device X3078 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 81328 Transformer X3078 | 17/2 5.04pm - smoke coming out of the middle pole fuse. 5.05pm - advise FM | F4 | CROFTON | ARAHINA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 114.7833 | 111.7833 | 111.7833 | 0.00034143 | 3.0544e-06 | 2015-02-17 | C | 0.00034143 | 3.054e-06 | 2015 | 2015-02-17 | C | 1 | 0.00034143 | 3.0544e-06
1 | 3876847 | 2015-02-17 20:48 | 2015-02-17 21:19 | 31.2167 | 1 | 31.2167 | 9.5474e-05 | 3.0584e-06 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 787899 | replace 2 amp ht fuse. cause: old age. pole 787899. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. This outage was inferenced up to an auto reclose on the feeder which has increased the customer n | F4 | PAPAKAI | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 31.2167 | 28.2167 | 28.2167 | 8.6186e-05 | 3.0544e-06 | 2015-02-17 | C | 8.6186e-05 | 3.054e-06 | 2015 | 2015-02-17 | C | 1 | 8.6186e-05 | 3.0544e-06
1 | 3688657 | 2015-02-18 08:17 | 2015-02-18 12:26 | 249.6 | 1 | 249.6 | 0.00076338 | 3.0584e-06 | NAPA ID:05720 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 832717 | At T2003 replace pole with busck structure pole 832717. Works location: West Bush Rd Masterton. WO 10170778. | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 249.6 | 246.6 | 246.6 | 0.00075322 | 3.0544e-06 | 2015-02-18 | B | 0.00037661 | 1.527e-06 | 2015 | 2015-02-18 | B | 1 | 0.00075322 | 3.0544e-06
1 | 3693595 | 2015-02-18 08:34 | 2015-02-18 08:46 | 12.3667 | 20 | 247.3333 | 0.00075645 | 6.1168e-05 | NAPA ID:05696 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7989/2 | 11kv Live Tank oil sampling 7989/2. Works location: McDonald Way, Masterton. WO 10138661. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 12.3667 | 9.3667 | 187.3333 | 0.0005722 | 6.1088e-05 | 2015-02-18 | B | 0.0002861 | 3.0544e-05 | 2015 | 2015-02-18 | B | 20 | 0.0005722 | 6.1088e-05
1 | 3744707 | 2015-02-18 08:45 | 2015-02-18 14:28 | 342.95 | 46 | 15775.7 | 0.048249 | 0.00014069 | NAPA ID:05740 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4840 | Replace transformer TC4840 with unitised new 200kVA. Install new DP next to transformer for new Cafe. Works location: Waitete Rd, Waihi. WO 10148220. | F3 | VICTORIA ST | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 342.95 | 339.95 | 15637.7 | 0.047764 | 0.0001405 | 2015-02-18 | B | 0.023882 | 7.0252e-05 | 2015 | 2015-02-18 | B | 46 | 0.047764 | 0.0001405
1 | 3879372 | 2015-02-18 09:00 | 2015-02-18 15:17 | 377 | 76 | 28652 | 0.08763 | 0.00023244 | Restore Supply on Device SC2-122 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209319 | This is part of a planned Job: NAPA 5395. OMS: 3744886 | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 377 | 374 | 28424 | 0.086819 | 0.00023214 | 2015-02-18 | C | 0.086819 | 0.00023214 | 2015 | 2015-02-18 | C | 76 | 0.086819 | 0.00023214
1 | 3876382 | 2015-02-18 09:03 | 2015-02-18 10:01 | 58.0167 | 158 | 8008.9 | 0.024495 | 0.00048323 | NAPA ID:07113 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220006 | INSTALL NEW SPUR LINE DDO UNITS FP 1667 AT POLE 268104 REPLACE DOUBLE ARM AT POLE 220006. DFT 101-39354 Works location: Waitao Rd WO 30001384 | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 50.6892 | 47.6892 | 7534.9 | 0.023015 | 0.0004826 | 2015-02-18 | B | 0.011507 | 0.0002413 | 2015 | 2015-02-18 | B | 158 | 0.023015 | 0.0004826
1 | 3623940 | 2015-02-18 09:03 | 2015-02-18 12:49 | 225.7667 | 3 | 677.3 | 0.0020715 | 9.1753e-06 | NAPA ID:04502 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1481 | Replace 11kV crossarms. Works location: Tamatea Rd, Tokoroa. WO 10155882. | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 225.7667 | 222.7667 | 668.3 | 0.0020413 | 9.1633e-06 | 2015-02-18 | B | 0.0010206 | 4.582e-06 | 2015 | 2015-02-18 | B | 3 | 0.0020413 | 9.1633e-06
1 | 3706318 | 2015-02-18 09:08 | 2015-02-18 15:26 | 377.95 | 26 | 9826.7 | 0.030054 | 7.9519e-05 | NAPA ID:06212 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer W2082 | Replacing three 11kv poles including three transformers W2082, W20280, C6005 also ABS WH291. Works location: Ararata Rd Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 377.95 | 374.95 | 9748.7 | 0.029777 | 7.9415e-05 | 2015-02-18 | B | 0.014888 | 3.9708e-05 | 2015 | 2015-02-18 | B | 26 | 0.029777 | 7.9415e-05
1 | 3745050 | 2015-02-18 09:15 | 2015-02-18 15:06 | 350.5167 | 295 | 95904.25 | 0.29332 | 0.00090223 | NAPA ID:06073 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV W1153 | Reconductoring. Works location: Irishtown Rd Kuaotunu. WO 10148314 | F3 | KUAOTUNU | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 325.0992 | 322.0992 | 95019.25 | 0.29023 | 0.00090105 | 2015-02-18 | B | 0.14511 | 0.00045053 | 2015 | 2015-02-18 | B | 295 | 0.29023 | 0.00090105
1 | 3693601 | 2015-02-18 10:34 | 2015-02-18 10:50 | 16.4333 | 79 | 1298.2333 | 0.0039705 | 0.00024162 | NAPA ID:05699 TP_MASTERTON GXP > CHAPEL SUB > SOUTH RD CHAPEL | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8006/1, 8006/2 | 11kv oil sampling out of fuse switch's 8006-1 and 8006-2. Works location: William Donald Drive, Masterton. WO 10138661. | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 16.4333 | 13.4333 | 1061.2333 | 0.0032415 | 0.0002413 | 2015-02-18 | B | 0.0016207 | 0.00012065 | 2015 | 2015-02-18 | B | 79 | 0.0032415 | 0.0002413
1 | 3880032 | 2015-02-19 04:57 | 2015-02-19 07:03 | 125.7667 | 7 | 879.6 | 0.0026902 | 2.1409e-05 | Restore Supply on Device 7551 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuses 7551 | Suspect bird strike. Replaced 2x10Amp fuse links | F3 | BELVEDERE | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 125.6571 | 122.6571 | 858.6 | 0.0026225 | 2.1381e-05 | 2015-02-19 | C | 0.0026225 | 2.1381e-05 | 2015 | 2015-02-19 | C | 7 | 0.0026225 | 2.1381e-05
1 | 3869254 | 2015-02-19 08:01 | 2015-02-19 17:55 | 594.5667 | 105 | 3040.3167 | 0.0092986 | 0.00032113 | NAPA ID:06421 TP_TE MATAI GXP > TE PUKE SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 222639 | Replace Pole 222657, change to 11m Busck, also joint together 2 X 185mm 3c Ali that go up pole 222670 and remove ABS SE5 112 from pole 222670 Replace Fuses to TE5 198 and relabel FP1664. Works location: Queens St and Beatty Ave Junction. WO 10147934 | F3 | PAPAMOA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 28.9554 | 25.9554 | 2725.3167 | 0.0083243 | 0.00032071 | 2015-02-19 | B | 0.0041621 | 0.00016036 | 2015 | 2015-02-19 | B | 105 | 0.0083243 | 0.00032071
1 | 3875258 | 2015-02-19 08:30 | 2015-02-19 15:50 | 440.2 | 231 | 101686.2 | 0.311 | 0.0007065 | NAPA ID:07099 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11klV pole 749346 | Replace various network poles in work area and Install temp mid span break at pole 749346. Install new fused ABS 12059 and commission new ground mount TX 588. Works location: Fitzroy Rd. WO 30002060 | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 440.2 | 437.2 | 100993.2 | 0.30848 | 0.00070557 | 2015-02-19 | B | 0.15424 | 0.00035279 | 2015 | 2015-02-19 | B | 231 | 0.30848 | 0.00070557
1 | 3715427 | 2015-02-19 09:02 | 2015-02-19 14:39 | 336.8667 | 27 | 9095.4 | 0.027818 | 8.2577e-05 | NAPA ID:03752 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | L30 | Run new AL conductor from L30 to Temp DDos #39. Works location: Lake Road, Oroua Downs. WO 10162444. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 336.8667 | 333.8667 | 9014.4 | 0.027534 | 8.2469e-05 | 2015-02-19 | B | 0.013767 | 4.1235e-05 | 2015 | 2015-02-19 | B | 27 | 0.027534 | 8.2469e-05
1 | 3623981 | 2015-02-19 09:12 | 2015-02-19 15:21 | 369.0167 | 13 | 4797.2167 | 0.014672 | 3.9759e-05 | NAPA ID:04503 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1099 | replace 11kV crossarms. Works location: West Rd Tokoroa. WO 10155882 | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 369.0167 | 366.0167 | 4758.2167 | 0.014534 | 3.9708e-05 | 2015-02-19 | B | 0.0072668 | 1.9854e-05 | 2015 | 2015-02-19 | B | 13 | 0.014534 | 3.9708e-05
1 | 3714786 | 2015-02-19 09:46 | 2015-02-19 14:54 | 308.9 | 24 | 7413.6 | 0.022674 | 7.3402e-05 | NAPA ID:06095 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole F0389 | To replace 11kV poles cross arms and hardware between Pole # F0389 and F12518. Tower Road Matamata. Works location: IC762. WO 10148256 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 308.9 | 305.9 | 7341.6 | 0.022424 | 7.3306e-05 | 2015-02-19 | B | 0.011212 | 3.6653e-05 | 2015 | 2015-02-19 | B | 24 | 0.022424 | 7.3306e-05
1 | 3704993 | 2015-02-19 10:16 | 2015-02-19 13:50 | 214.7167 | 5 | 1073.5833 | 0.0032835 | 1.5292e-05 | NAPA ID:06219 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 723117 | replace two 11kv poles 723117, 723122. Works location: Ohangai Rd Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 214.7167 | 211.7167 | 1058.5833 | 0.0032334 | 1.5272e-05 | 2015-02-19 | B | 0.0016167 | 7.636e-06 | 2015 | 2015-02-19 | B | 5 | 0.0032334 | 1.5272e-05
1 | 3880650 | 2015-02-19 11:03 | 2015-02-19 15:07 | 244.05 | 323 | 10108.95 | 0.030917 | 0.00098787 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N12539 | CB 7 Trip. O/C. L/O. Caused by lines down at Poles M12539 (ABS IC371) and Lines contacting ground caused a small grass fire at both sites. Fire Service in attendance. Safety Manager completed # 449640. 160 mtrs Squirrel conductor 7 Tension sleeves used to | F3 | SHAW AVE | PAEROA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 31.2971 | 28.2971 | 9139.95 | 0.027917 | 0.00098658 | 2015-02-19 | C | 0.027917 | 0.00098658 | 2015 | 2015-02-19 | C | 323 | 0.027917 | 0.00098658
1 | 3880983 | 2015-02-19 11:11 | 2015-02-19 13:00 | 109.25 | 24 | 2604.05 | 0.0079643 | 7.3402e-05 | Restore Supply on Device TC764 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1474 | HV Fuse FC1474 found blown. 1 X HV Fuse replaced. No apparent fault found. | F4/F5 | COLVILLE | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 108.5021 | 105.5021 | 2532.05 | 0.007734 | 7.3306e-05 | 2015-02-19 | C | 0.007734 | 7.3306e-05 | 2015 | 2015-02-19 | C | 24 | 0.007734 | 7.3306e-05
1 | 3881485 | 2015-02-19 12:38 | 2015-02-19 16:12 | 213.6833 | 2 | 335.3667 | 0.0010257 | 6.1168e-06 | Restore Supply on Device 7901 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 7901 | 12.39pm advised Shan @ svs hub & control 1.08pm fire service calling for eta update.. called Joanne at service hub and she advised 1.15pm - faultman onsite now 1.11pm Fuses 7901 opened to isolate lines so fire could be extinguished & trees cleared from | F4 | MOUNT BRUCE | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 167.6833 | 164.6833 | 329.3667 | 0.001006 | 6.1088e-06 | 2015-02-19 | C | 0.001006 | 6.109e-06 | 2015 | 2015-02-19 | C | 2 | 0.001006 | 6.1088e-06
1 | 3882890 | 2015-02-19 16:15 | 2015-02-19 17:35 | 80 | 1 | 80 | 0.00024467 | 3.0584e-06 | Restore Supply on Device 2674T | 6600 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 130 LOWER NORFOLK RD | Part of the Te Rata Road power outage, power came back on when the area power was restored. OMS 3881686 is the parent to this outage. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 77 | 0.00023519 | 3.0544e-06 | 2015-02-19 | C | 0.00023519 | 3.054e-06 | 2015 | 2015-02-19 | C | 1 | 0.00023519 | 3.0544e-06
1 | 3881686 | 2015-02-19 16:15 | 2015-02-19 18:35 | 140.1667 | 188 | 26351.3333 | 0.080593 | 0.00057498 | Restore Supply on Device I21 | 6600 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 760533 | Tripping on CB I21 on E/F. Report of a Contractor (G.Moratti LTD). mulching a hedge and then hit a stay wire. This wire flicked up to 6.6kV line causing the tripping. Outside Road Phase). 33kV above offloaded and wire removed safely with fuse stick. reli | F3 | KAIMATA | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 140.1667 | 137.1667 | 25787.3333 | 0.078765 | 0.00057423 | 2015-02-19 | C | 0.078765 | 0.00057423 | 2015 | 2015-02-19 | C | 188 | 0.078765 | 0.00057423
1 | 3881900 | 2015-02-19 16:36 | 2015-02-19 18:18 | 102 | 903 | 34944.3833 | 0.10687 | 0.0027618 | Restore Supply on Device 3035 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | ARA 3086, RAT 3085 | CB 3086b A/R, L/O, E/F, O/C B Phase. Also tripped CB 3035 at Rata Sub. Total Outage of Rata Sub. Hunterville 22kV Feeder backfed via VS 848. 33kV Line Patrolled with no fault found & relivened ok. Backfeeds restored to normal. | F1, F2, F3 | ARAHINA 33KV | TP_MARTON | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 38.6981 | 35.6981 | 32235.3833 | 0.098461 | 0.0027581 | 2015-02-19 | C | 0.098461 | 0.0027581 | 2015 | 2015-02-19 | C | 903 | 0.098461 | 0.0027581
1 | 3883025 | 2015-02-19 18:23 | 2015-02-19 19:40 | 77 | 1 | 151.7833 | 0.00046422 | 3.0584e-06 | Restore Supply on Device O78 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P34326 |  | F4 | RONGOTEA | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 151.7833 | 148.7833 | 148.7833 | 0.00045445 | 3.0544e-06 | 2015-02-19 | C | 0.00045445 | 3.054e-06 | 2015 | 2015-02-19 | C | 1 | 0.00045445 | 3.0544e-06
1 | 3883824 | 2015-02-19 21:20 | 2015-02-20 01:15 | 234.7333 | 2 | 311.3667 | 0.00095229 | 6.1168e-06 | Restore Supply on Device TC4-400 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4-370 | 19/02/15 - at 21:20 Triton Sub, CB 2 Hewletts Rd Feeder. Call came in from Fire Service of Transformer on fire. Faultman dispatched. Found transformer TC4-370 on fire. Isolated Transformer at Fuses SC4-580 and fire service put out fire. Once fire out, iso | F2 | HEWLETTS RD | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 155.6833 | 152.6833 | 305.3667 | 0.00093272 | 6.1088e-06 | 2015-02-19 | C | 0.00093272 | 6.109e-06 | 2015 | 2015-02-19 | C | 2 | 0.00093272 | 6.1088e-06
1 | 3715390 | 2015-02-19 22:03 | 2015-02-19 22:11 | 8.3833 | 1 | 8.3833 | 2.564e-05 | 3.0584e-06 | NAPA ID:05700 TP_GREYTOWN GXP > KEMPTON SUB > WEST ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 11006 | 11kv Live Tank oil sampling CB 11006. Works location: West St Greytown. WO 10138659 | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 8.3833 | 5.3833 | 5.3833 | 1.6443e-05 | 3.0544e-06 | 2015-02-19 | B | 8.221e-06 | 1.527e-06 | 2015 | 2015-02-19 | B | 1 | 1.6443e-05 | 3.0544e-06
1 | 3884357 | 2015-02-20 04:48 | 2015-02-20 10:12 | 324.1667 | 21 | 1769.0833 | 0.0054106 | 6.4227e-05 | Restore Supply on Device 920 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758177 | 6:42am 2R Request as broken insulator on HV line and require more materials and requested for warren to assist. Initial auto-reclose on CB 8 on E/F. Broken Insulator found on Leith Rd. Outage required from Fuses 8459 to replace. (One Insulator and Binde | F4 | SEAWARD COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 84.2421 | 81.2421 | 1706.0833 | 0.0052111 | 6.4143e-05 | 2015-02-20 | C | 0.0052111 | 6.4143e-05 | 2015 | 2015-02-20 | C | 21 | 0.0052111 | 6.4143e-05
1 | 3773809 | 2015-02-20 08:48 | 2015-02-20 16:47 | 478.3833 | 137 | 65538.5167 | 0.20044 | 0.000419 | NAPA ID:06570 TP_OPUNAKE GXP > TASMAN SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 714032 | Replacing 8 x 11Kv double circuit Poles/xarms between poles 714032~713890~713924. Also installing new 11Kv 185 u/g cable from existing Pole 373025 with new 11kv links 12040 installed & at other end of cable replacing pole 713924 with new 11Kv links 12041o | F3 | OPUNAKE | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 478.3833 | 475.3833 | 65127.5167 | 0.19893 | 0.00041846 | 2015-02-20 | B | 0.099464 | 0.00020923 | 2015 | 2015-02-20 | B | 137 | 0.19893 | 0.00041846
1 | 3773796 | 2015-02-20 09:00 | 2015-02-20 15:13 | 373 | 23 | 8579 | 0.026238 | 7.0344e-05 | NAPA ID:03754 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P31881 | Run new AL conductor from Temp DDos #39 to Temp DDos #40. Works location: Lake Rd Oroua Downs. WO 10162444. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 373 | 370 | 8510 | 0.025993 | 7.0252e-05 | 2015-02-20 | B | 0.012997 | 3.5126e-05 | 2015 | 2015-02-20 | B | 23 | 0.025993 | 7.0252e-05
1 | 3744672 | 2015-02-20 09:00 | 2015-02-20 15:07 | 366.75 | 38 | 1943.0667 | 0.0059427 | 0.00011622 | NAPA ID:05290 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > TE AROHA BOROUGH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4253 | To Disconnect the 11kV Cable From FC4253. Connect new 11kV Cable From new CFC 9886/3 to the Base of FC4253. Connect the existing cable from TC4253 into 9886/2. Replace Links FP89 to Solid Links. Works location: Waihou Rd, Te Aroha. WO 30000221. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.1333 | 48.1333 | 1829.0667 | 0.0055867 | 0.00011607 | 2015-02-20 | B | 0.0027934 | 5.8034e-05 | 2015 | 2015-02-20 | B | 38 | 0.0055867 | 0.00011607
1 | 3771240 | 2015-02-20 09:03 | 2015-02-20 09:31 | 27.8833 | 57 | 1589.35 | 0.0048609 | 0.00017433 | NAPA ID:05483 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 231044 | To Check Replace Fuse Links and replace cross arm on pole 231044. Works location: Maniatutu Rd. WO 10146569. | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 27.8833 | 24.8833 | 1418.35 | 0.0043322 | 0.0001741 | 2015-02-20 | B | 0.0021661 | 8.7051e-05 | 2015 | 2015-02-20 | B | 57 | 0.0043322 | 0.0001741
1 | 3744473 | 2015-02-20 10:00 | 2015-02-20 13:07 | 186.6 | 69 | 12875.4 | 0.039378 | 0.00021103 | NAPA ID:06490 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 795063 | Replace rotten hardwood pole 795063 transformer X787 erect pole and liven to tops of fuses. Works location: Tiriakawa Rd, Taihape. WO 30000868. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 186.6 | 183.6 | 12668.4 | 0.038695 | 0.00021076 | 2015-02-20 | B | 0.019347 | 0.00010538 | 2015 | 2015-02-20 | B | 69 | 0.038695 | 0.00021076
1 | 3886287 | 2015-02-20 19:04 | 2015-02-21 00:08 | 304.2833 | 1 | 304.2833 | 0.00093063 | 3.0584e-06 | Restore Supply on Device E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G215/T1 & T2 |  | F2 | MAIN ST 26 | MAIN ST SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 304.2833 | 301.2833 | 301.2833 | 0.00092025 | 3.0544e-06 | 2015-02-20 | C | 0.00092025 | 3.054e-06 | 2015 | 2015-02-20 | C | 1 | 0.00092025 | 3.0544e-06
1 | 3886316 | 2015-02-20 21:25 | 2015-02-20 23:22 | 117.2 | 9 | 937.4 | 0.002867 | 2.7526e-05 | Restore Supply on Device T1995 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7236 | *** check if oms 3886321 - #107 Buicks Road is also part of this outage *** Replaced 2x 10Amp HV Fuselinks. Suspect bird strike | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 104.1556 | 101.1556 | 910.4 | 0.0027807 | 2.749e-05 | 2015-02-20 | C | 0.0027807 | 2.749e-05 | 2015 | 2015-02-20 | C | 9 | 0.0027807 | 2.749e-05
1 | 3886886 | 2015-02-21 03:44 | 2015-02-21 04:05 | 20.9 | 526 | 9614.45 | 0.029405 | 0.0016087 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Kerepehi Sub CB 5 Mangatarata Feeder | At 03:44 Kerepehi Sub, CB 5 Mangatarata Feeder, Tripped, E/F, L/O. Faultmen dispatched and investigation began. Partial Backfeed from KPE 1 at 03:59, Recloser RC24 Opened, Sectionaliser SC8 Closed. Waited 15 Minutes and manual reclose tried on CB 5 and he | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 18.2784 | 15.2784 | 8036.45 | 0.024547 | 0.0016066 | 2015-02-21 | C | 0.024547 | 0.0016066 | 2015 | 2015-02-21 | C | 526 | 0.024547 | 0.0016066
1 | 3776109 | 2015-02-21 05:20 | 2015-02-21 07:26 | 125.5333 | 36 | 4519.2 | 0.013822 | 0.0001101 | NAPA ID:06573 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 9 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV G206B | 3 yearly Maint on Switchgear & Tx . Works location: Pioneer Hwy Palmerston North. WO 10142830 | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 125.5333 | 122.5333 | 4411.2 | 0.013474 | 0.00010996 | 2015-02-21 | B | 0.0067368 | 5.498e-05 | 2015 | 2015-02-21 | B | 36 | 0.013474 | 0.00010996
1 | 3771802 | 2015-02-21 09:00 | 2015-02-21 15:24 | 383.6333 | 23 | 8823.5667 | 0.026986 | 7.0344e-05 | NAPA ID:06708 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD3-073 | Replace poles,crossarms and conductor. Works location: Te Puna Station Rd. WO 30000216 | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 383.6333 | 380.6333 | 8754.5667 | 0.02674 | 7.0252e-05 | 2015-02-21 | B | 0.01337 | 3.5126e-05 | 2015 | 2015-02-21 | B | 23 | 0.02674 | 7.0252e-05
1 | 3771801 | 2015-02-21 09:23 | 2015-02-21 14:55 | 331.65 | 433 | 116949.6 | 0.35768 | 0.0013243 | NAPA ID:06010 TP_STRATFORD GXP > KAPONGA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5990 | 6 Yearly 33kV ABS 444, 448, 447, 446 AND 11kV ABS T27, T13, T34, T45 maintenance. Has to be done during school holiday or weekend, 2 schools affected. Works location: Kaponga Sub. WO 10154818 | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 270.0915 | 267.0915 | 115650.6 | 0.35325 | 0.0013226 | 2015-02-21 | B | 0.17662 | 0.00066128 | 2015 | 2015-02-21 | B | 433 | 0.35325 | 0.0013226
1 | 3890297 | 2015-02-21 23:08 | 2015-02-22 00:55 | 107.05 | 30 | 3211.5 | 0.0098221 | 9.1753e-05 | Restore Supply on Device TA2-080/F1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 204272 | Broken insulator found on pole 204272. Additional faultman requested for Safety. (HV Fault alone at night). Insulator and jumper replaced. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 107.05 | 104.05 | 3121.5 | 0.0095344 | 9.1633e-05 | 2015-02-21 | C | 0.0095344 | 9.1633e-05 | 2015 | 2015-02-21 | C | 30 | 0.0095344 | 9.1633e-05
1 | 3890359 | 2015-02-22 04:43 | 2015-02-22 08:33 | 229.8 | 429 | 61848.2 | 0.18916 | 0.0013121 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole O1533 | CB 2 tripped to L/O - E/F & O/C flags - line sectionalised & patrolled with blown HV insulator located on pole O1533 - isolation points were CB 2, ABS IC398, ABS IC365 - backfeeds established from ABS IC436 & ABS IC1276 - insulator replaced & all supply r | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 144.1683 | 141.1683 | 60561.2 | 0.18498 | 0.0013103 | 2015-02-22 | C | 0.18498 | 0.0013103 | 2015 | 2015-02-22 | C | 429 | 0.18498 | 0.0013103
1 | 3891749 | 2015-02-22 12:32 | 2015-02-22 13:39 | 67.1667 | 1 | 67.1667 | 0.00020542 | 3.0584e-06 | Restore Supply on Device X5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 792455 | Replaced 2X 15a HV fuses. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 67.1667 | 64.1667 | 64.1667 | 0.00019599 | 3.0544e-06 | 2015-02-22 | C | 0.00019599 | 3.054e-06 | 2015 | 2015-02-22 | C | 1 | 0.00019599 | 3.0544e-06
1 | 3891847 | 2015-02-22 20:02 | 2015-02-22 21:45 | 103 | 6 | 618 | 0.0018901 | 1.8351e-05 | Restore Supply on Device 6243 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 6243 | Faultman found a blown fuse at Fuses 6243,line patrolled no fault found. 1 x 10HV rewirable fuse replaced. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 103 | 100 | 600 | 0.0018327 | 1.8327e-05 | 2015-02-22 | C | 0.0018327 | 1.8327e-05 | 2015 | 2015-02-22 | C | 6 | 0.0018327 | 1.8327e-05
1 | 3891840 | 2015-02-22 21:13 | 2015-02-22 21:55 | 42 | 29 | 1217.1 | 0.0037224 | 8.8694e-05 | Restore Supply on Device X1065 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Fuses 2611 | Faultman found 2 blown fuses at Fuses 2611, line was patrolled suspect bird strike. 2 X 10Amp HV rewirable fuses replaced | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 41.969 | 38.969 | 1130.1 | 0.0034518 | 8.8578e-05 | 2015-02-22 | C | 0.0034518 | 8.8578e-05 | 2015 | 2015-02-22 | C | 29 | 0.0034518 | 8.8578e-05
1 | 3891887 | 2015-02-22 22:30 | 2015-02-23 02:38 | 247.7 | 528 | 93333.4167 | 0.28545 | 0.0016148 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9773 | Recloser 9773 Trip. E/F. L/O. Tried closing after 15mins and Recloser tripped. Feeder sectionalised and no fault found. Unknown Cause. | F4 | CAMBRIDGE RD TIRAU | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 176.7678 | 173.7678 | 91749.4167 | 0.28024 | 0.0016127 | 2015-02-22 | C | 0.28024 | 0.0016127 | 2015 | 2015-02-22 | C | 528 | 0.28024 | 0.0016127
1 | 3893482 | 2015-02-23 08:36 | 2015-02-23 10:27 | 111.3667 | 246 | 15887.1833 | 0.04859 | 0.00075237 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P41779 | CB 11, tripped on E/F. Lines patrolled and fault found to be insulator at Pole P41779. No backfeeds possibele. Relivened OK. Shazil Khan attended. | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 64.582 | 61.582 | 15149.1833 | 0.046272 | 0.00075139 | 2015-02-23 | C | 0.046272 | 0.00075139 | 2015 | 2015-02-23 | C | 246 | 0.046272 | 0.00075139
1 | 3893730 | 2015-02-23 08:39 | 2015-02-23 10:58 | 138.35 | 216 | 23581.4667 | 0.072122 | 0.00066062 | Restore Supply on Device R11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2541T | CB R11 L/O on O/C. Sectionalised and found faulty transformer 2541T. Isolated and relivened rest of feeder Transformer to be defected and replaced at later stage as per customer request. Transformer 2541T was not in use at the time of the outage, resulted | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.1735 | 106.1735 | 22933.4667 | 0.070049 | 0.00065976 | 2015-02-23 | C | 0.070049 | 0.00065976 | 2015 | 2015-02-23 | C | 216 | 0.070049 | 0.00065976
1 | 3777568 | 2015-02-23 09:07 | 2015-02-23 15:34 | 386.55 | 17 | 6571.35 | 0.020098 | 5.1993e-05 | NAPA ID:05051 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-011 | Replace poles,crossarms and conductor between IP510 & SD3-011. Works location: Te Puna Station Rd. WO 30000216 | F4 | WAIPUNA | BETHLEHEM SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 386.55 | 383.55 | 6520.35 | 0.019916 | 5.1925e-05 | 2015-02-23 | B | 0.009958 | 2.5963e-05 | 2015 | 2015-02-23 | B | 17 | 0.019916 | 5.1925e-05
1 | 3773798 | 2015-02-23 09:25 | 2015-02-23 15:00 | 335 | 19 | 6365 | 0.019467 | 5.811e-05 | NAPA ID:03821 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P32846 | Run new AL conductor from Temp DDos #40 to Temp DDos #41. Works location: Lake Rd Oroua Downs. WO 10162444 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 335 | 332 | 6308 | 0.019267 | 5.8034e-05 | 2015-02-23 | B | 0.0096337 | 2.9017e-05 | 2015 | 2015-02-23 | B | 19 | 0.019267 | 5.8034e-05
1 | 3721534 | 2015-02-23 09:36 | 2015-02-23 15:21 | 345.05 | 28 | 9565.8 | 0.029256 | 8.5636e-05 | NAPA ID:05513 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 229220 | To Replace arms And 11kV Fuses on pole 229220. To replace pole 229243, Hardware 7 replace fuses SF7-051 with Fused ABS. Works locatioN: Benner Rd. WO 10146569 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 341.6357 | 338.6357 | 9481.8 | 0.028961 | 8.5524e-05 | 2015-02-23 | B | 0.014481 | 4.2762e-05 | 2015 | 2015-02-23 | B | 28 | 0.028961 | 8.5524e-05
1 | 3906326 | 2015-02-23 09:52 | 2015-02-23 10:21 | 29 | 2826 | 79317 | 0.24258 | 0.0086431 | Restore Supply on Device XT60 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p16999 | Job 3895646 whole sub trip found blown insulator at pole P16999. | F1, F2, F3 | MANGAMUTU 2 33KV | TP_MANGAMAIRE | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 28.0669 | 25.0669 | 70839 | 0.21637 | 0.0086318 | 2015-02-23 | C | 0.21637 | 0.0086318 | 2015 | 2015-02-23 | C | 2826 | 0.21637 | 0.0086318
1 | 3895202 | 2015-02-23 09:53 | 2015-02-23 11:32 | 99.1667 | 439 | 30313.5167 | 0.092712 | 0.0013426 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 2217444 | Fault caused by tree cutting. Trees to be pulled over with digger, Colin Winch aware of site & procedure being under taken. NOC rung Mike to accertain all personnel safe. Mike carried out the isolation's. Mike Strange on site under OMS 3881683 as a stando | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 69.0513 | 66.0513 | 28996.5167 | 0.088568 | 0.0013409 | 2015-02-23 | C | 0.088568 | 0.0013409 | 2015 | 2015-02-23 | C | 439 | 0.088568 | 0.0013409
1 | 3899146 | 2015-02-23 14:01 | 2015-02-23 15:23 | 82.0333 | 529 | 13584.3167 | 0.041547 | 0.0016179 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB8 | CB Trip, Flags E/F. Line patrolled & sectionalized no fault found Back feeds used Rec RP09 NOC Open Rec 9462 NOC Close (WBY 3) | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 25.6792 | 22.6792 | 11997.3167 | 0.036645 | 0.0016158 | 2015-02-23 | C | 0.036645 | 0.0016158 | 2015 | 2015-02-23 | C | 529 | 0.036645 | 0.0016158
1 | 3900313 | 2015-02-23 15:50 | 2015-02-24 02:03 | 613.2333 | 513 | 75557.3333 | 0.23109 | 0.001569 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | Pole 50674 | *** Complete safety manager or when signing off oms 3900303 *** 1 x A/R on CB 2 was followed by report from public of tree through line at pole number 50674 with lines down. CB 2 Thames opened by NOC & line isolated at ABS 358 & IC936. Back feed establ | F3 | TOTARA | THAMES SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 147.2853 | 144.2853 | 74018.3333 | 0.22608 | 0.0015669 | 2015-02-23 | C | 0.22608 | 0.0015669 | 2015 | 2015-02-23 | C | 513 | 0.22608 | 0.0015669
1 | 3900467 | 2015-02-23 15:52 | 2015-02-23 16:13 | 21.4833 | 127 | 2728.3833 | 0.0083445 | 0.00038842 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 4200/2 | Tree contractors were working on the line and HLT was applied to Recloser 4200. Contractors were all clear but report that were was thunder and lightening. Relivened OK. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 21.4833 | 18.4833 | 2347.3833 | 0.0071699 | 0.00038791 | 2015-02-23 | C | 0.0071699 | 0.00038791 | 2015 | 2015-02-23 | C | 127 | 0.0071699 | 0.00038791
1 | 3900311 | 2015-02-23 15:56 | 2015-02-23 22:09 | 373.5833 | 2 | 745.6667 | 0.0022806 | 6.1168e-06 | Restore Supply on Device T5/177 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | T5/177 | No power to both 472 and 471 LOWER PAKIHIKURA ROAD both feed from the same TX T5/177. 6:56pm Request for 2r to replaced blown TX T5/177. Replaced 50KVA TX - cause was due to lightning. No other assets repaired or replaced. Adjacent assets were checke | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 372.8333 | 369.8333 | 739.6667 | 0.0022593 | 6.1088e-06 | 2015-02-23 | C | 0.0022593 | 6.109e-06 | 2015 | 2015-02-23 | C | 2 | 0.0022593 | 6.1088e-06
1 | 3898619 | 2015-02-23 17:26 | 2015-02-24 17:34 | 1448 | 6 | 2430 | 0.007432 | 1.8351e-05 | Restore Supply on Device TE6-170 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE6-088 | Fuses SE6-088 reloaded 1 fuse blown cable & transformer need to be tested. Cable proved faulty. Fault location and repairs to be commenced 24/02/15. Generator was installed at transformer TE6-170 @ 00:06. OMS will still be showing transformer off. Needs t | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 405 | 402 | 2412 | 0.0073673 | 1.8327e-05 | 2015-02-23 | C | 0.0073673 | 1.8327e-05 | 2015 | 2015-02-23 | C | 6 | 0.0073673 | 1.8327e-05
1 | 3744737 | 2015-02-24 00:07 | 2015-02-24 01:14 | 67 | 39 | 2613 | 0.0079917 | 0.00011928 | NAPA ID:05295 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > STANLEY AVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1345 | To Disconnect & Remove 11kV Cable Suppling TC1345. To connect new cable from 9887/2. Works location: Waihou Rd Stanley Ave, Te Aroha. WO 30000221. | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 67 | 64 | 2496 | 0.0076238 | 0.00011912 | 2015-02-24 | B | 0.0038119 | 5.9561e-05 | 2015 | 2015-02-24 | B | 39 | 0.0076238 | 0.00011912
1 | 3797951 | 2015-02-24 08:35 | 2015-02-24 15:25 | 410.2167 | 12 | 4922.6 | 0.015055 | 3.6701e-05 | NAPA ID:05654 TP_MASTERTON GXP > AWATOITOI SUB > ROROKOKO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 833933 | Replace 33Kv/11kv pole 833933. the 33kV will already be isolated under NAPA 5648. | F5 | ROROKOKO | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 410.2167 | 407.2167 | 4886.6 | 0.014926 | 3.6653e-05 | 2015-02-24 | B | 0.0074629 | 1.8327e-05 | 2015 | 2015-02-24 | B | 12 | 0.014926 | 3.6653e-05
1 | 3906297 | 2015-02-24 09:00 | 2015-02-24 15:37 | 397 | 15 | 5955 | 0.018213 | 4.5876e-05 | Restore Supply on Device T1/324 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | temp 41 | Unable to link this planned job to Parent OMS 3773802 NAPA 3822. Run new conductor from temp Fuses 41 to Temp fuses 42. This is job 7 of 20 for network project 6973. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 397 | 394 | 5910 | 0.018052 | 4.5816e-05 | 2015-02-24 | C | 0.018052 | 4.5816e-05 | 2015 | 2015-02-24 | C | 15 | 0.018052 | 4.5816e-05
1 | 3628305 | 2015-02-24 09:10 | 2015-02-24 14:55 | 345 | 1 | 345 | 0.0010552 | 3.0584e-06 | NAPA ID:05585 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M1159 | To replace 11kV poles and cross arms in preparation for conductor upgrade. Works location: Waotu Rd. WO 10134042 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 345 | 342 | 342 | 0.0010446 | 3.0544e-06 | 2015-02-24 | B | 0.00052231 | 1.527e-06 | 2015 | 2015-02-24 | B | 1 | 0.0010446 | 3.0544e-06
1 | 3799632 | 2015-02-24 09:55 | 2015-02-24 15:19 | 323.6167 | 9 | 2885.8833 | 0.0088262 | 2.7526e-05 | NAPA ID:05527 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses Sf6-027 | To replace SF6-022 with a fuses ABS. To replace the fuse arm SF6-027 | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 320.6537 | 317.6537 | 2858.8833 | 0.0087322 | 2.749e-05 | 2015-02-24 | B | 0.0043661 | 1.3745e-05 | 2015 | 2015-02-24 | B | 9 | 0.0087322 | 2.749e-05
1 | 3903027 | 2015-02-24 09:57 | 2015-02-24 13:44 | 227.05 | 22 | 1469.55 | 0.0044945 | 6.7285e-05 | Restore Supply on Device X4333 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 791493 | Cross arm is on a angle and hanging on by one bolt. Pole has a tag on it. Electrix contractor is reporting a broken cross arm on pole 791493 24/02 10.06am advised hub 12.20 hv oh lost main bolt requesting 2r to replace the main bolt not needing to r | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 66.7977 | 63.7977 | 1403.55 | 0.004287 | 6.7197e-05 | 2015-02-24 | C | 0.004287 | 6.7197e-05 | 2015 | 2015-02-24 | C | 22 | 0.004287 | 6.7197e-05
1 | 3904615 | 2015-02-24 12:00 | 2015-02-24 13:20 | 80 | 1 | 80 | 0.00024467 | 3.0584e-06 | Restore Supply on Device T1258 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1258 | Replace transformer T1258 W/O 10156526. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 77 | 0.00023519 | 3.0544e-06 | 2015-02-24 | C | 0.00023519 | 3.054e-06 | 2015 | 2015-02-24 | C | 1 | 0.00023519 | 3.0544e-06
1 | 3905249 | 2015-02-24 20:46 | 2015-02-24 23:13 | 147.6333 | 4 | 152.0833 | 0.00046514 | 1.2234e-05 | Restore Supply on Device TC4839 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP767 | Have experienced outages before. cust can see 2 fuses hanging from the power line 10:08pm another 1r request as x2 DDO fuses keep popping out and F/man wanting help with line patrol. 2 x HV fuses replaced at fuses FP767. Suspected bird strike. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 38.0208 | 35.0208 | 140.0833 | 0.00042787 | 1.2218e-05 | 2015-02-24 | C | 0.00042787 | 1.2218e-05 | 2015 | 2015-02-24 | C | 4 | 0.00042787 | 1.2218e-05
1 | 3905872 | 2015-02-25 06:15 | 2015-02-25 08:04 | 109.8167 | 66 | 6975.3333 | 0.021334 | 0.00020186 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3901996 | at 06:14 Te Maunga Sub, CB 6 Sandhurt Feeder, Tripped, Ph A Fault, Ph B Fault, O/C INST, O/C INVT, L/O. Loss of Supply to Te Maunga Depot & Tenix Service Hub. Backup Generator did not come online for the service hub. Faultmen dispatched & investigation be | F3 | SANDHURST | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 105.6869 | 102.6869 | 6777.3333 | 0.020701 | 0.00020159 | 2015-02-25 | C | 0.020701 | 0.00020159 | 2015 | 2015-02-25 | C | 66 | 0.020701 | 0.00020159
1 | 3906010 | 2015-02-25 06:57 | 2015-02-25 08:05 | 67.85 | 1 | 67.85 | 0.00020751 | 3.0584e-06 | Restore Supply on Device X1165 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1165 | check if OMS 3906208, 3906246 is related. 2x 15amp hv fuses. 1x dropout candle unknown. Full power restored nothing else repaired or replaced. Adjacent assets - ok This also affected properties of Tx's X1576, X2999 & X2618 | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 67.85 | 64.85 | 64.85 | 0.00019808 | 3.0544e-06 | 2015-02-25 | C | 0.00019808 | 3.054e-06 | 2015 | 2015-02-25 | C | 1 | 0.00019808 | 3.0544e-06
1 | 3797952 | 2015-02-25 08:42 | 2015-02-25 12:25 | 222.75 | 2 | 445.5 | 0.0013625 | 6.1168e-06 | NAPA ID:05663 TP_MASTERTON GXP > AWATOITOI SUB > ROROKOKO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 833896 | Replace 11kv/33kv pole 833896. | F5 | ROROKOKO | AWATOITOI SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 222.75 | 219.75 | 439.5 | 0.0013424 | 6.1088e-06 | 2015-02-25 | B | 0.00067121 | 3.054e-06 | 2015 | 2015-02-25 | B | 2 | 0.0013424 | 6.1088e-06
1 | 3799012 | 2015-02-25 09:00 | 2015-02-25 15:12 | 371.8167 | 4 | 1487.2667 | 0.0045487 | 1.2234e-05 | NAPA ID:03824 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/265 | Run new AL conductor from Temp DDos #42 trrough to transformer T1/265 | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 371.8167 | 368.8167 | 1475.2667 | 0.0045061 | 1.2218e-05 | 2015-02-25 | B | 0.002253 | 6.109e-06 | 2015 | 2015-02-25 | B | 4 | 0.0045061 | 1.2218e-05
1 | 3806261 | 2015-02-25 09:09 | 2015-02-25 13:31 | 261.8333 | 7 | 1832.8333 | 0.0056056 | 2.1409e-05 | NAPA ID:05530 TP_TE MATAI GXP > PONGAKAWA SUB > OLD COACH RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-161 | To replace fuses SF6-161 with a fused ABS. Work Location: 232 Old Coach Road, Te Puke. Work Order 10146569 | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 261.8333 | 258.8333 | 1811.8333 | 0.0055341 | 2.1381e-05 | 2015-02-25 | B | 0.0027671 | 1.069e-05 | 2015 | 2015-02-25 | B | 7 | 0.0055341 | 2.1381e-05
1 | 3768319 | 2015-02-25 09:30 | 2015-02-25 13:05 | 215 | 91 | 19565 | 0.059838 | 0.00027832 | NAPA ID:05947 TP_PIAKO GXP > PIAKO SUB > MVILLE NORTH | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6142 | Replace Transformer TC6142 and install streetlight box next to transformer. Works location: Maple Place Morrinsville. WO 10148203. | F3 | MVILLE NORTH | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 215 | 212 | 19292 | 0.058926 | 0.00027795 | 2015-02-25 | B | 0.029463 | 0.00013898 | 2015 | 2015-02-25 | B | 91 | 0.058926 | 0.00027795
1 | 3773791 | 2015-02-25 09:34 | 2015-02-25 16:06 | 392 | 95 | 36875 | 0.11278 | 0.00029055 | NAPA ID:06642 TP_OPUNAKE GXP > TASMAN SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 713896 | Replace wire on Whitcombe Road between poles 713896 & 356910. Works location: Whitcombe Road. WO 10162610 | F3 | OPUNAKE | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 388.1579 | 385.1579 | 36590 | 0.11176 | 0.00029017 | 2015-02-25 | B | 0.055881 | 0.00014509 | 2015 | 2015-02-25 | B | 95 | 0.11176 | 0.00029017
1 | 3806007 | 2015-02-25 09:35 | 2015-02-25 15:50 | 375.1833 | 27 | 10129.95 | 0.030982 | 8.2577e-05 | NAPA ID:06759 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209319 | Replace poles and conductors. 11kV and 33kV. Work Location: Esdaile Road. Work Order 10146566. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 375.1833 | 372.1833 | 10048.95 | 0.030694 | 8.2469e-05 | 2015-02-25 | B | 0.015347 | 4.1235e-05 | 2015 | 2015-02-25 | B | 27 | 0.030694 | 8.2469e-05
1 | 3909733 | 2015-02-25 10:45 | 2015-02-25 12:47 | 121.25 | 1 | 121.25 | 0.00037083 | 3.0584e-06 | Restore Supply on Device T699 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Tx 699 | Also known as Te Whiti Road. 2x 10amp hv fuses. Link 7644. Tx 699. Bird Strike Full power restored. Nothing else repaired or replaced. adjacent assets - ok | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 121.25 | 118.25 | 118.25 | 0.00036119 | 3.0544e-06 | 2015-02-25 | C | 0.00036119 | 3.054e-06 | 2015 | 2015-02-25 | C | 1 | 0.00036119 | 3.0544e-06
1 | 3911200 | 2015-02-25 22:10 | 2015-02-25 23:04 | 53.8667 | 1 | 53.8667 | 0.00016475 | 3.0584e-06 | Restore Supply on Device TC2-010 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | ABS SC2-043 | Insulator is burning red outside on pole. 10:12pm advised Leanne at the Hub. Fault Indicator flashing at ABS SC2-043. FM to see techs in morning about flash sequence | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 53.8667 | 50.8667 | 50.8667 | 0.00015537 | 3.0544e-06 | 2015-02-25 | C | 0.00015537 | 3.054e-06 | 2015 | 2015-02-25 | C | 1 | 0.00015537 | 3.0544e-06
1 | 3911222 | 2015-02-25 23:13 | 2015-02-26 02:03 | 169.9667 | 258 | 15106.1667 | 0.046201 | 0.00078907 | Restore Supply on Device H131 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P01625 | CB H131 ARC & Tripped C phase O/C & E/F during sectionalising and patrol found an opossum on pole P01625 and removed using fuse sticks. | F2 | LINTON | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 58.551 | 55.551 | 14332.1667 | 0.043777 | 0.00078804 | 2015-02-25 | C | 0.043777 | 0.00078804 | 2015 | 2015-02-25 | C | 258 | 0.043777 | 0.00078804
1 | 3911983 | 2015-02-26 06:34 | 2015-02-26 08:22 | 107.6333 | 1 | 107.6333 | 0.00032919 | 3.0584e-06 | Restore Supply on Device 5068T | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8991 | 8991. Replaced 2x 10a HV fuse links due to possible bird strike . Nothing else repaired or replaced, adjacent assets up to Powerco standard. | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 107.6333 | 104.6333 | 104.6333 | 0.00031959 | 3.0544e-06 | 2015-02-26 | C | 0.00031959 | 3.054e-06 | 2015 | 2015-02-26 | C | 1 | 0.00031959 | 3.0544e-06
1 | 3912706 | 2015-02-26 08:01 | 2015-02-26 08:15 | 14 | 1 | 14 | 4.2818e-05 | 3.0584e-06 | Restore Supply on Device 8991 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8991 | suspect bird strike 2 x 10 amp fuses replaced | F4 | MOUNTAIN RD | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 14 | 11 | 11 | 3.3599e-05 | 3.0544e-06 | 2015-02-26 | C | 3.3599e-05 | 3.054e-06 | 2015 | 2015-02-26 | C | 1 | 3.3599e-05 | 3.0544e-06
1 | 3705372 | 2015-02-26 08:41 | 2015-02-26 14:50 | 369.4667 | 125 | 46183.3333 | 0.14125 | 0.0003823 | NAPA ID:06084 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8247 | Replace various network poles in work area. Works location: Fitzroy Rd. WO 30002060 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 369.4667 | 366.4667 | 45808.3333 | 0.13992 | 0.0003818 | 2015-02-26 | B | 0.069959 | 0.0001909 | 2015 | 2015-02-26 | B | 125 | 0.13992 | 0.0003818
1 | 3630871 | 2015-02-26 09:39 | 2015-02-26 15:15 | 336.05 | 17 | 5712.85 | 0.017472 | 5.1993e-05 | NAPA ID:05588 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole M1177 | To replace 11kV conductor between Poles M1177 and M1200. Works location: Waotu Rd WO 10134042 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 336.05 | 333.05 | 5661.85 | 0.017294 | 5.1925e-05 | 2015-02-26 | B | 0.0086468 | 2.5963e-05 | 2015 | 2015-02-26 | B | 17 | 0.017294 | 5.1925e-05
1 | 3913823 | 2015-02-26 12:55 | 2015-02-26 13:48 | 53.4 | 1 | 53.4 | 0.00016332 | 3.0584e-06 | Restore Supply on Device T6/442 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | T6-442 | 12.57pm - advise smc. transformer doors open T6-442, no sign of forced entry and no damage to doors. | F2 | RANGITIKEI | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 53.4 | 50.4 | 50.4 | 0.00015394 | 3.0544e-06 | 2015-02-26 | C | 0.00015394 | 3.054e-06 | 2015 | 2015-02-26 | C | 1 | 0.00015394 | 3.0544e-06
1 | 3915612 | 2015-02-27 00:57 | 2015-02-27 02:34 | 96.35 | 70 | 2074.35 | 0.0063442 | 0.00021409 | Restore Supply on Device T7/585 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P15588 Transformer T7/585 | Repaired Jumper at Pole P15588 transformer T7/585. Left like this for high load on Sunday night. | F2 | PAHIATUA | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 29.6336 | 26.6336 | 1864.35 | 0.0056945 | 0.00021381 | 2015-02-27 | C | 0.0056945 | 0.00021381 | 2015 | 2015-02-27 | C | 70 | 0.0056945 | 0.00021381
1 | 3916116 | 2015-02-27 07:01 | 2015-02-27 10:37 | 215.95 | 1 | 215.95 | 0.00066047 | 3.0584e-06 | Restore Supply on Device TC3-139 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tc31/139 | replaced hv ddo 3amp tc 3/139 due to lightning NOTHING ELSE REPAIRED OR REPLACED AT SITE ADJACENT ASSET UP TO POWERCO STANDARD | F4/F5 | MATAKANA RD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 215.95 | 212.95 | 212.95 | 0.00065044 | 3.0544e-06 | 2015-02-27 | C | 0.00065044 | 3.054e-06 | 2015 | 2015-02-27 | C | 1 | 0.00065044 | 3.0544e-06
1 | 3773846 | 2015-02-27 09:23 | 2015-02-27 16:18 | 415 | 42 | 17430 | 0.053308 | 0.00012845 | NAPA ID:06609 TP_OPUNAKE GXP > TASMAN SUB > OPUNAKE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 713907 | replacing poles. Works location: Ihaia Rd. WO 10162610 | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 415 | 412 | 17304 | 0.052854 | 0.00012829 | 2015-02-27 | B | 0.026427 | 6.4143e-05 | 2015 | 2015-02-27 | B | 42 | 0.052854 | 0.00012829
1 | 3916884 | 2015-02-27 16:41 | 2015-02-27 17:26 | 45.05 | 1 | 45.05 | 0.00013778 | 3.0584e-06 | Restore Supply on Device TC498 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tc498 | *** check if # 1078 is also affected - oms 3916894 and oms 3916913, 3916906, 3916910 are also part of this outage *** tc498. replace 3 amp ht fuse. cause: lightning. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are che | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 45.05 | 42.05 | 42.05 | 0.00012844 | 3.0544e-06 | 2015-02-27 | C | 0.00012844 | 3.054e-06 | 2015 | 2015-02-27 | C | 1 | 0.00012844 | 3.0544e-06
1 | 3916995 | 2015-02-27 17:02 | 2015-02-27 19:10 | 128.3667 | 4 | 513.4667 | 0.0015704 | 1.2234e-05 | Restore Supply on Device TC2056 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC2056 | 2 X fuses found blown at transformer TC 2056. Cause: Lightning - Used two 3amp Fuses. Marty Keenan attended. | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 128.3667 | 125.3667 | 501.4667 | 0.0015317 | 1.2218e-05 | 2015-02-27 | C | 0.0015317 | 1.2218e-05 | 2015 | 2015-02-27 | C | 4 | 0.0015317 | 1.2218e-05
1 | 3916913 | 2015-02-27 17:04 | 2015-02-27 18:51 | 107.1 | 1 | 107.1 | 0.00032756 | 3.0584e-06 | Restore Supply on Device TC4191 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tc4191 | possibly part of oms 3916884 repalce 1 x 3 amp ht fuse. 1 out of 3 phases. tc4191. cause: lightning. | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 107.1 | 104.1 | 104.1 | 0.00031797 | 3.0544e-06 | 2015-02-27 | C | 0.00031797 | 3.054e-06 | 2015 | 2015-02-27 | C | 1 | 0.00031797 | 3.0544e-06
1 | 3916981 | 2015-02-27 17:53 | 2015-02-28 14:43 | 1250.2833 | 7 | 8577.6833 | 0.026234 | 2.1409e-05 | Restore Supply on Device TP1110 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TP1109 | Transformer TP1109 Replaced due to Lightning Strike. | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 1225.3833 | 1222.3833 | 8556.6833 | 0.026136 | 2.1381e-05 | 2015-02-27 | C | 0.026136 | 2.1381e-05 | 2015 | 2015-02-27 | C | 7 | 0.026136 | 2.1381e-05
1 | 3917075 | 2015-02-27 21:40 | 2015-02-27 23:54 | 133.4833 | 13 | 382.4 | 0.0011695 | 3.9759e-05 | Restore Supply on Device T2/378 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | Fuses B50 | heard a bang after the power went out *pole fuse* Check to see if OMS 3917081 is related 1658 B State highway 56 / 51 Hamilton line Replaced 2X 10 Amp Fuses Bird Strike. | F4/F5 | BAINESSE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 29.4154 | 26.4154 | 343.4 | 0.0010489 | 3.9708e-05 | 2015-02-27 | C | 0.0010489 | 3.9708e-05 | 2015 | 2015-02-27 | C | 13 | 0.0010489 | 3.9708e-05
1 | 3815953 | 2015-02-28 05:00 | 2015-02-28 06:28 | 88 | 2 | 176 | 0.00053828 | 6.1168e-06 | NAPA ID:06565 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 6 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV G56 | 3 yearly Maint on Switchgear & Tx. Works location: Main St Palmerston North WO 10142830 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 88 | 85 | 170 | 0.00051925 | 6.1088e-06 | 2015-02-28 | B | 0.00025963 | 3.054e-06 | 2015 | 2015-02-28 | B | 2 | 0.00051925 | 6.1088e-06
1 | 3917779 | 2015-02-28 07:08 | 2015-02-28 16:31 | 562.55 | 331 | 42773.4 | 0.13082 | 0.0010123 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M0012 | CB 5 Trip. E/F. Car V Pole MOO12. Feeder originally Autoreclosed but was opened by NOC for Safety Reasons. NDR # 34192. 1 X Pole. 3 X HV Arms. 3 X LV Arms. 3 X DDO's Complete. 3 Polymer Insulators. 4 X 11kV Insulators. 4 X LV Insulators used. Josh Reid an | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 129.2248 | 126.2248 | 41780.4 | 0.12762 | 0.001011 | 2015-02-28 | C | 0.12762 | 0.001011 | 2015 | 2015-02-28 | C | 331 | 0.12762 | 0.001011
1 | 3915584 | 2015-02-28 09:00 | 2015-02-28 15:00 | 359.5167 | 23 | 8268.8833 | 0.02529 | 7.0344e-05 | NAPA ID:05335 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > STANLEY AVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C3207, C3203 | To Replace poles C3207 & C3203. This OMS Parent ID replaces OMS Parent ID 3744907. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 359.5167 | 356.5167 | 8199.8833 | 0.025046 | 7.0252e-05 | 2015-02-28 | B | 0.012523 | 3.5126e-05 | 2015 | 2015-02-28 | B | 23 | 0.025046 | 7.0252e-05
1 | 3919065 | 2015-03-01 03:45 | 2015-03-01 05:14 | 88.8833 | 2 | 177.7667 | 0.00054369 | 6.1168e-06 | Restore Supply on Device 2911 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 2911 | Fuses 2911 tripped. Patrolled and no fault found. Suspect bird strike. 2 x 10A fuses links and holders replaced. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 88.8833 | 85.8833 | 171.7667 | 0.00052465 | 6.1088e-06 | 2015-03-01 | C | 0.00052465 | 6.109e-06 | 2015 | 2015-03-01 | C | 2 | 0.00052465 | 6.1088e-06
1 | 3856612 | 2015-03-01 05:02 | 2015-03-01 06:51 | 108.8167 | 27 | 2938.05 | 0.0089858 | 8.2577e-05 | NAPA ID:06583 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 12 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Transformer G225 | 3 yearly Maint on Switchgear & Tx. Work location: Dittmer Dr Palmerston North. WO 10142830 | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 108.8167 | 105.8167 | 2857.05 | 0.0087266 | 8.2469e-05 | 2015-03-01 | B | 0.0043633 | 4.1235e-05 | 2015 | 2015-03-01 | B | 27 | 0.0087266 | 8.2469e-05
1 | 3920767 | 2015-03-01 16:37 | 2015-03-01 18:23 | 106 | 676 | 47382 | 0.14491 | 0.0020675 | Restore Supply on Device S61 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 1 | CB S61 tripped on E/F. Sectionalised and found NO fault. Jade Williams Attended. | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 70.0917 | 67.0917 | 45354 | 0.13853 | 0.0020648 | 2015-03-01 | C | 0.13853 | 0.0020648 | 2015 | 2015-03-01 | C | 676 | 0.13853 | 0.0020648
1 | 3922395 | 2015-03-01 19:12 | 2015-03-01 19:26 | 13.7833 | 11270 | 137361.9333 | 0.42011 | 0.034468 | Restore Supply on Device 1092 | 66000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB1092 | CB 1092 at Kopu Tripped E/F. L/O. Note, Transpower confirmed the CB did not attempt to an Auto reclose, it went straight to lockout. Line Patrol Required on Monday. M Pratt and A Wilson agreed to the use of conducting a Helipatrol of the lines to speed th | F1, F2, F3 | KOPU1092-KAUAERANGA 66KV | TP_KOPU | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 12.1883 | 9.1883 | 103551.9333 | 0.31629 | 0.034423 | 2015-03-01 | C | 0.31629 | 0.034423 | 2015 | 2015-03-01 | C | 11270 | 0.31629 | 0.034423
1 | 3934787 | 2015-03-01 22:56 | 2015-03-01 23:52 | 56 | 3007 | 166675 | 0.50976 | 0.0091967 | Restore Supply on Device X60 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | X60 Feilding to Sanson 33kV | CB X60, Trip, E/F. Partial Patrol nothing found. Relivened ok. Full patrol to be carried out tomorrow in daylight hours under this job number. Line patrol complete and no apparent cause found . | F1, F2, F3 | FEILDING-SANSON 33KV | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55.429 | 52.429 | 157654 | 0.48154 | 0.0091847 | 2015-03-01 | C | 0.48154 | 0.0091847 | 2015 | 2015-03-01 | C | 3007 | 0.48154 | 0.0091847
1 | 3915550 | 2015-03-02 09:03 | 2015-03-02 15:02 | 358.95 | 29 | 10409.55 | 0.031837 | 8.8694e-05 | NAPA ID:05564 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 205455, TC2-156 | To replace pole 205455 and associated equipment including the transformer. This OMS Parent ID replaces OMS Parent ID 3856472. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 358.95 | 355.95 | 10322.55 | 0.031529 | 8.8578e-05 | 2015-03-02 | B | 0.015765 | 4.4289e-05 | 2015 | 2015-03-02 | B | 29 | 0.031529 | 8.8578e-05
1 | 3939242 | 2015-03-02 11:02 | 2015-03-02 14:07 | 185 | 88 | 5280 | 0.016148 | 0.00026914 | Restore Supply on Device 2112T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 730272 | 11:35am power is not on Reported lines down at 1829 Eltham Rd. Found lines down so islated between ABS 5968 & 5977, Backfeed rest of area via ABS 5960. Repaired lines and re livened NDR 43423. Cause of fault was hedge cutter flicking barb wire into 11kV. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 60 | 57 | 5016 | 0.015321 | 0.00026879 | 2015-03-02 | C | 0.015321 | 0.00026879 | 2015 | 2015-03-02 | C | 88 | 0.015321 | 0.00026879
1 | 3939558 | 2015-03-02 14:20 | 2015-03-02 15:32 | 72.4167 | 1 | 72.4167 | 0.00022148 | 3.0584e-06 | Restore Supply on Device X2500 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4709 | Replaced 2X 3a HV Fuses | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 72.4167 | 69.4167 | 69.4167 | 0.00021203 | 3.0544e-06 | 2015-03-02 | C | 0.00021203 | 3.054e-06 | 2015 | 2015-03-02 | C | 1 | 0.00021203 | 3.0544e-06
1 | 3940007 | 2015-03-02 17:52 | 2015-03-02 23:47 | 354.9667 | 118 | 20331.6333 | 0.062183 | 0.00036089 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2800T | Recloser 8763/2 tripped on E/F flags, line was patrolled and sectionalised and a blown transformer 2800T was found transformer was isolated and supply restored. Faultman informed control room that this transformer had been replaced last year he thinks ar | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 172.302 | 169.302 | 19977.6333 | 0.06102 | 0.00036042 | 2015-03-02 | C | 0.06102 | 0.00036042 | 2015 | 2015-03-02 | C | 118 | 0.06102 | 0.00036042
1 | 3856574 | 2015-03-02 19:30 | 2015-03-02 23:25 | 235 | 17 | 3995 | 0.012218 | 5.1993e-05 | NAPA ID:06817 TP_MASTERTON GXP > CHAPEL SUB > HEAD OFFICE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2575 | Replace 400v Lv cabinet supplied by T2575. Works location: Russell St Masterton. WO 10157264 | F2 | HEAD OFFICE | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 235 | 232 | 3944 | 0.012047 | 5.1925e-05 | 2015-03-02 | B | 0.0060233 | 2.5963e-05 | 2015 | 2015-03-02 | B | 17 | 0.012047 | 5.1925e-05
1 | 3941018 | 2015-03-03 06:57 | 2015-03-03 11:36 | 278.6833 | 2 | 479.4667 | 0.0014664 | 6.1168e-06 | Restore Supply on Device 3265T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 14 MAKARA ROAD | related to OMS 3940886- refer to here for job closures | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 239.7333 | 236.7333 | 473.4667 | 0.0014462 | 6.1088e-06 | 2015-03-03 | C | 0.0014462 | 6.109e-06 | 2015 | 2015-03-03 | C | 2 | 0.0014462 | 6.1088e-06
1 | 3939227 | 2015-03-03 08:15 | 2015-03-03 17:19 | 544 | 137 | 70042.5 | 0.21422 | 0.000419 | NAPA ID:07487 TP_OPUNAKE GXP > TASMAN SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA206 | Replace poles and wire on Ihaia Road. Works location: Ihaia Rd. WO 10162610. | F3 | OPUNAKE | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 511.2591 | 508.2591 | 69631.5 | 0.21268 | 0.00041846 | 2015-03-03 | B | 0.10634 | 0.00020923 | 2015 | 2015-03-03 | B | 137 | 0.21268 | 0.00041846
1 | 3856388 | 2015-03-03 08:30 | 2015-03-03 14:27 | 357 | 17 | 6069 | 0.018562 | 5.1993e-05 | NAPA ID:06155 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC1078 | Replace poles & x-arms between IC1078 & pole F0865. Works location: Old Te Aroha Rd. WO 10163038 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 357 | 354 | 6018 | 0.018382 | 5.1925e-05 | 2015-03-03 | B | 0.0091908 | 2.5963e-05 | 2015 | 2015-03-03 | B | 17 | 0.018382 | 5.1925e-05
1 | 3909812 | 2015-03-03 08:45 | 2015-03-03 15:44 | 418.7167 | 27 | 11305.35 | 0.034577 | 8.2577e-05 | NAPA ID:06780 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS Temp 68 | Replace 11kV poles, crossarms and conductors. | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 418.7167 | 415.7167 | 11224.35 | 0.034284 | 8.2469e-05 | 2015-03-03 | B | 0.017142 | 4.1235e-05 | 2015 | 2015-03-03 | B | 27 | 0.034284 | 8.2469e-05
1 | 3915575 | 2015-03-03 08:45 | 2015-03-03 15:10 | 385 | 2 | 770 | 0.002355 | 6.1168e-06 | NAPA ID:05602 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9307/2, 9308/2 | To replace 11kV poles and cross arms in preparation for conductor upgrade. This OMS Parent ID supersedes 3634280. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 385 | 382 | 764 | 0.0023336 | 6.1088e-06 | 2015-03-03 | B | 0.0011668 | 3.054e-06 | 2015 | 2015-03-03 | B | 2 | 0.0023336 | 6.1088e-06
1 | 3822285 | 2015-03-03 09:04 | 2015-03-03 15:18 | 374 | 63 | 23562 | 0.072063 | 0.00019268 | NAPA ID:05965 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 756097 | First we have to do liveline break on pole 756097. This will be situated on the seaward side of CB7 cable feed so power will stay on to the rest of wairau rd. The pole we change is pole 843309 this also has ABS 6584 on it. Second we are changing ABS 37 so | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 374 | 371 | 23373 | 0.071391 | 0.00019243 | 2015-03-03 | B | 0.035696 | 9.6214e-05 | 2015 | 2015-03-03 | B | 63 | 0.071391 | 0.00019243
1 | 3798966 | 2015-03-03 09:10 | 2015-03-03 15:54 | 404.65 | 46 | 18613.9 | 0.056929 | 0.00014069 | NAPA ID:05927 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC1220 | To replace 11kV and LV cross arms Chepmell Road Morrinsville. Works location: Chapmell Rd Kiwitahi. WO 30000212 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 404.65 | 401.65 | 18475.9 | 0.056433 | 0.0001405 | 2015-03-03 | B | 0.028217 | 7.0252e-05 | 2015 | 2015-03-03 | B | 46 | 0.056433 | 0.0001405
1 | 3916207 | 2015-03-03 09:29 | 2015-03-03 15:38 | 369.0167 | 116 | 42584.9333 | 0.13024 | 0.00035478 | NAPA ID:06444 TP_KAITIMAKO GXP > WELCOME BAY SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP35 | REPLACE POLE AND RECONDUCTOR HV FEEDER. Work Location: Waitaha Road, Kaitimako. Note: Generator in service on TD4-748 prior to fuses being opened. | F3 | VICTORY STREET | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 367.1115 | 364.1115 | 42236.9333 | 0.12901 | 0.00035431 | 2015-03-03 | B | 0.064505 | 0.00017716 | 2015 | 2015-03-03 | B | 116 | 0.12901 | 0.00035431
1 | 3941385 | 2015-03-03 10:20 | 2015-03-03 10:25 | 5.2167 | 185 | 965.0833 | 0.0029516 | 0.00056581 | Restore Supply on Device TC3755 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 861235 | 9.00am called through to svs hub. Fm opening fuses to remove dead sea gull. Isolation at fuses FC2284 to remove dead seagull from pole 861235. Seagull removed by hotstick. | F3 | OTAHU RD | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 5.2167 | 2.2167 | 410.0833 | 0.0012526 | 0.00056507 | 2015-03-03 | C | 0.0012526 | 0.00056507 | 2015 | 2015-03-03 | C | 185 | 0.0012526 | 0.00056507
1 | 3856610 | 2015-03-03 10:28 | 2015-03-03 11:48 | 79.65 | 86 | 6849.9 | 0.02095 | 0.00026302 | NAPA ID:06581 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 12 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | 11kV Transformer G227 | 3 yearly Maint on Switchgear & Tx. Works location: Wikiriwhi Crescent Palmerston North WO 10142830 | F3 | PASCAL ST 6 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 79.65 | 76.65 | 6591.9 | 0.020134 | 0.00026268 | 2015-03-03 | B | 0.010067 | 0.00013134 | 2015 | 2015-03-03 | B | 86 | 0.020134 | 0.00026268
1 | 3875360 | 2015-03-04 06:50 | 2015-03-04 17:10 | 620 | 16 | 304 | 0.00092976 | 4.8935e-05 | NAPA ID:06680 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB8 Moawhango | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 19 | 16 | 256 | 0.00078193 | 4.8871e-05 | 2015-03-04 | B | 0.00039097 | 2.4435e-05 | 2015 | 2015-03-04 | B | 16 | 0.00078193 | 4.8871e-05
1 | 3869219 | 2015-03-04 09:08 | 2015-03-04 10:35 | 87 | 7 | 609 | 0.0018626 | 2.1409e-05 | NAPA ID:06330 TP_TAURANGA 33 GXP > KATIKATI SUB > TETLEY ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TB2-028 | Replace DDO cross arm and DDO's Isolating transformer because it is to dangerous to replace DDO's with transformer Live. | F3 | TETLEY ROAD | KATIKATI SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 87 | 84 | 588 | 0.001796 | 2.1381e-05 | 2015-03-04 | B | 0.000898 | 1.069e-05 | 2015 | 2015-03-04 | B | 7 | 0.001796 | 2.1381e-05
1 | 3944025 | 2015-03-04 09:15 | 2015-03-04 09:40 | 25.4333 | 4 | 101.7333 | 0.00031114 | 1.2234e-05 | Restore Supply on Device TC3646 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P13584 | Go to 53 - 55 Old Tauranga Road fuses hanging down. Duck through lines blown 2xfuses at FC2403. Duck at pole P13584. 2 x 6amp HV Fuses. Wayne Seath Attended. | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 25.4333 | 22.4333 | 89.7333 | 0.00027408 | 1.2218e-05 | 2015-03-04 | C | 0.00027408 | 1.2218e-05 | 2015 | 2015-03-04 | C | 4 | 0.00027408 | 1.2218e-05
1 | 3942217 | 2015-03-04 09:15 | 2015-03-04 14:57 | 341.5833 | 15 | 5123.75 | 0.015671 | 4.5876e-05 | NAPA ID:06818 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP768 | Replace 11kv X-arms @ various sites. Works location: Rawerawe West Rd, Ngatea. WO 30000324 | F3/F4 | NGATEA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 341.5833 | 338.5833 | 5078.75 | 0.015513 | 4.5816e-05 | 2015-03-04 | B | 0.0077563 | 2.2908e-05 | 2015 | 2015-03-04 | B | 15 | 0.015513 | 4.5816e-05
1 | 3869239 | 2015-03-04 10:05 | 2015-03-04 15:23 | 317.1167 | 10 | 3171.1667 | 0.0096988 | 3.0584e-05 | NAPA ID:06211 TP_KAITIMAKO GXP > WELCOME BAY SUB > OHAUITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TE4-039 | Replace TX Pole TE4-039. Works location: Rowe Rd, Tauranga. WO 10162630. | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 317.1167 | 314.1167 | 3141.1667 | 0.0095945 | 3.0544e-05 | 2015-03-04 | B | 0.0047972 | 1.5272e-05 | 2015 | 2015-03-04 | B | 10 | 0.0095945 | 3.0544e-05
1 | 3945220 | 2015-03-04 12:56 | 2015-03-04 13:08 | 12 | 5 | 160.2167 | 0.00049001 | 1.5292e-05 | Restore Supply on Device V64 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V64 | Two Fuses found blown at Fuses V64 - No Fault found - Used 2X 6 amp HV fuses. Trevor Pocock attended. | F5 | COAST ROAD | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 32.0433 | 29.0433 | 145.2167 | 0.00044355 | 1.5272e-05 | 2015-03-04 | C | 0.00044355 | 1.5272e-05 | 2015 | 2015-03-04 | C | 5 | 0.00044355 | 1.5272e-05
1 | 3945261 | 2015-03-04 14:05 | 2015-03-04 18:13 | 248.1333 | 1 | 248.1333 | 0.0007589 | 3.0584e-06 | Restore Supply on Device TC4255 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4255 | replaced TX and F/man forgot to seek permission to replace TX - 3 phase 30KVA - W12898 cause was due to deterioration. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F4 | COROGLEN | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 248.1333 | 245.1333 | 245.1333 | 0.00074874 | 3.0544e-06 | 2015-03-04 | C | 0.00074874 | 3.054e-06 | 2015 | 2015-03-04 | C | 1 | 0.00074874 | 3.0544e-06
1 | 3945393 | 2015-03-04 17:07 | 2015-03-04 19:31 | 144.2833 | 420 | 20289.8 | 0.062055 | 0.0012845 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | K1103 | lines down at 60 Cameron Road, Morrinsville. Harvesting machine brought lines down, lying in the paddock. TAH CB2 tripped E/F, A, B & C Ph O/C, L/O. Isolation at ABS 580 with remainder of feeder returned to service. Conductor x 2 Phases between Poles K110 | F4 | MANGATEPARU | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 48.309 | 45.309 | 19029.8 | 0.058125 | 0.0012829 | 2015-03-04 | C | 0.058125 | 0.0012829 | 2015 | 2015-03-04 | C | 420 | 0.058125 | 0.0012829
1 | 3875362 | 2015-03-05 07:00 | 2015-03-05 16:58 | 598 | 16 | 160 | 0.00048935 | 4.8935e-05 | NAPA ID:06681 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 112 | 0.0003421 | 4.8871e-05 | 2015-03-05 | B | 0.00017105 | 2.4435e-05 | 2015 | 2015-03-05 | B | 16 | 0.0003421 | 4.8871e-05
1 | 3946669 | 2015-03-05 08:25 | 2015-03-05 11:09 | 163.85 | 1 | 163.85 | 0.00050112 | 3.0584e-06 | Restore Supply on Device T9/293 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | v83 | replace 10 amp ht fuse at fuse # v83. cause: possible bird strike. 1 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 163.85 | 160.85 | 160.85 | 0.0004913 | 3.0544e-06 | 2015-03-05 | C | 0.0004913 | 3.054e-06 | 2015 | 2015-03-05 | C | 1 | 0.0004913 | 3.0544e-06
1 | 3876356 | 2015-03-05 08:30 | 2015-03-05 14:10 | 339.7 | 72 | 24458.4 | 0.074804 | 0.00022021 | NAPA ID:06405 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 724752 | Replace three11kv poles 724752, 724724, 724650. Works location: Ngawhini Rd, Hawera. WO 10141791. | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 339.7 | 336.7 | 24242.4 | 0.074047 | 0.00021992 | 2015-03-05 | B | 0.037023 | 0.00010996 | 2015 | 2015-03-05 | B | 72 | 0.074047 | 0.00021992
1 | 3915580 | 2015-03-05 08:45 | 2015-03-05 15:08 | 383 | 11 | 4213 | 0.012885 | 3.3643e-05 | NAPA ID:05605 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9307/2, 9308/2 | To replace 11kV poles and cross arms in preparation for conductor replacement. OMS Parent ID 3634310 is replaced by this OMS Parent ID 3915580. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 383 | 380 | 4180 | 0.012767 | 3.3599e-05 | 2015-03-05 | B | 0.0063837 | 1.6799e-05 | 2015 | 2015-03-05 | B | 11 | 0.012767 | 3.3599e-05
1 | 3822100 | 2015-03-05 08:57 | 2015-03-05 13:58 | 301 | 29 | 8729 | 0.026697 | 8.8694e-05 | NAPA ID:06162 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 387396 | Replace x-arms between poles 387396 & F0835. Re-conductor between poles F12789 & F0835. Works location: Old Te Aroha Rd. WO 10163038. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 301 | 298 | 8642 | 0.026396 | 8.8578e-05 | 2015-03-05 | B | 0.013198 | 4.4289e-05 | 2015 | 2015-03-05 | B | 29 | 0.026396 | 8.8578e-05
1 | 3916382 | 2015-03-05 09:13 | 2015-03-05 15:12 | 359.1 | 131 | 47042.1 | 0.14387 | 0.00040065 | NAPA ID:07441 TP_KAITIMAKO GXP > WELCOME BAY SUB > KAITEMAKO RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 215486 | REPLACE POLES AND RECONDUCTOR HV FEEDER. INSTALL TEMP ABS 20 ON POLE 215486 FOR UP AND COMING SHUTDOWNS. Works location: Waitaha Rd. WO 10148368 | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 359.1 | 356.1 | 46649.1 | 0.14249 | 0.00040013 | 2015-03-05 | B | 0.071243 | 0.00020007 | 2015 | 2015-03-05 | B | 131 | 0.14249 | 0.00040013
1 | 3939573 | 2015-03-05 09:15 | 2015-03-05 13:20 | 245 | 29 | 7105 | 0.02173 | 8.8694e-05 | NAPA ID:05941 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 1220 | To replace 11kV poles and cross arms on Waterworks Road Te Miro between IC1220 and IC2605. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 245 | 242 | 7018 | 0.021436 | 8.8578e-05 | 2015-03-05 | B | 0.010718 | 4.4289e-05 | 2015 | 2015-03-05 | B | 29 | 0.021436 | 8.8578e-05
1 | 3939670 | 2015-03-05 09:17 | 2015-03-05 16:01 | 404.4333 | 20 | 8088.6667 | 0.024739 | 6.1168e-05 | NAPA ID:07418 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGAMAIRE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Scarborough Rd | Replace 11kv wire between temp fuses 51 ABS R43.Also installed Switch 10237, Replaced Transformer T7126 with Transformer 7297P and removed Temp ABS 50 | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 404.4333 | 401.4333 | 8028.6667 | 0.024523 | 6.1088e-05 | 2015-03-05 | B | 0.012261 | 3.0544e-05 | 2015 | 2015-03-05 | B | 20 | 0.024523 | 6.1088e-05
1 | 3822303 | 2015-03-05 09:30 | 2015-03-05 13:44 | 253.7667 | 45 | 11419.5 | 0.034926 | 0.00013763 | NAPA ID:05970 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ABS 535 | Pole replacements and crossarm changes. Works location: Wairau Rd. WO 10154759. | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 253.7667 | 250.7667 | 11284.5 | 0.034468 | 0.00013745 | 2015-03-05 | B | 0.017234 | 6.8725e-05 | 2015 | 2015-03-05 | B | 45 | 0.034468 | 0.00013745
1 | 3947842 | 2015-03-05 09:52 | 2015-03-05 12:17 | 144.5833 | 1 | 144.5833 | 0.0004422 | 3.0584e-06 | Restore Supply on Device X645 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 789957 | replace 6 amp ht fuse. pole 789957. cause: bird or possum. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 144.5833 | 141.5833 | 141.5833 | 0.00043246 | 3.0544e-06 | 2015-03-05 | C | 0.00043245 | 3.054e-06 | 2015 | 2015-03-05 | C | 1 | 0.00043246 | 3.0544e-06
1 | 3952539 | 2015-03-05 09:59 | 2015-03-06 13:13 | 1634.1 | 137 | 77424.25 | 0.2368 | 0.000419 | Restore Supply on Device Q31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735787 | Cardiff Q31 Auto Reclosed. ABC Phase No Flags. Momentary Loss of Supply. Line patrolled and floating conductor located at pole 735787. Bruce Kerr attended. | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 565.1405 | 562.1405 | 77013.25 | 0.23523 | 0.00041846 | 2015-03-05 | C | 0.23523 | 0.00041846 | 2015 | 2015-03-05 | C | 137 | 0.23523 | 0.00041846
1 | 3948657 | 2015-03-05 10:39 | 2015-03-05 12:09 | 90.4167 | 175 | 15822.9167 | 0.048393 | 0.00053522 | Restore Supply on Device T255 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 7417 | possibly part of 394852. CB 948 Found Tripped After A/R on RS 7417 (see OMS 3948431 Work Parties on CXAC's stood Down) No Fault found feeder relivened | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 90.4167 | 87.4167 | 15297.9167 | 0.046726 | 0.00053452 | 2015-03-05 | C | 0.046726 | 0.00053452 | 2015 | 2015-03-05 | C | 175 | 0.046726 | 0.00053452
1 | 3948558 | 2015-03-05 10:59 | 2015-03-05 13:50 | 171.1 | 1 | 171.1 | 0.0005233 | 3.0584e-06 | Restore Supply on Device T1596 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 798782 | x2 HV fuses 10amp fuse at pole 798782 cause unknown. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 171.1 | 168.1 | 168.1 | 0.00051345 | 3.0544e-06 | 2015-03-05 | C | 0.00051345 | 3.054e-06 | 2015 | 2015-03-05 | C | 1 | 0.00051345 | 3.0544e-06
1 | 3875314 | 2015-03-05 11:05 | 2015-03-05 11:38 | 33 | 65 | 2145 | 0.0065603 | 0.0001988 | NAPA ID:06687 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3802 | Need TC3802 Isolated / Earthed so Cable can be connected to Sourse B from IC3089. This Cable was disconnected from TC3802 so Cable Fault in same Cable could be located and Repaired. Chian Ho would like TC3802 Livened up to open IC3089 for a week before pu | F4 | OWERA RD | WHITIANGA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 33 | 30 | 1950 | 0.0059561 | 0.00019854 | 2015-03-05 | B | 0.0029781 | 9.9269e-05 | 2015 | 2015-03-05 | B | 65 | 0.0059561 | 0.00019854
1 | 3949230 | 2015-03-05 15:08 | 2015-03-05 16:32 | 83.8667 | 280 | 18903.25 | 0.057814 | 0.00085636 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | CB8 | Possible blown ring main unit. Marc Askin at site. | F2 | CLIFF RD | HAMILTON STREET SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 67.5116 | 64.5116 | 18063.25 | 0.055173 | 0.00085524 | 2015-03-05 | C | 0.055173 | 0.00085524 | 2015 | 2015-03-05 | C | 280 | 0.055173 | 0.00085524
1 | 3950181 | 2015-03-05 16:13 | 2015-03-05 17:04 | 50.95 | 1 | 50.95 | 0.00015583 | 3.0584e-06 | Restore Supply on Device TC3800 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | Tx TC3800 | f/man confirms that this has now been locked shut. No idea how this was opened. Tx TC3800 Adjacent assets - ok. | F3 | STANLEY AVE | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 50.95 | 47.95 | 47.95 | 0.00014646 | 3.0544e-06 | 2015-03-05 | C | 0.00014646 | 3.054e-06 | 2015 | 2015-03-05 | C | 1 | 0.00014646 | 3.0544e-06
1 | 3950231 | 2015-03-05 18:35 | 2015-03-05 22:45 | 250 | 4 | 1000 | 0.0030584 | 1.2234e-05 | Restore Supply on Device TE4-166 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer TE4-166 | Replace transformer due to holes in side of transformer. Issue own AP Materials 1x 15kVA 2 phase transformer, 2 x LV Fuse assemblies (Complete) | F3/F4 | OHAUITI RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 988 | 0.0030178 | 1.2218e-05 | 2015-03-05 | C | 0.0030178 | 1.2218e-05 | 2015 | 2015-03-05 | C | 4 | 0.0030178 | 1.2218e-05
1 | 3950287 | 2015-03-05 20:48 | 2015-03-05 22:12 | 83.9833 | 4 | 335.9333 | 0.0010274 | 1.2234e-05 | Restore Supply on Device TC4839 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP767 | Two HV Fuses Blown at FP767. Sugest transformers are logged as this has happened a couple pf times recently. Upgraded fuses to 10 Amp Fuses. LV is fused on the transformers & transformers are individually fused. Material 3x10Amp Fuses | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 83.9833 | 80.9833 | 323.9333 | 0.00098943 | 1.2218e-05 | 2015-03-05 | C | 0.00098943 | 1.2218e-05 | 2015 | 2015-03-05 | C | 4 | 0.00098943 | 1.2218e-05
1 | 3949191 | 2015-03-05 23:53 | 2015-03-06 01:56 | 122.1833 | 40 | 4887.3333 | 0.014948 | 0.00012234 | NAPA ID:07596 TP_BUNNYTHORPE GXP > SANSON SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P22110 & P22131 | Replacing broken insulators on poles P22110 & P22131 | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 122.1833 | 119.1833 | 4767.3333 | 0.014561 | 0.00012218 | 2015-03-05 | B | 0.0072807 | 6.1088e-05 | 2015 | 2015-03-05 | B | 40 | 0.014561 | 0.00012218
1 | 3951988 | 2015-03-06 07:02 | 2015-03-06 10:16 | 194.2333 | 18 | 1023.3667 | 0.0031299 | 5.5052e-05 | Restore Supply on Device V83 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P04557 | 2x HV Fuse Links. Goose hit lines. Trevor Pocock attended. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 56.8537 | 53.8537 | 969.3667 | 0.0029609 | 5.498e-05 | 2015-03-06 | C | 0.0029609 | 5.498e-05 | 2015 | 2015-03-06 | C | 18 | 0.0029609 | 5.498e-05
1 | 3951012 | 2015-03-06 08:37 | 2015-03-06 10:16 | 99.1 | 1 | 99.1 | 0.00030309 | 3.0584e-06 | Restore Supply on Device TC2122 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | TC2122 | check for safety- customer reporting that a stay wire has come off the pole, and its come off the supporter off the ground, dangling around the tx on the pole. pls attend for safety. Isolated transformer Removed stay wire from transformer, installed sta | F4 | STATION RD | BROWNE STREET SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 99.1 | 96.1 | 96.1 | 0.00029353 | 3.0544e-06 | 2015-03-06 | C | 0.00029353 | 3.054e-06 | 2015 | 2015-03-06 | C | 1 | 0.00029353 | 3.0544e-06
1 | 3879326 | 2015-03-06 08:45 | 2015-03-06 08:54 | 9.3333 | 101 | 942.6667 | 0.0028831 | 0.0003089 | NAPA ID:06075 TP_KINLEITH GXP > MARAETAI ROAD SUB > MOSSOPS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 380224 | Cut 11kV jumpers between underground cable termination and overhead line on pole 380224. Switching to be carried out to close switch IC1521 and open Links LC2078 prior to the issue of the live-line permit. Works location: Baberton St, Tokoroa. WO 101478 | F3 | CAMPBELL ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 9.3333 | 6.3333 | 639.6667 | 0.0019538 | 0.0003085 | 2015-03-06 | B | 0.00097691 | 0.00015425 | 2015 | 2015-03-06 | B | 101 | 0.0019538 | 0.0003085
1 | 3869323 | 2015-03-06 08:50 | 2015-03-06 15:24 | 393.75 | 57 | 22443.75 | 0.068642 | 0.00017433 | NAPA ID:06504 TP_MASTERTON GXP > AKURA SUB > EDITH ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 382607 | REPLACEMENT OF THREE RED TAG POLES T680 T2002 AND POLE 832607. Works location: Westbush Rd and Upper Manaia Rd. WO 30001163. | F3 | EDITH ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 393.75 | 390.75 | 22272.75 | 0.06803 | 0.0001741 | 2015-03-06 | B | 0.034015 | 8.7051e-05 | 2015 | 2015-03-06 | B | 57 | 0.06803 | 0.0001741
1 | 3950975 | 2015-03-06 09:07 | 2015-03-06 10:08 | 61 | 7 | 427 | 0.0013059 | 2.1409e-05 | Restore Supply on Device WH267 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725943 | Part power call received. Line patrolled and conductor found on ground at pole 725943. Line isolated beyond Fuses WH267 and repairs undertaken. Materials Used: 3 x 7061 Sleeves. Chris Katene attended, | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 61 | 58 | 406 | 0.0012401 | 2.1381e-05 | 2015-03-06 | C | 0.0012401 | 2.1381e-05 | 2015 | 2015-03-06 | C | 7 | 0.0012401 | 2.1381e-05
1 | 3951219 | 2015-03-06 09:13 | 2015-03-06 09:34 | 20.4167 | 281 | 5737.0833 | 0.017546 | 0.00085942 | Restore Supply on Device RC01 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | RC 01 | Gordon Recloser RC01 tripped. No Flags. Auto reclosed disabled and line patrolled. No cause of fault located. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 20.4167 | 17.4167 | 4894.0833 | 0.014949 | 0.00085829 | 2015-03-06 | C | 0.014949 | 0.00085829 | 2015 | 2015-03-06 | C | 281 | 0.014949 | 0.00085829
1 | 3951726 | 2015-03-06 09:35 | 2015-03-06 10:38 | 62.65 | 15 | 939.75 | 0.0028742 | 4.5876e-05 | Restore Supply on Device 5135 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5135 | Planned outage: 11kv lines and equipment reinstall structure earth wire to fused ABS 8923 pole 858918 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 62.65 | 59.65 | 894.75 | 0.0027329 | 4.5816e-05 | 2015-03-06 | C | 0.0027329 | 4.5816e-05 | 2015 | 2015-03-06 | C | 15 | 0.0027329 | 4.5816e-05
1 | 3950960 | 2015-03-06 09:55 | 2015-03-06 14:50 | 294.9 | 103 | 30374.7 | 0.092899 | 0.00031502 | NAPA ID:07617 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11000 | PLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | O3700 | Replace pole O3700 following car v pole. Work Location: 619 State Highway 25, Waitakaruru. Work Order 10183668. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 294.9 | 291.9 | 30065.7 | 0.091833 | 0.00031461 | 2015-03-06 | B | 0.045917 | 0.0001573 | 2015 | 2015-03-06 | B | 103 | 0.091833 | 0.00031461
1 | 3954257 | 2015-03-06 10:57 | 2015-03-06 13:34 | 157.1667 | 118 | 11391.1167 | 0.034839 | 0.00036089 | Restore Supply on Device 3265T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 3265T | 11.00am - couple of recloser on feeder, line patrol being done on OMS 3953878 as no cause for outage yet. (S61 tripped and L/O at 13:12 OMS 4013025- no fault found) | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 96.5349 | 93.5349 | 11037.1167 | 0.033712 | 0.00036042 | 2015-03-06 | C | 0.033712 | 0.00036042 | 2015 | 2015-03-06 | C | 118 | 0.033712 | 0.00036042
1 | 3954484 | 2015-03-06 11:04 | 2015-03-06 17:20 | 375.8833 | 198 | 24555.3667 | 0.075101 | 0.00060557 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742938 | Recloser 499 tripped. Replace insulator at pole 742938 and cut trees near by | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 124.017 | 121.017 | 23961.3667 | 0.073188 | 0.00060478 | 2015-03-06 | C | 0.073188 | 0.00060478 | 2015 | 2015-03-06 | C | 198 | 0.073188 | 0.00060478
1 | 3955122 | 2015-03-06 11:17 | 2015-03-06 17:06 | 348.95 | 167 | 50935.9833 | 0.15578 | 0.00051076 | Restore Supply on Device 6286 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5195 | replaced insulator at abs 5195 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 305.0059 | 302.0059 | 50434.9833 | 0.15405 | 0.00051009 | 2015-03-06 | C | 0.15405 | 0.00051009 | 2015 | 2015-03-06 | C | 167 | 0.15405 | 0.00051009
1 | 3955539 | 2015-03-06 11:19 | 2015-03-06 12:22 | 63.7333 | 246 | 12862.3667 | 0.039339 | 0.00075237 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB11 | Kelvin Grove CB11 Stoney Creek Tripped. Line sectionalised nothing found. Anjay Prasad and Shazil Khan attended. | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 52.286 | 49.286 | 12124.3667 | 0.037033 | 0.00075139 | 2015-03-06 | C | 0.037033 | 0.00075139 | 2015 | 2015-03-06 | C | 246 | 0.037033 | 0.00075139
1 | 3957504 | 2015-03-06 11:55 | 2015-03-06 16:17 | 262.15 | 899 | 136497.05 | 0.41747 | 0.0027495 | Restore Supply on Device F31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739936 | 11kV CB F31 tripped no flags, L/O. 2R. Lines down, traffic management required. 3m wire and sleeves. Darren Spademan attended. | F3 | WEST QUAY | WAITARA WEST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 151.8321 | 148.8321 | 133800.05 | 0.40868 | 0.0027459 | 2015-03-06 | C | 0.40868 | 0.0027459 | 2015 | 2015-03-06 | C | 899 | 0.40868 | 0.0027459
1 | 3958404 | 2015-03-06 11:57 | 2015-03-06 19:38 | 461.3667 | 163 | 75145.7167 | 0.22983 | 0.00049852 | Restore Supply on Device 4897 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 768337 | Broken crossarm/insulator. Suspect farmer cutting trees damaged the arm. NDR 43035. Paul Fitzpatrick attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 461.0167 | 458.0167 | 74656.7167 | 0.22803 | 0.00049787 | 2015-03-06 | C | 0.22803 | 0.00049787 | 2015 | 2015-03-06 | C | 163 | 0.22803 | 0.00049787
1 | 3958686 | 2015-03-06 11:59 | 2015-03-06 16:16 | 257.3333 | 35 | 4046.8667 | 0.012377 | 0.00010704 | Restore Supply on Device N2060 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 189 RAHOTU ROAD, RAHOTU | Lines down 189 RAHOTU ROAD, RAHOTU. Check if this affects OMS 3969854. Part of feeder fault that chris katene was attending | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 115.6248 | 112.6248 | 3941.8667 | 0.01204 | 0.0001069 | 2015-03-06 | C | 0.01204 | 0.0001069 | 2015 | 2015-03-06 | C | 35 | 0.01204 | 0.0001069
1 | 3958888 | 2015-03-06 12:14 | 2015-03-06 14:58 | 164 | 13 | 2132 | 0.0065206 | 3.9759e-05 | Restore Supply on Device 6420 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6420 | LV line all tangled pushed isolation back due to access. Isolated beyond Fuses 6420. Warren Wright attended. | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 164 | 161 | 2093 | 0.0063929 | 3.9708e-05 | 2015-03-06 | C | 0.0063929 | 3.9708e-05 | 2015 | 2015-03-06 | C | 13 | 0.0063929 | 3.9708e-05
1 | 4031092 | 2015-03-06 12:17 | 2015-03-06 20:41 | 504 | 904 | 121618 | 0.37196 | 0.0027648 | Restore Supply on Device 1133 | 22000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | N/A - NOT APPLICABLE | Received initial tripping on CB4138 (NOTE: Unsure on tripping time due to loss of Comms on Ashcroft repeater - suspect around 17:00 - Also unable to supply any backfeeds for this reason. ABS 4091 open to "simulate" CB4138 tripping and produce OMS No.). F | F4 | LEEDSTOWN 22KV | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 134.5332 | 131.5332 | 118906 | 0.36319 | 0.0027612 | 2015-03-06 | C | 0.36319 | 0.0027612 | 2015 | 2015-03-06 | C | 904 | 0.36319 | 0.0027612
1 | 3963556 | 2015-03-06 13:09 | 2015-03-06 18:45 | 335.5667 | 653 | 162628.9833 | 0.49739 | 0.0019971 | Restore Supply on Device 1112 | 33000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 779116 | 6/3 - FM signed job off with control but was not completed from site. Completed faultman from site so that they could be onsited at another job. Floating 33kV conductor at pole 79116. Back feed from OKN 4621 up to Recloser 142 on CB 5. Materials used: 1 | F1, F2, F3 | WAIOURU 33KV | TP_MATAROA | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 249.049 | 246.049 | 160669.9833 | 0.49075 | 0.0019945 | 2015-03-06 | C | 0.49075 | 0.0019945 | 2015 | 2015-03-06 | C | 653 | 0.49075 | 0.0019945
1 | 3963553 | 2015-03-06 13:10 | 2015-03-06 15:05 | 115.1333 | 764 | 74702.9 | 0.22847 | 0.0023366 | Restore Supply on Device 3102 | 33000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 3102 | 33kV CB 3102 tripped O/C A & B Ph, L/O. Line patrolled. Possible tree branch. | F1, F2, F3 | KAI IWI 33KV | PEAT ST SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 97.7787 | 94.7787 | 72410.9 | 0.22117 | 0.0023336 | 2015-03-06 | C | 0.22117 | 0.0023336 | 2015 | 2015-03-06 | C | 764 | 0.22117 | 0.0023336
1 | 3964619 | 2015-03-06 13:22 | 2015-03-06 14:24 | 61.35 | 194 | 7119.1667 | 0.021773 | 0.00059333 | Restore Supply on Device C279 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 7645 | Te Ore Ore - C829 Church Street Recloser C279 Tripped. Line patrolled. Found 1 blown fuse at Fuses 7645. Joe Matthews attended. | F3 | CHURCH ST | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 36.6967 | 33.6967 | 6537.1667 | 0.019967 | 0.00059256 | 2015-03-06 | C | 0.019967 | 0.00059256 | 2015 | 2015-03-06 | C | 194 | 0.019967 | 0.00059256
1 | 3967216 | 2015-03-06 13:58 | 2015-03-06 17:27 | 208.9333 | 335 | 28544.4667 | 0.087301 | 0.0010246 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T4/330 | Turitea CB4 Aouketere Recloser 10050 Tripped E/F. Line patrolled. Replace glass strain insulator on pole with no number by transformer T4/330. Materials Used: Squirrel Deadend, Squirrel Knuckle, Polymer Insulator, Squirrel Makeoff. Chris Naylor and Tracey | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 85.2074 | 82.2074 | 27539.4667 | 0.084117 | 0.0010232 | 2015-03-06 | C | 0.084117 | 0.0010232 | 2015 | 2015-03-06 | C | 335 | 0.084117 | 0.0010232
1 | 3967552 | 2015-03-06 13:59 | 2015-03-06 15:36 | 96.9833 | 246 | 17094.9833 | 0.052284 | 0.00075237 | Restore Supply on Device 11 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB11 | Kelvin Grove CB11 - Stoney Creek Fault. Line patrolled with no cause of fault located. Shazil Khan attended. | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 69.4918 | 66.4918 | 16356.9833 | 0.049961 | 0.00075139 | 2015-03-06 | C | 0.049961 | 0.00075139 | 2015 | 2015-03-06 | C | 246 | 0.049961 | 0.00075139
1 | 3970293 | 2015-03-06 14:28 | 2015-03-06 18:14 | 225.8833 | 58 | 13101.2333 | 0.040069 | 0.00017739 | Restore Supply on Device T423 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 832071 | part of OMS 3968041 and PARENT 3971375 . Should be child to 3971375. Tree Branch on line, no damage. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 225.8833 | 222.8833 | 12927.2333 | 0.039485 | 0.00017716 | 2015-03-06 | C | 0.039485 | 0.00017716 | 2015 | 2015-03-06 | C | 58 | 0.039485 | 0.00017716
1 | 3968160 | 2015-03-06 14:47 | 2015-03-06 21:54 | 426.8333 | 27 | 7614.9667 | 0.02329 | 8.2577e-05 | Restore Supply on Device 5193 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5193 | Retailer calling for an update - emailed the hub for an update 5:57pm Mark Paterson assigned - email from hub. Patrol carried out. 2 fuses found tripped at 5193 (Reloaded OK - 15A). High winds. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 282.0358 | 279.0358 | 7533.9667 | 0.023012 | 8.2469e-05 | 2015-03-06 | C | 0.023012 | 8.2469e-05 | 2015 | 2015-03-06 | C | 27 | 0.023012 | 8.2469e-05
1 | 3968424 | 2015-03-06 15:10 | 2015-03-06 23:43 | 512.75 | 2 | 514.5667 | 0.0015738 | 6.1168e-06 | Restore Supply on Device T3/241 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M68 | 2 Fuses found tripped at M68 due to high winds. reloaded / relivened after a patrol. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 257.2833 | 254.2833 | 508.5667 | 0.0015534 | 6.1088e-06 | 2015-03-06 | C | 0.0015534 | 6.109e-06 | 2015 | 2015-03-06 | C | 2 | 0.0015534 | 6.1088e-06
1 | 3968709 | 2015-03-06 15:24 | 2015-03-09 16:16 | 4372 | 926 | 86858 | 0.26565 | 0.0028321 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-547 | Auto Reclosed after planned switching on SIS 6376 - believe there to be a possible cable/transformer fault. Faulted cable joint found at TD4-547. Generator was connected to supply until repairs could be made. This record has the outage for TD4-547 where t | F3 | BELLEVUE RD | MATUA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 93.7991 | 90.7991 | 84080 | 0.25682 | 0.0028284 | 2015-03-06 | C | 0.25682 | 0.0028284 | 2015 | 2015-03-06 | C | 926 | 0.25682 | 0.0028284
1 | 3969948 | 2015-03-06 15:57 | 2015-03-06 21:52 | 355.5 | 2 | 641.15 | 0.0019609 | 6.1168e-06 | Restore Supply on Device X2564 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2829 | link # 2829. replace 2 x 15 amp ht fuses. cause: wind. 2 out 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. 2 x HV fuses | F4 | MAKIRIKIRI | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 320.575 | 317.575 | 635.15 | 0.00194 | 6.1088e-06 | 2015-03-06 | C | 0.00194 | 6.109e-06 | 2015 | 2015-03-06 | C | 2 | 0.00194 | 6.1088e-06
1 | 3969998 | 2015-03-06 16:17 | 2015-03-06 17:54 | 96.8 | 143 | 13839.6 | 0.042327 | 0.00043735 | Restore Supply on Device 1297 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 784028 | Line down brought down by tree in notice zone. NDR41474. Materials used: 2 sleeves and 7m conductor. Jeremy Hill attended. | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 96.7804 | 93.7804 | 13410.6 | 0.040962 | 0.00043678 | 2015-03-06 | C | 0.040962 | 0.00043678 | 2015 | 2015-03-06 | C | 143 | 0.040962 | 0.00043678
1 | 3970144 | 2015-03-06 16:20 | 2015-03-06 22:52 | 391.0333 | 3 | 1134.0333 | 0.0034684 | 9.1753e-06 | Restore Supply on Device 3161T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3166T | Please make second response - Transformer X3161T changed for another 30kVA. (Transformer faulted, stormy conditions). | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 378.0111 | 375.0111 | 1125.0333 | 0.0034363 | 9.1633e-06 | 2015-03-06 | C | 0.0034363 | 9.163e-06 | 2015 | 2015-03-06 | C | 3 | 0.0034363 | 9.1633e-06
1 | 3971093 | 2015-03-06 17:17 | 2015-03-06 19:36 | 138.5833 | 80 | 11086.6667 | 0.033908 | 0.00024467 | Restore Supply on Device 5386 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708076 | Tree through lines at pole 708076. 3 conductors down. Isolation at ABS 5386 no back feeds available. Darren Stapleman attended. | F3 | ELLIOT ST | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 138.5833 | 135.5833 | 10846.6667 | 0.03313 | 0.00024435 | 2015-03-06 | C | 0.03313 | 0.00024435 | 2015 | 2015-03-06 | C | 80 | 0.03313 | 0.00024435
1 | 3971375 | 2015-03-06 17:44 | 2015-03-06 20:16 | 151.75 | 115 | 17451.25 | 0.053373 | 0.00035172 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 832071 | Tripping on CB C948 out of Gladstone Sub. A Patrol found a Broken tree branch across the conductors (Wind blown). Isolation from ABS C420/1 to end. Branch removed (no damage) with Tree Contractors carrying out further work in area. Relivened OK. Lee Wilt | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 151.75 | 148.75 | 17106.25 | 0.05225 | 0.00035126 | 2015-03-06 | C | 0.05225 | 0.00035126 | 2015 | 2015-03-06 | C | 115 | 0.05225 | 0.00035126
1 | 3971612 | 2015-03-06 18:06 | 2015-03-06 18:58 | 52.1667 | 28 | 1460.6667 | 0.0044673 | 8.5636e-05 | Restore Supply on Device E62 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40818 | Should have been part of OMS 3971612 2x Faulty insulators at pole P40818. isolation at ABS F70 & E62 | F4 | STONEY CREEK | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 52.1667 | 49.1667 | 1376.6667 | 0.0042049 | 8.5524e-05 | 2015-03-06 | C | 0.0042049 | 8.5524e-05 | 2015 | 2015-03-06 | C | 28 | 0.0042049 | 8.5524e-05
1 | 3971685 | 2015-03-06 18:34 | 2015-03-06 19:17 | 43 | 40 | 1703.1 | 0.0052088 | 0.00012234 | Restore Supply on Device TA719 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 713543 | A twisted crossarm (Pole 713543) had been seen during the day which could have resulted in a tripping. An outage was required between ABS TA917, TA720 and 6661 with backfeeds at TA119 and 6438 to carryout repairs. (NOTE: Tasman CB TA3 was also isolated du | F4 | OAONUI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 42.5775 | 39.5775 | 1583.1 | 0.0048355 | 0.00012218 | 2015-03-06 | C | 0.0048355 | 0.00012218 | 2015 | 2015-03-06 | C | 40 | 0.0048355 | 0.00012218
1 | 3972202 | 2015-03-06 20:49 | 2015-03-07 00:16 | 207.4167 | 143 | 19909.95 | 0.060893 | 0.00043735 | Restore Supply on Device 1297 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | CB 2032 | Received initial tripping on recloser CB2032. (NOTE: No comms to this recloser - flags unknown). Feeder patrolled / sectionalised and eventually all restored to service. Have had tree problems in the past, high winds present. J HIll attended. | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 139.2304 | 136.2304 | 19480.95 | 0.059503 | 0.00043678 | 2015-03-06 | C | 0.059503 | 0.00043678 | 2015 | 2015-03-06 | C | 143 | 0.059503 | 0.00043678
1 | 3972194 | 2015-03-06 20:59 | 2015-03-07 14:27 | 1048.4667 | 1 | 1048.4667 | 0.0032067 | 3.0584e-06 | Restore Supply on Device X1035 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | x1035 | replace 8 amp fuse. cause: wind yesterday. tx x1035. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 1048.4667 | 1045.4667 | 1045.4667 | 0.0031933 | 3.0544e-06 | 2015-03-06 | C | 0.0031933 | 3.054e-06 | 2015 | 2015-03-06 | C | 1 | 0.0031933 | 3.0544e-06
1 | 3973306 | 2015-03-07 02:22 | 2015-03-07 05:41 | 198.3833 | 2 | 395.8167 | 0.0012106 | 6.1168e-06 | Restore Supply on Device M83 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M83 | OMS picked up wrong transformer (T3/528). Fault on spur to T3/49 (2 Fuses tripped at M83 - dead goose found. Reloaded OK). | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 197.9083 | 194.9083 | 389.8167 | 0.0011907 | 6.1088e-06 | 2015-03-07 | C | 0.0011907 | 6.109e-06 | 2015 | 2015-03-07 | C | 2 | 0.0011907 | 6.1088e-06
1 | 3973314 | 2015-03-07 07:15 | 2015-03-07 12:50 | 335.2 | 31 | 4282.75 | 0.013098 | 9.4811e-05 | Restore Supply on Device TE6-268 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 224216 | 9.02am advised Teresa at Trustpower that f/m just attending to line down then will attend this job. This is part of feeder fault. Line down at Pole 224216 - possibly due to high winds in the area at the time. Line repaired with 2 mtrs Namu Conductor 2 X s | F4 | MAKETU | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 138.1532 | 135.1532 | 4189.75 | 0.012797 | 9.4687e-05 | 2015-03-07 | C | 0.012797 | 9.4687e-05 | 2015 | 2015-03-07 | C | 31 | 0.012797 | 9.4687e-05
1 | 3973855 | 2015-03-07 08:07 | 2015-03-07 12:06 | 238.65 | 2 | 477.3 | 0.0014598 | 6.1168e-06 | Restore Supply on Device 5234 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5234 | Related to 3973348 | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 238.65 | 235.65 | 471.3 | 0.0014395 | 6.1088e-06 | 2015-03-07 | C | 0.0014395 | 6.109e-06 | 2015 | 2015-03-07 | C | 2 | 0.0014395 | 6.1088e-06
1 | 3973348 | 2015-03-07 08:07 | 2015-03-07 12:05 | 237.75 | 1 | 237.75 | 0.00072714 | 3.0584e-06 | Restore Supply on Device 4031T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5234 | 2x 6Amp Fuse Links. Mark Patterson attended. | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 237.75 | 234.75 | 234.75 | 0.00071703 | 3.0544e-06 | 2015-03-07 | C | 0.00071703 | 3.054e-06 | 2015 | 2015-03-07 | C | 1 | 0.00071703 | 3.0544e-06
1 | 3977500 | 2015-03-07 09:00 | 2015-03-07 14:09 | 308.75 | 23 | 7101.25 | 0.021719 | 7.0344e-05 | Restore Supply on Device 763 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP89 | This outage tied to NAPA ID 7507. OMS Job 3939554. Could not find this job in OMS. | F2/F4 | TE AROHA BOROUGH | MIKKELSEN ROAD SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 308.75 | 305.75 | 7032.25 | 0.021479 | 7.0252e-05 | 2015-03-07 | C | 0.021479 | 7.0252e-05 | 2015 | 2015-03-07 | C | 23 | 0.021479 | 7.0252e-05
1 | 3973527 | 2015-03-07 09:13 | 2015-03-07 19:06 | 593.2667 | 143 | 22821.5167 | 0.069798 | 0.00043735 | Restore Supply on Device 1026 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 784165 | Lines found tangled between Poles 784165 & 784167 - Line came untangled when hit with hot sticks. Jumper replaced due to corrosion. Materials used: 1 x parallel groove connector. Scott Bullock and Jeremy Hill attended. | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 159.591 | 156.591 | 22392.5167 | 0.068396 | 0.00043678 | 2015-03-07 | C | 0.068396 | 0.00043678 | 2015 | 2015-03-07 | C | 143 | 0.068396 | 0.00043678
1 | 4048826 | 2015-03-07 11:36 | 2015-03-07 19:44 | 488 | 194 | 44765 | 0.13691 | 0.00059333 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | RS 499 A/R, L/O, E/F B Phase. Feeder sectionalised and extensively patrolled with no fault found. Ongoing fault from previous day. Extra faultman called out to patrol with Thermovision camera. Later found in fault OMS 3973577 to be an insulator. | F3 | BROOKLANDS 5 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 230.7474 | 227.7474 | 44183 | 0.13495 | 0.00059256 | 2015-03-07 | C | 0.13495 | 0.00059256 | 2015 | 2015-03-07 | C | 194 | 0.13495 | 0.00059256
1 | 3973781 | 2015-03-07 11:44 | 2015-03-07 13:00 | 76 | 54 | 4104 | 0.012552 | 0.00016515 | Restore Supply on Device 7111 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7111 | 11kV CB 7111, tripped L/O, no flags, Patrolled, no fault found. Phil Webby attended. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 76 | 73 | 3942 | 0.012041 | 0.00016494 | 2015-03-07 | C | 0.012041 | 0.00016494 | 2015 | 2015-03-07 | C | 54 | 0.012041 | 0.00016494
1 | 3974244 | 2015-03-07 12:12 | 2015-03-07 13:48 | 95.9167 | 4 | 383.6667 | 0.0011734 | 1.2234e-05 | Restore Supply on Device 2888 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2191 | Connected to OMS 3964268 | F4 | RANGIKURA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 95.9167 | 92.9167 | 371.6667 | 0.0011352 | 1.2218e-05 | 2015-03-07 | C | 0.0011352 | 1.2218e-05 | 2015 | 2015-03-07 | C | 4 | 0.0011352 | 1.2218e-05
1 | 3974256 | 2015-03-07 12:13 | 2015-03-07 13:09 | 55.5333 | 6 | 331.8333 | 0.0010149 | 1.8351e-05 | Restore Supply on Device V18 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P29076 | Pole P29076 on fire. Top of pole has burnt off. Isolated at Fuses V18 and Temp repairs made. Trevor Pocock attended. | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 55.3056 | 52.3056 | 313.8333 | 0.00095858 | 1.8327e-05 | 2015-03-07 | C | 0.00095858 | 1.8327e-05 | 2015 | 2015-03-07 | C | 6 | 0.00095858 | 1.8327e-05
1 | 3974294 | 2015-03-07 12:27 | 2015-03-07 15:41 | 194 | 248 | 29232 | 0.089404 | 0.00075849 | Restore Supply on Device TA9 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 715985 | 11kV CB TA9 tripped E/F L/O. High Windds in area at time. One span, one Phase down at pole 715985. Iso by ABS TA876, TA916, TA914, Back fed via TA115. All work complete. Paul Fitzpatrick attended. Fiona, may be 2R Works. | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 117.871 | 114.871 | 28488 | 0.087014 | 0.0007575 | 2015-03-07 | C | 0.087014 | 0.0007575 | 2015 | 2015-03-07 | C | 248 | 0.087014 | 0.0007575
1 | 3974556 | 2015-03-07 12:42 | 2015-03-07 18:01 | 319.5333 | 339 | 71270.8 | 0.21798 | 0.0010368 | Restore Supply on Device TA8 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 366607, 717428 | 11kV CB TA 8 tripped E/F L/O. HIgh winds in area. Line down past Fuses TA857 at Pole 366607. Also damage conductor at pole 717428-both repaired. Nick Webby attended. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 210.2383 | 207.2383 | 70253.8 | 0.21458 | 0.0010354 | 2015-03-07 | C | 0.21458 | 0.0010355 | 2015 | 2015-03-07 | C | 339 | 0.21458 | 0.0010354
1 | 3975153 | 2015-03-07 12:55 | 2015-03-07 21:27 | 512.3667 | 1 | 512.3667 | 0.001567 | 3.0584e-06 | Restore Supply on Device 3340T | 6600 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3340t | replaced 2 amp ht fuse at tx 3340t due to lightning. customer's service line is also twisted and has been advised to get a contractor out to have it fixed. No other assets repaired or replaced on site. | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 512.3667 | 509.3667 | 509.3667 | 0.0015558 | 3.0544e-06 | 2015-03-07 | C | 0.0015558 | 3.054e-06 | 2015 | 2015-03-07 | C | 1 | 0.0015558 | 3.0544e-06
1 | 3975761 | 2015-03-07 13:20 | 2015-03-07 16:54 | 214 | 251 | 43058.15 | 0.13169 | 0.00076766 | Restore Supply on Device KA7 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | K4082 | 11kV CB KA7 tripped E/F L/O. HIgh Wind in area at time. Extensively patrolled. The only fault found was blown transformer fusing and lightning arrestor on Tx K4082. Feeder relivened OK via sectionalising. Transformer K4082 re-livened OK. Arrestor has been | F1/F4 | MATAPU | KAPUNI SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 171.5464 | 168.5464 | 42305.15 | 0.12922 | 0.00076666 | 2015-03-07 | C | 0.12922 | 0.00076666 | 2015 | 2015-03-07 | C | 251 | 0.12922 | 0.00076666
1 | 3976040 | 2015-03-07 13:43 | 2015-03-07 15:07 | 84 | 78 | 6552 | 0.020039 | 0.00023856 | Restore Supply on Device I41 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 760458 | 1R OMS 3973510 - Insulator broken and wire hanging low outside property. (2R) 33kv line floating, needing bucket truck and traffic management. Backfeed prepared via ABS ING I31. Line isolated between ING I41 and ABS 5386 and repairs undertaken. Restoratio | F3 | ELLIOT ST | INGLEWOOD SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 84 | 81 | 6318 | 0.019298 | 0.00023825 | 2015-03-07 | C | 0.019298 | 0.00023824 | 2015 | 2015-03-07 | C | 78 | 0.019298 | 0.00023825
1 | 3976618 | 2015-03-07 14:16 | 2015-03-07 15:15 | 58.6333 | 4 | 233 | 0.00071261 | 1.2234e-05 | Restore Supply on Device 7227 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 799461 | Power lines have arched and sparked and caused fire outside address. 1.46pm advised Sammy at svs hub and control 20mins eta - 1.53pm called Fire service and advised eta. Tree in power lines at 222 Te Maire Rd were inside notice zone & contacted HV starti | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 58.25 | 55.25 | 221 | 0.00067503 | 1.2218e-05 | 2015-03-07 | C | 0.00067503 | 1.2218e-05 | 2015 | 2015-03-07 | C | 4 | 0.00067503 | 1.2218e-05
1 | 3976605 | 2015-03-07 14:52 | 2015-03-07 21:30 | 398.2333 | 58 | 23097.5333 | 0.070642 | 0.00017739 | Restore Supply on Device P2060 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710196 | Past 11kV Fuses 5555 - Lines and broken cross arms. Tornado been through area. Correct, ASW- related to either 3976009 or 3975159 both lines down on Pungarehu Road. HV & LV Lines repaired at Pole 710196 - Isolated at Fuses 5555 - Used 1X complete HV cr | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 398.2333 | 395.2333 | 22923.5333 | 0.070018 | 0.00017716 | 2015-03-07 | C | 0.070018 | 0.00017716 | 2015 | 2015-03-07 | C | 58 | 0.070018 | 0.00017716
1 | 3978116 | 2015-03-07 15:04 | 2015-03-07 15:08 | 4.1 | 324 | 1328.4 | 0.0040628 | 0.00099093 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 6610 | Tripped whilst backfeeding OMS Job 3973865. | F3 | BELL BLOCK 2 | BELL BLOCK SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 4.1 | 1.1 | 356.4 | 0.0010886 | 0.00098963 | 2015-03-07 | C | 0.0010886 | 0.00098963 | 2015 | 2015-03-07 | C | 324 | 0.0010886 | 0.00098963
1 | 3978600 | 2015-03-07 15:50 | 2015-03-07 17:43 | 113.0833 | 1 | 113.0833 | 0.00034586 | 3.0584e-06 | Restore Supply on Device X2197 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | x2197 | replace 3 amp ht fuse. x2197. cause: weather. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 113.0833 | 110.0833 | 110.0833 | 0.00033624 | 3.0544e-06 | 2015-03-07 | C | 0.00033624 | 3.054e-06 | 2015 | 2015-03-07 | C | 1 | 0.00033624 | 3.0544e-06
1 | 3978545 | 2015-03-07 16:51 | 2015-03-07 20:49 | 237.7667 | 1 | 237.7667 | 0.00072719 | 3.0584e-06 | Restore Supply on Device 5193 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 8513 | replaced x2 15amp HV fuses at fuse 8513 Cause unknown No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 237.7667 | 234.7667 | 234.7667 | 0.00071708 | 3.0544e-06 | 2015-03-07 | C | 0.00071708 | 3.054e-06 | 2015 | 2015-03-07 | C | 1 | 0.00071708 | 3.0544e-06
1 | 4026946 | 2015-03-07 17:05 | 2015-03-09 00:41 | 1896 | 3187 | 149540 | 0.45736 | 0.0097472 | Restore Supply on Device 17 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB17, CB18, CB19 | at 17:05 Kerepehi Sub, CB 17 & CB 19 Tripped, Ph A & C O/C, E/F, L/O. CB 4 County Water also flagged with Ph A & C O/C, E/F but did not trip. Loss of Supply to Kerepehi Sub. Duty NC believed fault was on CB 4 due to fault flaggings. Sub re-livened except | F4 | AWAITI | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 46.9219 | 43.9219 | 139979 | 0.42756 | 0.0097344 | 2015-03-07 | C | 0.42756 | 0.0097344 | 2015 | 2015-03-07 | C | 3187 | 0.42756 | 0.0097344
1 | 4061171 | 2015-03-07 17:50 | 2015-03-07 23:47 | 357 | 246 | 40955 | 0.12526 | 0.00075237 | Restore Supply on Device KA7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KA7 | at 17:50 Kapuni Sub, CB KA7 Matapu Feeder, Tripped, E/F, L/O. Faultmen dispatched and investigation began. Feeder Sectionalised. Found blown insulator at Transformer K4125. Transformer left isolated over night. All Power Restored on completion.Line was is | F1/F4 | MATAPU | KAPUNI SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 166.4837 | 163.4837 | 40217 | 0.12284 | 0.00075139 | 2015-03-07 | C | 0.12284 | 0.00075139 | 2015 | 2015-03-07 | C | 246 | 0.12284 | 0.00075139
1 | 3987757 | 2015-03-07 20:21 | 2015-03-08 09:13 | 772 | 2 | 267.4 | 0.00081782 | 6.1168e-06 | Restore Supply on Device X711 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200 | related to 3985254 blown fuse at fuses 200 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 133.7 | 130.7 | 261.4 | 0.00079843 | 6.1088e-06 | 2015-03-07 | C | 0.00079843 | 6.109e-06 | 2015 | 2015-03-07 | C | 2 | 0.00079843 | 6.1088e-06
1 | 3984012 | 2015-03-07 20:55 | 2015-03-07 22:58 | 122.6833 | 11 | 1463.1667 | 0.004475 | 3.3643e-05 | Restore Supply on Device TF8-040 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227875 | at 20:55 Pongakawa Sub, CB 3 Rotoehu Feeder. Found lines down at Pole 227875. Trees were found in lines but faultman did not believe this caused fault. Isolated lines at Fuses SF8-002. Permit Issued & Repairs carried out. All Power Restored on completion. | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 133.0152 | 130.0152 | 1430.1667 | 0.0043683 | 3.3599e-05 | 2015-03-07 | C | 0.0043683 | 3.3599e-05 | 2015 | 2015-03-07 | C | 11 | 0.0043683 | 3.3599e-05
1 | 3985596 | 2015-03-07 21:21 | 2015-03-08 10:30 | 788.9833 | 2 | 1577.3667 | 0.0048243 | 6.1168e-06 | Restore Supply on Device Y164 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x164 | plz check 3987294. 3x 3amp hv ht fuses blown to tx x164. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F2 | WATERWORKS RD | KAI IWI SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 788.6833 | 785.6833 | 1571.3667 | 0.0047996 | 6.1088e-06 | 2015-03-07 | C | 0.0047996 | 6.109e-06 | 2015 | 2015-03-07 | C | 2 | 0.0047996 | 6.1088e-06
1 | 3985799 | 2015-03-07 21:43 | 2015-03-07 22:25 | 41.7 | 1 | 41.7 | 0.00012754 | 3.0584e-06 | Restore Supply on Device X6 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x6 | 30/3 - sent e-mail to smc requesting FM to contact Dispatch with notes again as Control did not add job notes when signing off the FM. 30/3 - response from smc: Jeremy Hill is on rest time all day today ? not sure if on tonight, but I can call him tomorro | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 41.7 | 38.7 | 38.7 | 0.00011821 | 3.0544e-06 | 2015-03-07 | C | 0.00011821 | 3.054e-06 | 2015 | 2015-03-07 | C | 1 | 0.00011821 | 3.0544e-06
1 | 3984021 | 2015-03-07 22:03 | 2015-03-07 22:59 | 55.85 | 8 | 446.8 | 0.0013665 | 2.4467e-05 | Restore Supply on Device 6088 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3831T | Stay Wire broken and fell into lines - Isolated at fuses 6088 - Stay wire removed and fuses and carrier replaced. Paul Fitzpatrick attended. | F4 | TE ROTI | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 55.85 | 52.85 | 422.8 | 0.0012914 | 2.4435e-05 | 2015-03-07 | C | 0.0012914 | 2.4435e-05 | 2015 | 2015-03-07 | C | 8 | 0.0012914 | 2.4435e-05
1 | 3979148 | 2015-03-07 22:53 | 2015-03-08 00:05 | 71.65 | 34 | 2436.1 | 0.0074506 | 0.00010399 | Restore Supply on Device X780 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 788674 | Cross arm report on fire - Isolated at Fuses 2578 - Cross arm checked some arc marks on cross arm but ok - 1 x insulator used. Glen Most attended. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 71.65 | 68.65 | 2334.1 | 0.0071293 | 0.00010385 | 2015-03-07 | C | 0.0071293 | 0.00010385 | 2015 | 2015-03-07 | C | 34 | 0.0071293 | 0.00010385
1 | 3986030 | 2015-03-08 00:04 | 2015-03-08 14:50 | 886 | 408 | 8378 | 0.025623 | 0.0012478 | Restore Supply on Device D11 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 708780 | faultman found line down at pole 708780, line was isolated at Fuses 4977 to repair the lines. 4 meters No: 8 wire & 6 sleeves used. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 20.5343 | 17.5343 | 7154 | 0.021851 | 0.0012462 | 2015-03-08 | C | 0.021851 | 0.0012462 | 2015 | 2015-03-08 | C | 408 | 0.021851 | 0.0012462
1 | 3986943 | 2015-03-08 04:41 | 2015-03-08 04:41 | 0.1 | 69 | 5993 | 0.018329 | 0.00021103 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 795050 | Faultman found line down at pole 795050, line was isolated at Links 4240/6 & ABS 4240/1 to repair the line. 1 meter 16mm copper replaced, 2 x sleeves, 1 x binder. Glen Most attended. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 86.8551 | 83.8551 | 5786 | 0.017673 | 0.00021076 | 2015-03-08 | C | 0.017673 | 0.00021075 | 2015 | 2015-03-08 | C | 69 | 0.017673 | 0.00021076
1 | 3987109 | 2015-03-08 07:06 | 2015-03-08 09:13 | 127 | 201 | 25465.7 | 0.077885 | 0.00061474 | Restore Supply on Device X1634 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | Fuses 200 | possibly related to 3987051. Replace blown fuses at Fuses 200 after high winds pass through area. Line clash suspected. Materials Used: 2 x 30 Amp Fuses replaced. Glen Most attended. | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 126.695 | 123.695 | 24862.7 | 0.075941 | 0.00061394 | 2015-03-08 | C | 0.075941 | 0.00061394 | 2015 | 2015-03-08 | C | 201 | 0.075941 | 0.00061394
1 | 3987143 | 2015-03-08 08:22 | 2015-03-08 16:24 | 481.8667 | 1 | 481.8667 | 0.0014738 | 3.0584e-06 | Restore Supply on Device X1154 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | X1154 | possibly related to 3987102. Was part of 3986943 - job would not unlock and wouldn't roll up for control so have cleared off.. plz refer to Mainline job 3986943 | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 481.8667 | 478.8667 | 478.8667 | 0.0014627 | 3.0544e-06 | 2015-03-08 | C | 0.0014627 | 3.054e-06 | 2015 | 2015-03-08 | C | 1 | 0.0014627 | 3.0544e-06
1 | 3987165 | 2015-03-08 08:29 | 2015-03-08 16:22 | 472.5667 | 1 | 472.5667 | 0.0014453 | 3.0584e-06 | Restore Supply on Device X1659 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | X1659 | possibly related 3987102. was part of 3986943 - job would not unlock and wouldn't roll up for control so have cleared off.. plz refer to Mainline job 3986943. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 472.5667 | 469.5667 | 469.5667 | 0.0014343 | 3.0544e-06 | 2015-03-08 | C | 0.0014343 | 3.054e-06 | 2015 | 2015-03-08 | C | 1 | 0.0014343 | 3.0544e-06
1 | 3987346 | 2015-03-08 09:40 | 2015-03-08 16:20 | 400.5667 | 1 | 400.5667 | 0.0012251 | 3.0584e-06 | Restore Supply on Device X959 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | X959 | possibly related 3987102. was part of 3986943 - job would not unlock and wouldn't roll up for control so have cleared off.. please refer to Mainline job 3986943. | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 400.5667 | 397.5667 | 397.5667 | 0.0012143 | 3.0544e-06 | 2015-03-08 | C | 0.0012143 | 3.054e-06 | 2015 | 2015-03-08 | C | 1 | 0.0012143 | 3.0544e-06
1 | 3987408 | 2015-03-08 09:56 | 2015-03-08 10:15 | 19 | 2 | 38 | 0.00011622 | 6.1168e-06 | Restore Supply on Device Y297 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Y297 | Faultman found 2 blown fuses on transformer Y297 suspect lightning strike as a lot of lightning went through the area. 2 X 2 Amp HV fuses replaced. Scot Bullock attended. | F4 | BRUNSWICK | ROBERTS AVE SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 19 | 16 | 32 | 9.7742e-05 | 6.1088e-06 | 2015-03-08 | C | 9.7742e-05 | 6.109e-06 | 2015 | 2015-03-08 | C | 2 | 9.7742e-05 | 6.1088e-06
1 | 3988865 | 2015-03-08 15:35 | 2015-03-08 17:29 | 114.0667 | 115 | 13117.6667 | 0.040119 | 0.00035172 | Restore Supply on Device 564 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 810149 | Faultman found a branch on the lines at pole 810149 (B & C Phase), faultman removed branch with hot sticks. Alan Cox attended. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 114.0667 | 111.0667 | 12772.6667 | 0.039013 | 0.00035126 | 2015-03-08 | C | 0.039013 | 0.00035126 | 2015 | 2015-03-08 | C | 115 | 0.039013 | 0.00035126
1 | 3987939 | 2015-03-08 15:48 | 2015-03-08 16:40 | 52 | 73 | 3796 | 0.01161 | 0.00022326 | Restore Supply on Device 244 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8209 | Faultman requesting 2R needing to change full set of DDO fuses. Line was isolated at ABS's 150 & 471 and at Sw/Gear 30/1 to replace full set of fuse holders on Fuses 8209. Blair Gregg attended. | F3 | BROOKLANDS 10 | BROOKLANDS SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 52 | 49 | 3577 | 0.010926 | 0.00022297 | 2015-03-08 | C | 0.010926 | 0.00022297 | 2015 | 2015-03-08 | C | 73 | 0.010926 | 0.00022297
1 | 3987948 | 2015-03-08 17:06 | 2015-03-08 19:10 | 123.6833 | 19 | 2091.8667 | 0.0063978 | 5.811e-05 | Restore Supply on Device TP2163 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole B0238 | At 17:06 Baird Rd Sub, CB 4 Campbell St Feeder. Found broken crossarms & broken insulators. Isolated lines at Fuses FC1199. All Power Restored on completion. Steve Doran Attended. 1.29pm advised Glo of job. Replaced 2x HV Strain Crossarms, 3x Strain Insul | F3 | CAMPBELL ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 110.0982 | 107.0982 | 2034.8667 | 0.0062153 | 5.8034e-05 | 2015-03-08 | C | 0.0062153 | 5.8034e-05 | 2015 | 2015-03-08 | C | 19 | 0.0062153 | 5.8034e-05
1 | 3989552 | 2015-03-08 19:23 | 2015-03-08 20:32 | 69.7167 | 15 | 431.9333 | 0.001321 | 4.5876e-05 | Restore Supply on Device 6032 | 6600 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 6032 | Line patrolled and 2 x HV Fuses found blown. 2x 8 Amp Fuse Links. Phil Webby attended. | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 28.7956 | 25.7956 | 386.9333 | 0.0011819 | 4.5816e-05 | 2015-03-08 | C | 0.0011819 | 4.5816e-05 | 2015 | 2015-03-08 | C | 15 | 0.0011819 | 4.5816e-05
1 | 3989669 | 2015-03-09 02:33 | 2015-03-09 04:24 | 110.3167 | 4 | 110.3167 | 0.00033739 | 1.2234e-05 | Restore Supply on Device TE5-137 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP315 | Reloaded, Relivened 2x 10A HV Fuses and Replaced Fuse Carriers at FP315. Steve Doran Attended. Suspect Bird Strike but no evidence of this was found. | F1/F3 | TE PUKE NORTH | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 27.5792 | 24.5792 | 98.3167 | 0.0003003 | 1.2218e-05 | 2015-03-09 | C | 0.0003003 | 1.2218e-05 | 2015 | 2015-03-09 | C | 4 | 0.0003003 | 1.2218e-05
1 | 3946674 | 2015-03-09 08:36 | 2015-03-09 16:44 | 488 | 37 | 16280 | 0.049791 | 0.00011316 | NAPA ID:07571 TP_MANGAMAIRE GXP > MANGAMUTU SUB > MANGAMAIRE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P00303 | Run new 33KV line from P00303 to P40509 above existing 11KV | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 440 | 437 | 16169 | 0.049387 | 0.00011301 | 2015-03-09 | B | 0.024693 | 5.6507e-05 | 2015 | 2015-03-09 | B | 37 | 0.049387 | 0.00011301
1 | 3878656 | 2015-03-09 09:00 | 2015-03-09 15:30 | 390 | 326 | 127140 | 0.38885 | 0.00099705 | NAPA ID:03889 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp Links 29 | Run new conductor from pole p366107 Koputara Rd to pole p49319 Hunia Tce | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 390 | 387 | 126162 | 0.38535 | 0.00099574 | 2015-03-09 | B | 0.19268 | 0.00049787 | 2015 | 2015-03-09 | B | 326 | 0.38535 | 0.00099574
1 | 3885972 | 2015-03-09 09:13 | 2015-03-09 11:53 | 160 | 4 | 640 | 0.0019574 | 1.2234e-05 | NAPA ID:05596 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-025 | Morning, To replace Transformer TC2-025. Works location: Work Rd, Tauranga. WO 10147830 | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 160 | 157 | 628 | 0.0019182 | 1.2218e-05 | 2015-03-09 | B | 0.00095909 | 6.109e-06 | 2015 | 2015-03-09 | B | 4 | 0.0019182 | 1.2218e-05
1 | 3916174 | 2015-03-09 09:22 | 2015-03-09 15:02 | 340.4167 | 2 | 680.8333 | 0.0020823 | 6.1168e-06 | NAPA ID:05946 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC795 | To replace 11kV Poles and cross arms beyond FC795. This OMS Parent ID replaces OMS Parent ID 3799030. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 340.4167 | 337.4167 | 674.8333 | 0.0020612 | 6.1088e-06 | 2015-03-09 | B | 0.0010306 | 3.054e-06 | 2015 | 2015-03-09 | B | 2 | 0.0020612 | 6.1088e-06
1 | 3915594 | 2015-03-09 09:39 | 2015-03-09 14:54 | 314.35 | 2 | 628.7 | 0.0019228 | 6.1168e-06 | NAPA ID:06057 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1446 | To replace rotten 11kV cross arms beyond FC1446. This OMS Parent ID replaces OMS Parent ID 3714977. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 314.35 | 311.35 | 622.7 | 0.001902 | 6.1088e-06 | 2015-03-09 | B | 0.000951 | 3.054e-06 | 2015 | 2015-03-09 | B | 2 | 0.001902 | 6.1088e-06
1 | 3915597 | 2015-03-09 09:55 | 2015-03-09 12:55 | 179.9333 | 4 | 719.7333 | 0.0022012 | 1.2234e-05 | NAPA ID:06063 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP43 | To replace 11kV cross arm on existing spur line. This OMS Parent ID replaces OMS Parent ID 3715282 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 179.9333 | 176.9333 | 707.7333 | 0.0021617 | 1.2218e-05 | 2015-03-09 | B | 0.0010809 | 6.109e-06 | 2015 | 2015-03-09 | B | 4 | 0.0021617 | 1.2218e-05
1 | 3990485 | 2015-03-09 10:08 | 2015-03-09 11:54 | 106 | 7 | 742 | 0.0022693 | 2.1409e-05 | Restore Supply on Device T343 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T343 | Joe Matthews onsite, no comms. call from Gavin Gray advising HV line broken on pole. Extra 1R. request to help as there is a broken HV line on site which needs fixing. Line was isolated at Fuses 7636 to repair jumper to tramsformer T343. | F4 | PUKETIRO | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 106 | 103 | 721 | 0.0022022 | 2.1381e-05 | 2015-03-09 | C | 0.0022022 | 2.1381e-05 | 2015 | 2015-03-09 | C | 7 | 0.0022022 | 2.1381e-05
1 | 3990543 | 2015-03-09 11:47 | 2015-03-09 12:45 | 58.7167 | 1 | 58.7167 | 0.00017958 | 3.0584e-06 | Restore Supply on Device M1160 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | UNKNOWN - NO FAULT FOUND | nn | meter burnt out, advised customer to get meter sorted via retailer. no fault on network | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 58.7167 | 55.7167 | 55.7167 | 0.00017018 | 3.0544e-06 | 2015-03-09 | C | 0.00017018 | 3.054e-06 | 2015 | 2015-03-09 | C | 1 | 0.00017018 | 3.0544e-06
1 | 3886035 | 2015-03-09 13:00 | 2015-03-09 14:30 | 90 | 1 | 90 | 0.00027526 | 3.0584e-06 | NAPA ID:05769 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-192 | Afternoon, To replace Transformer TC2-192. Works location: Work Rd, Tauranga. WO 10147830. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 90 | 87 | 87 | 0.00026573 | 3.0544e-06 | 2015-03-09 | B | 0.00013287 | 1.527e-06 | 2015 | 2015-03-09 | B | 1 | 0.00026573 | 3.0544e-06
1 | 3988762 | 2015-03-09 14:25 | 2015-03-09 16:01 | 96 | 2 | 192 | 0.00058722 | 6.1168e-06 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X1508 | Paul Osborne advised they were working at this ppty under SRC and went to reliven and found that the tx x1508 is faulty and needs replacing. Paul Osborne advised that this will be attended to tomorrow Mon 9/3. replace 30 kva 3 phases transformer. cause: | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 96 | 93 | 186 | 0.00056812 | 6.1088e-06 | 2015-03-09 | B | 0.00028406 | 3.054e-06 | 2015 | 2015-03-09 | B | 2 | 0.00056812 | 6.1088e-06
1 | 3991091 | 2015-03-09 21:20 | 2015-03-09 22:43 | 83.3667 | 65 | 5418.8333 | 0.016573 | 0.0001988 | Restore Supply on Device 5043T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4994 | 8.11pm - advised smc. Reterminated jumper into DDO on two phases. Nil materials used. | F4 | CARDIFF RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 83.3667 | 80.3667 | 5223.8333 | 0.015956 | 0.00019854 | 2015-03-09 | C | 0.015956 | 0.00019854 | 2015 | 2015-03-09 | C | 65 | 0.015956 | 0.00019854
1 | 3991140 | 2015-03-09 21:43 | 2015-03-09 23:29 | 105.75 | 18 | 410.6167 | 0.0012558 | 5.5052e-05 | Restore Supply on Device T9/293 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V83 | possibly part of oms 3991136. Replaced 2x10Amp HV Links | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 22.812 | 19.812 | 356.6167 | 0.0010893 | 5.498e-05 | 2015-03-09 | C | 0.0010893 | 5.498e-05 | 2015 | 2015-03-09 | C | 18 | 0.0010893 | 5.498e-05
1 | 3991234 | 2015-03-10 00:20 | 2015-03-10 01:49 | 88.8167 | 1900 | 94013.6667 | 0.28753 | 0.005811 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E56 | CB 7 Trip, E/F, O/C B Phase. Feeder sectionalised with use of fault locators. Fault found to be at Fuses E56 where Lightning Arrestor had blown & Earth wire had fallen down onto live cable termination tripping feeder. Earth wire removed & 10 Amp Fuse Link | F3 | ROBERTS LINE | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 49.4809 | 46.4809 | 88313.6667 | 0.26975 | 0.0058034 | 2015-03-10 | C | 0.26975 | 0.0058034 | 2015 | 2015-03-10 | C | 1900 | 0.26975 | 0.0058034
1 | 3876357 | 2015-03-10 06:53 | 2015-03-10 17:06 | 613 | 16 | 272 | 0.00083189 | 4.8935e-05 | NAPA ID:06683 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 224 | 0.00068419 | 4.8871e-05 | 2015-03-10 | B | 0.00034209 | 2.4435e-05 | 2015 | 2015-03-10 | B | 16 | 0.00068419 | 4.8871e-05
1 | 3994048 | 2015-03-10 08:30 | 2015-03-10 12:15 | 225.0667 | 1 | 225.0667 | 0.00068835 | 3.0584e-06 | Restore Supply on Device X456 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 849434 | Replaced x2 6amp main line HV fuses 849434 TX 2912 line clash due to wind No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F4 | MATAROA A | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 225.0667 | 222.0667 | 222.0667 | 0.00067829 | 3.0544e-06 | 2015-03-10 | C | 0.00067829 | 3.054e-06 | 2015 | 2015-03-10 | C | 1 | 0.00067829 | 3.0544e-06
1 | 3876399 | 2015-03-10 08:43 | 2015-03-10 14:24 | 340.9833 | 9 | 3068.85 | 0.0093858 | 2.7526e-05 | NAPA ID:06245 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV WH887 | Replace poles and conductor on Hicks road. Works location: Hicks Rd. WO 10160005 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 340.9833 | 337.9833 | 3041.85 | 0.0092911 | 2.749e-05 | 2015-03-10 | B | 0.0046455 | 1.3745e-05 | 2015 | 2015-03-10 | B | 9 | 0.0092911 | 2.749e-05
1 | 3915581 | 2015-03-10 08:54 | 2015-03-10 15:57 | 423 | 11 | 4653 | 0.014231 | 3.3643e-05 | NAPA ID:05607 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9307/2, 9308/2 | To replace 11kV conductors between Poles M1214 and M1228. OMS Parent ID 3640042 is replaced by this OMS Parent ID 3915581. | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 423 | 420 | 4620 | 0.014111 | 3.3599e-05 | 2015-03-10 | B | 0.0070557 | 1.6799e-05 | 2015 | 2015-03-10 | B | 11 | 0.014111 | 3.3599e-05
1 | 3822173 | 2015-03-10 08:57 | 2015-03-10 13:53 | 295.6333 | 29 | 8573.3667 | 0.026221 | 8.8694e-05 | NAPA ID:06167 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 387396 | Re-conductor between poles 387396 & F0835. Works location: Old Te Aroha Rd. WO 10163038 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 295.6333 | 292.6333 | 8486.3667 | 0.025921 | 8.8578e-05 | 2015-03-10 | B | 0.01296 | 4.4289e-05 | 2015 | 2015-03-10 | B | 29 | 0.025921 | 8.8578e-05
1 | 3893234 | 2015-03-10 09:16 | 2015-03-10 15:00 | 344 | 26 | 8944 | 0.027355 | 7.9519e-05 | NAPA ID:06459 TP_KAITIMAKO GXP > WELCOME BAY SUB > KAITEMAKO RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | transformer TD4 559 | REPLACE POLES AND RECONDUCTOR HV FEEDER | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 8866 | 0.027081 | 7.9415e-05 | 2015-03-10 | B | 0.01354 | 3.9708e-05 | 2015 | 2015-03-10 | B | 26 | 0.027081 | 7.9415e-05
1 | 3899106 | 2015-03-10 09:18 | 2015-03-10 11:04 | 106 | 2 | 212 | 0.00064839 | 6.1168e-06 | NAPA ID:05598 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1-034 | Morning to replace transformer TC1-034. Works location: Lockington Rd Tauranga WO 10147830 | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 106 | 103 | 206 | 0.00062921 | 6.1088e-06 | 2015-03-10 | B | 0.00031461 | 3.054e-06 | 2015 | 2015-03-10 | B | 2 | 0.00062921 | 6.1088e-06
1 | 3869517 | 2015-03-10 09:24 | 2015-03-10 11:17 | 112.3 | 8 | 898.4 | 0.0027477 | 2.4467e-05 | NAPA ID:06436 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 723254 | Replace two 11kv poles 723254, & 723259. Works location: Sommerville Rd Hawera WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 112.3 | 109.3 | 874.4 | 0.0026708 | 2.4435e-05 | 2015-03-10 | B | 0.0013354 | 1.2218e-05 | 2015 | 2015-03-10 | B | 8 | 0.0026708 | 2.4435e-05
1 | 3822305 | 2015-03-10 09:30 | 2015-03-10 15:14 | 344 | 63 | 21672 | 0.066282 | 0.00019268 | NAPA ID:05971 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 37 | pole replacements and crossarm changes.(just note i was unable to change isolations and earths on phasing equip sheet. Works location: Wairau Rd. WO 10154759 | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 21483 | 0.065618 | 0.00019243 | 2015-03-10 | B | 0.032809 | 9.6214e-05 | 2015 | 2015-03-10 | B | 63 | 0.065618 | 0.00019243
1 | 3898484 | 2015-03-10 09:36 | 2015-03-10 14:10 | 274 | 6 | 1644 | 0.005028 | 1.8351e-05 | NAPA ID:05409 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | pole 227953 | To replace 1 pole & Remove Tempoary Links TEMP05 | F4 | ROTOEHU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 274 | 271 | 1626 | 0.0049665 | 1.8327e-05 | 2015-03-10 | B | 0.0024832 | 9.163e-06 | 2015 | 2015-03-10 | B | 6 | 0.0049665 | 1.8327e-05
1 | 3876459 | 2015-03-10 09:37 | 2015-03-10 14:44 | 307.2667 | 15 | 4609 | 0.014096 | 4.5876e-05 | NAPA ID:06216 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P41300 | Replace 11kv xarms and fuse arm under LLP replace TX under AP. Works location: Totara Rd WO 10153157 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 307.2667 | 304.2667 | 4564 | 0.01394 | 4.5816e-05 | 2015-03-10 | B | 0.0069702 | 2.2908e-05 | 2015 | 2015-03-10 | B | 15 | 0.01394 | 4.5816e-05
1 | 4006551 | 2015-03-10 11:20 | 2015-03-10 12:28 | 68 | 119 | 7455 | 0.022801 | 0.00036395 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | ABS 226 | CB 2 tripped during switching on SIS 5669 for routine CB maintenance at Moturoa sub. Line sectionalising was commenced when CB tripped again following cursory line patrol. CB 4 also tripped during sectionalising sequence losing supply also to CB 3 also as | F4 | MOTUROA 2 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 62.6471 | 59.6471 | 7098 | 0.02168 | 0.00036348 | 2015-03-10 | C | 0.02168 | 0.00036348 | 2015 | 2015-03-10 | C | 119 | 0.02168 | 0.00036348
1 | 4004939 | 2015-03-10 11:20 | 2015-03-10 11:31 | 11 | 1434 | 10046 | 0.030725 | 0.0043858 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | part of feeder fault | F4 | MOTUROA 2 | MOTUROA SUB | TP_NEW PLYMOUTH | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 7.0056 | 4.0056 | 5744 | 0.017545 | 0.00438 | 2015-03-10 | C | 0.017545 | 0.00438 | 2015 | 2015-03-10 | C | 1434 | 0.017545 | 0.00438
1 | 4008936 | 2015-03-10 12:26 | 2015-03-10 18:56 | 389.4667 | 2 | 725.1167 | 0.0022177 | 6.1168e-06 | Restore Supply on Device TC3580 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | B0326 | This was part of 4008916. NDR 048057. 400v line tangled together - Untangled line blown hv fuse on tx & tripped feeder out. Aluminium on road crossing has been damaged pole B0326. Line is 5.2 high & needs to be raised. F/man requested 2R to resag both | F4 | PAPANUI ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 362.5583 | 359.5583 | 719.1167 | 0.0021965 | 6.1088e-06 | 2015-03-10 | C | 0.0021965 | 6.109e-06 | 2015 | 2015-03-10 | C | 2 | 0.0021965 | 6.1088e-06
1 | 3899118 | 2015-03-10 13:00 | 2015-03-10 14:04 | 64 | 5 | 320 | 0.0009787 | 1.5292e-05 | NAPA ID:05766 TP_TAURANGA 33 GXP > AONGATETE SUB > LOCKINGTON ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-030 | Morning to replace transformer TC1-034. Afternnon to replace Transformer TC2-030. Works location: Wright Rd Tauranga. WO 10147830 | F4 | LOCKINGTON ROAD | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 64 | 61 | 305 | 0.0009316 | 1.5272e-05 | 2015-03-10 | B | 0.0004658 | 7.636e-06 | 2015 | 2015-03-10 | B | 5 | 0.0009316 | 1.5272e-05
1 | 4013025 | 2015-03-10 13:12 | 2015-03-10 15:13 | 120.6333 | 676 | 71378.8 | 0.21831 | 0.0020675 | Restore Supply on Device S61 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB S61 | CB S61 tripped to L/O - E/F flag - line sectionalised & patrolled - no fault found - all supply restored - Brett Bensley & Chris Katene attended | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 105.5899 | 102.5899 | 69350.8 | 0.21183 | 0.0020648 | 2015-03-10 | C | 0.21183 | 0.0020648 | 2015 | 2015-03-10 | C | 676 | 0.21183 | 0.0020648
1 | 4013769 | 2015-03-10 14:16 | 2015-03-10 15:21 | 64.75 | 1 | 64.75 | 0.00019803 | 3.0584e-06 | Restore Supply on Device 3517T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | 762647 | Using the nearest ICP - Digger has pulled lines out of the ground next to pole 762647.939 - MAIN NORTH ROAD - Urenui They believe there is currently no damage. 2:18pm - called through to hub - advised Talia pulled cable up slightly, cable is all | F5 | PRINCESS ST | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 64.75 | 61.75 | 61.75 | 0.00018861 | 3.0544e-06 | 2015-03-10 | C | 0.00018861 | 3.054e-06 | 2015 | 2015-03-10 | C | 1 | 0.00018861 | 3.0544e-06
1 | 4013765 | 2015-03-10 14:32 | 2015-03-10 15:00 | 28 | 26 | 728 | 0.0022265 | 7.9519e-05 | Restore Supply on Device X1074 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758028 | Repaired jumper on pole 758028 | F5 | IRIRANGI | WAIOURU SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 650 | 0.0019854 | 7.9415e-05 | 2015-03-10 | C | 0.0019854 | 7.9415e-05 | 2015 | 2015-03-10 | C | 26 | 0.0019854 | 7.9415e-05
1 | 4013835 | 2015-03-10 14:40 | 2015-03-10 15:18 | 37.6833 | 9 | 339.15 | 0.0010373 | 2.7526e-05 | Restore Supply on Device WH887 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 722684 | remove tree from lines at pole 722684 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 37.6833 | 34.6833 | 312.15 | 0.00095344 | 2.749e-05 | 2015-03-10 | C | 0.00095344 | 2.749e-05 | 2015 | 2015-03-10 | C | 9 | 0.00095344 | 2.749e-05
1 | 3881359 | 2015-03-11 06:01 | 2015-03-11 17:23 | 682.5 | 101 | 68932.5 | 0.21082 | 0.0003089 | NAPA ID:06077 TP_KINLEITH GXP > MARAETAI ROAD SUB > MOSSOPS RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 380224 | AP1: Connect temporary generator to TC2997 and TC2998. Disconnect LV from transformers. AP2: Install new Safelink CFCF, 9899, and remove Magenfix units from TC2997 and TC2998. TP1: Test 11kV cables connected to 9899. AP3: Complete connections to 9899. AP | F3 | CAMPBELL ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 682.5 | 679.5 | 68629.5 | 0.20962 | 0.0003085 | 2015-03-11 | B | 0.10481 | 0.00015425 | 2015 | 2015-03-11 | B | 101 | 0.20962 | 0.0003085
1 | 4015268 | 2015-03-11 08:06 | 2015-03-11 16:41 | 515.6333 | 1 | 515.6333 | 0.001577 | 3.0584e-06 | Restore Supply on Device 2495T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 4333 | Replaced x2 3amp HV fuses at TX 4333 due to opossum. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 515.6333 | 512.6333 | 512.6333 | 0.0015658 | 3.0544e-06 | 2015-03-11 | C | 0.0015658 | 3.054e-06 | 2015 | 2015-03-11 | C | 1 | 0.0015658 | 3.0544e-06
1 | 4015371 | 2015-03-11 08:37 | 2015-03-11 11:07 | 149.2667 | 1 | 149.2667 | 0.00045652 | 3.0584e-06 | Restore Supply on Device TC5052 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | Between pols U12753 - U0767 | 325 Hikuai School Road, Hikuai tree has fallen on line, there is still power, tree is located at the ford down the drive way due to strong winds on Saturday 8.39am advised Joanne svs hub of job & control Tree fallen on 11KV line over 1 phase. Push tr | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 149.2667 | 146.2667 | 146.2667 | 0.00044676 | 3.0544e-06 | 2015-03-11 | C | 0.00044676 | 3.054e-06 | 2015 | 2015-03-11 | C | 1 | 0.00044676 | 3.0544e-06
1 | 3915325 | 2015-03-11 08:45 | 2015-03-11 16:08 | 442.55 | 27 | 11948.85 | 0.036545 | 8.2577e-05 | NAPA ID:07426 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 328717 | Replace 11kV poles, crossarms and conductors. 33kV line isolated and earthed while reconductoring taking place. Works location: Esdaile Rd. WO 10146566 | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 442.55 | 439.55 | 11867.85 | 0.036249 | 8.2469e-05 | 2015-03-11 | B | 0.018125 | 4.1235e-05 | 2015 | 2015-03-11 | B | 27 | 0.036249 | 8.2469e-05
1 | 3886025 | 2015-03-11 09:47 | 2015-03-11 13:00 | 193.7833 | 67 | 12983.4833 | 0.039709 | 0.00020491 | NAPA ID:06792 TP_TE MATAI GXP > ATUAROA AVE SUB > NO 3 ROAD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE5-279 | Replace kiosk sub Transformer TE5-285 with new micro sub. Works location: 1161 No 3 Rd, Te Puke. WO 10163311. | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 193.7833 | 190.7833 | 12782.4833 | 0.039043 | 0.00020465 | 2015-03-11 | B | 0.019522 | 0.00010232 | 2015 | 2015-03-11 | B | 67 | 0.039043 | 0.00020465
1 | 3902132 | 2015-03-11 10:04 | 2015-03-11 13:52 | 227.85 | 38 | 8658.3 | 0.026481 | 0.00011622 | NAPA ID:06437 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 722617 | Replace one 11kv pole 722617. Works location: Arthur St Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 227.85 | 224.85 | 8544.3 | 0.026098 | 0.00011607 | 2015-03-11 | B | 0.013049 | 5.8034e-05 | 2015 | 2015-03-11 | B | 38 | 0.026098 | 0.00011607
1 | 4102066 | 2015-03-11 11:48 | 2015-03-11 12:21 | 33 | 2 | 66 | 0.00020186 | 6.1168e-06 | Restore Supply on Device T7/216 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | t7/216 | Remove RHS of 11kV switchboard, includes physical isolation of CB10245/8,10245/9,10245/10 cables from circuits & LST cables off R5. | F4 | KONINI | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 33 | 30 | 60 | 0.00018327 | 6.1088e-06 | 2015-03-11 | C | 0.00018327 | 6.109e-06 | 2015 | 2015-03-11 | C | 2 | 0.00018327 | 6.1088e-06
1 | 4017930 | 2015-03-11 13:05 | 2015-03-11 15:26 | 140.7 | 17 | 2391.9 | 0.0073154 | 5.1993e-05 | Restore Supply on Device 612 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 801800 | hv outage, farm machinery took line out. ndr # 23094. replace 10m of 16mm copper wire and re-sleeved back in place. pole 801800. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 140.7 | 137.7 | 2340.9 | 0.0071501 | 5.1925e-05 | 2015-03-11 | C | 0.0071501 | 5.1925e-05 | 2015 | 2015-03-11 | C | 17 | 0.0071501 | 5.1925e-05
1 | 4017947 | 2015-03-11 13:11 | 2015-03-11 17:50 | 279.0333 | 86 | 13199.8667 | 0.040371 | 0.00026302 | Restore Supply on Device 5329 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 763932 | Recloser 5329 tripped to L/O - O/C & E/F flags - report of tree through line reported on Piko Rd - isolation at fuses 5193 - tree had been felled through line by land owner - NDR number 43971 - all supply restored following repairs - safety manager entry | F5 | MAIN RD MOTONUI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 153.4868 | 150.4868 | 12941.8667 | 0.03953 | 0.00026268 | 2015-03-11 | C | 0.03953 | 0.00026268 | 2015 | 2015-03-11 | C | 86 | 0.03953 | 0.00026268
1 | 4019390 | 2015-03-11 15:12 | 2015-03-11 16:23 | 70.9333 | 65 | 6658.55 | 0.020365 | 0.0001988 | Restore Supply on Device SL2-087 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TL2-002 | Restoration of feeder after planned switching. | F1 | CHAPEL ST | HAMILTON STREET SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 102.4392 | 99.4392 | 6463.55 | 0.019742 | 0.00019854 | 2015-03-11 | C | 0.019742 | 0.00019854 | 2015 | 2015-03-11 | C | 65 | 0.019742 | 0.00019854
1 | 4019527 | 2015-03-11 18:10 | 2015-03-11 18:50 | 40 | 19 | 746.8167 | 0.0022841 | 5.811e-05 | Restore Supply on Device T7/13 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses R48 | possibly part of OMS 4019517 Faultman found 2 blown fuses at Fuses R48 sespects birds. 2 x 10Amp HV fuses replaced. | F4 | MANGAMAIRE | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 39.3061 | 36.3061 | 689.8167 | 0.002107 | 5.8034e-05 | 2015-03-11 | C | 0.002107 | 5.8034e-05 | 2015 | 2015-03-11 | C | 19 | 0.002107 | 5.8034e-05
1 | 4019876 | 2015-03-11 22:45 | 2015-03-11 23:55 | 70 | 18 | 1260 | 0.0038536 | 5.5052e-05 | Restore Supply on Device T9/292 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P15367 | Faultman found damaged joint between No. 8 wire & copper conductor at pole P15367, line was isolated at Fuses V83 to make a temporary jumper faultman will defect section of line needs to be replaced. | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 70 | 67 | 1206 | 0.0036836 | 5.498e-05 | 2015-03-11 | C | 0.0036836 | 5.498e-05 | 2015 | 2015-03-11 | C | 18 | 0.0036836 | 5.498e-05
1 | 3912702 | 2015-03-12 00:30 | 2015-03-12 02:20 | 110.0833 | 81 | 8916.75 | 0.027271 | 0.00024773 | NAPA ID:07354 TP_WAIKINO GXP > WHANGAMATA SUB > HETHERINGTON RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC6271 | Isolate and Earth TC6271 to allow termination of LV cables only. A subcircuit for Whangamata CBD will be isolated at 2030 11.3.15 for Metal Clad Pillar replacement and cable upgrade. This is to mitigate LV outages in the CBD as experienced at New Years be | F3 | HETHERINGTON RD | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 110.0833 | 107.0833 | 8673.75 | 0.026493 | 0.00024741 | 2015-03-12 | B | 0.013247 | 0.0001237 | 2015 | 2015-03-12 | B | 81 | 0.026493 | 0.00024741
1 | 4033935 | 2015-03-12 07:19 | 2015-03-12 14:16 | 417.6 | 379 | 47038.15 | 0.14386 | 0.0011591 | Restore Supply on Device PU2 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5554E | 1.03pm Wes advised replaced tx 5554E. Was Feeder fault got feeder back on was only 1 transformer off which went back on at 1240 | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 124.1112 | 121.1112 | 45901.15 | 0.1402 | 0.0011576 | 2015-03-12 | C | 0.1402 | 0.0011576 | 2015 | 2015-03-12 | C | 379 | 0.1402 | 0.0011576
1 | 3876400 | 2015-03-12 08:31 | 2015-03-12 13:15 | 284.0833 | 9 | 2556.75 | 0.0078196 | 2.7526e-05 | NAPA ID:06247 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV WH887 | Replace poles and Wire on Hicks road. Works location: Hicks Rd. WO 10160005 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 284.0833 | 281.0833 | 2529.75 | 0.0077269 | 2.749e-05 | 2015-03-12 | B | 0.0038635 | 1.3745e-05 | 2015 | 2015-03-12 | B | 9 | 0.0077269 | 2.749e-05
1 | 4034963 | 2015-03-12 08:41 | 2015-03-12 10:47 | 125.7167 | 1 | 125.7167 | 0.00038449 | 3.0584e-06 | Restore Supply on Device TC3984 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP761 | 2X 8 Amp h/T Fuses. Swam hit Lines Fuses FP761. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 125.7167 | 122.7167 | 122.7167 | 0.00037483 | 3.0544e-06 | 2015-03-12 | C | 0.00037483 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00037483 | 3.0544e-06
1 | 3893947 | 2015-03-12 08:45 | 2015-03-12 14:11 | 326 | 13 | 4238 | 0.012962 | 3.9759e-05 | NAPA ID:06464 TP_KAITIMAKO GXP > WELCOME BAY SUB > KAITEMAKO RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | abs temp 20 | REPLACE POLES AND RECONDUCTOR HV FEEDER | F4 | KAITEMAKO RD | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 326 | 323 | 4199 | 0.012826 | 3.9708e-05 | 2015-03-12 | B | 0.0064128 | 1.9854e-05 | 2015 | 2015-03-12 | B | 13 | 0.012826 | 3.9708e-05
1 | 3822175 | 2015-03-12 08:51 | 2015-03-12 14:59 | 368.55 | 17 | 6265.35 | 0.019162 | 5.1993e-05 | NAPA ID:06170 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F0835 | Re-conductor between poles F0835 & F0854. Works location: Old Te Aroha Rd. WO 10163038 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 368.55 | 365.55 | 6214.35 | 0.018981 | 5.1925e-05 | 2015-03-12 | B | 0.0094906 | 2.5963e-05 | 2015 | 2015-03-12 | B | 17 | 0.018981 | 5.1925e-05
1 | 4015265 | 2015-03-12 09:01 | 2015-03-12 16:07 | 425.9667 | 75 | 31947.5 | 0.097709 | 0.00022938 | NAPA ID:07711 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10205 | Install a new pot and tail to 11kV cable feeding ABS 10204. Works location: Koputara Rd, Himatangi Beach. WO 10162444. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 425.9667 | 422.9667 | 31722.5 | 0.096894 | 0.00022908 | 2015-03-12 | B | 0.048447 | 0.00011454 | 2015 | 2015-03-12 | B | 75 | 0.096894 | 0.00022908
1 | 4035110 | 2015-03-12 09:22 | 2015-03-12 17:17 | 474.3333 | 1 | 2887.4333 | 0.008831 | 3.0584e-06 | Restore Supply on Device P2370 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P2375 | plz check 4035106 if related. Tx needs to be replaced - lightning strike P2375. 11.12am Chris leaving site, tested tx ht hv tx needs replacing. Replaced transformer and 2x 3a HV fuse links. nothing else repaired or replaced, adjacent assets up to Powerco | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2887.4333 | 2884.4333 | 2884.4333 | 0.0088103 | 3.0544e-06 | 2015-03-12 | C | 0.0088103 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0088103 | 3.0544e-06
1 | 3902144 | 2015-03-12 09:31 | 2015-03-12 13:36 | 245.65 | 23 | 5649.95 | 0.01728 | 7.0344e-05 | NAPA ID:06402 TP_HAWERA GXP > CAMBRIA SUB > TAWHITI RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 725070 | Replace seven 11kv poles 725070, 725101, 725104, 725114, 725116, 725120, 725127. Works location: Ararata Rd Hawera. WO 10141791 | F4 | TAWHITI RD | CAMBRIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 245.65 | 242.65 | 5580.95 | 0.017047 | 7.0252e-05 | 2015-03-12 | B | 0.0085233 | 3.5126e-05 | 2015 | 2015-03-12 | B | 23 | 0.017047 | 7.0252e-05
1 | 4037080 | 2015-03-12 11:33 | 2015-03-12 20:17 | 524.1667 | 2 | 1037.5 | 0.0031731 | 6.1168e-06 | Restore Supply on Device M1297 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718038 | plz check if 4038508 related. NEEDS TO CHANGE TX , SENT 2R REQUEST TO HUB 3.13pm Tallia calling to get brett bensley taken off site as he will not be replacing tx. Replaced 50kva transformer, 3x a6a HV fuses also replaced. | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 518.75 | 515.75 | 1031.5 | 0.0031506 | 6.1088e-06 | 2015-03-12 | C | 0.0031506 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.0031506 | 6.1088e-06
1 | 4037430 | 2015-03-12 11:36 | 2015-03-12 16:39 | 303.7333 | 339 | 8182 | 0.025024 | 0.0010368 | Restore Supply on Device TA8 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CB TA8 | replaced TX T5-188 due to lightning - Paul tried to sign this off with control but they were busy | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 24.1357 | 21.1357 | 7165 | 0.021885 | 0.0010354 | 2015-03-12 | C | 0.021885 | 0.0010355 | 2015 | 2015-03-12 | C | 339 | 0.021885 | 0.0010354
1 | 4039503 | 2015-03-12 12:08 | 2015-03-12 18:12 | 364 | 216 | 15580.4 | 0.047651 | 0.00066062 | Restore Supply on Device T31 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4647T | 11kV CB T31 tripped O/C E/F L/O. Due to blown transformer 4674T. Still requires Requires a replacment transformer 50KVA pole mount transformer. Replaced Transformer 2 Fuses Down Off 12-19 (12/03/15) ON 12-16 ( 13/03/15) | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 72.1315 | 69.1315 | 14932.4 | 0.04561 | 0.00065976 | 2015-03-12 | C | 0.04561 | 0.00065976 | 2015 | 2015-03-12 | C | 216 | 0.04561 | 0.00065976
1 | 4039883 | 2015-03-12 12:34 | 2015-03-12 18:28 | 353.65 | 1 | 353.65 | 0.0010816 | 3.0584e-06 | Restore Supply on Device T1425 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730392 | links#5874, pole#730392 - replaced 3x 3a hv fuse links. links#4909, pole#730382 - replaced 2x 6a hv fuse links. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | IHAIA RD | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 353.65 | 350.65 | 350.65 | 0.001071 | 3.0544e-06 | 2015-03-12 | C | 0.001071 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.001071 | 3.0544e-06
1 | 4039889 | 2015-03-12 12:35 | 2015-03-12 16:11 | 216.55 | 1 | 216.55 | 0.0006623 | 3.0584e-06 | Restore Supply on Device X1685 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1685 | 2x2amp hv tx fuses. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 216.55 | 213.55 | 213.55 | 0.00065227 | 3.0544e-06 | 2015-03-12 | C | 0.00065227 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00065227 | 3.0544e-06
1 | 4039895 | 2015-03-12 12:38 | 2015-03-12 20:14 | 456.3667 | 315 | 35700.1333 | 0.10919 | 0.0009634 | Restore Supply on Device 6427 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | on site | 2x tx W5210 & 5081E both tx blown and need replacing - checked weth Glen in Control he has oked for me to clear faultman from site and put through 2R request for 2x tx to be replaced Both transformers replaced | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 113.3338 | 110.3338 | 34755.1333 | 0.10616 | 0.00096214 | 2015-03-12 | C | 0.10616 | 0.00096214 | 2015 | 2015-03-12 | C | 315 | 0.10616 | 0.00096214
1 | 4040212 | 2015-03-12 12:40 | 2015-03-14 09:06 | 2665.4333 | 1 | 2665.4333 | 0.008152 | 3.0584e-06 | Restore Supply on Device M1195 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M1195 | 8.03 - Morgan from Energy Direct advise customer still no power. 8.06am - advised smc. 2x2Amp Links replaced at transformer M1195. | F4 | AUROA | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2665.4333 | 2662.4333 | 2662.4333 | 0.0081322 | 3.0544e-06 | 2015-03-12 | C | 0.0081322 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0081322 | 3.0544e-06
1 | 4047795 | 2015-03-12 13:06 | 2015-03-12 20:53 | 467.15 | 5 | 1301.05 | 0.0039792 | 1.5292e-05 | Restore Supply on Device X1690 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fuse#171 | Possibly related to 4039889 - spoke with Te Maire and advised him of this job and he has advised that this job will prob not be related to oms 4039889, have sent through crew request and advised the hub - lightning is the cause of this possibly. Transform | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 260.21 | 257.21 | 1286.05 | 0.0039281 | 1.5272e-05 | 2015-03-12 | C | 0.0039281 | 1.5272e-05 | 2015 | 2015-03-12 | C | 5 | 0.0039281 | 1.5272e-05
1 | 4047813 | 2015-03-12 13:09 | 2015-03-12 21:23 | 493.2833 | 2 | 973.4667 | 0.0029773 | 6.1168e-06 | Restore Supply on Device W5090 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | W5090 | Lightning bolt struck the power pole & things are hanging off the power pole. 1.13pm adv Shan at svs hub & control. Advised Shannon this is MacAlpine Road Hawera, Not Alpine road. 2 R request to replace TX. Check if oms 405226 is related. Replaced transf | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 486.7333 | 483.7333 | 967.4667 | 0.0029551 | 6.1088e-06 | 2015-03-12 | C | 0.0029551 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.0029551 | 6.1088e-06
1 | 4048045 | 2015-03-12 13:40 | 2015-03-12 19:09 | 329 | 1264 | 394702.7167 | 1.2072 | 0.0038658 | Restore Supply on Device N1210 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N1210 | Lightning storm in the area. LOS to both Ngariki and Pungarehu Substations. Perfromance Review 456981 | F4 | NGARIKI RD | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 312.2648 | 309.2648 | 390910.7167 | 1.194 | 0.0038608 | 2015-03-12 | C | 1.194 | 0.0038608 | 2015 | 2015-03-12 | C | 1264 | 1.194 | 0.0038608
1 | 4049941 | 2015-03-12 14:42 | 2015-03-14 00:07 | 2004.7167 | 3 | 2996.05 | 0.0091632 | 9.1753e-06 | Restore Supply on Device M4125 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M4125 | Blown tx M4125 needs to be replaced. transformer verified. check if oms 4055331 and 4060816 is related. | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 998.6833 | 995.6833 | 2987.05 | 0.0091237 | 9.1633e-06 | 2015-03-12 | C | 0.0091237 | 9.163e-06 | 2015 | 2015-03-12 | C | 3 | 0.0091237 | 9.1633e-06
1 | 4053329 | 2015-03-12 15:00 | 2015-03-12 22:24 | 443.7167 | 16 | 5680 | 0.017372 | 4.8935e-05 | Restore Supply on Device WH880 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | W5090 | Unable to close out. PAUL DOUGLAS to resolve. NCTL Replaced transformer W5090 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 355 | 352 | 5632 | 0.017203 | 4.8871e-05 | 2015-03-12 | C | 0.017203 | 4.8871e-05 | 2015 | 2015-03-12 | C | 16 | 0.017203 | 4.8871e-05
1 | 4051558 | 2015-03-12 15:30 | 2015-03-14 14:30 | 2819.8667 | 1 | 2819.8667 | 0.0086243 | 3.0584e-06 | Restore Supply on Device M2215 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | m2215 | 14/03 1.41pm - rung customer but no answer or voicemail 14/03 1.45pm - advise smc. 14/03 2.30pm - FM advise: signed off with Control before. replaced 3 amp ht fuse due to lightning. tx: can't recall the tx number now but tx m2215 sounds like this may be | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2819.8667 | 2816.8667 | 2816.8667 | 0.0086039 | 3.0544e-06 | 2015-03-12 | C | 0.0086039 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0086039 | 3.0544e-06
1 | 4051801 | 2015-03-12 15:34 | 2015-03-12 18:44 | 190.5333 | 20 | 3288.0167 | 0.010056 | 6.1168e-05 | Restore Supply on Device N30 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N30 | Tx T5/78. Two Fuses found blown at Fuses N30 - Lightening in area - used 2 x 6amp | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 164.4008 | 161.4008 | 3228.0167 | 0.0098597 | 6.1088e-05 | 2015-03-12 | C | 0.0098597 | 6.1088e-05 | 2015 | 2015-03-12 | C | 20 | 0.0098597 | 6.1088e-05
1 | 4051805 | 2015-03-12 15:40 | 2015-03-12 17:28 | 108 | 1104 | 99332.15 | 0.3038 | 0.0033765 | Restore Supply on Device CB2862 | 33000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | UNKNOWN - NO FAULT FOUND | Kaponga Sub | 33kV CB 2862 tripped L/O O/C due to lightning striking Cardiff equipment. All power restored, no damage found. Performance Review 456982 | F1, F2, F3 | CARDIFF NORTH 33KV | TP_STRATFORD | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 89.9748 | 86.9748 | 96020.15 | 0.29329 | 0.0033721 | 2015-03-12 | C | 0.29329 | 0.0033721 | 2015 | 2015-03-12 | C | 1104 | 0.29329 | 0.0033721
1 | 4052983 | 2015-03-12 15:55 | 2015-03-13 13:40 | 1305.4167 | 3 | 3916.25 | 0.011978 | 9.1753e-06 | Restore Supply on Device 5841 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2409T | Transformer 3080T & 2409T (both Pad mount 30KVA) destroyed by lightning, Both require replacment and transformer 2409T suspect and to be inspected both left isolated ... Customer advised. Phil was onsite and sorted issues on 12/03/15. Both Transformers I | F1 | ORIGIN 2 | WAIHAPA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1305.4167 | 1302.4167 | 3907.25 | 0.011934 | 9.1633e-06 | 2015-03-12 | C | 0.011934 | 9.163e-06 | 2015 | 2015-03-12 | C | 3 | 0.011934 | 9.1633e-06
1 | 4052987 | 2015-03-12 15:55 | 2015-03-12 18:17 | 142.1167 | 270 | 33371.5 | 0.10206 | 0.00082577 | Restore Supply on Device WH1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | WH1 | feeder restored but HV UG cable from sub blown up, 2R to repair cable tomorrow, back feeds in place. Completed to remove active ICPs from system | F4 | MANUTAHI | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 123.5981 | 120.5981 | 32561.5 | 0.099457 | 0.00082469 | 2015-03-12 | C | 0.099457 | 0.00082469 | 2015 | 2015-03-12 | C | 270 | 0.099457 | 0.00082469
1 | 4053350 | 2015-03-12 16:12 | 2015-03-12 21:16 | 303.7667 | 1 | 303.7667 | 0.00092905 | 3.0584e-06 | Restore Supply on Device T5440 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | nn | cld be related to 4047827 related to OMS 4047827, power restorered - replaced 3a hv fuse at transformer, | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 303.7667 | 300.7667 | 300.7667 | 0.00091867 | 3.0544e-06 | 2015-03-12 | C | 0.00091867 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00091867 | 3.0544e-06
1 | 4053498 | 2015-03-12 16:35 | 2015-03-14 10:38 | 2522.5667 | 2 | 5045.1333 | 0.01543 | 6.1168e-06 | Restore Supply on Device 1600 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1600 | check if oms4053509 and 4053509 and 4056221is related. 14/3 10.35am - power restore under oms 4053509 but Control did not link or sign this job off and Dispatch did not follow up. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2522.5667 | 2519.5667 | 5039.1333 | 0.015392 | 6.1088e-06 | 2015-03-12 | C | 0.015392 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.015392 | 6.1088e-06
1 | 4053509 | 2015-03-12 16:38 | 2015-03-13 16:04 | 1406.8333 | 1 | 1406.8333 | 0.0043027 | 3.0584e-06 | Restore Supply on Device 783 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | trtansformer1401 | Found @ 529 Upper Pitone road transformer 1401 blown - replaced Tx's: 1600 - 2x 3amp hv fuse 784 - 2x 3amp hv fuse 783 - 1x 3amp hv fuse 790 - 2x 3amp hv fuse all due to lightning all ppty's affected were on Upper Pitone road full power restore | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1406.8333 | 1403.8333 | 1403.8333 | 0.0042879 | 3.0544e-06 | 2015-03-12 | C | 0.0042879 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0042879 | 3.0544e-06
1 | 4053551 | 2015-03-12 17:17 | 2015-03-12 23:39 | 382.45 | 16 | 3817.45 | 0.011675 | 4.8935e-05 | Restore Supply on Device X291 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 806754 | Removed trees from lines between poles 806753 & 806754. NDR 41920. Karl Rodgers attended. | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 238.5906 | 235.5906 | 3769.45 | 0.011513 | 4.8871e-05 | 2015-03-12 | C | 0.011513 | 4.8871e-05 | 2015 | 2015-03-12 | C | 16 | 0.011513 | 4.8871e-05
1 | 4053570 | 2015-03-12 17:30 | 2015-03-14 12:32 | 2582.6167 | 6 | 7709.6833 | 0.023579 | 1.8351e-05 | Restore Supply on Device 5011E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5011E | Retailer follow up sent to svs hub 5.32pm. Blown transformer 5011E, to be replaced tomorrow. Craig Brogden attended. Replaced Transformer (Dennis Embling attended). | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1284.9472 | 1281.9472 | 7691.6833 | 0.023494 | 1.8327e-05 | 2015-03-12 | C | 0.023494 | 1.8327e-05 | 2015 | 2015-03-12 | C | 6 | 0.023494 | 1.8327e-05
1 | 4053574 | 2015-03-12 17:33 | 2015-03-12 18:57 | 83.9167 | 1 | 83.9167 | 0.00025665 | 3.0584e-06 | Restore Supply on Device T3/49 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3/49 | Replaced 3 X HV Fuses due to lightning | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 83.9167 | 80.9167 | 80.9167 | 0.00024715 | 3.0544e-06 | 2015-03-12 | C | 0.00024715 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00024715 | 3.0544e-06
1 | 4053582 | 2015-03-12 17:39 | 2015-03-12 19:21 | 102.8167 | 2 | 201.4333 | 0.00061607 | 6.1168e-06 | Restore Supply on Device T3/227 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3/227 | check if oms 4054107 is related. Replaced 2x 6a hv fuse links at transformer. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | MT STEWART | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 100.7167 | 97.7167 | 195.4333 | 0.00059694 | 6.1088e-06 | 2015-03-12 | C | 0.00059694 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.00059694 | 6.1088e-06
1 | 4054110 | 2015-03-12 17:50 | 2015-03-12 22:53 | 303.1333 | 1 | 303.1333 | 0.00092711 | 3.0584e-06 | Restore Supply on Device 3345T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3345T | check if oms 4055294 is related replaced 3a hv fuse link due to weather. nothing else repaired or replaced, adjacent assets up to powerco standard. | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 303.1333 | 300.1333 | 300.1333 | 0.00091673 | 3.0544e-06 | 2015-03-12 | C | 0.00091673 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00091673 | 3.0544e-06
1 | 4054332 | 2015-03-12 18:01 | 2015-03-13 17:24 | 1402.5667 | 1 | 1402.5667 | 0.0042896 | 3.0584e-06 | Restore Supply on Device T5120 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Transformer T5120 | Possibly related to oms 4055258. Tx has blown T5120. ON 17-23 ( 13/03/15 ) | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1402.5667 | 1399.5667 | 1399.5667 | 0.0042749 | 3.0544e-06 | 2015-03-12 | C | 0.0042749 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0042749 | 3.0544e-06
1 | 4055249 | 2015-03-12 18:09 | 2015-03-12 20:56 | 166.9333 | 1 | 166.9333 | 0.00051055 | 3.0584e-06 | Restore Supply on Device P1410 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | part of earlier feeder fault | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 166.9333 | 163.9333 | 163.9333 | 0.00050072 | 3.0544e-06 | 2015-03-12 | C | 0.00050072 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00050072 | 3.0544e-06
1 | 4055258 | 2015-03-12 18:11 | 2015-03-12 22:34 | 262.5667 | 1 | 262.5667 | 0.00080304 | 3.0584e-06 | Restore Supply on Device T5098 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5098 | replaced hv fuse links x3 | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 262.5667 | 259.5667 | 259.5667 | 0.00079283 | 3.0544e-06 | 2015-03-12 | C | 0.00079283 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00079283 | 3.0544e-06
1 | 4055263 | 2015-03-12 18:12 | 2015-03-13 12:38 | 1106.2833 | 1 | 1106.2833 | 0.0033835 | 3.0584e-06 | Restore Supply on Device T5175 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA806 | Possibly related to oms 4055258. REPLACED 3 X 3 AMP DUE TO, LIGHTNING. 3 X SLEEVES AS HAD TO CUT JUMPER TO ISOLATE TX. No other assets repaired or replaced. Adjacent assets ok. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1106.2833 | 1103.2833 | 1103.2833 | 0.0033699 | 3.0544e-06 | 2015-03-12 | C | 0.0033699 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0033699 | 3.0544e-06
1 | 4055272 | 2015-03-12 18:21 | 2015-03-13 07:38 | 797.1333 | 1 | 797.1333 | 0.002438 | 3.0584e-06 | Restore Supply on Device X973 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 806754 | Related to job 4053551: "Removed trees from lines between poles 806753 & 806754" | F3 | HUNTERVILLE 22KV | RATA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 797.1333 | 794.1333 | 794.1333 | 0.0024256 | 3.0544e-06 | 2015-03-12 | C | 0.0024256 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0024256 | 3.0544e-06
1 | 4055308 | 2015-03-12 18:38 | 2015-03-13 16:03 | 1285.2833 | 1 | 1285.2833 | 0.0039309 | 3.0584e-06 | Restore Supply on Device 1401 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformers After Storm | possibly related to oms 4053498 | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1285.2833 | 1282.2833 | 1282.2833 | 0.0039166 | 3.0544e-06 | 2015-03-12 | C | 0.0039166 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0039166 | 3.0544e-06
1 | 4055314 | 2015-03-12 18:38 | 2015-03-14 13:12 | 2553.6667 | 5 | 7752.2667 | 0.02371 | 1.5292e-05 | Restore Supply on Device T5320 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | t5320 | T5320 pole#367147 - 30kva transformer to be replaced, crew to attend and replace. FM advise: replaced tx T5320. cause: lightning earlier this week. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1550.4533 | 1547.4533 | 7737.2667 | 0.023633 | 1.5272e-05 | 2015-03-12 | C | 0.023633 | 1.5272e-05 | 2015 | 2015-03-12 | C | 5 | 0.023633 | 1.5272e-05
1 | 4056319 | 2015-03-12 18:49 | 2015-03-13 01:15 | 386 | 1459 | 75256.5167 | 0.23017 | 0.0044622 | Restore Supply on Device 316 | 33000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | UNKNOWN - NO FAULT FOUND | 312 | 33kV CB 312 tripped Red Phase O/C L/O | F1, F2, F3 | WAIHOU312-TAHUNA 33KV | TP_WAIHOU | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 51.5809 | 48.5809 | 70879.5167 | 0.2165 | 0.0044564 | 2015-03-12 | C | 0.2165 | 0.0044564 | 2015 | 2015-03-12 | C | 1459 | 0.2165 | 0.0044564
1 | 4055335 | 2015-03-12 18:49 | 2015-03-13 19:35 | 1485.7167 | 186 | 40211.65 | 0.12298 | 0.00056887 | Restore Supply on Device RP5 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K2244 | Recloser RP05 ( TAH 3 ) tripped E/F, L/O. Reclosed & held but TP Waihou CB 312 tripped B & R Ph O/C, L/O offloading Tahuna Sub OMS 4056319 ( cause unknown heavy rain at time of tripping ) 33WHU - TAH line patrolled no fault found Tahuna Sub restored to se | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 216.1917 | 213.1917 | 39653.65 | 0.12112 | 0.00056812 | 2015-03-12 | C | 0.12112 | 0.00056812 | 2015 | 2015-03-12 | C | 186 | 0.12112 | 0.00056812
1 | 4055966 | 2015-03-12 18:54 | 2015-03-13 20:18 | 1524.1833 | 1 | 1524.1833 | 0.0046616 | 3.0584e-06 | Restore Supply on Device M2257 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2257 | Rosita calling for update - called Tallia and she advised they are working through the jobs no eta. Replaced 2x 2amp HV links at M2257. Nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1524.1833 | 1521.1833 | 1521.1833 | 0.0046463 | 3.0544e-06 | 2015-03-12 | C | 0.0046463 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0046463 | 3.0544e-06
1 | 4073414 | 2015-03-12 19:03 | 2015-03-13 00:02 | 299.5 | 2 | 599 | 0.001832 | 6.1168e-06 | Restore Supply on Device 5006E | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 5006E | 15/03 3.32pm - advise smc that Scott still onsite. smc will ring Dennis and advise Dispatch. Dennis and team replaced many tx's in the area on Saturday 14/3. 15/03 4.01 pm - smc advise: left message on Dennis's phone, he is not on-call today and is there | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 299.5 | 296.5 | 593 | 0.0018113 | 6.1088e-06 | 2015-03-12 | C | 0.0018113 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.0018113 | 6.1088e-06
1 | 4055986 | 2015-03-12 19:04 | 2015-03-13 07:22 | 737.8833 | 1 | 737.8833 | 0.0022568 | 3.0584e-06 | Restore Supply on Device N2250 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | n2250 | possibly related to oms 4055995. 2 x 3 amp hv fuses replaced. No other assets repaired or replaced. Adjacent assets ok. | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 737.8833 | 734.8833 | 734.8833 | 0.0022446 | 3.0544e-06 | 2015-03-12 | C | 0.0022446 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0022446 | 3.0544e-06
1 | 4055992 | 2015-03-12 19:06 | 2015-03-13 17:11 | 1324.9333 | 6 | 3219.2167 | 0.0098457 | 1.8351e-05 | Restore Supply on Device N2165 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N2165 | check if oms 4061001 is related, same tranny. Paul fitzpatrick attended oms 4064018 and confirmed tx N2165 needs replacing. Put through 2R request to get tx replaced. Transformer replaced with 50kVa N2165. Nothing else repaired or replaced, adjacent asse | F4 | RAHOTU | NGARIKI SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 536.5361 | 533.5361 | 3201.2167 | 0.0097779 | 1.8327e-05 | 2015-03-12 | C | 0.0097779 | 1.8327e-05 | 2015 | 2015-03-12 | C | 6 | 0.0097779 | 1.8327e-05
1 | 4055995 | 2015-03-12 19:07 | 2015-03-12 20:31 | 84.65 | 1 | 84.65 | 0.0002589 | 3.0584e-06 | Restore Supply on Device 5143E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | pole | check if oms 4055992 and oms 4055986 are related. Replaced 2 X3a hV fuses. | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 84.65 | 81.65 | 81.65 | 0.00024939 | 3.0544e-06 | 2015-03-12 | C | 0.00024939 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00024939 | 3.0544e-06
1 | 4056221 | 2015-03-12 19:16 | 2015-03-13 16:16 | 1259.3167 | 1 | 1259.3167 | 0.0038515 | 3.0584e-06 | Restore Supply on Device 790 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790 | Possibly related to oms 4053498. fuses hanging out. 2x3amp hv fuses at tx 790. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1259.3167 | 1256.3167 | 1256.3167 | 0.0038373 | 3.0544e-06 | 2015-03-12 | C | 0.0038373 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0038373 | 3.0544e-06
1 | 4056229 | 2015-03-12 19:18 | 2015-03-13 10:46 | 928.45 | 1 | 928.45 | 0.0028396 | 3.0584e-06 | Restore Supply on Device T5165 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5165 | Possibly related to oms 4055258. 2X Fuses after Lightning. Off 19-17 ( 12/03/15) on 10-43(13/03/15). | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 928.45 | 925.45 | 925.45 | 0.0028267 | 3.0544e-06 | 2015-03-12 | C | 0.0028267 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0028267 | 3.0544e-06
1 | 4056244 | 2015-03-12 19:23 | 2015-03-13 09:37 | 854.1333 | 1 | 854.1333 | 0.0026123 | 3.0584e-06 | Restore Supply on Device 3477T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 735098 | 2 X 6 AMP FUSES DUE TO LIGHTNING. No other assets repaired or replaced. Adjacent assets ok. Email sent to Jo to calculate possible SAIDI component. | F4 | MAHOE | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 854.1333 | 851.1333 | 851.1333 | 0.0025997 | 3.0544e-06 | 2015-03-12 | C | 0.0025997 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0025997 | 3.0544e-06
1 | 4056249 | 2015-03-12 19:25 | 2015-03-13 00:38 | 313.1667 | 1 | 313.1667 | 0.0009578 | 3.0584e-06 | Restore Supply on Device T2286 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7298 | replace 2X HV Fuses | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 313.1667 | 310.1667 | 310.1667 | 0.00094738 | 3.0544e-06 | 2015-03-12 | C | 0.00094738 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00094738 | 3.0544e-06
1 | 4056274 | 2015-03-12 19:31 | 2015-03-13 14:14 | 1122.6333 | 3 | 3367.9 | 0.0103 | 9.1753e-06 | Restore Supply on Device 4244T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4244T | Chris Katene advises 11kV Transformer 4244T is blown, requires replacement. 50KVA Replace & Relivened Off 19-31 (12/03/15) On 14-12 ( 13/03/15) | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1122.6333 | 1119.6333 | 3358.9 | 0.01026 | 9.1633e-06 | 2015-03-12 | C | 0.01026 | 9.163e-06 | 2015 | 2015-03-12 | C | 3 | 0.01026 | 9.1633e-06
1 | 4056302 | 2015-03-12 19:35 | 2015-03-13 16:13 | 1237.95 | 2 | 2475.9 | 0.0075723 | 6.1168e-06 | Restore Supply on Device 3288T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3288T | Chris Katene advises transformer 3288T is blown due to a lightning strike. 15KVA Off at 19-34 (12/03/150 On at 16-10 (13/03/15) | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1237.95 | 1234.95 | 2469.9 | 0.0075441 | 6.1088e-06 | 2015-03-12 | C | 0.0075441 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.0075441 | 6.1088e-06
1 | 4060789 | 2015-03-12 19:58 | 2015-03-13 13:11 | 1033.2667 | 1 | 1033.2667 | 0.0031602 | 3.0584e-06 | Restore Supply on Device 3194T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 709028 X 2AM | 11.13 Holly calling from Meridian wanting eta update.. called svs hub and Tallia advised 2 faultman working in the area and are working their way through jobs. 2 X 2 AMP FUSES DUE TO LIGHTNING. No other assets repaired or replaced. Adjacent assets ok. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1033.2667 | 1030.2667 | 1030.2667 | 0.0031469 | 3.0544e-06 | 2015-03-12 | C | 0.0031469 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0031469 | 3.0544e-06
1 | 4060816 | 2015-03-12 20:20 | 2015-03-13 15:41 | 1160.3833 | 2 | 1160.3833 | 0.0035489 | 6.1168e-06 | Restore Supply on Device M4095 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 718346 | possibly related to oms 4049941 Paul has confirmed that this job was related to oms 4055331 where he replaced hv fuse | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 580.1917 | 577.1917 | 1154.3833 | 0.003526 | 6.1088e-06 | 2015-03-12 | C | 0.003526 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.003526 | 6.1088e-06
1 | 4060821 | 2015-03-12 20:21 | 2015-03-14 11:49 | 2368.15 | 1 | 2368.15 | 0.0072428 | 3.0584e-06 | Restore Supply on Device 5435E | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5435E | possibly related to oms 4055258. 2R required to replace transformer 5435E (100kVA 3 Phase). Site location: 153 Little Oeo Road. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 2368.15 | 2365.15 | 2365.15 | 0.0072242 | 3.0544e-06 | 2015-03-12 | C | 0.0072242 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0072242 | 3.0544e-06
1 | 4060836 | 2015-03-12 20:29 | 2015-03-13 07:28 | 659.1 | 1 | 659.1 | 0.0020158 | 3.0584e-06 | Restore Supply on Device 4987T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4987t | possibly related to oms 4060802 had full power on arrival but found at tx 2628t fuses out reloaded No other assets repaired or replaced Adjacent assets ok | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 659.1 | 656.1 | 656.1 | 0.002004 | 3.0544e-06 | 2015-03-12 | C | 0.002004 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.002004 | 3.0544e-06
1 | 4060852 | 2015-03-12 20:40 | 2015-03-13 12:29 | 949.2333 | 1 | 949.2333 | 0.0029032 | 3.0584e-06 | Restore Supply on Device 2885T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2885T | Replaced Transformer after Lightning Storm. | F5 | CLIMIE RD | CARDIFF SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 949.2333 | 946.2333 | 946.2333 | 0.0028902 | 3.0544e-06 | 2015-03-12 | C | 0.0028902 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.0028902 | 3.0544e-06
1 | 4060912 | 2015-03-12 21:00 | 2015-03-12 23:13 | 132.0833 | 1 | 132.0833 | 0.00040397 | 3.0584e-06 | Restore Supply on Device T5/78 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | transformer T5-78 | replaced 2 X 6a HV Fuses, | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 132.0833 | 129.0833 | 129.0833 | 0.00039428 | 3.0544e-06 | 2015-03-12 | C | 0.00039427 | 3.054e-06 | 2015 | 2015-03-12 | C | 1 | 0.00039428 | 3.0544e-06
1 | 4060922 | 2015-03-12 21:08 | 2015-03-14 13:50 | 2441.5667 | 3 | 2792.5833 | 0.0085409 | 9.1753e-06 | Restore Supply on Device T5090 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | t5090 | check if oms 4060784 is related. 14/03 8.10am - Kensi from Genesis phoned to advise customer is still having part power. 14/03 10.55am - unlocked oms 4060784 to roll up to this job as it was still in crews required since 12/03. Replaced 30 kVa tx. hit by | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 930.8611 | 927.8611 | 2783.5833 | 0.0085022 | 9.1633e-06 | 2015-03-12 | C | 0.0085022 | 9.163e-06 | 2015 | 2015-03-12 | C | 3 | 0.0085022 | 9.1633e-06
1 | 4060934 | 2015-03-12 21:14 | 2015-03-13 16:02 | 1127.5167 | 48 | 4088.5167 | 0.012504 | 0.0001468 | Restore Supply on Device 4190T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4190T | HV fuse carrier requires replacement. Bucket truck required. DDO's to be replaced at transformer 4190T. Scott van Dyk attended. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 85.1774 | 82.1774 | 3944.5167 | 0.012048 | 0.00014661 | 2015-03-12 | C | 0.012048 | 0.00014661 | 2015 | 2015-03-12 | C | 48 | 0.012048 | 0.00014661
1 | 4060956 | 2015-03-12 21:21 | 2015-03-13 18:02 | 1241.55 | 2 | 1839.2 | 0.005625 | 6.1168e-06 | Restore Supply on Device P4055 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P4055 | Check if this affects 4064206. Emailed svs hub for update. Reliven Used 3 X3 amp Fuses On at 17-58. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 919.6 | 916.6 | 1833.2 | 0.0055994 | 6.1088e-06 | 2015-03-12 | C | 0.0055994 | 6.109e-06 | 2015 | 2015-03-12 | C | 2 | 0.0055994 | 6.1088e-06
1 | 4061157 | 2015-03-13 06:20 | 2015-03-14 12:28 | 1808.5167 | 2 | 3027.4333 | 0.0092592 | 6.1168e-06 | Restore Supply on Device T5435 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T5435 | Blown tx 30kva T5435. Transformer verified Replaced Transformer | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1513.7167 | 1510.7167 | 3021.4333 | 0.0092287 | 6.1088e-06 | 2015-03-13 | C | 0.0092287 | 6.109e-06 | 2015 | 2015-03-13 | C | 2 | 0.0092287 | 6.1088e-06
1 | 4062496 | 2015-03-13 07:18 | 2015-03-14 10:57 | 1659.5 | 1 | 1659.5 | 0.0050755 | 3.0584e-06 | Restore Supply on Device W5235 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | W5235 | Transformer blown to be replaced tomorrow. Replaced transformer W5235. 30 kVA transformer. All power restored 10:40am. Cause: lightning. Craig Brogden and Dennis Embling attended. | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1659.5 | 1656.5 | 1656.5 | 0.0050597 | 3.0544e-06 | 2015-03-13 | C | 0.0050597 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0050597 | 3.0544e-06
1 | 4062500 | 2015-03-13 07:21 | 2015-03-13 16:17 | 535.9167 | 4 | 1546.75 | 0.0047306 | 1.2234e-05 | Restore Supply on Device 790 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790 | 2x3amp hv fuses at tx 790. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard | F4 | INLAND COAST | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 386.6875 | 383.6875 | 1534.75 | 0.0046878 | 1.2218e-05 | 2015-03-13 | C | 0.0046878 | 1.2218e-05 | 2015 | 2015-03-13 | C | 4 | 0.0046878 | 1.2218e-05
1 | 4062509 | 2015-03-13 07:25 | 2015-03-13 10:00 | 155.0333 | 1 | 155.0333 | 0.00047416 | 3.0584e-06 | Restore Supply on Device T2286 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2286 798864 | t2286 798864 =- 3x 3amp ddo fuse elements due to lightening. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 155.0333 | 152.0333 | 152.0333 | 0.00046437 | 3.0544e-06 | 2015-03-13 | C | 0.00046437 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.00046437 | 3.0544e-06
1 | 4062529 | 2015-03-13 07:41 | 2015-03-13 20:27 | 765.75 | 1 | 765.75 | 0.002342 | 3.0584e-06 | Restore Supply on Device P4035 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710854 | replaceed 3x 3a hv fuse links. nothing else repaired or replaced, adjacent assets up to powerco standard. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 765.75 | 762.75 | 762.75 | 0.0023298 | 3.0544e-06 | 2015-03-13 | C | 0.0023298 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0023298 | 3.0544e-06
1 | 4062588 | 2015-03-13 08:03 | 2015-03-13 11:54 | 231.3167 | 1 | 231.3167 | 0.00070746 | 3.0584e-06 | Restore Supply on Device T5180 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6522 | 2x 3amp hv fuses. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 231.3167 | 228.3167 | 228.3167 | 0.00069738 | 3.0544e-06 | 2015-03-13 | C | 0.00069738 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.00069738 | 3.0544e-06
1 | 3885980 | 2015-03-13 08:36 | 2015-03-13 14:46 | 370 | 125 | 46250 | 0.14145 | 0.0003823 | NAPA ID:07102 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8247 | Replace various network poles in work area. Works location: Fitzroy Rd. WO 300002060. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 370 | 367 | 45875 | 0.14012 | 0.0003818 | 2015-03-13 | B | 0.070061 | 0.0001909 | 2015 | 2015-03-13 | B | 125 | 0.14012 | 0.0003818
1 | 3893128 | 2015-03-13 09:01 | 2015-03-13 14:56 | 355 | 71 | 25205 | 0.077088 | 0.00021715 | NAPA ID:06471 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF3-010 | REPLACE POLES AND ARMS ALONG MCLAREN FALLS ROAD. Works location: McLaren Falls Road. WO 30000217. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 355 | 352 | 24992 | 0.076336 | 0.00021686 | 2015-03-13 | B | 0.038168 | 0.00010843 | 2015 | 2015-03-13 | B | 71 | 0.076336 | 0.00021686
1 | 3799034 | 2015-03-13 09:15 | 2015-03-13 15:16 | 360.75 | 46 | 16594.5 | 0.050753 | 0.00014069 | NAPA ID:05951 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC788 | To replace 11kV and LV cross arms on Chepmell Road Morrinsville. Works location: Chepmell Rd. WO 30000212. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 360.75 | 357.75 | 16456.5 | 0.050265 | 0.0001405 | 2015-03-13 | B | 0.025133 | 7.0252e-05 | 2015 | 2015-03-13 | B | 46 | 0.050265 | 0.0001405
1 | 4064662 | 2015-03-13 09:24 | 2015-03-13 15:41 | 377.1333 | 1 | 377.1333 | 0.0011534 | 3.0584e-06 | Restore Supply on Device X2946 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | x1693, x1703. | REPLACED 2 X 3 AMP HV TX FUSES DUE TO LIGHTNING. ALSO AT 665 MORIKAU RD FUSES OUT AT TX onsite at 1.40pm: offsite 2.13pm. 2x 3amp hv fuse pole 777482 x1703. Otaranoho road. x1693 - 2x 3a hv fuses. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 377.1333 | 374.1333 | 374.1333 | 0.0011428 | 3.0544e-06 | 2015-03-13 | C | 0.0011428 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0011428 | 3.0544e-06
1 | 3915601 | 2015-03-13 09:31 | 2015-03-13 12:45 | 194.1167 | 5 | 970.5833 | 0.0029685 | 1.5292e-05 | NAPA ID:06153 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2385 | To replace 11kV cross arms beyond FC2385. This OMS Parent ID 3915601 supersedes OMS Parent ID 3715284 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 194.1167 | 191.1167 | 955.5833 | 0.0029188 | 1.5272e-05 | 2015-03-13 | B | 0.0014594 | 7.636e-06 | 2015 | 2015-03-13 | B | 5 | 0.0029188 | 1.5272e-05
1 | 3885710 | 2015-03-13 10:00 | 2015-03-13 11:22 | 81.6667 | 7 | 571.6667 | 0.0017484 | 2.1409e-05 | NAPA ID:07144 TP_GREYTOWN GXP > TUHITARATA SUB > KUMENGA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7300 | Resag 11kv lines causing trippings. Works location: Wairio Rd, South Wairarapa. WO 10161257 | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 81.6667 | 78.6667 | 550.6667 | 0.001682 | 2.1381e-05 | 2015-03-13 | B | 0.00084099 | 1.069e-05 | 2015 | 2015-03-13 | B | 7 | 0.001682 | 2.1381e-05
1 | 4070788 | 2015-03-13 11:26 | 2015-03-13 14:25 | 179.45 | 1 | 179.45 | 0.00054883 | 3.0584e-06 | Restore Supply on Device 3672T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 759381 | 2x 6amp hv fuse due to lightning. Pole 759381, full power restored. Nothing else repaired or replaced. Adjacent assets - ok. | F3 | TOKO | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 179.45 | 176.45 | 176.45 | 0.00053895 | 3.0544e-06 | 2015-03-13 | C | 0.00053895 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.00053895 | 3.0544e-06
1 | 4071056 | 2015-03-13 11:45 | 2015-03-14 13:45 | 1559.5333 | 2 | 2927.1333 | 0.0089524 | 6.1168e-06 | Restore Supply on Device 4267T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5616 | 14/03 10.59am - Kensi from genesis advise customer still power at cowshed, cant feed animals and no water. 14/03 11.03am - advise smc that job still open and dispatch has taken the parent job away as it was never signed off any way. 2x 2 Amp Fuses. | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1463.5667 | 1460.5667 | 2921.1333 | 0.0089224 | 6.1088e-06 | 2015-03-13 | C | 0.0089224 | 6.109e-06 | 2015 | 2015-03-13 | C | 2 | 0.0089224 | 6.1088e-06
1 | 4071479 | 2015-03-13 12:43 | 2015-03-13 21:20 | 517.1 | 1 | 517.1 | 0.0015815 | 3.0584e-06 | Restore Supply on Device 5223E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5223E | Replaced 3x 3a hv fuse links at transformer 5223E nothing else repaired or replaced, adjacent assets up to Powerco standard. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 517.1 | 514.1 | 514.1 | 0.0015703 | 3.0544e-06 | 2015-03-13 | C | 0.0015703 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0015703 | 3.0544e-06
1 | 4073194 | 2015-03-13 16:01 | 2015-03-14 11:22 | 1161.1833 | 1 | 1161.1833 | 0.0035514 | 3.0584e-06 | Restore Supply on Device T5430 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5430 | Blown tx confirmed by Paul Fitzpatrick. Transformer verified. 14/3 11.20am - e-map closed at 11.14am and had to lock back in and out and could only restore it now. Replaced tx T5430 due to lightning during the week. | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1161.1833 | 1158.1833 | 1158.1833 | 0.0035376 | 3.0544e-06 | 2015-03-13 | C | 0.0035376 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0035376 | 3.0544e-06
1 | 4073334 | 2015-03-13 16:49 | 2015-03-14 12:25 | 1176 | 2 | 1177.1667 | 0.0036003 | 6.1168e-06 | Restore Supply on Device 4687T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4687T | Customer is going to talk to fault crew regarding repositioning Tx to allow easier access. Customer does have a modified water supply to provide water to animals for tonight. Happy to wait until tomorrow. Customer : Shaun Pattenson 0274874345. Advised s | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 588.5833 | 585.5833 | 1171.1667 | 0.0035772 | 6.1088e-06 | 2015-03-13 | C | 0.0035772 | 6.109e-06 | 2015 | 2015-03-13 | C | 2 | 0.0035772 | 6.1088e-06
1 | 4073339 | 2015-03-13 16:52 | 2015-03-14 10:25 | 1052.85 | 6 | 1166.9333 | 0.003569 | 1.8351e-05 | Restore Supply on Device 3730T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3730T | 2x 3 Amp Links. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 194.4889 | 191.4889 | 1148.9333 | 0.0035093 | 1.8327e-05 | 2015-03-13 | C | 0.0035093 | 1.8327e-05 | 2015 | 2015-03-13 | C | 6 | 0.0035093 | 1.8327e-05
1 | 4073353 | 2015-03-13 17:02 | 2015-03-14 14:49 | 1306.9 | 1 | 1306.9 | 0.0039971 | 3.0584e-06 | Restore Supply on Device 2115T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2115T | Brett Bensly advising 15kVA transformer onsite. 2R required to replace transformer. 2165 Opunake Road, Transformer 2115T.pole#730465 to be replaced tomorrow (14/03/2015). Only one customer affected and they have been advised. 14/03 between 11.30am and 11. | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1306.9 | 1303.9 | 1303.9 | 0.0039827 | 3.0544e-06 | 2015-03-13 | C | 0.0039827 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0039827 | 3.0544e-06
1 | 4073481 | 2015-03-13 19:44 | 2015-03-13 21:28 | 104.0167 | 1 | 104.0167 | 0.00031813 | 3.0584e-06 | Restore Supply on Device T5/139 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5/139 | Replaced 2X HV Fuses. Michael Thompson attended. | F4 | RANGIWAHIA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 104.0167 | 101.0167 | 101.0167 | 0.00030855 | 3.0544e-06 | 2015-03-13 | C | 0.00030855 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.00030855 | 3.0544e-06
1 | 4075588 | 2015-03-13 21:25 | 2015-03-15 00:13 | 1608 | 5 | 8040 | 0.02459 | 1.5292e-05 | Restore Supply on Device 3194T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3194T | 15/3 8.05am - Control advise these customers are on generator. Refer oms 4073545. 16/3 14:02 TX CHANGE COMPLETED WAS HIT BY LIGHTNING. 1415 CANNOT SIGN OFF EMAP UPDATE. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1608 | 1605 | 8025 | 0.024512 | 1.5272e-05 | 2015-03-13 | C | 0.024512 | 1.5272e-05 | 2015 | 2015-03-13 | C | 5 | 0.024512 | 1.5272e-05
1 | 4073567 | 2015-03-13 22:07 | 2015-03-14 08:35 | 628.4833 | 1 | 628.4833 | 0.0019222 | 3.0584e-06 | Restore Supply on Device X1676 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | tx x1676 and links # 247 | replace 2 x 3 amp ht fuses at tx x1676 and 1 x links at links # 247. cause: out since lightning went through according to customer. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 628.4833 | 625.4833 | 625.4833 | 0.0019105 | 3.0544e-06 | 2015-03-13 | C | 0.0019105 | 3.054e-06 | 2015 | 2015-03-13 | C | 1 | 0.0019105 | 3.0544e-06
1 | 3885772 | 2015-03-13 23:35 | 2015-03-14 02:45 | 190.3667 | 114 | 9014.4333 | 0.02757 | 0.00034866 | NAPA ID:06567 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 8 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G137, G138 | 3 yearly Maintenance on Switchgear & Tx. Works location: The Square, Palmerston North. WO 10142830. | F2 | PASCAL ST 8 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 79.074 | 76.074 | 8672.4333 | 0.026489 | 0.0003482 | 2015-03-13 | B | 0.013245 | 0.0001741 | 2015 | 2015-03-13 | B | 114 | 0.026489 | 0.0003482
1 | 4076216 | 2015-03-14 05:03 | 2015-03-15 10:19 | 1756.45 | 185 | 14962.9167 | 0.045763 | 0.00056581 | Restore Supply on Device F55 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P13000, P14492 | RS F55 A/R, L/O, O/C. E/F. Sectionalised & Patrolled. Branch had broken off tree by pole P14492 & caused line to come down. NDR #30883. Materials used: 10mtrs squirrel conductor, 1x Squirrel deadend, 1x full tension sleeve, 4m Ali Binder. Mike Thompson at | F4 | POHANGINA | KELVIN GROVE SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 80.8806 | 77.8806 | 14407.9167 | 0.044008 | 0.00056507 | 2015-03-14 | C | 0.044008 | 0.00056507 | 2015 | 2015-03-14 | C | 185 | 0.044008 | 0.00056507
1 | 4073789 | 2015-03-14 08:31 | 2015-03-14 10:35 | 123.2167 | 5 | 239.2833 | 0.00073183 | 1.5292e-05 | Restore Supply on Device P1100 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 709812 | 2x 3 Amp Links replaced at Fuses PU446. | F4 | PARIHAKA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 47.8567 | 44.8567 | 224.2833 | 0.00068506 | 1.5272e-05 | 2015-03-14 | C | 0.00068506 | 1.5272e-05 | 2015 | 2015-03-14 | C | 5 | 0.00068506 | 1.5272e-05
1 | 4071537 | 2015-03-14 09:49 | 2015-03-14 10:43 | 54.4833 | 7 | 381.3833 | 0.0011664 | 2.1409e-05 | NAPA ID:07764 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/491 | Replace TX as lid has rusted off. Work Location: Mt Biggs Road. Work Order 10154054. | F4 | KAKARIKI | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 54.4833 | 51.4833 | 360.3833 | 0.0011008 | 2.1381e-05 | 2015-03-14 | B | 0.00055038 | 1.069e-05 | 2015 | 2015-03-14 | B | 7 | 0.0011008 | 2.1381e-05
1 | 4074021 | 2015-03-14 12:44 | 2015-03-14 12:53 | 8.8 | 3 | 26.4 | 8.0742e-05 | 9.1753e-06 | Restore Supply on Device T5170 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T5170 | 3x 3 Amp Links | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 8.8 | 5.8 | 17.4 | 5.3147e-05 | 9.1633e-06 | 2015-03-14 | C | 5.3147e-05 | 9.163e-06 | 2015 | 2015-03-14 | C | 3 | 5.3147e-05 | 9.1633e-06
1 | 4075031 | 2015-03-14 15:27 | 2015-03-15 13:50 | 1343.0167 | 1 | 1343.0167 | 0.0041075 | 3.0584e-06 | Restore Supply on Device 5023E | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5023E | 3.30pm - advise smc. Transformer has blown up and spilled oil onto the road. Roydon Collingwood called to site for traffic management & to clean up oil (reported approximately 20 litres lost). Transformer to be replaced possibly the next day due to shorta | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 1343.0167 | 1340.0167 | 1340.0167 | 0.004093 | 3.0544e-06 | 2015-03-14 | C | 0.004093 | 3.054e-06 | 2015 | 2015-03-14 | C | 1 | 0.004093 | 3.0544e-06
1 | 4075299 | 2015-03-14 16:15 | 2015-03-14 19:17 | 182.1 | 46 | 4972.6 | 0.015208 | 0.00014069 | Restore Supply on Device S6011 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 248244 | Line Down at pole 248244. Line repaired. Materials used: conductor, 2x sleeves. Paul Cooper attended. | F4 | PAENGAROA | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 108.1 | 105.1 | 4834.6 | 0.014767 | 0.0001405 | 2015-03-14 | C | 0.014767 | 0.0001405 | 2015 | 2015-03-14 | C | 46 | 0.014767 | 0.0001405
1 | 4075094 | 2015-03-14 16:59 | 2015-03-14 17:21 | 21.6667 | 185 | 4008.3333 | 0.012259 | 0.00056581 | Restore Supply on Device RP02 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RP02 | Possibly tripped while resetting E/F flags following OMS 4074072. Line not patrolled - momentary loss of supply. | F4 | OKOROIRE | TIRAU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 21.6667 | 18.6667 | 3453.3333 | 0.010548 | 0.00056507 | 2015-03-14 | C | 0.010548 | 0.00056507 | 2015 | 2015-03-14 | C | 185 | 0.010548 | 0.00056507
1 | 4073545 | 2015-03-14 19:01 | 2015-03-14 19:55 | 54 | 222 | 11988 | 0.036664 | 0.00067897 | Restore Supply on Device 3194T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709020 | Close Attempted on Transformer 3194T but fuses blew. 30kVA single phase transformer requires replacement. *** CHORUS site - check if power restored and phone Noel on 027 464 5354 *** Broken Jumper found at Pole 709020 - Isolated at ABS 5229 _ Jumper repa | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 54 | 51 | 11322 | 0.034582 | 0.00067808 | 2015-03-14 | C | 0.034582 | 0.00067808 | 2015 | 2015-03-14 | C | 222 | 0.034582 | 0.00067808
1 | 3885785 | 2015-03-15 00:17 | 2015-03-15 04:10 | 232.7833 | 76 | 7138.0667 | 0.021831 | 0.00023244 | NAPA ID:06569 TP_LINTON GXP > PASCAL ST SUB > PASCAL ST 8 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | G135 | 3 yearly Maint on Switchgear & Tx. Works location: The Square, Palmerston North. WO 10142830 | F2 | PASCAL ST 8 | PASCAL ST SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 93.9219 | 90.9219 | 6910.0667 | 0.021106 | 0.00023214 | 2015-03-15 | B | 0.010553 | 0.00011607 | 2015 | 2015-03-15 | B | 76 | 0.021106 | 0.00023214
1 | 4075931 | 2015-03-15 04:31 | 2015-03-15 10:09 | 337.4 | 281 | 12101.0167 | 0.03701 | 0.00085942 | Restore Supply on Device RC01 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12795 | Caused by lines clashing. Lines across gully had very uneven sagging. Lines re-sagged correctly. Northpower have just upgraded this line and left it like this?? Dave Ngatai attended. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 43.0641 | 40.0641 | 11258.0167 | 0.034387 | 0.00085829 | 2015-03-15 | C | 0.034387 | 0.00085829 | 2015 | 2015-03-15 | C | 281 | 0.034387 | 0.00085829
1 | 4077763 | 2015-03-15 07:00 | 2015-03-15 10:13 | 192.8 | 30 | 5676.9167 | 0.017362 | 9.1753e-05 | Other Request on Device NA | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SA2-031 | 1 X Fuse Blown at SA2-031. Caused by Blown Lightning Arrestor at Fuses SA2-026 (Pole 204272). Lines isolated at Fuses SA2-031 and Lightning Arrestor Repaired. 1 X HV Fuse. ! x HV Lightning Arrestor. | F4 | LINDERMANN RD | KAURI POINT | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 189.2306 | 186.2306 | 5586.9167 | 0.017065 | 9.1633e-05 | 2015-03-15 | B | 0.0085324 | 4.5816e-05 | 2015 | 2015-03-15 | B | 30 | 0.017065 | 9.1633e-05
1 | 4078780 | 2015-03-15 11:04 | 2015-03-15 11:33 | 28.7333 | 281 | 8074.0667 | 0.024694 | 0.00085942 | Restore Supply on Device RC01 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | RC01 | RC 01 Trip. O/C. L/O. Not Patrolled. Suspect Line Clash. Wind getting up | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 28.7333 | 25.7333 | 7231.0667 | 0.022087 | 0.00085829 | 2015-03-15 | C | 0.022087 | 0.00085829 | 2015 | 2015-03-15 | C | 281 | 0.022087 | 0.00085829
1 | 4079097 | 2015-03-15 12:19 | 2015-03-15 16:32 | 252.7 | 281 | 28390.3 | 0.08683 | 0.00085942 | Restore Supply on Device RC01 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 392332 | Line found down beyond ABS 1078 at Pole Line Restored 1 mtr 3064 conductor and 2 sleeves used. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 101.0331 | 98.0331 | 27547.3 | 0.084141 | 0.00085829 | 2015-03-15 | C | 0.084141 | 0.00085829 | 2015 | 2015-03-15 | C | 281 | 0.084141 | 0.00085829
1 | 4080189 | 2015-03-15 16:03 | 2015-03-15 16:22 | 18.8833 | 688 | 12991.7333 | 0.039734 | 0.0021042 | Restore Supply on Device 3 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | CB 3 Coromandel Pole V1064 | Tree branch found on lines at Pole V1064. Wind blown debris. Removed with fuse stick. | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 18.8833 | 15.8833 | 10927.7333 | 0.033378 | 0.0021014 | 2015-03-15 | C | 0.033378 | 0.0021014 | 2015 | 2015-03-15 | C | 688 | 0.033378 | 0.0021014
1 | 4081133 | 2015-03-15 19:06 | 2015-03-16 09:42 | 875.35 | 7 | 5281.8 | 0.016154 | 2.1409e-05 | Restore Supply on Device TC2638 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 2638 | Trees in LV Lines. Found Transformer TC2638 fuses blown - Dave Ngatai attended and checked open and tagged. Safety Tag A4960. Trees need to be cut away before transformer can be relivened. LV disconnected & transformer restored at 09:42. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 754.5429 | 751.5429 | 5260.8 | 0.016069 | 2.1381e-05 | 2015-03-15 | C | 0.016069 | 2.1381e-05 | 2015 | 2015-03-15 | C | 7 | 0.016069 | 2.1381e-05
1 | 4081685 | 2015-03-16 01:10 | 2015-03-16 08:48 | 458.0667 | 480 | 4722.1667 | 0.014442 | 0.001468 | Restore Supply on Device TC486 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | I0628 | 1x A/R on CB 4 followed by report of part power on Dodd Rd - tree branch found over line between pole I0628 & I0629 - line isolated at ABS IC1210 to carry out repairs - 2 metres 16mm Cu conductor & 3 sleeves material required. Steve Martin attended. | F4 | MOTUMAOHO | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 9.8378 | 6.8378 | 3282.1667 | 0.010025 | 0.0014661 | 2015-03-16 | C | 0.010025 | 0.0014661 | 2015 | 2015-03-16 | C | 480 | 0.010025 | 0.0014661
1 | 4081769 | 2015-03-16 06:54 | 2015-03-16 06:54 | 0.083333 | 92 | 8237.3 | 0.025193 | 0.00028137 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 817047 | After auto reclose received a call from customer of pole on fire, faultman investigated and found a Oposum a cross the phase on pole 817047, it was removed with hot line sticks and supply restored. Gavin Gray attended. Isolation beyond Sectionaliser C637/ | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 89.5359 | 86.5359 | 7961.3 | 0.024317 | 0.00028101 | 2015-03-16 | C | 0.024317 | 0.00028101 | 2015 | 2015-03-16 | C | 92 | 0.024317 | 0.00028101
1 | 4082466 | 2015-03-16 08:42 | 2015-03-16 10:31 | 109.5667 | 1 | 109.5667 | 0.0003351 | 3.0584e-06 | Restore Supply on Device TC205 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T2638 | check for safety- tree branch has fallen on the network lines outside of the property, no power. 8.43am advised Tallia at svs hub & control. replaced 2x 6amp ddo fuses at tx T2638 - SRC 116561 cut trees and removed from line relivened and tested ok. | F4 | TE PUNINGA | TAHUNA SUB | TP_WAIHOU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 109.5667 | 106.5667 | 106.5667 | 0.0003255 | 3.0544e-06 | 2015-03-16 | C | 0.0003255 | 3.054e-06 | 2015 | 2015-03-16 | C | 1 | 0.0003255 | 3.0544e-06
1 | 4082769 | 2015-03-16 09:19 | 2015-03-16 09:27 | 7.9 | 1 | 7.9 | 2.4162e-05 | 3.0584e-06 | Restore Supply on Device T399 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | A Part of OMS 4081769 | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 7.9 | 4.9 | 4.9 | 1.4967e-05 | 3.0544e-06 | 2015-03-16 | C | 1.4967e-05 | 3.054e-06 | 2015 | 2015-03-16 | C | 1 | 1.4967e-05 | 3.0544e-06
1 | 4082906 | 2015-03-16 09:45 | 2015-03-16 10:51 | 65.9167 | 4 | 263.6667 | 0.0008064 | 1.2234e-05 | Restore Supply on Device FC1409 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1409 | 2 X 6A HV DDO's Caused by high winds. Shane Walker attended. | F3 | WYUNA BAY | COROMANDEL SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 65.9167 | 62.9167 | 251.6667 | 0.0007687 | 1.2218e-05 | 2015-03-16 | C | 0.0007687 | 1.2218e-05 | 2015 | 2015-03-16 | C | 4 | 0.0007687 | 1.2218e-05
1 | 4082933 | 2015-03-16 11:24 | 2015-03-16 14:21 | 176.55 | 1 | 176.55 | 0.00053996 | 3.0584e-06 | Restore Supply on Device TP2539 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FP1514 388039 | 2x2amp ht fuses blown cause wind. No other assets repaired or replaced and all adjacent assets checked and are up to Powerco standard. 2.40pm EMAP update, unable to Locate this job to complete. Steve Johnson is clear of this job at 2.41pm 2.55pm emap upda | F4 | HIKUAI | TAIRUA SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 176.55 | 173.55 | 173.55 | 0.0005301 | 3.0544e-06 | 2015-03-16 | C | 0.00053009 | 3.054e-06 | 2015 | 2015-03-16 | C | 1 | 0.0005301 | 3.0544e-06
1 | 4082997 | 2015-03-16 12:07 | 2015-03-16 15:11 | 184 | 213 | 15326 | 0.046873 | 0.00065144 | Restore Supply on Device T31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730436 | 1458B Auroa Road, Line down opp this address.... - line is on the road. Kain advised replaced an hv xarm and will sign off with control after switching but he advised this should be 2r so changed to 2r. CB T31 tripped to L/O - O/C & E/F flags - line down | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 71.9531 | 68.9531 | 14687 | 0.04486 | 0.00065059 | 2015-03-16 | C | 0.04486 | 0.00065059 | 2015 | 2015-03-16 | C | 213 | 0.04486 | 0.00065059
1 | 4083578 | 2015-03-16 12:33 | 2015-03-16 17:28 | 295.4333 | 1 | 295.4333 | 0.00090356 | 3.0584e-06 | Restore Supply on Device 4756T | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4756T | Pole struck by lightening... power unaffected, pole fuse has been hit on pole, suspect pole hit last night advised control check for safety on pole completed, no damage done to network, all power on | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 295.4333 | 292.4333 | 292.4333 | 0.00089322 | 3.0544e-06 | 2015-03-16 | C | 0.00089322 | 3.054e-06 | 2015 | 2015-03-16 | C | 1 | 0.00089322 | 3.0544e-06
1 | 4083882 | 2015-03-16 14:00 | 2015-03-16 18:18 | 257.7333 | 4 | 1030.9333 | 0.003153 | 1.2234e-05 | Restore Supply on Device 3059T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 3059T | job completed. power restored | F4 | CLOTON RD INDUSTRIAL | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 257.7333 | 254.7333 | 1018.9333 | 0.0031123 | 1.2218e-05 | 2015-03-16 | C | 0.0031123 | 1.2218e-05 | 2015 | 2015-03-16 | C | 4 | 0.0031123 | 1.2218e-05
1 | 4084049 | 2015-03-16 20:09 | 2015-03-16 21:10 | 61.1167 | 3 | 90.65 | 0.00027725 | 9.1753e-06 | Restore Supply on Device 8471 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 8471 | No Power received. Line patrolled. Fuses 8471 found tripped. 2x 3Amp Links replaced. Neil Woodhead attended. | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 30.2167 | 27.2167 | 81.65 | 0.00024939 | 9.1633e-06 | 2015-03-16 | C | 0.00024939 | 9.163e-06 | 2015 | 2015-03-16 | C | 3 | 0.00024939 | 9.1633e-06
1 | 4084066 | 2015-03-16 20:48 | 2015-03-17 00:37 | 229.0667 | 75 | 17180 | 0.052544 | 0.00022938 | Restore Supply on Device S366 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 820097 | Car vs Pole. Isolated for safety in first instance and then to replace pole. Materials used:11m Busck Pole, Double Pin Arm, Donut, Breast Block, Span of 14mm Guy wire, Assorted Bolts. NDR # 20635. Gavin Gray attended. | F3 | TAVERNER ST | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 229.0667 | 226.0667 | 16955 | 0.051788 | 0.00022908 | 2015-03-16 | C | 0.051788 | 0.00022908 | 2015 | 2015-03-16 | C | 75 | 0.051788 | 0.00022908
1 | 4087286 | 2015-03-17 03:02 | 2015-03-17 08:48 | 345.65 | 76 | 8494.3167 | 0.025979 | 0.00023244 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 7417/2 | Recloser 7417/2 tripped on A,B,C phase O/C, flags line was patrolled and no fault was found by faultman. | F4 | WESTMERE GLADSTONE | GLADSTONE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 111.7673 | 108.7673 | 8266.3167 | 0.025249 | 0.00023214 | 2015-03-17 | C | 0.025249 | 0.00023214 | 2015 | 2015-03-17 | C | 76 | 0.025249 | 0.00023214
1 | 4085213 | 2015-03-17 03:23 | 2015-03-17 11:35 | 492.05 | 1 | 492.05 | 0.0015049 | 3.0584e-06 | Restore Supply on Device 7762 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 836953 | Faultman isolated line at Fuses 7762 to replaced cross arm king pin on pole 836953, pole has been defected and needs replacement when area is dry. | F5 | BIDEFORD | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 492.05 | 489.05 | 489.05 | 0.0014938 | 3.0544e-06 | 2015-03-17 | C | 0.0014938 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.0014938 | 3.0544e-06
1 | 4094206 | 2015-03-17 04:39 | 2015-03-17 07:25 | 166 | 353 | 20980 | 0.064166 | 0.0010796 | Restore Supply on Device 6 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 718388 | CB 6 tripped to L/O - E/F & O/C flags - Line sectionalised & patrolled, broken insulator located on pole #718388 - isolation at fuses MA574 - 1 x 11kv pin & insulator material required - all supply restored - Kaine McKay & Craig Brogden attended. Recreati | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 59.4334 | 56.4334 | 19921 | 0.060847 | 0.0010782 | 2015-03-17 | C | 0.060847 | 0.0010782 | 2015 | 2015-03-17 | C | 353 | 0.060847 | 0.0010782
1 | 4087455 | 2015-03-17 05:28 | 2015-03-17 06:55 | 87 | 10 | 869.95 | 0.0026607 | 3.0584e-05 | Restore Supply on Device X745 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O45 | 2 X HT FUSES AND BARRELS 10 AMP UNKNOWN. No other assets repaired or replaced. Adjacent assets ok | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 86.995 | 83.995 | 839.95 | 0.0025656 | 3.0544e-05 | 2015-03-17 | C | 0.0025656 | 3.0544e-05 | 2015 | 2015-03-17 | C | 10 | 0.0025656 | 3.0544e-05
1 | 3876362 | 2015-03-17 07:00 | 2015-03-17 17:23 | 623 | 16 | 9968 | 0.030486 | 4.8935e-05 | NAPA ID:06710 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 623 | 620 | 9920 | 0.0303 | 4.8871e-05 | 2015-03-17 | B | 0.01515 | 2.4435e-05 | 2015 | 2015-03-17 | B | 16 | 0.0303 | 4.8871e-05
1 | 4088398 | 2015-03-17 08:19 | 2015-03-17 09:39 | 80 | 4 | 320 | 0.0009787 | 1.2234e-05 | Restore Supply on Device 532 | 22000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 532 | 2 x 6 amp ht fuse. fuse # 532. cause: possibly birds. 2 out of 3 phases. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | LEEDSTOWN 22KV | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 80 | 77 | 308 | 0.00094076 | 1.2218e-05 | 2015-03-17 | C | 0.00094076 | 1.2218e-05 | 2015 | 2015-03-17 | C | 4 | 0.00094076 | 1.2218e-05
1 | 3886160 | 2015-03-17 09:07 | 2015-03-17 18:32 | 564.9667 | 68 | 38417.7333 | 0.1175 | 0.00020797 | NAPA ID:06058 TP_KINLEITH GXP > MARAETAI ROAD SUB > BALMORAL DR | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch IC1583 | AP1: Replacing combination Magnefix/Transformer with a Safelink CFC and a new 300kVA transformer. If time is restricted the cable termination on switch 9897/3 will not be completed. TP1: Test 11kV cable connected to 9897/1. If the cable connected to 989 | F3 | BALMORAL DR | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 564.9667 | 561.9667 | 38213.7333 | 0.11672 | 0.0002077 | 2015-03-17 | B | 0.05836 | 0.00010385 | 2015 | 2015-03-17 | B | 68 | 0.11672 | 0.0002077
1 | 4082705 | 2015-03-17 09:30 | 2015-03-17 11:05 | 95.4667 | 22 | 2100.2667 | 0.0064235 | 6.7285e-05 | NAPA ID:07850 TP_TE MATAI GXP > TE PUKE SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9835/4 | This application is to track NAPA 6113 which was cancelled - the outage was moved to the alternate date 17/3/15 , switching carried out under 6113. Switching uploaded in this application - AP: Disconnect and isolate cable between TF5-056 and SF5-01 | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 95.4667 | 92.4667 | 2034.2667 | 0.0062135 | 6.7197e-05 | 2015-03-17 | B | 0.0031068 | 3.3599e-05 | 2015 | 2015-03-17 | B | 22 | 0.0062135 | 6.7197e-05
1 | 3856410 | 2015-03-17 09:38 | 2015-03-17 11:39 | 120.8667 | 45 | 5439 | 0.016635 | 0.00013763 | NAPA ID:05973 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 535 | Pole replacements and crossarm changes.(just note i was unable to change isolation's and earths on phasing equip sheet. Works location: Wairau Rd. WO 10154759 | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 120.8667 | 117.8667 | 5304 | 0.016201 | 0.00013745 | 2015-03-17 | B | 0.0081003 | 6.8725e-05 | 2015 | 2015-03-17 | B | 45 | 0.016201 | 0.00013745
1 | 4088395 | 2015-03-17 09:43 | 2015-03-17 15:01 | 318.2167 | 3 | 757.8833 | 0.0023179 | 9.1753e-06 | Restore Supply on Device 3056T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 3056T | ADVSIED HUB AND CONTROL. Blown 30 kva tx. tx 3056T. pole # 731991. FM advise. transformer replaced. | F4 | MANAIA RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 252.6278 | 249.6278 | 748.8833 | 0.0022874 | 9.1633e-06 | 2015-03-17 | C | 0.0022874 | 9.163e-06 | 2015 | 2015-03-17 | C | 3 | 0.0022874 | 9.1633e-06
1 | 4088660 | 2015-03-17 10:43 | 2015-03-17 11:58 | 74.95 | 1 | 74.95 | 0.00022923 | 3.0584e-06 | Restore Supply on Device X1037 | 11000 | UNPLANNED | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | tx 1039 | replace 2 x 3amp fuses at tx 1039. cause: weather. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | LAKE ALICE | PUKEPAPA SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 74.95 | 71.95 | 71.95 | 0.00021977 | 3.0544e-06 | 2015-03-17 | C | 0.00021977 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.00021977 | 3.0544e-06
1 | 4089614 | 2015-03-17 11:50 | 2015-03-17 15:16 | 206.1833 | 3 | 618.55 | 0.0018918 | 9.1753e-06 | Restore Supply on Device FC:O487/1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 014267 | KPE CB1 emergency switching to replace broken arm at pole 014267. Isolation at Fuses 0487-1 ( 668 ) no back feeds, arm replaced all service restored, Brian Fisher attended. See OMS No 4078762. materials 2 x double arms, 2 x H/V insulators | F4 | KAIHERE | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 206.1833 | 203.1833 | 609.55 | 0.0018618 | 9.1633e-06 | 2015-03-17 | C | 0.0018618 | 9.163e-06 | 2015 | 2015-03-17 | C | 3 | 0.0018618 | 9.1633e-06
1 | 4087982 | 2015-03-17 11:58 | 2015-03-17 12:40 | 41.8 | 307 | 12832.6 | 0.039248 | 0.00093894 | Restore Supply on Device T2451 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2450 | *** invoicing level - FM did request a 2R, please look into this ***Faultman isolated line at Links C627/6 & ABS C627/1 to replace fuse and fuse holder on transformer T2450. | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 41.8 | 38.8 | 11911.6 | 0.036383 | 0.00093771 | 2015-03-17 | C | 0.036383 | 0.00093771 | 2015 | 2015-03-17 | C | 307 | 0.036383 | 0.00093771
1 | 4089394 | 2015-03-17 12:45 | 2015-03-17 14:16 | 90.75 | 1 | 90.75 | 0.00027755 | 3.0584e-06 | Restore Supply on Device T2964 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | 11A TE MIHA CRESCENT, FEATHERSTON | part of feeder fault - oms 4087982 (***Faultman isolated line at Links C627/6 & ABS C627/1 to replace fuse and fuse holder on transformer T2450.) | F4 | BURNSIDE | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 90.75 | 87.75 | 87.75 | 0.00026803 | 3.0544e-06 | 2015-03-17 | C | 0.00026803 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.00026803 | 3.0544e-06
1 | 4089427 | 2015-03-17 13:39 | 2015-03-17 15:56 | 137.1833 | 1 | 137.1833 | 0.00041956 | 3.0584e-06 | Restore Supply on Device T2062 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | links # 7369 and pole # 816912 | links # 7369 and pole # 816912. replace 2 x 10 amp elements. cause: old age. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 137.1833 | 134.1833 | 134.1833 | 0.00040985 | 3.0544e-06 | 2015-03-17 | C | 0.00040985 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.00040985 | 3.0544e-06
1 | 4089364 | 2015-03-17 13:47 | 2015-03-17 14:40 | 53 | 15 | 795 | 0.0024314 | 4.5876e-05 | Restore Supply on Device 4765W | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781742 | FM advise: going to do a shutdown. need to replace a insulator for an 11 kv line. *** please check at invoicing - FM requested 2R ***. Faultman isolated line at Fuses 708 to rebind in floating wire & replace insulator on pole 781742. check if oms 408938 | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 53 | 50 | 750 | 0.0022908 | 4.5816e-05 | 2015-03-17 | C | 0.0022908 | 4.5816e-05 | 2015 | 2015-03-17 | C | 15 | 0.0022908 | 4.5816e-05
1 | 4089583 | 2015-03-17 15:13 | 2015-03-17 17:26 | 132.9167 | 1 | 132.9167 | 0.00040652 | 3.0584e-06 | Restore Supply on Device T773 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 798360 | Replaced 2x 10a hv fuse links due to bird strike. nothing else repaired or replaced, adjacent assets up to powerco standard. | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 132.9167 | 129.9167 | 129.9167 | 0.00039682 | 3.0544e-06 | 2015-03-17 | C | 0.00039682 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.00039682 | 3.0544e-06
1 | 4089822 | 2015-03-17 20:27 | 2015-03-17 23:15 | 168.6167 | 1 | 168.5167 | 0.0005154 | 3.0584e-06 | Restore Supply on Device FP740 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP740 | 2 X 10A HV DDO's | F3/F4 | OPOUTERE | WHANGAMATA SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 168.5167 | 165.5167 | 165.5167 | 0.00050556 | 3.0544e-06 | 2015-03-17 | C | 0.00050556 | 3.054e-06 | 2015 | 2015-03-17 | C | 1 | 0.00050556 | 3.0544e-06
1 | 3876363 | 2015-03-18 07:01 | 2015-03-18 17:05 | 604.1333 | 16 | 146.1333 | 0.00044694 | 4.8935e-05 | NAPA ID:06714 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Outage time 10 minutes only - Generators installed on all transformers. (Two outages to connect and remove genera | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 9.1333 | 6.1333 | 98.1333 | 0.00029974 | 4.8871e-05 | 2015-03-18 | B | 0.00014987 | 2.4435e-05 | 2015 | 2015-03-18 | B | 16 | 0.00029974 | 4.8871e-05
1 | 3705770 | 2015-03-18 08:31 | 2015-03-18 14:39 | 368 | 63 | 23184 | 0.070906 | 0.00019268 | NAPA ID:06088 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 194 | Replace various network poles in work area. replace existing overhead tx 1025 with new ground mount tx. Works location: Fitzroy Rd WO 30002060 | F2 | KATERE 10 | KATERE SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 368 | 365 | 22995 | 0.070236 | 0.00019243 | 2015-03-18 | B | 0.035118 | 9.6214e-05 | 2015 | 2015-03-18 | B | 63 | 0.070236 | 0.00019243
1 | 3911991 | 2015-03-18 08:45 | 2015-03-18 14:59 | 374 | 2 | 748 | 0.0022877 | 6.1168e-06 | NAPA ID:06781 TP_HINUERA GXP > PUTARURU SUB > WAOTU | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 22kV pole M1200 | To replace 11kV conductor between Ploe # M1200 and M1188 Waotu Road. Works location: Waotu Rd. WO 10134042 | F4 | WAOTU | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 374 | 371 | 742 | 0.0022664 | 6.1088e-06 | 2015-03-18 | B | 0.0011332 | 3.054e-06 | 2015 | 2015-03-18 | B | 2 | 0.0022664 | 6.1088e-06
1 | 3822199 | 2015-03-18 08:45 | 2015-03-18 14:29 | 344 | 17 | 5848 | 0.017886 | 5.1993e-05 | NAPA ID:06171 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F0835 | Re-conductor between poles F0835 & F0854. Works location: Old Te Aroha Rd. WO 10163038 | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 344 | 341 | 5797 | 0.017706 | 5.1925e-05 | 2015-03-18 | B | 0.0088532 | 2.5963e-05 | 2015 | 2015-03-18 | B | 17 | 0.017706 | 5.1925e-05
1 | 3941172 | 2015-03-18 08:46 | 2015-03-18 14:35 | 349.25 | 43 | 15017.75 | 0.045931 | 0.00013151 | NAPA ID:06750 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9807/1 | REPLACE POLES AND ARMS. Works location: McLaren Falls Rd. WO 30000217. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 349.25 | 346.25 | 14888.75 | 0.045477 | 0.00013134 | 2015-03-18 | B | 0.022738 | 6.567e-05 | 2015 | 2015-03-18 | B | 43 | 0.045477 | 0.00013134
1 | 4092192 | 2015-03-18 08:52 | 2015-03-18 18:00 | 547.5667 | 4 | 2190.2667 | 0.0066988 | 1.2234e-05 | Restore Supply on Device 5027E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5027e | 11:58am as per Talia took Brett back to assigned as unsure what job Brett was going to first 14:40 requests 2r for blown tx change Changed transformer 5027E | F4 | OTAKEHO | MANAIA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 547.5667 | 544.5667 | 2178.2667 | 0.0066533 | 1.2218e-05 | 2015-03-18 | C | 0.0066533 | 1.2218e-05 | 2015 | 2015-03-18 | C | 4 | 0.0066533 | 1.2218e-05
1 | 4093235 | 2015-03-18 10:03 | 2015-03-18 10:47 | 43.7667 | 15 | 656.5 | 0.0020079 | 4.5876e-05 | Restore Supply on Device 708 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781722 | Outage required from Fuses 708 (Brewer Rd) to replace one broken Insulator. Relivened OK. James Prime attended. | F4 | WAITOTARA | TP_WAVERLEY | TP_WAVERLEY | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 43.7667 | 40.7667 | 611.5 | 0.0018678 | 4.5816e-05 | 2015-03-18 | C | 0.0018678 | 4.5816e-05 | 2015 | 2015-03-18 | C | 15 | 0.0018678 | 4.5816e-05
1 | 4094164 | 2015-03-18 13:52 | 2015-03-18 17:23 | 210.55 | 1 | 210.55 | 0.00064395 | 3.0584e-06 | Restore Supply on Device T1051 | 11000 | UNPLANNED | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1051 | 1.55pm - can't locate, e-map update. 798137 transformer T1051 2x 10 amp fuses advised to go through control. Lightning - KPI exception. 2 HT fuses replaced at transformer T1051. (@a). Suspect tripped due to lightning other day. Paul is following up for | F4 | KUMENGA | TUHITARATA SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 210.55 | 207.55 | 207.55 | 0.00063395 | 3.0544e-06 | 2015-03-18 | C | 0.00063395 | 3.054e-06 | 2015 | 2015-03-18 | C | 1 | 0.00063395 | 3.0544e-06
1 | 3941717 | 2015-03-18 14:01 | 2015-03-18 19:30 | 329.3667 | 2 | 658.7333 | 0.0020147 | 6.1168e-06 | NAPA ID:07087 TP_MT MAUNGANUI 33 GXP > TRITON SUB > HULL RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4/325 | Remove Series 1 Switchgear and thru-joint cables from DDO SC4-201 to transformer TC4-325 also remove HV link-box SC4-282. Works location: Tyne St, Mt Maunganui. WO 10148303 | F2 | HULL RD | TRITON SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 329.3667 | 326.3667 | 652.7333 | 0.0019937 | 6.1088e-06 | 2015-03-18 | B | 0.00099686 | 3.054e-06 | 2015 | 2015-03-18 | B | 2 | 0.0019937 | 6.1088e-06
1 | 4096464 | 2015-03-19 06:57 | 2015-03-19 11:17 | 259.8 | 1226 | 26900.2333 | 0.082272 | 0.0037496 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 218066 | Line down at pole 218066 brought down by bird strike. Isolation at ABS IP 514, IP515 & IP153. ABF from sectionaliser 9760 to Recloser 9548. ABF 9460 not yet commissioned Rec 9513 open on feeder outage waited 15 mins closed sec 9460. Fault logged advising | F4 | TAINUI | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 21.9415 | 18.9415 | 23222.2333 | 0.070931 | 0.0037447 | 2015-03-19 | C | 0.070931 | 0.0037447 | 2015 | 2015-03-19 | C | 1226 | 0.070931 | 0.0037447
1 | 3876367 | 2015-03-19 07:00 | 2015-03-19 17:05 | 605.0167 | 16 | 160.2667 | 0.00049016 | 4.8935e-05 | NAPA ID:06716 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. All transformers on generators- 5 minute outage either side to connect, reconnect. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 10.0167 | 7.0167 | 112.2667 | 0.00034291 | 4.8871e-05 | 2015-03-19 | B | 0.00017145 | 2.4435e-05 | 2015 | 2015-03-19 | B | 16 | 0.00034291 | 4.8871e-05
1 | 3876406 | 2015-03-19 08:36 | 2015-03-19 12:56 | 260.2833 | 9 | 2342.55 | 0.0071645 | 2.7526e-05 | NAPA ID:06249 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links WH887 | Replace poles and Wire on Hicks road. Works location: Hicks Rd. WO 10160005 | F4 | MANAWAPOU RD | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 260.2833 | 257.2833 | 2315.55 | 0.0070727 | 2.749e-05 | 2015-03-19 | B | 0.0035363 | 1.3745e-05 | 2015 | 2015-03-19 | B | 9 | 0.0070727 | 2.749e-05
1 | 3912565 | 2015-03-19 08:45 | 2015-03-19 13:40 | 295 | 28 | 8260 | 0.025263 | 8.5636e-05 | NAPA ID:07126 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1137 | Replace 11kV x-arms. Works location: SH 1 Tokoroa. WO 10163039 | F4 | HARRIS BLOCK | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 295 | 292 | 8176 | 0.024973 | 8.5524e-05 | 2015-03-19 | B | 0.012486 | 4.2762e-05 | 2015 | 2015-03-19 | B | 28 | 0.024973 | 8.5524e-05
1 | 3941797 | 2015-03-19 08:45 | 2015-03-19 14:37 | 352 | 28 | 9856 | 0.030144 | 8.5636e-05 | NAPA ID:06752 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF3-010 | REPLACE POLES AND ARMS. Works location: McLaren Falls Rd. WO 30000217. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 352 | 349 | 9772 | 0.029848 | 8.5524e-05 | 2015-03-19 | B | 0.014924 | 4.2762e-05 | 2015 | 2015-03-19 | B | 28 | 0.029848 | 8.5524e-05
1 | 4083216 | 2015-03-19 09:01 | 2015-03-19 11:15 | 134.7333 | 22 | 2964.1333 | 0.0090656 | 6.7285e-05 | NAPA ID:06121 TP_TE MATAI GXP > TE PUKE SUB > ROADS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF5-056 | AP: Reconnected cable between TF5-056 and 9835/4 onto the HV bus in transformer cabinet TF5-056. Phasing to be carried out across open links 9835/4 after the AP is closed. WA: Commission Radio and SCADA Controls/Indications in Load Break Switch 9835/2. | F4 | ROADS | TE PUKE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 134.7333 | 131.7333 | 2898.1333 | 0.0088521 | 6.7197e-05 | 2015-03-19 | B | 0.0044261 | 3.3599e-05 | 2015 | 2015-03-19 | B | 22 | 0.0088521 | 6.7197e-05
1 | 3886112 | 2015-03-19 09:15 | 2015-03-19 15:29 | 374 | 141 | 52734 | 0.16128 | 0.00043124 | NAPA ID:06523 TP_WANGANUI GXP > HATRICKS WHARF SUB > MARANGAI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 774222 | Replacing 11kv pole 774222 and ABS 2677. Works location: Anzac Parade, Wanganui. WO 10147894. Restoration at 15:29 - (29 mins late). | F3 | MARANGAI | HATRICKS WHARF SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 374 | 371 | 52311 | 0.15978 | 0.00043067 | 2015-03-19 | B | 0.07989 | 0.00021534 | 2015 | 2015-03-19 | B | 141 | 0.15978 | 0.00043067
1 | 3799062 | 2015-03-19 09:45 | 2015-03-19 15:15 | 330 | 3 | 990 | 0.0030278 | 9.1753e-06 | NAPA ID:05934 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2251 | To replace 11kV cross arms and upgrade existing transformer to 50 kVa at TC3068. Works location: Chepmell Rd Morrinsville. WO 30000212. Safety Manager 456722. | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 330 | 327 | 981 | 0.0029964 | 9.1633e-06 | 2015-03-19 | B | 0.0014982 | 4.582e-06 | 2015 | 2015-03-19 | B | 3 | 0.0029964 | 9.1633e-06
1 | 3950961 | 2015-03-19 10:00 | 2015-03-19 16:16 | 375.9167 | 19 | 7142.4167 | 0.021845 | 5.811e-05 | NAPA ID:07535 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | H43 | Cut trees around the 11Kv. Works location: Forest Hill Rd. PPPD 46313. | F2 | AOKAUTERE | TURITEA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 375.9167 | 372.9167 | 7085.4167 | 0.021642 | 5.8034e-05 | 2015-03-19 | B | 0.010821 | 2.9017e-05 | 2015 | 2015-03-19 | B | 19 | 0.021642 | 5.8034e-05
1 | 3885992 | 2015-03-19 10:34 | 2015-03-19 14:13 | 218.25 | 189 | 40990.65 | 0.12537 | 0.00057804 | NAPA ID:07129 TP_STRATFORD GXP > MOTUKAWA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 6.6kkV Fuse H051 | 3 Yearly maintenance and testing of 33kV CB 240, 33/6.6kV TR27, 6.6kV ABS's H23 - H43 - H13, and 6.6kV Rec H21. This is the third attempt. Original switching was written under NAPA 4635. Works location: Motukawa Sub. WO 10143547. This outage started late | F1, F2, F3 | INGLEWOOD SOUTH 33KV | MOTUKAWA 33 SW | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 216.8817 | 213.8817 | 40423.65 | 0.12347 | 0.00057729 | 2015-03-19 | B | 0.061735 | 0.00028864 | 2015 | 2015-03-19 | B | 189 | 0.12347 | 0.00057729
1 | 4099656 | 2015-03-19 12:14 | 2015-03-20 13:37 | 1523.6167 | 163 | 52448.6833 | 0.16041 | 0.00049852 | Restore Supply on Device 4897 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 708467 | 11kV Recloser RS 4897 tripped B Phase, E/F lock out. 11kV Lines down past fuses 5272. The cause of the fault is suspected to be due to lightning from the week before. Replaced cross arm and assembly and rehung conductors. NOTE: OMS job indicates Fault man | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 321.7711 | 318.7711 | 51959.6833 | 0.15871 | 0.00049787 | 2015-03-19 | C | 0.15871 | 0.00049787 | 2015 | 2015-03-19 | C | 163 | 0.15871 | 0.00049787
1 | 3893229 | 2015-03-19 13:25 | 2015-03-19 16:00 | 155 | 3 | 465 | 0.0014222 | 9.1753e-06 | Restore Supply on Device T2/678 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/678 | F/man requested 2R for line crew to attend to replace Tx on pole P41041 as it is leaking badly on ground. Staywire is also missing from this pole & pole is on lean - staywire needs to be replaced. 25/02 Email sent to svs hub for update. 26/02 Svs hub advi | F4 | TE ARAKURA | MILSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 155 | 152 | 456 | 0.0013928 | 9.1633e-06 | 2015-03-19 | C | 0.0013928 | 9.163e-06 | 2015 | 2015-03-19 | C | 3 | 0.0013928 | 9.1633e-06
1 | 4100668 | 2015-03-19 15:14 | 2015-03-19 18:19 | 185.05 | 1 | 185.05 | 0.00056596 | 3.0584e-06 | Restore Supply on Device 3256T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 819 KOHURATAHI ROAD , STRATFORD | power was on 20 min prior to arrival fm thinks this is related to 4099854 which Chris Katene recloser tripping | F4 | HUIROA | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 185.05 | 182.05 | 182.05 | 0.00055606 | 3.0544e-06 | 2015-03-19 | C | 0.00055606 | 3.054e-06 | 2015 | 2015-03-19 | C | 1 | 0.00055606 | 3.0544e-06
1 | 4101086 | 2015-03-19 22:23 | 2015-03-19 23:45 | 81.6 | 52 | 2340 | 0.0071567 | 0.00015904 | Restore Supply on Device K29 | 11000 | UNPLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P19892 | Faultman found line down at pole P19892 caused by tree, line was isolated at ABS's K29, K31 & K32 to make a temp line break between ABS K29 and at pole P19892. Fault man will arrange in the morning for tree contractor to cut & remove the tree, a follow u | F4 | WAITUNA | KIMBOLTON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 45 | 42 | 2184 | 0.0066709 | 0.00015883 | 2015-03-19 | C | 0.0066709 | 0.00015883 | 2015 | 2015-03-19 | C | 52 | 0.0066709 | 0.00015883
1 | 3905255 | 2015-03-20 07:00 | 2015-03-20 16:55 | 594.9167 | 16 | 158.6667 | 0.00048527 | 4.8935e-05 | NAPA ID:06719 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1601 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Road, Moawhango. WO 10161206. Note: two short shutdowns while generators were connected an | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 9.9167 | 6.9167 | 110.6667 | 0.00033802 | 4.8871e-05 | 2015-03-20 | B | 0.00016901 | 2.4435e-05 | 2015 | 2015-03-20 | B | 16 | 0.00033802 | 4.8871e-05
1 | 3945241 | 2015-03-20 08:50 | 2015-03-20 14:51 | 360.9 | 74 | 26706.6 | 0.08168 | 0.00022632 | NAPA ID:06761 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-050 | REPLACE POLES AND ARMS AS PER SCOPE OF WORKS. Works location: Keenan Rd. Work Order 10148098. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 360.9 | 357.9 | 26484.6 | 0.080895 | 0.00022603 | 2015-03-20 | B | 0.040448 | 0.00011301 | 2015 | 2015-03-20 | B | 74 | 0.080895 | 0.00022603
1 | 3799633 | 2015-03-20 09:00 | 2015-03-20 15:09 | 368.9167 | 6 | 2213.5 | 0.0067698 | 1.8351e-05 | NAPA ID:05955 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP523 | To replace11klV pole and cross arms beyond FP523. Works location: Waimarama Rd, Morrinsville. WO 30000212 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 368.9167 | 365.9167 | 2195.5 | 0.006706 | 1.8327e-05 | 2015-03-20 | B | 0.003353 | 9.163e-06 | 2015 | 2015-03-20 | B | 6 | 0.006706 | 1.8327e-05
1 | 4102089 | 2015-03-20 09:58 | 2015-03-20 19:37 | 578.55 | 1 | 578.55 | 0.0017695 | 3.0584e-06 | Restore Supply on Device TA2-013 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | TA2/156 | Contractor has run over with possible tractor green pod box, which has affected some customer power. 9.59am advised Tallia at svs hub of job. Pillar box is smashed and needs to be replaced today. address is actually 123 & 125 Emerton road, Athenree. Feede | F3 | ATHENREE | WAIHI BEACH SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 578.55 | 575.55 | 575.55 | 0.001758 | 3.0544e-06 | 2015-03-20 | C | 0.001758 | 3.054e-06 | 2015 | 2015-03-20 | C | 1 | 0.001758 | 3.0544e-06
1 | 4101265 | 2015-03-20 12:53 | 2015-03-20 13:31 | 38.4333 | 52 | 1998.5333 | 0.0061124 | 0.00015904 | Electric Job | 11000 | PLANNED | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P19892 | Faultman to get tree contractor to cut trees between ABS K29 & Pole P19892and then close the temp line break in the morning. Please assign this to Dave Whale. REF. OMS 4101086. Tree all Felled and cleared - Isolation's installed at ABS's K29 K31, & K32 to | F3/F4 | MAKINO | FEILDING SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 38.4333 | 35.4333 | 1842.5333 | 0.0056279 | 0.00015883 | 2015-03-20 | B | 0.0028139 | 7.9415e-05 | 2015 | 2015-03-20 | B | 52 | 0.0056279 | 0.00015883
1 | 4104967 | 2015-03-20 13:15 | 2015-03-20 14:19 | 63.7167 | 10 | 637.1667 | 0.0019487 | 3.0584e-05 | Restore Supply on Device 1385 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | 1385 | Isolated Transformer X2455 for cables to be cleaned and tightened under Powerco W/O 30007097 - attended by Karl Rodgers. | F3/F4 | PAREWANUI | BULLS SUB | TP_MARTON | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 63.7167 | 60.7167 | 607.1667 | 0.0018545 | 3.0544e-05 | 2015-03-20 | C | 0.0018545 | 3.0544e-05 | 2015 | 2015-03-20 | C | 10 | 0.0018545 | 3.0544e-05
1 | 4110064 | 2015-03-21 13:37 | 2015-03-21 16:21 | 164.65 | 218 | 23431.1667 | 0.071662 | 0.00066674 | Restore Supply on Device PU3 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | P2140 | Fault weather dependent had to sectionlise a number of times. Fault some where between ABS's PU336 and 6391 - Transformer P2140 found disconnected on LV side and earth wire removed as well, used to feed school which has been removed, 2 HV carrier burnt - | F4 | PUNGAREHU | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 107.4824 | 104.4824 | 22777.1667 | 0.069571 | 0.00066586 | 2015-03-21 | C | 0.069571 | 0.00066586 | 2015 | 2015-03-21 | C | 218 | 0.069571 | 0.00066586
1 | 4111302 | 2015-03-21 19:28 | 2015-03-21 20:15 | 46.5667 | 306 | 10388.7 | 0.031773 | 0.00093588 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M2088 | Feeder opened due to police/ Fire etc removing car trailer from accident scene with no Isolations in place. The wires are in the air, Controller explained this doesn't make it safe to carryout this task. NOC rung SMC to try & arrange Don Masters to Attend | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 33.95 | 30.95 | 9470.7 | 0.028928 | 0.00093465 | 2015-03-21 | C | 0.028928 | 0.00093465 | 2015 | 2015-03-21 | C | 306 | 0.028928 | 0.00093465
1 | 4113764 | 2015-03-22 05:00 | 2015-03-22 14:45 | 585 | 66 | 37505 | 0.11471 | 0.00020186 | Restore Supply on Device SD4-293 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TD4-278 | at 05:00 Welcome Bay, CB 2 Mangatapu Feeder, CB 9492/1, Tripped. Cable Fault Between Transformers TD4-134 & TD4-278. | F3 | MAUNGATAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 568.2576 | 565.2576 | 37307 | 0.11395 | 0.00020159 | 2015-03-22 | C | 0.11395 | 0.00020159 | 2015 | 2015-03-22 | C | 66 | 0.11395 | 0.00020159
1 | 4128748 | 2015-03-22 05:00 | 2015-03-22 11:04 | 364 | 547 | 37825 | 0.11568 | 0.001673 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 67 |  | F3 | MAUNGATAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 69.1499 | 66.1499 | 36184 | 0.11052 | 0.0016708 | 2015-03-22 | C | 0.11052 | 0.0016708 | 2015 | 2015-03-22 | C | 547 | 0.11052 | 0.0016708
1 | 4104966 | 2015-03-22 08:12 | 2015-03-22 14:46 | 394.0667 | 1 | 394.0667 | 0.0012052 | 3.0584e-06 | NAPA ID:07999 TP_WANGANUI GXP > BEACH RD SUB | 33000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 1 | In Service Zone Transformer W29 has a severe oil leak that has been accelerating. Works location: Beach Rd Sub. WO NA | F1 | IMLAY | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 394.0667 | 391.0667 | 391.0667 | 0.0011945 | 3.0544e-06 | 2015-03-22 | B | 0.00059724 | 1.527e-06 | 2015 | 2015-03-22 | B | 1 | 0.0011945 | 3.0544e-06
1 | 4114281 | 2015-03-23 08:13 | 2015-03-23 11:46 | 213 | 213 | 2949 | 0.0090193 | 0.00065144 | Restore Supply on Device T31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730389 | 23/03 8.26am - Claire from 1730 Upper AUROA ROAD. Customer noticed lines on fire. She advised the flames has gone off. The lines were down the road from her house. Advised Control. Contact ID 4114501 rolled up to old oms job 4056274, therefore had to cop | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 13.8451 | 10.8451 | 2310 | 0.0070557 | 0.00065059 | 2015-03-23 | C | 0.0070557 | 0.00065059 | 2015 | 2015-03-23 | C | 213 | 0.0070557 | 0.00065059
1 | 3715388 | 2015-03-23 09:16 | 2015-03-23 15:24 | 368.1667 | 39 | 14358.5 | 0.043914 | 0.00011928 | NAPA ID:06093 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole F12491 | To replace 11kV and LV cross arms and hardware on existing 11kV lines. Works location: Tower Rd Matamata. WO 10148256. ABS TEMP07 failed to close during restoration switching. DNO created & job closed. Northpower to repair ABS under emergency live line pe | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 368.1667 | 365.1667 | 14241.5 | 0.0435 | 0.00011912 | 2015-03-23 | B | 0.02175 | 5.9561e-05 | 2015 | 2015-03-23 | B | 39 | 0.0435 | 0.00011912
1 | 4115088 | 2015-03-23 11:47 | 2015-03-23 12:15 | 28 | 153 | 4284 | 0.013102 | 0.00046794 | Restore Supply on Device SD4-293 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | SD4-293 | Reconnected cable to transformer TD4-134 | F3 | MAUNGATAPU | WELCOME BAY SUB | TP_KAITIMAKO | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 28 | 25 | 3825 | 0.011683 | 0.00046733 | 2015-03-23 | C | 0.011683 | 0.00046733 | 2015 | 2015-03-23 | C | 153 | 0.011683 | 0.00046733
1 | 4115957 | 2015-03-23 17:58 | 2015-03-23 23:14 | 315.55 | 249 | 36861.3667 | 0.11274 | 0.00076155 | Restore Supply on Device TA9 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Poles 715956 & 716047 | CB TA9 tripped to L/O - E/F flag - 2 x 1 r requested Two Faults found isulators replaced at Poles 715956 & 716047 - Isolated at ABS's TA916, TA914 & TA876 - Back feed installed via ABS TA928 - used 6x HV insulators | F4 | TE KIRI | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 148.0376 | 145.0376 | 36114.3667 | 0.11031 | 0.00076055 | 2015-03-23 | C | 0.11031 | 0.00076055 | 2015 | 2015-03-23 | C | 249 | 0.11031 | 0.00076055
1 | 4115703 | 2015-03-23 19:10 | 2015-03-23 21:00 | 110 | 1 | 110 | 0.00033643 | 3.0584e-06 | Restore Supply on Device TC4364 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | S12515 | Crossarm is going to fall any minute, Colin has taken photos and needs bucket truck to attend to replace crossarm. Colin will stay onsite. REPLACED CROSS ARM. No other assets repaired or replaced. Adjacent assets ok.at 19:10, Matatoki Sub, CB 1 Kopu Feede | F1/F4 | KOPU | MATATOKI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 110 | 107 | 107 | 0.00032682 | 3.0544e-06 | 2015-03-23 | C | 0.00032682 | 3.054e-06 | 2015 | 2015-03-23 | C | 1 | 0.00032682 | 3.0544e-06
1 | 4116212 | 2015-03-23 19:45 | 2015-03-23 21:17 | 91.65 | 1306 | 46597.35 | 0.14251 | 0.0039943 | Restore Supply on Device T354 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TRansformer T354 | Tx T354 making snapping and popping noises outside ppty. 124 West St, Greytown 6.05pm advised svs hub & control. Broken DDO holder on 11kv side of TX - will need to replace 3x 20amp ddo fuses & needs bucket truck. 11 kV Lines Isolated at ABS's S331, S304 | F3 | WEST ST | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 35.6794 | 32.6794 | 42679.35 | 0.13036 | 0.0039891 | 2015-03-23 | C | 0.13036 | 0.0039891 | 2015 | 2015-03-23 | C | 1306 | 0.13036 | 0.0039891
1 | 4117274 | 2015-03-23 19:50 | 2015-03-23 20:49 | 58.7667 | 34 | 1964.85 | 0.0060093 | 0.00010399 | Restore Supply on Device 7601 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 7301 | 11KV JUMPER BROKEN 2R REQUESTED. Isolated at Links 7601 - Jumper repaired - Used 3 Sleeves and 1 Mtr of conductor. Associated with 4116665. | F3/F4 | PARK RD | CLAREVILLE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 57.7897 | 54.7897 | 1862.85 | 0.0056899 | 0.00010385 | 2015-03-23 | C | 0.0056899 | 0.00010385 | 2015 | 2015-03-23 | C | 34 | 0.0056899 | 0.00010385
1 | 4117311 | 2015-03-23 20:14 | 2015-03-24 04:10 | 475.8667 | 775 | 97654.65 | 0.29867 | 0.0023703 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | Pole 215011 & 215009 | at 20:14, Matapihi Sub, CB 7 Te Maunga Feeder, Tripped, A & B O/C, L/O. Emergency calls came in of a Car Vs Pole on Maunganui Rd. Faultmen dispatched to site. Isolated at Sw/gear SD4-695 & SD4-430, ABS SD5-041, SD5-064 & SD5-057. Backfeeds supplied from M | F3 | TE MAUNGA | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 126.006 | 123.006 | 95329.65 | 0.29118 | 0.0023672 | 2015-03-23 | C | 0.29118 | 0.0023672 | 2015 | 2015-03-23 | C | 775 | 0.29118 | 0.0023672
1 | 3968141 | 2015-03-24 09:15 | 2015-03-24 14:34 | 319 | 158 | 50402 | 0.15415 | 0.00048323 | NAPA ID:05689 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220104 | Replace pole 220104 & Install a new ABS. Works location: Kaiati Falls Road. WO 10148379. | F4 | REID RD | PAPAMOA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 319 | 316 | 49928 | 0.1525 | 0.0004826 | 2015-03-24 | B | 0.076251 | 0.0002413 | 2015 | 2015-03-24 | B | 158 | 0.1525 | 0.0004826
1 | 3856609 | 2015-03-24 09:30 | 2015-03-24 14:11 | 281 | 108 | 30348 | 0.092817 | 0.00033031 | NAPA ID:05975 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 535 | run new wire between 11kv ABS 37 and 11kv ABS 535(main isolations are in work schedule as i couldnt change phasing and equipment doc). Work slocation: Wairau Rd. WO 10154759 | F3 | OAKURA | OAKURA SUB | TP_CARRINGTON | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 281 | 278 | 30024 | 0.091706 | 0.00032988 | 2015-03-24 | B | 0.045853 | 0.00016494 | 2015 | 2015-03-24 | B | 108 | 0.091706 | 0.00032988
1 | 3799634 | 2015-03-24 09:42 | 2015-03-24 15:40 | 357.9167 | 14 | 5010.8333 | 0.015325 | 4.2818e-05 | NAPA ID:05957 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC1424 | To replace 11kV and LV cross arms. Upgrade existing transformers TC4990 and TC5600 to 50kVa. Works locatioN: Washbourne Rd Morrinsville. WO 30000212 | F4 | KEREONE | PIAKO SUB | TP_PIAKO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 357.9167 | 354.9167 | 4968.8333 | 0.015177 | 4.2762e-05 | 2015-03-24 | B | 0.0075885 | 2.1381e-05 | 2015 | 2015-03-24 | B | 14 | 0.015177 | 4.2762e-05
1 | 3944416 | 2015-03-24 09:54 | 2015-03-24 15:05 | 311 | 4 | 1244 | 0.0038047 | 1.2234e-05 | NAPA ID:03950 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV L53 | Install new D/pole and TX install 3 x new 11kv poles. Works location: Ruakawa St WO 10162444 Tenix only arrived at 09:46 to start switching. | F4 | OROUA DOWNS | SANSON SUB | TP_BUNNYTHORPE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 311 | 308 | 1232 | 0.0037631 | 1.2218e-05 | 2015-03-24 | B | 0.0018815 | 6.109e-06 | 2015 | 2015-03-24 | B | 4 | 0.0037631 | 1.2218e-05
1 | 4121872 | 2015-03-24 09:59 | 2015-03-24 11:04 | 64.5333 | 393 | 12214.3 | 0.037356 | 0.001202 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 8 | CB 8 triped no flags, line was patrol and no fault was found. at time of tripping CB 8 had a HLT applied so Live Line work could be done so CB 8 would not be able to auto reclose, a back beed was put in place by opening Recloser 4222/2 and closing Reclose | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 31.0796 | 28.0796 | 11035.3 | 0.033706 | 0.0012004 | 2015-03-24 | C | 0.033706 | 0.0012004 | 2015 | 2015-03-24 | C | 393 | 0.033706 | 0.0012004
1 | 3969931 | 2015-03-24 13:18 | 2015-03-24 15:00 | 102 | 4 | 408 | 0.0012478 | 1.2234e-05 | NAPA ID:05787 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC-093 | Afternoon To replace TC2-093. Works location: Apita Station Rd. WO 10147830. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 102 | 99 | 396 | 0.0012096 | 1.2218e-05 | 2015-03-24 | B | 0.00060478 | 6.109e-06 | 2015 | 2015-03-24 | B | 4 | 0.0012096 | 1.2218e-05
1 | 4125096 | 2015-03-24 14:38 | 2015-03-24 15:06 | 27.8333 | 2990 | 79322.1667 | 0.2426 | 0.0091447 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T1 Tapchanger Buchholz. | CB 3043, CB 1 & CB 2 all tripped at the sub on tapchanger Buchholz flags. Sub was back feed via ABS's 702 & 998 to restore supply, faultman found that tripping was caused by tapchanger relay that was connected on the 17&18/03/15, under NAPA 7237 to to up | F2 | WANGANUI EAST LS | WANGANUI EAST SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 26.5292 | 23.5292 | 70352.1667 | 0.21489 | 0.0091327 | 2015-03-24 | C | 0.21489 | 0.0091327 | 2015 | 2015-03-24 | C | 2990 | 0.21489 | 0.0091327
1 | 4126617 | 2015-03-24 19:10 | 2015-03-24 20:53 | 103 | 8 | 824 | 0.0025201 | 2.4467e-05 | Restore Supply on Device 3191T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 740513 | Repaired jumper at Pole 740513 1 M 16mm Conductor 2 x Line taps | F5 | CLOTON RD SOUTH | CLOTON RD SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 103 | 100 | 800 | 0.0024435 | 2.4435e-05 | 2015-03-24 | C | 0.0024435 | 2.4435e-05 | 2015 | 2015-03-24 | C | 8 | 0.0024435 | 2.4435e-05
1 | 3903112 | 2015-03-25 08:51 | 2015-03-25 14:25 | 334.55 | 49 | 16392.95 | 0.050137 | 0.00014986 | NAPA ID:06805 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 262428 | Replace 11kV poles, crossarms and conductors. Works location: Esdaile Rd. WO 10146566 | F4 | PAHOIA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 334.55 | 331.55 | 16245.95 | 0.049622 | 0.00014967 | 2015-03-25 | B | 0.024811 | 7.4833e-05 | 2015 | 2015-03-25 | B | 49 | 0.049622 | 0.00014967
1 | 4015219 | 2015-03-25 08:52 | 2015-03-25 15:39 | 407.6833 | 50 | 20384.1667 | 0.062343 | 0.00015292 | NAPA ID:06090 TP_KINLEITH GXP > BAIRD ROAD SUB > DALMENY ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC3064 | AP1: Replace existing SD units with Safelink CFCC unit, 9896. Also replace TC4241. TP1: Test the 11kV cables connected to the new Safelink. Cables connected to 9896/1 and 9896/3 may not be ready for testing depending on the available time. AP2: Complet | F2/F3 | DALMENY ST | BAIRD ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 407.6833 | 404.6833 | 20234.1667 | 0.061804 | 0.00015272 | 2015-03-25 | B | 0.030902 | 7.6361e-05 | 2015 | 2015-03-25 | B | 50 | 0.061804 | 0.00015272
1 | 3916816 | 2015-03-25 09:00 | 2015-03-25 15:15 | 375 | 37 | 13875 | 0.042436 | 0.00011316 | NAPA ID:06821 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2456 | Replacement of 11kv T2456. Works location: Churchill Crescent Featherson. WO 10157264 Job had over run due to Tech difficulties | F3/F4 | REVANS ST | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 375 | 372 | 13764 | 0.042041 | 0.00011301 | 2015-03-25 | B | 0.021021 | 5.6507e-05 | 2015 | 2015-03-25 | B | 37 | 0.042041 | 0.00011301
1 | 4115061 | 2015-03-25 10:08 | 2015-03-25 12:50 | 162.15 | 52 | 8431.8 | 0.025788 | 0.00015904 | NAPA ID:08036 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole M2088 | Replace pole M2088 hit by car, pole is no longer there and needs to be replace as conductors do not have legal ground clearance. Works location: SHWY 1 Putaruru. WO: Unknown | F4 | LICHFIELD | PUTARURU SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 162.15 | 159.15 | 8275.8 | 0.025278 | 0.00015883 | 2015-03-25 | B | 0.012639 | 7.9415e-05 | 2015 | 2015-03-25 | B | 52 | 0.025278 | 0.00015883
1 | 4131100 | 2015-03-25 10:19 | 2015-03-25 10:58 | 38.7667 | 3 | 116.3 | 0.00035569 | 9.1753e-06 | Restore Supply on Device TE7-033 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE7 072 | Pole on the road as a cable that is glowing blue and sparking. 8.04am advised Joanne at svs hub & control. FM advise: shutdown to HV line. Em switching to repair burnt. Connection at fuses SE7 072, isolation at Fuses SE7 072 ( no back feeds ). Repairs com | F4 | OLD COACH RD | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 38.7667 | 35.7667 | 107.3 | 0.00032774 | 9.1633e-06 | 2015-03-25 | C | 0.00032774 | 9.163e-06 | 2015 | 2015-03-25 | C | 3 | 0.00032774 | 9.1633e-06
1 | 4132356 | 2015-03-25 11:51 | 2015-03-25 15:54 | 243.2833 | 216 | 2232.6667 | 0.0068284 | 0.00066062 | Restore Supply on Device T31 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730288 | 1 x A/R on CB T31 - E/F & O/C flags - line patrol required on feeder - 1 r requested. Broken crossarm and fauly insulator located on pole 730288 during line patrol. Possible damage caused by recent lightning strikes in area. Line isolated at ABS 5977 & | F4 | RIVERLEA | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 10.3364 | 7.3364 | 1584.6667 | 0.0048402 | 0.00065976 | 2015-03-25 | C | 0.0048402 | 0.00065976 | 2015 | 2015-03-25 | C | 216 | 0.0048402 | 0.00065976
1 | 4132635 | 2015-03-25 12:19 | 2015-03-25 17:25 | 306.55 | 713 | 89846.8833 | 0.27479 | 0.0021807 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Sw/gear IC3073 | CB 7 tripped to L/O - ITOC & Ground fault flags - 2 x 1 r requested. Report of explosion at switchgear IC3068/IC3073/IC3066 - unit isolated at sw/gear 9598/3 & 9896/3 to inspect unit. Evidence of blowout on one of the cable terminations in the switch were | F3 | MOSSOPS RD | MARAETAI ROAD SUB | TP_KINLEITH | Valley | EASTERN ELECTRICITY | Network (Powerco) | 126.0125 | 123.0125 | 87707.8833 | 0.2679 | 0.0021778 | 2015-03-25 | C | 0.2679 | 0.0021778 | 2015 | 2015-03-25 | C | 713 | 0.2679 | 0.0021778
1 | 4134219 | 2015-03-26 00:22 | 2015-03-26 00:38 | 15.3167 | 261 | 3997.65 | 0.012227 | 0.00079825 | Restore Supply on Device RC24 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | RC24 | Recloser RC24 L/O Reclosed | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 15.3167 | 12.3167 | 3214.65 | 0.0098189 | 0.0007972 | 2015-03-26 | C | 0.0098189 | 0.00079721 | 2015 | 2015-03-26 | C | 261 | 0.0098189 | 0.0007972
1 | 4100061 | 2015-03-26 07:03 | 2015-03-26 17:12 | 608.55 | 16 | 312.8 | 0.00095667 | 4.8935e-05 | NAPA ID:07934 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1601, X946, X4007, X465 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 19.55 | 16.55 | 264.8 | 0.00080881 | 4.8871e-05 | 2015-03-26 | B | 0.00040441 | 2.4435e-05 | 2015 | 2015-03-26 | B | 16 | 0.00080881 | 4.8871e-05
1 | 3745075 | 2015-03-26 08:45 | 2015-03-26 13:43 | 298 | 125 | 37250 | 0.11393 | 0.0003823 | NAPA ID:06089 TP_CARRINGTON GXP > KATERE SUB > KATERE 10 | 11000 | PLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | between pole 377019 to 749363 | reconductor between pole 377019 to 749363 | F3/F4 | MIRO ST | AKURA SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 298 | 295 | 36875 | 0.11263 | 0.0003818 | 2015-03-26 | B | 0.056316 | 0.0001909 | 2015 | 2015-03-26 | B | 125 | 0.11263 | 0.0003818
1 | 4135133 | 2015-03-26 09:11 | 2015-03-26 12:53 | 222.6167 | 1 | 222.6167 | 0.00068086 | 3.0584e-06 | Restore Supply on Device Y4404 | 6600 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | y4404 | replace 6 amp ht fuse. cause: unknown, possibly bird strike. tx y4404. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | RAETIHI | TP_OHAKUNE | TP_OHAKUNE | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 222.6167 | 219.6167 | 219.6167 | 0.0006708 | 3.0544e-06 | 2015-03-26 | C | 0.0006708 | 3.054e-06 | 2015 | 2015-03-26 | C | 1 | 0.0006708 | 3.0544e-06
1 | 4015253 | 2015-03-26 09:50 | 2015-03-26 14:00 | 250 | 3 | 750 | 0.0022938 | 9.1753e-06 | NAPA ID:07665 TP_HINUERA GXP > LAKE ROAD SUB > RANGITANUKU RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1304 | To replace Pole E0614 in increase the ground clearance of the conductors (LV only 3.5M From the Ground, In Paddock) due to the existing pole leaning and only a 9M pole. Farmer is aware of the safety issue and wants it fixed ASAP. Works location: Waiomou R | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 250 | 247 | 741 | 0.0022633 | 9.1633e-06 | 2015-03-26 | B | 0.0011317 | 4.582e-06 | 2015 | 2015-03-26 | B | 3 | 0.0022633 | 9.1633e-06
1 | 4133608 | 2015-03-26 10:15 | 2015-03-26 12:15 | 120 | 3 | 360 | 0.001101 | 9.1753e-06 | NAPA ID:08125 TP_OPUNAKE GXP > TASMAN SUB > OAONUI | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3005 | Replace 11kV Transformer T3005. Works location: South Rd Opunake WO 10162610 | F3 | OAONUI | TASMAN SUB | TP_OPUNAKE | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 120 | 117 | 351 | 0.0010721 | 9.1633e-06 | 2015-03-26 | B | 0.00053605 | 4.582e-06 | 2015 | 2015-03-26 | B | 3 | 0.0010721 | 9.1633e-06
1 | 4006538 | 2015-03-26 13:00 | 2015-03-26 14:25 | 85 | 2 | 170 | 0.00051993 | 6.1168e-06 | NAPA ID:05786 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-179 | Afternoon to replace TC2-179. Works location:12 Sargent Road and 4 Turner Road. WO 10147830. | F4 | MOTUROA 2 | MOTUROA SUB | TP_NEW PLYMOUTH | TARANAKI | WESTERN ELECTRICITY | Network (Powerco) | 85 | 82 | 164 | 0.00050093 | 6.1088e-06 | 2015-03-26 | B | 0.00025046 | 3.054e-06 | 2015 | 2015-03-26 | B | 2 | 0.00050093 | 6.1088e-06
1 | 4135526 | 2015-03-26 17:02 | 2015-03-26 20:55 | 233.0333 | 1 | 233.0333 | 0.00071271 | 3.0584e-06 | Restore Supply on Device 7227 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | T2045 | 2 HV Fuses blown at 7227 - patrolled carried out but nothing found. Reloaded / relivened but 1 fuse tripped. Transformer T2045 HV fuses open. Reloaded / relivened Fuses 7227 OK. (2 at 10A). Further investigation found dead bird on LV bushings - damaged Tr | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 233.0333 | 230.0333 | 230.0333 | 0.00070262 | 3.0544e-06 | 2015-03-26 | C | 0.00070262 | 3.054e-06 | 2015 | 2015-03-26 | C | 1 | 0.00070262 | 3.0544e-06
1 | 4135535 | 2015-03-26 17:37 | 2015-03-26 19:20 | 102.3167 | 261 | 23693.25 | 0.072464 | 0.00079825 | Restore Supply on Device RC24 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | O4023 | Customer called advising he had seen a flash from the nearest pole from the house outside 77 Baigent Rd - from TX TC472. Found possum on pole O4203 which was removed. Relivened. C Pepper attended. | F4 | MANGATARATA | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 90.7787 | 87.7787 | 22910.25 | 0.069978 | 0.0007972 | 2015-03-26 | C | 0.069978 | 0.00079721 | 2015 | 2015-03-26 | C | 261 | 0.069978 | 0.0007972
1 | 4136650 | 2015-03-26 19:49 | 2015-03-26 22:18 | 149 | 176 | 26224 | 0.080204 | 0.00053828 | Restore Supply on Device C642 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C642 | CB C642 tripped L/O no flags, line was patrolled and no fault was found. Adrian Marshall and Frank Martin attended. | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 149 | 146 | 25696 | 0.078486 | 0.00053758 | 2015-03-26 | C | 0.078486 | 0.00053758 | 2015 | 2015-03-26 | C | 176 | 0.078486 | 0.00053758
1 | 4137223 | 2015-03-26 20:09 | 2015-03-26 22:40 | 151.4333 | 5 | 314.3667 | 0.00096147 | 1.5292e-05 | Restore Supply on Device 5028 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 763352 | Faultman found a damaged insulator on pole 763352, after testing that it was not a fault on the customers side as Tenix had been to this site earlier in the week. 1 x 11kV insulator replaced & 1 x 3 Amp HV fuse. Chris Viviers attended. | F4 | TIKORANGI | WAITARA EAST SUB | TP_HUIRANGI | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 62.8733 | 59.8733 | 299.3667 | 0.00091439 | 1.5272e-05 | 2015-03-26 | C | 0.00091439 | 1.5272e-05 | 2015 | 2015-03-26 | C | 5 | 0.00091439 | 1.5272e-05
1 | 4137274 | 2015-03-26 23:53 | 2015-03-27 13:13 | 799.4 | 92 | 8850.65 | 0.027069 | 0.00028137 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 817047 | Tripping on recloser 8156 on A Phase O/C, E/F. Area patrolled and sectionalised with one blown insulator found with Isolation required from fuses 7360. Insulator replaced, relivened OK. Extended outage due to terrain / difficult to find (2nd response) | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 96.2027 | 93.2027 | 8574.65 | 0.026191 | 0.00028101 | 2015-03-26 | C | 0.026191 | 0.00028101 | 2015 | 2015-03-26 | C | 92 | 0.026191 | 0.00028101
1 | 4137480 | 2015-03-27 02:40 | 2015-03-27 03:06 | 26.2167 | 91 | 2385.7167 | 0.0072965 | 0.00027832 | Restore Supply on Device 2 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB 8156 | CB 8156 tripped. Associated with 4137274 | F3/F5 | COLOGNE ST | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 26.2167 | 23.2167 | 2112.7167 | 0.0064531 | 0.00027795 | 2015-03-27 | C | 0.0064531 | 0.00027795 | 2015 | 2015-03-27 | C | 91 | 0.0064531 | 0.00027795
1 | 4133599 | 2015-03-27 09:20 | 2015-03-27 10:00 | 40 | 2 | 80 | 0.00024467 | 6.1168e-06 | NAPA ID:08104 TP_STRATFORD GXP > KAPONGA SUB > PALMER RD | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 2243T | Upgrade Tx 2243T from 15Kva to 30Kva (customer has voltage issues). Works location: Lower Palmer Rd Kaponga. WO 30006646. Off Time 09:20. On Time 10:00 | F4 | RANGITANUKU RD | LAKE ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 40 | 37 | 74 | 0.00022603 | 6.1088e-06 | 2015-03-27 | B | 0.00011301 | 3.054e-06 | 2015 | 2015-03-27 | B | 2 | 0.00022603 | 6.1088e-06
1 | 3915598 | 2015-03-27 09:24 | 2015-03-27 14:56 | 332 | 2 | 664 | 0.0020308 | 6.1168e-06 | NAPA ID:06055 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1434 | To install 11kV Line Break at Pole # F0367 and replace 11kV cross arms on existing spur line. This OMS Parent ID 3915598 supersedes 3715408. Work Order 10148256. Work Location: Tower Road. | F4 | GORDON | TOWER ROAD SUB | TP_HINUERA | Valley | EASTERN ELECTRICITY | Network (Powerco) | 332 | 329 | 658 | 0.0020098 | 6.1088e-06 | 2015-03-27 | B | 0.0010049 | 3.054e-06 | 2015 | 2015-03-27 | B | 2 | 0.0020098 | 6.1088e-06
1 | 4071487 | 2015-03-27 09:55 | 2015-03-27 10:58 | 63 | 3 | 189 | 0.00057804 | 9.1753e-06 | NAPA ID:05683 TP_TAURANGA 33 GXP > AONGATETE SUB > APATA | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-199 | Replace transformer TC2-199. Work Location: 26 Wainui South Road. Work Order 10147830. | F4/F1 | APATA | AONGATETE SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 63 | 60 | 180 | 0.0005498 | 9.1633e-06 | 2015-03-27 | B | 0.0002749 | 4.582e-06 | 2015 | 2015-03-27 | B | 3 | 0.0005498 | 9.1633e-06
1 | 4143107 | 2015-03-27 12:59 | 2015-03-27 14:41 | 101.8833 | 1 | 101.8833 | 0.0003116 | 3.0584e-06 | Restore Supply on Device 4553T | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 739127 | Replace 2 x 3 amp ddo fuses. pole 739127. cause: possum. No other assets repaired or replaced on site. Adjacent assets are checked and are up to Powerco standard. | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 101.8833 | 98.8833 | 98.8833 | 0.00030203 | 3.0544e-06 | 2015-03-27 | C | 0.00030203 | 3.054e-06 | 2015 | 2015-03-27 | C | 1 | 0.00030203 | 3.0544e-06
1 | 4100065 | 2015-03-27 16:30 | 2015-03-27 16:39 | 9 | 16 | 144 | 0.00044041 | 4.8935e-05 | NAPA ID:07935 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2835 | Replacing poles and equipment on spur line supplying Tx's X1601, X4036, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. NOTE; Total outage for transformers only 5 minutes each - Total 20 mins. | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 9 | 6 | 96 | 0.00029322 | 4.8871e-05 | 2015-03-27 | B | 0.00014661 | 2.4435e-05 | 2015 | 2015-03-27 | B | 16 | 0.00029322 | 4.8871e-05
1 | 4143923 | 2015-03-28 00:49 | 2015-03-28 02:35 | 105.9667 | 6 | 255.1333 | 0.00078031 | 1.8351e-05 | Restore Supply on Device T1581 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7495 | Faultman found 2 blown fuses at Fuses 7495, line was patrolled and a dead duck was found under the line. 2x10 Amp fuses replaced. | F4 | MOROA | KEMPTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 42.5222 | 39.5222 | 237.1333 | 0.00072431 | 1.8327e-05 | 2015-03-28 | C | 0.00072431 | 1.8327e-05 | 2015 | 2015-03-28 | C | 6 | 0.00072431 | 1.8327e-05
1 | 4144009 | 2015-03-28 10:41 | 2015-03-28 11:48 | 67 | 176 | 11792 | 0.036065 | 0.00053828 | Restore Supply on Device C642 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810548 | Broken Isulator found at Pole 810548 during line being flown yesterday - Isolated at ABS C642/1 and Links C642/6 - Insulator replaced - Used 1x HV isulator and pin, 1x binder | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 67 | 64 | 11264 | 0.034405 | 0.00053758 | 2015-03-28 | C | 0.034405 | 0.00053758 | 2015 | 2015-03-28 | C | 176 | 0.034405 | 0.00053758
1 | 4143983 | 2015-03-28 10:49 | 2015-03-28 11:12 | 23.2667 | 10 | 232.6667 | 0.00071159 | 3.0584e-05 | Restore Supply on Device TE8-034 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SE8-007 | 2 fuses blown at SE8-007. Isolated check cable terminations, reloaded & livened, unknown fault possible bird strike. Material 2 x 15amp HV fuses, 2 x 35mm saddles etc. | F4 | OTAMARAKAU | PONGAKAWA SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 23.2667 | 20.2667 | 202.6667 | 0.00061903 | 3.0544e-05 | 2015-03-28 | C | 0.00061903 | 3.0544e-05 | 2015 | 2015-03-28 | C | 10 | 0.00061903 | 3.0544e-05
1 | 4144304 | 2015-03-28 11:51 | 2015-03-28 14:05 | 134.1833 | 1 | 134.1833 | 0.00041039 | 3.0584e-06 | Restore Supply on Device T452 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T452 | Job Part of OMS 4144009, unable to contact customer so faultman sent to confirm - no fault found | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 134.1833 | 131.1833 | 131.1833 | 0.00040069 | 3.0544e-06 | 2015-03-28 | C | 0.00040069 | 3.054e-06 | 2015 | 2015-03-28 | C | 1 | 0.00040069 | 3.0544e-06
1 | 4144340 | 2015-03-28 12:21 | 2015-03-28 13:24 | 63.1167 | 23 | 1451.6833 | 0.0044399 | 7.0344e-05 | Restore Supply on Device S1202 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811665 | Broken Binder found at Pole 811665 during line being flown yesterday - Isolater at ABS S1202 - Binder Replaced and feeder returned to service - Used 1 x binder | F5 | TUTURUMURI | HAU NUI SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 63.1167 | 60.1167 | 1382.6833 | 0.0042233 | 7.0252e-05 | 2015-03-28 | C | 0.0042233 | 7.0252e-05 | 2015 | 2015-03-28 | C | 23 | 0.0042233 | 7.0252e-05
1 | 4147348 | 2015-03-28 18:09 | 2015-03-29 07:18 | 789.15 | 601 | 16056.5 | 0.049108 | 0.0018381 | Restore Supply on Device 4 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB8 | Patrolled Nothing found | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 26.7163 | 23.7163 | 14253.5 | 0.043536 | 0.0018357 | 2015-03-28 | C | 0.043536 | 0.0018357 | 2015 | 2015-03-28 | C | 601 | 0.043536 | 0.0018357
1 | 4144561 | 2015-03-28 21:30 | 2015-03-28 21:34 | 4.4833 | 1 | 4.4833 | 1.3712e-05 | 3.0584e-06 | Restore Supply on Device TC4959 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses FC2480 | Replaced 2 x 2A H/V, O/H Fues at FC2480 suspect birds all service restored | F4 | WAIHI BEACH RD | WAIHI SUB | TP_WAIKINO | Valley | EASTERN ELECTRICITY | Network (Powerco) | 4.4833 | 1.4833 | 1.4833 | 4.5307e-06 | 3.0544e-06 | 2015-03-28 | C | 4.531e-06 | 3.054e-06 | 2015 | 2015-03-28 | C | 1 | 4.5307e-06 | 3.0544e-06
1 | 4144573 | 2015-03-29 01:58 | 2015-03-29 08:38 | 399.9833 | 1 | 399.9833 | 0.0012233 | 3.0584e-06 | Restore Supply on Device TE5-214 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 223348 | 2x 3amp hv fuses. Short circuit on low voltage repaired - separated & insulated. Pole 223348. Full power restored. Nothing else repaired or replaced. Adjacent assets - ok. | F3 | NO 3 ROAD | ATUAROA AVE SUB | TP_TE MATAI | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 399.9833 | 396.9833 | 396.9833 | 0.0012126 | 3.0544e-06 | 2015-03-29 | C | 0.0012126 | 3.054e-06 | 2015 | 2015-03-29 | C | 1 | 0.0012126 | 3.0544e-06
1 | 4144620 | 2015-03-29 04:55 | 2015-03-29 07:47 | 172 | 1100 | 156147.25 | 0.47756 | 0.0033643 | Restore Supply on Device 5 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 | CB Tripeed on O/C. Patrolled and nothing found. | F2 | KINGS AVENUE | BEACH RD SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 141.952 | 138.952 | 152847.25 | 0.46686 | 0.0033599 | 2015-03-29 | C | 0.46686 | 0.0033599 | 2015 | 2015-03-29 | C | 1100 | 0.46686 | 0.0033599
1 | 4145723 | 2015-03-29 05:11 | 2015-03-29 07:26 | 135.0333 | 1046 | 122079.1 | 0.37337 | 0.0031991 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 8 | CB8 tripped on Ph B, O/C and E/F. Patrolled and nothing found. | F3 | PURIRI ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 116.7104 | 113.7104 | 118941.1 | 0.3633 | 0.0031949 | 2015-03-29 | C | 0.3633 | 0.0031949 | 2015 | 2015-03-29 | C | 1046 | 0.3633 | 0.0031949
1 | 4149594 | 2015-03-29 06:58 | 2015-03-29 08:38 | 100.2 | 20 | 1972.0167 | 0.0060313 | 6.1168e-05 | Restore Supply on Device 7205 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7205 | Patrolled & Found Nothing Reloaded & Relivened | F4 | TAWAHA | MARTINBOROUGH SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 98.6008 | 95.6008 | 1912.0167 | 0.0058401 | 6.1088e-05 | 2015-03-29 | C | 0.0058401 | 6.1088e-05 | 2015 | 2015-03-29 | C | 20 | 0.0058401 | 6.1088e-05
1 | 4149948 | 2015-03-29 08:20 | 2015-03-29 09:51 | 91.25 | 284 | 20822 | 0.063682 | 0.00086859 | Restore Supply on Device 1087 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 4 |  | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 73.3169 | 70.3169 | 19970 | 0.060997 | 0.00086746 | 2015-03-29 | C | 0.060997 | 0.00086746 | 2015 | 2015-03-29 | C | 284 | 0.060997 | 0.00086746
1 | 4149638 | 2015-03-29 08:30 | 2015-03-29 15:08 | 398 | 2 | 796 | 0.0024345 | 6.1168e-06 | Restore Supply on Device C215 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T4268 |  | F2 | MASONIC | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 398 | 395 | 790 | 0.002413 | 6.1088e-06 | 2015-03-29 | C | 0.002413 | 6.109e-06 | 2015 | 2015-03-29 | C | 2 | 0.002413 | 6.1088e-06
1 | 4105064 | 2015-03-29 09:00 | 2015-03-29 15:33 | 392.9667 | 14 | 5501.5333 | 0.016826 | 4.2818e-05 | NAPA ID:07400 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | Replace poles on 33kv/11kv line between pole 386633 and 229388 | F4 | BRUCE RD | TE MAUNGA SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 392.9667 | 389.9667 | 5459.5333 | 0.016676 | 4.2762e-05 | 2015-03-29 | B | 0.0083379 | 2.1381e-05 | 2015 | 2015-03-29 | B | 14 | 0.016676 | 4.2762e-05
1 | 4151019 | 2015-03-29 10:27 | 2015-03-29 12:59 | 151.65 | 7 | 496.65 | 0.001519 | 2.1409e-05 | Restore Supply on Device T9/144 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P04908 | Check if affects OMS 4151029 Tx T9/140, 4151051 Tx T9/152, 4151064 Tx T9/137, 4151075 Tx T9/132, 4151079 Tx T9/151, 4151086 Tx T9/127, Issue could be at V41 - advised Sammy at svs hub. Removed bird from Pole P04908 transformer T9/124 Closed Sectionser V4 | F5 | WAIONE | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 70.95 | 67.95 | 475.65 | 0.0014528 | 2.1381e-05 | 2015-03-29 | C | 0.0014528 | 2.1381e-05 | 2015 | 2015-03-29 | C | 7 | 0.0014528 | 2.1381e-05
1 | 4151703 | 2015-03-29 14:40 | 2015-03-29 17:48 | 188.3667 | 284 | 18852.0167 | 0.057657 | 0.00086859 | Restore Supply on Device 1087 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NO FAULT FOUND | CB 1087 | Ongoing feeder fault with trippings at CB1087. Area backfed with ABS 2671 open to reduce faulted area. | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 66.3803 | 63.3803 | 18000.0167 | 0.05498 | 0.00086746 | 2015-03-29 | C | 0.05498 | 0.00086746 | 2015 | 2015-03-29 | C | 284 | 0.05498 | 0.00086746
1 | 4152719 | 2015-03-29 16:00 | 2015-03-29 17:17 | 77.1833 | 1 | 77.1833 | 0.00023606 | 3.0584e-06 | Restore Supply on Device T2013 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7105 | reload reliven 2 x 10 amp | F5 | WERAITI | TE ORE ORE SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 77.1833 | 74.1833 | 74.1833 | 0.00022659 | 3.0544e-06 | 2015-03-29 | C | 0.00022659 | 3.054e-06 | 2015 | 2015-03-29 | C | 1 | 0.00022659 | 3.0544e-06
1 | 4152729 | 2015-03-29 16:08 | 2015-03-29 17:17 | 69.0833 | 1 | 69.0833 | 0.00021129 | 3.0584e-06 | Restore Supply on Device 2386T | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | 836 PALMER ROAD, KAPONGA Taranaki caller advises that pole on private property has broken insulators and has caused lines to drop down low. power not affected. Access via tanker track. Advised svs hub - Sammy Emailed svs hub advised control Pole nee | F4 | PALMER RD | KAPONGA SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 69.0833 | 66.0833 | 66.0833 | 0.00020185 | 3.0544e-06 | 2015-03-29 | C | 0.00020185 | 3.054e-06 | 2015 | 2015-03-29 | C | 1 | 0.00020185 | 3.0544e-06
1 | 4152801 | 2015-03-29 18:30 | 2015-03-29 18:40 | 10 | 4 | 40 | 0.00012234 | 1.2234e-05 | Restore Supply on Device 7681 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7681 | 2 HV fuses found tripped at 7681. Reloaded / relivened OK. Suspect issue with lightning arrestor. | F2/F3 | SOUTH RD CHAPEL | CHAPEL SUB | TP_MASTERTON | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 28 | 8.5524e-05 | 1.2218e-05 | 2015-03-29 | C | 8.5524e-05 | 1.2218e-05 | 2015 | 2015-03-29 | C | 4 | 8.5524e-05 | 1.2218e-05
1 | 4152820 | 2015-03-29 19:45 | 2015-03-29 20:48 | 63.2167 | 34 | 2149.3667 | 0.0065737 | 0.00010399 | Restore Supply on Device 5370 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708554 | Reports of part power found a line down on Tahora Rd. (Bird strike - magpie at base of Pole. Conductor re-sleeved OK, relivened. NOTE: Fuses open from NOC before forcing up Bretts job which created a new No. (OOPS!!)- OMS No. will not be the same as TENI | F4 | STRATHMORE | DOUGLAS SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 63.2167 | 60.2167 | 2047.3667 | 0.0062535 | 0.00010385 | 2015-03-29 | C | 0.0062535 | 0.00010385 | 2015 | 2015-03-29 | C | 34 | 0.0062535 | 0.00010385
1 | 4152879 | 2015-03-29 20:25 | 2015-03-30 00:11 | 226.4 | 7 | 766.9667 | 0.0023457 | 2.1409e-05 | Restore Supply on Device 2292T | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738575 | Outage required from Fuses 4982 to repair one broken conductor on Wingrove Rd. Resleeved OK with about 2 metres of conductor / relivened. (Aged conductor). | F4 | NGAERE | ELTHAM SUB | TP_STRATFORD | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 109.5667 | 106.5667 | 745.9667 | 0.0022785 | 2.1381e-05 | 2015-03-29 | C | 0.0022785 | 2.1381e-05 | 2015 | 2015-03-29 | C | 7 | 0.0022785 | 2.1381e-05
1 | 4153005 | 2015-03-29 22:58 | 2015-03-30 05:46 | 408.0667 | 107 | 33572.2 | 0.10268 | 0.00032725 | Restore Supply on Device 1087 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 791841 | Tripping on recloser CB1087 on Phase A O/C, E/F. (Ongoing fault during the day - part of feeder had been backfed to help locate faulted area). Feeder patrolled and sectionalised during the night. Flash seen when relivening and blown insulator found. Isola | F4 | FORDELL | BLINK BONNIE SUB | TP_WANGANUI | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 313.7589 | 310.7589 | 33251.2 | 0.10156 | 0.00032682 | 2015-03-29 | C | 0.10156 | 0.00032682 | 2015 | 2015-03-29 | C | 107 | 0.10156 | 0.00032682
1 | 4153117 | 2015-03-29 23:43 | 2015-03-30 02:29 | 166.0833 | 1046 | 110348.6833 | 0.33749 | 0.0031991 | Restore Supply on Device 8 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 765823 | Tripping on CB8 on Phase B O./C. (Also Tripped earlier in the day but no fault found). Area patrolled / sectionalised with a blown insulator found on Maire St.(Isolation between ABS 1274, 1403 and 736). One insulator replaced / relivened OK. NOTE: Heavy | F3 | PURIRI ST | CASTLECLIFF SUB | TP_BRUNSWICK | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 105.4959 | 102.4959 | 107210.6833 | 0.32747 | 0.0031949 | 2015-03-29 | C | 0.32747 | 0.0031949 | 2015 | 2015-03-29 | C | 1046 | 0.32747 | 0.0031949
1 | 4155644 | 2015-03-30 06:00 | 2015-03-30 09:38 | 217.7833 | 2 | 328.15 | 0.0010036 | 6.1168e-06 | Restore Supply on Device T7/375 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | section fuse # t33 | *** please check if oms 4155674 - #6 Woodville Aohanga Rd is part of this outage *** replace 2 x 6 amp fuses. 2 out of 3 phases. section fuse # t33. cause: bird strike. No other assets repaired or replaced on site. Adjacent assets are checked and are up | F4/F5 | COONOOR | MANGAMUTU SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 164.075 | 161.075 | 322.15 | 0.00098398 | 6.1088e-06 | 2015-03-30 | C | 0.00098398 | 6.109e-06 | 2015 | 2015-03-30 | C | 2 | 0.00098398 | 6.1088e-06
1 | 4158808 | 2015-03-30 07:53 | 2015-03-30 08:10 | 17 | 7 | 119 | 0.00036395 | 2.1409e-05 | Restore Supply on Device TA833 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses TA833 | Fuses at Fuses TA833 - caused by fault at Transformer T5325 see OMS 4158758 | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 17 | 14 | 98 | 0.00029933 | 2.1381e-05 | 2015-03-30 | C | 0.00029933 | 2.1381e-05 | 2015 | 2015-03-30 | C | 7 | 0.00029933 | 2.1381e-05
1 | 4156079 | 2015-03-30 08:31 | 2015-03-30 14:47 | 375.5167 | 662 | 40229.0333 | 0.12304 | 0.0020247 | Restore Supply on Device 1 | 11000 | UNPLANNED | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 852977 | at 08:31, Omokoroa Sub, CB 1 Te Puna Feeder, Tripped, Ph A B C O/C, E/F, L/O. Faultmen dispatched and investigation began. Call came in from Fire service of Car V Pole in Borrell Rd at Pole 852977. Isolated Lines at Links 9805/4, ABS 9805/1 & SC3-045. Per | F4 | TE PUNA | OMOKOROA SUB | TP_TAURANGA 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 60.7689 | 57.7689 | 38243.0333 | 0.11681 | 0.002022 | 2015-03-30 | C | 0.11681 | 0.002022 | 2015 | 2015-03-30 | C | 662 | 0.11681 | 0.002022
1 | 4130856 | 2015-03-30 08:50 | 2015-03-30 14:30 | 339.7333 | 28 | 9512.5333 | 0.029093 | 8.5636e-05 | NAPA ID:06758 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A | REPLACE POLES AND ARMS ALONG MCLAREN FALLS ROAD | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 339.7333 | 336.7333 | 9428.5333 | 0.028799 | 8.5524e-05 | 2015-03-30 | B | 0.014399 | 4.2762e-05 | 2015 | 2015-03-30 | B | 28 | 0.028799 | 8.5524e-05
1 | 4157068 | 2015-03-30 12:31 | 2015-03-30 14:11 | 100 | 775 | 37733.4833 | 0.1154 | 0.0023703 | Restore Supply on Device 7 | 11000 | UNPLANNED | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | Matapihi Sub CB 7 Te Maunga Feeder | at 12:31, Matapihi Sub, CB 7 Te Maunga Feeder, Tripped, Ph C O/C, E/F, L/O. Faultman dispatched and investigation began. O/H lines patrolled. feeder sectionalised. No Fault Found. Unknown Cause. All Power Restored on completion. Clint Johnstone Attended. | F3 | TE MAUNGA | MATAPIHI SUB | TP_MT MAUNGANUI 33 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 48.6884 | 45.6884 | 35408.4833 | 0.10815 | 0.0023672 | 2015-03-30 | C | 0.10815 | 0.0023672 | 2015 | 2015-03-30 | C | 775 | 0.10815 | 0.0023672
1 | 4158758 | 2015-03-30 18:25 | 2015-03-30 20:39 | 133.7667 | 2 | 150.75 | 0.00046106 | 6.1168e-06 | Restore Supply on Device 5435E | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5325 | Job on wrong Transformer refer OMS 4158829 for replacement of transformer | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 75.375 | 72.375 | 144.75 | 0.00044213 | 6.1088e-06 | 2015-03-30 | C | 0.00044213 | 6.109e-06 | 2015 | 2015-03-30 | C | 2 | 0.00044213 | 6.1088e-06
1 | 4158792 | 2015-03-30 19:34 | 2015-03-30 22:15 | 161.2833 | 1 | 161.2833 | 0.00049327 | 3.0584e-06 | Restore Supply on Device P1060 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710056 | 2 x hv fuses 6amp due to age fuses pu 2502 pole 710056 SURROUNDING ASSET UP TO POWERCO STANDARD NOTHING ELSE REPAIRED OR REPLACED cannot see much in the dark fm advised he did work through control | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 161.2833 | 158.2833 | 158.2833 | 0.00048346 | 3.0544e-06 | 2015-03-30 | C | 0.00048346 | 3.054e-06 | 2015 | 2015-03-30 | C | 1 | 0.00048346 | 3.0544e-06
1 | 4158829 | 2015-03-30 20:38 | 2015-03-30 23:11 | 153.2167 | 3 | 459.65 | 0.0014058 | 9.1753e-06 | Restore Supply on Device T5325 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Transformer T5325 | Transformer T5325 Faulty - Isolated at own fuses for replacement - Used 1x 30kVA Transformer & 5x 3 amp HV fuses | F4 | PIHAMA | TASMAN SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 153.2167 | 150.2167 | 450.65 | 0.0013765 | 9.1633e-06 | 2015-03-30 | C | 0.0013765 | 9.163e-06 | 2015 | 2015-03-30 | C | 3 | 0.0013765 | 9.1633e-06
1 | 4158955 | 2015-03-30 21:48 | 2015-03-30 22:17 | 28.85 | 2 | 57.7 | 0.00017647 | 6.1168e-06 | Restore Supply on Device PU250 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU250 | Fuse PU250 found blown for OMS 4158792 job would not roll up when fuses opened. all futher details entered on that oms number | F4 | WAREA | PUNGAREHU SUB | TP_OPUNAKE | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 28.85 | 25.85 | 51.7 | 0.00015791 | 6.1088e-06 | 2015-03-30 | C | 0.00015791 | 6.109e-06 | 2015 | 2015-03-30 | C | 2 | 0.00015791 | 6.1088e-06
1 | 4082684 | 2015-03-31 05:30 | 2015-03-31 05:54 | 23.8333 | 57 | 1358.5 | 0.0041549 | 0.00017433 | NAPA ID:07798 TP_LINTON GXP > KAIRANGA SUB > PIONEER | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10242 | Change phasing at Switch 10242. Work Location: Maxwells Line. Work Order 10147864. | F4 | TREMAINE AVE | KAIRANGA SUB | TP_LINTON | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 23.8333 | 20.8333 | 1187.5 | 0.0036271 | 0.0001741 | 2015-03-31 | B | 0.0018136 | 8.7051e-05 | 2015 | 2015-03-31 | B | 57 | 0.0036271 | 0.0001741
1 | 4159761 | 2015-03-31 05:36 | 2015-03-31 06:00 | 24.2167 | 18 | 298.4833 | 0.00091289 | 5.5052e-05 | Restore Supply on Device WH223 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH223 | 2 fuses found blown at fuses WH223 -used 2x 8 amp HV fuses | F4 | WHAKAMARA | WHAREROA SUB | TP_HAWERA | Taranaki | WESTERN ELECTRICITY | Network (Powerco) | 16.5824 | 13.5824 | 244.4833 | 0.00074676 | 5.498e-05 | 2015-03-31 | C | 0.00074676 | 5.498e-05 | 2015 | 2015-03-31 | C | 18 | 0.00074676 | 5.498e-05
1 | 3905374 | 2015-03-31 07:00 | 2015-03-31 07:10 | 10 | 10 | 100 | 0.00030584 | 3.0584e-05 | NAPA ID:06729 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB8 Moawhango | Replacing poles and equipment on spur line supplying Tx's X465, X4007 & X946. As per Powerco Project IR6981 Moawhango Reconstruction. Works location: Kellys Rd Moawhango WO 10161206 | F4 | MOAWHANGO | TAIHAPE SUB | TP_MATAROA | Wanganui | WESTERN ELECTRICITY | Network (Powerco) | 10 | 7 | 70 | 0.00021381 | 3.0544e-05 | 2015-03-31 | B | 0.0001069 | 1.5272e-05 | 2015 | 2015-03-31 | B | 10 | 0.00021381 | 3.0544e-05
1 | 4159928 | 2015-03-31 07:53 | 2015-03-31 08:52 | 59 | 99 | 5841 | 0.017864 | 0.00030278 | Restore Supply on Device IC410 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc1380 | Kerepehi CB3, Hauraki Rd. IC 447 open and tagged to replace 1 x broken DDO at TC 1380. | F4 | HAURAKI RD | KEREPEHI SUB | TP_KOPU | Valley | EASTERN ELECTRICITY | Network (Powerco) | 59 | 56 | 5544 | 0.016934 | 0.00030239 | 2015-03-31 | C | 0.016934 | 0.00030239 | 2015 | 2015-03-31 | C | 99 | 0.016934 | 0.00030239
1 | 4073969 | 2015-03-31 09:05 | 2015-03-31 13:48 | 283 | 53 | 14999 | 0.045873 | 0.0001621 | NAPA ID:06762 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11000 | PLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-005 | REPLACE POLES AND ARMS AS PER SCOPE OF WORKS. Work Location: Keenan Road. Work Order 10148098. | F4 | KAIMAI DRIVE | TP_TAURANGA 11kV | TP_TAURANGA 11 | Tauranga | EASTERN ELECTRICITY | Network (Powerco) | 283 | 280 | 14840 | 0.045328 | 0.00016188 | 2015-03-31 | B | 0.022664 | 8.0942e-05 | 2015 | 2015-03-31 | B | 53 | 0.045328 | 0.00016188
1 | 4160121 | 2015-03-31 09:33 | 2015-03-31 09:42 | 9.2167 | 18 | 165.9 | 0.00050739 | 5.5052e-05 | Restore Supply on Device TEMP47 | 11000 | UNPLANNED | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB4 Tiraumea | Planned work NAPA id 7858. Generators supplied to all transfomers. Short shut to connect and disconnet. Replace 11kV poles and hardware, Waihoki Valley Road, Pongaroa | F4 | TIRAUMEA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 9.2167 | 6.2167 | 111.9 | 0.00034179 | 5.498e-05 | 2015-03-31 | C | 0.00034179 | 5.498e-05 | 2015 | 2015-03-31 | C | 18 | 0.00034179 | 5.498e-05
1 | 4160498 | 2015-03-31 16:56 | 2015-03-31 21:01 | 244.8333 | 6 | 2200.1667 | 0.006729 | 1.8351e-05 | Restore Supply on Device T9/24 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06230 | 6:211pm - 2 R Request as 2HV wires down and require assistance - Robin Smith to attend - Working through control. Isolated at Fuses V18 - Lines repaired - used 50 mtrs Conductor 2 x Sleeves, 4x AL 62. NDR # 19189 | F4 | HOROEKA | PONGAROA SUB | TP_MANGAMAIRE | MANAWATU | WESTERN ELECTRICITY | Network (Powerco) | 366.6944 | 363.6944 | 2182.1667 | 0.0066653 | 1.8327e-05 | 2015-03-31 | C | 0.0066653 | 1.8327e-05 | 2015 | 2015-03-31 | C | 6 | 0.0066653 | 1.8327e-05
1 | 4160550 | 2015-03-31 21:53 | 2015-04-01 16:43 | 1129.95 | 4 | 3613.65 | 0.011052 | 1.2234e-05 | Restore Supply on Device T1099 | 11000 | UNPLANNED | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1099 | Transformer T1099 found to be faulty - Customer happy for it to be replaced in the morning Replaced Pole 799665 as well as to Rotten to climb or mount Transformer On | F4 | DAIRY FACTORY | FEATHERSTON SUB | TP_GREYTOWN | WAIRARAPA | WESTERN ELECTRICITY | Network (Powerco) | 903.4125 | 900.4125 | 3601.65 | 0.011001 | 1.2218e-05 | 2015-03-31 | C | 0.011001 | 1.2218e-05 | 2015 | 2015-03-31 | C | 4 | 0.011001 | 1.2218e-05
[26 empty] | total | 277.7901 | 2.2839 | Total |  | 255.4563 | 2.1906
[26 empty] | DPP stmt | #REF! | #REF! | Variance to expected |  | -1.06e-05 | -5.6969e-05
[22 empty] | Total Planned |  |  |  |  | 44.6677 | 0.18662
[22 empty] | Toal Unplanned |  |  |  |  | 233.1224 | 2.0973
[22 empty] | Total |  |  |  |  | 277.7901 | 2.2839
[22 empty] | Expected result with planned weighted at 50% |  |  |  |  | 255.4563 | 2.1906
Formulas:
Date and time converted to Date only = INT([Interruption Date/Time])
date = INT([Interruption Date/Time])

## 2014
Fault Record ID | Interruption Date/Time | Restoration Date / Time | F_Total_interrupted_customers | Adjusted Duration | Adjusted Customer Minutes | Adjusted Interruptions | Adjusted Saidi | Adjusted Saifi | Fault Description | Planned / Unplanned | class | MOC Classification | Owner | Day | Year | disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
134008 | 41365.7049 | 41365.7778 | 661 | 102 | 27723.6 | 271.8 | 0.085384 | 0.0020358 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-01 | 2014 | 2014 | 2013-04-01 | C | 271.8 | 0.085384 | 0.0020358
134009 | 41366.3986 | 41366.4826 | 26 | 118 | 3068 | 26 | 0.009449 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 26 | 0.009449 | 8.0076e-05
134011 | 41366.5 | 41366.5403 | 5 | 55 | 275 | 5 | 0.00084696 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 5 | 0.00084696 | 1.5399e-05
134014 | 41366.3854 | 41366.4361 | 14 | 70 | 980 | 14 | 0.0030182 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 14 | 0.0030182 | 4.3118e-05
134015 | 41365.9444 | 41366.5306 | 27 | 841 | 7849.9976 | 9.3341 | 0.024177 | 8.3156e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-01 | 2014 | 2014 | 2013-04-01 | C | 9.3341 | 0.024177 | 8.3156e-05
134017 | 41366.6326 | 41366.7542 | 12 | 172 | 2236 | 13 | 0.0068865 | 3.6958e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | C | 13 | 0.0068865 | 3.6958e-05
134018 | 41366.4299 | 41366.6208 | 49 | 272 | 13328 | 49 | 0.041048 | 0.00015091 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 49 | 0.041048 | 0.00015091
134020 | 41366.3854 | 41366.6181 | 6 | 332 | 1992 | 6 | 0.006135 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 6 | 0.006135 | 1.8479e-05
134021 | 41366.3542 | 41366.6944 | 15 | 487 | 7305 | 15 | 0.022498 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 15 | 0.022498 | 4.6198e-05
134023 | 41366.375 | 41366.5778 | 69 | 289 | 19941 | 69 | 0.061415 | 0.00021251 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | B | 69 | 0.061415 | 0.00021251
134024 | 41366.7361 | 41366.7639 | 179 | 37 | 6623 | 179 | 0.020398 | 0.00055129 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | C | 179 | 0.020398 | 0.00055129
134026 | 41366.9778 | 41367.0569 | 581 | 111 | 57346.1053 | 516.6316 | 0.17662 | 0.0017894 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-02 | 2014 | 2014 | 2013-04-02 | C | 516.6316 | 0.17662 | 0.0017894
134027 | 41367.0653 | 41367.0764 | 317 | 13 | 4121 | 317 | 0.012692 | 0.00097631 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 317 | 0.012692 | 0.00097631
134028 | 41367.4583 | 41367.4715 | 1 | 16 | 16 | 1 | 4.9277e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 1 | 4.9277e-05 | 3.0798e-06
134029 | 41367.4111 | 41367.4569 | 11 | 63 | 693 | 11 | 0.0021343 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 11 | 0.0021343 | 3.3878e-05
134030 | 41367.4375 | 41367.5 | 7 | 87 | 609 | 7 | 0.0018756 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 7 | 0.0018756 | 2.1559e-05
134031 | 41367.3542 | 41367.5417 | 13 | 267 | 3471 | 13 | 0.01069 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 13 | 0.01069 | 4.0038e-05
134033 | 41367.3854 | 41367.4812 | 4 | 135 | 540 | 4 | 0.0016631 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 4 | 0.0016631 | 1.2319e-05
134034 | 41367.5479 | 41367.5764 | 233 | 38 | 8854 | 233 | 0.027269 | 0.0007176 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 233 | 0.027269 | 0.0007176
134035 | 41367.5417 | 41367.6667 | 11 | 177 | 1947 | 11 | 0.0059965 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 11 | 0.0059965 | 3.3878e-05
134036 | 41367.3854 | 41367.5972 | 7 | 302 | 2114 | 7 | 0.0065108 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 7 | 0.0065108 | 2.1559e-05
134037 | 41367.366 | 41367.6042 | 7 | 340 | 2380 | 7 | 0.00733 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 7 | 0.00733 | 2.1559e-05
134038 | 41367.3688 | 41367.6139 | 9 | 350 | 3150 | 9 | 0.0097015 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 9 | 0.0097015 | 2.7719e-05
134039 | 41367.5826 | 41367.5944 | 986 | 14 | 8032.7059 | 573.7647 | 0.024739 | 0.0030367 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 573.7647 | 0.024739 | 0.0030367
134040 | 41367.375 | 41367.625 | 36 | 357 | 12852 | 36 | 0.039582 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 36 | 0.039582 | 0.00011087
134041 | 41367.3646 | 41367.6396 | 48 | 393 | 18864 | 48 | 0.058098 | 0.00014783 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 48 | 0.058098 | 0.00014783
134042 | 41367.375 | 41367.6472 | 26 | 389 | 10114 | 26 | 0.03115 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 26 | 0.03115 | 8.0076e-05
134043 | 41367.375 | 41367.6042 | 6 | 327 | 1962 | 6 | 0.0060426 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 6 | 0.0060426 | 1.8479e-05
134044 | 41367.5354 | 41367.6472 | 20 | 158 | 3160 | 20 | 0.0097323 | 6.1597e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 20 | 0.0097323 | 6.1597e-05
134045 | 41367.3792 | 41367.6438 | 161 | 378 | 60858 | 161 | 0.18743 | 0.00049585 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | B | 161 | 0.18743 | 0.00049585
134047 | 41367.5889 | 41367.7056 | 65 | 165 | 5199.4643 | 31.5119 | 0.016014 | 0.00020019 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 31.5119 | 0.016014 | 0.00020019
134048 | 41367.6889 | 41367.8458 | 160 | 223 | 33437.1726 | 149.9425 | 0.10298 | 0.00049277 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 149.9425 | 0.10298 | 0.00049277
134049 | 41367.7771 | 41367.8924 | 404 | 163 | 25710.7952 | 157.7349 | 0.079185 | 0.0012443 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 157.7349 | 0.079185 | 0.0012443
134051 | 41367.6458 | 41367.7646 | 114 | 168 | 9702.7368 | 57.7544 | 0.029883 | 0.0003511 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-03 | 2014 | 2014 | 2013-04-03 | C | 57.7544 | 0.029883 | 0.0003511
134054 | 41368.4 | 41368.5792 | 17 | 255 | 4335 | 17 | 0.013351 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-04 | 2014 | 2014 | 2013-04-04 | B | 17 | 0.013351 | 5.2357e-05
134055 | 41368.3542 | 41368.5882 | 5 | 334 | 1670 | 5 | 0.0051433 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-04 | 2014 | 2014 | 2013-04-04 | B | 5 | 0.0051433 | 1.5399e-05
134059 | 41368.3812 | 41368.5757 | 2828 | 277 | 134035.3536 | 483.8821 | 0.41281 | 0.0087098 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-04 | 2014 | 2014 | 2013-04-04 | C | 483.8821 | 0.41281 | 0.0087098
134060 | 41368.4271 | 41368.6181 | 2 | 272 | 544 | 2 | 0.0016754 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-04 | 2014 | 2014 | 2013-04-04 | B | 2 | 0.0016754 | 6.1597e-06
134061 | 41368.375 | 41368.6146 | 6 | 342 | 2052 | 6 | 0.0063198 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-04 | 2014 | 2014 | 2013-04-04 | B | 6 | 0.0063198 | 1.8479e-05
134064 | 41369.3958 | 41369.4167 | 3 | 27 | 81 | 3 | 0.00024947 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 3 | 0.00024947 | 9.2395e-06
134065 | 41369.4375 | 41369.4688 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | B | 4 | 0.00051741 | 1.2319e-05
134066 | 41369.3729 | 41369.3771 | 1 | 3 | 3 | 1 | 9.2395e-06 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | B | 1 | 9.2395e-06 | 3.0798e-06
134067 | 41369.5208 | 41369.6188 | 4 | 138 | 552 | 4 | 0.0017001 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 4 | 0.0017001 | 1.2319e-05
134069 | 41369.6743 | 41369.7993 | 62 | 177 | 10974 | 62 | 0.033798 | 0.00019095 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 62 | 0.033798 | 0.00019095
134070 | 41369.8597 | 41369.8896 | 37 | 40 | 1480 | 37 | 0.0045582 | 0.00011395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 37 | 0.0045582 | 0.00011395
134073 | 41370.4042 | 41370.4563 | 22 | 72 | 1584 | 22 | 0.0048785 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-06 | 2014 | 2014 | 2013-04-06 | B | 22 | 0.0048785 | 6.7757e-05
134074 | 41370.5194 | 41370.5799 | 2166 | 84 | 107882.069 | 1284.3103 | 0.33226 | 0.0066709 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-06 | 2014 | 2014 | 2013-04-06 | C | 1284.3103 | 0.33226 | 0.0066709
134078 | 41369.7111 | 41369.7451 | 2 | 46 | 92 | 2 | 0.00028335 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 2 | 0.00028335 | 6.1597e-06
134079 | 41369.7417 | 41369.7701 | 238 | 38 | 9044 | 238 | 0.027854 | 0.000733 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-05 | 2014 | 2014 | 2013-04-05 | C | 238 | 0.027854 | 0.000733
134081 | 41371.375 | 41371.5368 | 29 | 230 | 6670 | 29 | 0.020543 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-07 | 2014 | 2014 | 2013-04-07 | B | 29 | 0.020543 | 8.9315e-05
134084 | 41371.375 | 41371.6 | 12 | 321 | 3852 | 12 | 0.011864 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-07 | 2014 | 2014 | 2013-04-07 | B | 12 | 0.011864 | 3.6958e-05
134086 | 41371.8569 | 41371.9722 | 217 | 163 | 20375 | 125 | 0.062752 | 0.00066833 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-07 | 2014 | 2014 | 2013-04-07 | C | 125 | 0.062752 | 0.00066833
134087 | 41371.7708 | 41371.775 | 904 | 3 | 2712 | 904 | 0.0083525 | 0.0027842 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-07 | 2014 | 2014 | 2013-04-07 | C | 904 | 0.0083525 | 0.0027842
134089 | 41371.6889 | 41371.8472 | 501 | 225 | 42495.3947 | 188.8684 | 0.13088 | 0.001543 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-07 | 2014 | 2014 | 2013-04-07 | C | 188.8684 | 0.13088 | 0.001543
134090 | 41372.3854 | 41372.4625 | 2 | 108 | 216 | 2 | 0.00066525 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | B | 2 | 0.00066525 | 6.1597e-06
134093 | 41372.3958 | 41372.4528 | 4 | 79 | 316 | 4 | 0.00097323 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | C | 4 | 0.00097323 | 1.2319e-05
134094 | 41372.3785 | 41372.4868 | 287 | 153 | 43911 | 287 | 0.13524 | 0.00088391 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | B | 287 | 0.13524 | 0.00088391
134095 | 41372.375 | 41372.6667 | 6 | 417 | 2502 | 6 | 0.0077058 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | B | 6 | 0.0077058 | 1.8479e-05
134096 | 41372.3646 | 41372.6354 | 57 | 387 | 22059 | 57 | 0.067938 | 0.00017555 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | B | 57 | 0.067938 | 0.00017555
134098 | 41372.375 | 41372.6854 | 50 | 444 | 22200 | 50 | 0.068372 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-08 | 2014 | 2014 | 2013-04-08 | B | 50 | 0.068372 | 0.00015399
134104 | 41373.3819 | 41373.5111 | 3 | 183 | 549 | 3 | 0.0016908 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 3 | 0.0016908 | 9.2395e-06
134105 | 41373.4632 | 41373.534 | 298 | 99 | 23067.9706 | 233.0098 | 0.071046 | 0.00091779 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | C | 233.0098 | 0.071046 | 0.00091779
134107 | 41373.375 | 41373.6333 | 339 | 369 | 125091 | 339 | 0.38526 | 0.0010441 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 339 | 0.38526 | 0.0010441
134108 | 41373.4069 | 41373.6285 | 6 | 316 | 1896 | 6 | 0.0058394 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 6 | 0.0058394 | 1.8479e-05
134109 | 41373.4014 | 41373.6097 | 17 | 297 | 5049 | 17 | 0.01555 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 17 | 0.01555 | 5.2357e-05
134110 | 41373.375 | 41373.6299 | 131 | 364 | 47684 | 131 | 0.14686 | 0.00040346 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 131 | 0.14686 | 0.00040346
134111 | 41373.3958 | 41373.6042 | 37 | 297 | 10989 | 37 | 0.033844 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 37 | 0.033844 | 0.00011395
134112 | 41373.5917 | 41373.6458 | 9 | 75 | 675 | 9 | 0.0020789 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | C | 9 | 0.0020789 | 2.7719e-05
134114 | 41373.3681 | 41373.6424 | 31 | 392 | 12152 | 31 | 0.037426 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | B | 31 | 0.037426 | 9.5475e-05
134116 | 41373.8097 | 41373.8333 | 80 | 31 | 2480 | 80 | 0.007638 | 0.00024639 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-09 | 2014 | 2014 | 2013-04-09 | C | 80 | 0.007638 | 0.00024639
134118 | 41374.166 | 41374.1778 | 581 | 14 | 8134 | 581 | 0.025051 | 0.0017894 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | C | 581 | 0.025051 | 0.0017894
134120 | 41374.4167 | 41374.4882 | 52 | 100 | 5200 | 52 | 0.016015 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | B | 52 | 0.016015 | 0.00016015
134121 | 41374.5417 | 41374.6146 | 40 | 102 | 4080 | 40 | 0.012566 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | B | 40 | 0.012566 | 0.00012319
134124 | 41374.4153 | 41374.625 | 62 | 299 | 18538 | 62 | 0.057094 | 0.00019095 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | B | 62 | 0.057094 | 0.00019095
134126 | 41374.3875 | 41374.584 | 11 | 280 | 3080 | 11 | 0.0094859 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | B | 11 | 0.0094859 | 3.3878e-05
134127 | 41374.8493 | 41374.9097 | 29 | 84 | 2436 | 29 | 0.0075025 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | C | 29 | 0.0075025 | 8.9315e-05
134128 | 41374.875 | 41374.941 | 96 | 92 | 8832 | 96 | 0.027201 | 0.00029566 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | C | 96 | 0.027201 | 0.00029566
134131 | 41375.2764 | 41375.3201 | 1856 | 60 | 92345.7143 | 1539.0952 | 0.28441 | 0.0057162 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | C | 1539.0952 | 0.28441 | 0.0057162
134134 | 41375.375 | 41375.6125 | 62 | 339 | 21018 | 62 | 0.064732 | 0.00019095 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 62 | 0.064732 | 0.00019095
134136 | 41375.3958 | 41375.6194 | 37 | 319 | 11803 | 37 | 0.036351 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 37 | 0.036351 | 0.00011395
134137 | 41375.375 | 41375.6347 | 54 | 371 | 20034 | 54 | 0.061702 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 54 | 0.061702 | 0.00016631
134138 | 41375.3646 | 41375.6458 | 9 | 402 | 3618 | 9 | 0.011143 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 9 | 0.011143 | 2.7719e-05
134139 | 41375.3854 | 41375.6389 | 14 | 362 | 5068 | 14 | 0.015609 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 14 | 0.015609 | 4.3118e-05
134140 | 41375.4896 | 41375.566 | 14 | 107 | 1498 | 14 | 0.0046136 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | C | 14 | 0.0046136 | 4.3118e-05
134142 | 41375.366 | 41375.6222 | 28 | 366 | 10248 | 28 | 0.031562 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 28 | 0.031562 | 8.6236e-05
134143 | 41375.5312 | 41375.6146 | 3 | 117 | 351 | 3 | 0.001081 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 3 | 0.001081 | 9.2395e-06
134144 | 41375.4062 | 41375.5104 | 9 | 147 | 1323 | 9 | 0.0040746 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | B | 9 | 0.0040746 | 2.7719e-05
134145 | 41375.6028 | 41375.6618 | 26 | 82 | 2132 | 26 | 0.0065662 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | C | 26 | 0.0065662 | 8.0076e-05
134146 | 41375.7097 | 41375.9014 | 234 | 273 | 31041.8804 | 113.7065 | 0.095604 | 0.00072068 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-11 | 2014 | 2014 | 2013-04-11 | C | 113.7065 | 0.095604 | 0.00072068
134148 | 41376.2819 | 41376.3375 | 87 | 77 | 6365.975 | 82.675 | 0.019606 | 0.00026795 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | C | 82.675 | 0.019606 | 0.00026795
134149 | 41376.241 | 41376.3306 | 1340 | 126 | 104345.5814 | 828.1395 | 0.32137 | 0.004127 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | C | 828.1395 | 0.32137 | 0.004127
134151 | 41376.375 | 41376.4222 | 5 | 65 | 325 | 5 | 0.0010009 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 5 | 0.0010009 | 1.5399e-05
134153 | 41376.4583 | 41376.5104 | 3 | 72 | 216 | 3 | 0.00066525 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 3 | 0.00066525 | 9.2395e-06
134154 | 41376.3542 | 41376.5611 | 6 | 295 | 1770 | 6 | 0.0054513 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 6 | 0.0054513 | 1.8479e-05
134155 | 41376.4792 | 41376.5493 | 55 | 98 | 5390 | 55 | 0.0166 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 55 | 0.0166 | 0.00016939
134158 | 41376.4563 | 41376.5583 | 31 | 144 | 4464 | 31 | 0.013748 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | C | 31 | 0.013748 | 9.5475e-05
134160 | 41377.375 | 41377.5729 | 82 | 282 | 23124 | 82 | 0.071218 | 0.00025255 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | B | 82 | 0.071218 | 0.00025255
134164 | 41377.5771 | 41377.6174 | 7 | 55 | 385 | 7 | 0.0011857 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | C | 7 | 0.0011857 | 2.1559e-05
134165 | 41378.3931 | 41378.4417 | 1124 | 67 | 44197.0286 | 659.6571 | 0.13612 | 0.0034617 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-14 | 2014 | 2014 | 2013-04-14 | C | 659.6571 | 0.13612 | 0.0034617
134166 | 41378.2937 | 41378.6424 | 347 | 499 | 30303.8127 | 60.7291 | 0.093331 | 0.0010687 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-14 | 2014 | 2014 | 2013-04-14 | C | 60.7291 | 0.093331 | 0.0010687
134167 | 41377.5451 | 41377.6271 | 1026 | 115 | 49660.5085 | 431.8305 | 0.15295 | 0.0031599 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | C | 431.8305 | 0.15295 | 0.0031599
134169 | 41378.3854 | 41378.5833 | 12 | 282 | 3384 | 12 | 0.010422 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-14 | 2014 | 2014 | 2013-04-14 | B | 12 | 0.010422 | 3.6958e-05
134170 | 41377.4236 | 41377.5083 | 169 | 119 | 12420.8689 | 104.377 | 0.038254 | 0.00052049 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | C | 104.377 | 0.038254 | 0.00052049
134171 | 41378.6514 | 41378.6694 | 969 | 23 | 13282.5 | 577.5 | 0.040908 | 0.0029844 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-14 | 2014 | 2014 | 2013-04-14 | C | 577.5 | 0.040908 | 0.0029844
134172 | 41377.3868 | 41377.4708 | 105 | 118 | 12390 | 105 | 0.038159 | 0.00032338 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | B | 105 | 0.038159 | 0.00032338
134173 | 41378.3833 | 41378.4528 | 144 | 97 | 13968 | 144 | 0.043019 | 0.0004435 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-14 | 2014 | 2014 | 2013-04-14 | B | 144 | 0.043019 | 0.0004435
134175 | 41377.7771 | 41377.8181 | 3 | 56 | 168 | 3 | 0.00051741 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-13 | 2014 | 2014 | 2013-04-13 | C | 3 | 0.00051741 | 9.2395e-06
134176 | 41379.1194 | 41379.1403 | 1429 | 27 | 38133 | 1412.3333 | 0.11744 | 0.0044011 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 1412.3333 | 0.11744 | 0.0044011
134177 | 41379.1528 | 41379.1882 | 245 | 48 | 11760 | 245 | 0.036219 | 0.00075456 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 245 | 0.036219 | 0.00075456
134178 | 41379.166 | 41379.1875 | 272 | 28 | 4421.2903 | 157.9032 | 0.013617 | 0.00083772 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 157.9032 | 0.013617 | 0.00083772
134181 | 41379.3611 | 41379.525 | 10 | 233 | 2330 | 10 | 0.007176 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | B | 10 | 0.007176 | 3.0798e-05
134182 | 41379.375 | 41379.4972 | 22 | 173 | 3806 | 22 | 0.011722 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | B | 22 | 0.011722 | 6.7757e-05
134183 | 41379.3854 | 41379.5819 | 28 | 280 | 7840 | 28 | 0.024146 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | B | 28 | 0.024146 | 8.6236e-05
134184 | 41379.5035 | 41379.6875 | 3 | 262 | 786 | 3 | 0.0024208 | 9.2395e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 3 | 0.0024208 | 9.2395e-06
134187 | 41380.0958 | 41380.2104 | 233 | 162 | 19482.2182 | 120.2606 | 0.060002 | 0.0007176 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 120.2606 | 0.060002 | 0.0007176
134188 | 41380.2063 | 41380.2326 | 189 | 35 | 6615 | 189 | 0.020373 | 0.00058209 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 189 | 0.020373 | 0.00058209
134189 | 41379.7528 | 41379.7694 | 226 | 21 | 4746 | 226 | 0.014617 | 0.00069604 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 226 | 0.014617 | 0.00069604
134190 | 41379.7528 | 41379.7722 | 481 | 25 | 12025 | 481 | 0.037035 | 0.0014814 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 481 | 0.037035 | 0.0014814
134191 | 41379.7528 | 41379.7764 | 867 | 31 | 26877 | 867 | 0.082777 | 0.0026702 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 867 | 0.082777 | 0.0026702
134192 | 41379.9174 | 41379.9674 | 17 | 69 | 1173 | 17 | 0.0036127 | 5.2357e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 17 | 0.0036127 | 5.2357e-05
134193 | 41379.9444 | 41380.075 | 22 | 185 | 4070 | 22 | 0.012535 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 22 | 0.012535 | 6.7757e-05
134194 | 41380.1854 | 41380.2972 | 409 | 158 | 28448.8323 | 180.0559 | 0.087618 | 0.0012597 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 180.0559 | 0.087618 | 0.0012597
134195 | 41380.1062 | 41380.1757 | 1686 | 97 | 78004.49 | 804.17 | 0.24024 | 0.0051926 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 804.17 | 0.24024 | 0.0051926
134197 | 41380.2014 | 41380.3007 | 213 | 140 | 17599.8601 | 125.7133 | 0.054205 | 0.00065601 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 125.7133 | 0.054205 | 0.00065601
134198 | 41376.5931 | 41376.8542 | 987 | 373 | 151822.9043 | 407.0319 | 0.46759 | 0.0030398 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | C | 407.0319 | 0.46759 | 0.0030398
134199 | 41380.4035 | 41380.4382 | 177 | 47 | 8319 | 177 | 0.025621 | 0.00054513 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 177 | 0.025621 | 0.00054513
134203 | 41380.3771 | 41380.4354 | 147 | 81 | 11826 | 146 | 0.036422 | 0.00045274 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 146 | 0.036422 | 0.00045274
134204 | 41380.4674 | 41380.4785 | 89 | 13 | 1157 | 89 | 0.0035634 | 0.00027411 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 89 | 0.0035634 | 0.00027411
134206 | 41380.4549 | 41380.5528 | 31 | 138 | 4278 | 31 | 0.013176 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 31 | 0.013176 | 9.5475e-05
134207 | 41379.8979 | 41380.4688 | 187 | 819 | 21235.2153 | 25.9282 | 0.065401 | 0.00057593 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-15 | 2014 | 2014 | 2013-04-15 | C | 25.9282 | 0.065401 | 0.00057593
134209 | 41380.6083 | 41380.6132 | 50 | 4 | 200 | 50 | 0.00061597 | 0.00015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 50 | 0.00061597 | 0.00015399
134210 | 41380.6056 | 41380.7 | 23 | 133 | 3059 | 23 | 0.0094212 | 7.0836e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 23 | 0.0094212 | 7.0836e-05
134211 | 41380.2201 | 41380.3028 | 411 | 116 | 27515.395 | 237.2017 | 0.084743 | 0.0012658 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 237.2017 | 0.084743 | 0.0012658
134212 | 41380.4076 | 41380.5917 | 289 | 262 | 66894.0377 | 255.3208 | 0.20602 | 0.00089007 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 255.3208 | 0.20602 | 0.00089007
134213 | 41380.4917 | 41380.5611 | 306 | 97 | 19438.8 | 200.4 | 0.059868 | 0.00094243 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 200.4 | 0.059868 | 0.00094243
134215 | 41380.5347 | 41380.5507 | 4 | 20 | 80 | 4 | 0.00024639 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 4 | 0.00024639 | 1.2319e-05
134216 | 41380.3854 | 41380.6285 | 13 | 347 | 4511 | 13 | 0.013893 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | B | 13 | 0.013893 | 4.0038e-05
134218 | 41380.375 | 41380.6229 | 45 | 354 | 15930 | 45 | 0.049062 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | B | 45 | 0.049062 | 0.00013859
134221 | 41376.5833 | 41376.625 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 4 | 0.0007022 | 1.2319e-05
134222 | 41376.5417 | 41376.5833 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-12 | 2014 | 2014 | 2013-04-12 | B | 4 | 0.0007022 | 1.2319e-05
134224 | 41380.6181 | 41380.6556 | 260 | 51 | 13260 | 260 | 0.040839 | 0.00080076 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 260 | 0.040839 | 0.00080076
134225 | 41380.7507 | 41380.766 | 17 | 19 | 323 | 17 | 0.00099479 | 5.2357e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 17 | 0.00099479 | 5.2357e-05
134226 | 41380.8299 | 41380.8403 | 307 | 12 | 3684 | 307 | 0.011346 | 0.00094551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 307 | 0.011346 | 0.00094551
134227 | 41380.9229 | 41380.9396 | 1058 | 21 | 14189 | 675.6667 | 0.0437 | 0.0032585 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 675.6667 | 0.0437 | 0.0032585
134228 | 41380.8028 | 41380.8583 | 23 | 77 | 1771 | 23 | 0.0054544 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-16 | 2014 | 2014 | 2013-04-16 | C | 23 | 0.0054544 | 7.0836e-05
134230 | 41381.1014 | 41381.1146 | 109 | 16 | 1744 | 109 | 0.0053712 | 0.0003357 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 109 | 0.0053712 | 0.0003357
134231 | 41381.0118 | 41381.1139 | 274 | 144 | 25592.8163 | 177.7279 | 0.078822 | 0.00084388 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 177.7279 | 0.078822 | 0.00084388
134232 | 41381.1458 | 41381.2118 | 6 | 92 | 552 | 6 | 0.0017001 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 6 | 0.0017001 | 1.8479e-05
134233 | 41381.3986 | 41381.4201 | 12 | 28 | 336 | 12 | 0.0010348 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 12 | 0.0010348 | 3.6958e-05
134234 | 41381.2785 | 41381.3181 | 1139 | 54 | 35267.6842 | 653.1053 | 0.10862 | 0.0035079 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 653.1053 | 0.10862 | 0.0035079
134236 | 41381.3354 | 41381.4299 | 288 | 133 | 17605.875 | 132.375 | 0.054223 | 0.00088699 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 132.375 | 0.054223 | 0.00088699
134237 | 41381.4729 | 41381.5139 | 572 | 56 | 29222.5085 | 521.8305 | 0.090001 | 0.0017617 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 521.8305 | 0.090001 | 0.0017617
134240 | 41381.5181 | 41381.5486 | 5 | 41 | 205 | 5 | 0.00063137 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 5 | 0.00063137 | 1.5399e-05
134243 | 41381.4708 | 41381.5736 | 135 | 145 | 6261.4527 | 43.1824 | 0.019284 | 0.00041578 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 43.1824 | 0.019284 | 0.00041578
134246 | 41381.375 | 41381.6049 | 71 | 328 | 23288 | 71 | 0.071723 | 0.00021867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 71 | 0.071723 | 0.00021867
134249 | 41381.3958 | 41381.584 | 35 | 268 | 9380 | 35 | 0.028889 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 35 | 0.028889 | 0.00010779
134252 | 41381.5833 | 41381.6007 | 9 | 22 | 198 | 9 | 0.00060981 | 2.7719e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 9 | 0.00060981 | 2.7719e-05
134253 | 41381.3764 | 41381.6389 | 57 | 375 | 21375 | 57 | 0.065832 | 0.00017555 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 57 | 0.065832 | 0.00017555
134254 | 41381.4792 | 41381.5868 | 9 | 152 | 1368 | 9 | 0.0042132 | 2.7719e-05 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 9 | 0.0042132 | 2.7719e-05
134255 | 41381.6944 | 41381.7139 | 390 | 25 | 9750 | 390 | 0.030028 | 0.0012011 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 390 | 0.030028 | 0.0012011
134256 | 41381.3854 | 41381.4931 | 3 | 152 | 456 | 3 | 0.0014044 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 3 | 0.0014044 | 9.2395e-06
134257 | 41381.75 | 41381.7917 | 3 | 57 | 171 | 3 | 0.00052665 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 3 | 0.00052665 | 9.2395e-06
134258 | 41381.9708 | 41382.009 | 22 | 52 | 1144 | 22 | 0.0035233 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 22 | 0.0035233 | 6.7757e-05
134259 | 41381.8458 | 41381.9799 | 94 | 190 | 6922.6943 | 36.4352 | 0.021321 | 0.00028951 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 36.4352 | 0.021321 | 0.00028951
134266 | 41382.4062 | 41382.4583 | 5 | 72 | 360 | 5 | 0.0011087 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 5 | 0.0011087 | 1.5399e-05
134268 | 41382.4583 | 41382.4833 | 35 | 33 | 1155 | 35 | 0.0035572 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 35 | 0.0035572 | 0.00010779
134269 | 41381.8701 | 41382.4583 | 40 | 844 | 33760 | 40 | 0.10398 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 40 | 0.10398 | 0.00012319
134271 | 41381.8368 | 41382.5972 | 53 | 1092 | 13992.5589 | 12.8137 | 0.043095 | 0.00016323 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | C | 12.8137 | 0.043095 | 0.00016323
134273 | 41382.5576 | 41382.6472 | 1 | 126 | 126 | 1 | 0.00038806 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 1 | 0.00038806 | 3.0798e-06
134275 | 41382.3542 | 41382.6215 | 70 | 382 | 26740 | 70 | 0.082355 | 0.00021559 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 70 | 0.082355 | 0.00021559
134276 | 41382.5264 | 41382.6076 | 3 | 114 | 342 | 3 | 0.0010533 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 3 | 0.0010533 | 9.2395e-06
134277 | 41382.3819 | 41382.6479 | 35 | 380 | 13300 | 35 | 0.040962 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 35 | 0.040962 | 0.00010779
134278 | 41382.3854 | 41382.5715 | 14 | 265 | 3710 | 14 | 0.011426 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | B | 14 | 0.011426 | 4.3118e-05
134279 | 41382.2917 | 41382.3396 | 67 | 66 | 4422 | 67 | 0.013619 | 0.00020635 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | C | 67 | 0.013619 | 0.00020635
134281 | 41382.6667 | 41382.7118 | 684 | 62 | 42408 | 684 | 0.13061 | 0.0021066 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | C | 684 | 0.13061 | 0.0021066
134286 | 41383.3958 | 41383.4201 | 2 | 32 | 64 | 2 | 0.00019711 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 2 | 0.00019711 | 6.1597e-06
134287 | 41383.4792 | 41383.5201 | 10 | 56 | 560 | 10 | 0.0017247 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | C | 10 | 0.0017247 | 3.0798e-05
134288 | 41383.4035 | 41383.5896 | 1 | 265 | 265 | 1 | 0.00081616 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | C | 1 | 0.00081616 | 3.0798e-06
134292 | 41382.3604 | 41382.5854 | 847 | 321 | 134342.463 | 418.5123 | 0.41375 | 0.0026086 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-18 | 2014 | 2014 | 2013-04-18 | C | 418.5123 | 0.41375 | 0.0026086
134295 | 41383.3958 | 41383.5972 | 19 | 287 | 5453 | 19 | 0.016794 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 19 | 0.016794 | 5.8517e-05
134297 | 41383.3757 | 41383.6076 | 29 | 331 | 9599 | 29 | 0.029563 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 29 | 0.029563 | 8.9315e-05
134299 | 41383.3854 | 41383.6354 | 28 | 357 | 9996 | 28 | 0.030786 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 28 | 0.030786 | 8.6236e-05
134300 | 41383.3924 | 41383.5521 | 9 | 227 | 2043 | 9 | 0.0062921 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 9 | 0.0062921 | 2.7719e-05
134301 | 41383.375 | 41383.6264 | 14 | 359 | 2004.2514 | 5.5829 | 0.0061728 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | B | 5.5829 | 0.0061728 | 4.3118e-05
134304 | 41383.7361 | 41383.8382 | 9 | 144 | 1296 | 9 | 0.0039915 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | C | 9 | 0.0039915 | 2.7719e-05
134305 | 41383.8708 | 41383.9194 | 2082 | 67 | 40808.7429 | 609.0857 | 0.12568 | 0.0064122 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | C | 609.0857 | 0.12568 | 0.0064122
134307 | 41383.9514 | 41384.0396 | 870 | 124 | 47246.9291 | 381.0236 | 0.14551 | 0.0026795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-19 | 2014 | 2014 | 2013-04-19 | C | 381.0236 | 0.14551 | 0.0026795
134308 | 41384.3542 | 41384.4861 | 10 | 187 | 1870 | 10 | 0.0057593 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 10 | 0.0057593 | 3.0798e-05
134311 | 41384.4507 | 41384.4757 | 39 | 33 | 1287 | 39 | 0.0039638 | 0.00012011 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 39 | 0.0039638 | 0.00012011
134312 | 41384.1319 | 41384.5292 | 413 | 569 | 83211.2762 | 146.2413 | 0.25628 | 0.001272 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 146.2413 | 0.25628 | 0.001272
134313 | 41384.4694 | 41384.5917 | 86 | 173 | 14878 | 86 | 0.045822 | 0.00026487 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 86 | 0.045822 | 0.00026487
134315 | 41384.1979 | 41384.6 | 6 | 576 | 3456 | 6 | 0.010644 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 6 | 0.010644 | 1.8479e-05
134316 | 41384.1562 | 41384.7104 | 1 | 795 | 795 | 1 | 0.0024485 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 1 | 0.0024485 | 3.0798e-06
134323 | 41385.4861 | 41385.5201 | 7 | 46 | 322 | 7 | 0.00099171 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 7 | 0.00099171 | 2.1559e-05
134324 | 41385.3701 | 41385.5188 | 1 | 211 | 211 | 1 | 0.00064985 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | B | 1 | 0.00064985 | 3.0798e-06
134325 | 41384.891 | 41385.2583 | 35 | 526 | 18410 | 35 | 0.0567 | 0.00010779 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 35 | 0.0567 | 0.00010779
134326 | 41385.5361 | 41385.5743 | 3 | 52 | 156 | 3 | 0.00048046 | 9.2395e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 3 | 0.00048046 | 9.2395e-06
134327 | 41385.6132 | 41385.6597 | 353 | 64 | 18318.3284 | 286.2239 | 0.056418 | 0.0010872 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 286.2239 | 0.056418 | 0.0010872
134328 | 41385.5826 | 41385.6736 | 442 | 128 | 28687.6336 | 224.1221 | 0.088353 | 0.0013613 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 224.1221 | 0.088353 | 0.0013613
134329 | 41385.5764 | 41385.6389 | 1 | 87 | 87 | 1 | 0.00026795 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 1 | 0.00026795 | 3.0798e-06
134330 | 41385.5243 | 41385.75 | 97 | 322 | 31234 | 97 | 0.096196 | 0.00029874 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 97 | 0.096196 | 0.00029874
134331 | 41385.7042 | 41385.7174 | 45 | 16 | 720 | 45 | 0.0022175 | 0.00013859 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 45 | 0.0022175 | 0.00013859
134334 | 41385.0354 | 41385.1333 | 2355 | 138 | 66997.5319 | 485.4894 | 0.20634 | 0.007253 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 485.4894 | 0.20634 | 0.007253
134335 | 41385.0354 | 41385.3819 | 255 | 496 | 125386.6132 | 252.7956 | 0.38617 | 0.00078536 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 252.7956 | 0.38617 | 0.00078536
134336 | 41384.9535 | 41385.0472 | 308 | 132 | 35134.4889 | 266.1704 | 0.10821 | 0.00094859 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-20 | 2014 | 2014 | 2013-04-20 | C | 266.1704 | 0.10821 | 0.00094859
134337 | 41385.8111 | 41385.9986 | 472 | 267 | 31633.5667 | 118.4778 | 0.097426 | 0.0014537 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 118.4778 | 0.097426 | 0.0014537
134338 | 41386.0729 | 41386.234 | 108 | 229 | 24732 | 108 | 0.076171 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 108 | 0.076171 | 0.00033262
134339 | 41386.0729 | 41386.3639 | 237 | 416 | 71671.1408 | 172.2864 | 0.22074 | 0.00072992 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 172.2864 | 0.22074 | 0.00072992
134340 | 41385.6042 | 41385.7806 | 5 | 251 | 1255 | 5 | 0.0038652 | 1.5399e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 5 | 0.0038652 | 1.5399e-05
134342 | 41386.0563 | 41386.0917 | 6 | 48 | 288 | 6 | 0.00088699 | 1.8479e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 6 | 0.00088699 | 1.8479e-05
134343 | 41385.9389 | 41385.9729 | 2 | 46 | 92 | 2 | 0.00028335 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 2 | 0.00028335 | 6.1597e-06
134344 | 41385.8667 | 41385.9194 | 2 | 73 | 146 | 2 | 0.00044966 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 2 | 0.00044966 | 6.1597e-06
134346 | 41386.4083 | 41386.4667 | 2071 | 81 | 79891.0714 | 986.3095 | 0.24605 | 0.0063784 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 986.3095 | 0.24605 | 0.0063784
134347 | 41386.3882 | 41386.4882 | 109 | 141 | 15369 | 109 | 0.047334 | 0.0003357 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 109 | 0.047334 | 0.0003357
134349 | 41386.3965 | 41386.5118 | 62 | 163 | 10106 | 62 | 0.031125 | 0.00019095 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 62 | 0.031125 | 0.00019095
134350 | 41386.3931 | 41386.5229 | 16 | 184 | 2944 | 16 | 0.0090671 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 16 | 0.0090671 | 4.9277e-05
134352 | 41386.3958 | 41386.4382 | 419 | 58 | 24302 | 419 | 0.074846 | 0.0012905 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 419 | 0.074846 | 0.0012905
134353 | 41386.4806 | 41386.5417 | 1 | 85 | 85 | 1 | 0.00026179 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 1 | 0.00026179 | 3.0798e-06
134354 | 41381.3715 | 41381.634 | 28 | 375 | 10500 | 28 | 0.032338 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 28 | 0.032338 | 8.6236e-05
134355 | 41381.375 | 41381.625 | 35 | 357 | 12495 | 35 | 0.038483 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 35 | 0.038483 | 0.00010779
134357 | 41374.5 | 41374.6153 | 64 | 163 | 10432 | 64 | 0.032129 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-10 | 2014 | 2014 | 2013-04-10 | B | 64 | 0.032129 | 0.00019711
134358 | 41381.9986 | 41382.0729 | 45 | 104 | 4680 | 45 | 0.014414 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-17 | 2014 | 2014 | 2013-04-17 | B | 45 | 0.014414 | 0.00013859
134359 | 41386.5375 | 41386.5604 | 982 | 30 | 29460 | 982 | 0.090732 | 0.0030244 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 982 | 0.090732 | 0.0030244
134360 | 41386.5861 | 41386.6312 | 3 | 62 | 186 | 3 | 0.00057285 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 3 | 0.00057285 | 9.2395e-06
134361 | 41386.559 | 41386.6312 | 3 | 101 | 303 | 3 | 0.00093319 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 3 | 0.00093319 | 9.2395e-06
134362 | 41386.6333 | 41386.7063 | 7 | 102 | 714 | 7 | 0.002199 | 2.1559e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 7 | 0.002199 | 2.1559e-05
134363 | 41386.6854 | 41386.8132 | 4 | 181 | 724 | 4 | 0.0022298 | 1.2319e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 4 | 0.0022298 | 1.2319e-05
134364 | 41386.3681 | 41386.6618 | 65 | 420 | 27300 | 65 | 0.08408 | 0.00020019 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 65 | 0.08408 | 0.00020019
134365 | 41386.5431 | 41386.6611 | 69 | 167 | 11523 | 69 | 0.035489 | 0.00021251 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 69 | 0.035489 | 0.00021251
134367 | 41386.7292 | 41386.7708 | 5 | 57 | 285 | 5 | 0.00087775 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | B | 5 | 0.00087775 | 1.5399e-05
134368 | 41386.6646 | 41386.8056 | 1 | 200 | 200 | 1 | 0.00061597 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 1 | 0.00061597 | 3.0798e-06
134369 | 41386.7549 | 41387.0153 | 94 | 372 | 34968 | 94 | 0.1077 | 0.00028951 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 94 | 0.1077 | 0.00028951
134370 | 41386.9583 | 41387.0681 | 294 | 155 | 44410.443 | 286.519 | 0.13678 | 0.00090547 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 286.519 | 0.13678 | 0.00090547
134371 | 41387.0424 | 41387.1278 | 1 | 120 | 120 | 1 | 0.00036958 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | C | 1 | 0.00036958 | 3.0798e-06
134373 | 41387.4271 | 41387.4826 | 1 | 77 | 77 | 1 | 0.00023715 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 1 | 0.00023715 | 3.0798e-06
134376 | 41387.4632 | 41387.5972 | 273 | 190 | 15454.9741 | 81.342 | 0.047599 | 0.0008408 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | C | 81.342 | 0.047599 | 0.0008408
134379 | 41387.4194 | 41387.5493 | 71 | 184 | 13064 | 71 | 0.040235 | 0.00021867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 71 | 0.040235 | 0.00021867
134380 | 41387.3646 | 41387.5625 | 31 | 282 | 8742 | 31 | 0.026924 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 31 | 0.026924 | 9.5475e-05
134381 | 41387.4062 | 41387.6042 | 40 | 282 | 11280 | 40 | 0.034741 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 40 | 0.034741 | 0.00012319
134384 | 41387.3646 | 41387.6458 | 65 | 402 | 26130 | 65 | 0.080476 | 0.00020019 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 65 | 0.080476 | 0.00020019
134385 | 41387.375 | 41387.6556 | 143 | 401 | 57343 | 143 | 0.17661 | 0.00044042 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | B | 143 | 0.17661 | 0.00044042
134388 | 41387.9514 | 41387.9611 | 38 | 11 | 418 | 38 | 0.0012874 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-23 | 2014 | 2014 | 2013-04-23 | C | 38 | 0.0012874 | 0.00011703
134389 | 41388.0083 | 41388.2708 | 279 | 375 | 34297.619 | 91.4603 | 0.10563 | 0.00085928 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 91.4603 | 0.10563 | 0.00085928
134391 | 41388.375 | 41388.3944 | 40 | 25 | 1000 | 40 | 0.0030798 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 40 | 0.0030798 | 0.00012319
134395 | 41388.4299 | 41388.5569 | 33 | 180 | 5940 | 33 | 0.018294 | 0.00010163 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 33 | 0.018294 | 0.00010163
134396 | 41388.4812 | 41388.4861 | 35 | 4 | 140 | 35 | 0.00043118 | 0.00010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 35 | 0.00043118 | 0.00010779
134397 | 41388.5625 | 41388.5833 | 432 | 27 | 11664 | 432 | 0.035923 | 0.0013305 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 432 | 0.035923 | 0.0013305
134400 | 41388.3854 | 41388.6465 | 87 | 373 | 32451 | 87 | 0.099944 | 0.00026795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | B | 87 | 0.099944 | 0.00026795
134401 | 41388.3646 | 41388.6667 | 4 | 432 | 1728 | 4 | 0.005322 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | B | 4 | 0.005322 | 1.2319e-05
134403 | 41388.5396 | 41388.5896 | 6 | 69 | 414 | 6 | 0.0012751 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 6 | 0.0012751 | 1.8479e-05
134404 | 41388.4264 | 41388.6299 | 35 | 290 | 10150 | 35 | 0.03126 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | B | 35 | 0.03126 | 0.00010779
134405 | 41388.3715 | 41388.5833 | 40 | 302 | 12080 | 40 | 0.037204 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | B | 40 | 0.037204 | 0.00012319
134406 | 41386.5549 | 41386.5799 | 1 | 33 | 33 | 1 | 0.00010163 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-22 | 2014 | 2014 | 2013-04-22 | C | 1 | 0.00010163 | 3.0798e-06
134407 | 41388.3444 | 41388.3576 | 9 | 16 | 144 | 9 | 0.0004435 | 2.7719e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 9 | 0.0004435 | 2.7719e-05
134413 | 41389.075 | 41389.1458 | 78 | 99 | 7722 | 78 | 0.023783 | 0.00024023 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-25 | 2014 | 2014 | 2013-04-25 | C | 78 | 0.023783 | 0.00024023
134414 | 41388.916 | 41389.5618 | 1195 | 927 | 201150.029 | 216.9903 | 0.61951 | 0.0036804 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 216.9903 | 0.61951 | 0.0036804
134416 | 41389.4597 | 41389.6736 | 161 | 305 | 49105 | 161 | 0.15124 | 0.00049585 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-04-25 | 2014 | 2014 | 2013-04-25 | C | 161 | 0.15124 | 0.00049585
134417 | 41389.3924 | 41389.7535 | 6 | 517 | 2858.4135 | 5.5288 | 0.0088035 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-25 | 2014 | 2014 | 2013-04-25 | C | 5.5288 | 0.0088035 | 1.8479e-05
134418 | 41389.9118 | 41390.0576 | 137 | 207 | 19599.9429 | 94.6857 | 0.060365 | 0.00042194 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-25 | 2014 | 2014 | 2013-04-25 | C | 94.6857 | 0.060365 | 0.00042194
134420 | 41390.4375 | 41390.4931 | 53 | 77 | 4081 | 53 | 0.012569 | 0.00016323 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | B | 53 | 0.012569 | 0.00016323
134422 | 41390.375 | 41390.6222 | 90 | 353 | 31770 | 90 | 0.097847 | 0.00027719 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | B | 90 | 0.097847 | 0.00027719
134423 | 41390.4201 | 41390.5035 | 98 | 117 | 11466 | 98 | 0.035313 | 0.00030182 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | B | 98 | 0.035313 | 0.00030182
134425 | 41390.3542 | 41390.4896 | 4 | 192 | 768 | 4 | 0.0023653 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | B | 4 | 0.0023653 | 1.2319e-05
134426 | 41390.375 | 41390.4229 | 15 | 66 | 990 | 15 | 0.003049 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 15 | 0.003049 | 4.6198e-05
134427 | 41390.4688 | 41390.5486 | 90 | 112 | 10080 | 90 | 0.031045 | 0.00027719 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 90 | 0.031045 | 0.00027719
134429 | 41390.5625 | 41390.5958 | 115 | 45 | 5265 | 117 | 0.016215 | 0.00035418 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 117 | 0.016215 | 0.00035418
134430 | 41390.5042 | 41390.5646 | 1258 | 84 | 105672 | 1258 | 0.32545 | 0.0038744 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 1258 | 0.32545 | 0.0038744
134431 | 41388.4764 | 41388.5194 | 662 | 59 | 38810.5806 | 657.8065 | 0.11953 | 0.0020389 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | C | 657.8065 | 0.11953 | 0.0020389
134432 | 41390.5653 | 41390.6493 | 204 | 118 | 16587.2893 | 140.5702 | 0.051086 | 0.00062829 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 140.5702 | 0.051086 | 0.00062829
134433 | 41390.4236 | 41390.4931 | 602 | 97 | 58394 | 602 | 0.17984 | 0.0018541 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 602 | 0.17984 | 0.0018541
134436 | 41391.325 | 41391.441 | 2 | 164 | 328 | 2 | 0.0010102 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-27 | 2014 | 2014 | 2013-04-27 | C | 2 | 0.0010102 | 6.1597e-06
134440 | 41391.5174 | 41391.6611 | 22 | 204 | 4488 | 22 | 0.013822 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-27 | 2014 | 2014 | 2013-04-27 | C | 22 | 0.013822 | 6.7757e-05
134447 | 41390.8292 | 41391.1924 | 506 | 520 | 88315.4876 | 169.8375 | 0.272 | 0.0015584 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 169.8375 | 0.272 | 0.0015584
134449 | 41392.4639 | 41392.5208 | 11 | 79 | 869 | 11 | 0.0026764 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-28 | 2014 | 2014 | 2013-04-28 | C | 11 | 0.0026764 | 3.3878e-05
134450 | 41392.4993 | 41392.5243 | 7 | 33 | 198 | 6 | 0.00060981 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-28 | 2014 | 2014 | 2013-04-28 | C | 6 | 0.00060981 | 2.1559e-05
134451 | 41390.9618 | 41391.1188 | 381 | 223 | 57969.146 | 259.9513 | 0.17854 | 0.0011734 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-26 | 2014 | 2014 | 2013-04-26 | C | 259.9513 | 0.17854 | 0.0011734
134452 | 41392.8354 | 41392.9625 | 96 | 180 | 7081.9672 | 39.3443 | 0.021811 | 0.00029566 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-28 | 2014 | 2014 | 2013-04-28 | C | 39.3443 | 0.021811 | 0.00029566
134455 | 41385.3757 | 41385.4306 | 3 | 76 | 228 | 3 | 0.0007022 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 3 | 0.0007022 | 9.2395e-06
134456 | 41385.4007 | 41385.4688 | 9 | 95 | 855 | 9 | 0.0026333 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-21 | 2014 | 2014 | 2013-04-21 | C | 9 | 0.0026333 | 2.7719e-05
134457 | 41393.3826 | 41393.6181 | 24 | 336 | 8064 | 24 | 0.024836 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-29 | 2014 | 2014 | 2013-04-29 | B | 24 | 0.024836 | 7.3916e-05
134459 | 41393.6111 | 41393.6479 | 16 | 50 | 800 | 16 | 0.0024639 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-29 | 2014 | 2014 | 2013-04-29 | C | 16 | 0.0024639 | 4.9277e-05
134460 | 41393.5 | 41393.5493 | 31 | 68 | 2108 | 31 | 0.0064923 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-29 | 2014 | 2014 | 2013-04-29 | C | 31 | 0.0064923 | 9.5475e-05
134462 | 41394.0535 | 41394.2479 | 541 | 277 | 34475.6179 | 124.4607 | 0.10618 | 0.0016662 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | C | 124.4607 | 0.10618 | 0.0016662
134466 | 41388.3889 | 41388.5757 | 156 | 266 | 41496 | 156 | 0.1278 | 0.00048046 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-24 | 2014 | 2014 | 2013-04-24 | B | 156 | 0.1278 | 0.00048046
134471 | 41393.3583 | 41393.3694 | 86 | 13 | 1118 | 86 | 0.0034433 | 0.00026487 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-29 | 2014 | 2014 | 2013-04-29 | B | 86 | 0.0034433 | 0.00026487
134473 | 41394.391 | 41394.5799 | 2 | 269 | 538 | 2 | 0.001657 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | B | 2 | 0.001657 | 6.1597e-06
134476 | 41394.3958 | 41394.6333 | 2 | 339 | 678 | 2 | 0.0020881 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | C | 2 | 0.0020881 | 6.1597e-06
134477 | 41394.3333 | 41394.3812 | 63 | 66 | 4158 | 63 | 0.012806 | 0.00019403 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | C | 63 | 0.012806 | 0.00019403
134481 | 41394.8347 | 41394.934 | 102 | 140 | 6797.3427 | 48.5524 | 0.020935 | 0.00031414 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | C | 48.5524 | 0.020935 | 0.00031414
134482 | 41395.409 | 41395.4958 | 35 | 122 | 4270 | 35 | 0.013151 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 35 | 0.013151 | 0.00010779
134483 | 41394.3958 | 41394.6299 | 37 | 334 | 12358 | 37 | 0.038061 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | B | 37 | 0.038061 | 0.00011395
134484 | 41394.375 | 41394.6389 | 26 | 377 | 9802 | 26 | 0.030189 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | B | 26 | 0.030189 | 8.0076e-05
134485 | 41395.366 | 41395.4062 | 371 | 55 | 18388.0172 | 334.3276 | 0.056632 | 0.0011426 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | C | 334.3276 | 0.056632 | 0.0011426
134486 | 41394.3854 | 41394.5903 | 35 | 292 | 10220 | 35 | 0.031476 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | B | 35 | 0.031476 | 0.00010779
134487 | 41394.3826 | 41394.5611 | 80 | 254 | 20320 | 80 | 0.062582 | 0.00024639 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-30 | 2014 | 2014 | 2013-04-30 | B | 80 | 0.062582 | 0.00024639
134488 | 41395.3847 | 41395.5792 | 28 | 277 | 7756 | 28 | 0.023887 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 28 | 0.023887 | 8.6236e-05
134489 | 41395.5729 | 41395.6194 | 47 | 64 | 3008 | 47 | 0.0092642 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | C | 47 | 0.0092642 | 0.00014475
134491 | 41395.375 | 41395.6375 | 115 | 375 | 43125 | 115 | 0.13282 | 0.00035418 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 115 | 0.13282 | 0.00035418
134492 | 41395.3549 | 41395.6257 | 4 | 387 | 1548 | 4 | 0.0047676 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 4 | 0.0047676 | 1.2319e-05
134493 | 41365.3646 | 41365.65 | 65 | 408 | 26520 | 65 | 0.081677 | 0.00020019 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-04-01 | 2014 | 2014 | 2013-04-01 | B | 65 | 0.081677 | 0.00020019
134495 | 41395.3847 | 41395.6625 | 121 | 397 | 48037 | 121 | 0.14795 | 0.00037266 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 121 | 0.14795 | 0.00037266
134501 | 41395.7236 | 41395.8597 | 388 | 193 | 26206.6429 | 135.7857 | 0.080712 | 0.001195 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | C | 135.7857 | 0.080712 | 0.001195
134502 | 41395.859 | 41395.925 | 370 | 92 | 33497.6842 | 364.1053 | 0.10317 | 0.0011395 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | C | 364.1053 | 0.10317 | 0.0011395
134503 | 41396.3417 | 41396.3514 | 375 | 11 | 4125 | 375 | 0.012704 | 0.0011549 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | C | 375 | 0.012704 | 0.0011549
134504 | 41395.5903 | 41395.6667 | 1 | 107 | 107 | 1 | 0.00032954 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | C | 1 | 0.00032954 | 3.0798e-06
134505 | 41396.3993 | 41396.4194 | 1125 | 26 | 29250 | 1125 | 0.090085 | 0.0034648 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | C | 1125 | 0.090085 | 0.0034648
134506 | 41396.4167 | 41396.4993 | 137 | 116 | 15892 | 137 | 0.048945 | 0.00042194 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 137 | 0.048945 | 0.00042194
134510 | 41396.3972 | 41396.5507 | 73 | 218 | 15914 | 73 | 0.049013 | 0.00022483 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 73 | 0.049013 | 0.00022483
134511 | 41396.4958 | 41396.5681 | 217 | 101 | 11044.9327 | 109.3558 | 0.034017 | 0.00066833 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | C | 109.3558 | 0.034017 | 0.00066833
134513 | 41396.375 | 41396.6188 | 28 | 348 | 9744 | 28 | 0.03001 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 28 | 0.03001 | 8.6236e-05
134515 | 41396.4167 | 41396.6389 | 10 | 317 | 3170 | 10 | 0.0097631 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 10 | 0.0097631 | 3.0798e-05
134517 | 41396.5771 | 41396.6847 | 392 | 152 | 27984.671 | 184.1097 | 0.086188 | 0.0012073 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | C | 184.1097 | 0.086188 | 0.0012073
134519 | 41396.375 | 41396.625 | 137 | 357 | 48909 | 137 | 0.15063 | 0.00042194 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 137 | 0.15063 | 0.00042194
134520 | 41396.3743 | 41396.6986 | 433 | 464 | 200912 | 433 | 0.61878 | 0.0013336 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | B | 433 | 0.61878 | 0.0013336
134521 | 41396.5833 | 41396.6729 | 1 | 126 | 126 | 1 | 0.00038806 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-02 | 2014 | 2014 | 2013-05-02 | C | 1 | 0.00038806 | 3.0798e-06
134524 | 41397.0604 | 41397.1556 | 242 | 134 | 13234.7007 | 98.7664 | 0.040761 | 0.00074532 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | C | 98.7664 | 0.040761 | 0.00074532
134526 | 41397.5819 | 41397.6201 | 19 | 52 | 988 | 19 | 0.0030429 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | C | 19 | 0.0030429 | 5.8517e-05
134527 | 41397.3681 | 41397.4264 | 3 | 81 | 243 | 3 | 0.0007484 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | B | 3 | 0.0007484 | 9.2395e-06
134529 | 41397.3792 | 41397.5611 | 26 | 259 | 6734 | 26 | 0.02074 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | B | 26 | 0.02074 | 8.0076e-05
134531 | 41397.7937 | 41397.8639 | 291 | 98 | 28518 | 291 | 0.087831 | 0.00089623 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | C | 291 | 0.087831 | 0.00089623
134532 | 41397.8208 | 41397.9264 | 74 | 149 | 11026 | 74 | 0.033958 | 0.00022791 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-03 | 2014 | 2014 | 2013-05-03 | C | 74 | 0.033958 | 0.00022791
134533 | 41398.3125 | 41398.3646 | 29 | 72 | 2088 | 29 | 0.0064307 | 8.9315e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-04 | 2014 | 2014 | 2013-05-04 | C | 29 | 0.0064307 | 8.9315e-05
134534 | 41398.2812 | 41398.4479 | 432 | 237 | 102384 | 432 | 0.31533 | 0.0013305 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-04 | 2014 | 2014 | 2013-05-04 | C | 432 | 0.31533 | 0.0013305
134538 | 41398.5132 | 41398.5181 | 2 | 4 | 8 | 2 | 2.4639e-05 | 6.1597e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-04 | 2014 | 2014 | 2013-05-04 | C | 2 | 2.4639e-05 | 6.1597e-06
134540 | 41398.6201 | 41398.6549 | 35 | 47 | 1645 | 35 | 0.0050663 | 0.00010779 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-04 | 2014 | 2014 | 2013-05-04 | C | 35 | 0.0050663 | 0.00010779
134547 | 41399.3542 | 41399.4382 | 50 | 118 | 5900 | 50 | 0.018171 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | B | 50 | 0.018171 | 0.00015399
134548 | 41398.375 | 41398.5069 | 20 | 187 | 3740 | 20 | 0.011519 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-04 | 2014 | 2014 | 2013-05-04 | B | 20 | 0.011519 | 6.1597e-05
134549 | 41399.5104 | 41399.5549 | 25 | 61 | 1525 | 25 | 0.0046968 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 25 | 0.0046968 | 7.6996e-05
134550 | 41399.5417 | 41399.7181 | 10 | 251 | 2510 | 10 | 0.0077304 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | B | 10 | 0.0077304 | 3.0798e-05
134554 | 41399.4875 | 41399.6403 | 236 | 217 | 34197.2273 | 157.5909 | 0.10532 | 0.00072684 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 157.5909 | 0.10532 | 0.00072684
134556 | 41399.7222 | 41399.7931 | 211 | 99 | 13865.8235 | 140.0588 | 0.042705 | 0.00064985 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 140.0588 | 0.042705 | 0.00064985
134557 | 41399.0299 | 41399.1319 | 22 | 144 | 3024 | 21 | 0.0093134 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 21 | 0.0093134 | 6.7757e-05
134559 | 41399.8757 | 41399.9437 | 211 | 95 | 9748.1633 | 102.6122 | 0.030023 | 0.00064985 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 102.6122 | 0.030023 | 0.00064985
134563 | 41400.0167 | 41400.1167 | 237 | 141 | 19704.75 | 139.75 | 0.060688 | 0.00072992 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 139.75 | 0.060688 | 0.00072992
134567 | 41399.9597 | 41400.1701 | 5 | 300 | 1500 | 5 | 0.0046198 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | B | 5 | 0.0046198 | 1.5399e-05
134569 | 41399.9847 | 41400.1944 | 257 | 299 | 40404.6026 | 135.1325 | 0.12444 | 0.00079152 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | C | 135.1325 | 0.12444 | 0.00079152
134570 | 41399.3562 | 41399.4382 | 48 | 115 | 5276.3559 | 45.8814 | 0.01625 | 0.00014783 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-05 | 2014 | 2014 | 2013-05-05 | B | 45.8814 | 0.01625 | 0.00014783
134571 | 41400.4062 | 41400.4778 | 60 | 100 | 6000 | 60 | 0.018479 | 0.00018479 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | B | 60 | 0.018479 | 0.00018479
134572 | 41400.3903 | 41400.5326 | 561 | 202 | 91456.7317 | 452.7561 | 0.28167 | 0.0017278 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 452.7561 | 0.28167 | 0.0017278
134573 | 41400.3854 | 41400.5299 | 22 | 205 | 4510 | 22 | 0.01389 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | B | 22 | 0.01389 | 6.7757e-05
134577 | 41400.3646 | 41400.6653 | 18 | 430 | 7740 | 18 | 0.023838 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | B | 18 | 0.023838 | 5.5437e-05
134578 | 41400.9792 | 41401.0278 | 3 | 67 | 201 | 3 | 0.00061905 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 3 | 0.00061905 | 9.2395e-06
134579 | 41401.0312 | 41401.075 | 82 | 60 | 4920 | 82 | 0.015153 | 0.00025255 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 82 | 0.015153 | 0.00025255
134580 | 41400.9021 | 41400.9965 | 194 | 133 | 21531.3309 | 161.8897 | 0.066313 | 0.00059749 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 161.8897 | 0.066313 | 0.00059749
134581 | 41400.7993 | 41400.8535 | 8 | 75 | 600 | 8 | 0.0018479 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 8 | 0.0018479 | 2.4639e-05
134582 | 41401.0847 | 41401.1569 | 1544 | 101 | 124657.3077 | 1234.2308 | 0.38392 | 0.0047553 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 1234.2308 | 0.38392 | 0.0047553
134583 | 41400.6583 | 41400.9097 | 1067 | 359 | 74025.4033 | 206.1989 | 0.22799 | 0.0032862 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 206.1989 | 0.22799 | 0.0032862
134586 | 41400.4111 | 41400.5833 | 1374 | 245 | 77789.4758 | 317.5081 | 0.23958 | 0.0042317 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | C | 317.5081 | 0.23958 | 0.0042317
134587 | 41401.1104 | 41401.3167 | 215 | 294 | 25555.2323 | 86.9226 | 0.078706 | 0.00066217 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 86.9226 | 0.078706 | 0.00066217
134588 | 41401.1611 | 41401.3458 | 51 | 263 | 13413 | 51 | 0.04131 | 0.00015707 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 51 | 0.04131 | 0.00015707
134590 | 41401.3854 | 41401.5625 | 91 | 252 | 22932 | 91 | 0.070627 | 0.00028027 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | B | 91 | 0.070627 | 0.00028027
134591 | 41401.4806 | 41401.5646 | 239 | 118 | 4219.719 | 35.7603 | 0.012996 | 0.00073608 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 35.7603 | 0.012996 | 0.00073608
134593 | 41401.3715 | 41401.634 | 40 | 375 | 15000 | 40 | 0.046198 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | B | 40 | 0.046198 | 0.00012319
134600 | 41401.5889 | 41401.6438 | 5 | 76 | 380 | 5 | 0.0011703 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 5 | 0.0011703 | 1.5399e-05
134603 | 41401.7882 | 41401.8361 | 101 | 66 | 6666 | 101 | 0.02053 | 0.00031106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 101 | 0.02053 | 0.00031106
134604 | 41401.6979 | 41401.7625 | 110 | 90 | 7732.2581 | 85.914 | 0.023814 | 0.00033878 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 85.914 | 0.023814 | 0.00033878
134605 | 41401.7611 | 41402.0417 | 27 | 401 | 10827 | 27 | 0.033345 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | B | 27 | 0.033345 | 8.3156e-05
134606 | 41401.4285 | 41401.5347 | 2 | 150 | 300 | 2 | 0.00092395 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | C | 2 | 0.00092395 | 6.1597e-06
134609 | 41402.4153 | 41402.5604 | 14 | 206 | 2884 | 14 | 0.0088823 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | B | 14 | 0.0088823 | 4.3118e-05
134610 | 41402.4167 | 41402.4924 | 88 | 106 | 8925.3945 | 84.2018 | 0.027489 | 0.00027103 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | C | 84.2018 | 0.027489 | 0.00027103
134612 | 41402.3861 | 41402.6285 | 16 | 346 | 5536 | 16 | 0.01705 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | B | 16 | 0.01705 | 4.9277e-05
134615 | 41402.4181 | 41402.5819 | 165 | 233 | 38445 | 165 | 0.1184 | 0.00050817 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | B | 165 | 0.1184 | 0.00050817
134619 | 41402.3854 | 41402.6583 | 35 | 390 | 13650 | 35 | 0.04204 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | B | 35 | 0.04204 | 0.00010779
134626 | 41402.6903 | 41402.9444 | 24 | 363 | 7671.5984 | 21.1339 | 0.023627 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | C | 21.1339 | 0.023627 | 7.3916e-05
134627 | 41403.7417 | 41403.7757 | 983 | 46 | 45218 | 983 | 0.13926 | 0.0030275 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 983 | 0.13926 | 0.0030275
134628 | 41402.7417 | 41402.9778 | 797 | 337 | 93433.25 | 277.25 | 0.28776 | 0.0024546 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | C | 277.25 | 0.28776 | 0.0024546
134629 | 41402.375 | 41402.6729 | 273 | 426 | 74425.8741 | 174.7086 | 0.22922 | 0.0008408 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | B | 174.7086 | 0.22922 | 0.0008408
134630 | 41402.4167 | 41402.6417 | 44 | 321 | 14124 | 44 | 0.0435 | 0.00013551 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-08 | 2014 | 2014 | 2013-05-08 | C | 44 | 0.0435 | 0.00013551
134631 | 41403.3861 | 41403.3958 | 2 | 11 | 22 | 2 | 6.7757e-05 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 2 | 6.7757e-05 | 6.1597e-06
134634 | 41403.4306 | 41403.4451 | 1 | 18 | 18 | 1 | 5.5437e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 1 | 5.5437e-05 | 3.0798e-06
134636 | 41403.3646 | 41403.5674 | 116 | 289 | 39608.8356 | 137.0548 | 0.12199 | 0.00035726 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 137.0548 | 0.12199 | 0.00035726
134638 | 41403.375 | 41403.5771 | 39 | 288 | 11579.3814 | 40.2062 | 0.035663 | 0.00012011 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 40.2062 | 0.035663 | 0.00012011
134639 | 41403.3854 | 41403.5944 | 20 | 298 | 5960 | 20 | 0.018356 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 20 | 0.018356 | 6.1597e-05
134641 | 41403.3646 | 41403.5944 | 37 | 328 | 12136 | 37 | 0.037377 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 37 | 0.037377 | 0.00011395
134643 | 41403.375 | 41403.6424 | 8 | 382 | 3056 | 8 | 0.009412 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 8 | 0.009412 | 2.4639e-05
134644 | 41403.3854 | 41403.6625 | 9 | 396 | 3564 | 9 | 0.010977 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 9 | 0.010977 | 2.7719e-05
134646 | 41403.375 | 41403.6465 | 25 | 388 | 9700 | 25 | 0.029874 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 25 | 0.029874 | 7.6996e-05
134648 | 41403.5938 | 41403.6917 | 1 | 138 | 138 | 1 | 0.00042502 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 1 | 0.00042502 | 3.0798e-06
134650 | 41403.7729 | 41403.7799 | 136 | 7 | 952 | 136 | 0.002932 | 0.00041886 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 136 | 0.002932 | 0.00041886
134651 | 41403.7729 | 41403.8771 | 4 | 147 | 588 | 4 | 0.0018109 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 4 | 0.0018109 | 1.2319e-05
134652 | 41404.3201 | 41404.3313 | 246 | 13 | 3198 | 246 | 0.0098493 | 0.00075764 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 246 | 0.0098493 | 0.00075764
134653 | 41404.3458 | 41404.391 | 91 | 62 | 5382.5538 | 86.8154 | 0.016577 | 0.00028027 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 86.8154 | 0.016577 | 0.00028027
134654 | 41404.3569 | 41404.4771 | 1 | 170 | 170 | 1 | 0.00052357 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 1 | 0.00052357 | 3.0798e-06
134655 | 41404.4062 | 41404.4486 | 54 | 58 | 3132 | 54 | 0.0096461 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | B | 54 | 0.0096461 | 0.00016631
134656 | 41404.375 | 41404.5243 | 8 | 212 | 1696 | 8 | 0.0052234 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | B | 8 | 0.0052234 | 2.4639e-05
134657 | 41404.5104 | 41404.5792 | 67 | 96 | 5020.1212 | 52.2929 | 0.015461 | 0.00020635 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 52.2929 | 0.015461 | 0.00020635
134658 | 41404.5743 | 41404.5882 | 205 | 17 | 3286.1 | 193.3 | 0.010121 | 0.00063137 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 193.3 | 0.010121 | 0.00063137
134660 | 41404.4701 | 41404.5764 | 141 | 150 | 7836.2745 | 52.2418 | 0.024134 | 0.00043426 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 52.2418 | 0.024134 | 0.00043426
134665 | 41404.7569 | 41404.7681 | 89 | 13 | 1157 | 89 | 0.0035634 | 0.00027411 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 89 | 0.0035634 | 0.00027411
134666 | 41404.7924 | 41404.8285 | 254 | 49 | 10054.4231 | 205.1923 | 0.030966 | 0.00078228 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 205.1923 | 0.030966 | 0.00078228
134667 | 41404.7694 | 41404.7896 | 89 | 26 | 2314 | 89 | 0.0071268 | 0.00027411 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 89 | 0.0071268 | 0.00027411
134669 | 41405.3368 | 41405.3819 | 26 | 62 | 1612 | 26 | 0.0049647 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-11 | 2014 | 2014 | 2013-05-11 | C | 26 | 0.0049647 | 8.0076e-05
134672 | 41405.5035 | 41405.5694 | 1 | 92 | 92 | 1 | 0.00028335 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-11 | 2014 | 2014 | 2013-05-11 | B | 1 | 0.00028335 | 3.0798e-06
134673 | 41404.6583 | 41404.7694 | 603 | 157 | 41374.4062 | 263.5312 | 0.12743 | 0.0018571 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-10 | 2014 | 2014 | 2013-05-10 | C | 263.5312 | 0.12743 | 0.0018571
134675 | 41405.6764 | 41405.8111 | 832 | 191 | 26421.9948 | 138.3351 | 0.081376 | 0.0025624 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-11 | 2014 | 2014 | 2013-05-11 | C | 138.3351 | 0.081376 | 0.0025624
134678 | 41406.5444 | 41406.675 | 9 | 185 | 1665 | 9 | 0.0051279 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-12 | 2014 | 2014 | 2013-05-12 | B | 9 | 0.0051279 | 2.7719e-05
134682 | 41407.2917 | 41407.3174 | 2706 | 34 | 89087.3514 | 2620.2162 | 0.27437 | 0.0083341 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | C | 2620.2162 | 0.27437 | 0.0083341
134683 | 41403.375 | 41403.5097 | 1 | 191 | 191 | 1 | 0.00058825 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 1 | 0.00058825 | 3.0798e-06
134684 | 41403.5104 | 41403.5493 | 9 | 53 | 477 | 9 | 0.0014691 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | C | 9 | 0.0014691 | 2.7719e-05
134687 | 41407.4028 | 41407.5556 | 2 | 217 | 434 | 2 | 0.0013367 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 2 | 0.0013367 | 6.1597e-06
134688 | 41407.5542 | 41407.6354 | 2 | 114 | 228 | 2 | 0.0007022 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | C | 2 | 0.0007022 | 6.1597e-06
134689 | 41407.3542 | 41407.6424 | 6 | 412 | 2472 | 6 | 0.0076134 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 6 | 0.0076134 | 1.8479e-05
134690 | 41407.5361 | 41407.5854 | 101 | 68 | 6868 | 101 | 0.021152 | 0.00031106 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | C | 101 | 0.021152 | 0.00031106
134691 | 41407.3854 | 41407.6111 | 278 | 322 | 89516 | 278 | 0.2757 | 0.0008562 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 278 | 0.2757 | 0.0008562
134693 | 41407.4514 | 41407.5882 | 32 | 194 | 6208 | 32 | 0.01912 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 32 | 0.01912 | 9.8555e-05
134695 | 41407.9583 | 41407.9889 | 60 | 41 | 2460 | 60 | 0.0075764 | 0.00018479 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 60 | 0.0075764 | 0.00018479
134697 | 41408.3826 | 41408.5903 | 31 | 296 | 9176 | 31 | 0.028261 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 31 | 0.028261 | 9.5475e-05
134698 | 41408.3854 | 41408.625 | 25 | 342 | 8550 | 25 | 0.026333 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 25 | 0.026333 | 7.6996e-05
134699 | 41408.3854 | 41408.6389 | 44 | 362 | 15928 | 44 | 0.049056 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 44 | 0.049056 | 0.00013551
134701 | 41408.375 | 41408.6639 | 50 | 413 | 20650 | 50 | 0.063599 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 50 | 0.063599 | 0.00015399
134702 | 41408.3646 | 41408.65 | 38 | 408 | 15504 | 38 | 0.04775 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 38 | 0.04775 | 0.00011703
134703 | 41408.7153 | 41408.7431 | 1 | 37 | 37 | 1 | 0.00011395 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | C | 1 | 0.00011395 | 3.0798e-06
134704 | 41408.375 | 41408.6479 | 121 | 390 | 47190 | 121 | 0.14534 | 0.00037266 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-14 | 2014 | 2014 | 2013-05-14 | B | 121 | 0.14534 | 0.00037266
134709 | 41409.3139 | 41409.334 | 91 | 26 | 2366 | 91 | 0.0072869 | 0.00028027 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-15 | 2014 | 2014 | 2013-05-15 | C | 91 | 0.0072869 | 0.00028027
134710 | 41409.3965 | 41409.5153 | 13 | 168 | 2184 | 13 | 0.0067264 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-15 | 2014 | 2014 | 2013-05-15 | B | 13 | 0.0067264 | 4.0038e-05
134711 | 41403.3958 | 41403.5146 | 5 | 168 | 840 | 5 | 0.0025871 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-09 | 2014 | 2014 | 2013-05-09 | B | 5 | 0.0025871 | 1.5399e-05
134712 | 41407.3646 | 41407.5993 | 6 | 335 | 2010 | 6 | 0.0061905 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-13 | 2014 | 2014 | 2013-05-13 | B | 6 | 0.0061905 | 1.8479e-05
134713 | 41400.4236 | 41400.6042 | 3 | 257 | 771 | 3 | 0.0023746 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-06 | 2014 | 2014 | 2013-05-06 | B | 3 | 0.0023746 | 9.2395e-06
134714 | 41401.3958 | 41401.6076 | 69 | 302 | 20838 | 69 | 0.064178 | 0.00021251 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-07 | 2014 | 2014 | 2013-05-07 | B | 69 | 0.064178 | 0.00021251
134715 | 41409.0139 | 41409.4618 | 13 | 642 | 8346 | 13 | 0.025704 | 4.0038e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-15 | 2014 | 2014 | 2013-05-15 | C | 13 | 0.025704 | 4.0038e-05
134716 | 41409.3562 | 41409.6097 | 3 | 362 | 1086 | 3 | 0.0033447 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-15 | 2014 | 2014 | 2013-05-15 | B | 3 | 0.0033447 | 9.2395e-06
134720 | 41410.4062 | 41410.5931 | 35 | 266 | 9310 | 35 | 0.028673 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 35 | 0.028673 | 0.00010779
134722 | 41410.3792 | 41410.6354 | 13 | 366 | 4758 | 13 | 0.014654 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 13 | 0.014654 | 4.0038e-05
134723 | 41410.375 | 41410.6458 | 121 | 387 | 46827 | 121 | 0.14422 | 0.00037266 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 121 | 0.14422 | 0.00037266
134724 | 41410.375 | 41410.6493 | 16 | 392 | 6272 | 16 | 0.019317 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 16 | 0.019317 | 4.9277e-05
134725 | 41410.3667 | 41410.5965 | 8 | 328 | 2624 | 8 | 0.0080815 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 8 | 0.0080815 | 2.4639e-05
134726 | 41410.3646 | 41410.5312 | 38 | 237 | 9006 | 38 | 0.027737 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 38 | 0.027737 | 0.00011703
134729 | 41410.4035 | 41410.6389 | 7 | 336 | 2352 | 7 | 0.0072438 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 7 | 0.0072438 | 2.1559e-05
134731 | 41410.375 | 41410.6181 | 8 | 347 | 2776 | 8 | 0.0085496 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | B | 8 | 0.0085496 | 2.4639e-05
134733 | 41410.691 | 41410.7451 | 149 | 75 | 6575 | 87.6667 | 0.02025 | 0.0004589 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | C | 87.6667 | 0.02025 | 0.0004589
134734 | 41410.4944 | 41410.866 | 585 | 532 | 122902.9383 | 231.0206 | 0.37852 | 0.0018017 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-16 | 2014 | 2014 | 2013-05-16 | C | 231.0206 | 0.37852 | 0.0018017
134736 | 41411.375 | 41411.5424 | 30 | 238 | 7140 | 30 | 0.02199 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | B | 30 | 0.02199 | 9.2395e-05
134737 | 41411.5 | 41411.625 | 3 | 177 | 531 | 3 | 0.0016354 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | B | 3 | 0.0016354 | 9.2395e-06
134738 | 41411.3854 | 41411.584 | 7 | 283 | 1981 | 7 | 0.0061012 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | B | 7 | 0.0061012 | 2.1559e-05
134739 | 41411.3958 | 41411.6549 | 35 | 370 | 12950 | 35 | 0.039884 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | B | 35 | 0.039884 | 0.00010779
134740 | 41411.5667 | 41411.6292 | 8 | 87 | 696 | 8 | 0.0021436 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | C | 8 | 0.0021436 | 2.4639e-05
134744 | 41412.316 | 41412.3653 | 4 | 68 | 272 | 4 | 0.00083772 | 1.2319e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-18 | 2014 | 2014 | 2013-05-18 | C | 4 | 0.00083772 | 1.2319e-05
134752 | 41412.8201 | 41412.9389 | 14 | 168 | 2352 | 14 | 0.0072438 | 4.3118e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-18 | 2014 | 2014 | 2013-05-18 | C | 14 | 0.0072438 | 4.3118e-05
134753 | 41412.6813 | 41412.7562 | 268 | 105 | 28140 | 268 | 0.086667 | 0.0008254 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-18 | 2014 | 2014 | 2013-05-18 | C | 268 | 0.086667 | 0.0008254
134758 | 41413.4174 | 41413.4285 | 258 | 13 | 3354 | 258 | 0.01033 | 0.0007946 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 258 | 0.01033 | 0.0007946
134760 | 41413.375 | 41413.5111 | 16 | 193 | 3088 | 16 | 0.0095106 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | B | 16 | 0.0095106 | 4.9277e-05
134762 | 41413.2125 | 41413.2667 | 277 | 75 | 20775 | 277 | 0.063984 | 0.00085312 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | B | 277 | 0.063984 | 0.00085312
134764 | 41413.4479 | 41413.5125 | 11 | 90 | 990 | 11 | 0.003049 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 11 | 0.003049 | 3.3878e-05
134765 | 41413.5694 | 41413.6458 | 16 | 107 | 1712 | 16 | 0.0052727 | 4.9277e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 16 | 0.0052727 | 4.9277e-05
134766 | 41413.6528 | 41413.6674 | 130 | 18 | 2340 | 130 | 0.0072068 | 0.00040038 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 130 | 0.0072068 | 0.00040038
134767 | 41413.6882 | 41413.7188 | 258 | 41 | 10578 | 258 | 0.032579 | 0.0007946 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 258 | 0.032579 | 0.0007946
134768 | 41413.5 | 41413.7083 | 2 | 297 | 594 | 2 | 0.0018294 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 2 | 0.0018294 | 6.1597e-06
134769 | 41413.7188 | 41413.7625 | 13 | 60 | 780 | 13 | 0.0024023 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 13 | 0.0024023 | 4.0038e-05
134770 | 41413.7812 | 41413.8125 | 6 | 42 | 252 | 6 | 0.00077612 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 6 | 0.00077612 | 1.8479e-05
134771 | 41413.95 | 41414.3271 | 368 | 540 | 27311.2707 | 50.5764 | 0.084114 | 0.0011334 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-19 | 2014 | 2014 | 2013-05-19 | C | 50.5764 | 0.084114 | 0.0011334
134772 | 41411.4243 | 41411.6167 | 73 | 274 | 20002 | 73 | 0.061603 | 0.00022483 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | B | 73 | 0.061603 | 0.00022483
134774 | 41414.5021 | 41414.5292 | 41 | 36 | 1476 | 41 | 0.0045458 | 0.00012627 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | C | 41 | 0.0045458 | 0.00012627
134777 | 41414.4104 | 41414.6299 | 4 | 313 | 1252 | 4 | 0.003856 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | B | 4 | 0.003856 | 1.2319e-05
134779 | 41414.3542 | 41414.6715 | 9 | 454 | 4086 | 9 | 0.012584 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | B | 9 | 0.012584 | 2.7719e-05
134780 | 41414.5507 | 41414.5903 | 10 | 54 | 540 | 10 | 0.0016631 | 3.0798e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | C | 10 | 0.0016631 | 3.0798e-05
134781 | 41414.7444 | 41414.7472 | 681 | 1 | 681 | 681 | 0.0020974 | 0.0020974 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | C | 681 | 0.0020974 | 0.0020974
134783 | 41414.859 | 41414.9139 | 7 | 76 | 470.4304 | 6.1899 | 0.0014489 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | C | 6.1899 | 0.0014489 | 2.1559e-05
134785 | 41414.5083 | 41414.5181 | 756 | 11 | 8316 | 756 | 0.025612 | 0.0023284 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | C | 756 | 0.025612 | 0.0023284
134787 | 41415.3958 | 41415.5451 | 4 | 212 | 848 | 4 | 0.0026117 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-21 | 2014 | 2014 | 2013-05-21 | B | 4 | 0.0026117 | 1.2319e-05
134788 | 41415.3542 | 41415.5729 | 160 | 312 | 49920 | 160 | 0.15375 | 0.00049277 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-21 | 2014 | 2014 | 2013-05-21 | B | 160 | 0.15375 | 0.00049277
134789 | 41415.3854 | 41415.5729 | 60 | 267 | 16020 | 60 | 0.049339 | 0.00018479 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-21 | 2014 | 2014 | 2013-05-21 | B | 60 | 0.049339 | 0.00018479
134790 | 41415.5819 | 41415.6347 | 1 | 73 | 73 | 1 | 0.00022483 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-21 | 2014 | 2014 | 2013-05-21 | C | 1 | 0.00022483 | 3.0798e-06
134792 | 41415.2986 | 41415.4799 | 258 | 258 | 43842.2069 | 169.931 | 0.13503 | 0.0007946 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-21 | 2014 | 2014 | 2013-05-21 | C | 169.931 | 0.13503 | 0.0007946
134793 | 41416.0049 | 41416.0604 | 680 | 77 | 34443.0625 | 447.3125 | 0.10608 | 0.0020943 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 447.3125 | 0.10608 | 0.0020943
134795 | 41416.3854 | 41416.4368 | 6 | 71 | 426 | 6 | 0.001312 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | B | 6 | 0.001312 | 1.8479e-05
134798 | 41416.3646 | 41416.5444 | 27 | 256 | 6912 | 27 | 0.021288 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | B | 27 | 0.021288 | 8.3156e-05
134799 | 41416.5708 | 41416.6875 | 44 | 165 | 6837.6786 | 41.4405 | 0.021059 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 41.4405 | 0.021059 | 0.00013551
134804 | 41416.4021 | 41416.6201 | 31 | 311 | 9641 | 31 | 0.029693 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | B | 31 | 0.029693 | 9.5475e-05
134806 | 41416.7694 | 41416.8993 | 545 | 184 | 63441.6257 | 344.7914 | 0.19539 | 0.0016785 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 344.7914 | 0.19539 | 0.0016785
134807 | 41416.7222 | 41416.7694 | 1 | 65 | 65 | 1 | 0.00020019 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 1 | 0.00020019 | 3.0798e-06
134809 | 41416.6597 | 41416.709 | 3 | 68 | 204 | 3 | 0.00062829 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 3 | 0.00062829 | 9.2395e-06
134810 | 41416.8125 | 41416.9201 | 6 | 152 | 912 | 6 | 0.0028088 | 1.8479e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 6 | 0.0028088 | 1.8479e-05
134811 | 41416.684 | 41417.0069 | 146 | 462 | 32980.8387 | 71.3871 | 0.10158 | 0.00044966 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | C | 71.3871 | 0.10158 | 0.00044966
134813 | 41416.375 | 41416.6701 | 443 | 422 | 186946 | 443 | 0.57576 | 0.0013644 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-22 | 2014 | 2014 | 2013-05-22 | B | 443 | 0.57576 | 0.0013644
134815 | 41417.3236 | 41417.35 | 667 | 35 | 22260 | 636 | 0.068557 | 0.0020543 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 636 | 0.068557 | 0.0020543
134818 | 41417.375 | 41417.6347 | 13 | 371 | 4823 | 13 | 0.014854 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 13 | 0.014854 | 4.0038e-05
134819 | 41417.3646 | 41417.625 | 540 | 372 | 74138.112 | 199.296 | 0.22833 | 0.0016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 199.296 | 0.22833 | 0.0016631
134820 | 41417.3896 | 41417.6125 | 42 | 318 | 13356 | 42 | 0.041134 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 42 | 0.041134 | 0.00012935
134822 | 41417.3646 | 41417.625 | 7 | 372 | 2604 | 7 | 0.0080199 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 7 | 0.0080199 | 2.1559e-05
134823 | 41417.4257 | 41417.4472 | 516 | 28 | 14448 | 516 | 0.044498 | 0.0015892 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 516 | 0.044498 | 0.0015892
134824 | 41417.575 | 41417.6042 | 3 | 39 | 117 | 3 | 0.00036034 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 3 | 0.00036034 | 9.2395e-06
134825 | 41417.3854 | 41417.4819 | 52 | 136 | 7072 | 52 | 0.021781 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 52 | 0.021781 | 0.00016015
134826 | 41417.5167 | 41417.6736 | 1 | 223 | 223 | 1 | 0.0006868 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 1 | 0.0006868 | 3.0798e-06
134827 | 41417.4257 | 41417.4771 | 819 | 71 | 58149 | 819 | 0.17909 | 0.0025224 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 819 | 0.17909 | 0.0025224
134828 | 41417.466 | 41417.6167 | 1 | 214 | 214 | 1 | 0.00065909 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 1 | 0.00065909 | 3.0798e-06
134830 | 41417.4472 | 41417.4521 | 1 | 4 | 4 | 1 | 1.2319e-05 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 1 | 1.2319e-05 | 3.0798e-06
134832 | 41417.7319 | 41417.7486 | 9 | 21 | 189 | 9 | 0.00058209 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 9 | 0.00058209 | 2.7719e-05
134833 | 41417.8333 | 41418.0312 | 2 | 282 | 564 | 2 | 0.001737 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 2 | 0.001737 | 6.1597e-06
134834 | 41417.3625 | 41418.6083 | 14 | 1791 | 7593.2809 | 4.2397 | 0.023386 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | C | 4.2397 | 0.023386 | 4.3118e-05
134839 | 41418.3646 | 41418.6271 | 41 | 375 | 15375 | 41 | 0.047353 | 0.00012627 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | B | 41 | 0.047353 | 0.00012627
134843 | 41418.375 | 41418.6521 | 74 | 396 | 29304 | 74 | 0.090252 | 0.00022791 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | B | 74 | 0.090252 | 0.00022791
134844 | 41418.375 | 41418.6319 | 13 | 367 | 4771 | 13 | 0.014694 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | B | 13 | 0.014694 | 4.0038e-05
134845 | 41417.3854 | 41417.625 | 20 | 342 | 6840 | 20 | 0.021066 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 20 | 0.021066 | 6.1597e-05
134846 | 41418.625 | 41418.7396 | 1 | 162 | 162 | 1 | 0.00049893 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | C | 1 | 0.00049893 | 3.0798e-06
134848 | 41418.9076 | 41418.9243 | 903 | 21 | 15771 | 751 | 0.048572 | 0.0027811 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | C | 751 | 0.048572 | 0.0027811
134849 | 41418.8438 | 41418.875 | 15 | 42 | 630 | 15 | 0.0019403 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | C | 15 | 0.0019403 | 4.6198e-05
134851 | 41418.866 | 41419.2215 | 1314 | 509 | 90890.3008 | 178.5664 | 0.27993 | 0.0040469 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-24 | 2014 | 2014 | 2013-05-24 | C | 178.5664 | 0.27993 | 0.0040469
134852 | 41419.3889 | 41419.4375 | 30 | 67 | 2010 | 30 | 0.0061905 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-25 | 2014 | 2014 | 2013-05-25 | C | 30 | 0.0061905 | 9.2395e-05
134854 | 41419.4104 | 41419.4361 | 288 | 34 | 9792 | 288 | 0.030158 | 0.00088699 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-25 | 2014 | 2014 | 2013-05-25 | C | 288 | 0.030158 | 0.00088699
134857 | 41419.6299 | 41419.7201 | 16 | 127 | 2032 | 16 | 0.0062582 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-25 | 2014 | 2014 | 2013-05-25 | C | 16 | 0.0062582 | 4.9277e-05
134860 | 41419.7299 | 41419.7451 | 156 | 19 | 2964 | 156 | 0.0091287 | 0.00048046 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-25 | 2014 | 2014 | 2013-05-25 | C | 156 | 0.0091287 | 0.00048046
134861 | 41419.7299 | 41419.7556 | 156 | 34 | 5304 | 156 | 0.016335 | 0.00048046 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-25 | 2014 | 2014 | 2013-05-25 | C | 156 | 0.016335 | 0.00048046
134862 | 41420.1701 | 41420.2826 | 679 | 159 | 33395.8889 | 210.037 | 0.10285 | 0.0020912 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 210.037 | 0.10285 | 0.0020912
134863 | 41420.4444 | 41420.4847 | 1069 | 55 | 31337.6724 | 569.7759 | 0.096515 | 0.0032924 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 569.7759 | 0.096515 | 0.0032924
134865 | 41420.5486 | 41420.5799 | 8 | 42 | 336 | 8 | 0.0010348 | 2.4639e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 8 | 0.0010348 | 2.4639e-05
134866 | 41420.6424 | 41420.7049 | 1114 | 87 | 63954.6667 | 735.1111 | 0.19697 | 0.0034309 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 735.1111 | 0.19697 | 0.0034309
134867 | 41420.5938 | 41420.8382 | 873 | 349 | 79379.6534 | 227.4489 | 0.24448 | 0.0026887 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 227.4489 | 0.24448 | 0.0026887
134868 | 41420.6438 | 41421.7292 | 69 | 1560 | 8716.238 | 5.5873 | 0.026845 | 0.00021251 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 5.5873 | 0.026845 | 0.00021251
134869 | 41420.4646 | 41420.5819 | 257 | 166 | 25765.3609 | 155.213 | 0.079353 | 0.00079152 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 155.213 | 0.079353 | 0.00079152
134872 | 41420.4042 | 41420.5285 | 51 | 176 | 5729.3408 | 32.5531 | 0.017645 | 0.00015707 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 32.5531 | 0.017645 | 0.00015707
134873 | 41421.0375 | 41421.0569 | 13 | 25 | 325 | 13 | 0.0010009 | 4.0038e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-27 | 2014 | 2014 | 2013-05-27 | C | 13 | 0.0010009 | 4.0038e-05
134874 | 41420.7521 | 41420.8285 | 1 | 107 | 107 | 1 | 0.00032954 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 1 | 0.00032954 | 3.0798e-06
134875 | 41420.909 | 41421.5056 | 22 | 856 | 17171.8184 | 20.0605 | 0.052886 | 6.7757e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 20.0605 | 0.052886 | 6.7757e-05
134876 | 41411.4826 | 41411.4917 | 56 | 10 | 560 | 56 | 0.0017247 | 0.00017247 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-17 | 2014 | 2014 | 2013-05-17 | C | 56 | 0.0017247 | 0.00017247
134878 | 41420.8938 | 41421.5486 | 5 | 940 | 4700 | 5 | 0.014475 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | C | 5 | 0.014475 | 1.5399e-05
134879 | 41421.3542 | 41421.6215 | 10 | 382 | 3820 | 10 | 0.011765 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-27 | 2014 | 2014 | 2013-05-27 | B | 10 | 0.011765 | 3.0798e-05
134880 | 41421.4097 | 41421.534 | 15 | 176 | 2640 | 15 | 0.0081308 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-27 | 2014 | 2014 | 2013-05-27 | C | 15 | 0.0081308 | 4.6198e-05
134881 | 41421.4326 | 41421.5306 | 363 | 138 | 50094 | 363 | 0.15428 | 0.001118 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-27 | 2014 | 2014 | 2013-05-27 | C | 363 | 0.15428 | 0.001118
134884 | 41420.3972 | 41420.5625 | 1 | 235 | 235 | 1 | 0.00072376 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-26 | 2014 | 2014 | 2013-05-26 | B | 1 | 0.00072376 | 3.0798e-06
134887 | 41422.3056 | 41422.3514 | 14 | 63 | 882 | 14 | 0.0027164 | 4.3118e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 14 | 0.0027164 | 4.3118e-05
134888 | 41414.3778 | 41414.5993 | 81 | 316 | 25596 | 81 | 0.078832 | 0.00024947 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-20 | 2014 | 2014 | 2013-05-20 | B | 81 | 0.078832 | 0.00024947
134890 | 41417.3771 | 41417.5375 | 1 | 228 | 228 | 1 | 0.0007022 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-23 | 2014 | 2014 | 2013-05-23 | B | 1 | 0.0007022 | 3.0798e-06
134891 | 41422.4896 | 41422.5028 | 287 | 16 | 4592 | 287 | 0.014143 | 0.00088391 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 287 | 0.014143 | 0.00088391
134893 | 41422.4062 | 41422.625 | 2 | 312 | 624 | 2 | 0.0019218 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | B | 2 | 0.0019218 | 6.1597e-06
134894 | 41422.375 | 41422.5757 | 8 | 286 | 2288 | 8 | 0.0070467 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | B | 8 | 0.0070467 | 2.4639e-05
134895 | 41422.375 | 41422.6937 | 388 | 456 | 166485.6993 | 365.1002 | 0.51275 | 0.001195 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | B | 365.1002 | 0.51275 | 0.001195
134897 | 41422.7736 | 41422.8438 | 1034 | 98 | 94664.1188 | 965.9604 | 0.29155 | 0.0031846 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 965.9604 | 0.29155 | 0.0031846
134898 | 41422.7736 | 41422.866 | 418 | 130 | 54340 | 418 | 0.16736 | 0.0012874 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 418 | 0.16736 | 0.0012874
134899 | 41422.7736 | 41422.8785 | 372 | 148 | 55056 | 372 | 0.16956 | 0.0011457 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 372 | 0.16956 | 0.0011457
134901 | 41423.0549 | 41423.0861 | 2154 | 42 | 61560.8 | 1465.7333 | 0.1896 | 0.006634 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 1465.7333 | 0.1896 | 0.006634
134902 | 41422.7875 | 41422.9931 | 1 | 293 | 293 | 1 | 0.00090239 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 1 | 0.00090239 | 3.0798e-06
134903 | 41422.5549 | 41422.7958 | 288 | 344 | 26546.4899 | 77.17 | 0.081759 | 0.00088699 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-28 | 2014 | 2014 | 2013-05-28 | C | 77.17 | 0.081759 | 0.00088699
134906 | 41423.4306 | 41423.4479 | 28 | 22 | 616 | 28 | 0.0018972 | 8.6236e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 28 | 0.0018972 | 8.6236e-05
134908 | 41421.75 | 41423.5486 | 12 | 2587 | 31044 | 12 | 0.095611 | 3.6958e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-27 | 2014 | 2014 | 2013-05-27 | C | 12 | 0.095611 | 3.6958e-05
134910 | 41423.5465 | 41423.6285 | 344 | 115 | 25569.9576 | 222.3475 | 0.078751 | 0.0010595 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 222.3475 | 0.078751 | 0.0010595
134912 | 41423.375 | 41423.5944 | 43 | 313 | 13459 | 43 | 0.041452 | 0.00013243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | B | 43 | 0.041452 | 0.00013243
134913 | 41423.509 | 41423.5486 | 33 | 54 | 1782 | 33 | 0.0054883 | 0.00010163 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 33 | 0.0054883 | 0.00010163
134914 | 41423.3347 | 41423.3812 | 1761 | 64 | 94551.8806 | 1477.3731 | 0.2912 | 0.0054236 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 1477.3731 | 0.2912 | 0.0054236
134915 | 41423.3972 | 41423.4625 | 13 | 91 | 1183 | 13 | 0.0036435 | 4.0038e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 13 | 0.0036435 | 4.0038e-05
134916 | 41424.0312 | 41424.1007 | 743 | 97 | 38137.49 | 393.17 | 0.11746 | 0.0022883 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | C | 393.17 | 0.11746 | 0.0022883
134917 | 41423.7465 | 41423.7604 | 108 | 17 | 1836 | 108 | 0.0056546 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 108 | 0.0056546 | 0.00033262
134919 | 41423.3389 | 41423.5014 | 27 | 231 | 6237 | 27 | 0.019209 | 8.3156e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-29 | 2014 | 2014 | 2013-05-29 | C | 27 | 0.019209 | 8.3156e-05
134920 | 41424.1326 | 41424.3444 | 228 | 302 | 26544.3148 | 87.8951 | 0.081752 | 0.0007022 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | C | 87.8951 | 0.081752 | 0.0007022
134921 | 41424.4208 | 41424.4319 | 1 | 13 | 13 | 1 | 4.0038e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | C | 1 | 4.0038e-05 | 3.0798e-06
134922 | 41424.3854 | 41424.591 | 40 | 293 | 11720 | 40 | 0.036096 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | B | 40 | 0.036096 | 0.00012319
134925 | 41424.3944 | 41424.6375 | 13 | 347 | 4511 | 13 | 0.013893 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | B | 13 | 0.013893 | 4.0038e-05
134927 | 41424.3674 | 41424.6458 | 45 | 398 | 17910 | 45 | 0.05516 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | B | 45 | 0.05516 | 0.00013859
134930 | 41424.4542 | 41424.5271 | 55 | 102 | 5610 | 55 | 0.017278 | 0.00016939 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | C | 55 | 0.017278 | 0.00016939
134931 | 41424.4965 | 41424.5167 | 22 | 26 | 572 | 22 | 0.0017617 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-30 | 2014 | 2014 | 2013-05-30 | C | 22 | 0.0017617 | 6.7757e-05
134934 | 41425.0632 | 41425.1104 | 167 | 65 | 8069.5588 | 124.1471 | 0.024853 | 0.00051433 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 124.1471 | 0.024853 | 0.00051433
134935 | 41425.0875 | 41425.1514 | 710 | 89 | 44977.8913 | 505.3696 | 0.13852 | 0.0021867 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 505.3696 | 0.13852 | 0.0021867
134937 | 41425.0729 | 41425.1319 | 1305 | 82 | 70057.9059 | 854.3647 | 0.21577 | 0.0040192 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 854.3647 | 0.21577 | 0.0040192
134938 | 41425.0729 | 41425.125 | 74 | 72 | 5328 | 74 | 0.016409 | 0.00022791 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 74 | 0.016409 | 0.00022791
134941 | 41425.4375 | 41425.5104 | 4 | 102 | 408 | 4 | 0.0012566 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 4 | 0.0012566 | 1.2319e-05
134943 | 41425.375 | 41425.5451 | 3 | 242 | 726 | 3 | 0.002236 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | B | 3 | 0.002236 | 9.2395e-06
134946 | 41425.4028 | 41425.4826 | 4 | 112 | 448 | 4 | 0.0013798 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 4 | 0.0013798 | 1.2319e-05
134948 | 41425.5 | 41425.6111 | 7 | 157 | 1099 | 7 | 0.0033847 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 7 | 0.0033847 | 2.1559e-05
134949 | 41425.5556 | 41425.5972 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 4 | 0.0007022 | 1.2319e-05
134950 | 41425.5292 | 41425.6035 | 94 | 104 | 9776 | 94 | 0.030109 | 0.00028951 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 94 | 0.030109 | 0.00028951
134956 | 41425.8597 | 41425.9583 | 417 | 139 | 56496.6479 | 406.4507 | 0.174 | 0.0012843 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 406.4507 | 0.174 | 0.0012843
134957 | 41425.8597 | 41425.9014 | 387 | 57 | 22059 | 387 | 0.067938 | 0.0011919 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 387 | 0.067938 | 0.0011919
134958 | 41425.8597 | 41425.891 | 264 | 42 | 11088 | 264 | 0.034149 | 0.00081308 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-05-31 | 2014 | 2014 | 2013-05-31 | C | 264 | 0.034149 | 0.00081308
134959 | 41426.2771 | 41426.5625 | 578 | 408 | 28008.0584 | 68.6472 | 0.08626 | 0.0017801 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-01 | 2014 | 2014 | 2013-06-01 | C | 68.6472 | 0.08626 | 0.0017801
134960 | 41426.5764 | 41426.7014 | 160 | 177 | 28320 | 160 | 0.087221 | 0.00049277 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-01 | 2014 | 2014 | 2013-06-01 | C | 160 | 0.087221 | 0.00049277
134963 | 41426.3792 | 41426.4583 | 214 | 111 | 23754 | 214 | 0.073159 | 0.00065909 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-01 | 2014 | 2014 | 2013-06-01 | C | 214 | 0.073159 | 0.00065909
134964 | 41426.9167 | 41426.9229 | 7 | 6 | 42 | 7 | 0.00012935 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-01 | 2014 | 2014 | 2013-06-01 | C | 7 | 0.00012935 | 2.1559e-05
134965 | 41427.7778 | 41427.7986 | 47 | 27 | 1269 | 47 | 0.0039083 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-02 | 2014 | 2014 | 2013-06-02 | C | 47 | 0.0039083 | 0.00014475
134966 | 41427.7556 | 41427.8056 | 633 | 69 | 37283.9583 | 540.3472 | 0.11483 | 0.0019495 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-02 | 2014 | 2014 | 2013-06-02 | C | 540.3472 | 0.11483 | 0.0019495
134969 | 41429.3958 | 41429.434 | 50 | 52 | 2600 | 50 | 0.0080076 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 50 | 0.0080076 | 0.00015399
134971 | 41429.4167 | 41429.5319 | 24 | 163 | 3912 | 24 | 0.012048 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 24 | 0.012048 | 7.3916e-05
134972 | 41429.3708 | 41429.5556 | 671 | 263 | 35096.6579 | 133.4474 | 0.10809 | 0.0020666 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 133.4474 | 0.10809 | 0.0020666
134973 | 41429.3806 | 41429.6368 | 14 | 366 | 5124 | 14 | 0.015781 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 14 | 0.015781 | 4.3118e-05
134974 | 41429.3819 | 41429.6458 | 279 | 377 | 105183 | 279 | 0.32395 | 0.00085928 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 279 | 0.32395 | 0.00085928
134975 | 41429.6229 | 41429.8257 | 360 | 289 | 14865.6849 | 51.4384 | 0.045784 | 0.0011087 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 51.4384 | 0.045784 | 0.0011087
134977 | 41429.3646 | 41429.6667 | 91 | 432 | 39312 | 91 | 0.12107 | 0.00028027 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 91 | 0.12107 | 0.00028027
134978 | 41429.6562 | 41429.7076 | 279 | 71 | 9761.5405 | 137.4865 | 0.030064 | 0.00085928 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 137.4865 | 0.030064 | 0.00085928
134979 | 41429.375 | 41429.625 | 75 | 357 | 26775 | 75 | 0.082463 | 0.00023099 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 75 | 0.082463 | 0.00023099
134980 | 41429.375 | 41429.5625 | 1 | 267 | 267 | 1 | 0.00082232 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 1 | 0.00082232 | 3.0798e-06
134981 | 41429.3889 | 41429.5049 | 2 | 164 | 328 | 2 | 0.0010102 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 2 | 0.0010102 | 6.1597e-06
134982 | 41429.6083 | 41429.6319 | 19 | 31 | 589 | 19 | 0.001814 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 19 | 0.001814 | 5.8517e-05
134984 | 41429.8542 | 41429.9764 | 999 | 173 | 51821.3636 | 299.5455 | 0.1596 | 0.0030768 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 299.5455 | 0.1596 | 0.0030768
134985 | 41430.8931 | 41431.4535 | 365 | 804 | 31568.2082 | 39.2639 | 0.097225 | 0.0011241 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | C | 39.2639 | 0.097225 | 0.0011241
134986 | 41429.6361 | 41429.7986 | 3 | 231 | 693 | 3 | 0.0021343 | 9.2395e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 3 | 0.0021343 | 9.2395e-06
134987 | 41429.534 | 41429.6889 | 577 | 220 | 114181.9731 | 519.009 | 0.35166 | 0.0017771 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | C | 519.009 | 0.35166 | 0.0017771
134988 | 41430.3889 | 41430.4118 | 27 | 30 | 810 | 27 | 0.0024947 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | C | 27 | 0.0024947 | 8.3156e-05
134989 | 41430.3958 | 41430.4931 | 3 | 137 | 411 | 3 | 0.0012658 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 3 | 0.0012658 | 9.2395e-06
134990 | 41430.4688 | 41430.5556 | 1 | 122 | 122 | 1 | 0.00037574 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 1 | 0.00037574 | 3.0798e-06
134992 | 41430.4167 | 41430.5833 | 76 | 237 | 18012 | 76 | 0.055474 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 76 | 0.055474 | 0.00023407
134993 | 41430.375 | 41430.6 | 9 | 321 | 2889 | 9 | 0.0088977 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 9 | 0.0088977 | 2.7719e-05
134994 | 41430.3938 | 41430.6014 | 25 | 296 | 7400 | 25 | 0.022791 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 25 | 0.022791 | 7.6996e-05
134996 | 41430.375 | 41430.5868 | 63 | 302 | 19026 | 63 | 0.058597 | 0.00019403 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 63 | 0.058597 | 0.00019403
134997 | 41430.4056 | 41430.55 | 76 | 205 | 15580 | 76 | 0.047984 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 76 | 0.047984 | 0.00023407
134998 | 41430.7722 | 41430.8569 | 178 | 119 | 21182 | 178 | 0.065237 | 0.00054821 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | C | 178 | 0.065237 | 0.00054821
134999 | 41430.7965 | 41430.8424 | 1180 | 63 | 46001.4545 | 730.1818 | 0.14168 | 0.0036342 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | C | 730.1818 | 0.14168 | 0.0036342
135001 | 41430.7368 | 41430.7681 | 360 | 42 | 15120 | 360 | 0.046567 | 0.0011087 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | C | 360 | 0.046567 | 0.0011087
135002 | 41431.4167 | 41431.4674 | 90 | 70 | 6300 | 90 | 0.019403 | 0.00027719 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 90 | 0.019403 | 0.00027719
135003 | 41431.4167 | 41431.4861 | 4 | 97 | 388 | 4 | 0.001195 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 4 | 0.001195 | 1.2319e-05
135004 | 41431.3931 | 41431.5417 | 3 | 211 | 633 | 3 | 0.0019495 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 3 | 0.0019495 | 9.2395e-06
135006 | 41431.5118 | 41431.5167 | 8 | 4 | 32 | 8 | 9.8555e-05 | 2.4639e-05 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | C | 8 | 9.8555e-05 | 2.4639e-05
135008 | 41430.3646 | 41430.575 | 31 | 300 | 9300 | 31 | 0.028643 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 31 | 0.028643 | 9.5475e-05
135009 | 41431.375 | 41431.6236 | 75 | 355 | 26625 | 75 | 0.082001 | 0.00023099 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 75 | 0.082001 | 0.00023099
135010 | 41431.4931 | 41431.6111 | 2 | 167 | 334 | 2 | 0.0010287 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 2 | 0.0010287 | 6.1597e-06
135011 | 41431.3646 | 41431.566 | 76 | 287 | 21812 | 76 | 0.067178 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 76 | 0.067178 | 0.00023407
135012 | 41431.375 | 41431.6389 | 67 | 377 | 25259 | 67 | 0.077794 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 67 | 0.077794 | 0.00020635
135013 | 41431.3889 | 41431.6597 | 28 | 387 | 10836 | 28 | 0.033373 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 28 | 0.033373 | 8.6236e-05
135014 | 41431.375 | 41431.7361 | 2 | 517 | 1034 | 2 | 0.0031846 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 2 | 0.0031846 | 6.1597e-06
135015 | 41431.4111 | 41431.6125 | 2 | 287 | 574 | 2 | 0.0017678 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 2 | 0.0017678 | 6.1597e-06
135016 | 41431.3854 | 41431.5889 | 40 | 290 | 11600 | 40 | 0.035726 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 40 | 0.035726 | 0.00012319
135021 | 41432.375 | 41432.3993 | 4 | 32 | 128 | 4 | 0.00039422 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-07 | 2014 | 2014 | 2013-06-07 | B | 4 | 0.00039422 | 1.2319e-05
135022 | 41432.3958 | 41432.4257 | 17 | 40 | 680 | 17 | 0.0020943 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-07 | 2014 | 2014 | 2013-06-07 | B | 17 | 0.0020943 | 5.2357e-05
135024 | 41430.3819 | 41430.616 | 19 | 334 | 6346 | 19 | 0.019545 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-05 | 2014 | 2014 | 2013-06-05 | B | 19 | 0.019545 | 5.8517e-05
135026 | 41432.3819 | 41432.5222 | 2 | 199 | 398 | 2 | 0.0012258 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-07 | 2014 | 2014 | 2013-06-07 | B | 2 | 0.0012258 | 6.1597e-06
135027 | 41432.3646 | 41432.5 | 20 | 192 | 3840 | 20 | 0.011827 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-07 | 2014 | 2014 | 2013-06-07 | B | 20 | 0.011827 | 6.1597e-05
135029 | 41433.3194 | 41433.3854 | 369 | 92 | 20464.6737 | 222.4421 | 0.063028 | 0.0011365 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-08 | 2014 | 2014 | 2013-06-08 | C | 222.4421 | 0.063028 | 0.0011365
135030 | 41395.375 | 41395.625 | 121 | 357 | 43197 | 121 | 0.13304 | 0.00037266 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-05-01 | 2014 | 2014 | 2013-05-01 | B | 121 | 0.13304 | 0.00037266
135031 | 41433.3125 | 41433.466 | 2 | 218 | 436 | 2 | 0.0013428 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-08 | 2014 | 2014 | 2013-06-08 | B | 2 | 0.0013428 | 6.1597e-06
135034 | 41433.375 | 41433.5576 | 1 | 260 | 260 | 1 | 0.00080076 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-08 | 2014 | 2014 | 2013-06-08 | B | 1 | 0.00080076 | 3.0798e-06
135037 | 41433.8778 | 41433.941 | 480 | 88 | 40400.7033 | 459.0989 | 0.12443 | 0.0014783 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-08 | 2014 | 2014 | 2013-06-08 | C | 459.0989 | 0.12443 | 0.0014783
135043 | 41434.559 | 41434.5764 | 30 | 22 | 660 | 30 | 0.0020327 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-09 | 2014 | 2014 | 2013-06-09 | C | 30 | 0.0020327 | 9.2395e-05
135044 | 41435.4993 | 41435.5285 | 2414 | 39 | 94146 | 2414 | 0.28995 | 0.0074347 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | C | 2414 | 0.28995 | 0.0074347
135045 | 41435.425 | 41435.5729 | 31 | 210 | 6510 | 31 | 0.02005 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | B | 31 | 0.02005 | 9.5475e-05
135046 | 41435.375 | 41435.625 | 8 | 357 | 2856 | 8 | 0.008796 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | B | 8 | 0.008796 | 2.4639e-05
135048 | 41435.4035 | 41435.666 | 25 | 375 | 9375 | 25 | 0.028874 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | B | 25 | 0.028874 | 7.6996e-05
135050 | 41435.6021 | 41435.6181 | 1228 | 20 | 24560 | 1228 | 0.075641 | 0.003782 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | C | 1228 | 0.075641 | 0.003782
135051 | 41435.809 | 41435.8826 | 84 | 103 | 8652 | 84 | 0.026647 | 0.00025871 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | C | 84 | 0.026647 | 0.00025871
135052 | 41435.8896 | 41435.9007 | 71 | 13 | 923 | 71 | 0.0028427 | 0.00021867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | C | 71 | 0.0028427 | 0.00021867
135054 | 41435.8993 | 41436.4167 | 262 | 742 | 45994.0403 | 61.9866 | 0.14165 | 0.00080692 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | C | 61.9866 | 0.14165 | 0.00080692
135055 | 41436.125 | 41436.159 | 1 | 46 | 46 | 1 | 0.00014167 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 1 | 0.00014167 | 3.0798e-06
135056 | 41435.3958 | 41435.5208 | 40 | 177 | 7080 | 40 | 0.021805 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-10 | 2014 | 2014 | 2013-06-10 | B | 40 | 0.021805 | 0.00012319
135058 | 41436.5347 | 41436.6076 | 3 | 102 | 306 | 3 | 0.00094243 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 3 | 0.00094243 | 9.2395e-06
135062 | 41436.375 | 41436.6285 | 55 | 362 | 19910 | 55 | 0.06132 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 55 | 0.06132 | 0.00016939
135063 | 41436.534 | 41436.6681 | 93 | 190 | 10493.3161 | 55.228 | 0.032318 | 0.00028643 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 55.228 | 0.032318 | 0.00028643
135064 | 41436.375 | 41436.6979 | 44 | 462 | 20328 | 44 | 0.062607 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 44 | 0.062607 | 0.00013551
135065 | 41436.534 | 41436.6681 | 93 | 190 | 10493.3161 | 55.228 | 0.032318 | 0.00028643 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 55.228 | 0.032318 | 0.00028643
135066 | 41436.375 | 41436.625 | 8 | 357 | 2856 | 8 | 0.008796 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 8 | 0.008796 | 2.4639e-05
135067 | 41436.3542 | 41436.5417 | 86 | 267 | 22962 | 86 | 0.070719 | 0.00026487 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 86 | 0.070719 | 0.00026487
135069 | 41436.75 | 41436.7799 | 74 | 40 | 2960 | 74 | 0.0091163 | 0.00022791 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 74 | 0.0091163 | 0.00022791
135071 | 41436.5 | 41436.6424 | 263 | 202 | 50066.439 | 247.8537 | 0.1542 | 0.00081 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 247.8537 | 0.1542 | 0.00081
135073 | 41436.6944 | 41436.7375 | 181 | 59 | 10679 | 181 | 0.03289 | 0.00055745 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 181 | 0.03289 | 0.00055745
135074 | 41436.6944 | 41436.9 | 115 | 293 | 22545.1622 | 76.9459 | 0.069436 | 0.00035418 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 76.9459 | 0.069436 | 0.00035418
135075 | 41437.0153 | 41437.0708 | 825 | 77 | 35489.3 | 460.9 | 0.1093 | 0.0025409 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | C | 460.9 | 0.1093 | 0.0025409
135081 | 41437.375 | 41437.625 | 62 | 357 | 22134 | 62 | 0.068169 | 0.00019095 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 62 | 0.068169 | 0.00019095
135084 | 41436.3861 | 41436.6319 | 28 | 351 | 9828 | 28 | 0.030269 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | B | 28 | 0.030269 | 8.6236e-05
135085 | 41437.3833 | 41437.6257 | 9 | 346 | 3114 | 9 | 0.0095906 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 9 | 0.0095906 | 2.7719e-05
135086 | 41437.4167 | 41437.6 | 35 | 261 | 9135 | 35 | 0.028134 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 35 | 0.028134 | 0.00010779
135087 | 41437.4132 | 41437.6194 | 52 | 294 | 15288 | 52 | 0.047085 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 52 | 0.047085 | 0.00016015
135088 | 41437.4056 | 41437.5743 | 26 | 240 | 6240 | 26 | 0.019218 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 26 | 0.019218 | 8.0076e-05
135089 | 41436.75 | 41436.8021 | 300 | 72 | 21600 | 300 | 0.066525 | 0.00092395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-11 | 2014 | 2014 | 2013-06-11 | C | 300 | 0.066525 | 0.00092395
135092 | 41431.0667 | 41431.2257 | 160 | 226 | 36160 | 160 | 0.11137 | 0.00049277 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-06 | 2014 | 2014 | 2013-06-06 | B | 160 | 0.11137 | 0.00049277
135093 | 41429.3854 | 41429.5646 | 6 | 255 | 1530 | 6 | 0.0047122 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-04 | 2014 | 2014 | 2013-06-04 | B | 6 | 0.0047122 | 1.8479e-05
135094 | 41438.4097 | 41438.4479 | 3 | 52 | 156 | 3 | 0.00048046 | 9.2395e-06 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | C | 3 | 0.00048046 | 9.2395e-06
135095 | 41438.391 | 41438.4722 | 8 | 114 | 912 | 8 | 0.0028088 | 2.4639e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | C | 8 | 0.0028088 | 2.4639e-05
135096 | 41438.3854 | 41438.5625 | 18 | 252 | 4536 | 18 | 0.01397 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | B | 18 | 0.01397 | 5.5437e-05
135100 | 41438.375 | 41438.625 | 46 | 357 | 16422 | 46 | 0.050577 | 0.00014167 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | B | 46 | 0.050577 | 0.00014167
135101 | 41438.4167 | 41438.5708 | 44 | 219 | 9636 | 44 | 0.029677 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | B | 44 | 0.029677 | 0.00013551
135102 | 41438.4306 | 41438.55 | 4 | 169 | 676 | 4 | 0.002082 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | C | 4 | 0.002082 | 1.2319e-05
135103 | 41438.4604 | 41438.5 | 825 | 54 | 40402.4211 | 748.193 | 0.12443 | 0.0025409 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | C | 748.193 | 0.12443 | 0.0025409
135104 | 41438.3875 | 41438.5938 | 67 | 294 | 19698 | 67 | 0.060667 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | B | 67 | 0.060667 | 0.00020635
135107 | 41438.8125 | 41438.9444 | 2 | 187 | 374 | 2 | 0.0011519 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-13 | 2014 | 2014 | 2013-06-13 | C | 2 | 0.0011519 | 6.1597e-06
135108 | 41439.4444 | 41439.5069 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-14 | 2014 | 2014 | 2013-06-14 | C | 3 | 0.00080384 | 9.2395e-06
135109 | 41439.1806 | 41439.5563 | 5 | 538 | 2690 | 5 | 0.0082848 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-14 | 2014 | 2014 | 2013-06-14 | C | 5 | 0.0082848 | 1.5399e-05
135110 | 41439.375 | 41439.6083 | 9 | 333 | 2997 | 9 | 0.0092303 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-14 | 2014 | 2014 | 2013-06-14 | B | 9 | 0.0092303 | 2.7719e-05
135112 | 41439.8465 | 41439.9347 | 783 | 124 | 55028.6614 | 443.7795 | 0.16948 | 0.0024115 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-14 | 2014 | 2014 | 2013-06-14 | C | 443.7795 | 0.16948 | 0.0024115
135117 | 41440.375 | 41440.4965 | 55 | 172 | 9460 | 55 | 0.029135 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-15 | 2014 | 2014 | 2013-06-15 | B | 55 | 0.029135 | 0.00016939
135121 | 41434.4167 | 41434.5833 | 33 | 237 | 7821 | 33 | 0.024087 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-09 | 2014 | 2014 | 2013-06-09 | B | 33 | 0.024087 | 0.00010163
135122 | 41441.5285 | 41441.559 | 595 | 41 | 22627.3409 | 551.8864 | 0.069689 | 0.0018325 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 551.8864 | 0.069689 | 0.0018325
135123 | 41441.4861 | 41441.5868 | 474 | 142 | 30249.9172 | 213.0276 | 0.093165 | 0.0014598 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 213.0276 | 0.093165 | 0.0014598
135124 | 41441.4729 | 41441.6687 | 193 | 279 | 14197.3404 | 50.8865 | 0.043726 | 0.00059441 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 50.8865 | 0.043726 | 0.00059441
135125 | 41441.559 | 41441.6618 | 116 | 145 | 16820 | 116 | 0.051803 | 0.00035726 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 116 | 0.051803 | 0.00035726
135126 | 41441.7625 | 41441.8118 | 272 | 68 | 18496 | 272 | 0.056965 | 0.00083772 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 272 | 0.056965 | 0.00083772
135127 | 41441.8514 | 41441.8764 | 138 | 33 | 4554 | 138 | 0.014026 | 0.00042502 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 138 | 0.014026 | 0.00042502
135128 | 41441.7604 | 41441.7944 | 478 | 46 | 21988 | 478 | 0.06772 | 0.0014722 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 478 | 0.06772 | 0.0014722
135129 | 41441.8604 | 41441.8757 | 85 | 19 | 1615 | 85 | 0.0049739 | 0.00026179 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 85 | 0.0049739 | 0.00026179
135130 | 41442.5312 | 41442.6215 | 48 | 127 | 6096 | 48 | 0.018775 | 0.00014783 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 48 | 0.018775 | 0.00014783
135131 | 41442.5028 | 41442.6667 | 208 | 233 | 15996.0424 | 68.6525 | 0.049265 | 0.00064061 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 68.6525 | 0.049265 | 0.00064061
135139 | 41442.375 | 41442.6333 | 100 | 369 | 36900 | 100 | 0.11365 | 0.00030798 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | B | 100 | 0.11365 | 0.00030798
135141 | 41442.4229 | 41442.5312 | 4 | 153 | 612 | 4 | 0.0018849 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | B | 4 | 0.0018849 | 1.2319e-05
135146 | 41442.1368 | 41442.3028 | 195 | 236 | 33866.4937 | 143.5021 | 0.1043 | 0.00060057 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 143.5021 | 0.1043 | 0.00060057
135147 | 41442.4958 | 41442.8868 | 204 | 560 | 15703.8721 | 28.0426 | 0.048365 | 0.00062829 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 28.0426 | 0.048365 | 0.00062829
135149 | 41442.6875 | 41442.6993 | 3 | 14 | 42 | 3 | 0.00012935 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 3 | 0.00012935 | 9.2395e-06
135150 | 41442.3958 | 41442.4444 | 3 | 67 | 201 | 3 | 0.00061905 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 3 | 0.00061905 | 9.2395e-06
135151 | 41442.7257 | 41442.7375 | 7 | 14 | 98 | 7 | 0.00030182 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 7 | 0.00030182 | 2.1559e-05
135153 | 41442.3542 | 41442.6736 | 8 | 457 | 3656 | 8 | 0.01126 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | B | 8 | 0.01126 | 2.4639e-05
135156 | 41441.7688 | 41442.9688 | 95 | 1725 | 38597.8733 | 22.3756 | 0.11888 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | C | 22.3756 | 0.11888 | 0.00029258
135158 | 41443.375 | 41443.4278 | 2 | 73 | 146 | 2 | 0.00044966 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | B | 2 | 0.00044966 | 6.1597e-06
135159 | 41443.3542 | 41443.4431 | 8 | 125 | 1000 | 8 | 0.0030798 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | B | 8 | 0.0030798 | 2.4639e-05
135161 | 41442.7972 | 41443.5146 | 3 | 1030 | 3090 | 3 | 0.0095167 | 9.2395e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 3 | 0.0095167 | 9.2395e-06
135164 | 41443.5715 | 41443.6354 | 4 | 89 | 356 | 4 | 0.0010964 | 1.2319e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | C | 4 | 0.0010964 | 1.2319e-05
135165 | 41442.4958 | 41443.5625 | 3 | 1533 | 4599 | 3 | 0.014164 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-06-17 | 2014 | 2014 | 2013-06-17 | C | 3 | 0.014164 | 9.2395e-06
135169 | 41443.375 | 41443.6368 | 159 | 374 | 59466 | 159 | 0.18315 | 0.00048969 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | B | 159 | 0.18315 | 0.00048969
135170 | 41443.8243 | 41443.8368 | 1328 | 15 | 18895.8333 | 1259.7222 | 0.058196 | 0.00409 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | C | 1259.7222 | 0.058196 | 0.00409
135174 | 41444.4861 | 41444.5229 | 4 | 50 | 200 | 4 | 0.00061597 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 4 | 0.00061597 | 1.2319e-05
135176 | 41444.375 | 41444.5896 | 67 | 306 | 20502 | 67 | 0.063143 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | B | 67 | 0.063143 | 0.00020635
135177 | 41443.3542 | 41443.625 | 6 | 387 | 2322 | 6 | 0.0071514 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | B | 6 | 0.0071514 | 1.8479e-05
135179 | 41444.375 | 41444.5861 | 9 | 301 | 2709 | 9 | 0.0083433 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | B | 9 | 0.0083433 | 2.7719e-05
135180 | 41444.6597 | 41444.6646 | 95 | 4 | 380 | 95 | 0.0011703 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 95 | 0.0011703 | 0.00029258
135181 | 41444.375 | 41444.6729 | 3 | 426 | 1278 | 3 | 0.003936 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | B | 3 | 0.003936 | 9.2395e-06
135185 | 41444.684 | 41444.7562 | 208 | 101 | 16720.3558 | 165.5481 | 0.051496 | 0.00064061 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 165.5481 | 0.051496 | 0.00064061
135186 | 41443.4667 | 41443.5076 | 31 | 56 | 1736 | 31 | 0.0053466 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | C | 31 | 0.0053466 | 9.5475e-05
135187 | 41443.3549 | 41443.3875 | 1 | 44 | 44 | 1 | 0.00013551 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | C | 1 | 0.00013551 | 3.0798e-06
135188 | 41444.7569 | 41444.8861 | 47 | 183 | 8601 | 47 | 0.02649 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 47 | 0.02649 | 0.00014475
135189 | 41444.6924 | 41444.8264 | 269 | 190 | 24898.8601 | 131.0466 | 0.076685 | 0.00082848 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 131.0466 | 0.076685 | 0.00082848
135190 | 41443.5257 | 41443.6083 | 86 | 116 | 6197.7143 | 53.4286 | 0.019088 | 0.00026487 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-18 | 2014 | 2014 | 2013-06-18 | C | 53.4286 | 0.019088 | 0.00026487
135191 | 41444.9167 | 41444.9326 | 116 | 20 | 2320 | 116 | 0.0071452 | 0.00035726 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-19 | 2014 | 2014 | 2013-06-19 | C | 116 | 0.0071452 | 0.00035726
135193 | 41445.375 | 41445.5021 | 67 | 180 | 12060 | 67 | 0.037143 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | B | 67 | 0.037143 | 0.00020635
135196 | 41445.375 | 41445.5986 | 310 | 319 | 98890 | 310 | 0.30457 | 0.00095475 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | B | 310 | 0.30457 | 0.00095475
135197 | 41445.3688 | 41445.5576 | 275 | 269 | 29350.6691 | 109.1103 | 0.090395 | 0.00084696 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 109.1103 | 0.090395 | 0.00084696
135199 | 41445.3854 | 41445.4688 | 75 | 117 | 8775 | 75 | 0.027026 | 0.00023099 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | B | 75 | 0.027026 | 0.00023099
135200 | 41445.6632 | 41445.6722 | 785 | 10 | 7850 | 785 | 0.024177 | 0.0024177 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 785 | 0.024177 | 0.0024177
135204 | 41446.2771 | 41446.2882 | 189 | 13 | 2457 | 189 | 0.0075672 | 0.00058209 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 189 | 0.0075672 | 0.00058209
135205 | 41445.9521 | 41446.2083 | 768 | 366 | 191677.8699 | 523.71 | 0.59034 | 0.0023653 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 523.71 | 0.59034 | 0.0023653
135206 | 41446.0389 | 41446.1687 | 221 | 184 | 18888.0428 | 102.6524 | 0.058172 | 0.00068065 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 102.6524 | 0.058172 | 0.00068065
135207 | 41445.9833 | 41446.1986 | 530 | 307 | 132637.8645 | 432.0452 | 0.4085 | 0.0016323 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 432.0452 | 0.4085 | 0.0016323
135208 | 41446.1681 | 41446.2063 | 760 | 52 | 39370.6182 | 757.1273 | 0.12126 | 0.0023407 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 757.1273 | 0.12126 | 0.0023407
135209 | 41445.9313 | 41445.9854 | 314 | 75 | 23550 | 314 | 0.07253 | 0.00096707 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 314 | 0.07253 | 0.00096707
135211 | 41446.3396 | 41446.3667 | 108 | 36 | 3306.4615 | 91.8462 | 0.010183 | 0.00033262 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 91.8462 | 0.010183 | 0.00033262
135213 | 41446.3639 | 41446.4306 | 1000 | 93 | 40536.375 | 435.875 | 0.12485 | 0.0030798 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 435.875 | 0.12485 | 0.0030798
135214 | 41446.3785 | 41446.4792 | 4 | 142 | 568 | 4 | 0.0017494 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | B | 4 | 0.0017494 | 1.2319e-05
135216 | 41446.5278 | 41446.5896 | 31 | 86 | 2666 | 31 | 0.0082109 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | B | 31 | 0.0082109 | 9.5475e-05
135217 | 41446.5125 | 41446.6076 | 210 | 134 | 28140 | 210 | 0.086667 | 0.00064677 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 210 | 0.086667 | 0.00064677
135219 | 41446.4007 | 41446.809 | 417 | 585 | 196483.3929 | 335.869 | 0.60514 | 0.0012843 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 335.869 | 0.60514 | 0.0012843
135220 | 41446.6076 | 41446.6667 | 38 | 82 | 3116 | 38 | 0.0095968 | 0.00011703 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 38 | 0.0095968 | 0.00011703
135221 | 41446.1875 | 41446.3625 | 289 | 249 | 71961 | 289 | 0.22163 | 0.00089007 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 289 | 0.22163 | 0.00089007
135222 | 41446.0215 | 41446.6993 | 329 | 973 | 222885.7879 | 229.0707 | 0.68645 | 0.0010133 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 229.0707 | 0.68645 | 0.0010133
135223 | 41446.6646 | 41446.6785 | 20 | 17 | 340 | 20 | 0.0010471 | 6.1597e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 20 | 0.0010471 | 6.1597e-05
135224 | 41446.2646 | 41446.6431 | 315 | 542 | 170730 | 315 | 0.52582 | 0.00097015 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 315 | 0.52582 | 0.00097015
135226 | 41448.2236 | 41448.2486 | 92 | 33 | 3036 | 92 | 0.0093504 | 0.00028335 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 92 | 0.0093504 | 0.00028335
135227 | 41447.3778 | 41447.5035 | 325 | 178 | 18773.5912 | 105.4696 | 0.05782 | 0.0010009 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 105.4696 | 0.05782 | 0.0010009
135228 | 41447.4632 | 41447.5069 | 22 | 60 | 1320 | 22 | 0.0040654 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 22 | 0.0040654 | 6.7757e-05
135229 | 41446.6472 | 41447.5222 | 2 | 1257 | 2514 | 2 | 0.0077427 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 2 | 0.0077427 | 6.1597e-06
135230 | 41447.5389 | 41447.6146 | 617 | 106 | 54403.2844 | 513.2385 | 0.16755 | 0.0019003 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 513.2385 | 0.16755 | 0.0019003
135231 | 41447.5285 | 41447.6785 | 1 | 213 | 213 | 1 | 0.00065601 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 1 | 0.00065601 | 3.0798e-06
135232 | 41446.2188 | 41446.6882 | 39 | 673 | 26247 | 39 | 0.080837 | 0.00012011 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 39 | 0.080837 | 0.00012011
135233 | 41446.4396 | 41446.7403 | 24 | 430 | 10320 | 24 | 0.031784 | 7.3916e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 24 | 0.031784 | 7.3916e-05
135234 | 41448.5951 | 41448.6354 | 71 | 55 | 3905 | 71 | 0.012027 | 0.00021867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 71 | 0.012027 | 0.00021867
135235 | 41448.6847 | 41448.7243 | 177 | 54 | 9558 | 177 | 0.029437 | 0.00054513 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 177 | 0.029437 | 0.00054513
135238 | 41441.3132 | 41441.4583 | 11 | 206 | 2266 | 11 | 0.0069789 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-16 | 2014 | 2014 | 2013-06-16 | B | 11 | 0.0069789 | 3.3878e-05
135240 | 41446.7438 | 41447.9299 | 169 | 1705 | 156276.0275 | 91.6575 | 0.48131 | 0.00052049 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 91.6575 | 0.48131 | 0.00052049
135241 | 41447.4812 | 41447.6007 | 61 | 169 | 10309 | 61 | 0.03175 | 0.00018787 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 61 | 0.03175 | 0.00018787
135242 | 41447.1444 | 41447.4986 | 402 | 507 | 132308.1118 | 260.9627 | 0.40749 | 0.0012381 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 260.9627 | 0.40749 | 0.0012381
135245 | 41448.8431 | 41448.9847 | 16 | 201 | 3216 | 16 | 0.0099048 | 4.9277e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 16 | 0.0099048 | 4.9277e-05
135246 | 41446.0069 | 41446.5868 | 356 | 832 | 168309.1162 | 202.2946 | 0.51837 | 0.0010964 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 202.2946 | 0.51837 | 0.0010964
135248 | 41446.3083 | 41446.5819 | 334 | 391 | 130594 | 334 | 0.40221 | 0.0010287 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 334 | 0.40221 | 0.0010287
135249 | 41446.5694 | 41446.6056 | 14 | 49 | 686 | 14 | 0.0021128 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 14 | 0.0021128 | 4.3118e-05
135250 | 41446.7021 | 41446.8715 | 75 | 241 | 12755.2213 | 52.9262 | 0.039284 | 0.00023099 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 52.9262 | 0.039284 | 0.00023099
135251 | 41445.9583 | 41446.7549 | 145 | 1144 | 126423.4699 | 110.51 | 0.38936 | 0.00044658 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 110.51 | 0.38936 | 0.00044658
135252 | 41449.2229 | 41449.6104 | 7 | 555 | 3885 | 7 | 0.011965 | 2.1559e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 7 | 0.011965 | 2.1559e-05
135255 | 41445.9667 | 41446.4896 | 146 | 750 | 109500 | 146 | 0.33724 | 0.00044966 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 146 | 0.33724 | 0.00044966
135256 | 41446.6257 | 41447.6604 | 66 | 1487 | 92914.5463 | 62.4846 | 0.28616 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 62.4846 | 0.28616 | 0.00020327
135257 | 41446.5472 | 41446.5875 | 4 | 55 | 220 | 4 | 0.00067757 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 4 | 0.00067757 | 1.2319e-05
135258 | 41446.5375 | 41446.5917 | 107 | 75 | 4447.1154 | 59.2949 | 0.013696 | 0.00032954 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 59.2949 | 0.013696 | 0.00032954
135259 | 41445.9535 | 41447.4264 | 87 | 2118 | 70949.505 | 33.4983 | 0.21851 | 0.00026795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 33.4983 | 0.21851 | 0.00026795
135261 | 41446.4958 | 41446.5007 | 675 | 4 | 2700 | 675 | 0.0083156 | 0.0020789 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 675 | 0.0083156 | 0.0020789
135262 | 41448.3208 | 41448.5736 | 414 | 361 | 36363.8077 | 100.7308 | 0.11199 | 0.0012751 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 100.7308 | 0.11199 | 0.0012751
135263 | 41445.9625 | 41445.9882 | 108 | 34 | 3672 | 108 | 0.011309 | 0.00033262 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 108 | 0.011309 | 0.00033262
135265 | 41449.375 | 41449.4563 | 12 | 114 | 1368 | 12 | 0.0042132 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | B | 12 | 0.0042132 | 3.6958e-05
135267 | 41449.3924 | 41449.4271 | 8 | 47 | 376 | 8 | 0.001158 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 8 | 0.001158 | 2.4639e-05
135268 | 41446.1389 | 41446.7556 | 112 | 885 | 93461.1824 | 105.6059 | 0.28785 | 0.00034494 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 105.6059 | 0.28785 | 0.00034494
135269 | 41446.3417 | 41446.5354 | 58 | 276 | 16008 | 58 | 0.049302 | 0.00017863 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 58 | 0.049302 | 0.00017863
135270 | 41446.4715 | 41446.5312 | 20 | 83 | 1660 | 20 | 0.0051125 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 20 | 0.0051125 | 6.1597e-05
135271 | 41446.35 | 41446.4278 | 211 | 109 | 15792.3482 | 144.8839 | 0.048638 | 0.00064985 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 144.8839 | 0.048638 | 0.00064985
135272 | 41446.0069 | 41446.5257 | 255 | 744 | 76404.9157 | 102.6948 | 0.23532 | 0.00078536 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 102.6948 | 0.23532 | 0.00078536
135274 | 41446.375 | 41447.4729 | 71 | 1578 | 33874.5996 | 21.4668 | 0.10433 | 0.00021867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 21.4668 | 0.10433 | 0.00021867
135275 | 41446.9021 | 41447.4826 | 22 | 833 | 18326 | 22 | 0.056441 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 22 | 0.056441 | 6.7757e-05
135278 | 41448.9167 | 41449.5799 | 2 | 952 | 1904 | 2 | 0.005864 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 2 | 0.005864 | 6.1597e-06
135279 | 41446.6951 | 41446.7056 | 14 | 12 | 168 | 14 | 0.00051741 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 14 | 0.00051741 | 4.3118e-05
135280 | 41446.6167 | 41446.6889 | 66 | 101 | 6666 | 66 | 0.02053 | 0.00020327 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 66 | 0.02053 | 0.00020327
135282 | 41449.5312 | 41449.5528 | 1 | 28 | 28 | 1 | 8.6236e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 1 | 8.6236e-05 | 3.0798e-06
135283 | 41446.6375 | 41446.6521 | 305 | 18 | 5490 | 305 | 0.016908 | 0.00093935 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 305 | 0.016908 | 0.00093935
135285 | 41447.5757 | 41447.5826 | 2674 | 7 | 15526 | 2218 | 0.047818 | 0.0082355 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 2218 | 0.047818 | 0.0082355
135288 | 41446.4083 | 41446.5431 | 37 | 191 | 7067 | 37 | 0.021765 | 0.00011395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 37 | 0.021765 | 0.00011395
135289 | 41446.0326 | 41447.5833 | 78 | 2230 | 54917.1205 | 24.6265 | 0.16914 | 0.00024023 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 24.6265 | 0.16914 | 0.00024023
135290 | 41446.5833 | 41448.6653 | 9 | 2995 | 26955 | 9 | 0.083017 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 9 | 0.083017 | 2.7719e-05
135291 | 41446.1083 | 41446.5806 | 306 | 677 | 189311.1029 | 279.6324 | 0.58305 | 0.00094243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 279.6324 | 0.58305 | 0.00094243
135292 | 41447.1451 | 41447.6819 | 347 | 770 | 185416.5977 | 240.8008 | 0.57105 | 0.0010687 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 240.8008 | 0.57105 | 0.0010687
135293 | 41449.5486 | 41449.6042 | 251 | 77 | 19327 | 251 | 0.059524 | 0.00077304 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 251 | 0.059524 | 0.00077304
135294 | 41446.0729 | 41446.0806 | 1972 | 8 | 15776 | 1972 | 0.048588 | 0.0060734 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-21 | 2014 | 2014 | 2013-06-21 | C | 1972 | 0.048588 | 0.0060734
135296 | 41449.5833 | 41449.625 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 6 | 0.0010533 | 1.8479e-05
135297 | 41447.7361 | 41447.7417 | 2674 | 5 | 10520 | 2104 | 0.0324 | 0.0082355 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-22 | 2014 | 2014 | 2013-06-22 | C | 2104 | 0.0324 | 0.0082355
135298 | 41448.8944 | 41448.9681 | 1382 | 103 | 128109.6509 | 1243.783 | 0.39456 | 0.0042563 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 1243.783 | 0.39456 | 0.0042563
135300 | 41449.4514 | 41449.759 | 19 | 440 | 8360 | 19 | 0.025747 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 19 | 0.025747 | 5.8517e-05
135301 | 41449.7278 | 41449.9167 | 729 | 269 | 46247.2316 | 171.9228 | 0.14243 | 0.0022452 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 171.9228 | 0.14243 | 0.0022452
135305 | 41449.7569 | 41449.809 | 14 | 72 | 1008 | 14 | 0.0031045 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 14 | 0.0031045 | 4.3118e-05
135306 | 41449.0181 | 41449.0347 | 2975 | 21 | 50120 | 2386.6667 | 0.15436 | 0.0091625 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 2386.6667 | 0.15436 | 0.0091625
135307 | 41448.2924 | 41448.5125 | 856 | 314 | 186639.817 | 594.3943 | 0.57482 | 0.0026363 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-23 | 2014 | 2014 | 2013-06-23 | C | 594.3943 | 0.57482 | 0.0026363
135309 | 41449.7569 | 41449.7771 | 1 | 26 | 26 | 1 | 8.0076e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-24 | 2014 | 2014 | 2013-06-24 | C | 1 | 8.0076e-05 | 3.0798e-06
135310 | 41445.75 | 41450.4681 | 8 | 6791 | 54328 | 8 | 0.16732 | 2.4639e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | C | 8 | 0.16732 | 2.4639e-05
135316 | 41450.4347 | 41450.6083 | 14 | 247 | 3458 | 14 | 0.01065 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-25 | 2014 | 2014 | 2013-06-25 | C | 14 | 0.01065 | 4.3118e-05
135317 | 41450.4583 | 41450.6354 | 5 | 252 | 1260 | 5 | 0.0038806 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-25 | 2014 | 2014 | 2013-06-25 | C | 5 | 0.0038806 | 1.5399e-05
135321 | 41450.3646 | 41450.4986 | 16 | 190 | 3040 | 16 | 0.0093627 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-25 | 2014 | 2014 | 2013-06-25 | C | 16 | 0.0093627 | 4.9277e-05
135323 | 41451.241 | 41451.2903 | 1276 | 68 | 60767.0986 | 893.6338 | 0.18715 | 0.0039299 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-26 | 2014 | 2014 | 2013-06-26 | C | 893.6338 | 0.18715 | 0.0039299
135324 | 41451.5569 | 41451.5861 | 702 | 39 | 24877.3571 | 637.881 | 0.076618 | 0.002162 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-26 | 2014 | 2014 | 2013-06-26 | C | 637.881 | 0.076618 | 0.002162
135325 | 41451.4806 | 41451.6458 | 3 | 235 | 705 | 3 | 0.0021713 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-26 | 2014 | 2014 | 2013-06-26 | C | 3 | 0.0021713 | 9.2395e-06
135328 | 41451.6667 | 41451.7646 | 2 | 138 | 276 | 2 | 0.00085004 | 6.1597e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-26 | 2014 | 2014 | 2013-06-26 | C | 2 | 0.00085004 | 6.1597e-06
135331 | 41437.3757 | 41437.6174 | 75 | 345 | 25875 | 75 | 0.079691 | 0.00023099 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-12 | 2014 | 2014 | 2013-06-12 | B | 75 | 0.079691 | 0.00023099
135332 | 41452.3854 | 41452.625 | 17 | 342 | 5814 | 17 | 0.017906 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-27 | 2014 | 2014 | 2013-06-27 | B | 17 | 0.017906 | 5.2357e-05
135334 | 41445.3854 | 41445.6417 | 123 | 366 | 45018 | 123 | 0.13865 | 0.00037882 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-20 | 2014 | 2014 | 2013-06-20 | B | 123 | 0.13865 | 0.00037882
135335 | 41452.2819 | 41452.6653 | 176 | 549 | 53881.5652 | 98.1449 | 0.16595 | 0.00054205 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-27 | 2014 | 2014 | 2013-06-27 | B | 98.1449 | 0.16595 | 0.00054205
135340 | 41453.5278 | 41453.55 | 128 | 29 | 3712 | 128 | 0.011432 | 0.00039422 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-28 | 2014 | 2014 | 2013-06-28 | C | 128 | 0.011432 | 0.00039422
135342 | 41454.2965 | 41454.3826 | 1 | 121 | 121 | 1 | 0.00037266 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-29 | 2014 | 2014 | 2013-06-29 | C | 1 | 0.00037266 | 3.0798e-06
135344 | 41453.4701 | 41453.5625 | 47 | 130 | 6071.8797 | 46.7068 | 0.0187 | 0.00014475 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-06-28 | 2014 | 2014 | 2013-06-28 | C | 46.7068 | 0.0187 | 0.00014475
135345 | 41453.2993 | 41453.316 | 936 | 21 | 12148.5 | 578.5 | 0.037415 | 0.0028827 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-28 | 2014 | 2014 | 2013-06-28 | C | 578.5 | 0.037415 | 0.0028827
135346 | 41454.6951 | 41454.8833 | 499 | 268 | 35839.8081 | 133.7306 | 0.11038 | 0.0015368 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-29 | 2014 | 2014 | 2013-06-29 | C | 133.7306 | 0.11038 | 0.0015368
135347 | 41454.4236 | 41454.4708 | 157 | 65 | 10205 | 157 | 0.03143 | 0.00048354 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-29 | 2014 | 2014 | 2013-06-29 | C | 157 | 0.03143 | 0.00048354
135348 | 41454.4306 | 41454.5597 | 38 | 183 | 6954 | 38 | 0.021417 | 0.00011703 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-29 | 2014 | 2014 | 2013-06-29 | C | 38 | 0.021417 | 0.00011703
135353 | 41455.4625 | 41455.5299 | 9851 | 94 | 484589.3814 | 5155.2062 | 1.4925 | 0.03034 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-06-30 | 2014 | 2014 | 2013-06-30 | C | 5155.2062 | 1.4925 | 0.03034
135354 | 41454.4167 | 41454.575 | 1 | 225 | 225 | 1 | 0.00069296 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-06-29 | 2014 | 2014 | 2013-06-29 | C | 1 | 0.00069296 | 3.0798e-06
135356 | 41455.8299 | 41455.9722 | 52 | 202 | 10504 | 52 | 0.032351 | 0.00016015 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-30 | 2014 | 2014 | 2013-06-30 | C | 52 | 0.032351 | 0.00016015
135358 | 41455.9375 | 41456.1833 | 169 | 351 | 35585.8475 | 101.3842 | 0.1096 | 0.00052049 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-06-30 | 2014 | 2014 | 2013-06-30 | C | 101.3842 | 0.1096 | 0.00052049
135359 | 41455.3688 | 41455.4736 | 1 | 148 | 148 | 1 | 0.00045582 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-30 | 2014 | 2014 | 2013-06-30 | B | 1 | 0.00045582 | 3.0798e-06
135360 | 41453.3903 | 41453.4375 | 24 | 65 | 1560 | 24 | 0.0048046 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-06-28 | 2014 | 2014 | 2013-06-28 | B | 24 | 0.0048046 | 7.3916e-05
135363 | 41456.3854 | 41456.516 | 705 | 185 | 39403.0319 | 212.9894 | 0.12136 | 0.0021713 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | C | 212.9894 | 0.12136 | 0.0021713
135365 | 41456.3757 | 41456.4986 | 10 | 174 | 1740 | 10 | 0.0053589 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 10 | 0.0053589 | 3.0798e-05
135366 | 41456.5208 | 41456.5972 | 39 | 107 | 4173 | 39 | 0.012852 | 0.00012011 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 39 | 0.012852 | 0.00012011
135368 | 41456.375 | 41456.625 | 54 | 357 | 19278 | 54 | 0.059373 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 54 | 0.059373 | 0.00016631
135369 | 41456.375 | 41456.6431 | 36 | 383 | 13788 | 36 | 0.042465 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 36 | 0.042465 | 0.00011087
135371 | 41456.3889 | 41456.4812 | 54 | 130 | 7020 | 54 | 0.02162 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 54 | 0.02162 | 0.00016631
135372 | 41456.4062 | 41456.6111 | 18 | 292 | 5256 | 18 | 0.016188 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 18 | 0.016188 | 5.5437e-05
135373 | 41456.375 | 41456.6264 | 52 | 359 | 18668 | 52 | 0.057494 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-01 | 2014 | 2014 | 2013-07-01 | B | 52 | 0.057494 | 0.00016015
135375 | 41457.0417 | 41457.2451 | 33 | 290 | 9570 | 33 | 0.029474 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 33 | 0.029474 | 0.00010163
135377 | 41457.3819 | 41457.4028 | 6 | 27 | 162 | 6 | 0.00049893 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 6 | 0.00049893 | 1.8479e-05
135380 | 41457.3854 | 41457.4319 | 17 | 64 | 1088 | 17 | 0.0033509 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 17 | 0.0033509 | 5.2357e-05
135382 | 41457.3958 | 41457.5486 | 45 | 217 | 6115.4545 | 28.1818 | 0.018835 | 0.00013859 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 28.1818 | 0.018835 | 0.00013859
135384 | 41457.45 | 41457.4611 | 14 | 13 | 182 | 14 | 0.00056053 | 4.3118e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 14 | 0.00056053 | 4.3118e-05
135385 | 41457.4722 | 41457.5035 | 40 | 42 | 1680 | 40 | 0.0051741 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 40 | 0.0051741 | 0.00012319
135386 | 41457.4062 | 41457.516 | 10 | 155 | 1550 | 10 | 0.0047738 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 10 | 0.0047738 | 3.0798e-05
135387 | 41457.3854 | 41457.5208 | 9 | 192 | 1728 | 9 | 0.005322 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 9 | 0.005322 | 2.7719e-05
135388 | 41457.375 | 41457.625 | 16 | 357 | 5712 | 16 | 0.017592 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 16 | 0.017592 | 4.9277e-05
135390 | 41457.366 | 41457.6146 | 340 | 355 | 120700 | 340 | 0.37174 | 0.0010471 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 340 | 0.37174 | 0.0010471
135392 | 41457.4194 | 41457.6479 | 46 | 326 | 14996 | 46 | 0.046185 | 0.00014167 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 46 | 0.046185 | 0.00014167
135393 | 41457.3993 | 41457.6521 | 30 | 361 | 9623.0302 | 26.6566 | 0.029637 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 26.6566 | 0.029637 | 9.2395e-05
135394 | 41457.3646 | 41457.4889 | 36 | 176 | 6336 | 36 | 0.019514 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 36 | 0.019514 | 0.00011087
135395 | 41457.3854 | 41457.6201 | 137 | 335 | 45895 | 137 | 0.14135 | 0.00042194 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 137 | 0.14135 | 0.00042194
135396 | 41457.3333 | 41457.475 | 50 | 201 | 3000.2206 | 14.9265 | 0.0092402 | 0.00015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 14.9265 | 0.0092402 | 0.00015399
135397 | 41457.3958 | 41457.625 | 28 | 327 | 9156 | 28 | 0.028199 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 28 | 0.028199 | 8.6236e-05
135399 | 41458.0472 | 41458.0938 | 169 | 64 | 9287.6418 | 145.1194 | 0.028604 | 0.00052049 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 145.1194 | 0.028604 | 0.00052049
135401 | 41457.691 | 41457.7986 | 21 | 152 | 3192 | 21 | 0.0098309 | 6.4677e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | C | 21 | 0.0098309 | 6.4677e-05
135403 | 41458.2653 | 41458.4187 | 1112 | 218 | 119309.1312 | 547.2896 | 0.36745 | 0.0034248 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 547.2896 | 0.36745 | 0.0034248
135405 | 41458.2944 | 41458.3597 | 255 | 91 | 16757.5532 | 184.1489 | 0.051611 | 0.00078536 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 184.1489 | 0.051611 | 0.00078536
135406 | 41457.3938 | 41457.5118 | 120 | 167 | 20040 | 120 | 0.06172 | 0.00036958 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-02 | 2014 | 2014 | 2013-07-02 | B | 120 | 0.06172 | 0.00036958
135408 | 41458.3826 | 41458.6076 | 38 | 321 | 12198 | 38 | 0.037568 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | B | 38 | 0.037568 | 0.00011703
135409 | 41458.4028 | 41458.5729 | 71 | 242 | 4708.6286 | 19.4571 | 0.014502 | 0.00021867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | B | 19.4571 | 0.014502 | 0.00021867
135411 | 41458.375 | 41458.6285 | 36 | 362 | 13032 | 36 | 0.040136 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | B | 36 | 0.040136 | 0.00011087
135412 | 41458.6667 | 41458.7292 | 12 | 87 | 1044 | 12 | 0.0032154 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 12 | 0.0032154 | 3.6958e-05
135413 | 41459.0062 | 41459.2104 | 277 | 291 | 42497.8776 | 146.0408 | 0.13089 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 146.0408 | 0.13089 | 0.00085312
135414 | 41458.3333 | 41458.5417 | 30 | 297 | 6389.46 | 21.5133 | 0.019679 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 21.5133 | 0.019679 | 9.2395e-05
135415 | 41458.5208 | 41458.6875 | 3 | 237 | 711 | 3 | 0.0021898 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-03 | 2014 | 2014 | 2013-07-03 | C | 3 | 0.0021898 | 9.2395e-06
135417 | 41459.4167 | 41459.4299 | 17 | 16 | 272 | 17 | 0.00083772 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 17 | 0.00083772 | 5.2357e-05
135418 | 41459.3715 | 41459.6403 | 8 | 384 | 3072 | 8 | 0.0094613 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 8 | 0.0094613 | 2.4639e-05
135422 | 41459.375 | 41459.6528 | 23 | 397 | 8936.47 | 22.51 | 0.027523 | 7.0836e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 22.51 | 0.027523 | 7.0836e-05
135423 | 41459.3792 | 41459.591 | 41 | 302 | 12382 | 41 | 0.038135 | 0.00012627 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 41 | 0.038135 | 0.00012627
135425 | 41459.3924 | 41459.6181 | 28 | 322 | 9016 | 28 | 0.027768 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 28 | 0.027768 | 8.6236e-05
135426 | 41459.8014 | 41459.875 | 19 | 103 | 1957 | 19 | 0.0060273 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 19 | 0.0060273 | 5.8517e-05
135427 | 41459.5028 | 41459.6285 | 149 | 178 | 18705.7348 | 105.0884 | 0.057611 | 0.0004589 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 105.0884 | 0.057611 | 0.0004589
135428 | 41459.4076 | 41459.4792 | 13 | 100 | 1300 | 13 | 0.0040038 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 13 | 0.0040038 | 4.0038e-05
135430 | 41459.8403 | 41459.9062 | 19 | 92 | 1748 | 19 | 0.0053836 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 19 | 0.0053836 | 5.8517e-05
135431 | 41459.95 | 41459.9868 | 21 | 50 | 1050 | 21 | 0.0032338 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 21 | 0.0032338 | 6.4677e-05
135432 | 41459.8021 | 41459.9375 | 315 | 192 | 60480 | 315 | 0.18627 | 0.00097015 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 315 | 0.18627 | 0.00097015
135434 | 41459.9354 | 41460.225 | 8057 | 414 | 513758.1151 | 1240.9616 | 1.5823 | 0.024814 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | C | 1240.9616 | 1.5823 | 0.024814
135435 | 41460.3875 | 41460.4056 | 524 | 23 | 8626.7692 | 375.0769 | 0.026569 | 0.0016138 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | C | 375.0769 | 0.026569 | 0.0016138
135436 | 41460.3958 | 41460.5153 | 55 | 169 | 9295 | 55 | 0.028627 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | B | 55 | 0.028627 | 0.00016939
135437 | 41460.5188 | 41460.6188 | 60 | 141 | 4204.5417 | 29.8194 | 0.012949 | 0.00018479 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | C | 29.8194 | 0.012949 | 0.00018479
135438 | 41460.4931 | 41460.5556 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | C | 3 | 0.00080384 | 9.2395e-06
135440 | 41460.5208 | 41460.625 | 6 | 147 | 882 | 6 | 0.0027164 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | B | 6 | 0.0027164 | 1.8479e-05
135441 | 41460.3854 | 41460.4688 | 4 | 117 | 468 | 4 | 0.0014414 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | B | 4 | 0.0014414 | 1.2319e-05
135447 | 41460.9375 | 41461.025 | 1 | 123 | 123 | 1 | 0.00037882 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | B | 1 | 0.00037882 | 3.0798e-06
135448 | 41460.9896 | 41461.1146 | 487 | 177 | 86199 | 487 | 0.26548 | 0.0014999 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | B | 487 | 0.26548 | 0.0014999
135449 | 41461.0569 | 41461.0938 | 2 | 50 | 100 | 2 | 0.00030798 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | B | 2 | 0.00030798 | 6.1597e-06
135450 | 41461.1146 | 41461.1701 | 49 | 77 | 3773 | 49 | 0.01162 | 0.00015091 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | B | 49 | 0.01162 | 0.00015091
135451 | 41461.1771 | 41461.2083 | 55 | 42 | 2310 | 55 | 0.0071144 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | B | 55 | 0.0071144 | 0.00016939
135452 | 41460.7653 | 41460.9826 | 2 | 310 | 620 | 2 | 0.0019095 | 6.1597e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-05 | 2014 | 2014 | 2013-07-05 | C | 2 | 0.0019095 | 6.1597e-06
135453 | 41461.7361 | 41461.784 | 25 | 66 | 1650 | 25 | 0.0050817 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | C | 25 | 0.0050817 | 7.6996e-05
135454 | 41461.8333 | 41461.9167 | 292 | 117 | 12790.05 | 109.3167 | 0.039391 | 0.00089931 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | C | 109.3167 | 0.039391 | 0.00089931
135455 | 41461.9792 | 41461.9951 | 14 | 20 | 280 | 14 | 0.00086236 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | B | 14 | 0.00086236 | 4.3118e-05
135460 | 41461.2576 | 41461.8396 | 382 | 835 | 23854.2959 | 28.568 | 0.073467 | 0.0011765 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-06 | 2014 | 2014 | 2013-07-06 | C | 28.568 | 0.073467 | 0.0011765
135461 | 41462.3229 | 41462.7264 | 57 | 578 | 32946 | 57 | 0.10147 | 0.00017555 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 57 | 0.10147 | 0.00017555
135464 | 41462.3792 | 41462.4264 | 78 | 65 | 5070 | 78 | 0.015615 | 0.00024023 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | B | 78 | 0.015615 | 0.00024023
135465 | 41462.5944 | 41462.7063 | 941 | 158 | 90961.8758 | 575.7081 | 0.28015 | 0.0028981 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 575.7081 | 0.28015 | 0.0028981
135467 | 41462.6139 | 41462.6826 | 236 | 96 | 17334.303 | 180.5657 | 0.053387 | 0.00072684 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 180.5657 | 0.053387 | 0.00072684
135468 | 41462.5618 | 41462.5951 | 568 | 45 | 22561.875 | 501.375 | 0.069487 | 0.0017494 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 501.375 | 0.069487 | 0.0017494
135469 | 41462.7833 | 41462.8646 | 652 | 114 | 51302.9231 | 450.0256 | 0.158 | 0.0020081 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 450.0256 | 0.158 | 0.0020081
135472 | 41463.4167 | 41463.6069 | 180 | 271 | 48780 | 180 | 0.15023 | 0.00055437 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-08 | 2014 | 2014 | 2013-07-08 | C | 180 | 0.15023 | 0.00055437
135473 | 41463.5361 | 41463.5979 | 23 | 86 | 1978 | 23 | 0.0060919 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-08 | 2014 | 2014 | 2013-07-08 | C | 23 | 0.0060919 | 7.0836e-05
135475 | 41463.634 | 41463.6646 | 3 | 41 | 123 | 3 | 0.00037882 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-08 | 2014 | 2014 | 2013-07-08 | C | 3 | 0.00037882 | 9.2395e-06
135476 | 41463.5625 | 41463.5694 | 1 | 7 | 7 | 1 | 2.1559e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-08 | 2014 | 2014 | 2013-07-08 | C | 1 | 2.1559e-05 | 3.0798e-06
135477 | 41462.7292 | 41463.6722 | 1 | 1355 | 1355 | 1 | 0.0041732 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-07 | 2014 | 2014 | 2013-07-07 | C | 1 | 0.0041732 | 3.0798e-06
135480 | 41464.0146 | 41464.1896 | 277 | 249 | 68973 | 277 | 0.21243 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | C | 277 | 0.21243 | 0.00085312
135481 | 41464.0111 | 41464.0278 | 111 | 21 | 2331 | 111 | 0.0071791 | 0.00034186 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | C | 111 | 0.0071791 | 0.00034186
135482 | 41464.084 | 41464.1819 | 111 | 138 | 13066.9362 | 94.6879 | 0.040244 | 0.00034186 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | C | 94.6879 | 0.040244 | 0.00034186
135483 | 41464.3958 | 41464.466 | 186 | 98 | 18228 | 186 | 0.056139 | 0.00057285 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 186 | 0.056139 | 0.00057285
135484 | 41464.3542 | 41464.6083 | 27 | 363 | 9801 | 27 | 0.030186 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 27 | 0.030186 | 8.3156e-05
135490 | 41464.375 | 41464.5972 | 60 | 317 | 19020 | 60 | 0.058579 | 0.00018479 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 60 | 0.058579 | 0.00018479
135492 | 41464.3542 | 41464.616 | 275 | 374 | 102850 | 275 | 0.31676 | 0.00084696 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 275 | 0.31676 | 0.00084696
135494 | 41464.3681 | 41464.6319 | 24 | 377 | 9048 | 24 | 0.027866 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 24 | 0.027866 | 7.3916e-05
135495 | 41464.3854 | 41464.6361 | 31 | 358 | 11098 | 31 | 0.03418 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 31 | 0.03418 | 9.5475e-05
135497 | 41464.4236 | 41464.5694 | 4 | 207 | 828 | 4 | 0.0025501 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 4 | 0.0025501 | 1.2319e-05
135499 | 41464.3986 | 41464.7028 | 298 | 435 | 129630 | 298 | 0.39924 | 0.00091779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 298 | 0.39924 | 0.00091779
135500 | 41465.1931 | 41465.2049 | 237 | 14 | 3318 | 237 | 0.010219 | 0.00072992 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 237 | 0.010219 | 0.00072992
135501 | 41465.1465 | 41465.3021 | 111 | 221 | 18241.3795 | 82.5402 | 0.056181 | 0.00034186 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 82.5402 | 0.056181 | 0.00034186
135504 | 41465.4181 | 41465.4722 | 4 | 75 | 300 | 4 | 0.00092395 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 4 | 0.00092395 | 1.2319e-05
135506 | 41465.4014 | 41465.4507 | 174 | 68 | 11832 | 174 | 0.036441 | 0.00053589 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 174 | 0.036441 | 0.00053589
135508 | 41465.3854 | 41465.4167 | 29 | 42 | 1218 | 29 | 0.0037512 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 29 | 0.0037512 | 8.9315e-05
135509 | 41465.5542 | 41465.5799 | 2 | 34 | 68 | 2 | 0.00020943 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 2 | 0.00020943 | 6.1597e-06
135511 | 41465.5764 | 41465.5868 | 1 | 12 | 12 | 1 | 3.6958e-05 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 1 | 3.6958e-05 | 3.0798e-06
135512 | 41465.5549 | 41465.5799 | 62 | 33 | 2046 | 62 | 0.0063014 | 0.00019095 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 62 | 0.0063014 | 0.00019095
135513 | 41465.3167 | 41465.4451 | 236 | 182 | 19819.3081 | 108.8973 | 0.06104 | 0.00072684 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 108.8973 | 0.06104 | 0.00072684
135514 | 41465.5271 | 41465.5437 | 174 | 21 | 3654 | 174 | 0.011254 | 0.00053589 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 174 | 0.011254 | 0.00053589
135515 | 41465.3646 | 41465.5611 | 90 | 280 | 25200 | 90 | 0.077612 | 0.00027719 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 90 | 0.077612 | 0.00027719
135517 | 41465.375 | 41465.6049 | 125 | 328 | 40876.1329 | 124.6224 | 0.12589 | 0.00038498 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 124.6224 | 0.12589 | 0.00038498
135519 | 41465.5354 | 41465.5694 | 131 | 46 | 6026 | 131 | 0.018559 | 0.00040346 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 131 | 0.018559 | 0.00040346
135520 | 41465.5354 | 41465.5694 | 60 | 46 | 2760 | 60 | 0.0085004 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 60 | 0.0085004 | 0.00018479
135522 | 41465.4757 | 41465.5785 | 17 | 145 | 2465 | 17 | 0.0075918 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 17 | 0.0075918 | 5.2357e-05
135523 | 41465.8208 | 41466.0139 | 30 | 275 | 6914.5683 | 25.1439 | 0.021296 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 25.1439 | 0.021296 | 9.2395e-05
135524 | 41465.9417 | 41466.0569 | 152 | 163 | 17894.6506 | 109.7831 | 0.055113 | 0.00046814 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 109.7831 | 0.055113 | 0.00046814
135526 | 41466.3889 | 41466.4069 | 6 | 23 | 138 | 6 | 0.00042502 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 6 | 0.00042502 | 1.8479e-05
135527 | 41466.3854 | 41466.4257 | 18 | 55 | 990 | 18 | 0.003049 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 18 | 0.003049 | 5.5437e-05
135529 | 41466.3958 | 41466.6458 | 31 | 357 | 11067 | 31 | 0.034085 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | B | 31 | 0.034085 | 9.5475e-05
135530 | 41466.4167 | 41466.4514 | 5 | 47 | 235 | 5 | 0.00072376 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | B | 5 | 0.00072376 | 1.5399e-05
135531 | 41466.2292 | 41466.5486 | 50 | 457 | 4967.3913 | 10.8696 | 0.015299 | 0.00015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 10.8696 | 0.015299 | 0.00015399
135533 | 41466.3854 | 41466.6201 | 12 | 335 | 4020 | 12 | 0.012381 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | B | 12 | 0.012381 | 3.6958e-05
135534 | 41466.5694 | 41466.6146 | 76 | 62 | 4712 | 76 | 0.014512 | 0.00023407 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 76 | 0.014512 | 0.00023407
135535 | 41466.3854 | 41466.5833 | 3 | 282 | 846 | 3 | 0.0026055 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | B | 3 | 0.0026055 | 9.2395e-06
135536 | 41466.4375 | 41466.5208 | 3 | 117 | 351 | 3 | 0.001081 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 3 | 0.001081 | 9.2395e-06
135537 | 41466.375 | 41466.6667 | 10 | 417 | 4170 | 10 | 0.012843 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | B | 10 | 0.012843 | 3.0798e-05
135538 | 41466.5917 | 41466.6792 | 1206 | 123 | 92011.8095 | 748.0635 | 0.28338 | 0.0037143 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 748.0635 | 0.28338 | 0.0037143
135540 | 41466.8299 | 41466.8799 | 54 | 69 | 3726 | 54 | 0.011475 | 0.00016631 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 54 | 0.011475 | 0.00016631
135541 | 41467.0229 | 41467.1431 | 10 | 170 | 1700 | 10 | 0.0052357 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 10 | 0.0052357 | 3.0798e-05
135542 | 41467.2799 | 41467.4306 | 50 | 214 | 10700 | 50 | 0.032954 | 0.00015399 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 50 | 0.032954 | 0.00015399
135543 | 41467.4097 | 41467.5201 | 47 | 156 | 7332 | 47 | 0.022581 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 47 | 0.022581 | 0.00014475
135544 | 41467.4826 | 41467.4896 | 2 | 7 | 14 | 2 | 4.3118e-05 | 6.1597e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 2 | 4.3118e-05 | 6.1597e-06
135545 | 41466.875 | 41467.5764 | 1 | 1007 | 1007 | 1 | 0.0031014 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-11 | 2014 | 2014 | 2013-07-11 | C | 1 | 0.0031014 | 3.0798e-06
135546 | 41467.5486 | 41467.5868 | 6 | 52 | 312 | 6 | 0.00096091 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 6 | 0.00096091 | 1.8479e-05
135547 | 41467.4688 | 41467.5049 | 203 | 49 | 9947 | 203 | 0.030635 | 0.00062521 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 203 | 0.030635 | 0.00062521
135548 | 41465.9368 | 41469.6687 | 228 | 5371 | 408168.0156 | 75.9948 | 1.2571 | 0.0007022 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | C | 75.9948 | 1.2571 | 0.0007022
135550 | 41467.5125 | 41467.6229 | 4 | 156 | 624 | 4 | 0.0019218 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 4 | 0.0019218 | 1.2319e-05
135552 | 41467.4792 | 41467.6667 | 1 | 267 | 267 | 1 | 0.00082232 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-12 | 2014 | 2014 | 2013-07-12 | C | 1 | 0.00082232 | 3.0798e-06
135555 | 41469.5243 | 41469.5576 | 60 | 45 | 2700 | 60 | 0.0083156 | 0.00018479 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 60 | 0.0083156 | 0.00018479
135563 | 41469.9583 | 41470.5347 | 18 | 827 | 14886 | 18 | 0.045847 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 18 | 0.045847 | 5.5437e-05
135564 | 41470.4097 | 41470.441 | 3 | 42 | 126 | 3 | 0.00038806 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | B | 3 | 0.00038806 | 9.2395e-06
135565 | 41470.4062 | 41470.5472 | 2 | 200 | 400 | 2 | 0.0012319 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | B | 2 | 0.0012319 | 6.1597e-06
135566 | 41469.6458 | 41470.4667 | 29 | 1179 | 34191 | 29 | 0.1053 | 8.9315e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 29 | 0.1053 | 8.9315e-05
135567 | 41469.6458 | 41470.375 | 15 | 1047 | 15705 | 15 | 0.048369 | 4.6198e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 15 | 0.048369 | 4.6198e-05
135569 | 41470.5278 | 41470.559 | 2 | 42 | 84 | 2 | 0.00025871 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 2 | 0.00025871 | 6.1597e-06
135571 | 41469.7722 | 41469.9403 | 119 | 239 | 28441 | 119 | 0.087594 | 0.0003665 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 119 | 0.087594 | 0.0003665
135572 | 41470.3875 | 41470.5757 | 16 | 268 | 4288 | 16 | 0.013206 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | B | 16 | 0.013206 | 4.9277e-05
135574 | 41470.4375 | 41470.6403 | 4 | 289 | 1156 | 4 | 0.0035603 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | B | 4 | 0.0035603 | 1.2319e-05
135575 | 41469.9 | 41470.6222 | 253 | 1037 | 39027.0962 | 37.6346 | 0.1202 | 0.0007792 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 37.6346 | 0.1202 | 0.0007792
135576 | 41470.5764 | 41470.6736 | 570 | 137 | 14882.1143 | 108.6286 | 0.045835 | 0.0017555 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 108.6286 | 0.045835 | 0.0017555
135577 | 41470.5521 | 41470.6181 | 7 | 92 | 644 | 7 | 0.0019834 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 7 | 0.0019834 | 2.1559e-05
135578 | 41470.7722 | 41470.9403 | 119 | 239 | 4818.5165 | 20.1612 | 0.01484 | 0.0003665 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 20.1612 | 0.01484 | 0.0003665
135579 | 41470.7056 | 41470.7507 | 5 | 62 | 310 | 5 | 0.00095475 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 5 | 0.00095475 | 1.5399e-05
135580 | 41470.7389 | 41470.8056 | 8 | 93 | 744 | 8 | 0.0022914 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 8 | 0.0022914 | 2.4639e-05
135583 | 41470.784 | 41470.8285 | 12 | 61 | 732 | 12 | 0.0022544 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 12 | 0.0022544 | 3.6958e-05
135584 | 41469.6778 | 41471.3701 | 1233 | 2434 | 700402.7263 | 287.7579 | 2.1571 | 0.0037974 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 287.7579 | 2.1571 | 0.0037974
135585 | 41470.7104 | 41470.7535 | 11 | 59 | 649 | 11 | 0.0019988 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 11 | 0.0019988 | 3.3878e-05
135587 | 41470.6111 | 41470.6653 | 3 | 75 | 225 | 3 | 0.00069296 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 3 | 0.00069296 | 9.2395e-06
135588 | 41469.8819 | 41470.5847 | 249 | 1009 | 251241 | 249 | 0.77378 | 0.00076688 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 249 | 0.77378 | 0.00076688
135589 | 41469.5965 | 41470.4896 | 14 | 1283 | 6043.8678 | 4.7107 | 0.018614 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 4.7107 | 0.018614 | 4.3118e-05
135590 | 41469.6069 | 41469.7118 | 898 | 148 | 70928.2649 | 479.245 | 0.21845 | 0.0027657 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 479.245 | 0.21845 | 0.0027657
135592 | 41470.6701 | 41470.7562 | 21 | 121 | 2541 | 21 | 0.0078259 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 21 | 0.0078259 | 6.4677e-05
135593 | 41470.6153 | 41470.7458 | 10 | 185 | 1850 | 10 | 0.0056977 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 10 | 0.0056977 | 3.0798e-05
135595 | 41469.7167 | 41470.4715 | 53 | 1084 | 57452 | 53 | 0.17694 | 0.00016323 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 53 | 0.17694 | 0.00016323
135596 | 41470.6201 | 41470.6451 | 15 | 33 | 495 | 15 | 0.0015245 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 15 | 0.0015245 | 4.6198e-05
135597 | 41470.5465 | 41470.6472 | 9 | 142 | 1278 | 9 | 0.003936 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 9 | 0.003936 | 2.7719e-05
135598 | 41470.0743 | 41470.5049 | 255 | 617 | 108147.1629 | 175.279 | 0.33308 | 0.00078536 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 175.279 | 0.33308 | 0.00078536
135599 | 41469.6778 | 41470.5903 | 733 | 1311 | 317229.0753 | 241.9749 | 0.97702 | 0.0022575 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 241.9749 | 0.97702 | 0.0022575
135601 | 41470.6715 | 41470.7028 | 20 | 42 | 840 | 20 | 0.0025871 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 20 | 0.0025871 | 6.1597e-05
135602 | 41470.375 | 41470.7118 | 8 | 482 | 3856 | 8 | 0.011876 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 8 | 0.011876 | 2.4639e-05
135603 | 41469.75 | 41470.7049 | 1297 | 1372 | 346585.1607 | 252.6131 | 1.0674 | 0.0039946 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 252.6131 | 1.0674 | 0.0039946
135604 | 41470.4153 | 41470.6611 | 25 | 351 | 8775 | 25 | 0.027026 | 0 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 25 | 0.027026 | 0
135605 | 41469.6174 | 41469.6764 | 21 | 82 | 1722 | 21 | 0.0053035 | 6.4677e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 21 | 0.0053035 | 6.4677e-05
135606 | 41469.7132 | 41470.3007 | 1399 | 843 | 697227.7624 | 827.0792 | 2.1474 | 0.0043087 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 827.0792 | 2.1474 | 0.0043087
135607 | 41469.641 | 41470.6139 | 108 | 1398 | 150984 | 108 | 0.46501 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 108 | 0.46501 | 0.00033262
135608 | 41469.6021 | 41470.525 | 185 | 1326 | 45324.456 | 34.1813 | 0.13959 | 0.00056977 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 34.1813 | 0.13959 | 0.00056977
135609 | 41469.725 | 41470.1285 | 96 | 578 | 55270.1308 | 95.6231 | 0.17022 | 0.00029566 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 95.6231 | 0.17022 | 0.00029566
135611 | 41469.6764 | 41470.6535 | 275 | 1404 | 337993.791 | 240.7363 | 1.041 | 0.00084696 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 240.7363 | 1.041 | 0.00084696
135613 | 41469.4792 | 41469.6319 | 217 | 217 | 21842.0364 | 100.6545 | 0.06727 | 0.00066833 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 100.6545 | 0.06727 | 0.00066833
135614 | 41470.3847 | 41470.4368 | 144 | 72 | 5778.24 | 80.2533 | 0.017796 | 0.0004435 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 80.2533 | 0.017796 | 0.0004435
135615 | 41469.634 | 41470.5014 | 1048 | 1246 | 211393.028 | 169.6573 | 0.65106 | 0.0032277 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 169.6573 | 0.65106 | 0.0032277
135616 | 41469.6937 | 41470.4028 | 277 | 1018 | 75331.0029 | 73.999 | 0.23201 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 73.999 | 0.23201 | 0.00085312
135617 | 41469.791 | 41470.4674 | 1409 | 971 | 277217.5092 | 285.4969 | 0.85379 | 0.0043395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 285.4969 | 0.85379 | 0.0043395
135618 | 41469.6458 | 41470.5757 | 134 | 1336 | 101278.578 | 75.8073 | 0.31192 | 0.0004127 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 75.8073 | 0.31192 | 0.0004127
135619 | 41469.9521 | 41470.566 | 255 | 881 | 24438.7805 | 27.7398 | 0.075268 | 0.00078536 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 27.7398 | 0.075268 | 0.00078536
135620 | 41469.4653 | 41469.5951 | 236 | 184 | 26131.9358 | 142.0214 | 0.080482 | 0.00072684 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 142.0214 | 0.080482 | 0.00072684
135623 | 41469.5361 | 41469.5569 | 35 | 27 | 945 | 35 | 0.0029105 | 0.00010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 35 | 0.0029105 | 0.00010779
135624 | 41471.5139 | 41471.5861 | 454 | 101 | 27337.0096 | 270.6635 | 0.084194 | 0.0013982 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 270.6635 | 0.084194 | 0.0013982
135625 | 41470.4028 | 41471.4965 | 1 | 1572 | 1572 | 1 | 0.0048415 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 1 | 0.0048415 | 3.0798e-06
135626 | 41470.7167 | 41471.5625 | 1 | 1215 | 1215 | 1 | 0.003742 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 1 | 0.003742 | 3.0798e-06
135629 | 41471.3646 | 41471.6139 | 37 | 356 | 13172 | 37 | 0.040568 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | B | 37 | 0.040568 | 0.00011395
135630 | 41471.375 | 41471.6382 | 27 | 376 | 10152 | 27 | 0.031267 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | B | 27 | 0.031267 | 8.3156e-05
135631 | 41471.375 | 41471.6139 | 122 | 341 | 41602 | 122 | 0.12813 | 0.00037574 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | B | 122 | 0.12813 | 0.00037574
135633 | 41471.6535 | 41471.7243 | 1 | 99 | 99 | 1 | 0.0003049 | 3.0798e-06 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 1 | 0.0003049 | 3.0798e-06
135634 | 41471.6979 | 41471.7556 | 2 | 80 | 160 | 2 | 0.00049277 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 2 | 0.00049277 | 6.1597e-06
135635 | 41471.5 | 41471.6701 | 15 | 242 | 3630 | 15 | 0.01118 | 4.6198e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 15 | 0.01118 | 4.6198e-05
135636 | 41469.7486 | 41470.5674 | 19 | 1176 | 22344 | 19 | 0.068816 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 19 | 0.068816 | 5.8517e-05
135637 | 41469.234 | 41469.3111 | 216 | 108 | 23328 | 216 | 0.071847 | 0.00066525 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | B | 216 | 0.071847 | 0.00066525
135638 | 41469.5583 | 41470.6736 | 80 | 1603 | 26260.8531 | 16.3823 | 0.080879 | 0.00024639 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 16.3823 | 0.080879 | 0.00024639
135639 | 41471.8007 | 41471.8549 | 8 | 75 | 600 | 8 | 0.0018479 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 8 | 0.0018479 | 2.4639e-05
135640 | 41469.6639 | 41471.7944 | 44 | 3065 | 134860 | 44 | 0.41535 | 0.00013551 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 44 | 0.41535 | 0.00013551
135641 | 41470.3625 | 41471.5625 | 183 | 1725 | 49306.25 | 28.5833 | 0.15186 | 0.00056361 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 28.5833 | 0.15186 | 0.00056361
135642 | 41469.7917 | 41471.5861 | 95 | 2581 | 46489.9628 | 18.0124 | 0.14318 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 18.0124 | 0.14318 | 0.00029258
135643 | 41470.6604 | 41470.691 | 2306 | 41 | 94546 | 2306 | 0.29119 | 0.0071021 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 2306 | 0.29119 | 0.0071021
135644 | 41469.6458 | 41471.7188 | 30 | 2982 | 89460 | 30 | 0.27552 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 30 | 0.27552 | 9.2395e-05
135645 | 41469.5736 | 41471.3035 | 72 | 2488 | 41601.837 | 16.721 | 0.12813 | 0.00022175 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 16.721 | 0.12813 | 0.00022175
135648 | 41471.6715 | 41471.7014 | 9 | 40 | 360 | 9 | 0.0011087 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 9 | 0.0011087 | 2.7719e-05
135649 | 41472.3958 | 41472.4347 | 52 | 53 | 2756 | 52 | 0.008488 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-17 | 2014 | 2014 | 2013-07-17 | B | 52 | 0.008488 | 0.00016015
135651 | 41471.5792 | 41471.6 | 1 | 27 | 27 | 1 | 8.3156e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 1 | 8.3156e-05 | 3.0798e-06
135652 | 41471.5382 | 41471.5521 | 24 | 17 | 408 | 24 | 0.0012566 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 24 | 0.0012566 | 7.3916e-05
135653 | 41471.375 | 41471.4861 | 4 | 157 | 628 | 4 | 0.0019341 | 1.2319e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 4 | 0.0019341 | 1.2319e-05
135654 | 41471.3792 | 41471.4201 | 34 | 56 | 1904 | 34 | 0.005864 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 34 | 0.005864 | 0.00010471
135655 | 41471.3958 | 41471.4583 | 59 | 87 | 5133 | 59 | 0.015809 | 0.00018171 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 59 | 0.015809 | 0.00018171
135656 | 41469.625 | 41471.4465 | 7 | 2620 | 18340 | 7 | 0.056484 | 2.1559e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 7 | 0.056484 | 2.1559e-05
135657 | 41469.5771 | 41469.6021 | 32 | 33 | 1056 | 32 | 0.0032523 | 9.8555e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 32 | 0.0032523 | 9.8555e-05
135658 | 41471.4257 | 41471.4792 | 323 | 74 | 12290.7273 | 166.0909 | 0.037853 | 0.00099479 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 166.0909 | 0.037853 | 0.00099479
135659 | 41471.3889 | 41471.4431 | 22 | 75 | 1650 | 22 | 0.0050817 | 6.7757e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 22 | 0.0050817 | 6.7757e-05
135660 | 41469.6875 | 41472.5681 | 1148 | 4145 | 418716.9479 | 101.0174 | 1.2896 | 0.0035357 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-14 | 2014 | 2014 | 2013-07-14 | C | 101.0174 | 1.2896 | 0.0035357
135661 | 41470.6667 | 41470.6965 | 40 | 40 | 1600 | 40 | 0.0049277 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | C | 40 | 0.0049277 | 0.00012319
135663 | 41472.3854 | 41472.5951 | 173 | 299 | 51727 | 173 | 0.15931 | 0.00053281 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-17 | 2014 | 2014 | 2013-07-17 | B | 173 | 0.15931 | 0.00053281
135664 | 41472.375 | 41472.6299 | 47 | 364 | 17108 | 47 | 0.05269 | 0.00014475 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-17 | 2014 | 2014 | 2013-07-17 | B | 47 | 0.05269 | 0.00014475
135665 | 41472.5521 | 41472.6042 | 46 | 72 | 3312 | 46 | 0.0102 | 0.00014167 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-17 | 2014 | 2014 | 2013-07-17 | C | 46 | 0.0102 | 0.00014167
135666 | 41471.8465 | 41472.7771 | 44 | 1337 | 58828 | 44 | 0.18118 | 0.00013551 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 44 | 0.18118 | 0.00013551
135671 | 41473.4062 | 41473.484 | 164 | 109 | 17876 | 164 | 0.055055 | 0.00050509 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | B | 164 | 0.055055 | 0.00050509
135673 | 41473.3951 | 41473.5556 | 2 | 228 | 456 | 2 | 0.0014044 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | C | 2 | 0.0014044 | 6.1597e-06
135675 | 41473.3694 | 41473.6528 | 5 | 405 | 2025 | 5 | 0.0062367 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | B | 5 | 0.0062367 | 1.5399e-05
135676 | 41473.3854 | 41473.6479 | 7 | 375 | 2625 | 7 | 0.0080846 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | B | 7 | 0.0080846 | 2.1559e-05
135677 | 41473.3896 | 41473.6431 | 18 | 362 | 6516 | 18 | 0.020068 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | B | 18 | 0.020068 | 5.5437e-05
135678 | 41473.3951 | 41473.4861 | 47 | 128 | 6016 | 47 | 0.018528 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | C | 47 | 0.018528 | 0.00014475
135679 | 41474.4736 | 41474.4854 | 193 | 14 | 2702 | 193 | 0.0083217 | 0.00059441 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 193 | 0.0083217 | 0.00059441
135680 | 41474.4542 | 41474.4986 | 2448 | 61 | 149328 | 2448 | 0.45991 | 0.0075395 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 2448 | 0.45991 | 0.0075395
135681 | 41471.4132 | 41474.5972 | 5 | 4582 | 22910 | 5 | 0.070559 | 1.5399e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-16 | 2014 | 2014 | 2013-07-16 | C | 5 | 0.070559 | 1.5399e-05
135683 | 41474.5243 | 41474.575 | 2 | 70 | 140 | 2 | 0.00043118 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 2 | 0.00043118 | 6.1597e-06
135684 | 41474.5326 | 41474.6285 | 193 | 135 | 16059.1304 | 118.9565 | 0.04946 | 0.00059441 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 118.9565 | 0.04946 | 0.00059441
135686 | 41474.6979 | 41474.75 | 65 | 72 | 4680 | 65 | 0.014414 | 0.00020019 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 65 | 0.014414 | 0.00020019
135687 | 41474.7583 | 41474.9021 | 369 | 204 | 75276 | 369 | 0.23184 | 0.0011365 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 369 | 0.23184 | 0.0011365
135688 | 41474.7243 | 41474.8639 | 279 | 198 | 45273.0448 | 228.6517 | 0.13943 | 0.00085928 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 228.6517 | 0.13943 | 0.00085928
135689 | 41474.7583 | 41474.7611 | 321 | 1 | 321 | 321 | 0.00098863 | 0.00098863 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 321 | 0.00098863 | 0.00098863
135690 | 41474.9319 | 41475.1188 | 414 | 266 | 49215.9331 | 185.0223 | 0.15158 | 0.0012751 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 185.0223 | 0.15158 | 0.0012751
135691 | 41474.4792 | 41474.6222 | 34 | 203 | 6902 | 34 | 0.021257 | 0.00010471 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | B | 34 | 0.021257 | 0.00010471
135693 | 41474.3681 | 41474.6271 | 6 | 370 | 2220 | 6 | 0.0068372 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | B | 6 | 0.0068372 | 1.8479e-05
135695 | 41475.375 | 41475.5132 | 3 | 196 | 588 | 3 | 0.0018109 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-20 | 2014 | 2014 | 2013-07-20 | B | 3 | 0.0018109 | 9.2395e-06
135696 | 41475.375 | 41475.6153 | 2 | 343 | 686 | 2 | 0.0021128 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-20 | 2014 | 2014 | 2013-07-20 | B | 2 | 0.0021128 | 6.1597e-06
135698 | 41475.6646 | 41475.7188 | 113 | 75 | 8007.6923 | 106.7692 | 0.024662 | 0.00034802 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-20 | 2014 | 2014 | 2013-07-20 | C | 106.7692 | 0.024662 | 0.00034802
135699 | 41475.4792 | 41475.8958 | 22 | 597 | 3283.5 | 5.5 | 0.010113 | 6.7757e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-20 | 2014 | 2014 | 2013-07-20 | C | 5.5 | 0.010113 | 6.7757e-05
135701 | 41474.6937 | 41474.7396 | 907 | 63 | 37492.6364 | 595.1212 | 0.11547 | 0.0027934 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 595.1212 | 0.11547 | 0.0027934
135702 | 41476.4285 | 41476.4437 | 22 | 19 | 418 | 22 | 0.0012874 | 6.7757e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-21 | 2014 | 2014 | 2013-07-21 | C | 22 | 0.0012874 | 6.7757e-05
135703 | 41476.4167 | 41476.5938 | 37 | 252 | 9324 | 37 | 0.028716 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-21 | 2014 | 2014 | 2013-07-21 | B | 37 | 0.028716 | 0.00011395
135705 | 41476.9069 | 41476.9861 | 24 | 111 | 2664 | 24 | 0.0082047 | 7.3916e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-21 | 2014 | 2014 | 2013-07-21 | C | 24 | 0.0082047 | 7.3916e-05
135706 | 41476.3542 | 41476.3875 | 116 | 45 | 5220 | 116 | 0.016077 | 0.00035726 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-21 | 2014 | 2014 | 2013-07-21 | C | 116 | 0.016077 | 0.00035726
135708 | 41474.5333 | 41474.7007 | 820 | 238 | 101286.2822 | 425.5726 | 0.31195 | 0.0025255 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | C | 425.5726 | 0.31195 | 0.0025255
135710 | 41477.6979 | 41477.7354 | 11 | 51 | 561 | 11 | 0.0017278 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | C | 11 | 0.0017278 | 3.3878e-05
135711 | 41477.3958 | 41477.5576 | 30 | 230 | 6900 | 30 | 0.021251 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | B | 30 | 0.021251 | 9.2395e-05
135712 | 41477.7528 | 41477.8174 | 794 | 90 | 64763.2258 | 719.5914 | 0.19946 | 0.0024454 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | C | 719.5914 | 0.19946 | 0.0024454
135713 | 41477.809 | 41477.9167 | 246 | 152 | 37392 | 246 | 0.11516 | 0.00075764 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | C | 246 | 0.11516 | 0.00075764
135714 | 41477.8056 | 41478.0104 | 168 | 292 | 7576.1627 | 25.9458 | 0.023333 | 0.00051741 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | C | 25.9458 | 0.023333 | 0.00051741
135716 | 41478.375 | 41478.5278 | 12 | 217 | 2604 | 12 | 0.0080199 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | B | 12 | 0.0080199 | 3.6958e-05
135718 | 41473.5417 | 41473.6458 | 2 | 147 | 294 | 2 | 0.00090547 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-18 | 2014 | 2014 | 2013-07-18 | B | 2 | 0.00090547 | 6.1597e-06
135719 | 41464.5007 | 41464.5167 | 2 | 20 | 40 | 2 | 0.00012319 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-09 | 2014 | 2014 | 2013-07-09 | B | 2 | 0.00012319 | 6.1597e-06
135721 | 41478.4007 | 41478.4792 | 1 | 110 | 110 | 1 | 0.00033878 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | B | 1 | 0.00033878 | 3.0798e-06
135723 | 41465.9375 | 41466.0611 | 1 | 175 | 175 | 1 | 0.00053897 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-10 | 2014 | 2014 | 2013-07-10 | B | 1 | 0.00053897 | 3.0798e-06
135724 | 41474.9889 | 41475.0382 | 338 | 68 | 22984 | 338 | 0.070787 | 0.001041 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | B | 338 | 0.070787 | 0.001041
135726 | 41478.534 | 41478.5743 | 2 | 55 | 110 | 2 | 0.00033878 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | B | 2 | 0.00033878 | 6.1597e-06
135729 | 41478.375 | 41478.625 | 18 | 357 | 6426 | 18 | 0.019791 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | B | 18 | 0.019791 | 5.5437e-05
135734 | 41478.8181 | 41478.825 | 794 | 7 | 5558 | 794 | 0.017118 | 0.0024454 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | C | 794 | 0.017118 | 0.0024454
135736 | 41479.0104 | 41479.1875 | 794 | 252 | 81839.7176 | 324.7608 | 0.25205 | 0.0024454 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | C | 324.7608 | 0.25205 | 0.0024454
135737 | 41479.1104 | 41479.2042 | 1048 | 132 | 63693.4222 | 482.5259 | 0.19617 | 0.0032277 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | C | 482.5259 | 0.19617 | 0.0032277
135738 | 41479.1361 | 41479.2778 | 558 | 201 | 44108.6618 | 219.4461 | 0.13585 | 0.0017186 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | C | 219.4461 | 0.13585 | 0.0017186
135739 | 41479.375 | 41479.4938 | 16 | 168 | 2688 | 16 | 0.0082786 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | B | 16 | 0.0082786 | 4.9277e-05
135740 | 41479.3764 | 41479.4931 | 210 | 165 | 11034.375 | 66.875 | 0.033984 | 0.00064677 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | C | 66.875 | 0.033984 | 0.00064677
135742 | 41470.3924 | 41470.5257 | 149 | 189 | 28161 | 149 | 0.086731 | 0.0004589 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-15 | 2014 | 2014 | 2013-07-15 | B | 149 | 0.086731 | 0.0004589
135744 | 41479.3958 | 41479.6042 | 96 | 297 | 19382.22 | 65.26 | 0.059694 | 0.00029566 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | B | 65.26 | 0.059694 | 0.00029566
135748 | 41479.375 | 41479.5986 | 69 | 319 | 22011 | 69 | 0.06779 | 0.00021251 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | B | 69 | 0.06779 | 0.00021251
135749 | 41479.375 | 41479.6528 | 56 | 397 | 22232 | 56 | 0.068471 | 0.00017247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-24 | 2014 | 2014 | 2013-07-24 | B | 56 | 0.068471 | 0.00017247
135751 | 41480.3868 | 41480.4236 | 130 | 50 | 6500 | 130 | 0.020019 | 0.00040038 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 130 | 0.020019 | 0.00040038
135752 | 41480.4236 | 41480.4333 | 412 | 11 | 4532 | 412 | 0.013958 | 0.0012689 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 412 | 0.013958 | 0.0012689
135756 | 41480.3646 | 41480.6215 | 47 | 367 | 17249 | 47 | 0.053124 | 0.00014475 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | B | 47 | 0.053124 | 0.00014475
135758 | 41480.3778 | 41480.584 | 36 | 294 | 10584 | 36 | 0.032597 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | B | 36 | 0.032597 | 0.00011087
135759 | 41480.5 | 41480.5729 | 5 | 102 | 510 | 5 | 0.0015707 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | B | 5 | 0.0015707 | 1.5399e-05
135760 | 41477.4535 | 41480.4833 | 2 | 4360 | 8720 | 2 | 0.026856 | 6.1597e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-07-22 | 2014 | 2014 | 2013-07-22 | C | 2 | 0.026856 | 6.1597e-06
135761 | 41480.6431 | 41480.6514 | 904 | 9 | 8136 | 904 | 0.025058 | 0.0027842 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 904 | 0.025058 | 0.0027842
135762 | 41480.3958 | 41480.4583 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | B | 2 | 0.00053589 | 6.1597e-06
135763 | 41480.434 | 41480.4688 | 629 | 47 | 29563 | 629 | 0.091049 | 0.0019372 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 629 | 0.091049 | 0.0019372
135764 | 41480.5139 | 41480.5625 | 25 | 67 | 1675 | 25 | 0.0051587 | 7.6996e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 25 | 0.0051587 | 7.6996e-05
135765 | 41480.434 | 41480.5167 | 11 | 116 | 1276 | 11 | 0.0039299 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 11 | 0.0039299 | 3.3878e-05
135766 | 41480.6431 | 41480.7632 | 54 | 170 | 5567.7457 | 32.7514 | 0.017148 | 0.00016631 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 32.7514 | 0.017148 | 0.00016631
135768 | 41480.9271 | 41481.0431 | 904 | 164 | 83559.4731 | 509.509 | 0.25735 | 0.0027842 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 509.509 | 0.25735 | 0.0027842
135769 | 41481.4361 | 41481.6944 | 40 | 369 | 14760 | 40 | 0.045458 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-26 | 2014 | 2014 | 2013-07-26 | B | 40 | 0.045458 | 0.00012319
135771 | 41481.3958 | 41481.4583 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-26 | 2014 | 2014 | 2013-07-26 | B | 3 | 0.00080384 | 9.2395e-06
135772 | 41481.5 | 41481.5764 | 4 | 107 | 428 | 4 | 0.0013182 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-26 | 2014 | 2014 | 2013-07-26 | B | 4 | 0.0013182 | 1.2319e-05
135774 | 41481.375 | 41481.5104 | 5 | 192 | 960 | 5 | 0.0029566 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-26 | 2014 | 2014 | 2013-07-26 | C | 5 | 0.0029566 | 1.5399e-05
135777 | 41482.1417 | 41482.5194 | 210 | 541 | 113610 | 210 | 0.3499 | 0.00064677 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-27 | 2014 | 2014 | 2013-07-27 | C | 210 | 0.3499 | 0.00064677
135778 | 41482.1813 | 41482.5132 | 290 | 475 | 137750 | 290 | 0.42425 | 0.00089315 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-27 | 2014 | 2014 | 2013-07-27 | C | 290 | 0.42425 | 0.00089315
135779 | 41483.5493 | 41483.6104 | 471 | 85 | 20768.9773 | 244.3409 | 0.063965 | 0.0014506 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-28 | 2014 | 2014 | 2013-07-28 | C | 244.3409 | 0.063965 | 0.0014506
135780 | 41483.659 | 41483.7069 | 5 | 66 | 330 | 5 | 0.0010163 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-28 | 2014 | 2014 | 2013-07-28 | C | 5 | 0.0010163 | 1.5399e-05
135783 | 41482.4653 | 41482.5312 | 2 | 92 | 184 | 2 | 0.00056669 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-27 | 2014 | 2014 | 2013-07-27 | C | 2 | 0.00056669 | 6.1597e-06
135784 | 41478.6104 | 41480.691 | 1 | 2993 | 2993 | 1 | 0.009218 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-23 | 2014 | 2014 | 2013-07-23 | C | 1 | 0.009218 | 3.0798e-06
135786 | 41483.8264 | 41483.8854 | 34 | 82 | 2788 | 34 | 0.0085866 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-28 | 2014 | 2014 | 2013-07-28 | C | 34 | 0.0085866 | 0.00010471
135789 | 41480.4396 | 41480.459 | 25 | 25 | 625 | 25 | 0.0019249 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-25 | 2014 | 2014 | 2013-07-25 | C | 25 | 0.0019249 | 7.6996e-05
135790 | 41483.75 | 41483.7674 | 22 | 22 | 484 | 22 | 0.0014906 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-28 | 2014 | 2014 | 2013-07-28 | C | 22 | 0.0014906 | 6.7757e-05
135791 | 41483.0417 | 41483.2667 | 1 | 321 | 321 | 1 | 0.00098863 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-28 | 2014 | 2014 | 2013-07-28 | C | 1 | 0.00098863 | 3.0798e-06
135792 | 41484.2049 | 41484.3528 | 146 | 210 | 15836.7606 | 75.4131 | 0.048775 | 0.00044966 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | C | 75.4131 | 0.048775 | 0.00044966
135793 | 41484.3167 | 41484.3583 | 1130 | 57 | 45084.15 | 790.95 | 0.13885 | 0.0034802 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | C | 790.95 | 0.13885 | 0.0034802
135795 | 41484.3958 | 41484.4583 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | B | 2 | 0.00053589 | 6.1597e-06
135796 | 41484.5 | 41484.5972 | 2 | 137 | 274 | 2 | 0.00084388 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | B | 2 | 0.00084388 | 6.1597e-06
135797 | 41484.5417 | 41484.6042 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | C | 2 | 0.00053589 | 6.1597e-06
135798 | 41484.2812 | 41484.3375 | 221 | 78 | 14798.8148 | 189.7284 | 0.045578 | 0.00068065 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | C | 189.7284 | 0.045578 | 0.00068065
135799 | 41484.2333 | 41484.6333 | 277 | 573 | 31879.0938 | 55.6354 | 0.098183 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-29 | 2014 | 2014 | 2013-07-29 | C | 55.6354 | 0.098183 | 0.00085312
135800 | 41485.0569 | 41485.1764 | 316 | 169 | 22381.6919 | 132.436 | 0.068932 | 0.00097323 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 132.436 | 0.068932 | 0.00097323
135801 | 41474.4014 | 41474.4556 | 10 | 75 | 750 | 10 | 0.0023099 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | B | 10 | 0.0023099 | 3.0798e-05
135803 | 41474.5347 | 41474.5833 | 2 | 67 | 134 | 2 | 0.0004127 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-19 | 2014 | 2014 | 2013-07-19 | B | 2 | 0.0004127 | 6.1597e-06
135805 | 41485.5035 | 41485.6111 | 9 | 152 | 1368 | 9 | 0.0042132 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 9 | 0.0042132 | 2.7719e-05
135807 | 41485.3292 | 41485.3451 | 123 | 20 | 2460 | 123 | 0.0075764 | 0.00037882 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 123 | 0.0075764 | 0.00037882
135810 | 41485.2701 | 41485.3389 | 192 | 96 | 13228.6061 | 137.798 | 0.040742 | 0.00059133 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 137.798 | 0.040742 | 0.00059133
135812 | 41485.4236 | 41485.625 | 2 | 287 | 574 | 2 | 0.0017678 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | B | 2 | 0.0017678 | 6.1597e-06
135813 | 41485.375 | 41485.5736 | 8 | 283 | 2264 | 8 | 0.0069728 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | B | 8 | 0.0069728 | 2.4639e-05
135815 | 41475.3951 | 41475.5347 | 20 | 198 | 3960 | 20 | 0.012196 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-20 | 2014 | 2014 | 2013-07-20 | B | 20 | 0.012196 | 6.1597e-05
135820 | 41485.341 | 41485.35 | 19 | 10 | 190 | 19 | 0.00058517 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 19 | 0.00058517 | 5.8517e-05
135823 | 41486.5639 | 41486.5861 | 347 | 29 | 10063 | 347 | 0.030992 | 0.0010687 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-07-31 | 2014 | 2014 | 2013-07-31 | C | 347 | 0.030992 | 0.0010687
135825 | 41486.375 | 41486.6444 | 13 | 385 | 5005 | 13 | 0.015415 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-31 | 2014 | 2014 | 2013-07-31 | B | 13 | 0.015415 | 4.0038e-05
135828 | 41485.2431 | 41485.2549 | 236 | 14 | 3304 | 236 | 0.010176 | 0.00072684 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-07-30 | 2014 | 2014 | 2013-07-30 | C | 236 | 0.010176 | 0.00072684
135831 | 41487.4208 | 41487.4812 | 50 | 84 | 4200 | 50 | 0.012935 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | B | 50 | 0.012935 | 0.00015399
135832 | 41487.441 | 41487.5104 | 3 | 97 | 291 | 3 | 0.00089623 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | C | 3 | 0.00089623 | 9.2395e-06
135833 | 41487.3986 | 41487.5153 | 2 | 165 | 330 | 2 | 0.0010163 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | B | 2 | 0.0010163 | 6.1597e-06
135834 | 41487.3958 | 41487.5389 | 34 | 203 | 6902 | 34 | 0.021257 | 0.00010471 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | B | 34 | 0.021257 | 0.00010471
135835 | 41487.3958 | 41487.5493 | 146 | 218 | 31828 | 146 | 0.098025 | 0.00044966 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | B | 146 | 0.098025 | 0.00044966
135836 | 41487.5938 | 41487.6306 | 667 | 50 | 33043.3962 | 660.8679 | 0.10177 | 0.0020543 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | C | 660.8679 | 0.10177 | 0.0020543
135838 | 41487.375 | 41487.6368 | 150 | 374 | 56100 | 150 | 0.17278 | 0.00046198 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | B | 150 | 0.17278 | 0.00046198
135840 | 41487.7951 | 41488.1097 | 30 | 450 | 10807.947 | 24.0177 | 0.033287 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-01 | 2014 | 2014 | 2013-08-01 | C | 24.0177 | 0.033287 | 9.2395e-05
135841 | 41488.1299 | 41488.2028 | 238 | 102 | 20261.0857 | 198.6381 | 0.062401 | 0.000733 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 198.6381 | 0.062401 | 0.000733
135847 | 41488.4 | 41488.5104 | 11 | 156 | 1716 | 11 | 0.005285 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | B | 11 | 0.005285 | 3.3878e-05
135849 | 41488.5201 | 41488.5549 | 681 | 47 | 32007 | 681 | 0.098576 | 0.0020974 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 681 | 0.098576 | 0.0020974
135851 | 41488.684 | 41488.6951 | 9 | 13 | 117 | 9 | 0.00036034 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 9 | 0.00036034 | 2.7719e-05
135852 | 41488.0382 | 41488.5799 | 146 | 777 | 9308.0615 | 11.9795 | 0.028667 | 0.00044966 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 11.9795 | 0.028667 | 0.00044966
135853 | 41489.0625 | 41489.1368 | 120 | 104 | 12480 | 120 | 0.038436 | 0.00036958 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | B | 120 | 0.038436 | 0.00036958
135854 | 41489.1472 | 41489.2097 | 247 | 87 | 21489 | 247 | 0.066183 | 0.00076072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | B | 247 | 0.066183 | 0.00076072
135855 | 41488.8139 | 41488.8382 | 34 | 32 | 1088 | 34 | 0.0033509 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 34 | 0.0033509 | 0.00010471
135856 | 41488.4965 | 41488.5083 | 32 | 14 | 448 | 32 | 0.0013798 | 9.8555e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-02 | 2014 | 2014 | 2013-08-02 | C | 32 | 0.0013798 | 9.8555e-05
135857 | 41489.2417 | 41489.2764 | 268 | 47 | 12596 | 268 | 0.038794 | 0.0008254 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | C | 268 | 0.038794 | 0.0008254
135859 | 41489.3542 | 41489.5 | 70 | 207 | 14490 | 70 | 0.044627 | 0.00021559 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | B | 70 | 0.044627 | 0.00021559
135861 | 41489.3542 | 41489.6062 | 1 | 360 | 360 | 1 | 0.0011087 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | B | 1 | 0.0011087 | 3.0798e-06
135864 | 41490.2396 | 41490.4049 | 156 | 235 | 20773.8025 | 88.3992 | 0.06398 | 0.00048046 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-04 | 2014 | 2014 | 2013-08-04 | C | 88.3992 | 0.06398 | 0.00048046
135866 | 41490.25 | 41490.3333 | 10 | 117 | 1170 | 10 | 0.0036034 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-04 | 2014 | 2014 | 2013-08-04 | B | 10 | 0.0036034 | 3.0798e-05
135867 | 41490.3986 | 41490.6771 | 1 | 398 | 398 | 1 | 0.0012258 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-04 | 2014 | 2014 | 2013-08-04 | C | 1 | 0.0012258 | 3.0798e-06
135868 | 41489.5625 | 41489.8222 | 5 | 371 | 1855 | 5 | 0.0057131 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-03 | 2014 | 2014 | 2013-08-03 | C | 5 | 0.0057131 | 1.5399e-05
135872 | 41491.2833 | 41491.2965 | 311 | 16 | 4976 | 311 | 0.015325 | 0.00095783 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 311 | 0.015325 | 0.00095783
135873 | 41491.3444 | 41491.3479 | 284 | 2 | 568 | 284 | 0.0017494 | 0.00087468 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 284 | 0.0017494 | 0.00087468
135874 | 41491.4278 | 41491.4556 | 27 | 37 | 999 | 27 | 0.0030768 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 27 | 0.0030768 | 8.3156e-05
135875 | 41491.3799 | 41491.4861 | 3 | 150 | 450 | 3 | 0.0013859 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | B | 3 | 0.0013859 | 9.2395e-06
135876 | 41491.4278 | 41491.4556 | 38 | 37 | 1406 | 38 | 0.0043303 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 38 | 0.0043303 | 0.00011703
135877 | 41491.3694 | 41491.4 | 31 | 41 | 1271 | 31 | 0.0039145 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 31 | 0.0039145 | 9.5475e-05
135878 | 41490.6042 | 41491.7569 | 2 | 1657 | 3314 | 2 | 0.010207 | 6.1597e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-04 | 2014 | 2014 | 2013-08-04 | C | 2 | 0.010207 | 6.1597e-06
135879 | 41491.9792 | 41492.0146 | 55 | 48 | 2640 | 55 | 0.0081308 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-05 | 2014 | 2014 | 2013-08-05 | C | 55 | 0.0081308 | 0.00016939
135880 | 41492.2653 | 41492.391 | 1061 | 178 | 95786.6188 | 538.1271 | 0.29501 | 0.0032677 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 538.1271 | 0.29501 | 0.0032677
135883 | 41492.375 | 41492.6188 | 6 | 348 | 2088 | 6 | 0.0064307 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 6 | 0.0064307 | 1.8479e-05
135884 | 41492.3542 | 41492.609 | 59 | 364 | 21476 | 59 | 0.066143 | 0.00018171 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 59 | 0.066143 | 0.00018171
135885 | 41492.3646 | 41492.4979 | 225 | 189 | 42525 | 225 | 0.13097 | 0.00069296 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 225 | 0.13097 | 0.00069296
135886 | 41459.4618 | 41459.6396 | 161 | 253 | 40733 | 161 | 0.12545 | 0.00049585 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-07-04 | 2014 | 2014 | 2013-07-04 | B | 161 | 0.12545 | 0.00049585
135887 | 41492.3646 | 41492.6201 | 83 | 365 | 30295 | 83 | 0.093304 | 0.00025563 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 83 | 0.093304 | 0.00025563
135889 | 41492.3854 | 41492.6181 | 123 | 332 | 40836 | 123 | 0.12577 | 0.00037882 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 123 | 0.12577 | 0.00037882
135891 | 41492.3542 | 41492.6424 | 45 | 412 | 3395.2771 | 8.241 | 0.010457 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | B | 8.241 | 0.010457 | 0.00013859
135892 | 41492.5236 | 41492.6424 | 858 | 168 | 57582.7368 | 342.7544 | 0.17735 | 0.0026425 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 342.7544 | 0.17735 | 0.0026425
135893 | 41492.4347 | 41492.5417 | 427 | 151 | 49455.4416 | 327.5195 | 0.15231 | 0.0013151 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 327.5195 | 0.15231 | 0.0013151
135894 | 41492.691 | 41492.7396 | 904 | 67 | 41384.9429 | 617.6857 | 0.12746 | 0.0027842 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 617.6857 | 0.12746 | 0.0027842
135895 | 41492.941 | 41492.9736 | 286 | 44 | 12584 | 286 | 0.038757 | 0.00088083 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 286 | 0.038757 | 0.00088083
135896 | 41492.8861 | 41493.0444 | 309 | 225 | 39592.1053 | 175.9649 | 0.12194 | 0.00095167 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-06 | 2014 | 2014 | 2013-08-06 | C | 175.9649 | 0.12194 | 0.00095167
135898 | 41493.1014 | 41493.1125 | 236 | 13 | 3068 | 236 | 0.009449 | 0.00072684 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | C | 236 | 0.009449 | 0.00072684
135899 | 41493.3868 | 41493.3986 | 125 | 14 | 1750 | 125 | 0.0053897 | 0.00038498 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 125 | 0.0053897 | 0.00038498
135900 | 41493.5486 | 41493.5667 | 8 | 23 | 184 | 8 | 0.00056669 | 2.4639e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | C | 8 | 0.00056669 | 2.4639e-05
135901 | 41493.5208 | 41493.5556 | 42 | 47 | 1974 | 42 | 0.0060796 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 42 | 0.0060796 | 0.00012935
135903 | 41493.3882 | 41493.625 | 24 | 338 | 8112 | 24 | 0.024984 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 24 | 0.024984 | 7.3916e-05
135905 | 41493.459 | 41493.625 | 2 | 236 | 472 | 2 | 0.0014537 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 2 | 0.0014537 | 6.1597e-06
135906 | 41493.4104 | 41493.5625 | 19 | 216 | 4104 | 19 | 0.01264 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 19 | 0.01264 | 5.8517e-05
135908 | 41493.3944 | 41493.6354 | 50 | 344 | 17200 | 50 | 0.052973 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 50 | 0.052973 | 0.00015399
135909 | 41493.375 | 41493.625 | 276 | 357 | 55573 | 155.6667 | 0.17116 | 0.00085004 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 155.6667 | 0.17116 | 0.00085004
135912 | 41494.2708 | 41494.3035 | 5 | 44 | 220 | 5 | 0.00067757 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-08 | 2014 | 2014 | 2013-08-08 | C | 5 | 0.00067757 | 1.5399e-05
135913 | 41494.4062 | 41494.5264 | 6 | 170 | 1020 | 6 | 0.0031414 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-08 | 2014 | 2014 | 2013-08-08 | C | 6 | 0.0031414 | 1.8479e-05
135915 | 41494.4583 | 41494.5035 | 135 | 62 | 8370 | 135 | 0.025778 | 0.00041578 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-08 | 2014 | 2014 | 2013-08-08 | C | 135 | 0.025778 | 0.00041578
135917 | 41494.4014 | 41494.5729 | 38 | 244 | 9272 | 38 | 0.028556 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-08 | 2014 | 2014 | 2013-08-08 | B | 38 | 0.028556 | 0.00011703
135921 | 41494.3715 | 41494.6424 | 54 | 387 | 16680.6923 | 43.1026 | 0.051374 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-08 | 2014 | 2014 | 2013-08-08 | B | 43.1026 | 0.051374 | 0.00016631
135926 | 41495.1264 | 41495.6097 | 205 | 693 | 13137.1293 | 18.9569 | 0.04046 | 0.00063137 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | C | 18.9569 | 0.04046 | 0.00063137
135928 | 41495.375 | 41495.484 | 193 | 154 | 29722 | 193 | 0.091539 | 0.00059441 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | B | 193 | 0.091539 | 0.00059441
135929 | 41495.4236 | 41495.4924 | 5 | 96 | 480 | 5 | 0.0014783 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | C | 5 | 0.0014783 | 1.5399e-05
135930 | 41495.6285 | 41495.6729 | 43 | 61 | 2114.9844 | 34.6719 | 0.0065138 | 0.00013243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | C | 34.6719 | 0.0065138 | 0.00013243
135934 | 41493.4194 | 41493.6076 | 2 | 268 | 536 | 2 | 0.0016508 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-07 | 2014 | 2014 | 2013-08-07 | B | 2 | 0.0016508 | 6.1597e-06
135937 | 41495.825 | 41495.9007 | 361 | 106 | 13948.2385 | 131.5872 | 0.042958 | 0.0011118 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | C | 131.5872 | 0.042958 | 0.0011118
135940 | 41496.4437 | 41496.4993 | 15 | 77 | 1155 | 15 | 0.0035572 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-10 | 2014 | 2014 | 2013-08-10 | C | 15 | 0.0035572 | 4.6198e-05
135941 | 41496.3958 | 41496.5993 | 70 | 290 | 20300 | 70 | 0.062521 | 0.00021559 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-10 | 2014 | 2014 | 2013-08-10 | B | 70 | 0.062521 | 0.00021559
135942 | 41496.5278 | 41496.6007 | 4 | 102 | 408 | 4 | 0.0012566 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-10 | 2014 | 2014 | 2013-08-10 | C | 4 | 0.0012566 | 1.2319e-05
135945 | 41497.2076 | 41497.4757 | 517 | 383 | 18865.2306 | 49.2565 | 0.058102 | 0.0015923 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-11 | 2014 | 2014 | 2013-08-11 | C | 49.2565 | 0.058102 | 0.0015923
135946 | 41497.2097 | 41497.2132 | 904 | 2 | 1686 | 843 | 0.0051926 | 0.0027842 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-11 | 2014 | 2014 | 2013-08-11 | C | 843 | 0.0051926 | 0.0027842
135950 | 41497.3542 | 41497.4889 | 225 | 191 | 42975 | 225 | 0.13236 | 0.00069296 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-11 | 2014 | 2014 | 2013-08-11 | B | 225 | 0.13236 | 0.00069296
135951 | 41498.0396 | 41498.1764 | 456 | 194 | 36789.0964 | 189.6345 | 0.1133 | 0.0014044 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | C | 189.6345 | 0.1133 | 0.0014044
135952 | 41498.4549 | 41498.5243 | 2 | 97 | 194 | 2 | 0.00059749 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | B | 2 | 0.00059749 | 6.1597e-06
135954 | 41498.566 | 41498.6181 | 26 | 72 | 1872 | 26 | 0.0057655 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | C | 26 | 0.0057655 | 8.0076e-05
135957 | 41498.4174 | 41498.4382 | 643 | 27 | 17361 | 643 | 0.053469 | 0.0019803 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | C | 643 | 0.053469 | 0.0019803
135958 | 41498.3542 | 41498.4375 | 4 | 117 | 468 | 4 | 0.0014414 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | B | 4 | 0.0014414 | 1.2319e-05
135959 | 41499.3854 | 41499.5521 | 17 | 237 | 4029 | 17 | 0.012409 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | B | 17 | 0.012409 | 5.2357e-05
135960 | 41499.425 | 41499.55 | 1 | 177 | 177 | 1 | 0.00054513 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | B | 1 | 0.00054513 | 3.0798e-06
135961 | 41499.375 | 41499.6167 | 24 | 345 | 8280 | 24 | 0.025501 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | B | 24 | 0.025501 | 7.3916e-05
135964 | 41499.3646 | 41499.7083 | 6 | 492 | 2952 | 6 | 0.0090917 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | B | 6 | 0.0090917 | 1.8479e-05
135965 | 41499.9833 | 41500.0486 | 12 | 91 | 1092 | 12 | 0.0033632 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | C | 12 | 0.0033632 | 3.6958e-05
135966 | 41499.725 | 41499.7701 | 15 | 62 | 930 | 15 | 0.0028643 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | C | 15 | 0.0028643 | 4.6198e-05
135967 | 41498.7028 | 41498.7167 | 38 | 17 | 646 | 38 | 0.0019896 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-12 | 2014 | 2014 | 2013-08-12 | C | 38 | 0.0019896 | 0.00011703
135968 | 41500.3056 | 41500.5236 | 191 | 311 | 15647.0637 | 50.3121 | 0.04819 | 0.00058825 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | C | 50.3121 | 0.04819 | 0.00058825
135971 | 41500.3958 | 41500.5715 | 72 | 250 | 18000 | 72 | 0.055437 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | B | 72 | 0.055437 | 0.00022175
135972 | 41499.4118 | 41499.6208 | 2 | 298 | 596 | 2 | 0.0018356 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-13 | 2014 | 2014 | 2013-08-13 | B | 2 | 0.0018356 | 6.1597e-06
135973 | 41500.3833 | 41500.6 | 38 | 309 | 11742 | 38 | 0.036164 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | B | 38 | 0.036164 | 0.00011703
135974 | 41500.3854 | 41500.6236 | 6 | 340 | 2040 | 6 | 0.0062829 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | B | 6 | 0.0062829 | 1.8479e-05
135975 | 41500.3542 | 41500.6438 | 104 | 414 | 21502.1871 | 51.9376 | 0.066223 | 0.0003203 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | B | 51.9376 | 0.066223 | 0.0003203
135976 | 41500.5889 | 41500.6576 | 148 | 96 | 14208 | 148 | 0.043758 | 0.00045582 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | C | 148 | 0.043758 | 0.00045582
135977 | 41500.6764 | 41500.6958 | 20 | 25 | 500 | 20 | 0.0015399 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | C | 20 | 0.0015399 | 6.1597e-05
135978 | 41500.7764 | 41500.9153 | 751 | 197 | 44852.96 | 227.68 | 0.13814 | 0.002313 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | C | 227.68 | 0.13814 | 0.002313
135983 | 41501.3924 | 41501.4403 | 32 | 66 | 2112 | 32 | 0.0065046 | 9.8555e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | C | 32 | 0.0065046 | 9.8555e-05
135985 | 41501.2799 | 41501.4569 | 15 | 252 | 3780 | 15 | 0.011642 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | C | 15 | 0.011642 | 4.6198e-05
135988 | 41501.3667 | 41501.6556 | 32 | 413 | 13216 | 32 | 0.040703 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | B | 32 | 0.040703 | 9.8555e-05
135989 | 41500.375 | 41500.6236 | 67 | 355 | 23785 | 67 | 0.073254 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-14 | 2014 | 2014 | 2013-08-14 | B | 67 | 0.073254 | 0.00020635
135993 | 41501.4035 | 41501.6667 | 1 | 376 | 376 | 1 | 0.001158 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | B | 1 | 0.001158 | 3.0798e-06
135998 | 41501.4653 | 41501.4757 | 13 | 12 | 156 | 13 | 0.00048046 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | C | 13 | 0.00048046 | 4.0038e-05
135999 | 41501.375 | 41501.5458 | 222 | 243 | 53946 | 222 | 0.16615 | 0.00068372 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | B | 222 | 0.16615 | 0.00068372
136000 | 41502.3639 | 41502.3667 | 398 | 1 | 398 | 398 | 0.0012258 | 0.0012258 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 398 | 0.0012258 | 0.0012258
136004 | 41502.4014 | 41502.5264 | 5 | 177 | 885 | 5 | 0.0027257 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 5 | 0.0027257 | 1.5399e-05
136005 | 41502.5007 | 41502.5896 | 255 | 125 | 16812.5 | 134.5 | 0.05178 | 0.00078536 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 134.5 | 0.05178 | 0.00078536
136008 | 41502.5222 | 41502.6479 | 1395 | 178 | 104021.8232 | 584.3923 | 0.32037 | 0.0042964 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 584.3923 | 0.32037 | 0.0042964
136010 | 41501.3646 | 41501.6458 | 61 | 402 | 24522 | 61 | 0.075524 | 0.00018787 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-15 | 2014 | 2014 | 2013-08-15 | B | 61 | 0.075524 | 0.00018787
136011 | 41502.5854 | 41502.6514 | 161 | 92 | 13014.6105 | 141.4632 | 0.040083 | 0.00049585 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 141.4632 | 0.040083 | 0.00049585
136015 | 41502.6056 | 41502.766 | 716 | 228 | 45682.9091 | 200.3636 | 0.1407 | 0.0022052 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 200.3636 | 0.1407 | 0.0022052
136016 | 41502.8576 | 41502.875 | 30 | 22 | 660 | 30 | 0.0020327 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | C | 30 | 0.0020327 | 9.2395e-05
136017 | 41503.5007 | 41503.5618 | 27 | 85 | 2295 | 27 | 0.0070682 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 27 | 0.0070682 | 8.3156e-05
136018 | 41503.3611 | 41503.3826 | 83 | 28 | 2324 | 83 | 0.0071576 | 0.00025563 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 83 | 0.0071576 | 0.00025563
136019 | 41503.3944 | 41503.4049 | 268 | 12 | 3216 | 268 | 0.0099048 | 0.0008254 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 268 | 0.0099048 | 0.0008254
136020 | 41503.4799 | 41503.6618 | 280 | 259 | 23682.6832 | 91.4389 | 0.072939 | 0.00086236 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 91.4389 | 0.072939 | 0.00086236
136021 | 41503.6826 | 41503.7097 | 42 | 36 | 1512 | 42 | 0.0046567 | 0.00012935 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 42 | 0.0046567 | 0.00012935
136022 | 41503.7007 | 41503.7056 | 905 | 4 | 3620 | 905 | 0.011149 | 0.0027873 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 905 | 0.011149 | 0.0027873
136023 | 41503.8535 | 41503.9132 | 25 | 83 | 2075 | 25 | 0.0063907 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 25 | 0.0063907 | 7.6996e-05
136025 | 41503.5875 | 41503.6562 | 407 | 96 | 24749.5758 | 257.8081 | 0.076225 | 0.0012535 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-17 | 2014 | 2014 | 2013-08-17 | C | 257.8081 | 0.076225 | 0.0012535
136026 | 41504.3993 | 41504.4222 | 89 | 30 | 2670 | 89 | 0.0082232 | 0.00027411 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-18 | 2014 | 2014 | 2013-08-18 | C | 89 | 0.0082232 | 0.00027411
136027 | 41504.3153 | 41504.3736 | 338 | 81 | 27378 | 338 | 0.08432 | 0.001041 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-18 | 2014 | 2014 | 2013-08-18 | B | 338 | 0.08432 | 0.001041
136029 | 41504.2812 | 41504.4007 | 146 | 169 | 24674 | 146 | 0.075992 | 0.00044966 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-18 | 2014 | 2014 | 2013-08-18 | C | 146 | 0.075992 | 0.00044966
136035 | 41505.5417 | 41505.559 | 1 | 22 | 22 | 1 | 6.7757e-05 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | B | 1 | 6.7757e-05 | 3.0798e-06
136036 | 41505.6347 | 41505.6431 | 27 | 9 | 243 | 27 | 0.0007484 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | C | 27 | 0.0007484 | 8.3156e-05
136037 | 41505.3889 | 41505.4306 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | B | 4 | 0.0007022 | 1.2319e-05
136040 | 41505.6556 | 41505.6722 | 66 | 21 | 1386 | 66 | 0.0042687 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | C | 66 | 0.0042687 | 0.00020327
136042 | 41505.3674 | 41505.5868 | 5 | 313 | 1565 | 5 | 0.00482 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | B | 5 | 0.00482 | 1.5399e-05
136043 | 41502.375 | 41502.5021 | 3 | 180 | 540 | 3 | 0.0016631 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-16 | 2014 | 2014 | 2013-08-16 | B | 3 | 0.0016631 | 9.2395e-06
136044 | 41505.816 | 41505.8444 | 95 | 38 | 2208.6341 | 58.122 | 0.0068022 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | C | 58.122 | 0.0068022 | 0.00029258
136047 | 41506.1743 | 41506.2604 | 2449 | 121 | 83086.9919 | 686.6694 | 0.25589 | 0.0075425 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | C | 686.6694 | 0.25589 | 0.0075425
136050 | 41506.3958 | 41506.5542 | 25 | 225 | 5625 | 25 | 0.017324 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | B | 25 | 0.017324 | 7.6996e-05
136051 | 41506.4583 | 41506.5208 | 43 | 87 | 3741 | 43 | 0.011522 | 0.00013243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | B | 43 | 0.011522 | 0.00013243
136052 | 41506.4146 | 41506.45 | 37 | 48 | 1776 | 37 | 0.0054698 | 0.00011395 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | C | 37 | 0.0054698 | 0.00011395
136054 | 41506.375 | 41506.625 | 38 | 357 | 13566 | 38 | 0.041781 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | B | 38 | 0.041781 | 0.00011703
136056 | 41506.609 | 41506.9778 | 167 | 528 | 52460.9266 | 99.3578 | 0.16157 | 0.00051433 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-20 | 2014 | 2014 | 2013-08-20 | C | 99.3578 | 0.16157 | 0.00051433
136058 | 41507.3264 | 41507.3875 | 21 | 85 | 1785 | 21 | 0.0054975 | 6.4677e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | C | 21 | 0.0054975 | 6.4677e-05
136061 | 41507.375 | 41507.5563 | 50 | 258 | 12900 | 50 | 0.03973 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | B | 50 | 0.03973 | 0.00015399
136062 | 41507.6785 | 41507.7201 | 46 | 57 | 2622 | 46 | 0.0080753 | 0.00014167 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | C | 46 | 0.0080753 | 0.00014167
136063 | 41507.6653 | 41507.8229 | 21 | 224 | 2604.1233 | 11.6256 | 0.0080203 | 6.4677e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | C | 11.6256 | 0.0080203 | 6.4677e-05
136065 | 41508.1 | 41508.1285 | 803 | 38 | 30514 | 803 | 0.093978 | 0.0024731 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 803 | 0.093978 | 0.0024731
136066 | 41507.375 | 41507.6285 | 62 | 362 | 20069.6767 | 55.4411 | 0.061811 | 0.00019095 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | B | 55.4411 | 0.061811 | 0.00019095
136070 | 41504.2556 | 41504.734 | 287 | 686 | 20747.2685 | 30.2438 | 0.063898 | 0.00088391 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-18 | 2014 | 2014 | 2013-08-18 | B | 30.2438 | 0.063898 | 0.00088391
136073 | 41507.5292 | 41508.4563 | 77 | 1332 | 54747.6944 | 41.1019 | 0.16861 | 0.00023715 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-21 | 2014 | 2014 | 2013-08-21 | C | 41.1019 | 0.16861 | 0.00023715
136074 | 41508.4826 | 41508.6146 | 11 | 187 | 2057 | 11 | 0.0063352 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 11 | 0.0063352 | 3.3878e-05
136079 | 41508.4792 | 41508.525 | 1 | 63 | 63 | 1 | 0.00019403 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 1 | 0.00019403 | 3.0798e-06
136080 | 41508.3993 | 41508.5521 | 6 | 217 | 1302 | 6 | 0.00401 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 6 | 0.00401 | 1.8479e-05
136081 | 41508.4514 | 41508.5396 | 1 | 124 | 124 | 1 | 0.0003819 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 1 | 0.0003819 | 3.0798e-06
136082 | 41508.3924 | 41508.5208 | 44 | 182 | 8008 | 44 | 0.024663 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 44 | 0.024663 | 0.00013551
136083 | 41508.3792 | 41508.6062 | 9 | 324 | 2916 | 9 | 0.0089808 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 9 | 0.0089808 | 2.7719e-05
136084 | 41508.5729 | 41508.684 | 3 | 157 | 471 | 3 | 0.0014506 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 3 | 0.0014506 | 9.2395e-06
136085 | 41508.7292 | 41508.7465 | 16 | 22 | 352 | 16 | 0.0010841 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 16 | 0.0010841 | 4.9277e-05
136086 | 41508.7188 | 41508.7604 | 2 | 57 | 114 | 2 | 0.0003511 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 2 | 0.0003511 | 6.1597e-06
136089 | 41508.7222 | 41508.8403 | 2 | 167 | 334 | 2 | 0.0010287 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 2 | 0.0010287 | 6.1597e-06
136090 | 41508.8104 | 41509.4896 | 123 | 975 | 7510.8896 | 7.7035 | 0.023132 | 0.00037882 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | C | 7.7035 | 0.023132 | 0.00037882
136095 | 41509.3924 | 41509.434 | 11 | 57 | 627 | 11 | 0.0019311 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | B | 11 | 0.0019311 | 3.3878e-05
136096 | 41509.3583 | 41509.5757 | 3 | 310 | 633.8658 | 2.0447 | 0.0019522 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | C | 2.0447 | 0.0019522 | 9.2395e-06
136097 | 41509.5417 | 41509.5938 | 1 | 72 | 72 | 1 | 0.00022175 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | C | 1 | 0.00022175 | 3.0798e-06
136098 | 41508.3646 | 41508.5903 | 3 | 322 | 966 | 3 | 0.0029751 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-22 | 2014 | 2014 | 2013-08-22 | B | 3 | 0.0029751 | 9.2395e-06
136099 | 41509.3646 | 41509.6076 | 54 | 347 | 18738 | 54 | 0.05771 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | B | 54 | 0.05771 | 0.00016631
136101 | 41509.6736 | 41509.684 | 5 | 12 | 60 | 5 | 0.00018479 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | C | 5 | 0.00018479 | 1.5399e-05
136104 | 41510.4167 | 41510.4806 | 35 | 89 | 3115 | 35 | 0.0095937 | 0.00010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-24 | 2014 | 2014 | 2013-08-24 | C | 35 | 0.0095937 | 0.00010779
136105 | 41510.5833 | 41510.6764 | 6 | 131 | 786 | 6 | 0.0024208 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-24 | 2014 | 2014 | 2013-08-24 | C | 6 | 0.0024208 | 1.8479e-05
136106 | 41511.6285 | 41511.6375 | 44 | 10 | 440 | 44 | 0.0013551 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-25 | 2014 | 2014 | 2013-08-25 | C | 44 | 0.0013551 | 0.00013551
136109 | 41511.1493 | 41511.2688 | 821 | 169 | 73070.8837 | 432.3721 | 0.22505 | 0.0025286 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-25 | 2014 | 2014 | 2013-08-25 | C | 432.3721 | 0.22505 | 0.0025286
136110 | 41510.6236 | 41510.7993 | 200 | 250 | 50000 | 200 | 0.15399 | 0.00061597 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-24 | 2014 | 2014 | 2013-08-24 | C | 200 | 0.15399 | 0.00061597
136113 | 41512.3958 | 41512.616 | 89 | 314 | 27946 | 89 | 0.086069 | 0.00027411 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-26 | 2014 | 2014 | 2013-08-26 | B | 89 | 0.086069 | 0.00027411
136114 | 41512.3958 | 41512.6139 | 2 | 311 | 622 | 2 | 0.0019157 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-26 | 2014 | 2014 | 2013-08-26 | B | 2 | 0.0019157 | 6.1597e-06
136116 | 41512.5222 | 41512.6188 | 98 | 136 | 13328 | 98 | 0.041048 | 0.00030182 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-26 | 2014 | 2014 | 2013-08-26 | B | 98 | 0.041048 | 0.00030182
136119 | 41512.7514 | 41512.8493 | 4 | 138 | 552 | 4 | 0.0017001 | 1.2319e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-26 | 2014 | 2014 | 2013-08-26 | C | 4 | 0.0017001 | 1.2319e-05
136120 | 41512.9792 | 41513.0521 | 123 | 102 | 12546 | 123 | 0.03864 | 0.00037882 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-26 | 2014 | 2014 | 2013-08-26 | B | 123 | 0.03864 | 0.00037882
136121 | 41513.375 | 41513.5382 | 28 | 232 | 6496 | 28 | 0.020007 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-27 | 2014 | 2014 | 2013-08-27 | B | 28 | 0.020007 | 8.6236e-05
136123 | 41513.6208 | 41513.6389 | 67 | 23 | 1541 | 67 | 0.004746 | 0.00020635 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-27 | 2014 | 2014 | 2013-08-27 | C | 67 | 0.004746 | 0.00020635
136124 | 41513.3688 | 41513.5535 | 82 | 263 | 21566 | 82 | 0.06642 | 0.00025255 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-27 | 2014 | 2014 | 2013-08-27 | B | 82 | 0.06642 | 0.00025255
136125 | 41505.3299 | 41505.559 | 2 | 327 | 654 | 2 | 0.0020142 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-19 | 2014 | 2014 | 2013-08-19 | B | 2 | 0.0020142 | 6.1597e-06
136126 | 41509.4257 | 41509.5396 | 2 | 161 | 322 | 2 | 0.00099171 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-23 | 2014 | 2014 | 2013-08-23 | B | 2 | 0.00099171 | 6.1597e-06
136127 | 41514.375 | 41514.6292 | 235 | 363 | 85305 | 235 | 0.26273 | 0.00072376 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-28 | 2014 | 2014 | 2013-08-28 | B | 235 | 0.26273 | 0.00072376
136133 | 41514.2083 | 41514.2465 | 10 | 52 | 520 | 10 | 0.0016015 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-28 | 2014 | 2014 | 2013-08-28 | B | 10 | 0.0016015 | 3.0798e-05
136134 | 41515.3549 | 41515.3854 | 29 | 41 | 1189 | 29 | 0.0036619 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 29 | 0.0036619 | 8.9315e-05
136135 | 41515.4236 | 41515.4528 | 99 | 39 | 3861 | 99 | 0.011891 | 0.0003049 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 99 | 0.011891 | 0.0003049
136138 | 41515.3882 | 41515.5486 | 31 | 228 | 7068 | 31 | 0.021768 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | B | 31 | 0.021768 | 9.5475e-05
136139 | 41515.4424 | 41515.5549 | 610 | 159 | 32721.6111 | 205.7963 | 0.10078 | 0.0018787 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 205.7963 | 0.10078 | 0.0018787
136140 | 41515.4701 | 41515.5361 | 232 | 92 | 9504.0842 | 103.3053 | 0.029271 | 0.00071452 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 103.3053 | 0.029271 | 0.00071452
136143 | 41515.5535 | 41515.6319 | 5 | 110 | 550 | 5 | 0.0016939 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 5 | 0.0016939 | 1.5399e-05
136145 | 41515.591 | 41515.7153 | 402 | 176 | 28181.6313 | 160.1229 | 0.086795 | 0.0012381 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 160.1229 | 0.086795 | 0.0012381
136146 | 41515.866 | 41515.8694 | 50 | 2 | 100 | 50 | 0.00030798 | 0.00015399 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-29 | 2014 | 2014 | 2013-08-29 | C | 50 | 0.00030798 | 0.00015399
136148 | 41516.1354 | 41516.2125 | 1114 | 108 | 89327.6757 | 827.1081 | 0.27512 | 0.0034309 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-08-30 | 2014 | 2014 | 2013-08-30 | C | 827.1081 | 0.27512 | 0.0034309
136150 | 41516.3208 | 41516.3986 | 21 | 109 | 2289 | 21 | 0.0070498 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-30 | 2014 | 2014 | 2013-08-30 | C | 21 | 0.0070498 | 6.4677e-05
136151 | 41516.4132 | 41516.4854 | 50 | 101 | 3362.1346 | 33.2885 | 0.010355 | 0.00015399 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-30 | 2014 | 2014 | 2013-08-30 | C | 33.2885 | 0.010355 | 0.00015399
136152 | 41516.5799 | 41516.616 | 47 | 49 | 2303 | 47 | 0.0070929 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-30 | 2014 | 2014 | 2013-08-30 | C | 47 | 0.0070929 | 0.00014475
136153 | 41516.4167 | 41516.5833 | 356 | 237 | 79266.625 | 334.4583 | 0.24413 | 0.0010964 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-30 | 2014 | 2014 | 2013-08-30 | C | 334.4583 | 0.24413 | 0.0010964
136155 | 41517.0153 | 41517.0486 | 18 | 45 | 810 | 18 | 0.0024947 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-31 | 2014 | 2014 | 2013-08-31 | B | 18 | 0.0024947 | 5.5437e-05
136157 | 41517.5729 | 41517.5944 | 32 | 28 | 896 | 32 | 0.0027595 | 9.8555e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-08-31 | 2014 | 2014 | 2013-08-31 | C | 32 | 0.0027595 | 9.8555e-05
136161 | 41518.5354 | 41518.5813 | 304 | 63 | 19152 | 304 | 0.058985 | 0.00093627 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-01 | 2014 | 2014 | 2013-09-01 | C | 304 | 0.058985 | 0.00093627
136165 | 41518.5972 | 41518.6882 | 286 | 128 | 7573.4962 | 59.1679 | 0.023325 | 0.00088083 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-01 | 2014 | 2014 | 2013-09-01 | C | 59.1679 | 0.023325 | 0.00088083
136167 | 41518.7604 | 41518.7674 | 10 | 7 | 70 | 10 | 0.00021559 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-01 | 2014 | 2014 | 2013-09-01 | C | 10 | 0.00021559 | 3.0798e-05
136168 | 41519.4028 | 41519.4458 | 10 | 59 | 580.4839 | 9.8387 | 0.0017878 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-02 | 2014 | 2014 | 2013-09-02 | B | 9.8387 | 0.0017878 | 3.0798e-05
136170 | 41519.375 | 41519.5958 | 3 | 315 | 945 | 3 | 0.0029105 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-02 | 2014 | 2014 | 2013-09-02 | B | 3 | 0.0029105 | 9.2395e-06
136172 | 41519.4014 | 41519.5687 | 76 | 238 | 18088 | 76 | 0.055708 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-02 | 2014 | 2014 | 2013-09-02 | B | 76 | 0.055708 | 0.00023407
136173 | 41520.3556 | 41520.3799 | 14 | 32 | 448 | 14 | 0.0013798 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | C | 14 | 0.0013798 | 4.3118e-05
136174 | 41520.4431 | 41520.5118 | 11 | 96 | 1056 | 11 | 0.0032523 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | C | 11 | 0.0032523 | 3.3878e-05
136175 | 41520.4132 | 41520.5153 | 25 | 144 | 3600 | 25 | 0.011087 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 25 | 0.011087 | 7.6996e-05
136176 | 41520.375 | 41520.5653 | 9 | 271 | 2439 | 9 | 0.0075117 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 9 | 0.0075117 | 2.7719e-05
136177 | 41520.4375 | 41520.6042 | 2 | 237 | 474 | 2 | 0.0014598 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 2 | 0.0014598 | 6.1597e-06
136179 | 41520.4167 | 41520.6014 | 5 | 263 | 1315 | 5 | 0.00405 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 5 | 0.00405 | 1.5399e-05
136180 | 41520.3819 | 41520.6479 | 183 | 380 | 69540 | 183 | 0.21417 | 0.00056361 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 183 | 0.21417 | 0.00056361
136181 | 41520.375 | 41520.4792 | 52 | 147 | 7644 | 52 | 0.023542 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 52 | 0.023542 | 0.00016015
136183 | 41520.3785 | 41520.5042 | 82 | 178 | 14596 | 82 | 0.044953 | 0.00025255 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 82 | 0.044953 | 0.00025255
136184 | 41520.6153 | 41520.7014 | 298 | 121 | 15088.8952 | 124.7016 | 0.046471 | 0.00091779 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | C | 124.7016 | 0.046471 | 0.00091779
136186 | 41521.3882 | 41521.5861 | 1 | 282 | 282 | 1 | 0.00086852 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | B | 1 | 0.00086852 | 3.0798e-06
136190 | 41521.3472 | 41521.3882 | 764 | 56 | 42784 | 764 | 0.13177 | 0.002353 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | C | 764 | 0.13177 | 0.002353
136192 | 41520.4278 | 41520.6403 | 8 | 303 | 2424 | 8 | 0.0074655 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-03 | 2014 | 2014 | 2013-09-03 | B | 8 | 0.0074655 | 2.4639e-05
136193 | 41521.4625 | 41521.5521 | 38 | 126 | 4788 | 38 | 0.014746 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | C | 38 | 0.014746 | 0.00011703
136195 | 41521.3771 | 41521.6167 | 7 | 342 | 2394 | 7 | 0.0073731 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | B | 7 | 0.0073731 | 2.1559e-05
136200 | 41521.3472 | 41521.4757 | 5525 | 182 | 461300.1514 | 2534.6162 | 1.4207 | 0.017016 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | C | 2534.6162 | 1.4207 | 0.017016
136203 | 41521.7688 | 41521.8375 | 96 | 96 | 9216 | 96 | 0.028384 | 0.00029566 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | C | 96 | 0.028384 | 0.00029566
136204 | 41522.2271 | 41522.4556 | 480 | 326 | 50762.8571 | 155.7143 | 0.15634 | 0.0014783 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 155.7143 | 0.15634 | 0.0014783
136205 | 41522.3757 | 41522.4576 | 6 | 115 | 690 | 6 | 0.0021251 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 6 | 0.0021251 | 1.8479e-05
136206 | 41522.1062 | 41522.3646 | 150 | 369 | 51527.0806 | 139.6398 | 0.1587 | 0.00046198 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 139.6398 | 0.1587 | 0.00046198
136207 | 41522.1674 | 41522.3264 | 236 | 226 | 42708.0786 | 188.9738 | 0.13153 | 0.00072684 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 188.9738 | 0.13153 | 0.00072684
136208 | 41522.4132 | 41522.4514 | 40 | 52 | 2080 | 40 | 0.0064061 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 40 | 0.0064061 | 0.00012319
136209 | 41522.1861 | 41522.4722 | 15 | 409 | 6135 | 15 | 0.018895 | 4.6198e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 15 | 0.018895 | 4.6198e-05
136212 | 41522.516 | 41522.5514 | 34 | 48 | 1632 | 34 | 0.0050263 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 34 | 0.0050263 | 0.00010471
136213 | 41522.416 | 41522.5118 | 418 | 135 | 34647.0652 | 256.6449 | 0.10671 | 0.0012874 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 256.6449 | 0.10671 | 0.0012874
136214 | 41522.4132 | 41522.5958 | 1 | 260 | 260 | 1 | 0.00080076 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 1 | 0.00080076 | 3.0798e-06
136215 | 41522.4062 | 41522.4826 | 1 | 107 | 107 | 1 | 0.00032954 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 1 | 0.00032954 | 3.0798e-06
136216 | 41522.3125 | 41522.5076 | 3 | 278 | 834 | 3 | 0.0025686 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 3 | 0.0025686 | 9.2395e-06
136217 | 41522.2799 | 41522.5312 | 339 | 359 | 57522.3122 | 160.2293 | 0.17716 | 0.0010441 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 160.2293 | 0.17716 | 0.0010441
136218 | 41522.2688 | 41522.4319 | 307 | 232 | 54697.7021 | 235.766 | 0.16846 | 0.00094551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 235.766 | 0.16846 | 0.00094551
136219 | 41521.4285 | 41521.5708 | 14 | 202 | 2828 | 14 | 0.0087098 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | B | 14 | 0.0087098 | 4.3118e-05
136220 | 41521.4118 | 41521.6042 | 113 | 274 | 30962 | 113 | 0.095358 | 0.00034802 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | B | 113 | 0.095358 | 0.00034802
136222 | 41522.4993 | 41522.5347 | 114 | 48 | 5472 | 114 | 0.016853 | 0.0003511 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 114 | 0.016853 | 0.0003511
136223 | 41522.5035 | 41522.5437 | 95 | 55 | 5225 | 95 | 0.016092 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 95 | 0.016092 | 0.00029258
136224 | 41522.3653 | 41522.4722 | 6 | 151 | 906 | 6 | 0.0027903 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 6 | 0.0027903 | 1.8479e-05
136225 | 41522.4167 | 41522.4681 | 30 | 71 | 2130 | 30 | 0.0065601 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 30 | 0.0065601 | 9.2395e-05
136226 | 41522.6458 | 41522.709 | 6 | 88 | 528 | 6 | 0.0016262 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 6 | 0.0016262 | 1.8479e-05
136227 | 41522.375 | 41522.6562 | 56 | 402 | 22512 | 56 | 0.069333 | 0.00017247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 56 | 0.069333 | 0.00017247
136228 | 41522.5257 | 41522.5465 | 1428 | 27 | 38556 | 1428 | 0.11875 | 0.004398 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 1428 | 0.11875 | 0.004398
136229 | 41522.3938 | 41522.5604 | 25 | 237 | 5925 | 25 | 0.018248 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 25 | 0.018248 | 7.6996e-05
136233 | 41522.2139 | 41522.2604 | 5 | 64 | 320 | 5 | 0.00098555 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 5 | 0.00098555 | 1.5399e-05
136234 | 41522.7257 | 41522.7861 | 4 | 84 | 336 | 4 | 0.0010348 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 4 | 0.0010348 | 1.2319e-05
136235 | 41522.8021 | 41522.8438 | 47 | 57 | 2679 | 47 | 0.0082509 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 47 | 0.0082509 | 0.00014475
136236 | 41522.0799 | 41522.5056 | 94 | 610 | 18459.217 | 30.261 | 0.056851 | 0.00028951 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 30.261 | 0.056851 | 0.00028951
136238 | 41522.2347 | 41522.2382 | 108 | 2 | 216 | 108 | 0.00066525 | 0.00033262 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 108 | 0.00066525 | 0.00033262
136239 | 41522.2347 | 41522.2403 | 74 | 5 | 370 | 74 | 0.0011395 | 0.00022791 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 74 | 0.0011395 | 0.00022791
136243 | 41523.0049 | 41523.1472 | 78 | 202 | 15756 | 78 | 0.048526 | 0.00024023 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-06 | 2014 | 2014 | 2013-09-06 | C | 78 | 0.048526 | 0.00024023
136244 | 41522.9167 | 41523.1562 | 8 | 342 | 2736 | 8 | 0.0084264 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 8 | 0.0084264 | 2.4639e-05
136245 | 41522.6076 | 41522.6667 | 18 | 82 | 1476 | 18 | 0.0045458 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 18 | 0.0045458 | 5.5437e-05
136246 | 41522.1764 | 41522.3562 | 40 | 256 | 9838.7027 | 38.4324 | 0.030302 | 0.00012319 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 38.4324 | 0.030302 | 0.00012319
136247 | 41522.5104 | 41522.6319 | 133 | 172 | 22876 | 133 | 0.070454 | 0.00040962 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 133 | 0.070454 | 0.00040962
136248 | 41522.1417 | 41522.3979 | 321 | 366 | 66661.5935 | 182.1355 | 0.20531 | 0.00098863 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 182.1355 | 0.20531 | 0.00098863
136249 | 41522.3611 | 41522.6438 | 9 | 404 | 3636 | 9 | 0.011198 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 9 | 0.011198 | 2.7719e-05
136250 | 41522.5257 | 41522.5458 | 75 | 26 | 1950 | 75 | 0.0060057 | 0.00023099 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 75 | 0.0060057 | 0.00023099
136251 | 41522.416 | 41522.4507 | 122 | 47 | 5734 | 122 | 0.01766 | 0.00037574 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 122 | 0.01766 | 0.00037574
136252 | 41522.3819 | 41522.4479 | 7 | 92 | 644 | 7 | 0.0019834 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 7 | 0.0019834 | 2.1559e-05
136253 | 41522.5667 | 41522.6354 | 1 | 96 | 96 | 1 | 0.00029566 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 1 | 0.00029566 | 3.0798e-06
136254 | 41521.4229 | 41521.6937 | 6 | 387 | 2322 | 6 | 0.0071514 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-04 | 2014 | 2014 | 2013-09-04 | C | 6 | 0.0071514 | 1.8479e-05
136255 | 41523.375 | 41523.6299 | 67 | 364 | 24388 | 67 | 0.075111 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-06 | 2014 | 2014 | 2013-09-06 | B | 67 | 0.075111 | 0.00020635
136256 | 41523.5042 | 41523.6458 | 237 | 201 | 15581.4412 | 77.5196 | 0.047988 | 0.00072992 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-06 | 2014 | 2014 | 2013-09-06 | C | 77.5196 | 0.047988 | 0.00072992
136257 | 41523.5625 | 41523.6181 | 2 | 77 | 154 | 2 | 0.0004743 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-06 | 2014 | 2014 | 2013-09-06 | C | 2 | 0.0004743 | 6.1597e-06
136259 | 41524.3326 | 41524.4528 | 4 | 170 | 680 | 4 | 0.0020943 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | C | 4 | 0.0020943 | 1.2319e-05
136261 | 41524.5222 | 41524.5833 | 3 | 85 | 255 | 3 | 0.00078536 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | C | 3 | 0.00078536 | 9.2395e-06
136262 | 41524.3958 | 41524.6438 | 47 | 354 | 16638 | 47 | 0.051242 | 0.00014475 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | B | 47 | 0.051242 | 0.00014475
136267 | 41525.2632 | 41525.3542 | 372 | 128 | 36369.5878 | 284.1374 | 0.11201 | 0.0011457 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 284.1374 | 0.11201 | 0.0011457
136268 | 41525.3368 | 41525.4569 | 101 | 170 | 17170 | 101 | 0.052881 | 0.00031106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 101 | 0.052881 | 0.00031106
136269 | 41525.1972 | 41525.4201 | 962 | 318 | 159216.9533 | 500.6822 | 0.49036 | 0.0029628 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 500.6822 | 0.49036 | 0.0029628
136271 | 41525.1972 | 41525.2528 | 1648 | 77 | 92211.35 | 1197.55 | 0.284 | 0.0050756 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 1197.55 | 0.284 | 0.0050756
136274 | 41525.3812 | 41525.4965 | 41 | 163 | 6683 | 41 | 0.020583 | 0.00012627 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | B | 41 | 0.020583 | 0.00012627
136275 | 41525.5458 | 41525.5729 | 8 | 36 | 288 | 8 | 0.00088699 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 8 | 0.00088699 | 2.4639e-05
136276 | 41524.9889 | 41525.166 | 132 | 252 | 22986.3529 | 91.2157 | 0.070794 | 0.00040654 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | C | 91.2157 | 0.070794 | 0.00040654
136277 | 41524.9889 | 41525.0319 | 288 | 59 | 16992 | 288 | 0.052333 | 0.00088699 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | C | 288 | 0.052333 | 0.00088699
136278 | 41525.5014 | 41525.6236 | 512 | 173 | 33727.1364 | 194.9545 | 0.10387 | 0.0015769 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 194.9545 | 0.10387 | 0.0015769
136279 | 41525.6368 | 41525.6875 | 90 | 70 | 6300 | 90 | 0.019403 | 0.00027719 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 90 | 0.019403 | 0.00027719
136281 | 41525.6389 | 41525.691 | 48 | 72 | 3456 | 48 | 0.010644 | 0.00014783 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 48 | 0.010644 | 0.00014783
136283 | 41525.7333 | 41525.7785 | 149 | 62 | 9238 | 149 | 0.028452 | 0.0004589 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-08 | 2014 | 2014 | 2013-09-08 | C | 149 | 0.028452 | 0.0004589
136284 | 41523.9361 | 41523.9986 | 373 | 87 | 29767.5333 | 342.1556 | 0.091679 | 0.0011488 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-06 | 2014 | 2014 | 2013-09-06 | C | 342.1556 | 0.091679 | 0.0011488
136286 | 41522.3938 | 41522.5604 | 25 | 237 | 5925 | 25 | 0.018248 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 25 | 0.018248 | 7.6996e-05
136293 | 41526.3958 | 41526.5979 | 63 | 288 | 18144 | 63 | 0.055881 | 0.00019403 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | B | 63 | 0.055881 | 0.00019403
136294 | 41526.5771 | 41526.6181 | 20 | 56 | 1120 | 20 | 0.0034494 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 20 | 0.0034494 | 6.1597e-05
136296 | 41495.3958 | 41495.4646 | 24 | 96 | 2304 | 24 | 0.007096 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-08-09 | 2014 | 2014 | 2013-08-09 | B | 24 | 0.007096 | 7.3916e-05
136298 | 41526.6639 | 41526.6806 | 161 | 21 | 3381 | 161 | 0.010413 | 0.00049585 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 161 | 0.010413 | 0.00049585
136299 | 41526.4604 | 41526.6965 | 4 | 337 | 1348 | 4 | 0.0041516 | 1.2319e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 4 | 0.0041516 | 1.2319e-05
136300 | 41526.3431 | 41526.4014 | 3 | 81 | 243 | 3 | 0.0007484 | 9.2395e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 3 | 0.0007484 | 9.2395e-06
136301 | 41526.5069 | 41526.5535 | 26 | 64 | 1664 | 26 | 0.0051249 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 26 | 0.0051249 | 8.0076e-05
136302 | 41526.4604 | 41526.6576 | 649 | 281 | 63673.2148 | 226.5951 | 0.1961 | 0.0019988 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 226.5951 | 0.1961 | 0.0019988
136303 | 41526.4299 | 41526.6701 | 2 | 343 | 686 | 2 | 0.0021128 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | B | 2 | 0.0021128 | 6.1597e-06
136304 | 41526.3271 | 41526.434 | 220 | 151 | 25248.3766 | 167.2078 | 0.077761 | 0.00067757 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 167.2078 | 0.077761 | 0.00067757
136306 | 41526.6486 | 41526.6861 | 1310 | 51 | 66810 | 1310 | 0.20576 | 0.0040346 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 1310 | 0.20576 | 0.0040346
136307 | 41526.716 | 41526.7785 | 4 | 87 | 348 | 4 | 0.0010718 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 4 | 0.0010718 | 1.2319e-05
136308 | 41526.716 | 41526.7785 | 19 | 87 | 1653 | 19 | 0.005091 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-09 | 2014 | 2014 | 2013-09-09 | C | 19 | 0.005091 | 5.8517e-05
136309 | 41524.684 | 41524.7306 | 1 | 64 | 64 | 1 | 0.00019711 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-07 | 2014 | 2014 | 2013-09-07 | C | 1 | 0.00019711 | 3.0798e-06
136311 | 41522.4201 | 41522.6632 | 1 | 347 | 347 | 1 | 0.0010687 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | B | 1 | 0.0010687 | 3.0798e-06
136312 | 41527.3035 | 41527.3618 | 167 | 81 | 8301.5357 | 102.4881 | 0.025567 | 0.00051433 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 102.4881 | 0.025567 | 0.00051433
136313 | 41527.5083 | 41527.5208 | 4 | 15 | 60 | 4 | 0.00018479 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 4 | 0.00018479 | 1.2319e-05
136318 | 41527.4049 | 41527.6632 | 8 | 369 | 2952 | 8 | 0.0090917 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 8 | 0.0090917 | 2.4639e-05
136319 | 41527.375 | 41527.6424 | 109 | 382 | 41638 | 109 | 0.12824 | 0.0003357 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 109 | 0.12824 | 0.0003357
136320 | 41527.375 | 41527.6271 | 13 | 360 | 4680 | 13 | 0.014414 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 13 | 0.014414 | 4.0038e-05
136322 | 41527.375 | 41527.4611 | 52 | 121 | 6292 | 52 | 0.019378 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 52 | 0.019378 | 0.00016015
136323 | 41527.3646 | 41527.5833 | 80 | 312 | 24960 | 80 | 0.076873 | 0.00024639 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 80 | 0.076873 | 0.00024639
136324 | 41527.375 | 41527.5833 | 74 | 297 | 21978 | 74 | 0.067689 | 0.00022791 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 74 | 0.067689 | 0.00022791
136325 | 41527.375 | 41527.625 | 7 | 357 | 2499 | 7 | 0.0076965 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | B | 7 | 0.0076965 | 2.1559e-05
136326 | 41527.7306 | 41527.7993 | 978 | 96 | 93598.0606 | 974.9798 | 0.28827 | 0.0030121 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 974.9798 | 0.28827 | 0.0030121
136329 | 41527.9535 | 41527.9667 | 1894 | 16 | 27711.1579 | 1731.9474 | 0.085346 | 0.0058332 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 1731.9474 | 0.085346 | 0.0058332
136330 | 41527.9535 | 41527.9833 | 174 | 40 | 6960 | 174 | 0.021436 | 0.00053589 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 174 | 0.021436 | 0.00053589
136331 | 41527.8722 | 41527.9569 | 80 | 119 | 9151.2951 | 76.9016 | 0.028185 | 0.00024639 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 76.9016 | 0.028185 | 0.00024639
136332 | 41527.7917 | 41527.8333 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 4 | 0.0007022 | 1.2319e-05
136333 | 41527.7153 | 41528.0972 | 5 | 547 | 2735 | 5 | 0.0084234 | 1.5399e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 5 | 0.0084234 | 1.5399e-05
136336 | 41528.4778 | 41528.5764 | 21 | 139 | 2919 | 21 | 0.0089901 | 6.4677e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 21 | 0.0089901 | 6.4677e-05
136345 | 41527.7333 | 41527.75 | 50 | 21 | 910 | 43.3333 | 0.0028027 | 0.00015399 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 43.3333 | 0.0028027 | 0.00015399
136346 | 41527.4715 | 41527.7229 | 772 | 359 | 38265.2348 | 106.5884 | 0.11785 | 0.0023776 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 106.5884 | 0.11785 | 0.0023776
136347 | 41528.5799 | 41528.616 | 112 | 49 | 5488 | 112 | 0.016902 | 0.00034494 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 112 | 0.016902 | 0.00034494
136348 | 41528.4653 | 41528.5542 | 124 | 125 | 8909.1797 | 71.2734 | 0.027439 | 0.0003819 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 71.2734 | 0.027439 | 0.0003819
136351 | 41527.9451 | 41528.141 | 180 | 279 | 43968.2234 | 157.5922 | 0.13542 | 0.00055437 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 157.5922 | 0.13542 | 0.00055437
136352 | 41522.0611 | 41522.2625 | 60 | 287 | 17220 | 60 | 0.053035 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-05 | 2014 | 2014 | 2013-09-05 | C | 60 | 0.053035 | 0.00018479
136354 | 41528.6097 | 41528.6667 | 18 | 79 | 1422 | 18 | 0.0043795 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 18 | 0.0043795 | 5.5437e-05
136355 | 41528.1653 | 41528.2458 | 1734 | 113 | 66102.0776 | 584.9741 | 0.20358 | 0.0053404 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 584.9741 | 0.20358 | 0.0053404
136358 | 41528.6174 | 41528.7319 | 364 | 162 | 58968 | 364 | 0.18161 | 0.0011211 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 364 | 0.18161 | 0.0011211
136360 | 41527.5062 | 41527.5771 | 2 | 99 | 198 | 2 | 0.00060981 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 2 | 0.00060981 | 6.1597e-06
136361 | 41527.3896 | 41527.4389 | 224 | 68 | 15232 | 224 | 0.046912 | 0.00068988 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 224 | 0.046912 | 0.00068988
136362 | 41527.5035 | 41527.5264 | 69 | 30 | 2070 | 69 | 0.0063753 | 0.00021251 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 69 | 0.0063753 | 0.00021251
136363 | 41527.6181 | 41527.6826 | 66 | 90 | 2478.3871 | 27.5376 | 0.007633 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-10 | 2014 | 2014 | 2013-09-10 | C | 27.5376 | 0.007633 | 0.00020327
136364 | 41528.4049 | 41528.5778 | 56 | 246 | 13776 | 56 | 0.042428 | 0.00017247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | B | 56 | 0.042428 | 0.00017247
136366 | 41528.3958 | 41528.6333 | 7 | 339 | 2373 | 7 | 0.0073085 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | B | 7 | 0.0073085 | 2.1559e-05
136368 | 41528.5903 | 41528.6167 | 55 | 35 | 1925 | 55 | 0.0059287 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 55 | 0.0059287 | 0.00016939
136369 | 41528.4861 | 41528.7063 | 221 | 314 | 66420.4101 | 211.53 | 0.20456 | 0.00068065 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 211.53 | 0.20456 | 0.00068065
136370 | 41528.6958 | 41530.8097 | 209 | 3041 | 296239.7543 | 97.4152 | 0.91237 | 0.00064369 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 97.4152 | 0.91237 | 0.00064369
136371 | 41528.6722 | 41528.75 | 672 | 109 | 73248 | 672 | 0.22559 | 0.0020697 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 672 | 0.22559 | 0.0020697
136372 | 41528.5222 | 41528.7153 | 71 | 275 | 15750.1799 | 57.2734 | 0.048508 | 0.00021867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 57.2734 | 0.048508 | 0.00021867
136373 | 41528.2056 | 41528.3125 | 234 | 151 | 15676.5455 | 103.8182 | 0.048281 | 0.00072068 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 103.8182 | 0.048281 | 0.00072068
136374 | 41528.4465 | 41528.4701 | 8 | 31 | 248 | 8 | 0.0007638 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 8 | 0.0007638 | 2.4639e-05
136375 | 41528.2951 | 41528.4965 | 282 | 287 | 46042.7172 | 160.4276 | 0.1418 | 0.00086852 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 160.4276 | 0.1418 | 0.00086852
136378 | 41528.7514 | 41528.95 | 364 | 283 | 65726.2552 | 232.2483 | 0.20243 | 0.0011211 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 232.2483 | 0.20243 | 0.0011211
136379 | 41528.9319 | 41528.9604 | 762 | 38 | 28956 | 762 | 0.08918 | 0.0023468 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 762 | 0.08918 | 0.0023468
136380 | 41528.8764 | 41528.9778 | 738 | 143 | 34260.2534 | 239.5822 | 0.10552 | 0.0022729 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 239.5822 | 0.10552 | 0.0022729
136381 | 41528.8278 | 41528.8785 | 1865 | 70 | 118784.2466 | 1696.9178 | 0.36584 | 0.0057439 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 1696.9178 | 0.36584 | 0.0057439
136382 | 41528.7903 | 41528.8639 | 96 | 103 | 7649.2075 | 74.2642 | 0.023558 | 0.00029566 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 74.2642 | 0.023558 | 0.00029566
136383 | 41528.5813 | 41528.734 | 394 | 217 | 50309.4773 | 231.8409 | 0.15495 | 0.0012135 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 231.8409 | 0.15495 | 0.0012135
136384 | 41528.0424 | 41528.7639 | 174 | 1036 | 139674.5371 | 134.821 | 0.43018 | 0.00053589 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 134.821 | 0.43018 | 0.00053589
136385 | 41528.6847 | 41528.7153 | 638 | 41 | 21598.6136 | 526.7955 | 0.06652 | 0.0019649 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 526.7955 | 0.06652 | 0.0019649
136386 | 41528.8104 | 41529.3931 | 696 | 836 | 135405.0965 | 161.9678 | 0.41703 | 0.0021436 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 161.9678 | 0.41703 | 0.0021436
136387 | 41528.825 | 41529.3306 | 394 | 725 | 20189.4574 | 27.8475 | 0.06218 | 0.0012135 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 27.8475 | 0.06218 | 0.0012135
136388 | 41529.0389 | 41529.0847 | 781 | 63 | 32511.8182 | 516.0606 | 0.10013 | 0.0024054 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 516.0606 | 0.10013 | 0.0024054
136389 | 41528.8326 | 41528.8375 | 209 | 4 | 836 | 209 | 0.0025747 | 0.00064369 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 209 | 0.0025747 | 0.00064369
136390 | 41529.3333 | 41529.3542 | 617 | 27 | 16659 | 617 | 0.051307 | 0.0019003 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 617 | 0.051307 | 0.0019003
136391 | 41528.7236 | 41528.8681 | 599 | 205 | 59634.3029 | 290.899 | 0.18366 | 0.0018448 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 290.899 | 0.18366 | 0.0018448
136393 | 41529.4007 | 41529.4236 | 10 | 30 | 300 | 10 | 0.00092395 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 10 | 0.00092395 | 3.0798e-05
136394 | 41528.0028 | 41528.0278 | 1401 | 33 | 46233 | 1401 | 0.14239 | 0.0043149 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 1401 | 0.14239 | 0.0043149
136397 | 41528.8236 | 41529.4458 | 24 | 893 | 21432 | 24 | 0.066007 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 24 | 0.066007 | 7.3916e-05
136400 | 41529.3646 | 41529.6458 | 54 | 402 | 21708 | 54 | 0.066857 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | B | 54 | 0.066857 | 0.00016631
136401 | 41528.3646 | 41528.6604 | 54 | 423 | 11430.9296 | 27.0235 | 0.035205 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | B | 27.0235 | 0.035205 | 0.00016631
136402 | 41529.2708 | 41529.5174 | 228 | 352 | 79378.4789 | 225.507 | 0.24447 | 0.0007022 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 225.507 | 0.24447 | 0.0007022
136403 | 41529.5493 | 41529.8021 | 5 | 361 | 1805 | 5 | 0.0055591 | 1.5399e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 5 | 0.0055591 | 1.5399e-05
136404 | 41529.5972 | 41529.6389 | 16 | 57 | 912 | 16 | 0.0028088 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 16 | 0.0028088 | 4.9277e-05
136405 | 41529.5035 | 41529.8264 | 3 | 462 | 1386 | 3 | 0.0042687 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 3 | 0.0042687 | 9.2395e-06
136406 | 41529.6424 | 41529.6528 | 67 | 12 | 804 | 67 | 0.0024762 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | B | 67 | 0.0024762 | 0.00020635
136407 | 41529.1472 | 41529.2368 | 692 | 126 | 40474.3256 | 321.2248 | 0.12465 | 0.0021313 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 321.2248 | 0.12465 | 0.0021313
136408 | 41529.8597 | 41530.0076 | 258 | 210 | 40539.8592 | 193.0469 | 0.12486 | 0.0007946 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 193.0469 | 0.12486 | 0.0007946
136409 | 41529.6736 | 41529.875 | 307 | 287 | 37369.3793 | 130.2069 | 0.11509 | 0.00094551 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 130.2069 | 0.11509 | 0.00094551
136410 | 41528.7049 | 41530.5521 | 265 | 2657 | 456832.194 | 171.9353 | 1.407 | 0.00081616 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 171.9353 | 1.407 | 0.00081616
136412 | 41529.5444 | 41529.6208 | 95 | 107 | 10165 | 95 | 0.031307 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 95 | 0.031307 | 0.00029258
136413 | 41529.366 | 41529.4264 | 8 | 84 | 672 | 8 | 0.0020697 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 8 | 0.0020697 | 2.4639e-05
136414 | 41528.8958 | 41530.6104 | 266 | 2466 | 240943.8809 | 97.7064 | 0.74207 | 0.00081924 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 97.7064 | 0.74207 | 0.00081924
136415 | 41528.5493 | 41529.7382 | 77 | 1709 | 19881.1005 | 11.6332 | 0.061231 | 0.00023715 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 11.6332 | 0.061231 | 0.00023715
136416 | 41529.4153 | 41529.591 | 226 | 250 | 56500 | 226 | 0.17401 | 0.00069604 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 226 | 0.17401 | 0.00069604
136417 | 41528.8764 | 41530.7222 | 1116 | 2655 | 147676.1343 | 55.6219 | 0.45482 | 0.0034371 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 55.6219 | 0.45482 | 0.0034371
136418 | 41529.5 | 41529.709 | 64 | 298 | 19072 | 64 | 0.058739 | 0.00019711 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 64 | 0.058739 | 0.00019711
136419 | 41529.4271 | 41529.5 | 13 | 102 | 1326 | 13 | 0.0040839 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 13 | 0.0040839 | 4.0038e-05
136420 | 41528.6826 | 41528.7292 | 12 | 64 | 768 | 12 | 0.0023653 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 12 | 0.0023653 | 3.6958e-05
136421 | 41529.4479 | 41529.4882 | 249 | 55 | 13695 | 249 | 0.042178 | 0.00076688 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 249 | 0.042178 | 0.00076688
136422 | 41528.7021 | 41529.5493 | 865 | 1217 | 444439.4221 | 365.1926 | 1.3688 | 0.0026641 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 365.1926 | 1.3688 | 0.0026641
136423 | 41528.9167 | 41529.6069 | 47 | 991 | 11582.9356 | 11.6881 | 0.035674 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 11.6881 | 0.035674 | 0.00014475
136424 | 41528.8333 | 41529.5535 | 9 | 1034 | 9306 | 9 | 0.028661 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 9 | 0.028661 | 2.7719e-05
136425 | 41528.7271 | 41529.4861 | 720 | 1090 | 158490.7868 | 145.4044 | 0.48813 | 0.0022175 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 145.4044 | 0.48813 | 0.0022175
136426 | 41529.5451 | 41529.6215 | 174 | 107 | 18618 | 174 | 0.05734 | 0.00053589 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 174 | 0.05734 | 0.00053589
136427 | 41529.5736 | 41529.6736 | 86 | 141 | 7194.9167 | 51.0278 | 0.022159 | 0.00026487 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 51.0278 | 0.022159 | 0.00026487
136428 | 41528.8549 | 41529.6917 | 112 | 1202 | 134624 | 112 | 0.41462 | 0.00034494 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 112 | 0.41462 | 0.00034494
136429 | 41528.9375 | 41529.6639 | 5 | 1043 | 5215 | 5 | 0.016061 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 5 | 0.016061 | 1.5399e-05
136430 | 41529.6708 | 41529.7076 | 91 | 50 | 4550 | 91 | 0.014013 | 0.00028027 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 91 | 0.014013 | 0.00028027
136432 | 41529.375 | 41529.4688 | 40 | 132 | 5280 | 40 | 0.016262 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | B | 40 | 0.016262 | 0.00012319
136433 | 41530.4688 | 41530.5104 | 76 | 57 | 4332 | 76 | 0.013342 | 0.00023407 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 76 | 0.013342 | 0.00023407
136434 | 41530.3958 | 41530.5271 | 2 | 186 | 372 | 2 | 0.0011457 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | B | 2 | 0.0011457 | 6.1597e-06
136436 | 41529.375 | 41529.6104 | 86 | 336 | 28896 | 86 | 0.088995 | 0.00026487 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | B | 86 | 0.088995 | 0.00026487
136437 | 41530.4986 | 41530.5729 | 8 | 104 | 832 | 8 | 0.0025624 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 8 | 0.0025624 | 2.4639e-05
136438 | 41530.5375 | 41530.6215 | 221 | 118 | 15200.5455 | 128.8182 | 0.046815 | 0.00068065 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 128.8182 | 0.046815 | 0.00068065
136439 | 41530.5868 | 41530.6215 | 4 | 47 | 188 | 4 | 0.00057901 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 4 | 0.00057901 | 1.2319e-05
136441 | 41531.3528 | 41531.4146 | 7 | 86 | 602 | 7 | 0.0018541 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 7 | 0.0018541 | 2.1559e-05
136443 | 41531.375 | 41531.434 | 7 | 82 | 574 | 7 | 0.0017678 | 2.1559e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 7 | 0.0017678 | 2.1559e-05
136444 | 41531.3889 | 41531.4722 | 10 | 117 | 1170 | 10 | 0.0036034 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 10 | 0.0036034 | 3.0798e-05
136445 | 41531.4493 | 41531.5667 | 167 | 166 | 10644.6272 | 64.1243 | 0.032784 | 0.00051433 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 64.1243 | 0.032784 | 0.00051433
136446 | 41531.4361 | 41531.5729 | 439 | 194 | 13996.5584 | 72.1472 | 0.043107 | 0.0013521 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 72.1472 | 0.043107 | 0.0013521
136447 | 41531.5722 | 41531.5979 | 38 | 34 | 1292 | 38 | 0.0039792 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 38 | 0.0039792 | 0.00011703
136448 | 41530.7229 | 41531.7104 | 4 | 1419 | 5676 | 4 | 0.017481 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 4 | 0.017481 | 1.2319e-05
136449 | 41531.6562 | 41531.7208 | 2 | 90 | 180 | 2 | 0.00055437 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 2 | 0.00055437 | 6.1597e-06
136450 | 41531.7681 | 41531.7951 | 39 | 36 | 1404 | 39 | 0.0043241 | 0.00012011 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 39 | 0.0043241 | 0.00012011
136452 | 41529.5021 | 41529.6458 | 632 | 204 | 128928 | 632 | 0.39708 | 0.0019465 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 632 | 0.39708 | 0.0019465
136453 | 41532.4944 | 41532.516 | 14 | 28 | 392 | 14 | 0.0012073 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-15 | 2014 | 2014 | 2013-09-15 | C | 14 | 0.0012073 | 4.3118e-05
136454 | 41530.5597 | 41530.5882 | 13 | 38 | 494 | 13 | 0.0015214 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 13 | 0.0015214 | 4.0038e-05
136455 | 41529.7681 | 41530.5687 | 62 | 1150 | 68144.2324 | 59.2559 | 0.20987 | 0.00019095 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 59.2559 | 0.20987 | 0.00019095
136456 | 41529.9569 | 41530.4688 | 30 | 734 | 22020 | 30 | 0.067818 | 9.2395e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 30 | 0.067818 | 9.2395e-05
136458 | 41528.1194 | 41529.7125 | 3 | 2291 | 6873 | 3 | 0.021168 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 3 | 0.021168 | 9.2395e-06
136459 | 41528.7153 | 41529.8319 | 42 | 1605 | 11919.7201 | 7.4266 | 0.036711 | 0.00012935 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 7.4266 | 0.036711 | 0.00012935
136460 | 41529.725 | 41530.4375 | 50 | 1023 | 17588.4211 | 17.193 | 0.05417 | 0.00015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 17.193 | 0.05417 | 0.00015399
136461 | 41528.6611 | 41529.6576 | 362 | 1432 | 155161.9401 | 108.3533 | 0.47787 | 0.0011149 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 108.3533 | 0.47787 | 0.0011149
136462 | 41528.8014 | 41529.7937 | 256 | 1426 | 90172.2967 | 63.2344 | 0.27772 | 0.00078844 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 63.2344 | 0.27772 | 0.00078844
136463 | 41529.6813 | 41529.8292 | 4 | 210 | 840 | 4 | 0.0025871 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 4 | 0.0025871 | 1.2319e-05
136464 | 41529.9583 | 41530.4104 | 40 | 648 | 2239.6313 | 3.4562 | 0.0068977 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 3.4562 | 0.0068977 | 0.00012319
136466 | 41529.7903 | 41530.5368 | 4 | 1072 | 4288 | 4 | 0.013206 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 4 | 0.013206 | 1.2319e-05
136467 | 41528.875 | 41529.6521 | 416 | 1116 | 316158.1126 | 283.2958 | 0.97372 | 0.0012812 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 283.2958 | 0.97372 | 0.0012812
136468 | 41528.5 | 41529.8264 | 140 | 1907 | 182117.5016 | 95.4995 | 0.56089 | 0.00043118 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-11 | 2014 | 2014 | 2013-09-11 | C | 95.4995 | 0.56089 | 0.00043118
136471 | 41530.5646 | 41530.609 | 1 | 61 | 61 | 1 | 0.00018787 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 1 | 0.00018787 | 3.0798e-06
136473 | 41529.1924 | 41530.8167 | 65 | 2336 | 14334.5909 | 6.1364 | 0.044148 | 0.00020019 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | C | 6.1364 | 0.044148 | 0.00020019
136475 | 41530.3639 | 41530.4882 | 19 | 176 | 3344 | 19 | 0.010299 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | B | 19 | 0.010299 | 5.8517e-05
136477 | 41533.4049 | 41533.4764 | 45 | 100 | 4500 | 45 | 0.013859 | 0.00013859 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | C | 45 | 0.013859 | 0.00013859
136479 | 41529.3861 | 41529.5062 | 6 | 170 | 1020 | 6 | 0.0031414 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-12 | 2014 | 2014 | 2013-09-12 | B | 6 | 0.0031414 | 1.8479e-05
136481 | 41533.5625 | 41533.6438 | 34 | 114 | 3876 | 34 | 0.011937 | 0.00010471 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | C | 34 | 0.011937 | 0.00010471
136484 | 41533.3646 | 41533.5819 | 30 | 310 | 9300 | 30 | 0.028643 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | B | 30 | 0.028643 | 9.2395e-05
136485 | 41533.375 | 41533.6028 | 29 | 325 | 9425 | 29 | 0.029028 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | B | 29 | 0.029028 | 8.9315e-05
136486 | 41533.5486 | 41533.5896 | 23 | 56 | 1288 | 23 | 0.0039668 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | C | 23 | 0.0039668 | 7.0836e-05
136487 | 41530.4764 | 41530.6597 | 9 | 261 | 2349 | 9 | 0.0072345 | 2.7719e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 9 | 0.0072345 | 2.7719e-05
136488 | 41530.7465 | 41530.7549 | 44 | 9 | 396 | 44 | 0.0012196 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 44 | 0.0012196 | 0.00013551
136489 | 41533.3785 | 41533.5972 | 7 | 312 | 2184 | 7 | 0.0067264 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-16 | 2014 | 2014 | 2013-09-16 | B | 7 | 0.0067264 | 2.1559e-05
136490 | 41530.441 | 41530.7382 | 2 | 425 | 850 | 2 | 0.0026179 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-13 | 2014 | 2014 | 2013-09-13 | C | 2 | 0.0026179 | 6.1597e-06
136491 | 41531.4437 | 41533.6424 | 1 | 3163 | 3163 | 1 | 0.0097415 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-14 | 2014 | 2014 | 2013-09-14 | C | 1 | 0.0097415 | 3.0798e-06
136497 | 41534.4757 | 41534.6354 | 5 | 227 | 1135 | 5 | 0.0034956 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 5 | 0.0034956 | 1.5399e-05
136498 | 41534.5785 | 41534.5924 | 6 | 17 | 102 | 6 | 0.00031414 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 6 | 0.00031414 | 1.8479e-05
136499 | 41534.525 | 41534.6611 | 161 | 193 | 31073 | 161 | 0.0957 | 0.00049585 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 161 | 0.0957 | 0.00049585
136500 | 41534.3854 | 41534.6146 | 67 | 327 | 21909 | 67 | 0.067476 | 0.00020635 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 67 | 0.067476 | 0.00020635
136502 | 41534.3646 | 41534.6188 | 2 | 363 | 726 | 2 | 0.002236 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 2 | 0.002236 | 6.1597e-06
136503 | 41534.4187 | 41534.5833 | 168 | 234 | 39312 | 168 | 0.12107 | 0.00051741 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 168 | 0.12107 | 0.00051741
136505 | 41534.3854 | 41534.6139 | 54 | 326 | 17604 | 54 | 0.054218 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 54 | 0.054218 | 0.00016631
136506 | 41534.3542 | 41534.65 | 6 | 423 | 2538 | 6 | 0.0078166 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 6 | 0.0078166 | 1.8479e-05
136508 | 41534.4056 | 41534.6375 | 1 | 331 | 331 | 1 | 0.0010194 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 1 | 0.0010194 | 3.0798e-06
136510 | 41534.375 | 41534.6396 | 117 | 378 | 44226 | 117 | 0.13621 | 0.00036034 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 117 | 0.13621 | 0.00036034
136511 | 41534.3646 | 41534.6292 | 95 | 378 | 35910 | 95 | 0.1106 | 0.00029258 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 95 | 0.1106 | 0.00029258
136512 | 41534.3542 | 41534.5528 | 30 | 283 | 8490 | 30 | 0.026148 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | B | 30 | 0.026148 | 9.2395e-05
136513 | 41534.459 | 41534.5062 | 2 | 65 | 130 | 2 | 0.00040038 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 2 | 0.00040038 | 6.1597e-06
136514 | 41534.9167 | 41534.9583 | 118 | 57 | 6726 | 118 | 0.020715 | 0.00036342 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 118 | 0.020715 | 0.00036342
136516 | 41534.8931 | 41534.9396 | 3 | 64 | 192 | 3 | 0.00059133 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 3 | 0.00059133 | 9.2395e-06
136517 | 41534.7118 | 41534.8701 | 132 | 225 | 21144.0789 | 93.9737 | 0.06512 | 0.00040654 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 93.9737 | 0.06512 | 0.00040654
136521 | 41535.375 | 41535.6306 | 25 | 365 | 9125 | 25 | 0.028104 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | B | 25 | 0.028104 | 7.6996e-05
136522 | 41535.5965 | 41535.6222 | 44 | 34 | 1496 | 44 | 0.0046074 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | C | 44 | 0.0046074 | 0.00013551
136526 | 41535.5056 | 41535.7354 | 2 | 328 | 656 | 2 | 0.0020204 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | C | 2 | 0.0020204 | 6.1597e-06
136531 | 41535.1771 | 41535.2847 | 403 | 152 | 32593.7032 | 214.4323 | 0.10038 | 0.0012412 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | C | 214.4323 | 0.10038 | 0.0012412
136532 | 41534.7604 | 41535.6528 | 5 | 1282 | 6410 | 5 | 0.019742 | 1.5399e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-17 | 2014 | 2014 | 2013-09-17 | C | 5 | 0.019742 | 1.5399e-05
136533 | 41535.875 | 41535.9069 | 4 | 43 | 172 | 4 | 0.00052973 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | C | 4 | 0.00052973 | 1.2319e-05
136535 | 41536.4722 | 41536.4854 | 15 | 16 | 240 | 15 | 0.00073916 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | C | 15 | 0.00073916 | 4.6198e-05
136536 | 41536.4062 | 41536.591 | 12 | 263 | 3156 | 12 | 0.00972 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | B | 12 | 0.00972 | 3.6958e-05
136538 | 41536.3542 | 41536.5243 | 31 | 242 | 7502 | 31 | 0.023105 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | B | 31 | 0.023105 | 9.5475e-05
136540 | 41536.4167 | 41536.6146 | 15 | 282 | 4230 | 15 | 0.013028 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | B | 15 | 0.013028 | 4.6198e-05
136541 | 41536.5417 | 41536.6542 | 7 | 159 | 1113 | 7 | 0.0034279 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | B | 7 | 0.0034279 | 2.1559e-05
136542 | 41536.9354 | 41537.2153 | 9 | 400 | 3600 | 9 | 0.011087 | 2.7719e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | C | 9 | 0.011087 | 2.7719e-05
136543 | 41536.9292 | 41537.0243 | 780 | 134 | 36467.562 | 272.146 | 0.11231 | 0.0024023 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-19 | 2014 | 2014 | 2013-09-19 | C | 272.146 | 0.11231 | 0.0024023
136546 | 41537.2347 | 41537.3382 | 701 | 146 | 43753.9463 | 299.6846 | 0.13476 | 0.002159 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | C | 299.6846 | 0.13476 | 0.002159
136550 | 41537.3861 | 41537.4826 | 44 | 136 | 5984 | 44 | 0.01843 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | B | 44 | 0.01843 | 0.00013551
136554 | 41537.375 | 41537.5556 | 32 | 257 | 8224 | 32 | 0.025329 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | B | 32 | 0.025329 | 9.8555e-05
136555 | 41537.3542 | 41537.5493 | 20 | 278 | 5560 | 20 | 0.017124 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | B | 20 | 0.017124 | 6.1597e-05
136556 | 41537.375 | 41537.5931 | 150 | 311 | 46650 | 150 | 0.14367 | 0.00046198 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | B | 150 | 0.14367 | 0.00046198
136563 | 41537.8125 | 41537.8187 | 2020 | 6 | 10804 | 1800.6667 | 0.033275 | 0.0062213 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | C | 1800.6667 | 0.033275 | 0.0062213
136565 | 41538.9069 | 41538.9257 | 154 | 24 | 3696 | 154 | 0.011383 | 0.0004743 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-21 | 2014 | 2014 | 2013-09-21 | C | 154 | 0.011383 | 0.0004743
136566 | 41539.141 | 41539.1806 | 706 | 54 | 22683.7895 | 420.0702 | 0.069862 | 0.0021744 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 420.0702 | 0.069862 | 0.0021744
136567 | 41539.2306 | 41539.7069 | 34 | 683 | 23222 | 34 | 0.07152 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 34 | 0.07152 | 0.00010471
136568 | 41539.4007 | 41539.5153 | 3 | 162 | 486 | 3 | 0.0014968 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 3 | 0.0014968 | 9.2395e-06
136569 | 41539.4514 | 41539.4931 | 3 | 57 | 171 | 3 | 0.00052665 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 3 | 0.00052665 | 9.2395e-06
136570 | 41539.4917 | 41539.5417 | 8 | 69 | 552 | 8 | 0.0017001 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 8 | 0.0017001 | 2.4639e-05
136571 | 41539.4868 | 41539.5 | 250 | 16 | 4000 | 250 | 0.012319 | 0.00076996 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 250 | 0.012319 | 0.00076996
136572 | 41539.4979 | 41539.9049 | 7 | 583 | 3294.0495 | 5.6502 | 0.010145 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 5.6502 | 0.010145 | 2.1559e-05
136573 | 41539.5764 | 41539.8125 | 6 | 337 | 2022 | 6 | 0.0062274 | 1.8479e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 6 | 0.0062274 | 1.8479e-05
136574 | 41539.4931 | 41539.609 | 1 | 164 | 164 | 1 | 0.00050509 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 1 | 0.00050509 | 3.0798e-06
136575 | 41539.3125 | 41539.3229 | 713 | 12 | 8556 | 713 | 0.026351 | 0.0021959 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 713 | 0.026351 | 0.0021959
136579 | 41538.375 | 41538.6326 | 9 | 368 | 3312 | 9 | 0.0102 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-21 | 2014 | 2014 | 2013-09-21 | B | 9 | 0.0102 | 2.7719e-05
136584 | 41539.2188 | 41539.2299 | 714 | 13 | 4634.5 | 356.5 | 0.014274 | 0.002199 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-22 | 2014 | 2014 | 2013-09-22 | C | 356.5 | 0.014274 | 0.002199
136585 | 41537.5833 | 41537.8333 | 9 | 357 | 3213 | 9 | 0.0098955 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | C | 9 | 0.0098955 | 2.7719e-05
136586 | 41538.6 | 41538.65 | 2 | 69 | 138 | 2 | 0.00042502 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-21 | 2014 | 2014 | 2013-09-21 | C | 2 | 0.00042502 | 6.1597e-06
136588 | 41540.084 | 41540.0875 | 1916 | 2 | 3832 | 1916 | 0.011802 | 0.005901 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 1916 | 0.011802 | 0.005901
136589 | 41540.0479 | 41540.4688 | 306 | 603 | 26539.9604 | 44.0132 | 0.081739 | 0.00094243 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 44.0132 | 0.081739 | 0.00094243
136590 | 41540.1576 | 41540.1715 | 784 | 17 | 13328 | 784 | 0.041048 | 0.0024146 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 784 | 0.041048 | 0.0024146
136592 | 41537.4167 | 41537.534 | 9 | 166 | 1494 | 9 | 0.0046013 | 2.7719e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-20 | 2014 | 2014 | 2013-09-20 | C | 9 | 0.0046013 | 2.7719e-05
136594 | 41540.375 | 41540.6236 | 9 | 355 | 3195 | 9 | 0.0098401 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | B | 9 | 0.0098401 | 2.7719e-05
136595 | 41540.5854 | 41540.6111 | 29 | 34 | 986 | 29 | 0.0030367 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 29 | 0.0030367 | 8.9315e-05
136597 | 41540.6924 | 41540.709 | 53 | 21 | 1113 | 53 | 0.0034279 | 0.00016323 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 53 | 0.0034279 | 0.00016323
136600 | 41540.1396 | 41540.5778 | 47 | 628 | 13930.4532 | 22.1823 | 0.042904 | 0.00014475 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 22.1823 | 0.042904 | 0.00014475
136601 | 41540.0097 | 41540.0514 | 56 | 57 | 3192 | 56 | 0.0098309 | 0.00017247 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 56 | 0.0098309 | 0.00017247
136603 | 41541.3826 | 41541.5035 | 33 | 171 | 5643 | 33 | 0.01738 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | B | 33 | 0.01738 | 0.00010163
136604 | 41541.4201 | 41541.5174 | 22 | 137 | 3014 | 22 | 0.0092826 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | B | 22 | 0.0092826 | 6.7757e-05
136605 | 41541.4986 | 41541.5549 | 178 | 78 | 13884 | 178 | 0.042761 | 0.00054821 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 178 | 0.042761 | 0.00054821
136606 | 41541.391 | 41541.6632 | 36 | 389 | 14004 | 36 | 0.04313 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | B | 36 | 0.04313 | 0.00011087
136610 | 41541.4653 | 41541.4889 | 30 | 31 | 930 | 30 | 0.0028643 | 9.2395e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 30 | 0.0028643 | 9.2395e-05
136611 | 41540.5854 | 41540.7014 | 403 | 164 | 21908.2395 | 133.5868 | 0.067474 | 0.0012412 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-23 | 2014 | 2014 | 2013-09-23 | C | 133.5868 | 0.067474 | 0.0012412
136612 | 41541.6611 | 41541.7069 | 531 | 63 | 13106.8636 | 208.0455 | 0.040367 | 0.0016354 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 208.0455 | 0.040367 | 0.0016354
136613 | 41541.7215 | 41542.7069 | 865 | 1416 | 432868.9049 | 305.6984 | 1.3332 | 0.0026641 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 305.6984 | 1.3332 | 0.0026641
136614 | 41542.0194 | 41542.0222 | 30 | 1 | 30 | 30 | 9.2395e-05 | 9.2395e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 30 | 9.2395e-05 | 9.2395e-05
136615 | 41542.0014 | 41542.134 | 236 | 188 | 23186.9948 | 123.3351 | 0.071412 | 0.00072684 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 123.3351 | 0.071412 | 0.00072684
136616 | 41542.1146 | 41542.1958 | 103 | 114 | 4282.3077 | 37.5641 | 0.013189 | 0.00031722 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 37.5641 | 0.013189 | 0.00031722
136617 | 41542.1875 | 41542.2014 | 288 | 17 | 4896 | 288 | 0.015079 | 0.00088699 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 288 | 0.015079 | 0.00088699
136618 | 41541.9035 | 41541.9174 | 1149 | 17 | 19533 | 1149 | 0.060159 | 0.0035387 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 1149 | 0.060159 | 0.0035387
136619 | 41541.9069 | 41541.9368 | 61 | 40 | 2440 | 61 | 0.0075148 | 0.00018787 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 61 | 0.0075148 | 0.00018787
136620 | 41542.1069 | 41542.15 | 20 | 59 | 1180 | 20 | 0.0036342 | 6.1597e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 20 | 0.0036342 | 6.1597e-05
136621 | 41542.0903 | 41542.125 | 42 | 47 | 1974 | 42 | 0.0060796 | 0.00012935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 42 | 0.0060796 | 0.00012935
136622 | 41541.9931 | 41542.0278 | 99 | 47 | 4653 | 99 | 0.014331 | 0.0003049 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 99 | 0.014331 | 0.0003049
136623 | 41541.8938 | 41542.0215 | 601 | 181 | 83254.0978 | 459.9674 | 0.25641 | 0.001851 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 459.9674 | 0.25641 | 0.001851
136624 | 41541.6104 | 41541.9479 | 1 | 483 | 483 | 1 | 0.0014876 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 1 | 0.0014876 | 3.0798e-06
136625 | 41541.8715 | 41542.0292 | 6098 | 224 | 1356978.185 | 6057.9383 | 4.1793 | 0.018781 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 6057.9383 | 4.1793 | 0.018781
136632 | 41542.3333 | 41542.4611 | 37 | 181 | 6697 | 37 | 0.020626 | 0.00011395 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 37 | 0.020626 | 0.00011395
136635 | 41542.3333 | 41542.4729 | 12 | 198 | 2376 | 12 | 0.0073177 | 3.6958e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 12 | 0.0073177 | 3.6958e-05
136636 | 41542.2326 | 41542.2479 | 775 | 19 | 14725 | 775 | 0.045351 | 0.0023869 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 775 | 0.045351 | 0.0023869
136641 | 41542.2639 | 41542.4861 | 77 | 317 | 23410.45 | 73.85 | 0.0721 | 0.00023715 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 73.85 | 0.0721 | 0.00023715
136642 | 41541.6757 | 41541.7326 | 2949 | 79 | 171140.9756 | 2166.3415 | 0.52709 | 0.0090825 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 2166.3415 | 0.52709 | 0.0090825
136643 | 41542.4167 | 41542.4993 | 19 | 116 | 2204 | 19 | 0.006788 | 5.8517e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 19 | 0.006788 | 5.8517e-05
136644 | 41542.3208 | 41542.3951 | 49 | 104 | 5096 | 49 | 0.015695 | 0.00015091 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 49 | 0.015695 | 0.00015091
136645 | 41541.8965 | 41542.4931 | 149 | 856 | 21920.1769 | 25.6077 | 0.067511 | 0.0004589 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 25.6077 | 0.067511 | 0.0004589
136646 | 41542.3639 | 41542.391 | 301 | 36 | 10836 | 301 | 0.033373 | 0.00092703 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 301 | 0.033373 | 0.00092703
136647 | 41542.1042 | 41542.5611 | 3 | 655 | 1965 | 3 | 0.0060519 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 3 | 0.0060519 | 9.2395e-06
136648 | 41542.3979 | 41542.5674 | 13 | 241 | 3133 | 13 | 0.0096491 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | B | 13 | 0.0096491 | 4.0038e-05
136649 | 41542.4583 | 41542.6222 | 5 | 233 | 1165 | 5 | 0.003588 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 5 | 0.003588 | 1.5399e-05
136650 | 41542.0035 | 41542.6146 | 50 | 877 | 14472.4932 | 16.5023 | 0.044573 | 0.00015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 16.5023 | 0.044573 | 0.00015399
136651 | 41541.8778 | 41541.9167 | 1427 | 53 | 75631 | 1427 | 0.23293 | 0.0043949 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 1427 | 0.23293 | 0.0043949
136652 | 41538.3542 | 41538.6521 | 6 | 426 | 2556 | 6 | 0.0078721 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-21 | 2014 | 2014 | 2013-09-21 | B | 6 | 0.0078721 | 1.8479e-05
136653 | 41542.3333 | 41542.3674 | 288 | 46 | 11107.5918 | 241.4694 | 0.03421 | 0.00088699 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 241.4694 | 0.03421 | 0.00088699
136654 | 41541.8819 | 41542.1229 | 351 | 344 | 118733.5331 | 345.1556 | 0.36568 | 0.001081 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 345.1556 | 0.36568 | 0.001081
136655 | 41543.0597 | 41543.1 | 60 | 55 | 3300 | 60 | 0.010163 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 60 | 0.010163 | 0.00018479
136656 | 41543.0104 | 41543.5014 | 181 | 704 | 12663.0382 | 17.9873 | 0.039 | 0.00055745 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 17.9873 | 0.039 | 0.00055745
136658 | 41542.8396 | 41542.9104 | 8 | 99 | 792 | 8 | 0.0024392 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 8 | 0.0024392 | 2.4639e-05
136659 | 41542.8618 | 41542.9486 | 19 | 122 | 2318 | 19 | 0.0071391 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 19 | 0.0071391 | 5.8517e-05
136660 | 41542.625 | 41542.6514 | 19 | 35 | 665 | 19 | 0.0020481 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 19 | 0.0020481 | 5.8517e-05
136661 | 41542.6875 | 41542.7743 | 10 | 122 | 1220 | 10 | 0.0037574 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 10 | 0.0037574 | 3.0798e-05
136662 | 41542.6528 | 41542.6875 | 3 | 47 | 141 | 3 | 0.00043426 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 3 | 0.00043426 | 9.2395e-06
136663 | 41541.7444 | 41541.9701 | 707 | 322 | 131924.8862 | 409.7046 | 0.40631 | 0.0021774 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 409.7046 | 0.40631 | 0.0021774
136664 | 41543.3056 | 41543.3347 | 77 | 39 | 3003 | 77 | 0.0092488 | 0.00023715 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 77 | 0.0092488 | 0.00023715
136665 | 41542.4514 | 41542.4583 | 11 | 7 | 77 | 11 | 0.00023715 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 11 | 0.00023715 | 3.3878e-05
136666 | 41541.8118 | 41541.8417 | 239 | 40 | 9560 | 239 | 0.029443 | 0.00073608 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 239 | 0.029443 | 0.00073608
136668 | 41541.85 | 41542.1201 | 1210 | 386 | 357551.1054 | 926.2982 | 1.1012 | 0.0037266 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 926.2982 | 1.1012 | 0.0037266
136669 | 41541.8187 | 41542.6271 | 502 | 1161 | 30365.5361 | 26.1546 | 0.093521 | 0.0015461 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 26.1546 | 0.093521 | 0.0015461
136670 | 41542.4792 | 41542.6875 | 8 | 297 | 2376 | 8 | 0.0073177 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 8 | 0.0073177 | 2.4639e-05
136672 | 41541.75 | 41542.3674 | 463 | 886 | 291073.4241 | 328.5253 | 0.89646 | 0.001426 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 328.5253 | 0.89646 | 0.001426
136673 | 41541.9618 | 41542.6264 | 31 | 954 | 29574 | 31 | 0.091083 | 9.5475e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 31 | 0.091083 | 9.5475e-05
136675 | 41541.7812 | 41541.7917 | 513 | 12 | 6156 | 513 | 0.01896 | 0.00158 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 513 | 0.01896 | 0.00158
136677 | 41541.8271 | 41542.3118 | 1 | 695 | 695 | 1 | 0.0021405 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 1 | 0.0021405 | 3.0798e-06
136678 | 41541.791 | 41542.6097 | 431 | 1176 | 286229.8219 | 243.3927 | 0.88154 | 0.0013274 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 243.3927 | 0.88154 | 0.0013274
136679 | 41543.4028 | 41543.4833 | 1 | 113 | 113 | 1 | 0.00034802 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 1 | 0.00034802 | 3.0798e-06
136680 | 41542.125 | 41542.4618 | 58 | 482 | 27956 | 58 | 0.0861 | 0.00017863 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 58 | 0.0861 | 0.00017863
136681 | 41542.7174 | 41542.7465 | 9 | 39 | 351 | 9 | 0.001081 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 9 | 0.001081 | 2.7719e-05
136682 | 41543.4236 | 41543.4972 | 11 | 103 | 1133 | 11 | 0.0034895 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 11 | 0.0034895 | 3.3878e-05
136683 | 41542.4514 | 41542.4618 | 59 | 12 | 708 | 59 | 0.0021805 | 0.00018171 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 59 | 0.0021805 | 0.00018171
136687 | 41543.3993 | 41543.5986 | 19 | 284 | 5396 | 19 | 0.016619 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | B | 19 | 0.016619 | 5.8517e-05
136689 | 41541.459 | 41543.6201 | 1 | 3109 | 3109 | 1 | 0.0095752 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 1 | 0.0095752 | 3.0798e-06
136690 | 41543.3993 | 41543.6181 | 100 | 312 | 31200 | 100 | 0.096091 | 0.00030798 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | B | 100 | 0.096091 | 0.00030798
136695 | 41543.6451 | 41543.6806 | 19 | 48 | 912 | 19 | 0.0028088 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 19 | 0.0028088 | 5.8517e-05
136696 | 41543.709 | 41543.7208 | 238 | 14 | 3332 | 238 | 0.010262 | 0.000733 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 238 | 0.010262 | 0.000733
136698 | 41543.7361 | 41543.7674 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 5 | 0.00064677 | 1.5399e-05
136699 | 41543.6736 | 41543.7882 | 69 | 162 | 11178 | 69 | 0.034426 | 0.00021251 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 69 | 0.034426 | 0.00021251
136700 | 41543.8194 | 41543.8667 | 13 | 65 | 845 | 13 | 0.0026025 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 13 | 0.0026025 | 4.0038e-05
136701 | 41543.7889 | 41543.8722 | 30 | 117 | 3510 | 30 | 0.01081 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 30 | 0.01081 | 9.2395e-05
136702 | 41541.9292 | 41543.6326 | 5 | 2450 | 12250 | 5 | 0.037728 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 5 | 0.037728 | 1.5399e-05
136703 | 41541.75 | 41543.5139 | 16 | 2537 | 8052.478 | 3.174 | 0.0248 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 3.174 | 0.0248 | 4.9277e-05
136704 | 41541.75 | 41543.5333 | 22 | 2565 | 44314.1706 | 17.2765 | 0.13648 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 17.2765 | 0.13648 | 6.7757e-05
136705 | 41541.75 | 41543.5771 | 8 | 2628 | 21024 | 8 | 0.064751 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 8 | 0.064751 | 2.4639e-05
136706 | 41541.75 | 41542.7368 | 13 | 1418 | 18434 | 13 | 0.056774 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 13 | 0.056774 | 4.0038e-05
136707 | 41543.5361 | 41543.6007 | 1712 | 90 | 62157.0968 | 690.6344 | 0.19143 | 0.0052727 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 690.6344 | 0.19143 | 0.0052727
136708 | 41541.3785 | 41543.4167 | 366 | 2932 | 409079.433 | 139.5223 | 1.2599 | 0.0011272 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 139.5223 | 1.2599 | 0.0011272
136709 | 41541.9243 | 41543.5417 | 345 | 2326 | 98862.4903 | 42.5032 | 0.30448 | 0.0010625 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 42.5032 | 0.30448 | 0.0010625
136710 | 41541.7125 | 41542.6347 | 702 | 1325 | 267943.3358 | 202.2214 | 0.82522 | 0.002162 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 202.2214 | 0.82522 | 0.002162
136711 | 41541.9826 | 41542.6979 | 3 | 1027 | 3081 | 3 | 0.009489 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 3 | 0.009489 | 9.2395e-06
136712 | 41544.4201 | 41544.559 | 5 | 197 | 985 | 5 | 0.0030336 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | C | 5 | 0.0030336 | 1.5399e-05
136714 | 41541.6833 | 41542.5417 | 800 | 1233 | 80162.9563 | 65.0146 | 0.24689 | 0.0024639 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-24 | 2014 | 2014 | 2013-09-24 | C | 65.0146 | 0.24689 | 0.0024639
136715 | 41544.3958 | 41544.6326 | 15 | 338 | 5070 | 15 | 0.015615 | 4.6198e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | C | 15 | 0.015615 | 4.6198e-05
136716 | 41543.3542 | 41543.6444 | 6 | 415 | 2490 | 6 | 0.0076688 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | B | 6 | 0.0076688 | 1.8479e-05
136717 | 41544.7278 | 41544.7639 | 16 | 49 | 784 | 16 | 0.0024146 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | C | 16 | 0.0024146 | 4.9277e-05
136719 | 41544.7917 | 41544.8542 | 76 | 87 | 6612 | 76 | 0.020364 | 0.00023407 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | C | 76 | 0.020364 | 0.00023407
136720 | 41544.7326 | 41544.9028 | 169 | 242 | 8077.8612 | 33.3796 | 0.024879 | 0.00052049 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | C | 33.3796 | 0.024879 | 0.00052049
136722 | 41545.0563 | 41545.1007 | 175 | 61 | 10675 | 175 | 0.032877 | 0.00053897 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 175 | 0.032877 | 0.00053897
136726 | 41542.625 | 41544.6771 | 1 | 2952 | 2952 | 1 | 0.0090917 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 1 | 0.0090917 | 3.0798e-06
136727 | 41543.5271 | 41544.5139 | 3 | 1418 | 4254 | 3 | 0.013102 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | C | 3 | 0.013102 | 9.2395e-06
136728 | 41545.4757 | 41545.5694 | 662 | 132 | 43175.7333 | 327.0889 | 0.13297 | 0.0020389 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 327.0889 | 0.13297 | 0.0020389
136731 | 41545.2986 | 41545.3569 | 116 | 81 | 9396 | 116 | 0.028938 | 0.00035726 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | B | 116 | 0.028938 | 0.00035726
136732 | 41545.6181 | 41545.6306 | 22 | 15 | 330 | 22 | 0.0010163 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 22 | 0.0010163 | 6.7757e-05
136733 | 41545.5639 | 41545.6889 | 142 | 177 | 11364.3833 | 64.2056 | 0.035001 | 0.00043734 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 64.2056 | 0.035001 | 0.00043734
136734 | 41545.6354 | 41545.6889 | 3 | 74 | 222 | 3 | 0.00068372 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 3 | 0.00068372 | 9.2395e-06
136736 | 41545.8632 | 41545.9604 | 145 | 137 | 6239.3714 | 45.5429 | 0.019216 | 0.00044658 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 45.5429 | 0.019216 | 0.00044658
136737 | 41545.9333 | 41545.95 | 237 | 21 | 4977 | 237 | 0.015328 | 0.00072992 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 237 | 0.015328 | 0.00072992
136738 | 41545.9257 | 41546.05 | 1050 | 176 | 90500.3799 | 514.2067 | 0.27873 | 0.0032338 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 514.2067 | 0.27873 | 0.0032338
136739 | 41545.8299 | 41545.9542 | 838 | 176 | 41899.7989 | 238.067 | 0.12904 | 0.0025809 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 238.067 | 0.12904 | 0.0025809
136740 | 41545.8583 | 41545.8667 | 406 | 9 | 3654 | 406 | 0.011254 | 0.0012504 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 406 | 0.011254 | 0.0012504
136741 | 41545.5431 | 41545.6458 | 31 | 145 | 4495 | 31 | 0.013844 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 31 | 0.013844 | 9.5475e-05
136742 | 41545.3021 | 41545.6438 | 112 | 489 | 54768 | 112 | 0.16868 | 0.00034494 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 112 | 0.16868 | 0.00034494
136743 | 41545.384 | 41545.4688 | 884 | 119 | 62184.3279 | 522.5574 | 0.19152 | 0.0027226 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 522.5574 | 0.19152 | 0.0027226
136744 | 41545.5792 | 41545.7222 | 30 | 203 | 6090 | 30 | 0.018756 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 30 | 0.018756 | 9.2395e-05
136745 | 41546.2188 | 41546.3208 | 237 | 144 | 24973.7143 | 173.4286 | 0.076915 | 0.00072992 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 173.4286 | 0.076915 | 0.00072992
136748 | 41545.6111 | 41546.5132 | 5 | 1296 | 6480 | 5 | 0.019957 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 5 | 0.019957 | 1.5399e-05
136750 | 41545.6681 | 41545.6979 | 5 | 40 | 200 | 5 | 0.00061597 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-28 | 2014 | 2014 | 2013-09-28 | C | 5 | 0.00061597 | 1.5399e-05
136751 | 41546.6458 | 41546.75 | 1 | 147 | 147 | 1 | 0.00045274 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 1 | 0.00045274 | 3.0798e-06
136752 | 41546.8951 | 41547.034 | 228 | 197 | 28501.96 | 144.68 | 0.087782 | 0.0007022 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 144.68 | 0.087782 | 0.0007022
136753 | 41546.941 | 41547.0604 | 25 | 169 | 4225 | 25 | 0.013012 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 25 | 0.013012 | 7.6996e-05
136755 | 41547.1028 | 41547.1924 | 321 | 126 | 27346.8837 | 217.0388 | 0.084224 | 0.00098863 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 217.0388 | 0.084224 | 0.00098863
136756 | 41546.9958 | 41547.0715 | 208 | 106 | 22048 | 208 | 0.067904 | 0.00064061 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 208 | 0.067904 | 0.00064061
136758 | 41547.4028 | 41547.5 | 8 | 137 | 1096 | 8 | 0.0033755 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 8 | 0.0033755 | 2.4639e-05
136759 | 41547.3736 | 41547.4236 | 2 | 69 | 138 | 2 | 0.00042502 | 6.1597e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 2 | 0.00042502 | 6.1597e-06
136761 | 41547.2583 | 41547.4583 | 3 | 285 | 855 | 3 | 0.0026333 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 3 | 0.0026333 | 9.2395e-06
136764 | 41547.5431 | 41547.6132 | 696 | 98 | 42747.4059 | 436.198 | 0.13166 | 0.0021436 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 436.198 | 0.13166 | 0.0021436
136765 | 41547.6 | 41547.7049 | 3 | 148 | 444 | 3 | 0.0013674 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 3 | 0.0013674 | 9.2395e-06
136766 | 41547.6042 | 41547.7639 | 1 | 227 | 227 | 1 | 0.00069912 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 1 | 0.00069912 | 3.0798e-06
136767 | 41547.7069 | 41547.7472 | 896 | 55 | 30955.5172 | 562.8276 | 0.095338 | 0.0027595 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 562.8276 | 0.095338 | 0.0027595
136770 | 41547.7618 | 41547.9569 | 963 | 278 | 100234.3345 | 360.5552 | 0.30871 | 0.0029659 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 360.5552 | 0.30871 | 0.0029659
136771 | 41547.8083 | 41548.5174 | 16 | 1018 | 1962.2174 | 1.9275 | 0.0060433 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 1.9275 | 0.0060433 | 4.9277e-05
136772 | 41547.7806 | 41547.7986 | 55 | 23 | 1265 | 55 | 0.003896 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 55 | 0.003896 | 0.00016939
136774 | 41547.9979 | 41548.0403 | 1395 | 58 | 69159.7705 | 1192.4098 | 0.213 | 0.0042964 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 1192.4098 | 0.213 | 0.0042964
136776 | 41548.3889 | 41548.4875 | 66 | 139 | 9174 | 66 | 0.028254 | 0.00020327 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 66 | 0.028254 | 0.00020327
136777 | 41547.8299 | 41548.434 | 5 | 867 | 4335 | 5 | 0.013351 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 5 | 0.013351 | 1.5399e-05
136778 | 41548.4375 | 41548.5021 | 1 | 90 | 90 | 1 | 0.00027719 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | C | 1 | 0.00027719 | 3.0798e-06
136779 | 41548.375 | 41548.5625 | 3 | 267 | 801 | 3 | 0.002467 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 3 | 0.002467 | 9.2395e-06
136780 | 41548.375 | 41548.559 | 6 | 262 | 1572 | 6 | 0.0048415 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 6 | 0.0048415 | 1.8479e-05
136781 | 41546.6632 | 41546.709 | 413 | 63 | 14785.9091 | 234.697 | 0.045538 | 0.001272 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-09-29 | 2014 | 2014 | 2013-09-29 | C | 234.697 | 0.045538 | 0.001272
136782 | 41548.4375 | 41548.5646 | 8 | 180 | 1440 | 8 | 0.004435 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | C | 8 | 0.004435 | 2.4639e-05
136783 | 41548.4743 | 41548.5625 | 55 | 124 | 6820 | 55 | 0.021005 | 0.00016939 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | C | 55 | 0.021005 | 0.00016939
136785 | 41547.3125 | 41547.6458 | 1 | 477 | 477 | 1 | 0.0014691 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 1 | 0.0014691 | 3.0798e-06
136786 | 41548.3819 | 41548.6285 | 5 | 352 | 1760 | 5 | 0.0054205 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 5 | 0.0054205 | 1.5399e-05
136787 | 41547.6514 | 41547.6604 | 29 | 10 | 290 | 29 | 0.00089315 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 29 | 0.00089315 | 8.9315e-05
136788 | 41548.4792 | 41548.7236 | 3 | 349 | 1047 | 3 | 0.0032246 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | C | 3 | 0.0032246 | 9.2395e-06
136789 | 41548.3646 | 41548.6451 | 144 | 401 | 57744 | 144 | 0.17784 | 0.0004435 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 144 | 0.17784 | 0.0004435
136791 | 41548.6937 | 41548.7208 | 766 | 36 | 16111.3846 | 447.5385 | 0.049621 | 0.0023592 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | C | 447.5385 | 0.049621 | 0.0023592
136793 | 41549.375 | 41549.3958 | 10 | 27 | 270 | 10 | 0.00083156 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | B | 10 | 0.00083156 | 3.0798e-05
136795 | 41547.641 | 41547.7028 | 2 | 86 | 172 | 2 | 0.00052973 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | C | 2 | 0.00052973 | 6.1597e-06
136797 | 41549.3778 | 41549.5903 | 43 | 303 | 13029 | 43 | 0.040127 | 0.00013243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | B | 43 | 0.040127 | 0.00013243
136798 | 41549.466 | 41549.5208 | 17 | 76 | 1292 | 17 | 0.0039792 | 5.2357e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | C | 17 | 0.0039792 | 5.2357e-05
136799 | 41549.3854 | 41549.6285 | 72 | 347 | 24984 | 72 | 0.076947 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | B | 72 | 0.076947 | 0.00022175
136800 | 41549.4167 | 41549.5965 | 880 | 256 | 219550.1467 | 857.6178 | 0.67618 | 0.0027103 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | B | 857.6178 | 0.67618 | 0.0027103
136801 | 41549.3694 | 41549.4 | 616 | 41 | 18412.7273 | 449.0909 | 0.056708 | 0.0018972 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | C | 449.0909 | 0.056708 | 0.0018972
136802 | 41549.6681 | 41549.7562 | 334 | 124 | 33307.1811 | 268.6063 | 0.10258 | 0.0010287 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | C | 268.6063 | 0.10258 | 0.0010287
136805 | 41549.75 | 41549.7674 | 35 | 22 | 770 | 35 | 0.0023715 | 0.00010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | C | 35 | 0.0023715 | 0.00010779
136806 | 41550.2799 | 41550.3778 | 179 | 138 | 9433.9149 | 68.3617 | 0.029055 | 0.00055129 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | C | 68.3617 | 0.029055 | 0.00055129
136807 | 41550.5437 | 41550.5549 | 3 | 13 | 39 | 3 | 0.00012011 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | C | 3 | 0.00012011 | 9.2395e-06
136808 | 41550.5347 | 41550.5972 | 7 | 87 | 609 | 7 | 0.0018756 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 7 | 0.0018756 | 2.1559e-05
136809 | 41550.4583 | 41550.4931 | 5 | 47 | 235 | 5 | 0.00072376 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 5 | 0.00072376 | 1.5399e-05
136810 | 41550.3854 | 41550.4306 | 5 | 62 | 310 | 5 | 0.00095475 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 5 | 0.00095475 | 1.5399e-05
136811 | 41550.3854 | 41550.4479 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 2 | 0.00053589 | 6.1597e-06
136812 | 41550.4583 | 41550.4896 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 5 | 0.00064677 | 1.5399e-05
136814 | 41550.4722 | 41550.5521 | 3 | 112 | 336 | 3 | 0.0010348 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 3 | 0.0010348 | 9.2395e-06
136815 | 41550.5625 | 41550.625 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 2 | 0.00053589 | 6.1597e-06
136816 | 41550.375 | 41550.5194 | 22 | 205 | 4510 | 22 | 0.01389 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 22 | 0.01389 | 6.7757e-05
136817 | 41542.6556 | 41542.8194 | 2 | 233 | 466 | 2 | 0.0014352 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-25 | 2014 | 2014 | 2013-09-25 | C | 2 | 0.0014352 | 6.1597e-06
136818 | 41550.6354 | 41550.6674 | 17 | 43 | 731 | 17 | 0.0022514 | 5.2357e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | C | 17 | 0.0022514 | 5.2357e-05
136819 | 41550.3854 | 41550.5903 | 17 | 292 | 4964 | 17 | 0.015288 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 17 | 0.015288 | 5.2357e-05
136820 | 41550.3861 | 41550.5042 | 72 | 167 | 12024 | 72 | 0.037032 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 72 | 0.037032 | 0.00022175
136821 | 41550.3708 | 41550.4958 | 176 | 177 | 31152 | 176 | 0.095943 | 0.00054205 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 176 | 0.095943 | 0.00054205
136823 | 41550.3861 | 41550.6458 | 4 | 371 | 1484 | 4 | 0.0045705 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 4 | 0.0045705 | 1.2319e-05
136825 | 41550.3958 | 41550.4736 | 5 | 109 | 545 | 5 | 0.0016785 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 5 | 0.0016785 | 1.5399e-05
136833 | 41550.5417 | 41550.5625 | 5 | 27 | 135 | 5 | 0.00041578 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 5 | 0.00041578 | 1.5399e-05
136834 | 41550.3785 | 41550.3965 | 8 | 23 | 184 | 8 | 0.00056669 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-03 | 2014 | 2014 | 2013-10-03 | B | 8 | 0.00056669 | 2.4639e-05
136835 | 41551.4632 | 41551.4688 | 5 | 5 | 25 | 5 | 7.6996e-05 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | C | 5 | 7.6996e-05 | 1.5399e-05
136838 | 41551.4799 | 41551.5903 | 68 | 156 | 10608 | 68 | 0.032671 | 0.00020943 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | B | 68 | 0.032671 | 0.00020943
136839 | 41551.375 | 41551.6208 | 1 | 351 | 351 | 1 | 0.001081 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | B | 1 | 0.001081 | 3.0798e-06
136840 | 41551.6375 | 41551.6562 | 65 | 24 | 1560 | 65 | 0.0048046 | 0.00020019 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | C | 65 | 0.0048046 | 0.00020019
136841 | 41551.3792 | 41551.3875 | 154 | 9 | 1386 | 154 | 0.0042687 | 0.0004743 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | C | 154 | 0.0042687 | 0.0004743
136843 | 41547.375 | 41547.5444 | 2 | 241 | 482 | 2 | 0.0014845 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-30 | 2014 | 2014 | 2013-09-30 | B | 2 | 0.0014845 | 6.1597e-06
136844 | 41551.6424 | 41551.6979 | 598 | 77 | 46046 | 598 | 0.14181 | 0.0018417 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | C | 598 | 0.14181 | 0.0018417
136845 | 41551.375 | 41551.625 | 53 | 357 | 18921 | 53 | 0.058274 | 0.00016323 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | B | 53 | 0.058274 | 0.00016323
136846 | 41551.4167 | 41551.4361 | 190 | 25 | 4750 | 190 | 0.014629 | 0.00058517 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-04 | 2014 | 2014 | 2013-10-04 | B | 190 | 0.014629 | 0.00058517
136848 | 41552.375 | 41552.5097 | 16 | 191 | 3056 | 16 | 0.009412 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-05 | 2014 | 2014 | 2013-10-05 | B | 16 | 0.009412 | 4.9277e-05
136850 | 41552.7917 | 41552.9563 | 2 | 234 | 468 | 2 | 0.0014414 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-05 | 2014 | 2014 | 2013-10-05 | C | 2 | 0.0014414 | 6.1597e-06
136852 | 41553.375 | 41553.5972 | 2 | 317 | 634 | 2 | 0.0019526 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-06 | 2014 | 2014 | 2013-10-06 | B | 2 | 0.0019526 | 6.1597e-06
136854 | 41553.8542 | 41554.0819 | 2 | 325 | 650 | 2 | 0.0020019 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-06 | 2014 | 2014 | 2013-10-06 | C | 2 | 0.0020019 | 6.1597e-06
136855 | 41553.6292 | 41554.2201 | 1301 | 848 | 135732.8132 | 160.0623 | 0.41804 | 0.0040069 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-06 | 2014 | 2014 | 2013-10-06 | C | 160.0623 | 0.41804 | 0.0040069
136858 | 41554.3812 | 41554.4819 | 277 | 142 | 21353.8621 | 150.3793 | 0.065767 | 0.00085312 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | C | 150.3793 | 0.065767 | 0.00085312
136859 | 41554.375 | 41554.5312 | 4 | 222 | 888 | 4 | 0.0027349 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | B | 4 | 0.0027349 | 1.2319e-05
136860 | 41554.3875 | 41554.5375 | 10 | 213 | 2130 | 10 | 0.0065601 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | B | 10 | 0.0065601 | 3.0798e-05
136861 | 41554.3854 | 41554.5833 | 27 | 282 | 7614 | 27 | 0.02345 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | B | 27 | 0.02345 | 8.3156e-05
136864 | 41554.5924 | 41554.6438 | 64 | 71 | 4544 | 64 | 0.013995 | 0.00019711 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | C | 64 | 0.013995 | 0.00019711
136866 | 41554.9368 | 41554.9806 | 569 | 60 | 33165.7143 | 552.7619 | 0.10215 | 0.0017524 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | C | 552.7619 | 0.10215 | 0.0017524
136867 | 41554.0639 | 41555.6042 | 316 | 2215 | 22391.6727 | 10.1091 | 0.068963 | 0.00097323 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | C | 10.1091 | 0.068963 | 0.00097323
136869 | 41554.6903 | 41554.7778 | 77 | 123 | 9471 | 77 | 0.029169 | 0.00023715 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-07 | 2014 | 2014 | 2013-10-07 | C | 77 | 0.029169 | 0.00023715
136872 | 41555.3778 | 41555.625 | 40 | 353 | 14120 | 40 | 0.043487 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | B | 40 | 0.043487 | 0.00012319
136873 | 41555.3667 | 41555.5944 | 28 | 325 | 9100 | 28 | 0.028027 | 8.6236e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | B | 28 | 0.028027 | 8.6236e-05
136875 | 41555.3958 | 41555.6944 | 137 | 427 | 58499 | 137 | 0.18017 | 0.00042194 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | B | 137 | 0.18017 | 0.00042194
136876 | 41555.6215 | 41555.6417 | 6 | 26 | 156 | 6 | 0.00048046 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 6 | 0.00048046 | 1.8479e-05
136877 | 41555.4264 | 41555.4854 | 33 | 82 | 2706 | 33 | 0.0083341 | 0.00010163 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 33 | 0.0083341 | 0.00010163
136878 | 41555.5361 | 41555.5646 | 137 | 38 | 5206 | 137 | 0.016034 | 0.00042194 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 137 | 0.016034 | 0.00042194
136879 | 41555.6472 | 41555.7319 | 6 | 119 | 714 | 6 | 0.002199 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 6 | 0.002199 | 1.8479e-05
136880 | 41555.8486 | 41555.9104 | 415 | 86 | 20397.4607 | 237.1798 | 0.062821 | 0.0012781 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 237.1798 | 0.062821 | 0.0012781
136881 | 41555.8014 | 41555.8313 | 26 | 40 | 1040 | 26 | 0.003203 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | C | 26 | 0.003203 | 8.0076e-05
136882 | 41555.9583 | 41556.2056 | 19 | 353 | 6707 | 19 | 0.020656 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | B | 19 | 0.020656 | 5.8517e-05
136883 | 41556.0306 | 41556.0424 | 172 | 14 | 2408 | 172 | 0.0074163 | 0.00052973 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 172 | 0.0074163 | 0.00052973
136884 | 41556.4292 | 41556.7104 | 330 | 402 | 25158.2519 | 62.5827 | 0.077483 | 0.0010163 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 62.5827 | 0.077483 | 0.0010163
136885 | 41556.4757 | 41556.5764 | 8 | 142 | 1136 | 8 | 0.0034987 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 8 | 0.0034987 | 2.4639e-05
136888 | 41556.584 | 41556.641 | 6 | 79 | 474 | 6 | 0.0014598 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 6 | 0.0014598 | 1.8479e-05
136890 | 41556.3854 | 41556.6389 | 31 | 362 | 11222 | 31 | 0.034562 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | B | 31 | 0.034562 | 9.5475e-05
136895 | 41556.3771 | 41556.541 | 18 | 233 | 4194 | 18 | 0.012917 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | B | 18 | 0.012917 | 5.5437e-05
136896 | 41556.4396 | 41556.5833 | 1 | 204 | 204 | 1 | 0.00062829 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | B | 1 | 0.00062829 | 3.0798e-06
136898 | 41556.3979 | 41556.4229 | 4 | 33 | 132 | 4 | 0.00040654 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 4 | 0.00040654 | 1.2319e-05
136900 | 41556.4882 | 41556.5396 | 92 | 71 | 6532 | 92 | 0.020118 | 0.00028335 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 92 | 0.020118 | 0.00028335
136903 | 41556.5285 | 41556.6979 | 73 | 241 | 17593 | 73 | 0.054184 | 0.00022483 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 73 | 0.054184 | 0.00022483
136905 | 41556.5708 | 41556.625 | 131 | 75 | 9825 | 131 | 0.030259 | 0.00040346 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 131 | 0.030259 | 0.00040346
136906 | 41556.4708 | 41556.5514 | 312 | 113 | 8626.9655 | 76.3448 | 0.02657 | 0.00096091 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 76.3448 | 0.02657 | 0.00096091
136907 | 41556.4215 | 41556.525 | 287 | 146 | 20882.8993 | 143.0336 | 0.064316 | 0.00088391 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 143.0336 | 0.064316 | 0.00088391
136909 | 41556.7569 | 41556.8542 | 2 | 137 | 274 | 2 | 0.00084388 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 2 | 0.00084388 | 6.1597e-06
136913 | 41556.85 | 41556.8722 | 1 | 29 | 29 | 1 | 8.9315e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 1 | 8.9315e-05 | 3.0798e-06
136914 | 41557.009 | 41557.0257 | 2160 | 21 | 45360 | 2160 | 0.1397 | 0.0066525 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 2160 | 0.1397 | 0.0066525
136915 | 41556.6896 | 41556.8361 | 267 | 208 | 14418.0474 | 69.3175 | 0.044405 | 0.00082232 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-09 | 2014 | 2014 | 2013-10-09 | C | 69.3175 | 0.044405 | 0.00082232
136917 | 41557.009 | 41557.0229 | 143 | 17 | 2431 | 143 | 0.0074871 | 0.00044042 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 143 | 0.0074871 | 0.00044042
136918 | 41557.2625 | 41557.3632 | 22 | 142 | 3124 | 22 | 0.0096214 | 6.7757e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 22 | 0.0096214 | 6.7757e-05
136922 | 41557.375 | 41557.5451 | 15 | 242 | 3630 | 15 | 0.01118 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | B | 15 | 0.01118 | 4.6198e-05
136926 | 41557.5507 | 41557.5542 | 5 | 2 | 10 | 5 | 3.0798e-05 | 1.5399e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 5 | 3.0798e-05 | 1.5399e-05
136928 | 41557.5868 | 41557.5938 | 6 | 7 | 42 | 6 | 0.00012935 | 1.8479e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 6 | 0.00012935 | 1.8479e-05
136930 | 41557.466 | 41557.6924 | 8 | 323 | 2584 | 8 | 0.0079583 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | B | 8 | 0.0079583 | 2.4639e-05
136932 | 41557.4611 | 41557.5306 | 2 | 97 | 194 | 2 | 0.00059749 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 2 | 0.00059749 | 6.1597e-06
136933 | 41557.5743 | 41557.6514 | 2 | 108 | 216 | 2 | 0.00066525 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | C | 2 | 0.00066525 | 6.1597e-06
136936 | 41558.1924 | 41558.2771 | 253 | 119 | 11366.4508 | 95.5164 | 0.035007 | 0.0007792 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 95.5164 | 0.035007 | 0.0007792
136937 | 41558.2125 | 41558.2403 | 31 | 37 | 1147 | 31 | 0.0035326 | 9.5475e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 31 | 0.0035326 | 9.5475e-05
136940 | 41558.3472 | 41558.3854 | 29 | 52 | 1508 | 29 | 0.0046444 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 29 | 0.0046444 | 8.9315e-05
136941 | 41558.3889 | 41558.4493 | 188 | 84 | 10456.5517 | 124.4828 | 0.032205 | 0.00057901 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 124.4828 | 0.032205 | 0.00057901
136942 | 41558.55 | 41558.5687 | 57 | 24 | 1368 | 57 | 0.0042132 | 0.00017555 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 57 | 0.0042132 | 0.00017555
136944 | 41558.5917 | 41558.7049 | 9 | 160 | 1440 | 9 | 0.004435 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 9 | 0.004435 | 2.7719e-05
136945 | 41558.5597 | 41558.5743 | 4 | 18 | 72 | 4 | 0.00022175 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 4 | 0.00022175 | 1.2319e-05
136948 | 41558.8653 | 41558.9917 | 271 | 179 | 47440.9011 | 265.033 | 0.14611 | 0.00083464 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 265.033 | 0.14611 | 0.00083464
136950 | 41558.9944 | 41559.1076 | 141 | 160 | 13136.6871 | 82.1043 | 0.040459 | 0.00043426 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-11 | 2014 | 2014 | 2013-10-11 | C | 82.1043 | 0.040459 | 0.00043426
136953 | 41559.0819 | 41559.4757 | 781 | 564 | 88303.3016 | 156.5661 | 0.27196 | 0.0024054 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 156.5661 | 0.27196 | 0.0024054
136954 | 41559.0042 | 41559.4062 | 311 | 576 | 34375.9585 | 59.6805 | 0.10587 | 0.00095783 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 59.6805 | 0.10587 | 0.00095783
136956 | 41559.1375 | 41559.2465 | 462 | 154 | 65259.707 | 423.7643 | 0.20099 | 0.0014229 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 423.7643 | 0.20099 | 0.0014229
136959 | 41559.0174 | 41559.4431 | 679 | 610 | 78294.9429 | 128.3524 | 0.24114 | 0.0020912 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 128.3524 | 0.24114 | 0.0020912
136963 | 41559.5736 | 41559.6181 | 26 | 61 | 1586 | 26 | 0.0048846 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 26 | 0.0048846 | 8.0076e-05
136964 | 41559.7264 | 41559.809 | 108 | 116 | 12528 | 108 | 0.038584 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 108 | 0.038584 | 0.00033262
136965 | 41559.934 | 41560.0556 | 3 | 172 | 516 | 3 | 0.0015892 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-12 | 2014 | 2014 | 2013-10-12 | C | 3 | 0.0015892 | 9.2395e-06
136970 | 41560.3681 | 41560.4042 | 18 | 49 | 882 | 18 | 0.0027164 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-13 | 2014 | 2014 | 2013-10-13 | C | 18 | 0.0027164 | 5.5437e-05
136972 | 41560.5694 | 41560.6118 | 14 | 58 | 812 | 14 | 0.0025008 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-13 | 2014 | 2014 | 2013-10-13 | C | 14 | 0.0025008 | 4.3118e-05
136974 | 41560.5833 | 41560.8063 | 1 | 318 | 318 | 1 | 0.00097939 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-13 | 2014 | 2014 | 2013-10-13 | C | 1 | 0.00097939 | 3.0798e-06
136979 | 41561.3063 | 41561.375 | 17 | 96 | 1632 | 17 | 0.0050263 | 5.2357e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 17 | 0.0050263 | 5.2357e-05
136981 | 41561.3889 | 41561.4271 | 4 | 52 | 208 | 4 | 0.00064061 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 4 | 0.00064061 | 1.2319e-05
136984 | 41544.4299 | 41544.5153 | 2 | 120 | 240 | 2 | 0.00073916 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-27 | 2014 | 2014 | 2013-09-27 | B | 2 | 0.00073916 | 6.1597e-06
136987 | 41561.5347 | 41561.5736 | 2 | 53 | 106 | 2 | 0.00032646 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 2 | 0.00032646 | 6.1597e-06
136990 | 41561.384 | 41561.5049 | 4 | 171 | 684 | 4 | 0.0021066 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 4 | 0.0021066 | 1.2319e-05
136991 | 41561.5278 | 41561.6104 | 5 | 116 | 580 | 5 | 0.0017863 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 5 | 0.0017863 | 1.5399e-05
136993 | 41561.4639 | 41561.4965 | 6 | 44 | 264 | 6 | 0.00081308 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 6 | 0.00081308 | 1.8479e-05
136994 | 41561.5451 | 41561.5833 | 4 | 52 | 208 | 4 | 0.00064061 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 4 | 0.00064061 | 1.2319e-05
136995 | 41561.3785 | 41561.4201 | 5 | 57 | 285 | 5 | 0.00087775 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 5 | 0.00087775 | 1.5399e-05
136996 | 41561.5451 | 41561.5972 | 4 | 72 | 288 | 4 | 0.00088699 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 4 | 0.00088699 | 1.2319e-05
136997 | 41561.4618 | 41561.5035 | 7 | 57 | 399 | 7 | 0.0012289 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 7 | 0.0012289 | 2.1559e-05
136998 | 41561.3854 | 41561.434 | 15 | 67 | 1005 | 15 | 0.0030952 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 15 | 0.0030952 | 4.6198e-05
136999 | 41561.4583 | 41561.5035 | 8 | 62 | 496 | 8 | 0.0015276 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 8 | 0.0015276 | 2.4639e-05
137000 | 41561.375 | 41561.4049 | 6 | 40 | 240 | 6 | 0.00073916 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 6 | 0.00073916 | 1.8479e-05
137001 | 41561.5472 | 41561.6271 | 2 | 112 | 224 | 2 | 0.00068988 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 2 | 0.00068988 | 6.1597e-06
137002 | 41561.4354 | 41561.6438 | 3 | 297 | 891 | 3 | 0.0027441 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 3 | 0.0027441 | 9.2395e-06
137005 | 41561.9167 | 41561.9771 | 12 | 84 | 1008 | 12 | 0.0031045 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | B | 12 | 0.0031045 | 3.6958e-05
137006 | 41561.5257 | 41561.5771 | 11 | 71 | 781 | 11 | 0.0024054 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 11 | 0.0024054 | 3.3878e-05
137007 | 41561.9944 | 41562.0076 | 144 | 16 | 2304 | 144 | 0.007096 | 0.0004435 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 144 | 0.007096 | 0.0004435
137009 | 41561.4306 | 41561.6764 | 72 | 351 | 19080.9153 | 54.3616 | 0.058766 | 0.00022175 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 54.3616 | 0.058766 | 0.00022175
137010 | 41561.7236 | 41561.7514 | 184 | 37 | 6808 | 184 | 0.020968 | 0.00056669 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 184 | 0.020968 | 0.00056669
137011 | 41561.8319 | 41561.8438 | 132 | 14 | 1848 | 132 | 0.0056915 | 0.00040654 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 132 | 0.0056915 | 0.00040654
137012 | 41562.3528 | 41562.4243 | 538 | 100 | 46596.1165 | 465.9612 | 0.14351 | 0.001657 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 465.9612 | 0.14351 | 0.001657
137013 | 41561.7812 | 41561.8243 | 16 | 59 | 944 | 16 | 0.0029074 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 16 | 0.0029074 | 4.9277e-05
137019 | 41562.2965 | 41562.3417 | 185 | 62 | 9739.7231 | 157.0923 | 0.029997 | 0.00056977 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 157.0923 | 0.029997 | 0.00056977
137024 | 41561.2722 | 41563.6597 | 256 | 3435 | 395166.8761 | 115.0413 | 1.2171 | 0.00078844 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 115.0413 | 1.2171 | 0.00078844
137029 | 41562.5062 | 41562.5243 | 10 | 23 | 230 | 10 | 0.00070836 | 3.0798e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 10 | 0.00070836 | 3.0798e-05
137030 | 41561.8271 | 41561.8535 | 4304 | 35 | 150640 | 4304 | 0.46395 | 0.013256 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 4304 | 0.46395 | 0.013256
137031 | 41561.8271 | 41561.8458 | 634 | 24 | 15216 | 634 | 0.046863 | 0.0019526 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 634 | 0.046863 | 0.0019526
137032 | 41561.8271 | 41561.8458 | 594 | 24 | 14256 | 594 | 0.043906 | 0.0018294 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 594 | 0.043906 | 0.0018294
137033 | 41561.8271 | 41561.8583 | 3180 | 42 | 133560 | 3180 | 0.41134 | 0.0097939 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 3180 | 0.41134 | 0.0097939
137034 | 41561.9028 | 41561.9722 | 97 | 97 | 9409 | 97 | 0.028978 | 0.00029874 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 97 | 0.028978 | 0.00029874
137035 | 41562.6542 | 41562.6826 | 18 | 38 | 684 | 18 | 0.0021066 | 5.5437e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 18 | 0.0021066 | 5.5437e-05
137036 | 41562.4812 | 41562.5646 | 311 | 117 | 14942.85 | 127.7167 | 0.046022 | 0.00095783 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 127.7167 | 0.046022 | 0.00095783
137038 | 41562.4632 | 41562.4965 | 44 | 45 | 1980 | 44 | 0.0060981 | 0.00013551 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 44 | 0.0060981 | 0.00013551
137039 | 41562.6389 | 41562.6667 | 58 | 37 | 2146 | 58 | 0.0066093 | 0.00017863 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 58 | 0.0066093 | 0.00017863
137041 | 41562.3646 | 41562.5486 | 12 | 262 | 3144 | 12 | 0.009683 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | B | 12 | 0.009683 | 3.6958e-05
137042 | 41562.5208 | 41562.7132 | 247 | 274 | 67678 | 247 | 0.20844 | 0.00076072 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 247 | 0.20844 | 0.00076072
137044 | 41543.375 | 41543.5625 | 12 | 267 | 3204 | 12 | 0.0098678 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-09-26 | 2014 | 2014 | 2013-09-26 | B | 12 | 0.0098678 | 3.6958e-05
137047 | 41562.4444 | 41562.6264 | 1 | 259 | 259 | 1 | 0.00079768 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | B | 1 | 0.00079768 | 3.0798e-06
137048 | 41562.3854 | 41562.6521 | 13 | 381 | 4953 | 13 | 0.015254 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | B | 13 | 0.015254 | 4.0038e-05
137049 | 41562.5764 | 41562.7847 | 14 | 297 | 4158 | 14 | 0.012806 | 4.3118e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 14 | 0.012806 | 4.3118e-05
137055 | 41561.691 | 41561.7431 | 1426 | 72 | 79731.84 | 1107.3867 | 0.24556 | 0.0043919 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 1107.3867 | 0.24556 | 0.0043919
137056 | 41561.3757 | 41561.4792 | 679 | 146 | 47211.8926 | 323.3691 | 0.14541 | 0.0020912 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 323.3691 | 0.14541 | 0.0020912
137057 | 41562.9931 | 41563.0132 | 112 | 26 | 2912 | 112 | 0.0089685 | 0.00034494 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 112 | 0.0089685 | 0.00034494
137058 | 41561.5069 | 41561.5986 | 52 | 129 | 5808.9091 | 45.0303 | 0.017891 | 0.00016015 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 45.0303 | 0.017891 | 0.00016015
137059 | 41561.9028 | 41561.9722 | 257 | 97 | 24929 | 257 | 0.076777 | 0.00079152 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 257 | 0.076777 | 0.00079152
137060 | 41562.625 | 41563.0722 | 163 | 641 | 81793.1925 | 127.6025 | 0.25191 | 0.00050201 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 127.6025 | 0.25191 | 0.00050201
137061 | 41562.5139 | 41562.5826 | 2948 | 96 | 103960.2424 | 1082.9192 | 0.32018 | 0.0090794 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 1082.9192 | 0.32018 | 0.0090794
137062 | 41561.6729 | 41562.5347 | 42 | 1238 | 28287.4521 | 22.8493 | 0.087121 | 0.00012935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 22.8493 | 0.087121 | 0.00012935
137063 | 41562.5188 | 41563.0694 | 341 | 790 | 81545.3342 | 103.2219 | 0.25115 | 0.0010502 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 103.2219 | 0.25115 | 0.0010502
137065 | 41561.7285 | 41562.491 | 109 | 1095 | 94156.0383 | 85.9872 | 0.28999 | 0.0003357 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 85.9872 | 0.28999 | 0.0003357
137066 | 41562.5139 | 41562.525 | 6115 | 13 | 79495 | 6115 | 0.24483 | 0.018833 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 6115 | 0.24483 | 0.018833
137067 | 41562.5139 | 41562.6007 | 3831 | 122 | 37502.8 | 307.4 | 0.1155 | 0.011799 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 307.4 | 0.1155 | 0.011799
137069 | 41563.3715 | 41563.3979 | 25 | 35 | 875 | 25 | 0.0026949 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 25 | 0.0026949 | 7.6996e-05
137070 | 41561.4743 | 41561.6826 | 53 | 297 | 14460.93 | 48.69 | 0.044537 | 0.00016323 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 48.69 | 0.044537 | 0.00016323
137071 | 41562.4667 | 41562.6486 | 5 | 259 | 1295 | 5 | 0.0039884 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 5 | 0.0039884 | 1.5399e-05
137072 | 41562.6493 | 41562.7958 | 5 | 208 | 1040 | 5 | 0.003203 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 5 | 0.003203 | 1.5399e-05
137074 | 41563.4306 | 41563.4722 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 6 | 0.0010533 | 1.8479e-05
137075 | 41561.741 | 41561.9319 | 614 | 272 | 133973.3527 | 492.5491 | 0.41262 | 0.001891 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 492.5491 | 0.41262 | 0.001891
137076 | 41562.5132 | 41562.6576 | 746 | 205 | 75227.1154 | 366.9615 | 0.23169 | 0.0022976 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 366.9615 | 0.23169 | 0.0022976
137078 | 41561.5889 | 41562.5312 | 26 | 1354 | 35204 | 26 | 0.10842 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 26 | 0.10842 | 8.0076e-05
137079 | 41562.5222 | 41562.5458 | 11254 | 31 | 334273 | 10783 | 1.0295 | 0.034661 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 10783 | 1.0295 | 0.034661
137080 | 41562.5465 | 41562.6917 | 242 | 206 | 29381.1196 | 142.6268 | 0.090489 | 0.00074532 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 142.6268 | 0.090489 | 0.00074532
137081 | 41561.8403 | 41562.6799 | 362 | 1206 | 68618.3077 | 56.8974 | 0.21133 | 0.0011149 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 56.8974 | 0.21133 | 0.0011149
137083 | 41561.4424 | 41561.5403 | 174 | 138 | 18991.1489 | 137.617 | 0.05849 | 0.00053589 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 137.617 | 0.05849 | 0.00053589
137085 | 41561.9444 | 41562.875 | 5 | 1337 | 6685 | 5 | 0.020589 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 5 | 0.020589 | 1.5399e-05
137086 | 41561.7979 | 41562.575 | 1432 | 1116 | 286637.4692 | 256.8436 | 0.8828 | 0.0044103 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 256.8436 | 0.8828 | 0.0044103
137087 | 41561.4583 | 41564.2972 | 370 | 4085 | 258712.0034 | 63.3322 | 0.79679 | 0.0011395 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 63.3322 | 0.79679 | 0.0011395
137088 | 41561.5417 | 41561.7292 | 767 | 267 | 19969.6222 | 74.7926 | 0.061503 | 0.0023622 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 74.7926 | 0.061503 | 0.0023622
137089 | 41562.634 | 41562.6951 | 24 | 85 | 2040 | 24 | 0.0062829 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 24 | 0.0062829 | 7.3916e-05
137090 | 41562.6007 | 41562.6986 | 3 | 138 | 414 | 3 | 0.0012751 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 3 | 0.0012751 | 9.2395e-06
137092 | 41562.3646 | 41562.5799 | 125 | 307 | 38375 | 125 | 0.11819 | 0.00038498 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | B | 125 | 0.11819 | 0.00038498
137093 | 41563.5035 | 41563.6056 | 277 | 144 | 14101.2245 | 97.9252 | 0.04343 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 97.9252 | 0.04343 | 0.00085312
137094 | 41561.7361 | 41561.8056 | 117 | 97 | 2723.76 | 28.08 | 0.0083887 | 0.00036034 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 28.08 | 0.0083887 | 0.00036034
137095 | 41561.7833 | 41562.8056 | 285 | 1469 | 268004.6793 | 182.4402 | 0.82541 | 0.00087775 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 182.4402 | 0.82541 | 0.00087775
137097 | 41561.8757 | 41562.6042 | 436 | 1046 | 42378.4557 | 40.5148 | 0.13052 | 0.0013428 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 40.5148 | 0.13052 | 0.0013428
137098 | 41561.5049 | 41561.6389 | 1117 | 190 | 106989.6891 | 563.1036 | 0.32951 | 0.0034402 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 563.1036 | 0.32951 | 0.0034402
137099 | 41562.5 | 41562.8181 | 418 | 455 | 98311.7904 | 216.0699 | 0.30278 | 0.0012874 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 216.0699 | 0.30278 | 0.0012874
137101 | 41561.6667 | 41564.5701 | 288 | 4178 | 56873.1624 | 13.6125 | 0.17516 | 0.00088699 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 13.6125 | 0.17516 | 0.00088699
137102 | 41563.5563 | 41563.6229 | 121 | 93 | 11253 | 121 | 0.034657 | 0.00037266 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 121 | 0.034657 | 0.00037266
137103 | 41563.5139 | 41563.5632 | 32 | 68 | 2176 | 32 | 0.0067017 | 9.8555e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 32 | 0.0067017 | 9.8555e-05
137104 | 41563.4236 | 41563.6319 | 8 | 297 | 2376 | 8 | 0.0073177 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | B | 8 | 0.0073177 | 2.4639e-05
137107 | 41563.9618 | 41563.9951 | 24 | 45 | 1080 | 24 | 0.0033262 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 24 | 0.0033262 | 7.3916e-05
137109 | 41563.6333 | 41564.6868 | 313 | 1514 | 417262.1925 | 275.6025 | 1.2851 | 0.00096399 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 275.6025 | 1.2851 | 0.00096399
137112 | 41561.75 | 41561.7875 | 104 | 51 | 5304 | 104 | 0.016335 | 0.0003203 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 104 | 0.016335 | 0.0003203
137113 | 41561.5833 | 41561.6431 | 288 | 83 | 23904 | 288 | 0.073621 | 0.00088699 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 288 | 0.073621 | 0.00088699
137114 | 41561.9486 | 41562.55 | 227 | 863 | 71389.8314 | 82.7229 | 0.21987 | 0.00069912 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 82.7229 | 0.21987 | 0.00069912
137115 | 41561.4382 | 41561.5958 | 108 | 224 | 24192 | 108 | 0.074508 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 108 | 0.074508 | 0.00033262
137116 | 41561.5417 | 41561.8854 | 55 | 492 | 14972.703 | 30.4323 | 0.046114 | 0.00016939 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 30.4323 | 0.046114 | 0.00016939
137117 | 41561.4215 | 41561.7292 | 172 | 440 | 29594.2212 | 67.2596 | 0.091146 | 0.00052973 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 67.2596 | 0.091146 | 0.00052973
137118 | 41563.5118 | 41563.6597 | 5 | 210 | 1050 | 5 | 0.0032338 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 5 | 0.0032338 | 1.5399e-05
137119 | 41562.4868 | 41562.7993 | 144 | 447 | 24887.9667 | 55.6778 | 0.076651 | 0.0004435 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 55.6778 | 0.076651 | 0.0004435
137120 | 41562.5417 | 41562.5958 | 341 | 75 | 22240.3846 | 296.5385 | 0.068497 | 0.0010502 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 296.5385 | 0.068497 | 0.0010502
137121 | 41563.4236 | 41563.4507 | 28 | 36 | 1008 | 28 | 0.0031045 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 28 | 0.0031045 | 8.6236e-05
137122 | 41561.8215 | 41561.8771 | 221 | 77 | 17017 | 221 | 0.05241 | 0.00068065 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 221 | 0.05241 | 0.00068065
137123 | 41561.7882 | 41562.5931 | 671 | 1156 | 451493.3046 | 390.5651 | 1.3905 | 0.0020666 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 390.5651 | 1.3905 | 0.0020666
137124 | 41564.3729 | 41564.3854 | 25 | 15 | 375 | 25 | 0.0011549 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 25 | 0.0011549 | 7.6996e-05
137126 | 41564.375 | 41564.4549 | 6 | 112 | 672 | 6 | 0.0020697 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 6 | 0.0020697 | 1.8479e-05
137127 | 41561.7937 | 41562.0069 | 373 | 304 | 62997.316 | 207.228 | 0.19402 | 0.0011488 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 207.228 | 0.19402 | 0.0011488
137128 | 41561.8313 | 41563.7896 | 42 | 2817 | 19778.9362 | 7.0213 | 0.060916 | 0.00012935 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 7.0213 | 0.060916 | 0.00012935
137129 | 41561.7083 | 41562.5847 | 233 | 1259 | 54472.2013 | 43.2662 | 0.16777 | 0.0007176 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 43.2662 | 0.16777 | 0.0007176
137137 | 41564.3778 | 41564.6035 | 3 | 322 | 966 | 3 | 0.0029751 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 3 | 0.0029751 | 9.2395e-06
137140 | 41564.3889 | 41564.4958 | 6 | 151 | 906 | 6 | 0.0027903 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 6 | 0.0027903 | 1.8479e-05
137141 | 41564.8299 | 41564.866 | 288 | 49 | 14112 | 288 | 0.043463 | 0.00088699 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 288 | 0.043463 | 0.00088699
137142 | 41564.9812 | 41565.0139 | 55 | 44 | 2420 | 55 | 0.0074532 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 55 | 0.0074532 | 0.00016939
137143 | 41564.7035 | 41564.791 | 1336 | 123 | 66454.1667 | 540.2778 | 0.20467 | 0.0041147 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 540.2778 | 0.20467 | 0.0041147
137145 | 41561.8847 | 41562.6521 | 114 | 1102 | 28436.5864 | 25.8045 | 0.08758 | 0.0003511 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 25.8045 | 0.08758 | 0.0003511
137146 | 41564.4396 | 41564.6056 | 7 | 236 | 1652 | 7 | 0.0050879 | 2.1559e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 7 | 0.0050879 | 2.1559e-05
137148 | 41561.2354 | 41561.5382 | 77 | 433 | 33341 | 77 | 0.10269 | 0.00023715 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 77 | 0.10269 | 0.00023715
137149 | 41561.375 | 41563.7757 | 278 | 3454 | 241668.0972 | 69.9676 | 0.7443 | 0.0008562 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 69.9676 | 0.7443 | 0.0008562
137150 | 41565.3924 | 41565.4201 | 10 | 37 | 370 | 10 | 0.0011395 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 10 | 0.0011395 | 3.0798e-05
137151 | 41563.4882 | 41563.6125 | 10 | 176 | 1760 | 10 | 0.0054205 | 3.0798e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 10 | 0.0054205 | 3.0798e-05
137152 | 41561.6042 | 41561.6903 | 1067 | 121 | 55012.0645 | 454.6452 | 0.16943 | 0.0032862 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 454.6452 | 0.16943 | 0.0032862
137153 | 41561.9868 | 41562.0979 | 184 | 157 | 28888 | 184 | 0.08897 | 0.00056669 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 184 | 0.08897 | 0.00056669
137154 | 41561.9271 | 41562.5292 | 23 | 864 | 4705.6609 | 5.4464 | 0.014493 | 7.0836e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 5.4464 | 0.014493 | 7.0836e-05
137155 | 41561.4472 | 41561.5931 | 220 | 207 | 14335.2429 | 69.2524 | 0.04415 | 0.00067757 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 69.2524 | 0.04415 | 0.00067757
137156 | 41562.5569 | 41562.8111 | 122 | 363 | 40441.7705 | 111.4098 | 0.12455 | 0.00037574 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 111.4098 | 0.12455 | 0.00037574
137157 | 41565.4583 | 41565.6361 | 96 | 253 | 16709.8594 | 66.0469 | 0.051464 | 0.00029566 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 66.0469 | 0.051464 | 0.00029566
137158 | 41563.4069 | 41563.5069 | 6 | 141 | 846 | 6 | 0.0026055 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 6 | 0.0026055 | 1.8479e-05
137159 | 41565.5125 | 41565.5417 | 27 | 39 | 1053 | 27 | 0.0032431 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 27 | 0.0032431 | 8.3156e-05
137160 | 41563.0569 | 41563.6521 | 221 | 854 | 20694.3034 | 24.2322 | 0.063735 | 0.00068065 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 24.2322 | 0.063735 | 0.00068065
137163 | 41562.3542 | 41562.6007 | 3 | 352 | 1056 | 3 | 0.0032523 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | B | 3 | 0.0032523 | 9.2395e-06
137164 | 41561.5965 | 41561.6285 | 301 | 43 | 12943 | 301 | 0.039862 | 0.00092703 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 301 | 0.039862 | 0.00092703
137166 | 41561.3812 | 41563.5611 | 344 | 3136 | 15395.2724 | 4.9092 | 0.047415 | 0.0010595 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 4.9092 | 0.047415 | 0.0010595
137168 | 41566.0076 | 41566.1458 | 123 | 196 | 24108 | 123 | 0.074249 | 0.00037882 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | C | 123 | 0.074249 | 0.00037882
137169 | 41565.7396 | 41565.7521 | 422 | 15 | 4530 | 302 | 0.013952 | 0.0012997 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 302 | 0.013952 | 0.0012997
137170 | 41565.6097 | 41565.7708 | 111 | 229 | 25419 | 111 | 0.078286 | 0.00034186 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 111 | 0.078286 | 0.00034186
137172 | 41564.5417 | 41564.5868 | 3 | 62 | 186 | 3 | 0.00057285 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 3 | 0.00057285 | 9.2395e-06
137173 | 41566.375 | 41566.4125 | 3 | 51 | 153 | 3 | 0.00047122 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | B | 3 | 0.00047122 | 9.2395e-06
137175 | 41566.3764 | 41566.6639 | 8 | 411 | 3288 | 8 | 0.010127 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | B | 8 | 0.010127 | 2.4639e-05
137176 | 41566.7194 | 41566.8597 | 14 | 199 | 2786 | 14 | 0.0085804 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | C | 14 | 0.0085804 | 4.3118e-05
137177 | 41566.8819 | 41566.9431 | 15 | 85 | 1174.5455 | 13.8182 | 0.0036174 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | C | 13.8182 | 0.0036174 | 4.6198e-05
137180 | 41563.3646 | 41563.6201 | 3 | 365 | 1095 | 3 | 0.0033724 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | B | 3 | 0.0033724 | 9.2395e-06
137184 | 41567.7917 | 41567.8403 | 45 | 67 | 3015 | 45 | 0.0092857 | 0.00013859 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-20 | 2014 | 2014 | 2013-10-20 | C | 45 | 0.0092857 | 0.00013859
137185 | 41567.5521 | 41567.8438 | 143 | 417 | 38974.6071 | 93.4643 | 0.12004 | 0.00044042 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-20 | 2014 | 2014 | 2013-10-20 | C | 93.4643 | 0.12004 | 0.00044042
137186 | 41564.3958 | 41565.6882 | 691 | 1858 | 78706.9167 | 42.3611 | 0.2424 | 0.0021282 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | C | 42.3611 | 0.2424 | 0.0021282
137187 | 41565.5312 | 41565.5951 | 42 | 89 | 2368.1739 | 26.6087 | 0.0072936 | 0.00012935 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-10-18 | 2014 | 2014 | 2013-10-18 | C | 26.6087 | 0.0072936 | 0.00012935
137191 | 41562.4611 | 41562.4931 | 117 | 43 | 5031 | 117 | 0.015495 | 0.00036034 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 117 | 0.015495 | 0.00036034
137192 | 41562.4986 | 41562.5972 | 12 | 139 | 1668 | 12 | 0.0051372 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 12 | 0.0051372 | 3.6958e-05
137193 | 41561.3812 | 41562.7333 | 132 | 1944 | 57460.3267 | 29.5578 | 0.17697 | 0.00040654 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 29.5578 | 0.17697 | 0.00040654
137194 | 41562.6417 | 41562.7785 | 67 | 194 | 8695.533 | 44.8223 | 0.026781 | 0.00020635 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 44.8223 | 0.026781 | 0.00020635
137196 | 41562.741 | 41562.7514 | 11435 | 12 | 95511.2 | 7959.2667 | 0.29416 | 0.035218 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 7959.2667 | 0.29416 | 0.035218
137197 | 41562.6417 | 41563.7785 | 10 | 1634 | 9682.2236 | 5.9255 | 0.02982 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 5.9255 | 0.02982 | 3.0798e-05
137198 | 41568.3611 | 41568.4 | 20 | 53 | 1060 | 20 | 0.0032646 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | C | 20 | 0.0032646 | 6.1597e-05
137199 | 41561.4889 | 41561.7368 | 66 | 354 | 23364 | 66 | 0.071957 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 66 | 0.071957 | 0.00020327
137200 | 41561.8125 | 41561.8187 | 14 | 6 | 84 | 14 | 0.00025871 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 14 | 0.00025871 | 4.3118e-05
137201 | 41563.5764 | 41563.7069 | 13 | 185 | 2405 | 13 | 0.007407 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 13 | 0.007407 | 4.0038e-05
137202 | 41563.5903 | 41563.6354 | 1 | 62 | 62 | 1 | 0.00019095 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 1 | 0.00019095 | 3.0798e-06
137203 | 41561.6222 | 41561.8757 | 118 | 362 | 42716 | 118 | 0.13156 | 0.00036342 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 118 | 0.13156 | 0.00036342
137204 | 41568.3924 | 41568.4236 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 5 | 0.00064677 | 1.5399e-05
137206 | 41568.4618 | 41568.4896 | 5 | 37 | 185 | 5 | 0.00056977 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 5 | 0.00056977 | 1.5399e-05
137207 | 41561.5361 | 41561.9514 | 187 | 595 | 41175.393 | 69.2023 | 0.12681 | 0.00057593 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 69.2023 | 0.12681 | 0.00057593
137211 | 41561.8611 | 41562.8938 | 232 | 1484 | 138521.9691 | 93.3436 | 0.42663 | 0.00071452 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 93.3436 | 0.42663 | 0.00071452
137212 | 41561.7382 | 41562.7382 | 33 | 1437 | 45790.4042 | 31.8653 | 0.14103 | 0.00010163 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 31.8653 | 0.14103 | 0.00010163
137213 | 41562.4597 | 41562.4979 | 8 | 52 | 416 | 8 | 0.0012812 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 8 | 0.0012812 | 2.4639e-05
137214 | 41561.5458 | 41561.6542 | 437 | 153 | 30390.1154 | 198.6282 | 0.093597 | 0.0013459 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 198.6282 | 0.093597 | 0.0013459
137215 | 41561.7792 | 41562.5667 | 238 | 1131 | 148902.0344 | 131.6552 | 0.45859 | 0.000733 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 131.6552 | 0.45859 | 0.000733
137216 | 41568.4201 | 41568.4549 | 6 | 47 | 282 | 6 | 0.00086852 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 6 | 0.00086852 | 1.8479e-05
137217 | 41568.4618 | 41568.5104 | 1 | 67 | 67 | 1 | 0.00020635 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 1 | 0.00020635 | 3.0798e-06
137218 | 41568.5417 | 41568.5729 | 6 | 42 | 252 | 6 | 0.00077612 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 6 | 0.00077612 | 1.8479e-05
137219 | 41568.4167 | 41568.6076 | 107 | 272 | 29104 | 107 | 0.089636 | 0.00032954 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 107 | 0.089636 | 0.00032954
137220 | 41568.3958 | 41568.4514 | 3 | 77 | 231 | 3 | 0.00071144 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 3 | 0.00071144 | 9.2395e-06
137221 | 41568.4653 | 41568.4931 | 4 | 37 | 148 | 4 | 0.00045582 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 4 | 0.00045582 | 1.2319e-05
137222 | 41568.5417 | 41568.5764 | 6 | 47 | 282 | 6 | 0.00086852 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 6 | 0.00086852 | 1.8479e-05
137223 | 41568.5417 | 41568.6146 | 4 | 102 | 408 | 4 | 0.0012566 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 4 | 0.0012566 | 1.2319e-05
137225 | 41568.3535 | 41568.6937 | 249 | 487 | 121263 | 249 | 0.37347 | 0.00076688 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | C | 249 | 0.37347 | 0.00076688
137233 | 41562.941 | 41564.6194 | 869 | 2414 | 200776.4849 | 83.1717 | 0.61836 | 0.0026764 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 83.1717 | 0.61836 | 0.0026764
137234 | 41561.4229 | 41568.5993 | 203 | 10331 | 58540.0007 | 5.6664 | 0.18029 | 0.00062521 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 5.6664 | 0.18029 | 0.00062521
137235 | 41562.4083 | 41562.4778 | 6 | 97 | 582 | 6 | 0.0017925 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-15 | 2014 | 2014 | 2013-10-15 | C | 6 | 0.0017925 | 1.8479e-05
137237 | 41561.5507 | 41564.6181 | 169 | 4414 | 290032.8775 | 65.7075 | 0.89326 | 0.00052049 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 65.7075 | 0.89326 | 0.00052049
137242 | 41569.416 | 41569.434 | 6 | 23 | 138 | 6 | 0.00042502 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 6 | 0.00042502 | 1.8479e-05
137243 | 41563.7361 | 41563.775 | 2256 | 53 | 114763.9286 | 2165.3571 | 0.35345 | 0.0069481 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-16 | 2014 | 2014 | 2013-10-16 | C | 2165.3571 | 0.35345 | 0.0069481
137244 | 41569.3993 | 41569.5111 | 106 | 158 | 16748 | 106 | 0.051581 | 0.00032646 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 106 | 0.051581 | 0.00032646
137245 | 41569.4375 | 41569.6271 | 8 | 270 | 2160 | 8 | 0.0066525 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 8 | 0.0066525 | 2.4639e-05
137248 | 41569.5097 | 41569.5569 | 298 | 65 | 19370 | 298 | 0.059657 | 0.00091779 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 298 | 0.059657 | 0.00091779
137249 | 41569.6028 | 41569.6611 | 346 | 81 | 19348.3929 | 238.869 | 0.05959 | 0.0010656 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 238.869 | 0.05959 | 0.0010656
137250 | 41569.1062 | 41570.8069 | 66 | 2446 | 161436 | 66 | 0.4972 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 66 | 0.4972 | 0.00020327
137251 | 41569.6451 | 41569.7042 | 394 | 82 | 18175.0588 | 221.6471 | 0.055976 | 0.0012135 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 221.6471 | 0.055976 | 0.0012135
137252 | 41569.75 | 41570.5785 | 22 | 1190 | 26180 | 22 | 0.08063 | 6.7757e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 22 | 0.08063 | 6.7757e-05
137257 | 41569.5417 | 41569.5729 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 4 | 0.00051741 | 1.2319e-05
137258 | 41569.4583 | 41569.5 | 2 | 57 | 114 | 2 | 0.0003511 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 2 | 0.0003511 | 6.1597e-06
137259 | 41569.375 | 41569.4049 | 10 | 40 | 400 | 10 | 0.0012319 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 10 | 0.0012319 | 3.0798e-05
137260 | 41569.4583 | 41569.4792 | 2 | 27 | 54 | 2 | 0.00016631 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 2 | 0.00016631 | 6.1597e-06
137261 | 41569.375 | 41569.4201 | 3 | 62 | 186 | 3 | 0.00057285 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 3 | 0.00057285 | 9.2395e-06
137262 | 41569.4896 | 41569.5312 | 5 | 57 | 285 | 5 | 0.00087775 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 5 | 0.00087775 | 1.5399e-05
137263 | 41569.375 | 41569.4167 | 8 | 57 | 456 | 8 | 0.0014044 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 8 | 0.0014044 | 2.4639e-05
137264 | 41569.5556 | 41569.5972 | 2 | 57 | 114 | 2 | 0.0003511 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 2 | 0.0003511 | 6.1597e-06
137265 | 41570.3986 | 41570.4583 | 3 | 83 | 249 | 3 | 0.00076688 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 3 | 0.00076688 | 9.2395e-06
137267 | 41570.4167 | 41570.5083 | 2 | 129 | 258 | 2 | 0.0007946 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 2 | 0.0007946 | 6.1597e-06
137270 | 41570.4896 | 41570.5243 | 2 | 47 | 94 | 2 | 0.00028951 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 2 | 0.00028951 | 6.1597e-06
137272 | 41570.5556 | 41570.5847 | 2 | 39 | 78 | 2 | 0.00024023 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 2 | 0.00024023 | 6.1597e-06
137273 | 41570.4167 | 41570.616 | 161 | 284 | 45724 | 161 | 0.14082 | 0.00049585 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 161 | 0.14082 | 0.00049585
137274 | 41570.375 | 41570.6194 | 17 | 349 | 5933 | 17 | 0.018273 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 17 | 0.018273 | 5.2357e-05
137275 | 41570.4333 | 41570.6333 | 1 | 285 | 285 | 1 | 0.00087775 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 1 | 0.00087775 | 3.0798e-06
137276 | 41570.5333 | 41570.6514 | 3 | 167 | 501 | 3 | 0.001543 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 3 | 0.001543 | 9.2395e-06
137277 | 41570.5417 | 41570.5938 | 3 | 72 | 216 | 3 | 0.00066525 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 3 | 0.00066525 | 9.2395e-06
137278 | 41570.4583 | 41570.5417 | 5 | 117 | 585 | 5 | 0.0018017 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 5 | 0.0018017 | 1.5399e-05
137281 | 41570.5778 | 41570.5944 | 13 | 21 | 273 | 13 | 0.0008408 | 4.0038e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 13 | 0.0008408 | 4.0038e-05
137282 | 41569.5222 | 41569.5486 | 16 | 35 | 560 | 16 | 0.0017247 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | C | 16 | 0.0017247 | 4.9277e-05
137283 | 41561.8063 | 41562.3333 | 124 | 756 | 23998.7668 | 31.7444 | 0.073912 | 0.0003819 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 31.7444 | 0.073912 | 0.0003819
137284 | 41570.4125 | 41570.5243 | 10 | 158 | 1580 | 10 | 0.0048662 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 10 | 0.0048662 | 3.0798e-05
137287 | 41570.9069 | 41571.5326 | 147 | 898 | 30128.3485 | 33.5505 | 0.092791 | 0.00045274 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 33.5505 | 0.092791 | 0.00045274
137288 | 41570.9479 | 41570.9931 | 5 | 62 | 310 | 5 | 0.00095475 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 5 | 0.00095475 | 1.5399e-05
137292 | 41570.9167 | 41571.5 | 3 | 837 | 2511 | 3 | 0.0077335 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | C | 3 | 0.0077335 | 9.2395e-06
137293 | 41571.375 | 41571.5611 | 17 | 265 | 4505 | 17 | 0.013875 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | B | 17 | 0.013875 | 5.2357e-05
137295 | 41571.4028 | 41571.5403 | 29 | 195 | 5613.6364 | 28.7879 | 0.017289 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 28.7879 | 0.017289 | 8.9315e-05
137297 | 41570.5437 | 41570.5938 | 8 | 69 | 552 | 8 | 0.0017001 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 8 | 0.0017001 | 2.4639e-05
137298 | 41570.4653 | 41570.5208 | 4 | 77 | 308 | 4 | 0.00094859 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 4 | 0.00094859 | 1.2319e-05
137299 | 41570.3819 | 41570.4479 | 4 | 92 | 368 | 4 | 0.0011334 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 4 | 0.0011334 | 1.2319e-05
137300 | 41571.4021 | 41571.6181 | 298 | 308 | 91784 | 298 | 0.28268 | 0.00091779 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 298 | 0.28268 | 0.00091779
137302 | 41571.5167 | 41571.5903 | 66 | 103 | 6798 | 66 | 0.020937 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 66 | 0.020937 | 0.00020327
137307 | 41571.7167 | 41571.7562 | 14 | 54 | 756 | 14 | 0.0023284 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 14 | 0.0023284 | 4.3118e-05
137308 | 41571.7771 | 41571.7958 | 75 | 24 | 1800 | 75 | 0.0055437 | 0.00023099 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 75 | 0.0055437 | 0.00023099
137309 | 41571.8694 | 41571.9167 | 298 | 65 | 19370 | 298 | 0.059657 | 0.00091779 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 298 | 0.059657 | 0.00091779
137310 | 41571.8889 | 41572.1389 | 350 | 357 | 112316.1667 | 314.6111 | 0.34592 | 0.0010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | C | 314.6111 | 0.34592 | 0.0010779
137311 | 41571.9313 | 41572.1292 | 1 | 282 | 282 | 1 | 0.00086852 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-24 | 2014 | 2014 | 2013-10-24 | B | 1 | 0.00086852 | 3.0798e-06
137312 | 41572.2708 | 41572.5208 | 337 | 357 | 30604.8167 | 85.7278 | 0.094258 | 0.0010379 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 85.7278 | 0.094258 | 0.0010379
137313 | 41561.6854 | 41562.7396 | 613 | 1515 | 109254.6542 | 72.1153 | 0.33649 | 0.0018879 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-14 | 2014 | 2014 | 2013-10-14 | C | 72.1153 | 0.33649 | 0.0018879
137316 | 41572.4833 | 41572.6757 | 276 | 274 | 24986.426 | 91.1913 | 0.076954 | 0.00085004 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 91.1913 | 0.076954 | 0.00085004
137317 | 41572.7153 | 41572.9146 | 6129 | 284 | 1720965.784 | 6059.7387 | 5.3003 | 0.018876 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 6059.7387 | 5.3003 | 0.018876
137318 | 41572.8576 | 41572.9062 | 697 | 67 | 41355.2714 | 617.2429 | 0.12737 | 0.0021466 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 617.2429 | 0.12737 | 0.0021466
137321 | 41572.7125 | 41572.9417 | 23 | 327 | 7521 | 23 | 0.023163 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 23 | 0.023163 | 7.0836e-05
137322 | 41572.6646 | 41572.7972 | 35 | 188 | 6580 | 35 | 0.020265 | 0.00010779 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 35 | 0.020265 | 0.00010779
137323 | 41572.7847 | 41573.3708 | 298 | 841 | 177183.9526 | 210.6825 | 0.5457 | 0.00091779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 210.6825 | 0.5457 | 0.00091779
137324 | 41572.4556 | 41572.7618 | 298 | 438 | 130524 | 298 | 0.40199 | 0.00091779 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 298 | 0.40199 | 0.00091779
137325 | 41572.5389 | 41572.6681 | 53 | 183 | 9699 | 53 | 0.029871 | 0.00016323 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 53 | 0.029871 | 0.00016323
137326 | 41572.6396 | 41572.65 | 5 | 12 | 60 | 5 | 0.00018479 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 5 | 0.00018479 | 1.5399e-05
137328 | 41572.5924 | 41572.6049 | 354 | 15 | 5310 | 354 | 0.016354 | 0.0010903 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 354 | 0.016354 | 0.0010903
137330 | 41572.4542 | 41572.5486 | 28 | 133 | 3724 | 28 | 0.011469 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 28 | 0.011469 | 8.6236e-05
137332 | 41572.5083 | 41572.5208 | 3 | 15 | 45 | 3 | 0.00013859 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 3 | 0.00013859 | 9.2395e-06
137333 | 41572.3847 | 41572.5104 | 72 | 178 | 9318.9392 | 52.3536 | 0.028701 | 0.00022175 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 52.3536 | 0.028701 | 0.00022175
137334 | 41572.4465 | 41572.4604 | 20 | 17 | 340 | 20 | 0.0010471 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 20 | 0.0010471 | 6.1597e-05
137335 | 41572.4764 | 41572.6493 | 118 | 246 | 24309.5422 | 98.8193 | 0.07487 | 0.00036342 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 98.8193 | 0.07487 | 0.00036342
137338 | 41573.3986 | 41573.5569 | 436 | 225 | 45300.9868 | 201.3377 | 0.13952 | 0.0013428 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 201.3377 | 0.13952 | 0.0013428
137339 | 41572.3333 | 41572.4028 | 249 | 97 | 24153 | 249 | 0.074387 | 0.00076688 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 249 | 0.074387 | 0.00076688
137340 | 41573.4375 | 41573.5139 | 44 | 107 | 4708 | 44 | 0.0145 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 44 | 0.0145 | 0.00013551
137341 | 41573.5833 | 41573.6611 | 54 | 109 | 5886 | 54 | 0.018128 | 0.00016631 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 54 | 0.018128 | 0.00016631
137343 | 41573.2653 | 41573.2965 | 232 | 42 | 9744 | 232 | 0.03001 | 0.00071452 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 232 | 0.03001 | 0.00071452
137344 | 41573.4826 | 41573.5028 | 22 | 26 | 572 | 22 | 0.0017617 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 22 | 0.0017617 | 6.7757e-05
137345 | 41573.5701 | 41573.6604 | 62 | 127 | 6246.4462 | 49.1846 | 0.019238 | 0.00019095 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-26 | 2014 | 2014 | 2013-10-26 | C | 49.1846 | 0.019238 | 0.00019095
137347 | 41574.3618 | 41574.5222 | 30 | 228 | 6204.3636 | 27.2121 | 0.019108 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-27 | 2014 | 2014 | 2013-10-27 | C | 27.2121 | 0.019108 | 9.2395e-05
137350 | 41574.5903 | 41574.6993 | 30 | 154 | 4620 | 30 | 0.014229 | 9.2395e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-27 | 2014 | 2014 | 2013-10-27 | C | 30 | 0.014229 | 9.2395e-05
137354 | 41575.3167 | 41575.3354 | 54 | 24 | 1296 | 54 | 0.0039915 | 0.00016631 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-28 | 2014 | 2014 | 2013-10-28 | C | 54 | 0.0039915 | 0.00016631
137356 | 41574.9201 | 41575.5417 | 30 | 892 | 20735.2626 | 23.2458 | 0.063861 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-27 | 2014 | 2014 | 2013-10-27 | C | 23.2458 | 0.063861 | 9.2395e-05
137357 | 41575.3118 | 41575.5028 | 514 | 272 | 43388.4509 | 159.5164 | 0.13363 | 0.001583 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-28 | 2014 | 2014 | 2013-10-28 | C | 159.5164 | 0.13363 | 0.001583
137358 | 41575.9243 | 41575.9708 | 18 | 64 | 1152 | 18 | 0.003548 | 5.5437e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-28 | 2014 | 2014 | 2013-10-28 | C | 18 | 0.003548 | 5.5437e-05
137359 | 41576.084 | 41576.1687 | 461 | 119 | 32191.4508 | 270.5164 | 0.099145 | 0.0014198 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 270.5164 | 0.099145 | 0.0014198
137361 | 41572.4958 | 41572.6354 | 271 | 198 | 24958.8358 | 126.0547 | 0.076869 | 0.00083464 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | C | 126.0547 | 0.076869 | 0.00083464
137363 | 41576.1292 | 41576.3924 | 29 | 376 | 10729.3931 | 28.5356 | 0.033045 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 28.5356 | 0.033045 | 8.9315e-05
137365 | 41576.5521 | 41576.6181 | 1 | 92 | 92 | 1 | 0.00028335 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 1 | 0.00028335 | 3.0798e-06
137366 | 41576.3854 | 41576.5847 | 17 | 284 | 4828 | 17 | 0.014869 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | B | 17 | 0.014869 | 5.2357e-05
137368 | 41576.5458 | 41576.5875 | 573 | 57 | 32661 | 573 | 0.10059 | 0.0017647 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 573 | 0.10059 | 0.0017647
137369 | 41576.6312 | 41576.7535 | 883 | 173 | 59108.0057 | 341.6648 | 0.18204 | 0.0027195 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 341.6648 | 0.18204 | 0.0027195
137370 | 41576.5653 | 41576.6035 | 357 | 52 | 17186.4727 | 330.5091 | 0.052932 | 0.0010995 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 330.5091 | 0.052932 | 0.0010995
137371 | 41576.375 | 41576.4132 | 7 | 52 | 364 | 7 | 0.0011211 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | B | 7 | 0.0011211 | 2.1559e-05
137372 | 41576.6965 | 41576.7368 | 14 | 55 | 770 | 14 | 0.0023715 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | C | 14 | 0.0023715 | 4.3118e-05
137373 | 41576.5417 | 41576.5708 | 3 | 39 | 117 | 3 | 0.00036034 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | B | 3 | 0.00036034 | 9.2395e-06
137374 | 41576.4583 | 41576.5035 | 5 | 62 | 310 | 5 | 0.00095475 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | B | 5 | 0.00095475 | 1.5399e-05
137376 | 41576.9583 | 41577.0174 | 35 | 82 | 2870 | 35 | 0.0088391 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-29 | 2014 | 2014 | 2013-10-29 | B | 35 | 0.0088391 | 0.00010779
137378 | 41577.4583 | 41577.4736 | 3 | 19 | 57 | 3 | 0.00017555 | 9.2395e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-10-30 | 2014 | 2014 | 2013-10-30 | C | 3 | 0.00017555 | 9.2395e-06
137380 | 41577.4062 | 41577.5312 | 3 | 177 | 531 | 3 | 0.0016354 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-30 | 2014 | 2014 | 2013-10-30 | C | 3 | 0.0016354 | 9.2395e-06
137383 | 41577.3854 | 41577.575 | 17 | 270 | 4590 | 17 | 0.014136 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-30 | 2014 | 2014 | 2013-10-30 | B | 17 | 0.014136 | 5.2357e-05
137387 | 41578.4819 | 41578.5174 | 7 | 48 | 336 | 7 | 0.0010348 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 7 | 0.0010348 | 2.1559e-05
137388 | 41578.4382 | 41578.5111 | 493 | 102 | 30275.5429 | 296.819 | 0.093244 | 0.0015184 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 296.819 | 0.093244 | 0.0015184
137389 | 41578.2708 | 41578.6021 | 1 | 474 | 474 | 1 | 0.0014598 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 1 | 0.0014598 | 3.0798e-06
137390 | 41578.375 | 41578.4479 | 6 | 102 | 612 | 6 | 0.0018849 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 6 | 0.0018849 | 1.8479e-05
137391 | 41578.4583 | 41578.5243 | 4 | 92 | 368 | 4 | 0.0011334 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 4 | 0.0011334 | 1.2319e-05
137392 | 41578.5417 | 41578.5972 | 7 | 77 | 539 | 7 | 0.00166 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 7 | 0.00166 | 2.1559e-05
137393 | 41578.3819 | 41578.4549 | 5 | 102 | 510 | 5 | 0.0015707 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 5 | 0.0015707 | 1.5399e-05
137394 | 41578.4688 | 41578.5208 | 5 | 72 | 360 | 5 | 0.0011087 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 5 | 0.0011087 | 1.5399e-05
137395 | 41578.5417 | 41578.6562 | 7 | 162 | 1134 | 7 | 0.0034925 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 7 | 0.0034925 | 2.1559e-05
137396 | 41578.375 | 41578.4062 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 4 | 0.00051741 | 1.2319e-05
137397 | 41578.4583 | 41578.5104 | 3 | 72 | 216 | 3 | 0.00066525 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 3 | 0.00066525 | 9.2395e-06
137398 | 41578.5417 | 41578.6042 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 3 | 0.00080384 | 9.2395e-06
137399 | 41578.4062 | 41578.6097 | 103 | 290 | 29870 | 103 | 0.091995 | 0.00031722 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 103 | 0.091995 | 0.00031722
137401 | 41578.3854 | 41578.5326 | 2 | 209 | 418 | 2 | 0.0012874 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 2 | 0.0012874 | 6.1597e-06
137403 | 41578.484 | 41578.8493 | 404 | 523 | 15521.9639 | 29.6787 | 0.047805 | 0.0012443 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 29.6787 | 0.047805 | 0.0012443
137405 | 41578.5208 | 41578.7847 | 11 | 377 | 4147 | 11 | 0.012772 | 3.3878e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 11 | 0.012772 | 3.3878e-05
137406 | 41578.775 | 41578.8125 | 21 | 51 | 1071 | 21 | 0.0032985 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 21 | 0.0032985 | 6.4677e-05
137407 | 41578.9792 | 41579.0264 | 152 | 65 | 9880 | 152 | 0.030429 | 0.00046814 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | B | 152 | 0.030429 | 0.00046814
137408 | 41578.9944 | 41582.6222 | 20 | 5221 | 5714.7163 | 1.0946 | 0.0176 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-10-31 | 2014 | 2014 | 2013-10-31 | C | 1.0946 | 0.0176 | 6.1597e-05
137409 | 41579.0465 | 41579.0931 | 1155 | 64 | 60270.806 | 941.7313 | 0.18562 | 0.0035572 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | C | 941.7313 | 0.18562 | 0.0035572
137410 | 41579.125 | 41579.2382 | 37 | 160 | 4889.3252 | 30.5583 | 0.015058 | 0.00011395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | C | 30.5583 | 0.015058 | 0.00011395
137412 | 41579.1986 | 41579.2354 | 181 | 50 | 9050 | 181 | 0.027873 | 0.00055745 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | C | 181 | 0.027873 | 0.00055745
137416 | 41579.375 | 41579.5417 | 26 | 237 | 6162 | 26 | 0.018978 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | B | 26 | 0.018978 | 8.0076e-05
137417 | 41579.4479 | 41579.6181 | 4 | 242 | 968 | 4 | 0.0029813 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | B | 4 | 0.0029813 | 1.2319e-05
137418 | 41579.5576 | 41579.575 | 28 | 22 | 616 | 28 | 0.0018972 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-01 | 2014 | 2014 | 2013-11-01 | C | 28 | 0.0018972 | 8.6236e-05
137425 | 41580.1257 | 41580.1451 | 8 | 25 | 200 | 8 | 0.00061597 | 2.4639e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | C | 8 | 0.00061597 | 2.4639e-05
137426 | 41580.3646 | 41580.5069 | 40 | 202 | 8080 | 40 | 0.024885 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | B | 40 | 0.024885 | 0.00012319
137429 | 41580.4868 | 41580.525 | 19 | 52 | 988 | 19 | 0.0030429 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | C | 19 | 0.0030429 | 5.8517e-05
137430 | 41580.625 | 41580.6875 | 18 | 87 | 1566 | 18 | 0.004823 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | C | 18 | 0.004823 | 5.5437e-05
137431 | 41580.4375 | 41580.5333 | 8 | 135 | 1080 | 8 | 0.0033262 | 2.4639e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | C | 8 | 0.0033262 | 2.4639e-05
137432 | 41580.8444 | 41580.9243 | 184 | 112 | 14882.3652 | 132.8783 | 0.045835 | 0.00056669 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-02 | 2014 | 2014 | 2013-11-02 | C | 132.8783 | 0.045835 | 0.00056669
137435 | 41581.4688 | 41581.4944 | 21 | 34 | 714 | 21 | 0.002199 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-03 | 2014 | 2014 | 2013-11-03 | C | 21 | 0.002199 | 6.4677e-05
137439 | 41582.3229 | 41582.3458 | 14 | 30 | 420 | 14 | 0.0012935 | 4.3118e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | C | 14 | 0.0012935 | 4.3118e-05
137440 | 41582.3646 | 41582.5215 | 173 | 223 | 38579 | 173 | 0.11882 | 0.00053281 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 173 | 0.11882 | 0.00053281
137441 | 41582.4167 | 41582.584 | 3 | 238 | 714 | 3 | 0.002199 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 3 | 0.002199 | 9.2395e-06
137442 | 41582.3993 | 41582.6417 | 5 | 346 | 1730 | 5 | 0.0053281 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 5 | 0.0053281 | 1.5399e-05
137444 | 41582.3861 | 41582.5681 | 8 | 259 | 2072 | 8 | 0.0063814 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 8 | 0.0063814 | 2.4639e-05
137445 | 41582.4028 | 41582.5625 | 1 | 227 | 227 | 1 | 0.00069912 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 1 | 0.00069912 | 3.0798e-06
137447 | 41582.4826 | 41582.5 | 743 | 22 | 16346 | 743 | 0.050343 | 0.0022883 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | C | 743 | 0.050343 | 0.0022883
137448 | 41583.3958 | 41583.5312 | 8 | 192 | 1536 | 8 | 0.0047306 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 8 | 0.0047306 | 2.4639e-05
137449 | 41583.3778 | 41583.5403 | 16 | 231 | 3696 | 16 | 0.011383 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 16 | 0.011383 | 4.9277e-05
137450 | 41583.5653 | 41583.6354 | 8 | 98 | 784 | 8 | 0.0024146 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 8 | 0.0024146 | 2.4639e-05
137451 | 41583.375 | 41583.6083 | 31 | 333 | 10323 | 31 | 0.031793 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 31 | 0.031793 | 9.5475e-05
137452 | 41583.3958 | 41583.6243 | 14 | 326 | 4564 | 14 | 0.014056 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 14 | 0.014056 | 4.3118e-05
137456 | 41583.5778 | 41583.6229 | 2 | 62 | 124 | 2 | 0.0003819 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 2 | 0.0003819 | 6.1597e-06
137457 | 41583.3333 | 41583.6597 | 9 | 467 | 4203 | 9 | 0.012945 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 9 | 0.012945 | 2.7719e-05
137458 | 41583.375 | 41583.4583 | 4 | 117 | 468 | 4 | 0.0014414 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 4 | 0.0014414 | 1.2319e-05
137459 | 41583.4583 | 41583.5417 | 33 | 117 | 3861 | 33 | 0.011891 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | B | 33 | 0.011891 | 0.00010163
137460 | 41583.3826 | 41583.4132 | 23 | 41 | 943 | 23 | 0.0029043 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 23 | 0.0029043 | 7.0836e-05
137461 | 41583.7674 | 41583.9535 | 294 | 265 | 24146.6418 | 91.1194 | 0.074368 | 0.00090547 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 91.1194 | 0.074368 | 0.00090547
137462 | 41568.9826 | 41569.0368 | 152 | 75 | 11400 | 152 | 0.03511 | 0.00046814 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-21 | 2014 | 2014 | 2013-10-21 | B | 152 | 0.03511 | 0.00046814
137463 | 41583.6507 | 41583.7243 | 320 | 103 | 19774.0566 | 191.9811 | 0.060901 | 0.00098555 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 191.9811 | 0.060901 | 0.00098555
137464 | 41583.7201 | 41583.7479 | 50 | 37 | 1850 | 50 | 0.0056977 | 0.00015399 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-05 | 2014 | 2014 | 2013-11-05 | C | 50 | 0.0056977 | 0.00015399
137465 | 41584.2951 | 41584.4201 | 183 | 177 | 11725.2667 | 66.2444 | 0.036112 | 0.00056361 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 66.2444 | 0.036112 | 0.00056361
137466 | 41584.1931 | 41584.4375 | 155 | 349 | 31791.7188 | 91.0938 | 0.097913 | 0.00047738 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 91.0938 | 0.097913 | 0.00047738
137467 | 41584.525 | 41584.5535 | 3 | 38 | 114 | 3 | 0.0003511 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 3 | 0.0003511 | 9.2395e-06
137468 | 41584.3333 | 41584.5604 | 9 | 324 | 2916 | 9 | 0.0089808 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 9 | 0.0089808 | 2.7719e-05
137469 | 41584.4375 | 41584.5278 | 39 | 127 | 4953 | 39 | 0.015254 | 0.00012011 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 39 | 0.015254 | 0.00012011
137470 | 41584.3333 | 41584.559 | 113 | 322 | 36386 | 113 | 0.11206 | 0.00034802 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 113 | 0.11206 | 0.00034802
137471 | 41584.3646 | 41584.5889 | 4 | 320 | 1280 | 4 | 0.0039422 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 4 | 0.0039422 | 1.2319e-05
137472 | 41584.375 | 41584.5875 | 26 | 303 | 7878 | 26 | 0.024263 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 26 | 0.024263 | 8.0076e-05
137473 | 41584.3854 | 41584.5889 | 44 | 290 | 12760 | 44 | 0.039299 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 44 | 0.039299 | 0.00013551
137475 | 41584.4437 | 41584.5486 | 3 | 148 | 444 | 3 | 0.0013674 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 3 | 0.0013674 | 9.2395e-06
137476 | 41584.3646 | 41584.6236 | 8 | 370 | 2960 | 8 | 0.0091163 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 8 | 0.0091163 | 2.4639e-05
137477 | 41584.5417 | 41584.5903 | 7 | 67 | 469 | 7 | 0.0014444 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 7 | 0.0014444 | 2.1559e-05
137478 | 41584.4618 | 41584.5104 | 6 | 67 | 402 | 6 | 0.0012381 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 6 | 0.0012381 | 1.8479e-05
137480 | 41584.5417 | 41584.6076 | 7 | 92 | 644 | 7 | 0.0019834 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 7 | 0.0019834 | 2.1559e-05
137481 | 41584.4583 | 41584.5229 | 1 | 90 | 90 | 1 | 0.00027719 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 1 | 0.00027719 | 3.0798e-06
137482 | 41584.5778 | 41584.6222 | 28 | 61 | 1708 | 28 | 0.0052604 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 28 | 0.0052604 | 8.6236e-05
137483 | 41584.5451 | 41584.5764 | 1 | 42 | 42 | 1 | 0.00012935 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 1 | 0.00012935 | 3.0798e-06
137484 | 41584.4618 | 41584.5396 | 3 | 109 | 327 | 3 | 0.0010071 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | B | 3 | 0.0010071 | 9.2395e-06
137486 | 41584.3965 | 41584.5528 | 111 | 222 | 16837.4667 | 75.8444 | 0.051857 | 0.00034186 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 75.8444 | 0.051857 | 0.00034186
137487 | 41584.5194 | 41584.5396 | 38 | 26 | 988 | 38 | 0.0030429 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 38 | 0.0030429 | 0.00011703
137488 | 41584.8333 | 41584.8729 | 72 | 54 | 3888 | 72 | 0.011974 | 0.00022175 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 72 | 0.011974 | 0.00022175
137489 | 41584.7312 | 41584.7688 | 902 | 51 | 14331 | 281 | 0.044137 | 0.002778 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 281 | 0.044137 | 0.002778
137490 | 41584.8458 | 41584.9167 | 343 | 99 | 10719.1765 | 108.2745 | 0.033013 | 0.0010564 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 108.2745 | 0.033013 | 0.0010564
137494 | 41584.5194 | 41584.5396 | 38 | 26 | 988 | 38 | 0.0030429 | 0.00011703 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 38 | 0.0030429 | 0.00011703
137497 | 41585.0451 | 41585.3625 | 209 | 454 | 24286.5164 | 53.4945 | 0.074799 | 0.00064369 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 53.4945 | 0.074799 | 0.00064369
137498 | 41585.425 | 41585.5333 | 134 | 153 | 2636.3077 | 17.2308 | 0.0081194 | 0.0004127 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 17.2308 | 0.0081194 | 0.0004127
137500 | 41584.9688 | 41585.5528 | 45 | 838 | 10976.7039 | 13.0987 | 0.033807 | 0.00013859 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 13.0987 | 0.033807 | 0.00013859
137502 | 41585.4333 | 41585.5868 | 14 | 218 | 3052 | 14 | 0.0093997 | 4.3118e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 14 | 0.0093997 | 4.3118e-05
137506 | 41585.3646 | 41585.6514 | 42 | 410 | 17220 | 42 | 0.053035 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 42 | 0.053035 | 0.00012935
137508 | 41585.4257 | 41585.5021 | 4 | 107 | 428 | 4 | 0.0013182 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 4 | 0.0013182 | 1.2319e-05
137509 | 41585.5028 | 41585.5722 | 2 | 97 | 194 | 2 | 0.00059749 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 2 | 0.00059749 | 6.1597e-06
137510 | 41585.5417 | 41585.5694 | 3 | 37 | 111 | 3 | 0.00034186 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 3 | 0.00034186 | 9.2395e-06
137511 | 41585.7472 | 41585.7674 | 55 | 26 | 1430 | 55 | 0.0044042 | 0.00016939 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 55 | 0.0044042 | 0.00016939
137512 | 41585.8063 | 41585.9514 | 1 | 206 | 206 | 1 | 0.00063445 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 1 | 0.00063445 | 3.0798e-06
137514 | 41585.984 | 41585.9875 | 4306 | 2 | 8612 | 4306 | 0.026524 | 0.013262 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 4306 | 0.026524 | 0.013262
137515 | 41585.9326 | 41586.0326 | 1 | 141 | 141 | 1 | 0.00043426 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 1 | 0.00043426 | 3.0798e-06
137516 | 41586.0757 | 41586.0958 | 272 | 26 | 7072 | 272 | 0.021781 | 0.00083772 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 272 | 0.021781 | 0.00083772
137517 | 41585.3889 | 41585.4271 | 9 | 52 | 468 | 9 | 0.0014414 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 9 | 0.0014414 | 2.7719e-05
137518 | 41585.3958 | 41585.4375 | 3 | 57 | 171 | 3 | 0.00052665 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 3 | 0.00052665 | 9.2395e-06
137519 | 41585.6042 | 41585.625 | 3 | 27 | 81 | 3 | 0.00024947 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 3 | 0.00024947 | 9.2395e-06
137524 | 41586.4361 | 41586.4514 | 13 | 19 | 247 | 13 | 0.00076072 | 4.0038e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 13 | 0.00076072 | 4.0038e-05
137525 | 41586.3507 | 41586.375 | 301 | 32 | 9632 | 301 | 0.029665 | 0.00092703 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 301 | 0.029665 | 0.00092703
137526 | 41584.1979 | 41584.2396 | 7 | 57 | 399 | 7 | 0.0012289 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 7 | 0.0012289 | 2.1559e-05
137527 | 41584.1667 | 41584.2396 | 4 | 102 | 408 | 4 | 0.0012566 | 1.2319e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-06 | 2014 | 2014 | 2013-11-06 | C | 4 | 0.0012566 | 1.2319e-05
137528 | 41585.3757 | 41585.5104 | 4 | 191 | 764 | 4 | 0.002353 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | B | 4 | 0.002353 | 1.2319e-05
137531 | 41586.375 | 41586.4479 | 7 | 102 | 714 | 7 | 0.002199 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 7 | 0.002199 | 2.1559e-05
137532 | 41586.3889 | 41586.5597 | 7 | 243 | 1701 | 7 | 0.0052388 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 7 | 0.0052388 | 2.1559e-05
137533 | 41586.4583 | 41586.5104 | 10 | 72 | 720 | 10 | 0.0022175 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 10 | 0.0022175 | 3.0798e-05
137534 | 41586.5417 | 41586.6042 | 4 | 87 | 348 | 4 | 0.0010718 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 4 | 0.0010718 | 1.2319e-05
137535 | 41586.375 | 41586.4306 | 3 | 77 | 231 | 3 | 0.00071144 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 3 | 0.00071144 | 9.2395e-06
137536 | 41586.4653 | 41586.5146 | 3 | 68 | 204 | 3 | 0.00062829 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 3 | 0.00062829 | 9.2395e-06
137538 | 41586.5472 | 41586.5806 | 6 | 45 | 270 | 6 | 0.00083156 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 6 | 0.00083156 | 1.8479e-05
137540 | 41586.9778 | 41586.9951 | 259 | 22 | 5698 | 259 | 0.017549 | 0.00079768 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 259 | 0.017549 | 0.00079768
137541 | 41586.6917 | 41586.8035 | 1 | 158 | 158 | 1 | 0.00048662 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 1 | 0.00048662 | 3.0798e-06
137544 | 41585.6174 | 41586.684 | 277 | 1533 | 63649.4414 | 41.5195 | 0.19603 | 0.00085312 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 41.5195 | 0.19603 | 0.00085312
137545 | 41587.3736 | 41587.4097 | 20 | 49 | 980 | 20 | 0.0030182 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-09 | 2014 | 2014 | 2013-11-09 | C | 20 | 0.0030182 | 6.1597e-05
137546 | 41586.3542 | 41586.5625 | 17 | 297 | 5049 | 17 | 0.01555 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 17 | 0.01555 | 5.2357e-05
137547 | 41586.3917 | 41586.5799 | 94 | 268 | 25192 | 94 | 0.077587 | 0.00028951 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 94 | 0.077587 | 0.00028951
137548 | 41586.3854 | 41586.625 | 9 | 342 | 3078 | 9 | 0.0094798 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | B | 9 | 0.0094798 | 2.7719e-05
137549 | 41586.4514 | 41586.4722 | 9 | 27 | 243 | 9 | 0.0007484 | 2.7719e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 9 | 0.0007484 | 2.7719e-05
137550 | 41586.4132 | 41586.4479 | 2 | 47 | 94 | 2 | 0.00028951 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 2 | 0.00028951 | 6.1597e-06
137551 | 41587.3646 | 41587.5882 | 55 | 319 | 17545 | 55 | 0.054036 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-09 | 2014 | 2014 | 2013-11-09 | B | 55 | 0.054036 | 0.00016939
137552 | 41587.9514 | 41587.9722 | 181 | 27 | 4887 | 181 | 0.015051 | 0.00055745 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-09 | 2014 | 2014 | 2013-11-09 | C | 181 | 0.015051 | 0.00055745
137554 | 41588.3153 | 41588.4403 | 252 | 177 | 12803 | 72.3333 | 0.039431 | 0.00077612 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-10 | 2014 | 2014 | 2013-11-10 | C | 72.3333 | 0.039431 | 0.00077612
137556 | 41589.0083 | 41589.0493 | 2936 | 56 | 156241.8983 | 2790.0339 | 0.4812 | 0.0090424 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 2790.0339 | 0.4812 | 0.0090424
137557 | 41586.4028 | 41586.434 | 8 | 42 | 336 | 8 | 0.0010348 | 2.4639e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-08 | 2014 | 2014 | 2013-11-08 | C | 8 | 0.0010348 | 2.4639e-05
137558 | 41588.7431 | 41588.8333 | 2 | 127 | 254 | 2 | 0.00078228 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-10 | 2014 | 2014 | 2013-11-10 | C | 2 | 0.00078228 | 6.1597e-06
137559 | 41585.8917 | 41586.7812 | 7 | 1278 | 8946 | 7 | 0.027552 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 7 | 0.027552 | 2.1559e-05
137561 | 41566.3646 | 41566.5069 | 40 | 202 | 8080 | 40 | 0.024885 | 0.00012319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | B | 40 | 0.024885 | 0.00012319
137562 | 41588.3694 | 41588.5542 | 81 | 263 | 21303 | 81 | 0.06561 | 0.00024947 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-10 | 2014 | 2014 | 2013-11-10 | B | 81 | 0.06561 | 0.00024947
137563 | 41585.5465 | 41586.4667 | 273 | 1322 | 43113.1638 | 32.6121 | 0.13278 | 0.0008408 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-07 | 2014 | 2014 | 2013-11-07 | C | 32.6121 | 0.13278 | 0.0008408
137564 | 41566.5 | 41566.625 | 10 | 177 | 1770 | 10 | 0.0054513 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-19 | 2014 | 2014 | 2013-10-19 | B | 10 | 0.0054513 | 3.0798e-05
137566 | 41549.375 | 41549.5521 | 13 | 252 | 3276 | 13 | 0.01009 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-02 | 2014 | 2014 | 2013-10-02 | B | 13 | 0.01009 | 4.0038e-05
137567 | 41552.5188 | 41552.6417 | 1 | 174 | 174 | 1 | 0.00053589 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-05 | 2014 | 2014 | 2013-10-05 | B | 1 | 0.00053589 | 3.0798e-06
137568 | 41555.3715 | 41555.6215 | 20 | 357 | 7140 | 20 | 0.02199 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-08 | 2014 | 2014 | 2013-10-08 | B | 20 | 0.02199 | 6.1597e-05
137569 | 41548.4375 | 41548.5535 | 3 | 164 | 492 | 3 | 0.0015153 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-01 | 2014 | 2014 | 2013-10-01 | B | 3 | 0.0015153 | 9.2395e-06
137571 | 41557.3472 | 41557.6333 | 3 | 409 | 1227 | 3 | 0.003779 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | B | 3 | 0.003779 | 9.2395e-06
137572 | 41564.4174 | 41564.6229 | 2 | 293 | 586 | 2 | 0.0018048 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 2 | 0.0018048 | 6.1597e-06
137573 | 41569.3542 | 41569.5931 | 6 | 341 | 2046 | 6 | 0.0063014 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-22 | 2014 | 2014 | 2013-10-22 | B | 6 | 0.0063014 | 1.8479e-05
137574 | 41570.4167 | 41570.6236 | 1 | 295 | 295 | 1 | 0.00090855 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-23 | 2014 | 2014 | 2013-10-23 | B | 1 | 0.00090855 | 3.0798e-06
137575 | 41572.4583 | 41572.5569 | 9 | 139 | 1251 | 9 | 0.0038529 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-25 | 2014 | 2014 | 2013-10-25 | B | 9 | 0.0038529 | 2.7719e-05
137576 | 41577.375 | 41577.6 | 3 | 321 | 963 | 3 | 0.0029659 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-30 | 2014 | 2014 | 2013-10-30 | B | 3 | 0.0029659 | 9.2395e-06
137577 | 41564.9792 | 41565.0264 | 152 | 65 | 9880 | 152 | 0.030429 | 0.00046814 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-17 | 2014 | 2014 | 2013-10-17 | B | 152 | 0.030429 | 0.00046814
137583 | 41589.4688 | 41589.4896 | 4 | 27 | 108 | 4 | 0.00033262 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 4 | 0.00033262 | 1.2319e-05
137584 | 41589.5417 | 41589.5729 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 4 | 0.00051741 | 1.2319e-05
137585 | 41589.375 | 41589.4583 | 7 | 117 | 819 | 7 | 0.0025224 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 7 | 0.0025224 | 2.1559e-05
137587 | 41589.3958 | 41589.5035 | 8 | 152 | 1216 | 8 | 0.0037451 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 8 | 0.0037451 | 2.4639e-05
137588 | 41589.4215 | 41589.6444 | 14 | 318 | 4452 | 14 | 0.013711 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 14 | 0.013711 | 4.3118e-05
137589 | 41589.5687 | 41589.6875 | 1 | 168 | 168 | 1 | 0.00051741 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 1 | 0.00051741 | 3.0798e-06
137590 | 41589.3854 | 41589.6042 | 42 | 312 | 13104 | 42 | 0.040358 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | B | 42 | 0.040358 | 0.00012935
137591 | 41589.6701 | 41589.6826 | 378 | 15 | 5670 | 378 | 0.017463 | 0.0011642 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 378 | 0.017463 | 0.0011642
137592 | 41589.6979 | 41589.7535 | 2 | 77 | 154 | 2 | 0.0004743 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 2 | 0.0004743 | 6.1597e-06
137593 | 41589.6236 | 41589.6667 | 9 | 59 | 531 | 9 | 0.0016354 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 9 | 0.0016354 | 2.7719e-05
137594 | 41589.5174 | 41589.5944 | 8 | 108 | 864 | 8 | 0.002661 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 8 | 0.002661 | 2.4639e-05
137595 | 41589.3819 | 41589.4472 | 341 | 91 | 31031 | 341 | 0.095571 | 0.0010502 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-11 | 2014 | 2014 | 2013-11-11 | C | 341 | 0.095571 | 0.0010502
137599 | 41590.3854 | 41590.5792 | 13 | 276 | 3588 | 13 | 0.01105 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 13 | 0.01105 | 4.0038e-05
137600 | 41590.3632 | 41590.5819 | 50 | 312 | 15600 | 50 | 0.048046 | 0.00015399 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 50 | 0.048046 | 0.00015399
137604 | 41590.3854 | 41590.625 | 35 | 342 | 11970 | 35 | 0.036866 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 35 | 0.036866 | 0.00010779
137605 | 41590.3958 | 41590.6306 | 15 | 335 | 5025 | 15 | 0.015476 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 15 | 0.015476 | 4.6198e-05
137607 | 41590.3778 | 41590.6236 | 15 | 351 | 5265 | 15 | 0.016215 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 15 | 0.016215 | 4.6198e-05
137608 | 41590.6431 | 41590.6979 | 21 | 76 | 1596 | 21 | 0.0049154 | 6.4677e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | C | 21 | 0.0049154 | 6.4677e-05
137609 | 41590.6618 | 41590.9604 | 814 | 427 | 19418.5698 | 45.4767 | 0.059806 | 0.002507 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | C | 45.4767 | 0.059806 | 0.002507
137614 | 41590.4431 | 41590.4715 | 337 | 38 | 12806 | 337 | 0.03944 | 0.0010379 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | C | 337 | 0.03944 | 0.0010379
137616 | 41590.5417 | 41590.6042 | 11 | 87 | 957 | 11 | 0.0029474 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | C | 11 | 0.0029474 | 3.3878e-05
137627 | 41591.3833 | 41591.4375 | 2 | 75 | 150 | 2 | 0.00046198 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | C | 2 | 0.00046198 | 6.1597e-06
137630 | 41591.416 | 41591.6194 | 14 | 290 | 4060 | 14 | 0.012504 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | B | 14 | 0.012504 | 4.3118e-05
137633 | 41591.4938 | 41591.6181 | 4 | 176 | 704 | 4 | 0.0021682 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | C | 4 | 0.0021682 | 1.2319e-05
137636 | 41591.3958 | 41591.625 | 72 | 327 | 23544 | 72 | 0.072512 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | B | 72 | 0.072512 | 0.00022175
137643 | 41592.3854 | 41592.4931 | 1 | 152 | 152 | 1 | 0.00046814 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-14 | 2014 | 2014 | 2013-11-14 | B | 1 | 0.00046814 | 3.0798e-06
137648 | 41592.3854 | 41592.609 | 9 | 319 | 2871 | 9 | 0.0088422 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-14 | 2014 | 2014 | 2013-11-14 | B | 9 | 0.0088422 | 2.7719e-05
137652 | 41592.375 | 41592.65 | 43 | 393 | 9021.1364 | 22.9545 | 0.027784 | 0.00013243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-14 | 2014 | 2014 | 2013-11-14 | B | 22.9545 | 0.027784 | 0.00013243
137653 | 41592.9236 | 41593.0243 | 8 | 142 | 1136 | 8 | 0.0034987 | 2.4639e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-14 | 2014 | 2014 | 2013-11-14 | C | 8 | 0.0034987 | 2.4639e-05
137656 | 41593.4514 | 41593.4965 | 7 | 62 | 434 | 7 | 0.0013367 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | C | 7 | 0.0013367 | 2.1559e-05
137657 | 41593.375 | 41593.4167 | 13 | 57 | 741 | 13 | 0.0022822 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 13 | 0.0022822 | 4.0038e-05
137658 | 41593.3542 | 41593.4854 | 2 | 186 | 372 | 2 | 0.0011457 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 2 | 0.0011457 | 6.1597e-06
137659 | 41593.4653 | 41593.5312 | 2 | 92 | 184 | 2 | 0.00056669 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 2 | 0.00056669 | 6.1597e-06
137662 | 41593.2958 | 41593.3569 | 831 | 85 | 70635 | 831 | 0.21754 | 0.0025593 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | C | 831 | 0.21754 | 0.0025593
137664 | 41593.3854 | 41593.4167 | 7 | 42 | 294 | 7 | 0.00090547 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 7 | 0.00090547 | 2.1559e-05
137665 | 41593.4688 | 41593.5 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 5 | 0.00064677 | 1.5399e-05
137666 | 41593.5521 | 41593.5729 | 9 | 27 | 243 | 9 | 0.0007484 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 9 | 0.0007484 | 2.7719e-05
137668 | 41593.5521 | 41593.5938 | 16 | 57 | 912 | 16 | 0.0028088 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 16 | 0.0028088 | 4.9277e-05
137669 | 41593.3333 | 41593.5 | 1 | 237 | 237 | 1 | 0.00072992 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | C | 1 | 0.00072992 | 3.0798e-06
137670 | 41593.3889 | 41593.541 | 32 | 216 | 6912 | 32 | 0.021288 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 32 | 0.021288 | 9.8555e-05
137671 | 41593.2958 | 41593.4924 | 788 | 280 | 115684.523 | 413.159 | 0.35629 | 0.0024269 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | C | 413.159 | 0.35629 | 0.0024269
137672 | 41593.441 | 41593.6125 | 33 | 244 | 8052 | 33 | 0.024799 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 33 | 0.024799 | 0.00010163
137673 | 41593.3785 | 41593.6285 | 4 | 357 | 1428 | 4 | 0.004398 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | B | 4 | 0.004398 | 1.2319e-05
137675 | 41593.7049 | 41593.7729 | 14 | 95 | 1330 | 14 | 0.0040962 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-15 | 2014 | 2014 | 2013-11-15 | C | 14 | 0.0040962 | 4.3118e-05
137677 | 41594.4556 | 41594.4938 | 706 | 52 | 18800.3636 | 361.5455 | 0.057902 | 0.0021744 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-16 | 2014 | 2014 | 2013-11-16 | C | 361.5455 | 0.057902 | 0.0021744
137678 | 41594.5104 | 41594.5285 | 101 | 23 | 2323 | 101 | 0.0071545 | 0.00031106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-16 | 2014 | 2014 | 2013-11-16 | C | 101 | 0.0071545 | 0.00031106
137682 | 41594.375 | 41594.5417 | 22 | 237 | 5214 | 22 | 0.016058 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-16 | 2014 | 2014 | 2013-11-16 | B | 22 | 0.016058 | 6.7757e-05
137685 | 41595.3042 | 41595.4472 | 3 | 203 | 609 | 3 | 0.0018756 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-17 | 2014 | 2014 | 2013-11-17 | C | 3 | 0.0018756 | 9.2395e-06
137686 | 41595.3125 | 41595.5306 | 4 | 311 | 1244 | 4 | 0.0038313 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-17 | 2014 | 2014 | 2013-11-17 | C | 4 | 0.0038313 | 1.2319e-05
137693 | 41596.3854 | 41596.4688 | 2 | 117 | 234 | 2 | 0.00072068 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.00072068 | 6.1597e-06
137698 | 41596.3958 | 41596.4583 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | C | 3 | 0.00080384 | 9.2395e-06
137700 | 41596.4618 | 41596.5382 | 2 | 107 | 214 | 2 | 0.00065909 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.00065909 | 6.1597e-06
137701 | 41596.4167 | 41596.4653 | 2 | 67 | 134 | 2 | 0.0004127 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.0004127 | 6.1597e-06
137702 | 41596.5417 | 41596.625 | 4 | 117 | 468 | 4 | 0.0014414 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 4 | 0.0014414 | 1.2319e-05
137704 | 41596.4201 | 41596.4688 | 2 | 67 | 134 | 2 | 0.0004127 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.0004127 | 6.1597e-06
137705 | 41596.4792 | 41596.5417 | 4 | 87 | 348 | 4 | 0.0010718 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 4 | 0.0010718 | 1.2319e-05
137706 | 41596.5417 | 41596.625 | 2 | 117 | 234 | 2 | 0.00072068 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.00072068 | 6.1597e-06
137707 | 41596.5417 | 41596.625 | 3 | 117 | 351 | 3 | 0.001081 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 3 | 0.001081 | 9.2395e-06
137708 | 41596.5 | 41596.5521 | 2 | 72 | 144 | 2 | 0.0004435 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 2 | 0.0004435 | 6.1597e-06
137709 | 41596.4375 | 41596.4722 | 8 | 47 | 376 | 8 | 0.001158 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 8 | 0.001158 | 2.4639e-05
137712 | 41596.3882 | 41596.6667 | 6 | 398 | 2388 | 6 | 0.0073547 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 6 | 0.0073547 | 1.8479e-05
137713 | 41596.8118 | 41596.8667 | 244 | 76 | 11852.1519 | 155.9494 | 0.036503 | 0.00075148 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | C | 155.9494 | 0.036503 | 0.00075148
137716 | 41596.7444 | 41596.834 | 4 | 126 | 504 | 4 | 0.0015522 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | C | 4 | 0.0015522 | 1.2319e-05
137719 | 41597.4417 | 41597.4806 | 5 | 53 | 265 | 5 | 0.00081616 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 5 | 0.00081616 | 1.5399e-05
137721 | 41597.3854 | 41597.5986 | 103 | 304 | 31312 | 103 | 0.096436 | 0.00031722 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 103 | 0.096436 | 0.00031722
137724 | 41597.5382 | 41597.6424 | 1027 | 147 | 68566.68 | 466.44 | 0.21117 | 0.003163 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 466.44 | 0.21117 | 0.003163
137726 | 41597.3958 | 41597.4583 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 3 | 0.00080384 | 9.2395e-06
137727 | 41597.375 | 41597.6361 | 15 | 373 | 5595 | 15 | 0.017232 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 15 | 0.017232 | 4.6198e-05
137728 | 41597.4688 | 41597.5104 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 6 | 0.0010533 | 1.8479e-05
137729 | 41597.5417 | 41597.5868 | 3 | 62 | 186 | 3 | 0.00057285 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 3 | 0.00057285 | 9.2395e-06
137731 | 41597.3958 | 41597.4583 | 4 | 87 | 348 | 4 | 0.0010718 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 4 | 0.0010718 | 1.2319e-05
137732 | 41597.4792 | 41597.5417 | 11 | 87 | 957 | 11 | 0.0029474 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 11 | 0.0029474 | 3.3878e-05
137733 | 41597.5417 | 41597.625 | 2 | 117 | 234 | 2 | 0.00072068 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 2 | 0.00072068 | 6.1597e-06
137734 | 41597.4062 | 41597.4479 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 4 | 0.0007022 | 1.2319e-05
137735 | 41597.4792 | 41597.5208 | 2 | 57 | 114 | 2 | 0.0003511 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 2 | 0.0003511 | 6.1597e-06
137737 | 41597.5729 | 41597.6146 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 4 | 0.0007022 | 1.2319e-05
137738 | 41597.3958 | 41597.625 | 1 | 327 | 327 | 1 | 0.0010071 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 1 | 0.0010071 | 3.0798e-06
137739 | 41597.6424 | 41597.6667 | 259 | 32 | 8288 | 259 | 0.025526 | 0.00079768 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 259 | 0.025526 | 0.00079768
137740 | 41597.6986 | 41597.7375 | 1 | 53 | 53 | 1 | 0.00016323 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 1 | 0.00016323 | 3.0798e-06
137746 | 41597.7743 | 41597.8785 | 1 | 147 | 147 | 1 | 0.00045274 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 1 | 0.00045274 | 3.0798e-06
137747 | 41597.8264 | 41597.8472 | 1 | 27 | 27 | 1 | 8.3156e-05 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 1 | 8.3156e-05 | 3.0798e-06
137748 | 41597.7431 | 41597.7639 | 3 | 27 | 81 | 3 | 0.00024947 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 3 | 0.00024947 | 9.2395e-06
137751 | 41597.8493 | 41598.1028 | 804 | 362 | 84131.7753 | 232.4082 | 0.25911 | 0.0024762 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | C | 232.4082 | 0.25911 | 0.0024762
137752 | 41598.0292 | 41598.1972 | 32 | 239 | 7648 | 32 | 0.023555 | 9.8555e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 32 | 0.023555 | 9.8555e-05
137753 | 41598.0854 | 41598.2396 | 76 | 219 | 16644 | 76 | 0.051261 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 76 | 0.051261 | 0.00023407
137754 | 41591.8028 | 41591.9583 | 2 | 221 | 442 | 2 | 0.0013613 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | B | 2 | 0.0013613 | 6.1597e-06
137755 | 41591.4021 | 41591.5944 | 24 | 274 | 6576 | 24 | 0.020253 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-13 | 2014 | 2014 | 2013-11-13 | B | 24 | 0.020253 | 7.3916e-05
137756 | 41590.9583 | 41591.1687 | 24 | 300 | 7200 | 24 | 0.022175 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-12 | 2014 | 2014 | 2013-11-12 | B | 24 | 0.022175 | 7.3916e-05
137757 | 41582.3861 | 41582.5681 | 8 | 259 | 2072 | 8 | 0.0063814 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-04 | 2014 | 2014 | 2013-11-04 | B | 8 | 0.0063814 | 2.4639e-05
137761 | 41598.4535 | 41598.4938 | 21 | 55 | 737.7586 | 13.4138 | 0.0022722 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 13.4138 | 0.0022722 | 6.4677e-05
137764 | 41598.3889 | 41598.6174 | 37 | 326 | 12062 | 37 | 0.037149 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 37 | 0.037149 | 0.00011395
137766 | 41598.4792 | 41598.5104 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 4 | 0.00051741 | 1.2319e-05
137767 | 41598.4167 | 41598.5833 | 5 | 237 | 1185 | 5 | 0.0036496 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 5 | 0.0036496 | 1.5399e-05
137769 | 41598.3854 | 41598.4549 | 4 | 97 | 388 | 4 | 0.001195 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 4 | 0.001195 | 1.2319e-05
137770 | 41598.4583 | 41598.5312 | 4 | 102 | 408 | 4 | 0.0012566 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 4 | 0.0012566 | 1.2319e-05
137771 | 41598.5417 | 41598.6042 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 3 | 0.00080384 | 9.2395e-06
137772 | 41598.4583 | 41598.5417 | 14 | 117 | 1638 | 14 | 0.0050448 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 14 | 0.0050448 | 4.3118e-05
137774 | 41598.3854 | 41598.4479 | 7 | 87 | 609 | 7 | 0.0018756 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 7 | 0.0018756 | 2.1559e-05
137775 | 41598.5417 | 41598.5833 | 10 | 57 | 570 | 10 | 0.0017555 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | B | 10 | 0.0017555 | 3.0798e-05
137777 | 41597.9583 | 41598.0687 | 19 | 156 | 2964 | 19 | 0.0091287 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 19 | 0.0091287 | 5.8517e-05
137779 | 41598.234 | 41598.2444 | 1 | 12 | 12 | 1 | 3.6958e-05 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 1 | 3.6958e-05 | 3.0798e-06
137780 | 41598.234 | 41598.2542 | 1 | 26 | 26 | 1 | 8.0076e-05 | 3.0798e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 1 | 8.0076e-05 | 3.0798e-06
137782 | 41598.234 | 41598.2479 | 2166 | 17 | 36822 | 2166 | 0.11341 | 0.0066709 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 2166 | 0.11341 | 0.0066709
137783 | 41598.234 | 41598.2549 | 154 | 27 | 4158 | 154 | 0.012806 | 0.0004743 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 154 | 0.012806 | 0.0004743
137784 | 41598.4104 | 41598.709 | 18 | 427 | 7686 | 18 | 0.023672 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 18 | 0.023672 | 5.5437e-05
137785 | 41598.5361 | 41598.55 | 1 | 17 | 17 | 1 | 5.2357e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 1 | 5.2357e-05 | 3.0798e-06
137786 | 41598.725 | 41598.7674 | 1 | 58 | 58 | 1 | 0.00017863 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 1 | 0.00017863 | 3.0798e-06
137788 | 41598.3535 | 41598.3847 | 6296 | 42 | 106974.9333 | 2547.0222 | 0.32947 | 0.019391 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 2547.0222 | 0.32947 | 0.019391
137789 | 41598.8292 | 41598.8799 | 2740 | 70 | 161694.2466 | 2309.9178 | 0.49799 | 0.0084388 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 2309.9178 | 0.49799 | 0.0084388
137790 | 41598.8306 | 41598.8521 | 55 | 28 | 1540 | 55 | 0.004743 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 55 | 0.004743 | 0.00016939
137791 | 41598.5104 | 41598.8632 | 47 | 505 | 23735 | 47 | 0.0731 | 0.00014475 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 47 | 0.0731 | 0.00014475
137792 | 41598.5424 | 41598.7778 | 259 | 336 | 3850.6195 | 11.4602 | 0.011859 | 0.00079768 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-20 | 2014 | 2014 | 2013-11-20 | C | 11.4602 | 0.011859 | 0.00079768
137793 | 41599.0965 | 41599.1333 | 470 | 50 | 14123.5849 | 282.4717 | 0.043498 | 0.0014475 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | C | 282.4717 | 0.043498 | 0.0014475
137794 | 41599.2847 | 41599.3299 | 25 | 62 | 1550 | 25 | 0.0047738 | 7.6996e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | C | 25 | 0.0047738 | 7.6996e-05
137797 | 41599.3958 | 41599.5938 | 6 | 282 | 1692 | 6 | 0.0052111 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 6 | 0.0052111 | 1.8479e-05
137798 | 41599.3861 | 41599.6118 | 9 | 322 | 2898 | 9 | 0.0089254 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 9 | 0.0089254 | 2.7719e-05
137799 | 41599.5729 | 41599.6153 | 15 | 58 | 870 | 15 | 0.0026795 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | C | 15 | 0.0026795 | 4.6198e-05
137801 | 41599.3924 | 41599.4306 | 2 | 52 | 104 | 2 | 0.0003203 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 2 | 0.0003203 | 6.1597e-06
137802 | 41599.4583 | 41599.4965 | 2 | 52 | 104 | 2 | 0.0003203 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 2 | 0.0003203 | 6.1597e-06
137803 | 41599.5451 | 41599.5903 | 5 | 62 | 310 | 5 | 0.00095475 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 5 | 0.00095475 | 1.5399e-05
137804 | 41599.3785 | 41599.434 | 1 | 77 | 77 | 1 | 0.00023715 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 1 | 0.00023715 | 3.0798e-06
137805 | 41599.4583 | 41599.5208 | 7 | 87 | 609 | 7 | 0.0018756 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 7 | 0.0018756 | 2.1559e-05
137806 | 41599.5417 | 41599.5694 | 9 | 37 | 333 | 9 | 0.0010256 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 9 | 0.0010256 | 2.7719e-05
137807 | 41599.3542 | 41599.6875 | 84 | 477 | 11269.125 | 23.625 | 0.034707 | 0.00025871 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 23.625 | 0.034707 | 0.00025871
137808 | 41599.8528 | 41599.9201 | 2 | 94 | 188 | 2 | 0.00057901 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 2 | 0.00057901 | 6.1597e-06
137814 | 41600.3958 | 41600.4965 | 44 | 142 | 6248 | 44 | 0.019243 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | B | 44 | 0.019243 | 0.00013551
137815 | 41600.4167 | 41600.4965 | 3 | 112 | 336 | 3 | 0.0010348 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | B | 3 | 0.0010348 | 9.2395e-06
137816 | 41600.4854 | 41600.5104 | 1 | 33 | 33 | 1 | 0.00010163 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | C | 1 | 0.00010163 | 3.0798e-06
137818 | 41600.4688 | 41600.5312 | 1 | 87 | 87 | 1 | 0.00026795 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | B | 1 | 0.00026795 | 3.0798e-06
137820 | 41600.5868 | 41600.5986 | 7 | 14 | 98 | 7 | 0.00030182 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | B | 7 | 0.00030182 | 2.1559e-05
137822 | 41600.5521 | 41600.6111 | 5 | 82 | 410 | 5 | 0.0012627 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | B | 5 | 0.0012627 | 1.5399e-05
137825 | 41600.625 | 41600.6382 | 93 | 16 | 1488 | 93 | 0.0045828 | 0.00028643 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | C | 93 | 0.0045828 | 0.00028643
137826 | 41600.6194 | 41600.6486 | 59 | 39 | 1948.1429 | 49.9524 | 0.006 | 0.00018171 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | C | 49.9524 | 0.006 | 0.00018171
137827 | 41600.7215 | 41600.8625 | 205 | 200 | 17599.0148 | 87.9951 | 0.054202 | 0.00063137 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | C | 87.9951 | 0.054202 | 0.00063137
137830 | 41601.0972 | 41601.1181 | 60 | 27 | 1620 | 60 | 0.0049893 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-23 | 2014 | 2014 | 2013-11-23 | C | 60 | 0.0049893 | 0.00018479
137833 | 41600.8535 | 41601.6667 | 533 | 1168 | 52803.3749 | 45.2084 | 0.16263 | 0.0016416 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-22 | 2014 | 2014 | 2013-11-22 | C | 45.2084 | 0.16263 | 0.0016416
137834 | 41601.3646 | 41601.5451 | 35 | 257 | 8995 | 35 | 0.027703 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-23 | 2014 | 2014 | 2013-11-23 | B | 35 | 0.027703 | 0.00010779
137835 | 41601.6236 | 41601.6479 | 49 | 32 | 1568 | 49 | 0.0048292 | 0.00015091 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-23 | 2014 | 2014 | 2013-11-23 | C | 49 | 0.0048292 | 0.00015091
137837 | 41601.9375 | 41601.9701 | 830 | 44 | 31370.1277 | 712.9574 | 0.096615 | 0.0025563 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-23 | 2014 | 2014 | 2013-11-23 | C | 712.9574 | 0.096615 | 0.0025563
137838 | 41602.0465 | 41602.1243 | 298 | 109 | 32482 | 298 | 0.10004 | 0.00091779 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-24 | 2014 | 2014 | 2013-11-24 | C | 298 | 0.10004 | 0.00091779
137840 | 41602.6806 | 41603.5583 | 29 | 1261 | 5261.4826 | 4.1725 | 0.016205 | 8.9315e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-24 | 2014 | 2014 | 2013-11-24 | C | 4.1725 | 0.016205 | 8.9315e-05
137841 | 41602.5035 | 41602.5903 | 2 | 122 | 244 | 2 | 0.00075148 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-24 | 2014 | 2014 | 2013-11-24 | C | 2 | 0.00075148 | 6.1597e-06
137847 | 41603.2917 | 41603.3181 | 29 | 35 | 1015 | 29 | 0.003126 | 8.9315e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | C | 29 | 0.003126 | 8.9315e-05
137849 | 41603.3819 | 41603.4375 | 1 | 77 | 77 | 1 | 0.00023715 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | B | 1 | 0.00023715 | 3.0798e-06
137850 | 41603.4583 | 41603.5208 | 6 | 87 | 522 | 6 | 0.0016077 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | B | 6 | 0.0016077 | 1.8479e-05
137854 | 41603.4382 | 41603.5007 | 22 | 87 | 1914 | 22 | 0.0058948 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | C | 22 | 0.0058948 | 6.7757e-05
137855 | 41603.5521 | 41603.6285 | 4 | 107 | 428 | 4 | 0.0013182 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | B | 4 | 0.0013182 | 1.2319e-05
137857 | 41603.5 | 41603.6549 | 58 | 220 | 12760 | 58 | 0.039299 | 0.00017863 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | B | 58 | 0.039299 | 0.00017863
137858 | 41603.7076 | 41603.7257 | 45 | 23 | 1035 | 45 | 0.0031876 | 0.00013859 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | C | 45 | 0.0031876 | 0.00013859
137859 | 41603.7292 | 41603.7326 | 5 | 2 | 10 | 5 | 3.0798e-05 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | C | 5 | 3.0798e-05 | 1.5399e-05
137861 | 41604.1882 | 41604.3882 | 209 | 285 | 28781.0417 | 100.9861 | 0.088641 | 0.00064369 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 100.9861 | 0.088641 | 0.00064369
137863 | 41604.375 | 41604.5069 | 4 | 187 | 748 | 4 | 0.0023037 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 4 | 0.0023037 | 1.2319e-05
137864 | 41604.509 | 41604.525 | 51 | 20 | 1020 | 51 | 0.0031414 | 0.00015707 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 51 | 0.0031414 | 0.00015707
137865 | 41604.309 | 41604.3472 | 158 | 52 | 7289.4545 | 140.1818 | 0.02245 | 0.00048662 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 140.1818 | 0.02245 | 0.00048662
137866 | 41604.3917 | 41604.5924 | 2 | 286 | 572 | 2 | 0.0017617 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 2 | 0.0017617 | 6.1597e-06
137869 | 41604.3542 | 41604.625 | 29 | 387 | 11223 | 29 | 0.034565 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 29 | 0.034565 | 8.9315e-05
137870 | 41604.5917 | 41604.6319 | 9 | 55 | 495 | 9 | 0.0015245 | 2.7719e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 9 | 0.0015245 | 2.7719e-05
137871 | 41604.4181 | 41604.6646 | 3 | 352 | 1056 | 3 | 0.0032523 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 3 | 0.0032523 | 9.2395e-06
137872 | 41604.6347 | 41604.6486 | 357 | 17 | 6069 | 357 | 0.018692 | 0.0010995 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 357 | 0.018692 | 0.0010995
137873 | 41604.4028 | 41604.6285 | 25 | 322 | 8050 | 25 | 0.024793 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 25 | 0.024793 | 7.6996e-05
137875 | 41604.3771 | 41604.5757 | 2 | 283 | 566 | 2 | 0.0017432 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 2 | 0.0017432 | 6.1597e-06
137877 | 41604.3542 | 41604.7042 | 214 | 501 | 18576.7619 | 37.0794 | 0.057213 | 0.00065909 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | B | 37.0794 | 0.057213 | 0.00065909
137878 | 41604.4444 | 41604.5736 | 3 | 183 | 549 | 3 | 0.0016908 | 9.2395e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 3 | 0.0016908 | 9.2395e-06
137879 | 41604.5715 | 41604.7833 | 195 | 302 | 19279.482 | 63.8393 | 0.059378 | 0.00060057 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 63.8393 | 0.059378 | 0.00060057
137881 | 41605.0368 | 41605.5139 | 169 | 684 | 77569.7817 | 113.4061 | 0.2389 | 0.00052049 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 113.4061 | 0.2389 | 0.00052049
137883 | 41604.3611 | 41604.4958 | 77 | 191 | 14707 | 77 | 0.045295 | 0.00023715 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-26 | 2014 | 2014 | 2013-11-26 | C | 77 | 0.045295 | 0.00023715
137884 | 41605.4278 | 41605.4847 | 312 | 79 | 17304.8537 | 219.0488 | 0.053296 | 0.00096091 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 219.0488 | 0.053296 | 0.00096091
137889 | 41605.4174 | 41605.5785 | 7 | 229 | 1603 | 7 | 0.004937 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 7 | 0.004937 | 2.1559e-05
137891 | 41605.4062 | 41605.6049 | 2 | 283 | 566 | 2 | 0.0017432 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 2 | 0.0017432 | 6.1597e-06
137893 | 41605.4167 | 41605.4896 | 2 | 102 | 204 | 2 | 0.00062829 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 2 | 0.00062829 | 6.1597e-06
137894 | 41605.5 | 41605.5799 | 3 | 112 | 336 | 3 | 0.0010348 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 3 | 0.0010348 | 9.2395e-06
137895 | 41605.5521 | 41605.6076 | 4 | 77 | 308 | 4 | 0.00094859 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 4 | 0.00094859 | 1.2319e-05
137896 | 41605.4583 | 41605.5 | 7 | 57 | 399 | 7 | 0.0012289 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 7 | 0.0012289 | 2.1559e-05
137897 | 41605.3889 | 41605.4375 | 9 | 67 | 603 | 9 | 0.0018571 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 9 | 0.0018571 | 2.7719e-05
137898 | 41605.4986 | 41605.5396 | 1 | 56 | 56 | 1 | 0.00017247 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 1 | 0.00017247 | 3.0798e-06
137899 | 41605.7326 | 41605.7458 | 860 | 16 | 11183.1579 | 698.9474 | 0.034442 | 0.0026487 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 698.9474 | 0.034442 | 0.0026487
137900 | 41605.8396 | 41606.0326 | 355 | 275 | 16855.1259 | 61.2914 | 0.051911 | 0.0010933 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 61.2914 | 0.051911 | 0.0010933
137901 | 41605.8139 | 41605.9215 | 273 | 152 | 19347.1484 | 127.2839 | 0.059586 | 0.0008408 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 127.2839 | 0.059586 | 0.0008408
137902 | 41605.8549 | 41605.8806 | 3 | 34 | 102 | 3 | 0.00031414 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 3 | 0.00031414 | 9.2395e-06
137903 | 41605.9437 | 41605.9507 | 8 | 7 | 56 | 8 | 0.00017247 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 8 | 0.00017247 | 2.4639e-05
137904 | 41606.1028 | 41606.1576 | 343 | 76 | 19849.4684 | 261.1772 | 0.061133 | 0.0010564 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 261.1772 | 0.061133 | 0.0010564
137905 | 41605.3764 | 41605.5604 | 15 | 262 | 3930 | 15 | 0.012104 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | B | 15 | 0.012104 | 4.6198e-05
137909 | 41605.3104 | 41605.3236 | 902 | 16 | 10483.3684 | 655.2105 | 0.032287 | 0.002778 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 655.2105 | 0.032287 | 0.002778
137910 | 41605.6535 | 41605.6687 | 192 | 19 | 3072.8182 | 161.7273 | 0.0094638 | 0.00059133 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 161.7273 | 0.0094638 | 0.00059133
137912 | 41606.3403 | 41606.4507 | 9 | 156 | 1404 | 9 | 0.0043241 | 2.7719e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 9 | 0.0043241 | 2.7719e-05
137913 | 41606.4729 | 41606.5194 | 3 | 64 | 192 | 3 | 0.00059133 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 3 | 0.00059133 | 9.2395e-06
137914 | 41606.3604 | 41606.6458 | 214 | 408 | 60361.1679 | 147.944 | 0.1859 | 0.00065909 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | B | 147.944 | 0.1859 | 0.00065909
137915 | 41606.3764 | 41606.6285 | 19 | 360 | 6840 | 19 | 0.021066 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | B | 19 | 0.021066 | 5.8517e-05
137916 | 41606.375 | 41606.6354 | 5 | 372 | 1860 | 5 | 0.0057285 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 5 | 0.0057285 | 1.5399e-05
137919 | 41606.666 | 41606.6847 | 681 | 24 | 16344 | 681 | 0.050337 | 0.0020974 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 681 | 0.050337 | 0.0020974
137923 | 41606.375 | 41606.6354 | 25 | 372 | 9300 | 25 | 0.028643 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | B | 25 | 0.028643 | 7.6996e-05
137925 | 41606.6062 | 41606.6236 | 125 | 22 | 2750 | 125 | 0.0084696 | 0.00038498 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 125 | 0.0084696 | 0.00038498
137926 | 41606.3958 | 41606.4938 | 13 | 138 | 1794 | 13 | 0.0055252 | 4.0038e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 13 | 0.0055252 | 4.0038e-05
137928 | 41607.0007 | 41607.1528 | 157 | 216 | 33912 | 157 | 0.10444 | 0.00048354 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | B | 157 | 0.10444 | 0.00048354
137929 | 41606.8181 | 41606.8458 | 15 | 37 | 555 | 15 | 0.0017093 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 15 | 0.0017093 | 4.6198e-05
137931 | 41606.7368 | 41607.0556 | 121 | 456 | 36199.8431 | 79.3856 | 0.11149 | 0.00037266 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 79.3856 | 0.11149 | 0.00037266
137932 | 41605.3111 | 41605.3153 | 187 | 3 | 561 | 187 | 0.0017278 | 0.00057593 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-27 | 2014 | 2014 | 2013-11-27 | C | 187 | 0.0017278 | 0.00057593
137933 | 41607.1299 | 41607.3361 | 132 | 294 | 21924.2828 | 74.5724 | 0.067523 | 0.00040654 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 74.5724 | 0.067523 | 0.00040654
137934 | 41607.3854 | 41607.4674 | 5 | 115 | 575 | 5 | 0.0017709 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | B | 5 | 0.0017709 | 1.5399e-05
137935 | 41606.6972 | 41606.7139 | 232 | 21 | 4872 | 232 | 0.015005 | 0.00071452 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 232 | 0.015005 | 0.00071452
137938 | 41606.8215 | 41606.834 | 240 | 15 | 2895 | 193 | 0.0089161 | 0.00073916 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 193 | 0.0089161 | 0.00073916
137939 | 41606.7493 | 41606.7708 | 232 | 28 | 6496 | 232 | 0.020007 | 0.00071452 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 232 | 0.020007 | 0.00071452
137941 | 41606.7819 | 41606.8472 | 681 | 91 | 58853.766 | 646.7447 | 0.18126 | 0.0020974 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | C | 646.7447 | 0.18126 | 0.0020974
137942 | 41607.3861 | 41607.5833 | 34 | 281 | 9554 | 34 | 0.029425 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 34 | 0.029425 | 0.00010471
137943 | 41607.4333 | 41607.5764 | 1 | 203 | 203 | 1 | 0.00062521 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 1 | 0.00062521 | 3.0798e-06
137945 | 41607.375 | 41607.6639 | 83 | 413 | 34279 | 83 | 0.10557 | 0.00025563 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | B | 83 | 0.10557 | 0.00025563
137946 | 41607.6014 | 41607.6264 | 2000 | 33 | 66000 | 2000 | 0.20327 | 0.0061597 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 2000 | 0.20327 | 0.0061597
137950 | 41608.341 | 41608.384 | 21 | 59 | 1239 | 21 | 0.0038159 | 6.4677e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 21 | 0.0038159 | 6.4677e-05
137951 | 41608.3424 | 41608.4854 | 158 | 203 | 12869.8058 | 63.3981 | 0.039637 | 0.00048662 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 63.3981 | 0.039637 | 0.00048662
137952 | 41608.466 | 41608.5361 | 499 | 98 | 18859.6634 | 192.4455 | 0.058085 | 0.0015368 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 192.4455 | 0.058085 | 0.0015368
137953 | 41608.4646 | 41608.534 | 126 | 97 | 12222 | 126 | 0.037642 | 0.00038806 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 126 | 0.037642 | 0.00038806
137954 | 41608.6208 | 41608.6333 | 6 | 15 | 90 | 6 | 0.00027719 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 6 | 0.00027719 | 1.8479e-05
137955 | 41608.5208 | 41608.6188 | 6 | 138 | 828 | 6 | 0.0025501 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 6 | 0.0025501 | 1.8479e-05
137958 | 41608.0639 | 41608.1861 | 1902 | 173 | 179851.1932 | 1039.6023 | 0.55391 | 0.0058579 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 1039.6023 | 0.55391 | 0.0058579
137959 | 41607.6618 | 41607.7951 | 77 | 189 | 14553 | 77 | 0.044821 | 0.00023715 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 77 | 0.044821 | 0.00023715
137960 | 41608.591 | 41608.6597 | 60 | 96 | 5207.2727 | 54.2424 | 0.016038 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 54.2424 | 0.016038 | 0.00018479
137961 | 41608.7479 | 41608.8153 | 13 | 94 | 1222 | 13 | 0.0037636 | 4.0038e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 13 | 0.0037636 | 4.0038e-05
137962 | 41608.5868 | 41608.9042 | 161 | 454 | 31230.6302 | 68.7899 | 0.096185 | 0.00049585 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | C | 68.7899 | 0.096185 | 0.00049585
137963 | 41609.0236 | 41609.066 | 38 | 58 | 2204 | 38 | 0.006788 | 0.00011703 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | C | 38 | 0.006788 | 0.00011703
137964 | 41609.3333 | 41609.4167 | 19 | 117 | 2223 | 19 | 0.0068465 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | B | 19 | 0.0068465 | 5.8517e-05
137965 | 41609.3333 | 41609.3812 | 19 | 66 | 1254 | 19 | 0.0038621 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | B | 19 | 0.0038621 | 5.8517e-05
137967 | 41609.4542 | 41609.6062 | 279 | 216 | 60264 | 279 | 0.1856 | 0.00085928 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | C | 279 | 0.1856 | 0.00085928
137971 | 41609.6764 | 41609.7125 | 50 | 49 | 2450 | 50 | 0.0075456 | 0.00015399 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | C | 50 | 0.0075456 | 0.00015399
137973 | 41610.0931 | 41610.2556 | 803 | 231 | 88604.2949 | 383.5684 | 0.27289 | 0.0024731 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 383.5684 | 0.27289 | 0.0024731
137974 | 41610.4479 | 41610.4653 | 43 | 22 | 946 | 43 | 0.0029135 | 0.00013243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 43 | 0.0029135 | 0.00013243
137975 | 41609.9167 | 41609.9194 | 1734 | 1 | 1734 | 1734 | 0.0053404 | 0.0053404 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | C | 1734 | 0.0053404 | 0.0053404
137976 | 41607.3861 | 41607.441 | 646 | 76 | 49096 | 646 | 0.15121 | 0.0019896 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-11-29 | 2014 | 2014 | 2013-11-29 | C | 646 | 0.15121 | 0.0019896
137977 | 41609.8333 | 41610.4931 | 6 | 947 | 5682 | 6 | 0.0175 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-01 | 2014 | 2014 | 2013-12-01 | C | 6 | 0.0175 | 1.8479e-05
137979 | 41610.3806 | 41610.6111 | 8 | 329 | 2632 | 8 | 0.0081061 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 8 | 0.0081061 | 2.4639e-05
137980 | 41610.3549 | 41610.5694 | 2 | 306 | 612 | 2 | 0.0018849 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 2 | 0.0018849 | 6.1597e-06
137982 | 41610.6625 | 41610.8201 | 1 | 224 | 224 | 1 | 0.00068988 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 1 | 0.00068988 | 3.0798e-06
137984 | 41610.616 | 41610.6306 | 2 | 18 | 36 | 2 | 0.00011087 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 2 | 0.00011087 | 6.1597e-06
137985 | 41610.4715 | 41610.559 | 39 | 123 | 4797 | 39 | 0.014774 | 0.00012011 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 39 | 0.014774 | 0.00012011
137987 | 41610.4062 | 41610.6465 | 4 | 343 | 1372 | 4 | 0.0042255 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 4 | 0.0042255 | 1.2319e-05
137988 | 41610.5417 | 41610.6146 | 3 | 102 | 306 | 3 | 0.00094243 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 3 | 0.00094243 | 9.2395e-06
137989 | 41610.4653 | 41610.5312 | 3 | 92 | 276 | 3 | 0.00085004 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 3 | 0.00085004 | 9.2395e-06
137990 | 41610.3785 | 41610.4514 | 9 | 102 | 918 | 9 | 0.0028273 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | B | 9 | 0.0028273 | 2.7719e-05
137991 | 41610.6028 | 41610.7174 | 741 | 162 | 40746.4364 | 251.5212 | 0.12549 | 0.0022822 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-02 | 2014 | 2014 | 2013-12-02 | C | 251.5212 | 0.12549 | 0.0022822
137994 | 41611.4062 | 41611.425 | 5 | 24 | 120 | 5 | 0.00036958 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 5 | 0.00036958 | 1.5399e-05
137995 | 41611.3021 | 41611.3507 | 1 | 67 | 67 | 1 | 0.00020635 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | C | 1 | 0.00020635 | 3.0798e-06
137996 | 41611.3035 | 41611.4472 | 16 | 204 | 3264 | 16 | 0.010053 | 4.9277e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | C | 16 | 0.010053 | 4.9277e-05
137997 | 41611.4736 | 41611.5153 | 11 | 57 | 627 | 11 | 0.0019311 | 3.3878e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | C | 11 | 0.0019311 | 3.3878e-05
137999 | 41611.4757 | 41611.5514 | 3 | 106 | 318 | 3 | 0.00097939 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 3 | 0.00097939 | 9.2395e-06
138001 | 41611.3757 | 41611.5896 | 1 | 305 | 305 | 1 | 0.00093935 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 1 | 0.00093935 | 3.0798e-06
138003 | 41611.3958 | 41611.4306 | 2 | 47 | 94 | 2 | 0.00028951 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 2 | 0.00028951 | 6.1597e-06
138004 | 41611.4014 | 41611.5847 | 11 | 261 | 2871 | 11 | 0.0088422 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 11 | 0.0088422 | 3.3878e-05
138012 | 41611.3854 | 41611.4236 | 3 | 52 | 156 | 3 | 0.00048046 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 3 | 0.00048046 | 9.2395e-06
138015 | 41611.4583 | 41611.4833 | 3 | 33 | 99 | 3 | 0.0003049 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 3 | 0.0003049 | 9.2395e-06
138016 | 41611.5417 | 41611.5972 | 9 | 77 | 693 | 9 | 0.0021343 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 9 | 0.0021343 | 2.7719e-05
138017 | 41611.5785 | 41611.6194 | 4 | 56 | 224 | 4 | 0.00068988 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 4 | 0.00068988 | 1.2319e-05
138019 | 41611.3125 | 41611.4 | 2 | 123 | 246 | 2 | 0.00075764 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 2 | 0.00075764 | 6.1597e-06
138020 | 41611.3542 | 41611.6667 | 26 | 447 | 11622 | 26 | 0.035794 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 26 | 0.035794 | 8.0076e-05
138021 | 41611.3333 | 41611.5938 | 64 | 372 | 23808 | 64 | 0.073325 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 64 | 0.073325 | 0.00019711
138022 | 41611.375 | 41611.6875 | 5 | 447 | 2235 | 5 | 0.0068834 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 5 | 0.0068834 | 1.5399e-05
138023 | 41611.6562 | 41611.7604 | 1 | 147 | 147 | 1 | 0.00045274 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | C | 1 | 0.00045274 | 3.0798e-06
138027 | 41611.5417 | 41611.5833 | 5 | 57 | 285 | 5 | 0.00087775 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 5 | 0.00087775 | 1.5399e-05
138028 | 41611.4583 | 41611.5278 | 5 | 97 | 485 | 5 | 0.0014937 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 5 | 0.0014937 | 1.5399e-05
138029 | 41611.3854 | 41611.4479 | 4 | 87 | 348 | 4 | 0.0010718 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-03 | 2014 | 2014 | 2013-12-03 | B | 4 | 0.0010718 | 1.2319e-05
138032 | 41612.4271 | 41612.4688 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 4 | 0.0007022 | 1.2319e-05
138033 | 41612.4167 | 41612.5424 | 39 | 178 | 6942 | 39 | 0.02138 | 0.00012011 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 39 | 0.02138 | 0.00012011
138034 | 41612.4757 | 41612.5417 | 1 | 92 | 92 | 1 | 0.00028335 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 1 | 0.00028335 | 3.0798e-06
138035 | 41612.4375 | 41612.4688 | 6 | 42 | 252 | 6 | 0.00077612 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 6 | 0.00077612 | 1.8479e-05
138036 | 41612.5625 | 41612.5903 | 4 | 37 | 148 | 4 | 0.00045582 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 4 | 0.00045582 | 1.2319e-05
138037 | 41612.4062 | 41612.4799 | 39 | 103 | 4017 | 39 | 0.012372 | 0.00012011 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 39 | 0.012372 | 0.00012011
138043 | 41612.3646 | 41612.4132 | 8 | 67 | 536 | 8 | 0.0016508 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 8 | 0.0016508 | 2.4639e-05
138044 | 41612.4479 | 41612.4965 | 5 | 67 | 335 | 5 | 0.0010317 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 5 | 0.0010317 | 1.5399e-05
138045 | 41612.5312 | 41612.5799 | 7 | 67 | 469 | 7 | 0.0014444 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 7 | 0.0014444 | 2.1559e-05
138047 | 41612.375 | 41612.4132 | 4 | 52 | 208 | 4 | 0.00064061 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 4 | 0.00064061 | 1.2319e-05
138049 | 41612.4583 | 41612.4896 | 2 | 42 | 84 | 2 | 0.00025871 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 2 | 0.00025871 | 6.1597e-06
138051 | 41612.5417 | 41612.6042 | 6 | 87 | 522 | 6 | 0.0016077 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 6 | 0.0016077 | 1.8479e-05
138052 | 41612.6667 | 41612.6958 | 376 | 39 | 14664 | 376 | 0.045163 | 0.001158 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 376 | 0.045163 | 0.001158
138053 | 41612.7146 | 41612.7243 | 209 | 11 | 2299 | 209 | 0.0070806 | 0.00064369 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 209 | 0.0070806 | 0.00064369
138054 | 41612.375 | 41612.625 | 26 | 357 | 9282 | 26 | 0.028587 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | B | 26 | 0.028587 | 8.0076e-05
138055 | 41612.6382 | 41612.6965 | 241 | 81 | 16249.1786 | 200.6071 | 0.050045 | 0.00074224 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 200.6071 | 0.050045 | 0.00074224
138056 | 41612.8118 | 41612.8285 | 1153 | 21 | 24213 | 1153 | 0.074572 | 0.0035511 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 1153 | 0.074572 | 0.0035511
138057 | 41612.8118 | 41612.9597 | 1209 | 210 | 199183.5211 | 948.493 | 0.61345 | 0.0037235 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-04 | 2014 | 2014 | 2013-12-04 | C | 948.493 | 0.61345 | 0.0037235
138061 | 41613.375 | 41613.4583 | 7 | 117 | 819 | 7 | 0.0025224 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 7 | 0.0025224 | 2.1559e-05
138062 | 41613.3917 | 41613.4549 | 7 | 88 | 616 | 7 | 0.0018972 | 2.1559e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 7 | 0.0018972 | 2.1559e-05
138063 | 41613.5451 | 41613.5514 | 2 | 6 | 12 | 2 | 3.6958e-05 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 2 | 3.6958e-05 | 6.1597e-06
138064 | 41613.3646 | 41613.441 | 6 | 107 | 642 | 6 | 0.0019773 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 6 | 0.0019773 | 1.8479e-05
138065 | 41613.6493 | 41613.6979 | 2 | 67 | 134 | 2 | 0.0004127 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 2 | 0.0004127 | 6.1597e-06
138069 | 41613.3979 | 41613.5354 | 64 | 195 | 12480 | 64 | 0.038436 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 64 | 0.038436 | 0.00019711
138072 | 41613.375 | 41613.5847 | 32 | 299 | 9568 | 32 | 0.029468 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 32 | 0.029468 | 9.8555e-05
138074 | 41613.1104 | 41613.3389 | 1102 | 326 | 200968.5957 | 616.4681 | 0.61895 | 0.003394 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 616.4681 | 0.61895 | 0.003394
138075 | 41613.1104 | 41613.1139 | 1616 | 2 | 3232 | 1616 | 0.009954 | 0.004977 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 1616 | 0.009954 | 0.004977
138076 | 41613.1104 | 41613.1139 | 872 | 2 | 1744 | 872 | 0.0053712 | 0.0026856 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | C | 872 | 0.0053712 | 0.0026856
138077 | 41613.959 | 41614.1333 | 63 | 248 | 15624 | 63 | 0.048119 | 0.00019403 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 63 | 0.048119 | 0.00019403
138079 | 41614.241 | 41614.3056 | 4 | 90 | 360 | 4 | 0.0011087 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | C | 4 | 0.0011087 | 1.2319e-05
138081 | 41614.4028 | 41614.4868 | 24 | 118 | 2832 | 24 | 0.0087221 | 7.3916e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | C | 24 | 0.0087221 | 7.3916e-05
138082 | 41613.3826 | 41613.5361 | 1 | 218 | 218 | 1 | 0.00067141 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-05 | 2014 | 2014 | 2013-12-05 | B | 1 | 0.00067141 | 3.0798e-06
138083 | 41614.3646 | 41614.6118 | 29 | 353 | 10237 | 29 | 0.031528 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | B | 29 | 0.031528 | 8.9315e-05
138084 | 41614.5 | 41614.6667 | 1 | 237 | 237 | 1 | 0.00072992 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | C | 1 | 0.00072992 | 3.0798e-06
138087 | 41614.8493 | 41615.1215 | 102 | 389 | 20850.2015 | 53.5995 | 0.064215 | 0.00031414 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | C | 53.5995 | 0.064215 | 0.00031414
138088 | 41615.3785 | 41615.5174 | 4 | 197 | 788 | 4 | 0.0024269 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 4 | 0.0024269 | 1.2319e-05
138089 | 41615.3646 | 41615.4938 | 4 | 183 | 732 | 4 | 0.0022544 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 4 | 0.0022544 | 1.2319e-05
138090 | 41615.5139 | 41615.5903 | 2 | 107 | 214 | 2 | 0.00065909 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 2 | 0.00065909 | 6.1597e-06
138092 | 41615.884 | 41615.9861 | 121 | 144 | 10997.8776 | 76.3741 | 0.033872 | 0.00037266 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | C | 76.3741 | 0.033872 | 0.00037266
138093 | 41615.7431 | 41616.2417 | 13 | 715 | 9295 | 13 | 0.028627 | 4.0038e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | C | 13 | 0.028627 | 4.0038e-05
138095 | 41616.4326 | 41616.4861 | 5 | 74 | 370 | 5 | 0.0011395 | 1.5399e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-08 | 2014 | 2014 | 2013-12-08 | C | 5 | 0.0011395 | 1.5399e-05
138098 | 41617.309 | 41617.3785 | 2 | 97 | 194 | 2 | 0.00059749 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | C | 2 | 0.00059749 | 6.1597e-06
138100 | 41614.375 | 41614.4375 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | B | 3 | 0.00080384 | 9.2395e-06
138101 | 41617.3646 | 41617.3854 | 1 | 27 | 27 | 1 | 8.3156e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | C | 1 | 8.3156e-05 | 3.0798e-06
138102 | 41617.3653 | 41617.484 | 44 | 168 | 7392 | 44 | 0.022766 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | B | 44 | 0.022766 | 0.00013551
138104 | 41617.4097 | 41617.5743 | 11 | 234 | 2574 | 11 | 0.0079275 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | B | 11 | 0.0079275 | 3.3878e-05
138106 | 41617.5924 | 41617.6361 | 1 | 60 | 60 | 1 | 0.00018479 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | C | 1 | 0.00018479 | 3.0798e-06
138108 | 41617.4167 | 41617.6125 | 99 | 279 | 27621 | 99 | 0.085068 | 0.0003049 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-09 | 2014 | 2014 | 2013-12-09 | B | 99 | 0.085068 | 0.0003049
138112 | 41614.5451 | 41614.5868 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | B | 4 | 0.0007022 | 1.2319e-05
138114 | 41614.4625 | 41614.5035 | 6 | 56 | 336 | 6 | 0.0010348 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-06 | 2014 | 2014 | 2013-12-06 | B | 6 | 0.0010348 | 1.8479e-05
138116 | 41618.3917 | 41618.4062 | 387 | 18 | 6966 | 387 | 0.021454 | 0.0011919 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 387 | 0.021454 | 0.0011919
138117 | 41618.4514 | 41618.4896 | 10 | 52 | 520 | 10 | 0.0016015 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 10 | 0.0016015 | 3.0798e-05
138118 | 41618.4208 | 41618.5576 | 30 | 194 | 5820 | 30 | 0.017925 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 30 | 0.017925 | 9.2395e-05
138119 | 41618.5556 | 41618.5958 | 40 | 55 | 2200 | 40 | 0.0067757 | 0.00012319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 40 | 0.0067757 | 0.00012319
138120 | 41618.366 | 41618.5646 | 51 | 283 | 14433 | 51 | 0.044451 | 0.00015707 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 51 | 0.044451 | 0.00015707
138122 | 41618.375 | 41618.5694 | 2 | 277 | 554 | 2 | 0.0017062 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 2 | 0.0017062 | 6.1597e-06
138123 | 41618.5035 | 41618.5993 | 6 | 135 | 810 | 6 | 0.0024947 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 6 | 0.0024947 | 1.8479e-05
138125 | 41618.6208 | 41618.6632 | 153 | 58 | 5927.4098 | 102.1967 | 0.018255 | 0.00047122 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 102.1967 | 0.018255 | 0.00047122
138126 | 41618.4174 | 41618.6701 | 9 | 361 | 3249 | 9 | 0.010006 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 9 | 0.010006 | 2.7719e-05
138127 | 41618.6181 | 41618.684 | 317 | 92 | 29164 | 317 | 0.089821 | 0.00097631 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 317 | 0.089821 | 0.00097631
138128 | 41618.6424 | 41618.6882 | 22 | 63 | 1386 | 22 | 0.0042687 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 22 | 0.0042687 | 6.7757e-05
138129 | 41618.3889 | 41618.6375 | 45 | 355 | 15975 | 45 | 0.0492 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 45 | 0.0492 | 0.00013859
138131 | 41618.4167 | 41618.6146 | 13 | 282 | 638.2105 | 2.2632 | 0.0019656 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 2.2632 | 0.0019656 | 4.0038e-05
138132 | 41618.8424 | 41618.8708 | 125 | 38 | 4750 | 125 | 0.014629 | 0.00038498 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 125 | 0.014629 | 0.00038498
138134 | 41619.066 | 41619.1062 | 418 | 55 | 22990 | 418 | 0.070806 | 0.0012874 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | C | 418 | 0.070806 | 0.0012874
138135 | 41619.066 | 41619.9743 | 129 | 1305 | 38077.4656 | 29.1781 | 0.11727 | 0.0003973 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | C | 29.1781 | 0.11727 | 0.0003973
138136 | 41535.7083 | 41535.7222 | 3 | 17 | 51 | 3 | 0.00015707 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-09-18 | 2014 | 2014 | 2013-09-18 | C | 3 | 0.00015707 | 9.2395e-06
138137 | 41595.375 | 41595.6667 | 45 | 417 | 18765 | 45 | 0.057793 | 0.00013859 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-17 | 2014 | 2014 | 2013-11-17 | B | 45 | 0.057793 | 0.00013859
138138 | 41596.4167 | 41596.5 | 3 | 117 | 351 | 3 | 0.001081 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 3 | 0.001081 | 9.2395e-06
138139 | 41596.3701 | 41596.4139 | 154 | 60 | 9240 | 154 | 0.028458 | 0.0004743 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-18 | 2014 | 2014 | 2013-11-18 | B | 154 | 0.028458 | 0.0004743
138140 | 41599.4278 | 41599.4694 | 154 | 57 | 8778 | 154 | 0.027035 | 0.0004743 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-21 | 2014 | 2014 | 2013-11-21 | B | 154 | 0.027035 | 0.0004743
138141 | 41597.3722 | 41597.5757 | 44 | 290 | 12760 | 44 | 0.039299 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-19 | 2014 | 2014 | 2013-11-19 | B | 44 | 0.039299 | 0.00013551
138142 | 41603.4069 | 41603.4611 | 188 | 75 | 14100 | 188 | 0.043426 | 0.00057901 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-25 | 2014 | 2014 | 2013-11-25 | B | 188 | 0.043426 | 0.00057901
138143 | 41606.4361 | 41606.4917 | 188 | 77 | 14476 | 188 | 0.044584 | 0.00057901 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-28 | 2014 | 2014 | 2013-11-28 | B | 188 | 0.044584 | 0.00057901
138144 | 41619.4097 | 41619.5556 | 8 | 207 | 1656 | 8 | 0.0051002 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | C | 8 | 0.0051002 | 2.4639e-05
138146 | 41619.375 | 41619.6111 | 99 | 337 | 33363 | 99 | 0.10275 | 0.0003049 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | B | 99 | 0.10275 | 0.0003049
138147 | 41618.3542 | 41618.6215 | 18 | 382 | 6876 | 18 | 0.021177 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | B | 18 | 0.021177 | 5.5437e-05
138148 | 41619.3854 | 41619.6292 | 19 | 348 | 6612 | 19 | 0.020364 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | B | 19 | 0.020364 | 5.8517e-05
138149 | 41619.3646 | 41619.6576 | 147 | 419 | 9924.9384 | 23.6872 | 0.030567 | 0.00045274 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | B | 23.6872 | 0.030567 | 0.00045274
138150 | 41619.3646 | 41619.5799 | 31 | 307 | 9517 | 31 | 0.029311 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-11 | 2014 | 2014 | 2013-12-11 | B | 31 | 0.029311 | 9.5475e-05
138152 | 41618.3958 | 41618.4583 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-10 | 2014 | 2014 | 2013-12-10 | C | 2 | 0.00053589 | 6.1597e-06
138154 | 41620.3778 | 41620.4056 | 7 | 37 | 259 | 7 | 0.00079768 | 2.1559e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | C | 7 | 0.00079768 | 2.1559e-05
138156 | 41620.4167 | 41620.5833 | 4 | 237 | 948 | 4 | 0.0029197 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 4 | 0.0029197 | 1.2319e-05
138157 | 41620.4375 | 41620.5618 | 184 | 176 | 32143.1061 | 182.6313 | 0.098996 | 0.00056669 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 182.6313 | 0.098996 | 0.00056669
138159 | 41620.3542 | 41620.6111 | 18 | 367 | 6606 | 18 | 0.020345 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 18 | 0.020345 | 5.5437e-05
138162 | 41620.3958 | 41620.4375 | 66 | 57 | 3762 | 66 | 0.011586 | 0.00020327 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 66 | 0.011586 | 0.00020327
138164 | 41620.5521 | 41620.6042 | 11 | 72 | 792 | 11 | 0.0024392 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 11 | 0.0024392 | 3.3878e-05
138166 | 41620.3847 | 41620.6125 | 7 | 325 | 2275 | 7 | 0.0070066 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 7 | 0.0070066 | 2.1559e-05
138168 | 41621.1486 | 41621.4514 | 415 | 433 | 41444.8532 | 95.7156 | 0.12764 | 0.0012781 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | C | 95.7156 | 0.12764 | 0.0012781
138169 | 41621.4444 | 41621.4889 | 2 | 61 | 122 | 2 | 0.00037574 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | C | 2 | 0.00037574 | 6.1597e-06
138172 | 41621.3646 | 41621.6146 | 51 | 357 | 18207 | 51 | 0.056075 | 0.00015707 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | B | 51 | 0.056075 | 0.00015707
138175 | 41621.5556 | 41621.6069 | 4 | 71 | 284 | 4 | 0.00087468 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | C | 4 | 0.00087468 | 1.2319e-05
138177 | 41557.25 | 41557.6931 | 206 | 635 | 33376.3166 | 52.5611 | 0.10279 | 0.00063445 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-10-10 | 2014 | 2014 | 2013-10-10 | B | 52.5611 | 0.10279 | 0.00063445
138178 | 41621.375 | 41621.7326 | 9 | 512 | 4608 | 9 | 0.014192 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | B | 9 | 0.014192 | 2.7719e-05
138180 | 41620.3438 | 41620.6174 | 6 | 391 | 2346 | 6 | 0.0072253 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | B | 6 | 0.0072253 | 1.8479e-05
138181 | 41621.4576 | 41621.5625 | 46 | 148 | 6808 | 46 | 0.020968 | 0.00014167 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-13 | 2014 | 2014 | 2013-12-13 | B | 46 | 0.020968 | 0.00014167
138183 | 41622.6778 | 41622.8681 | 116 | 271 | 20530.7226 | 75.7591 | 0.063231 | 0.00035726 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-14 | 2014 | 2014 | 2013-12-14 | C | 75.7591 | 0.063231 | 0.00035726
138184 | 41622.8889 | 41622.9167 | 100 | 37 | 3700 | 100 | 0.011395 | 0.00030798 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-14 | 2014 | 2014 | 2013-12-14 | C | 100 | 0.011395 | 0.00030798
138185 | 41623.2972 | 41623.3111 | 405 | 17 | 4526.25 | 266.25 | 0.01394 | 0.0012473 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-15 | 2014 | 2014 | 2013-12-15 | C | 266.25 | 0.01394 | 0.0012473
138186 | 41623.3903 | 41623.475 | 1 | 119 | 119 | 1 | 0.0003665 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-15 | 2014 | 2014 | 2013-12-15 | B | 1 | 0.0003665 | 3.0798e-06
138187 | 41623.4208 | 41623.5694 | 1 | 211 | 211 | 1 | 0.00064985 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-15 | 2014 | 2014 | 2013-12-15 | C | 1 | 0.00064985 | 3.0798e-06
138188 | 41615.3562 | 41615.5278 | 64 | 244 | 15616 | 64 | 0.048095 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 64 | 0.048095 | 0.00019711
138191 | 41622.0208 | 41622.4167 | 266 | 567 | 129520.7053 | 228.4316 | 0.3989 | 0.00081924 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-14 | 2014 | 2014 | 2013-12-14 | C | 228.4316 | 0.3989 | 0.00081924
138193 | 41623.7917 | 41624.0354 | 2 | 348 | 696 | 2 | 0.0021436 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-15 | 2014 | 2014 | 2013-12-15 | C | 2 | 0.0021436 | 6.1597e-06
138195 | 41620.7264 | 41620.741 | 1811 | 18 | 32598 | 1811 | 0.1004 | 0.0055776 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | C | 1811 | 0.1004 | 0.0055776
138196 | 41620.7264 | 41620.7403 | 908 | 17 | 15436 | 908 | 0.04754 | 0.0027965 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | C | 908 | 0.04754 | 0.0027965
138197 | 41620.7264 | 41620.741 | 585 | 18 | 10530 | 585 | 0.032431 | 0.0018017 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-12 | 2014 | 2014 | 2013-12-12 | C | 585 | 0.032431 | 0.0018017
138198 | 41624.3757 | 41624.4958 | 36 | 170 | 6120 | 36 | 0.018849 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | B | 36 | 0.018849 | 0.00011087
138199 | 41624.4028 | 41624.5188 | 97 | 164 | 15908 | 97 | 0.048994 | 0.00029874 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | B | 97 | 0.048994 | 0.00029874
138202 | 41624.3958 | 41624.6542 | 68 | 369 | 25092 | 68 | 0.077279 | 0.00020943 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | B | 68 | 0.077279 | 0.00020943
138204 | 41624.4319 | 41624.5639 | 56 | 187 | 10472 | 56 | 0.032252 | 0.00017247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | B | 56 | 0.032252 | 0.00017247
138206 | 41624.634 | 41624.6486 | 123 | 18 | 2214 | 123 | 0.0068188 | 0.00037882 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | C | 123 | 0.0068188 | 0.00037882
138208 | 41624.8354 | 41625.1792 | 6146 | 492 | 198984.6788 | 404.4404 | 0.61284 | 0.018929 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | C | 404.4404 | 0.61284 | 0.018929
138210 | 41624.7014 | 41624.8375 | 4 | 193 | 772 | 4 | 0.0023776 | 1.2319e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | C | 4 | 0.0023776 | 1.2319e-05
138211 | 41625.0833 | 41625.2472 | 3 | 233 | 699 | 3 | 0.0021528 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 3 | 0.0021528 | 9.2395e-06
138212 | 41624.8854 | 41625.0521 | 192 | 237 | 27057.5 | 114.1667 | 0.083333 | 0.00059133 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | C | 114.1667 | 0.083333 | 0.00059133
138217 | 41625.4167 | 41625.5542 | 72 | 195 | 14040 | 72 | 0.043241 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 72 | 0.043241 | 0.00022175
138219 | 41625.3958 | 41625.4271 | 7 | 42 | 294 | 7 | 0.00090547 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 7 | 0.00090547 | 2.1559e-05
138222 | 41625.4271 | 41625.4583 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 5 | 0.00064677 | 1.5399e-05
138224 | 41625.375 | 41625.6493 | 25 | 392 | 9800 | 25 | 0.030182 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 25 | 0.030182 | 7.6996e-05
138226 | 41625.3854 | 41625.6701 | 5 | 407 | 2035 | 5 | 0.0062675 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 5 | 0.0062675 | 1.5399e-05
138228 | 41626.4021 | 41626.4951 | 9 | 131 | 1179 | 9 | 0.0036311 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 9 | 0.0036311 | 2.7719e-05
138231 | 41626.3958 | 41626.4792 | 1 | 117 | 117 | 1 | 0.00036034 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 1 | 0.00036034 | 3.0798e-06
138232 | 41626.4167 | 41626.541 | 35 | 176 | 6160 | 35 | 0.018972 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 35 | 0.018972 | 0.00010779
138234 | 41625.3799 | 41625.584 | 13 | 291 | 3783 | 13 | 0.011651 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 13 | 0.011651 | 4.0038e-05
138235 | 41626.3542 | 41626.625 | 1 | 387 | 387 | 1 | 0.0011919 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 1 | 0.0011919 | 3.0798e-06
138236 | 41626.3646 | 41626.5174 | 31 | 217 | 6727 | 31 | 0.020718 | 9.5475e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 31 | 0.020718 | 9.5475e-05
138237 | 41626.3854 | 41626.625 | 4 | 342 | 1368 | 4 | 0.0042132 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 4 | 0.0042132 | 1.2319e-05
138239 | 41626.3889 | 41626.5646 | 8 | 250 | 2000 | 8 | 0.0061597 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 8 | 0.0061597 | 2.4639e-05
138240 | 41626.3854 | 41626.6556 | 4 | 386 | 1544 | 4 | 0.0047553 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 4 | 0.0047553 | 1.2319e-05
138241 | 41626.6326 | 41626.6681 | 91 | 48 | 4368 | 91 | 0.013453 | 0.00028027 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | C | 91 | 0.013453 | 0.00028027
138242 | 41626.6264 | 41626.6729 | 2936 | 64 | 178842.7463 | 2794.4179 | 0.55081 | 0.0090424 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | C | 2794.4179 | 0.55081 | 0.0090424
138243 | 41626.3854 | 41626.6556 | 4 | 386 | 1544 | 4 | 0.0047553 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 4 | 0.0047553 | 1.2319e-05
138244 | 41626.4792 | 41626.5444 | 28 | 91 | 2548 | 28 | 0.0078474 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | C | 28 | 0.0078474 | 8.6236e-05
138246 | 41626.4792 | 41626.5444 | 28 | 91 | 2548 | 28 | 0.0078474 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | C | 28 | 0.0078474 | 8.6236e-05
138248 | 41627.375 | 41627.5368 | 15 | 230 | 3450 | 15 | 0.010625 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-19 | 2014 | 2014 | 2013-12-19 | B | 15 | 0.010625 | 4.6198e-05
138249 | 41627.375 | 41627.5069 | 101 | 187 | 18887 | 101 | 0.058169 | 0.00031106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-19 | 2014 | 2014 | 2013-12-19 | B | 101 | 0.058169 | 0.00031106
138252 | 41627.4062 | 41627.5563 | 144 | 213 | 10251.6111 | 48.1296 | 0.031573 | 0.0004435 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-19 | 2014 | 2014 | 2013-12-19 | C | 48.1296 | 0.031573 | 0.0004435
138254 | 41626.3556 | 41626.6951 | 14 | 486 | 6804 | 14 | 0.020955 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-18 | 2014 | 2014 | 2013-12-18 | B | 14 | 0.020955 | 4.3118e-05
138256 | 41627.375 | 41627.6125 | 26 | 339 | 8814 | 26 | 0.027146 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-19 | 2014 | 2014 | 2013-12-19 | B | 26 | 0.027146 | 8.0076e-05
138260 | 41627.7576 | 41627.7632 | 231 | 5 | 881.25 | 176.25 | 0.0027141 | 0.00071144 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-19 | 2014 | 2014 | 2013-12-19 | C | 176.25 | 0.0027141 | 0.00071144
138261 | 41628.2708 | 41628.4896 | 855 | 312 | 82894.9333 | 265.6889 | 0.2553 | 0.0026333 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-20 | 2014 | 2014 | 2013-12-20 | C | 265.6889 | 0.2553 | 0.0026333
138262 | 41628.3125 | 41628.3326 | 1194 | 26 | 14986.7586 | 576.4138 | 0.046157 | 0.0036773 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-20 | 2014 | 2014 | 2013-12-20 | C | 576.4138 | 0.046157 | 0.0036773
138265 | 41628.4056 | 41628.4354 | 6 | 40 | 240 | 6 | 0.00073916 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-20 | 2014 | 2014 | 2013-12-20 | C | 6 | 0.00073916 | 1.8479e-05
138266 | 41628.5486 | 41628.575 | 60 | 35 | 2100 | 60 | 0.0064677 | 0.00018479 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-20 | 2014 | 2014 | 2013-12-20 | C | 60 | 0.0064677 | 0.00018479
138267 | 41628.5118 | 41628.5319 | 8 | 26 | 208 | 8 | 0.00064061 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-20 | 2014 | 2014 | 2013-12-20 | C | 8 | 0.00064061 | 2.4639e-05
138268 | 41629.1236 | 41629.2618 | 3606 | 196 | 165847.5176 | 846.1608 | 0.51078 | 0.011106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 846.1608 | 0.51078 | 0.011106
138274 | 41629.5146 | 41629.7382 | 247 | 319 | 30411.0031 | 95.3323 | 0.093661 | 0.00076072 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 95.3323 | 0.093661 | 0.00076072
138275 | 41629.6806 | 41629.7153 | 27 | 47 | 1269 | 27 | 0.0039083 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 27 | 0.0039083 | 8.3156e-05
138276 | 41629.6139 | 41629.8917 | 132 | 397 | 26495.78 | 66.74 | 0.081603 | 0.00040654 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 66.74 | 0.081603 | 0.00040654
138277 | 41629.909 | 41629.9444 | 2 | 48 | 96 | 2 | 0.00029566 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 2 | 0.00029566 | 6.1597e-06
138279 | 41629.9118 | 41629.9708 | 962 | 82 | 52121.1294 | 635.6235 | 0.16052 | 0.0029628 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 635.6235 | 0.16052 | 0.0029628
138281 | 41630.0972 | 41630.2465 | 148 | 212 | 19493.1535 | 91.9488 | 0.060036 | 0.00045582 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 91.9488 | 0.060036 | 0.00045582
138282 | 41630.4403 | 41630.4604 | 228 | 26 | 5928 | 228 | 0.018257 | 0.0007022 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 228 | 0.018257 | 0.0007022
138284 | 41630.4792 | 41630.5833 | 228 | 147 | 25449.62 | 173.1267 | 0.078381 | 0 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 173.1267 | 0.078381 | 0
138285 | 41630.4236 | 41630.4319 | 98 | 9 | 882 | 98 | 0.0027164 | 0.00030182 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 98 | 0.0027164 | 0.00030182
138286 | 41630.4479 | 41630.5354 | 16 | 123 | 1968 | 16 | 0.0060611 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 16 | 0.0060611 | 4.9277e-05
138289 | 41630.6549 | 41630.8229 | 323 | 239 | 28998.0083 | 121.3306 | 0.089309 | 0.00099479 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-22 | 2014 | 2014 | 2013-12-22 | C | 121.3306 | 0.089309 | 0.00099479
138294 | 41631.375 | 41631.4062 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-23 | 2014 | 2014 | 2013-12-23 | B | 4 | 0.00051741 | 1.2319e-05
138295 | 41631.3993 | 41631.4187 | 2 | 25 | 50 | 2 | 0.00015399 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-23 | 2014 | 2014 | 2013-12-23 | C | 2 | 0.00015399 | 6.1597e-06
138301 | 41632.9514 | 41633.0215 | 20 | 98 | 1960 | 20 | 0.0060365 | 6.1597e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-12-24 | 2014 | 2014 | 2013-12-24 | C | 20 | 0.0060365 | 6.1597e-05
138302 | 41633.0653 | 41633.0778 | 239 | 15 | 3585 | 239 | 0.011041 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-25 | 2014 | 2014 | 2013-12-25 | C | 239 | 0.011041 | 0.00073608
138303 | 41633.0951 | 41633.2229 | 680 | 181 | 88944.7772 | 491.4076 | 0.27394 | 0.0020943 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-25 | 2014 | 2014 | 2013-12-25 | C | 491.4076 | 0.27394 | 0.0020943
138304 | 41633.175 | 41633.3069 | 112 | 187 | 11367.6316 | 60.7895 | 0.035011 | 0.00034494 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-25 | 2014 | 2014 | 2013-12-25 | C | 60.7895 | 0.035011 | 0.00034494
138310 | 41634.2847 | 41634.3444 | 659 | 83 | 37909.7674 | 456.7442 | 0.11676 | 0.0020296 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 456.7442 | 0.11676 | 0.0020296
138311 | 41634.3097 | 41634.4271 | 476 | 166 | 28684.6036 | 172.7988 | 0.088344 | 0.001466 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 172.7988 | 0.088344 | 0.001466
138314 | 41634.3736 | 41634.4306 | 65 | 79 | 5135 | 65 | 0.015815 | 0.00020019 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 65 | 0.015815 | 0.00020019
138315 | 41634.7049 | 41634.7465 | 28 | 57 | 1596 | 28 | 0.0049154 | 8.6236e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 28 | 0.0049154 | 8.6236e-05
138316 | 41633.7347 | 41634.4167 | 2 | 979 | 1958 | 2 | 0.0060303 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-25 | 2014 | 2014 | 2013-12-25 | C | 2 | 0.0060303 | 6.1597e-06
138317 | 41634.7208 | 41634.8243 | 94 | 146 | 8718.8456 | 59.7181 | 0.026853 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 59.7181 | 0.026853 | 0.00028951
138320 | 41634.9479 | 41635.3639 | 69 | 596 | 15122.8781 | 25.374 | 0.046576 | 0.00021251 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-26 | 2014 | 2014 | 2013-12-26 | C | 25.374 | 0.046576 | 0.00021251
138321 | 41635.3681 | 41635.4097 | 26 | 57 | 1482 | 26 | 0.0045643 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-27 | 2014 | 2014 | 2013-12-27 | C | 26 | 0.0045643 | 8.0076e-05
138327 | 41635.9125 | 41635.9299 | 16 | 22 | 352 | 16 | 0.0010841 | 4.9277e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-27 | 2014 | 2014 | 2013-12-27 | C | 16 | 0.0010841 | 4.9277e-05
138328 | 41635.9243 | 41635.9368 | 239 | 15 | 3343.3333 | 222.8889 | 0.010297 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-27 | 2014 | 2014 | 2013-12-27 | C | 222.8889 | 0.010297 | 0.00073608
138340 | 41635.4688 | 41635.6354 | 1 | 237 | 237 | 1 | 0.00072992 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2013-12-27 | 2014 | 2014 | 2013-12-27 | C | 1 | 0.00072992 | 3.0798e-06
138345 | 41636.9583 | 41636.9708 | 239 | 15 | 3585 | 239 | 0.011041 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-28 | 2014 | 2014 | 2013-12-28 | C | 239 | 0.011041 | 0.00073608
138346 | 41636.9514 | 41637.0458 | 24 | 133 | 3192 | 24 | 0.0098309 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-28 | 2014 | 2014 | 2013-12-28 | C | 24 | 0.0098309 | 7.3916e-05
138347 | 41637.0139 | 41637.0333 | 483 | 25 | 12075 | 483 | 0.037189 | 0.0014876 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 483 | 0.037189 | 0.0014876
138349 | 41637.3799 | 41637.6181 | 4 | 340 | 1360 | 4 | 0.0041886 | 1.2319e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 4 | 0.0041886 | 1.2319e-05
138350 | 41636.6875 | 41636.759 | 47 | 100 | 4700 | 47 | 0.014475 | 0.00014475 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-28 | 2014 | 2014 | 2013-12-28 | C | 47 | 0.014475 | 0.00014475
138351 | 41637.4299 | 41637.5319 | 412 | 144 | 24402.6122 | 169.4626 | 0.075156 | 0.0012689 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 169.4626 | 0.075156 | 0.0012689
138352 | 41637.4167 | 41637.5208 | 5 | 147 | 735 | 5 | 0.0022637 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 5 | 0.0022637 | 1.5399e-05
138356 | 41637.4271 | 41637.5486 | 3 | 172 | 516 | 3 | 0.0015892 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 3 | 0.0015892 | 9.2395e-06
138359 | 41637.8486 | 41637.9187 | 395 | 98 | 16989.901 | 173.3663 | 0.052326 | 0.0012165 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 173.3663 | 0.052326 | 0.0012165
138360 | 41636.7125 | 41636.7347 | 34 | 29 | 986 | 34 | 0.0030367 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-28 | 2014 | 2014 | 2013-12-28 | C | 34 | 0.0030367 | 0.00010471
138361 | 41637.8243 | 41637.8347 | 502 | 12 | 6024 | 502 | 0.018553 | 0.0015461 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 502 | 0.018553 | 0.0015461
138364 | 41638.1062 | 41638.1917 | 425 | 120 | 7516.0976 | 62.6341 | 0.023148 | 0.0013089 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 62.6341 | 0.023148 | 0.0013089
138366 | 41636.6042 | 41636.7917 | 2 | 267 | 534 | 2 | 0.0016446 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-28 | 2014 | 2014 | 2013-12-28 | C | 2 | 0.0016446 | 6.1597e-06
138368 | 41638.4056 | 41638.4208 | 94 | 19 | 1786 | 94 | 0.0055006 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 94 | 0.0055006 | 0.00028951
138369 | 41637.3042 | 41637.5931 | 448 | 413 | 58364.0481 | 141.3173 | 0.17975 | 0.0013798 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 141.3173 | 0.17975 | 0.0013798
138370 | 41638.5694 | 41642.6549 | 2 | 5880 | 11760 | 2 | 0.036219 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 2 | 0.036219 | 6.1597e-06
138372 | 41637.7465 | 41637.75 | 56 | 2 | 112 | 56 | 0.00034494 | 0.00017247 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-29 | 2014 | 2014 | 2013-12-29 | C | 56 | 0.00034494 | 0.00017247
138376 | 41638.4097 | 41638.6208 | 74 | 301 | 22274 | 74 | 0.0686 | 0.00022791 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 74 | 0.0686 | 0.00022791
138377 | 41638.684 | 41638.8438 | 25 | 227 | 5675 | 25 | 0.017478 | 7.6996e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 25 | 0.017478 | 7.6996e-05
138379 | 41638.8333 | 41638.8674 | 3 | 46 | 138 | 3 | 0.00042502 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-30 | 2014 | 2014 | 2013-12-30 | C | 3 | 0.00042502 | 9.2395e-06
138381 | 41639.1292 | 41639.2104 | 710 | 114 | 40809.0769 | 357.9744 | 0.12569 | 0.0021867 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-31 | 2014 | 2014 | 2013-12-31 | C | 357.9744 | 0.12569 | 0.0021867
138385 | 41639.5972 | 41639.6132 | 242 | 20 | 4840 | 242 | 0.014906 | 0.00074532 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-31 | 2014 | 2014 | 2013-12-31 | C | 242 | 0.014906 | 0.00074532
138386 | 41639.6333 | 41639.6937 | 125 | 84 | 10500 | 125 | 0.032338 | 0.00038498 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-31 | 2014 | 2014 | 2013-12-31 | C | 125 | 0.032338 | 0.00038498
138387 | 41639.691 | 41639.7292 | 7 | 52 | 364 | 7 | 0.0011211 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2013-12-31 | 2014 | 2014 | 2013-12-31 | C | 7 | 0.0011211 | 2.1559e-05
138392 | 41640.8278 | 41640.8472 | 65 | 25 | 1625 | 65 | 0.0050047 | 0.00020019 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 65 | 0.0050047 | 0.00020019
138394 | 41640.7715 | 41640.9597 | 448 | 268 | 17877.8745 | 66.7085 | 0.055061 | 0.0013798 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 66.7085 | 0.055061 | 0.0013798
138395 | 41640.7715 | 41640.9861 | 681 | 306 | 90054.1165 | 294.2945 | 0.27735 | 0.0020974 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 294.2945 | 0.27735 | 0.0020974
138396 | 41640.8569 | 41640.8639 | 681 | 7 | 4767 | 681 | 0.014682 | 0.0020974 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 681 | 0.014682 | 0.0020974
138397 | 41640.7493 | 41640.8569 | 94 | 152 | 11267.6129 | 74.129 | 0.034702 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 74.129 | 0.034702 | 0.00028951
138398 | 41640.7944 | 41640.8708 | 45 | 107 | 4815 | 45 | 0.014829 | 0.00013859 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 45 | 0.014829 | 0.00013859
138401 | 41640.684 | 41640.7549 | 448 | 99 | 13042.7647 | 131.7451 | 0.04017 | 0.0013798 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 131.7451 | 0.04017 | 0.0013798
138402 | 41641.0917 | 41641.1458 | 1771 | 75 | 55636.5385 | 741.8205 | 0.17135 | 0.0054544 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-02 | 2014 | 2014 | 2014-01-02 | C | 741.8205 | 0.17135 | 0.0054544
138407 | 41640.6667 | 41641.4792 | 2 | 1167 | 2334 | 2 | 0.0071884 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 2 | 0.0071884 | 6.1597e-06
138410 | 41641.7521 | 41641.8069 | 203 | 76 | 15428 | 203 | 0.047516 | 0.00062521 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-02 | 2014 | 2014 | 2014-01-02 | C | 203 | 0.047516 | 0.00062521
138412 | 41642.2118 | 41642.2347 | 58 | 30 | 1740 | 58 | 0.0053589 | 0.00017863 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 58 | 0.0053589 | 0.00017863
138420 | 41642.534 | 41642.5569 | 684 | 30 | 20520 | 684 | 0.063198 | 0.0021066 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 684 | 0.063198 | 0.0021066
138421 | 41640.9236 | 41640.9826 | 160 | 82 | 13120 | 160 | 0.040408 | 0.00049277 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 160 | 0.040408 | 0.00049277
138425 | 41642.5104 | 41642.5833 | 11 | 102 | 1122 | 11 | 0.0034556 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 11 | 0.0034556 | 3.3878e-05
138426 | 41642.4951 | 41642.5486 | 306 | 74 | 22644 | 306 | 0.06974 | 0.00094243 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 306 | 0.06974 | 0.00094243
138429 | 41642.3521 | 41642.4944 | 238 | 202 | 17921.8341 | 88.722 | 0.055196 | 0.000733 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 88.722 | 0.055196 | 0.000733
138431 | 41642.5097 | 41642.5903 | 7 | 113 | 791 | 7 | 0.0024362 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 7 | 0.0024362 | 2.1559e-05
138432 | 41642.6132 | 41642.6174 | 113 | 3 | 339 | 113 | 0.0010441 | 0.00034802 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 113 | 0.0010441 | 0.00034802
138435 | 41642.5778 | 41642.7375 | 53 | 227 | 12031 | 53 | 0.037054 | 0.00016323 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 53 | 0.037054 | 0.00016323
138437 | 41642.7708 | 41642.8319 | 8 | 85 | 680 | 8 | 0.0020943 | 2.4639e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 8 | 0.0020943 | 2.4639e-05
138438 | 41642.7875 | 41642.7965 | 36 | 10 | 360 | 36 | 0.0011087 | 0.00011087 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 36 | 0.0011087 | 0.00011087
138440 | 41642.6069 | 41642.6771 | 357 | 98 | 20772.1188 | 211.9604 | 0.063975 | 0.0010995 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 211.9604 | 0.063975 | 0.0010995
138441 | 41642.7118 | 41642.7743 | 5 | 87 | 435 | 5 | 0.0013397 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 5 | 0.0013397 | 1.5399e-05
138442 | 41642.7201 | 41642.8931 | 681 | 246 | 56018.8434 | 227.7189 | 0.17253 | 0.0020974 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 227.7189 | 0.17253 | 0.0020974
138443 | 41642.6993 | 41642.7424 | 341 | 59 | 20119 | 341 | 0.061963 | 0.0010502 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 341 | 0.061963 | 0.0010502
138444 | 41642.6451 | 41642.7285 | 437 | 117 | 51129 | 437 | 0.15747 | 0.0013459 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 437 | 0.15747 | 0.0013459
138445 | 41642.6181 | 41642.684 | 27 | 92 | 2484 | 27 | 0.0076503 | 8.3156e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 27 | 0.0076503 | 8.3156e-05
138446 | 41642.816 | 41642.9215 | 116 | 149 | 2284.9934 | 15.3355 | 0.0070374 | 0.00035726 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 15.3355 | 0.0070374 | 0.00035726
138447 | 41642.6194 | 41642.6424 | 2 | 30 | 60 | 2 | 0.00018479 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 2 | 0.00018479 | 6.1597e-06
138448 | 41642.6424 | 41642.6875 | 4 | 62 | 248 | 4 | 0.0007638 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 4 | 0.0007638 | 1.2319e-05
138449 | 41642.625 | 41642.684 | 3 | 82 | 246 | 3 | 0.00075764 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 3 | 0.00075764 | 9.2395e-06
138452 | 41642.9542 | 41643.0146 | 1 | 84 | 84 | 1 | 0.00025871 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-03 | 2014 | 2014 | 2014-01-03 | C | 1 | 0.00025871 | 3.0798e-06
138454 | 41643.1062 | 41643.3438 | 394 | 339 | 23196.7193 | 68.4269 | 0.071442 | 0.0012135 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 68.4269 | 0.071442 | 0.0012135
138456 | 41643.4792 | 41643.4944 | 65 | 19 | 1235 | 65 | 0.0038036 | 0.00020019 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 65 | 0.0038036 | 0.00020019
138457 | 41643.3056 | 41643.4972 | 237 | 273 | 20981.4348 | 76.8551 | 0.06462 | 0.00072992 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 76.8551 | 0.06462 | 0.00072992
138458 | 41643.0576 | 41643.1174 | 600 | 83 | 37082.6628 | 446.7791 | 0.11421 | 0.0018479 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 446.7791 | 0.11421 | 0.0018479
138459 | 41643.1757 | 41643.2583 | 162 | 116 | 12696.6387 | 109.4538 | 0.039104 | 0.00049893 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 109.4538 | 0.039104 | 0.00049893
138461 | 41643.9132 | 41643.9417 | 53 | 38 | 2014 | 53 | 0.0062028 | 0.00016323 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 53 | 0.0062028 | 0.00016323
138463 | 41643.991 | 41644.1681 | 65 | 252 | 9744 | 38.6667 | 0.03001 | 0.00020019 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-04 | 2014 | 2014 | 2014-01-04 | C | 38.6667 | 0.03001 | 0.00020019
138465 | 41644.0951 | 41644.4924 | 144 | 569 | 25370.2378 | 44.5874 | 0.078136 | 0.0004435 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 44.5874 | 0.078136 | 0.0004435
138467 | 41644.3375 | 41644.4111 | 10 | 103 | 1030 | 10 | 0.0031722 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 10 | 0.0031722 | 3.0798e-05
138468 | 41644.3979 | 41644.6465 | 7 | 355 | 2485 | 7 | 0.0076534 | 2.1559e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 7 | 0.0076534 | 2.1559e-05
138469 | 41644.325 | 41644.4826 | 2 | 224 | 448 | 2 | 0.0013798 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 2 | 0.0013798 | 6.1597e-06
138470 | 41644.5701 | 41644.6125 | 227 | 58 | 9677.4426 | 166.8525 | 0.029805 | 0.00069912 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 166.8525 | 0.029805 | 0.00069912
138471 | 41644.4431 | 41644.6361 | 269 | 275 | 43230.3957 | 157.2014 | 0.13314 | 0.00082848 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 157.2014 | 0.13314 | 0.00082848
138472 | 41644.5757 | 41644.6389 | 46 | 88 | 4048 | 46 | 0.012467 | 0.00014167 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 46 | 0.012467 | 0.00014167
138473 | 41644.6264 | 41644.6958 | 334 | 97 | 19447.53 | 200.49 | 0.059895 | 0.0010287 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 200.49 | 0.059895 | 0.0010287
138474 | 41644.459 | 41644.6424 | 7 | 261 | 1827 | 7 | 0.0056269 | 2.1559e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 7 | 0.0056269 | 2.1559e-05
138479 | 41644.7083 | 41644.8319 | 6 | 175 | 1050 | 6 | 0.0032338 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 6 | 0.0032338 | 1.8479e-05
138480 | 41644.6514 | 41644.7431 | 2 | 129 | 258 | 2 | 0.0007946 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 2 | 0.0007946 | 6.1597e-06
138481 | 41644.7653 | 41644.8049 | 2 | 54 | 108 | 2 | 0.00033262 | 6.1597e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 2 | 0.00033262 | 6.1597e-06
138482 | 41644.8049 | 41644.8819 | 155 | 108 | 11686.3784 | 108.2072 | 0.035992 | 0.00047738 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 108.2072 | 0.035992 | 0.00047738
138483 | 41645.05 | 41645.0611 | 94 | 13 | 1222 | 94 | 0.0037636 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 94 | 0.0037636 | 0.00028951
138485 | 41629.491 | 41629.5472 | 53 | 78 | 3284.6667 | 42.1111 | 0.010116 | 0.00016323 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2013-12-21 | 2014 | 2014 | 2013-12-21 | C | 42.1111 | 0.010116 | 0.00016323
138488 | 41645.441 | 41645.5014 | 6 | 84 | 504 | 6 | 0.0015522 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 6 | 0.0015522 | 1.8479e-05
138490 | 41645.4688 | 41645.5521 | 1 | 117 | 117 | 1 | 0.00036034 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 1 | 0.00036034 | 3.0798e-06
138492 | 41645.3868 | 41645.6562 | 1286 | 385 | 84601.7655 | 219.7448 | 0.26056 | 0.0039607 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 219.7448 | 0.26056 | 0.0039607
138493 | 41644.759 | 41645.6014 | 5 | 1210 | 6050 | 5 | 0.018633 | 1.5399e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-05 | 2014 | 2014 | 2014-01-05 | C | 5 | 0.018633 | 1.5399e-05
138494 | 41645.4083 | 41645.4965 | 1 | 124 | 124 | 1 | 0.0003819 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 1 | 0.0003819 | 3.0798e-06
138497 | 41645.9549 | 41646.0049 | 258 | 69 | 11789.4167 | 170.8611 | 0.03631 | 0.0007946 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 170.8611 | 0.03631 | 0.0007946
138498 | 41645.7708 | 41645.7917 | 5 | 27 | 135 | 5 | 0.00041578 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 5 | 0.00041578 | 1.5399e-05
138502 | 41646.4451 | 41646.5208 | 6 | 106 | 636 | 6 | 0.0019588 | 1.8479e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 6 | 0.0019588 | 1.8479e-05
138503 | 41645.5972 | 41645.6458 | 4 | 67 | 268 | 4 | 0.0008254 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-06 | 2014 | 2014 | 2014-01-06 | C | 4 | 0.0008254 | 1.2319e-05
138508 | 41646.3854 | 41646.6597 | 14 | 392 | 5488 | 14 | 0.016902 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 14 | 0.016902 | 4.3118e-05
138510 | 41646.375 | 41646.5938 | 3 | 312 | 936 | 3 | 0.0028827 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 3 | 0.0028827 | 9.2395e-06
138511 | 41646.4375 | 41646.4896 | 2 | 72 | 144 | 2 | 0.0004435 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 2 | 0.0004435 | 6.1597e-06
138512 | 41646.5417 | 41646.5833 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 4 | 0.0007022 | 1.2319e-05
138513 | 41646.375 | 41646.4583 | 5 | 117 | 585 | 5 | 0.0018017 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 5 | 0.0018017 | 1.5399e-05
138514 | 41646.4583 | 41646.4896 | 4 | 42 | 168 | 4 | 0.00051741 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 4 | 0.00051741 | 1.2319e-05
138515 | 41646.5417 | 41646.5833 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 6 | 0.0010533 | 1.8479e-05
138516 | 41646.6354 | 41646.6632 | 1 | 37 | 37 | 1 | 0.00011395 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 1 | 0.00011395 | 3.0798e-06
138517 | 41646.3451 | 41646.4278 | 185 | 116 | 14551.6639 | 125.4454 | 0.044817 | 0.00056977 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 125.4454 | 0.044817 | 0.00056977
138518 | 41646.4757 | 41646.5243 | 26 | 67 | 1742 | 26 | 0.0053651 | 8.0076e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 26 | 0.0053651 | 8.0076e-05
138519 | 41646.7486 | 41646.7639 | 5 | 19 | 95 | 5 | 0.00029258 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 5 | 0.00029258 | 1.5399e-05
138521 | 41646.6458 | 41646.8771 | 2 | 330 | 660 | 2 | 0.0020327 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | B | 2 | 0.0020327 | 6.1597e-06
138522 | 41646.3389 | 41646.9042 | 148 | 811 | 60210.274 | 74.242 | 0.18544 | 0.00045582 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-07 | 2014 | 2014 | 2014-01-07 | C | 74.242 | 0.18544 | 0.00045582
138526 | 41647.4583 | 41647.5417 | 3 | 117 | 351 | 3 | 0.001081 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 3 | 0.001081 | 9.2395e-06
138527 | 41647.375 | 41647.4583 | 2 | 117 | 234 | 2 | 0.00072068 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 2 | 0.00072068 | 6.1597e-06
138530 | 41647.4174 | 41647.5174 | 1435 | 141 | 13488.0208 | 95.6597 | 0.041541 | 0.0044196 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | C | 95.6597 | 0.041541 | 0.0044196
138531 | 41640.8333 | 41641.0347 | 8 | 287 | 2296 | 8 | 0.0070713 | 2.4639e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 8 | 0.0070713 | 2.4639e-05
138532 | 41640.8333 | 41640.9042 | 5 | 99 | 495 | 5 | 0.0015245 | 1.5399e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-01 | 2014 | 2014 | 2014-01-01 | C | 5 | 0.0015245 | 1.5399e-05
138533 | 41647.5312 | 41647.625 | 2 | 132 | 264 | 2 | 0.00081308 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 2 | 0.00081308 | 6.1597e-06
138534 | 41647.4479 | 41647.5417 | 1 | 132 | 132 | 1 | 0.00040654 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 1 | 0.00040654 | 3.0798e-06
138535 | 41647.3646 | 41647.4583 | 3 | 132 | 396 | 3 | 0.0012196 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 3 | 0.0012196 | 9.2395e-06
138536 | 41647.5417 | 41647.625 | 5 | 117 | 585 | 5 | 0.0018017 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 5 | 0.0018017 | 1.5399e-05
138537 | 41647.3958 | 41647.625 | 72 | 327 | 23544 | 72 | 0.072512 | 0.00022175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 72 | 0.072512 | 0.00022175
138541 | 41647.8403 | 41647.8701 | 55 | 40 | 2200 | 55 | 0.0067757 | 0.00016939 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | C | 55 | 0.0067757 | 0.00016939
138542 | 41647.725 | 41648.0326 | 187 | 440 | 82280 | 187 | 0.25341 | 0.00057593 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | C | 187 | 0.25341 | 0.00057593
138544 | 41647.7285 | 41648.0271 | 7 | 427 | 2989 | 7 | 0.0092056 | 2.1559e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | C | 7 | 0.0092056 | 2.1559e-05
138546 | 41648.4187 | 41648.559 | 41 | 199 | 8159 | 41 | 0.025128 | 0.00012627 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 41 | 0.025128 | 0.00012627
138549 | 41648.3958 | 41648.5889 | 292 | 275 | 80300 | 292 | 0.24731 | 0.00089931 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 292 | 0.24731 | 0.00089931
138550 | 41648.4062 | 41648.4583 | 5 | 72 | 360 | 5 | 0.0011087 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 5 | 0.0011087 | 1.5399e-05
138551 | 41648.4715 | 41648.5069 | 3 | 48 | 144 | 3 | 0.0004435 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 3 | 0.0004435 | 9.2395e-06
138552 | 41648.5347 | 41648.5972 | 10 | 87 | 870 | 10 | 0.0026795 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 10 | 0.0026795 | 3.0798e-05
138554 | 41648.375 | 41648.4167 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 6 | 0.0010533 | 1.8479e-05
138555 | 41648.4583 | 41648.5347 | 8 | 107 | 856 | 8 | 0.0026363 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 8 | 0.0026363 | 2.4639e-05
138556 | 41648.5451 | 41648.5833 | 7 | 52 | 364 | 7 | 0.0011211 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 7 | 0.0011211 | 2.1559e-05
138557 | 41647.375 | 41647.4167 | 4 | 57 | 228 | 4 | 0.0007022 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 4 | 0.0007022 | 1.2319e-05
138558 | 41647.4583 | 41647.4861 | 6 | 37 | 222 | 6 | 0.00068372 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 6 | 0.00068372 | 1.8479e-05
138559 | 41647.5521 | 41647.5729 | 8 | 27 | 216 | 8 | 0.00066525 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-08 | 2014 | 2014 | 2014-01-08 | B | 8 | 0.00066525 | 2.4639e-05
138560 | 41648.5938 | 41648.7007 | 16 | 151 | 2416 | 16 | 0.0074409 | 4.9277e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 16 | 0.0074409 | 4.9277e-05
138561 | 41648.7063 | 41648.7632 | 673 | 79 | 53167 | 673 | 0.16375 | 0.0020727 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 673 | 0.16375 | 0.0020727
138562 | 41648.7292 | 41648.9069 | 1 | 253 | 253 | 1 | 0.0007792 | 3.0798e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 1 | 0.0007792 | 3.0798e-06
138563 | 41648.9375 | 41649.2049 | 3 | 382 | 1146 | 3 | 0.0035295 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 3 | 0.0035295 | 9.2395e-06
138564 | 41648.8549 | 41648.9528 | 267 | 138 | 18563.4468 | 134.5177 | 0.057172 | 0.00082232 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 134.5177 | 0.057172 | 0.00082232
138565 | 41648.6979 | 41649.0306 | 3 | 476 | 1428 | 3 | 0.004398 | 9.2395e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 3 | 0.004398 | 9.2395e-06
138566 | 41649.0347 | 41649.5701 | 7 | 768 | 5376 | 7 | 0.016557 | 2.1559e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | C | 7 | 0.016557 | 2.1559e-05
138567 | 41648.8854 | 41648.9035 | 3002 | 23 | 69046 | 3002 | 0.21265 | 0.0092457 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 3002 | 0.21265 | 0.0092457
138568 | 41648.8854 | 41648.9056 | 4399 | 26 | 114374 | 4399 | 0.35225 | 0.013548 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 4399 | 0.35225 | 0.013548
138569 | 41648.8854 | 41648.9056 | 5294 | 26 | 137644 | 5294 | 0.42392 | 0.016305 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 5294 | 0.42392 | 0.016305
138570 | 41648.925 | 41649.1264 | 87 | 287 | 16531.2 | 57.6 | 0.050913 | 0.00026795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | B | 57.6 | 0.050913 | 0.00026795
138571 | 41649.3507 | 41649.3625 | 134 | 14 | 1876 | 134 | 0.0057778 | 0.0004127 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | C | 134 | 0.0057778 | 0.0004127
138572 | 41649.3889 | 41649.441 | 4 | 72 | 288 | 4 | 0.00088699 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | B | 4 | 0.00088699 | 1.2319e-05
138573 | 41649.375 | 41649.4271 | 7 | 72 | 504 | 7 | 0.0015522 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | B | 7 | 0.0015522 | 2.1559e-05
138574 | 41649.4583 | 41649.5104 | 4 | 72 | 288 | 4 | 0.00088699 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | B | 4 | 0.00088699 | 1.2319e-05
138575 | 41649.5417 | 41649.5903 | 2 | 67 | 134 | 2 | 0.0004127 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | B | 2 | 0.0004127 | 6.1597e-06
138576 | 41649.625 | 41649.6444 | 86 | 25 | 2150 | 86 | 0.0066217 | 0.00026487 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | B | 86 | 0.0066217 | 0.00026487
138581 | 41649.9528 | 41650.0542 | 805 | 143 | 43029.2877 | 300.9041 | 0.13252 | 0.0024793 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-10 | 2014 | 2014 | 2014-01-10 | C | 300.9041 | 0.13252 | 0.0024793
138583 | 41650.6986 | 41650.7285 | 60 | 40 | 2400 | 60 | 0.0073916 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-11 | 2014 | 2014 | 2014-01-11 | C | 60 | 0.0073916 | 0.00018479
138586 | 41650.5799 | 41650.6111 | 19 | 42 | 798 | 19 | 0.0024577 | 5.8517e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-11 | 2014 | 2014 | 2014-01-11 | C | 19 | 0.0024577 | 5.8517e-05
138593 | 41650.6444 | 41650.6722 | 5 | 37 | 185 | 5 | 0.00056977 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-11 | 2014 | 2014 | 2014-01-11 | C | 5 | 0.00056977 | 1.5399e-05
138594 | 41651.2431 | 41651.2951 | 689 | 72 | 42908.16 | 595.9467 | 0.13215 | 0.002122 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-12 | 2014 | 2014 | 2014-01-12 | C | 595.9467 | 0.13215 | 0.002122
138595 | 41650.9167 | 41651.4583 | 2 | 777 | 1554 | 2 | 0.0047861 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-11 | 2014 | 2014 | 2014-01-11 | C | 2 | 0.0047861 | 6.1597e-06
138596 | 41651.3944 | 41651.4042 | 258 | 11 | 1122 | 102 | 0.0034556 | 0.0007946 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-12 | 2014 | 2014 | 2014-01-12 | C | 102 | 0.0034556 | 0.0007946
138598 | 41651.659 | 41651.7083 | 12 | 68 | 816 | 12 | 0.0025132 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-12 | 2014 | 2014 | 2014-01-12 | C | 12 | 0.0025132 | 3.6958e-05
138599 | 41651.4743 | 41651.7743 | 689 | 429 | 10335.7222 | 24.0926 | 0.031832 | 0.002122 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-12 | 2014 | 2014 | 2014-01-12 | C | 24.0926 | 0.031832 | 0.002122
138600 | 41651.7542 | 41651.8049 | 674 | 70 | 20545.4795 | 293.5068 | 0.063277 | 0.0020758 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-12 | 2014 | 2014 | 2014-01-12 | C | 293.5068 | 0.063277 | 0.0020758
138609 | 41652.3542 | 41652.6069 | 9 | 361 | 3249 | 9 | 0.010006 | 2.7719e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 9 | 0.010006 | 2.7719e-05
138615 | 41652.584 | 41652.691 | 3 | 151 | 453 | 3 | 0.0013952 | 9.2395e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 3 | 0.0013952 | 9.2395e-06
138616 | 41652.7188 | 41652.7431 | 49 | 32 | 1568 | 49 | 0.0048292 | 0.00015091 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 49 | 0.0048292 | 0.00015091
138617 | 41653.5451 | 41653.7556 | 132 | 300 | 23808.9109 | 79.363 | 0.073328 | 0.00040654 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | C | 79.363 | 0.073328 | 0.00040654
138618 | 41652.234 | 41652.2368 | 630 | 1 | 630 | 630 | 0.0019403 | 0.0019403 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 630 | 0.0019403 | 0.0019403
138619 | 41652.7257 | 41652.7507 | 29 | 33 | 957 | 29 | 0.0029474 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 29 | 0.0029474 | 8.9315e-05
138620 | 41652.375 | 41652.5 | 13 | 177 | 2301 | 13 | 0.0070867 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | B | 13 | 0.0070867 | 4.0038e-05
138621 | 41652.5833 | 41652.6181 | 19 | 47 | 893 | 19 | 0.0027503 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 19 | 0.0027503 | 5.8517e-05
138622 | 41652.4854 | 41652.5549 | 372 | 97 | 19039.16 | 196.28 | 0.058638 | 0.0011457 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 196.28 | 0.058638 | 0.0011457
138623 | 41652.434 | 41652.4583 | 18 | 32 | 576 | 18 | 0.001774 | 5.5437e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 18 | 0.001774 | 5.5437e-05
138624 | 41652.5 | 41652.5285 | 20 | 38 | 760 | 20 | 0.0023407 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 20 | 0.0023407 | 6.1597e-05
138626 | 41652.8958 | 41652.9507 | 5 | 76 | 380 | 5 | 0.0011703 | 1.5399e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 5 | 0.0011703 | 1.5399e-05
138627 | 41652.8021 | 41653.0556 | 28 | 362 | 8455.9233 | 23.3589 | 0.026043 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 23.3589 | 0.026043 | 8.6236e-05
138635 | 41652.5694 | 41652.5729 | 6 | 2 | 12 | 6 | 3.6958e-05 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 6 | 3.6958e-05 | 1.8479e-05
138636 | 41653.6479 | 41653.7049 | 244 | 79 | 19276 | 244 | 0.059367 | 0.00075148 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | C | 244 | 0.059367 | 0.00075148
138637 | 41653.3542 | 41653.6792 | 217 | 465 | 55056.7949 | 118.4017 | 0.16957 | 0.00066833 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | B | 118.4017 | 0.16957 | 0.00066833
138639 | 41653.4062 | 41653.6236 | 15 | 310 | 4650 | 15 | 0.014321 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | B | 15 | 0.014321 | 4.6198e-05
138640 | 41653.4167 | 41653.5264 | 6 | 155 | 930 | 6 | 0.0028643 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | B | 6 | 0.0028643 | 1.8479e-05
138641 | 41653.3958 | 41653.6 | 53 | 291 | 15423 | 53 | 0.0475 | 0.00016323 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | B | 53 | 0.0475 | 0.00016323
138643 | 41653.9583 | 41654.1444 | 110 | 265 | 16286.6231 | 61.459 | 0.05016 | 0.00033878 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | C | 61.459 | 0.05016 | 0.00033878
138644 | 41653.7653 | 41653.8181 | 62 | 73 | 4526 | 62 | 0.013939 | 0.00019095 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | C | 62 | 0.013939 | 0.00019095
138647 | 41653.4764 | 41653.5076 | 108 | 42 | 4536 | 108 | 0.01397 | 0.00033262 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-14 | 2014 | 2014 | 2014-01-14 | C | 108 | 0.01397 | 0.00033262
138648 | 41654.2139 | 41654.5729 | 157 | 514 | 16363.4932 | 31.8356 | 0.050397 | 0.00048354 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | C | 31.8356 | 0.050397 | 0.00048354
138651 | 41652.7083 | 41652.7639 | 1 | 77 | 77 | 1 | 0.00023715 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-13 | 2014 | 2014 | 2014-01-13 | C | 1 | 0.00023715 | 3.0798e-06
138653 | 41654.3819 | 41654.5278 | 34 | 207 | 7038 | 34 | 0.021676 | 0.00010471 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 34 | 0.021676 | 0.00010471
138654 | 41654.4167 | 41654.4694 | 37 | 73 | 2701 | 37 | 0.0083187 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 37 | 0.0083187 | 0.00011395
138655 | 41654.3958 | 41654.5139 | 57 | 167 | 9519 | 57 | 0.029317 | 0.00017555 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 57 | 0.029317 | 0.00017555
138656 | 41654.3958 | 41654.5451 | 1 | 212 | 212 | 1 | 0.00065293 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | C | 1 | 0.00065293 | 3.0798e-06
138657 | 41654.5208 | 41654.5417 | 4 | 27 | 108 | 4 | 0.00033262 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 4 | 0.00033262 | 1.2319e-05
138659 | 41625.3819 | 41625.5215 | 19 | 198 | 3762 | 19 | 0.011586 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 19 | 0.011586 | 5.8517e-05
138660 | 41625.3576 | 41625.5639 | 49 | 294 | 14406 | 49 | 0.044368 | 0.00015091 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-17 | 2014 | 2014 | 2013-12-17 | B | 49 | 0.044368 | 0.00015091
138661 | 41624.3549 | 41624.584 | 3 | 327 | 981 | 3 | 0.0030213 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-16 | 2014 | 2014 | 2013-12-16 | B | 3 | 0.0030213 | 9.2395e-06
138662 | 41615.3417 | 41615.4049 | 3 | 88 | 264 | 3 | 0.00081308 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 3 | 0.00081308 | 9.2395e-06
138663 | 41608.3438 | 41608.55 | 23 | 294 | 6762 | 23 | 0.020826 | 7.0836e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | B | 23 | 0.020826 | 7.0836e-05
138666 | 41608.3542 | 41608.5201 | 33 | 236 | 7788 | 33 | 0.023986 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-11-30 | 2014 | 2014 | 2013-11-30 | B | 33 | 0.023986 | 0.00010163
138668 | 41654.3542 | 41654.6389 | 167 | 407 | 28612.1 | 70.3 | 0.088121 | 0.00051433 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 70.3 | 0.088121 | 0.00051433
138670 | 41654.4181 | 41654.5868 | 169 | 240 | 40560 | 169 | 0.12492 | 0.00052049 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 169 | 0.12492 | 0.00052049
138671 | 41654.3854 | 41654.5 | 3 | 162 | 486 | 3 | 0.0014968 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-15 | 2014 | 2014 | 2014-01-15 | B | 3 | 0.0014968 | 9.2395e-06
138676 | 41655.1674 | 41655.2986 | 752 | 186 | 16864 | 90.6667 | 0.051938 | 0.002316 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 90.6667 | 0.051938 | 0.002316
138678 | 41655.375 | 41655.4146 | 22 | 54 | 1188 | 22 | 0.0036589 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 22 | 0.0036589 | 6.7757e-05
138679 | 41655.4743 | 41655.5007 | 95 | 35 | 3325 | 95 | 0.01024 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 95 | 0.01024 | 0.00029258
138680 | 41655.4062 | 41655.625 | 41 | 312 | 12792 | 41 | 0.039397 | 0.00012627 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 41 | 0.039397 | 0.00012627
138681 | 41655.375 | 41655.625 | 11 | 357 | 3927 | 11 | 0.012095 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 11 | 0.012095 | 3.3878e-05
138682 | 41655.4271 | 41655.5903 | 26 | 232 | 6032 | 26 | 0.018578 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 26 | 0.018578 | 8.0076e-05
138683 | 41655.3819 | 41655.6181 | 11 | 337 | 3707 | 11 | 0.011417 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 11 | 0.011417 | 3.3878e-05
138685 | 41655.3854 | 41655.4167 | 8 | 42 | 336 | 8 | 0.0010348 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 8 | 0.0010348 | 2.4639e-05
138686 | 41655.5 | 41655.5347 | 2 | 47 | 94 | 2 | 0.00028951 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 2 | 0.00028951 | 6.1597e-06
138687 | 41655.3854 | 41655.4062 | 4 | 27 | 108 | 4 | 0.00033262 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 4 | 0.00033262 | 1.2319e-05
138688 | 41655.5312 | 41655.5451 | 1 | 17 | 17 | 1 | 5.2357e-05 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 1 | 5.2357e-05 | 3.0798e-06
138689 | 41655.5208 | 41655.5451 | 4 | 32 | 128 | 4 | 0.00039422 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 4 | 0.00039422 | 1.2319e-05
138690 | 41655.375 | 41655.6354 | 12 | 372 | 4464 | 12 | 0.013748 | 3.6958e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 12 | 0.013748 | 3.6958e-05
138694 | 41655.3542 | 41655.6562 | 240 | 432 | 56055.7241 | 129.7586 | 0.17264 | 0.00073916 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 129.7586 | 0.17264 | 0.00073916
138699 | 41655.6306 | 41655.6424 | 244 | 14 | 3416 | 244 | 0.010521 | 0.00075148 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 244 | 0.010521 | 0.00075148
138704 | 41655.8528 | 41656.1028 | 414 | 357 | 22163.75 | 62.0833 | 0.068261 | 0.0012751 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 62.0833 | 0.068261 | 0.0012751
138711 | 41656.0299 | 41656.7396 | 271 | 1019 | 62287.6213 | 61.1262 | 0.19184 | 0.00083464 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 61.1262 | 0.19184 | 0.00083464
138712 | 41655.6597 | 41655.8125 | 402 | 217 | 39362.8136 | 181.3955 | 0.12123 | 0.0012381 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 181.3955 | 0.12123 | 0.0012381
138715 | 41655.4403 | 41655.6042 | 1 | 233 | 233 | 1 | 0.0007176 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 1 | 0.0007176 | 3.0798e-06
138716 | 41655.9785 | 41656.0243 | 2560 | 63 | 161280 | 2560 | 0.49672 | 0.0078844 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 2560 | 0.49672 | 0.0078844
138717 | 41655.3854 | 41655.5826 | 1 | 281 | 281 | 1 | 0.00086544 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 1 | 0.00086544 | 3.0798e-06
138718 | 41655.3958 | 41655.6153 | 53 | 313 | 16589 | 53 | 0.051091 | 0.00016323 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 53 | 0.051091 | 0.00016323
138720 | 41655.375 | 41655.6542 | 105 | 399 | 41895 | 105 | 0.12903 | 0.00032338 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 105 | 0.12903 | 0.00032338
138725 | 41655.4306 | 41655.7188 | 114 | 412 | 46968 | 114 | 0.14465 | 0.0003511 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 114 | 0.14465 | 0.0003511
138726 | 41655.3597 | 41655.4208 | 95 | 85 | 8075 | 95 | 0.02487 | 0.00029258 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 95 | 0.02487 | 0.00029258
138728 | 41656.3229 | 41656.3562 | 371 | 45 | 16695 | 371 | 0.051418 | 0.0011426 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 371 | 0.051418 | 0.0011426
138729 | 41656.3958 | 41656.4056 | 5 | 11 | 55 | 5 | 0.00016939 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 5 | 0.00016939 | 1.5399e-05
138731 | 41655.4993 | 41655.7278 | 207 | 326 | 22373.1125 | 68.6292 | 0.068906 | 0.00063753 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | C | 68.6292 | 0.068906 | 0.00063753
138733 | 41656.3868 | 41656.4139 | 41 | 36 | 1476 | 41 | 0.0045458 | 0.00012627 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 41 | 0.0045458 | 0.00012627
138735 | 41656.3785 | 41656.4563 | 1 | 109 | 109 | 1 | 0.0003357 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 1 | 0.0003357 | 3.0798e-06
138737 | 41648.4451 | 41648.534 | 6 | 125 | 750 | 6 | 0.0023099 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-09 | 2014 | 2014 | 2014-01-09 | C | 6 | 0.0023099 | 1.8479e-05
138738 | 41656.3854 | 41656.4375 | 14 | 72 | 1008 | 14 | 0.0031045 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 14 | 0.0031045 | 4.3118e-05
138739 | 41656.5903 | 41656.6007 | 1 | 12 | 12 | 1 | 3.6958e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 1 | 3.6958e-05 | 3.0798e-06
138740 | 41656.3854 | 41656.4062 | 9 | 27 | 243 | 9 | 0.0007484 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 9 | 0.0007484 | 2.7719e-05
138741 | 41656.5278 | 41656.5486 | 8 | 27 | 216 | 8 | 0.00066525 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 8 | 0.00066525 | 2.4639e-05
138742 | 41656.4271 | 41656.5833 | 52 | 222 | 11544 | 52 | 0.035554 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 52 | 0.035554 | 0.00016015
138744 | 41656.6118 | 41656.6931 | 925 | 114 | 45573.6923 | 399.7692 | 0.14036 | 0.0028489 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 399.7692 | 0.14036 | 0.0028489
138746 | 41656.3646 | 41656.6542 | 20 | 414 | 8280 | 20 | 0.025501 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 20 | 0.025501 | 6.1597e-05
138747 | 41656.7819 | 41656.7986 | 3 | 21 | 63 | 3 | 0.00019403 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 3 | 0.00019403 | 9.2395e-06
138748 | 41656.8083 | 41656.8306 | 8 | 29 | 232 | 8 | 0.00071452 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 8 | 0.00071452 | 2.4639e-05
138749 | 41656.7465 | 41656.8174 | 13 | 99 | 1287 | 13 | 0.0039638 | 4.0038e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 13 | 0.0039638 | 4.0038e-05
138751 | 41656.6264 | 41656.7569 | 500 | 185 | 59640.8511 | 322.383 | 0.18368 | 0.0015399 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 322.383 | 0.18368 | 0.0015399
138752 | 41656.7118 | 41656.7243 | 1422 | 15 | 21330 | 1422 | 0.065693 | 0.0043795 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 1422 | 0.065693 | 0.0043795
138753 | 41656.7118 | 41656.7292 | 1221 | 22 | 26862 | 1221 | 0.082731 | 0.0037605 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 1221 | 0.082731 | 0.0037605
138754 | 41656.7118 | 41656.7354 | 2427 | 31 | 75237 | 2427 | 0.23172 | 0.0074748 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 2427 | 0.23172 | 0.0074748
138755 | 41656.9646 | 41656.9819 | 86 | 22 | 1892 | 86 | 0.0058271 | 0.00026487 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 86 | 0.0058271 | 0.00026487
138756 | 41656.9215 | 41656.9361 | 294 | 18 | 4258.2857 | 236.5714 | 0.013115 | 0.00090547 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 236.5714 | 0.013115 | 0.00090547
138757 | 41657.8479 | 41657.9181 | 110 | 98 | 10780 | 110 | 0.033201 | 0.00033878 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 110 | 0.033201 | 0.00033878
138759 | 41657.0465 | 41657.0528 | 313 | 6 | 1878 | 313 | 0.0057839 | 0.00096399 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 313 | 0.0057839 | 0.00096399
138762 | 41656.2944 | 41656.3264 | 27 | 43 | 1161 | 27 | 0.0035757 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 27 | 0.0035757 | 8.3156e-05
138763 | 41656.7549 | 41656.8028 | 104 | 66 | 6864 | 104 | 0.02114 | 0.0003203 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 104 | 0.02114 | 0.0003203
138765 | 41657.0174 | 41657.1687 | 359 | 215 | 49207.3853 | 228.8716 | 0.15155 | 0.0011057 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 228.8716 | 0.15155 | 0.0011057
138766 | 41657.1958 | 41657.4583 | 325 | 375 | 20531.746 | 54.7513 | 0.063235 | 0.0010009 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 54.7513 | 0.063235 | 0.0010009
138767 | 41656.3542 | 41656.6549 | 240 | 430 | 35428.8222 | 82.3926 | 0.10912 | 0.00073916 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 82.3926 | 0.10912 | 0.00073916
138768 | 41656.4167 | 41656.6181 | 3 | 287 | 861 | 3 | 0.0026517 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | B | 3 | 0.0026517 | 9.2395e-06
138771 | 41657.3931 | 41657.4528 | 688 | 83 | 50982.2674 | 614.2442 | 0.15702 | 0.0021189 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 614.2442 | 0.15702 | 0.0021189
138772 | 41656.6069 | 41656.7021 | 148 | 134 | 19832 | 148 | 0.061079 | 0.00045582 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 148 | 0.061079 | 0.00045582
138775 | 41615.3833 | 41615.5771 | 16 | 276 | 4416 | 16 | 0.013601 | 4.9277e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2013-12-07 | 2014 | 2014 | 2013-12-07 | B | 16 | 0.013601 | 4.9277e-05
138776 | 41657.3889 | 41657.625 | 13 | 337 | 4381 | 13 | 0.013493 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | B | 13 | 0.013493 | 4.0038e-05
138778 | 41657.7903 | 41658.134 | 303 | 492 | 36760.8485 | 74.7172 | 0.11322 | 0.00093319 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-18 | 2014 | 2014 | 2014-01-18 | C | 74.7172 | 0.11322 | 0.00093319
138780 | 41658.3472 | 41658.3618 | 2514 | 18 | 45252 | 2514 | 0.13937 | 0.0077427 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | C | 2514 | 0.13937 | 0.0077427
138781 | 41658.2604 | 41658.5167 | 50 | 366 | 8551.9024 | 23.3659 | 0.026339 | 0.00015399 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | C | 23.3659 | 0.026339 | 0.00015399
138782 | 41658.4715 | 41658.4938 | 28 | 29 | 812 | 28 | 0.0025008 | 8.6236e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | C | 28 | 0.0025008 | 8.6236e-05
138783 | 41658.375 | 41658.6424 | 13 | 382 | 4966 | 13 | 0.015294 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | B | 13 | 0.015294 | 4.0038e-05
138784 | 41658.6639 | 41658.6951 | 2 | 42 | 84 | 2 | 0.00025871 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | C | 2 | 0.00025871 | 6.1597e-06
138787 | 41658.6104 | 41658.6785 | 638 | 95 | 30109.1837 | 316.9388 | 0.092732 | 0.0019649 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-19 | 2014 | 2014 | 2014-01-19 | C | 316.9388 | 0.092732 | 0.0019649
138789 | 41656.6139 | 41656.7917 | 12 | 253 | 3036 | 12 | 0.0093504 | 3.6958e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-17 | 2014 | 2014 | 2014-01-17 | C | 12 | 0.0093504 | 3.6958e-05
138791 | 41659.5938 | 41659.6875 | 672 | 132 | 53985.0667 | 408.9778 | 0.16627 | 0.0020697 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 408.9778 | 0.16627 | 0.0020697
138797 | 41659.7722 | 41659.925 | 1496 | 217 | 110561.5 | 509.5 | 0.34051 | 0.0046074 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 509.5 | 0.34051 | 0.0046074
138799 | 41659.3854 | 41659.4132 | 8 | 37 | 296 | 8 | 0.00091163 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | B | 8 | 0.00091163 | 2.4639e-05
138801 | 41659.5208 | 41659.5417 | 4 | 27 | 108 | 4 | 0.00033262 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | B | 4 | 0.00033262 | 1.2319e-05
138803 | 41659.916 | 41659.9458 | 101 | 40 | 4040 | 101 | 0.012443 | 0.00031106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 101 | 0.012443 | 0.00031106
138804 | 41659.6618 | 41659.6757 | 394 | 17 | 6698 | 394 | 0.020629 | 0.0012135 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 394 | 0.020629 | 0.0012135
138805 | 41659.6618 | 41659.8403 | 258 | 254 | 41583.8521 | 163.716 | 0.12807 | 0.0007946 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 163.716 | 0.12807 | 0.0007946
138806 | 41659.7722 | 41659.8125 | 93 | 55 | 5115 | 93 | 0.015753 | 0.00028643 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 93 | 0.015753 | 0.00028643
138807 | 41659.6618 | 41659.7688 | 2470 | 151 | 370532.4286 | 2453.8571 | 1.1412 | 0.0076072 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 2453.8571 | 1.1412 | 0.0076072
138808 | 41659.7021 | 41659.7736 | 287 | 100 | 26686.4078 | 266.8641 | 0.08219 | 0.00088391 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 266.8641 | 0.08219 | 0.00088391
138809 | 41659.6618 | 41659.7604 | 1090 | 139 | 111000.3099 | 798.5634 | 0.34186 | 0.003357 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 798.5634 | 0.34186 | 0.003357
138810 | 41659.6618 | 41659.7069 | 330 | 62 | 19876.2462 | 320.5846 | 0.061216 | 0.0010163 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 320.5846 | 0.061216 | 0.0010163
138811 | 41659.6618 | 41659.684 | 1 | 29 | 29 | 1 | 8.9315e-05 | 3.0798e-06 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 1 | 8.9315e-05 | 3.0798e-06
138812 | 41659.8819 | 41660.4194 | 108 | 771 | 79506.6357 | 103.1214 | 0.24487 | 0.00033262 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 103.1214 | 0.24487 | 0.00033262
138813 | 41660.3194 | 41660.3993 | 4 | 112 | 448 | 4 | 0.0013798 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 4 | 0.0013798 | 1.2319e-05
138814 | 41659.8799 | 41660.3951 | 225 | 739 | 134075.7143 | 181.4286 | 0.41293 | 0.00069296 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 181.4286 | 0.41293 | 0.00069296
138815 | 41660.2153 | 41660.3083 | 170 | 131 | 12250.4552 | 93.5149 | 0.037729 | 0.00052357 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 93.5149 | 0.037729 | 0.00052357
138816 | 41660.3653 | 41660.4375 | 4 | 101 | 404 | 4 | 0.0012443 | 1.2319e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 4 | 0.0012443 | 1.2319e-05
138817 | 41659.6861 | 41659.7764 | 1456 | 127 | 166724.6231 | 1312.7923 | 0.51349 | 0.0044842 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 1312.7923 | 0.51349 | 0.0044842
138818 | 41659.8597 | 41659.8632 | 77 | 2 | 154 | 77 | 0.0004743 | 0.00023715 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 77 | 0.0004743 | 0.00023715
138819 | 41659.8618 | 41659.9812 | 527 | 169 | 49630.9767 | 293.6744 | 0.15286 | 0.0016231 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 293.6744 | 0.15286 | 0.0016231
138821 | 41659.8819 | 41660.0104 | 94 | 182 | 16147.827 | 88.7243 | 0.049733 | 0.00028951 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 88.7243 | 0.049733 | 0.00028951
138822 | 41659.9444 | 41659.9896 | 16 | 62 | 992 | 16 | 0.0030552 | 4.9277e-05 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 16 | 0.0030552 | 4.9277e-05
138823 | 41660.1625 | 41660.2535 | 343 | 128 | 24765.5573 | 193.4809 | 0.076274 | 0.0010564 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 193.4809 | 0.076274 | 0.0010564
138824 | 41659.9021 | 41660.4639 | 1 | 806 | 806 | 1 | 0.0024824 | 3.0798e-06 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 1 | 0.0024824 | 3.0798e-06
138825 | 41659.9514 | 41660.4896 | 14 | 772 | 7206.9935 | 9.3355 | 0.022196 | 4.3118e-05 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 9.3355 | 0.022196 | 4.3118e-05
138826 | 41660.4951 | 41660.5368 | 38 | 57 | 2166 | 38 | 0.0066709 | 0.00011703 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 38 | 0.0066709 | 0.00011703
138827 | 41659.9688 | 41660.1667 | 415 | 282 | 21413.2 | 75.9333 | 0.065949 | 0.0012781 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 75.9333 | 0.065949 | 0.0012781
138828 | 41660.0194 | 41660.109 | 654 | 126 | 38825.5814 | 308.1395 | 0.11958 | 0.0020142 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 308.1395 | 0.11958 | 0.0020142
138829 | 41660.3854 | 41660.616 | 63 | 329 | 20727 | 63 | 0.063836 | 0.00019403 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 63 | 0.063836 | 0.00019403
138830 | 41660.0167 | 41660.1264 | 663 | 155 | 29698.1962 | 191.6013 | 0.091466 | 0.0020419 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 191.6013 | 0.091466 | 0.0020419
138831 | 41660.0951 | 41660.1076 | 478 | 15 | 7170 | 478 | 0.022082 | 0.0014722 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 478 | 0.022082 | 0.0014722
138832 | 41660.375 | 41660.625 | 5 | 357 | 1785 | 5 | 0.0054975 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 5 | 0.0054975 | 1.5399e-05
138833 | 41660.541 | 41660.6438 | 1 | 145 | 145 | 1 | 0.00044658 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 1 | 0.00044658 | 3.0798e-06
138834 | 41659.9431 | 41660.5014 | 77 | 801 | 52572.1007 | 65.6331 | 0.16191 | 0.00023715 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 65.6331 | 0.16191 | 0.00023715
138835 | 41660.6562 | 41660.6993 | 4 | 59 | 236 | 4 | 0.00072684 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 4 | 0.00072684 | 1.2319e-05
138836 | 41660.6035 | 41660.6458 | 88 | 58 | 5104 | 88 | 0.01572 | 0.00027103 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 88 | 0.01572 | 0.00027103
138838 | 41660.7146 | 41660.7701 | 155 | 77 | 11935 | 155 | 0.036758 | 0.00047738 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 155 | 0.036758 | 0.00047738
138839 | 41659.916 | 41660.6854 | 4 | 1105 | 4420 | 4 | 0.013613 | 1.2319e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-20 | 2014 | 2014 | 2014-01-20 | C | 4 | 0.013613 | 1.2319e-05
138840 | 41660.3958 | 41660.4444 | 6 | 67 | 402 | 6 | 0.0012381 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 6 | 0.0012381 | 1.8479e-05
138842 | 41660.309 | 41660.3785 | 7 | 97 | 679 | 7 | 0.0020912 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 7 | 0.0020912 | 2.1559e-05
138843 | 41660.7347 | 41660.8076 | 733 | 102 | 43993.0857 | 431.3048 | 0.13549 | 0.0022575 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 431.3048 | 0.13549 | 0.0022575
138846 | 41660.7986 | 41660.8125 | 30 | 17 | 510 | 30 | 0.0015707 | 9.2395e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 30 | 0.0015707 | 9.2395e-05
138847 | 41660.7792 | 41660.8764 | 466 | 137 | 58608.6 | 427.8 | 0.18051 | 0.0014352 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 427.8 | 0.18051 | 0.0014352
138848 | 41661.0854 | 41661.1458 | 1023 | 84 | 84122.6207 | 1001.4598 | 0.25908 | 0.0031507 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 1001.4598 | 0.25908 | 0.0031507
138849 | 41660.8271 | 41661.4042 | 110 | 828 | 11690.6426 | 14.1191 | 0.036005 | 0.00033878 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 14.1191 | 0.036005 | 0.00033878
138850 | 41660.7007 | 41661.4104 | 290 | 1019 | 45312.5969 | 44.4677 | 0.13956 | 0.00089315 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 44.4677 | 0.13956 | 0.00089315
138851 | 41660.7806 | 41661.4507 | 787 | 962 | 73605.4611 | 76.513 | 0.22669 | 0.0024238 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 76.513 | 0.22669 | 0.0024238
138852 | 41661.4028 | 41661.4132 | 6 | 12 | 72 | 6 | 0.00022175 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 6 | 0.00022175 | 1.8479e-05
138853 | 41661.409 | 41661.4278 | 169 | 24 | 4056 | 169 | 0.012492 | 0.00052049 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 169 | 0.012492 | 0.00052049
138854 | 41660.9271 | 41661.5312 | 4 | 867 | 3468 | 4 | 0.010681 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 4 | 0.010681 | 1.2319e-05
138856 | 41661.559 | 41661.5674 | 1 | 9 | 9 | 1 | 2.7719e-05 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 1 | 2.7719e-05 | 3.0798e-06
138860 | 41660.425 | 41660.5069 | 37 | 115 | 4255 | 37 | 0.013105 | 0.00011395 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 37 | 0.013105 | 0.00011395
138862 | 41661.5007 | 41661.5736 | 59 | 102 | 6018 | 59 | 0.018534 | 0.00018171 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 59 | 0.018534 | 0.00018171
138865 | 41660.6618 | 41661.5521 | 2 | 1279 | 2558 | 2 | 0.0078782 | 6.1597e-06 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 2 | 0.0078782 | 6.1597e-06
138869 | 41655.375 | 41655.6097 | 136 | 335 | 45560 | 136 | 0.14032 | 0.00041886 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-16 | 2014 | 2014 | 2014-01-16 | B | 136 | 0.14032 | 0.00041886
138871 | 41661.3903 | 41661.6347 | 5 | 349 | 1745 | 5 | 0.0053743 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 5 | 0.0053743 | 1.5399e-05
138872 | 41661.4062 | 41661.5535 | 82 | 209 | 17138 | 82 | 0.052782 | 0.00025255 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 82 | 0.052782 | 0.00025255
138876 | 41661.6181 | 41661.6271 | 3 | 10 | 30 | 3 | 9.2395e-05 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | C | 3 | 9.2395e-05 | 9.2395e-06
138878 | 41661.5417 | 41661.559 | 7 | 22 | 154 | 7 | 0.0004743 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 7 | 0.0004743 | 2.1559e-05
138880 | 41661.4583 | 41661.4826 | 6 | 32 | 192 | 6 | 0.00059133 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 6 | 0.00059133 | 1.8479e-05
138881 | 41661.3785 | 41661.4028 | 8 | 32 | 256 | 8 | 0.00078844 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 8 | 0.00078844 | 2.4639e-05
138882 | 41661.5417 | 41661.6042 | 3 | 87 | 261 | 3 | 0.00080384 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 3 | 0.00080384 | 9.2395e-06
138883 | 41660.8438 | 41661.6701 | 3 | 1187 | 3561 | 3 | 0.010967 | 9.2395e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 3 | 0.010967 | 9.2395e-06
138884 | 41661.5417 | 41661.6042 | 5 | 87 | 435 | 5 | 0.0013397 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 5 | 0.0013397 | 1.5399e-05
138885 | 41661.375 | 41661.4375 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-22 | 2014 | 2014 | 2014-01-22 | B | 2 | 0.00053589 | 6.1597e-06
138888 | 41662.3903 | 41662.4667 | 2 | 107 | 214 | 2 | 0.00065909 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 2 | 0.00065909 | 6.1597e-06
138895 | 41662.5208 | 41662.559 | 644 | 52 | 11908.9455 | 229.0182 | 0.036678 | 0.0019834 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | C | 229.0182 | 0.036678 | 0.0019834
138896 | 41662.4215 | 41662.4646 | 85 | 59 | 5015 | 85 | 0.015445 | 0.00026179 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 85 | 0.015445 | 0.00026179
138898 | 41662.3542 | 41662.6104 | 14 | 366 | 5124 | 14 | 0.015781 | 4.3118e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 14 | 0.015781 | 4.3118e-05
138900 | 41662.375 | 41662.625 | 58 | 357 | 20706 | 58 | 0.063771 | 0.00017863 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 58 | 0.063771 | 0.00017863
138902 | 41662.3854 | 41662.641 | 105 | 365 | 38325 | 105 | 0.11803 | 0.00032338 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 105 | 0.11803 | 0.00032338
138903 | 41660.4764 | 41660.5403 | 94 | 89 | 6183.5652 | 69.4783 | 0.019044 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 69.4783 | 0.019044 | 0.00028951
138904 | 41662.65 | 41662.6819 | 14 | 43 | 602 | 14 | 0.0018541 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | C | 14 | 0.0018541 | 4.3118e-05
138905 | 41662.375 | 41662.5292 | 4 | 219 | 876 | 4 | 0.0026979 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 4 | 0.0026979 | 1.2319e-05
138907 | 41660.5 | 41660.5139 | 2 | 17 | 34 | 2 | 0.00010471 | 6.1597e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | C | 2 | 0.00010471 | 6.1597e-06
138910 | 41663.3806 | 41663.566 | 54 | 264 | 14256 | 54 | 0.043906 | 0.00016631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | B | 54 | 0.043906 | 0.00016631
138911 | 41663.4951 | 41663.5743 | 1 | 111 | 111 | 1 | 0.00034186 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | C | 1 | 0.00034186 | 3.0798e-06
138915 | 41660.375 | 41660.4597 | 76 | 119 | 9044 | 76 | 0.027854 | 0.00023407 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 76 | 0.027854 | 0.00023407
138916 | 41663.3139 | 41663.4 | 417 | 121 | 50457 | 417 | 0.1554 | 0.0012843 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | C | 417 | 0.1554 | 0.0012843
138917 | 41663.4167 | 41663.5799 | 3 | 232 | 696 | 3 | 0.0021436 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | B | 3 | 0.0021436 | 9.2395e-06
138919 | 41663.7007 | 41663.7556 | 125 | 76 | 9500 | 125 | 0.029258 | 0.00038498 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | C | 125 | 0.029258 | 0.00038498
138920 | 41663.7562 | 41663.7931 | 1 | 50 | 50 | 1 | 0.00015399 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-24 | 2014 | 2014 | 2014-01-24 | C | 1 | 0.00015399 | 3.0798e-06
138925 | 41664.4215 | 41664.4507 | 5 | 39 | 195 | 5 | 0.00060057 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-25 | 2014 | 2014 | 2014-01-25 | C | 5 | 0.00060057 | 1.5399e-05
138926 | 41664.375 | 41664.4375 | 2 | 87 | 174 | 2 | 0.00053589 | 6.1597e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-25 | 2014 | 2014 | 2014-01-25 | C | 2 | 0.00053589 | 6.1597e-06
138927 | 41665.0667 | 41665.1306 | 920 | 89 | 81221.2065 | 912.5978 | 0.25015 | 0.0028335 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 912.5978 | 0.25015 | 0.0028335
138933 | 41665.8306 | 41665.8708 | 167 | 55 | 5701.9828 | 103.6724 | 0.017561 | 0.00051433 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 103.6724 | 0.017561 | 0.00051433
138934 | 41665.5868 | 41665.8208 | 27 | 334 | 9018 | 27 | 0.027774 | 8.3156e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 27 | 0.027774 | 8.3156e-05
138936 | 41665.7243 | 41665.825 | 5 | 142 | 710 | 5 | 0.0021867 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 5 | 0.0021867 | 1.5399e-05
138937 | 41665.6167 | 41665.6361 | 37 | 25 | 925 | 37 | 0.0028489 | 0.00011395 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 37 | 0.0028489 | 0.00011395
138939 | 41665.6056 | 41665.7201 | 402 | 162 | 65124 | 402 | 0.20057 | 0.0012381 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 402 | 0.20057 | 0.0012381
138940 | 41665.3618 | 41665.416 | 856 | 75 | 54175 | 722.3333 | 0.16685 | 0.0026363 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 722.3333 | 0.16685 | 0.0026363
138941 | 41665.7319 | 41665.8903 | 279 | 225 | 31575 | 140.3333 | 0.097246 | 0.00085928 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 140.3333 | 0.097246 | 0.00085928
138942 | 41666.0278 | 41666.0306 | 264 | 1 | 264 | 264 | 0.00081308 | 0.00081308 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-27 | 2014 | 2014 | 2014-01-27 | C | 264 | 0.00081308 | 0.00081308
138945 | 41665.7354 | 41666.6514 | 44 | 1316 | 57904 | 44 | 0.17834 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 44 | 0.17834 | 0.00013551
138948 | 41666.6139 | 41666.6319 | 42 | 23 | 966 | 42 | 0.0029751 | 0.00012935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-27 | 2014 | 2014 | 2014-01-27 | C | 42 | 0.0029751 | 0.00012935
138949 | 41666.4062 | 41666.5715 | 33 | 235 | 7755 | 33 | 0.023884 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-27 | 2014 | 2014 | 2014-01-27 | B | 33 | 0.023884 | 0.00010163
138952 | 41665.8993 | 41666.5681 | 4 | 960 | 1127.4766 | 1.1745 | 0.0034724 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 1.1745 | 0.0034724 | 1.2319e-05
138954 | 41665.6667 | 41665.7701 | 137 | 146 | 20002 | 137 | 0.061603 | 0.00042194 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-26 | 2014 | 2014 | 2014-01-26 | C | 137 | 0.061603 | 0.00042194
138957 | 41666.9417 | 41666.9535 | 120 | 14 | 1680 | 120 | 0.0051741 | 0.00036958 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-27 | 2014 | 2014 | 2014-01-27 | C | 120 | 0.0051741 | 0.00036958
138960 | 41667.5201 | 41667.5243 | 380 | 3 | 1140 | 380 | 0.003511 | 0.0011703 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-01-28 | 2014 | 2014 | 2014-01-28 | C | 380 | 0.003511 | 0.0011703
138962 | 41667.359 | 41667.3861 | 9286 | 36 | 266450.7692 | 7401.4103 | 0.82063 | 0.028599 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-01-28 | 2014 | 2014 | 2014-01-28 | C | 7401.4103 | 0.82063 | 0.028599
138965 | 41667.3681 | 41667.5215 | 6 | 218 | 1308 | 6 | 0.0040284 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-28 | 2014 | 2014 | 2014-01-28 | B | 6 | 0.0040284 | 1.8479e-05
138966 | 41667.8819 | 41667.9104 | 3 | 38 | 114 | 3 | 0.0003511 | 9.2395e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-01-28 | 2014 | 2014 | 2014-01-28 | C | 3 | 0.0003511 | 9.2395e-06
138967 | 41667.7736 | 41667.8125 | 423 | 53 | 21268.1429 | 401.2857 | 0.065503 | 0.0013028 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-28 | 2014 | 2014 | 2014-01-28 | C | 401.2857 | 0.065503 | 0.0013028
138969 | 41660.9187 | 41661.125 | 11 | 294 | 3234 | 11 | 0.0099602 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 11 | 0.0099602 | 3.3878e-05
138972 | 41668.3854 | 41668.5299 | 107 | 205 | 21935 | 107 | 0.067556 | 0.00032954 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | B | 107 | 0.067556 | 0.00032954
138973 | 41668.375 | 41668.5875 | 2 | 303 | 606 | 2 | 0.0018664 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | B | 2 | 0.0018664 | 6.1597e-06
138975 | 41668.5799 | 41668.6104 | 232 | 41 | 9512 | 232 | 0.029295 | 0.00071452 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | C | 232 | 0.029295 | 0.00071452
138976 | 41668.3681 | 41668.609 | 19 | 344 | 6536 | 19 | 0.02013 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | B | 19 | 0.02013 | 5.8517e-05
138977 | 41668.3875 | 41668.6458 | 77 | 369 | 28413 | 77 | 0.087508 | 0.00023715 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | B | 77 | 0.087508 | 0.00023715
138979 | 41668.3958 | 41668.6007 | 104 | 292 | 21103.1864 | 72.2712 | 0.064994 | 0.0003203 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | B | 72.2712 | 0.064994 | 0.0003203
138983 | 41668.6556 | 41668.8354 | 423 | 256 | 96859.9228 | 378.3591 | 0.29831 | 0.0013028 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-29 | 2014 | 2014 | 2014-01-29 | C | 378.3591 | 0.29831 | 0.0013028
138984 | 41669.0625 | 41669.0736 | 264 | 13 | 3432 | 264 | 0.01057 | 0.00081308 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 264 | 0.01057 | 0.00081308
138987 | 41662.8882 | 41663.0604 | 1 | 245 | 245 | 1 | 0.00075456 | 3.0798e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | C | 1 | 0.00075456 | 3.0798e-06
138988 | 41669.3993 | 41669.4847 | 51 | 120 | 6120 | 51 | 0.018849 | 0.00015707 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | B | 51 | 0.018849 | 0.00015707
138989 | 41669.4528 | 41669.5236 | 7 | 99 | 693 | 7 | 0.0021343 | 2.1559e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 7 | 0.0021343 | 2.1559e-05
138990 | 41669.2847 | 41669.4583 | 98 | 247 | 11904.412 | 48.196 | 0.036664 | 0.00030182 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 48.196 | 0.036664 | 0.00030182
138991 | 41669.4847 | 41669.5208 | 26 | 49 | 1274 | 26 | 0.0039237 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 26 | 0.0039237 | 8.0076e-05
138994 | 41660.3542 | 41660.6125 | 2 | 369 | 738 | 2 | 0.0022729 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 2 | 0.0022729 | 6.1597e-06
138996 | 41669.6111 | 41669.6521 | 54 | 56 | 3024 | 54 | 0.0093134 | 0.00016631 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 54 | 0.0093134 | 0.00016631
138997 | 41669.3757 | 41669.6549 | 126 | 399 | 17915.2985 | 44.9005 | 0.055176 | 0.00038806 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | B | 44.9005 | 0.055176 | 0.00038806
138998 | 41669.809 | 41669.8681 | 1 | 82 | 82 | 1 | 0.00025255 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 1 | 0.00025255 | 3.0798e-06
139000 | 41669.8938 | 41670.1083 | 161 | 306 | 43046.9709 | 140.6764 | 0.13258 | 0.00049585 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 140.6764 | 0.13258 | 0.00049585
139001 | 41669.9931 | 41670.0021 | 168 | 10 | 1680 | 168 | 0.0051741 | 0.00051741 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | C | 168 | 0.0051741 | 0.00051741
139003 | 41670.5479 | 41670.5639 | 76 | 20 | 1520 | 76 | 0.0046814 | 0.00023407 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-01-31 | 2014 | 2014 | 2014-01-31 | C | 76 | 0.0046814 | 0.00023407
139004 | 41669.3854 | 41669.5417 | 11 | 222 | 2442 | 11 | 0.007521 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | B | 11 | 0.007521 | 3.3878e-05
139005 | 41670.3854 | 41670.5715 | 18 | 265 | 4770 | 18 | 0.014691 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-31 | 2014 | 2014 | 2014-01-31 | B | 18 | 0.014691 | 5.5437e-05
139008 | 41671.8542 | 41671.875 | 27 | 27 | 729 | 27 | 0.0022452 | 8.3156e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-01 | 2014 | 2014 | 2014-02-01 | C | 27 | 0.0022452 | 8.3156e-05
139011 | 41672.4701 | 41672.5146 | 278 | 61 | 12634.625 | 207.125 | 0.038913 | 0.0008562 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-02 | 2014 | 2014 | 2014-02-02 | C | 207.125 | 0.038913 | 0.0008562
139012 | 41672.4 | 41672.5625 | 4 | 231 | 924 | 4 | 0.0028458 | 1.2319e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-02 | 2014 | 2014 | 2014-02-02 | C | 4 | 0.0028458 | 1.2319e-05
139013 | 41672.4993 | 41672.5875 | 27 | 124 | 3348 | 27 | 0.010311 | 8.3156e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-02 | 2014 | 2014 | 2014-02-02 | C | 27 | 0.010311 | 8.3156e-05
139016 | 41672.7236 | 41672.75 | 565 | 35 | 18791.3158 | 536.8947 | 0.057874 | 0.0017401 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-02 | 2014 | 2014 | 2014-02-02 | C | 536.8947 | 0.057874 | 0.0017401
139018 | 41669.3715 | 41669.5306 | 4 | 226 | 904 | 4 | 0.0027842 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-30 | 2014 | 2014 | 2014-01-30 | B | 4 | 0.0027842 | 1.2319e-05
139019 | 41660.3958 | 41660.4271 | 5 | 42 | 210 | 5 | 0.00064677 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-21 | 2014 | 2014 | 2014-01-21 | B | 5 | 0.00064677 | 1.5399e-05
139020 | 41673.4167 | 41673.4583 | 6 | 57 | 342 | 6 | 0.0010533 | 1.8479e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-03 | 2014 | 2014 | 2014-02-03 | C | 6 | 0.0010533 | 1.8479e-05
139021 | 41673.4167 | 41673.5104 | 6 | 132 | 792 | 6 | 0.0024392 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-03 | 2014 | 2014 | 2014-02-03 | C | 6 | 0.0024392 | 1.8479e-05
139022 | 41673.375 | 41673.6319 | 126 | 367 | 9001.4189 | 24.527 | 0.027723 | 0.00038806 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-03 | 2014 | 2014 | 2014-02-03 | B | 24.527 | 0.027723 | 0.00038806
139025 | 41673.3438 | 41673.6181 | 25 | 392 | 9800 | 25 | 0.030182 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-03 | 2014 | 2014 | 2014-02-03 | B | 25 | 0.030182 | 7.6996e-05
139033 | 41674.25 | 41674.2646 | 35 | 18 | 630 | 35 | 0.0019403 | 0.00010779 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 35 | 0.0019403 | 0.00010779
139037 | 41674.3764 | 41674.5694 | 3 | 275 | 825 | 3 | 0.0025409 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 3 | 0.0025409 | 9.2395e-06
139038 | 41674.5625 | 41674.5972 | 8 | 47 | 376 | 8 | 0.001158 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 8 | 0.001158 | 2.4639e-05
139040 | 41674.4792 | 41674.5417 | 6 | 87 | 522 | 6 | 0.0016077 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 6 | 0.0016077 | 1.8479e-05
139041 | 41674.4375 | 41674.4722 | 5 | 47 | 235 | 5 | 0.00072376 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 5 | 0.00072376 | 1.5399e-05
139042 | 41674.4271 | 41674.625 | 13 | 282 | 3666 | 13 | 0.011291 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 13 | 0.011291 | 4.0038e-05
139043 | 41674.3646 | 41674.6472 | 23 | 404 | 8665.6511 | 21.4496 | 0.026689 | 7.0836e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 21.4496 | 0.026689 | 7.0836e-05
139044 | 41674.4465 | 41674.5833 | 52 | 194 | 10088 | 52 | 0.031069 | 0.00016015 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 52 | 0.031069 | 0.00016015
139045 | 41674.3854 | 41674.6361 | 1 | 358 | 358 | 1 | 0.0011026 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 1 | 0.0011026 | 3.0798e-06
139046 | 41674.4076 | 41674.5201 | 409 | 159 | 22768.4074 | 143.1975 | 0.070123 | 0.0012597 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | C | 143.1975 | 0.070123 | 0.0012597
139047 | 41674.4833 | 41674.5021 | 74 | 24 | 1776 | 74 | 0.0054698 | 0.00022791 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 74 | 0.0054698 | 0.00022791
139049 | 41674.3854 | 41674.5743 | 18 | 269 | 4842 | 18 | 0.014913 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 18 | 0.014913 | 5.5437e-05
139050 | 41674.4347 | 41674.4493 | 101 | 18 | 1818 | 101 | 0.0055992 | 0.00031106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 101 | 0.0055992 | 0.00031106
139053 | 41674.859 | 41675.0083 | 22 | 212 | 4664 | 22 | 0.014364 | 6.7757e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-04 | 2014 | 2014 | 2014-02-04 | B | 22 | 0.014364 | 6.7757e-05
139055 | 41675.2125 | 41675.3111 | 795 | 139 | 25622.9859 | 184.338 | 0.078915 | 0.0024485 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | C | 184.338 | 0.078915 | 0.0024485
139056 | 41675.4472 | 41675.4583 | 2 | 13 | 26 | 2 | 8.0076e-05 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | C | 2 | 8.0076e-05 | 6.1597e-06
139057 | 41675.425 | 41675.4736 | 1 | 67 | 67 | 1 | 0.00020635 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | B | 1 | 0.00020635 | 3.0798e-06
139059 | 41675.3854 | 41675.5924 | 27 | 295 | 7965 | 27 | 0.024531 | 8.3156e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | B | 27 | 0.024531 | 8.3156e-05
139060 | 41675.375 | 41675.6389 | 5 | 377 | 1885 | 5 | 0.0058055 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | B | 5 | 0.0058055 | 1.5399e-05
139061 | 41675.4375 | 41675.4563 | 64 | 24 | 1536 | 64 | 0.0047306 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | B | 64 | 0.0047306 | 0.00019711
139062 | 41675.3854 | 41675.5292 | 18 | 204 | 3672 | 18 | 0.011309 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | B | 18 | 0.011309 | 5.5437e-05
139064 | 41675.8229 | 41675.8576 | 24 | 47 | 1128 | 24 | 0.0034741 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-05 | 2014 | 2014 | 2014-02-05 | C | 24 | 0.0034741 | 7.3916e-05
139076 | 41677.4215 | 41677.5799 | 488 | 225 | 69994.7368 | 311.0877 | 0.21557 | 0.001503 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-07 | 2014 | 2014 | 2014-02-07 | C | 311.0877 | 0.21557 | 0.001503
139077 | 41677.3333 | 41677.3868 | 4 | 74 | 296 | 4 | 0.00091163 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-07 | 2014 | 2014 | 2014-02-07 | C | 4 | 0.00091163 | 1.2319e-05
139078 | 41677.3958 | 41677.6264 | 33 | 329 | 10857 | 33 | 0.033438 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-07 | 2014 | 2014 | 2014-02-07 | B | 33 | 0.033438 | 0.00010163
139081 | 41677.5729 | 41677.5799 | 16 | 7 | 112 | 16 | 0.00034494 | 4.9277e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-07 | 2014 | 2014 | 2014-02-07 | C | 16 | 0.00034494 | 4.9277e-05
139085 | 41678.1201 | 41678.1326 | 406 | 15 | 5365 | 357.6667 | 0.016523 | 0.0012504 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 357.6667 | 0.016523 | 0.0012504
139088 | 41678.2403 | 41678.4542 | 263 | 305 | 33751.0227 | 110.6591 | 0.10395 | 0.00081 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 110.6591 | 0.10395 | 0.00081
139095 | 41678.2639 | 41678.2757 | 239 | 14 | 3107.1765 | 221.9412 | 0.0095696 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 221.9412 | 0.0095696 | 0.00073608
139096 | 41678.8632 | 41678.9146 | 2 | 71 | 142 | 2 | 0.00043734 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 2 | 0.00043734 | 6.1597e-06
139097 | 41678.9576 | 41679.1188 | 671 | 229 | 33595.8793 | 146.7069 | 0.10347 | 0.0020666 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 146.7069 | 0.10347 | 0.0020666
139099 | 41679.1396 | 41679.4569 | 1094 | 454 | 267381.1641 | 588.9453 | 0.82349 | 0.0033693 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-09 | 2014 | 2014 | 2014-02-09 | C | 588.9453 | 0.82349 | 0.0033693
139101 | 41679.2368 | 41679.309 | 221 | 101 | 18483 | 183 | 0.056925 | 0.00068065 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-02-09 | 2014 | 2014 | 2014-02-09 | C | 183 | 0.056925 | 0.00068065
139104 | 41678.2868 | 41678.4653 | 406 | 254 | 16461.572 | 64.8093 | 0.050699 | 0.0012504 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 64.8093 | 0.050699 | 0.0012504
139105 | 41678.5236 | 41678.6222 | 2 | 139 | 278 | 2 | 0.0008562 | 6.1597e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 2 | 0.0008562 | 6.1597e-06
139106 | 41678.3778 | 41678.7139 | 50 | 481 | 8916.3884 | 18.5372 | 0.027461 | 0.00015399 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 18.5372 | 0.027461 | 0.00015399
139107 | 41678.5458 | 41678.9007 | 8 | 508 | 1609.4951 | 3.1683 | 0.004957 | 2.4639e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2014-02-08 | 2014 | 2014 | 2014-02-08 | C | 3.1683 | 0.004957 | 2.4639e-05
139108 | 41679.8854 | 41679.9049 | 39 | 25 | 975 | 39 | 0.0030028 | 0.00012011 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-09 | 2014 | 2014 | 2014-02-09 | C | 39 | 0.0030028 | 0.00012011
139112 | 41680.3889 | 41680.4069 | 181 | 23 | 4163 | 181 | 0.012821 | 0.00055745 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | B | 181 | 0.012821 | 0.00055745
139114 | 41680.4014 | 41680.5722 | 85 | 243 | 15320.8537 | 63.0488 | 0.047186 | 0.00026179 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 63.0488 | 0.047186 | 0.00026179
139115 | 41680.4076 | 41680.4667 | 239 | 82 | 13086.2353 | 159.5882 | 0.040304 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 159.5882 | 0.040304 | 0.00073608
139117 | 41680.3542 | 41680.6146 | 20 | 372 | 7440 | 20 | 0.022914 | 6.1597e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | B | 20 | 0.022914 | 6.1597e-05
139122 | 41680.6257 | 41680.6965 | 94 | 99 | 9306 | 94 | 0.028661 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 94 | 0.028661 | 0.00028951
139123 | 41680.0118 | 41680.7174 | 145 | 1013 | 73297.9281 | 72.3573 | 0.22575 | 0.00044658 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 72.3573 | 0.22575 | 0.00044658
139124 | 41680.7361 | 41680.784 | 79 | 66 | 5214 | 79 | 0.016058 | 0.00024331 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 79 | 0.016058 | 0.00024331
139128 | 41680.7979 | 41680.9056 | 38 | 152 | 5776 | 38 | 0.017789 | 0.00011703 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 38 | 0.017789 | 0.00011703
139129 | 41680.4125 | 41680.6007 | 4 | 268 | 1072 | 4 | 0.0033016 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | B | 4 | 0.0033016 | 1.2319e-05
139131 | 41680.441 | 41680.6076 | 26 | 237 | 6162 | 26 | 0.018978 | 8.0076e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-10 | 2014 | 2014 | 2014-02-10 | C | 26 | 0.018978 | 8.0076e-05
139135 | 41681.3542 | 41681.6125 | 33 | 369 | 12177 | 33 | 0.037503 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | B | 33 | 0.037503 | 0.00010163
139136 | 41681.6382 | 41681.6465 | 132 | 9 | 1188 | 132 | 0.0036589 | 0.00040654 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | C | 132 | 0.0036589 | 0.00040654
139137 | 41681.4965 | 41681.5694 | 5 | 102 | 510 | 5 | 0.0015707 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | C | 5 | 0.0015707 | 1.5399e-05
139138 | 41681.3854 | 41681.6701 | 39 | 407 | 15873 | 39 | 0.048886 | 0.00012011 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | B | 39 | 0.048886 | 0.00012011
139139 | 41681.4368 | 41681.5778 | 9 | 200 | 1800 | 9 | 0.0055437 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | B | 9 | 0.0055437 | 2.7719e-05
139140 | 41681.8653 | 41681.9069 | 2493 | 57 | 142101 | 2493 | 0.43765 | 0.007678 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | C | 2493 | 0.43765 | 0.007678
139142 | 41681.9708 | 41681.9792 | 2170 | 9 | 19530 | 2170 | 0.060149 | 0.0066833 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | C | 2170 | 0.060149 | 0.0066833
139144 | 41682.3785 | 41682.4479 | 48 | 97 | 4656 | 48 | 0.01434 | 0.00014783 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-12 | 2014 | 2014 | 2014-02-12 | B | 48 | 0.01434 | 0.00014783
139147 | 41682.3646 | 41682.6347 | 33 | 386 | 12738 | 33 | 0.039231 | 0.00010163 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-12 | 2014 | 2014 | 2014-02-12 | B | 33 | 0.039231 | 0.00010163
139148 | 41682.3854 | 41682.45 | 217 | 90 | 19530 | 217 | 0.060149 | 0.00066833 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-12 | 2014 | 2014 | 2014-02-12 | B | 217 | 0.060149 | 0.00066833
139150 | 41683.1576 | 41683.2083 | 681 | 70 | 45476.0274 | 649.6575 | 0.14006 | 0.0020974 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | C | 649.6575 | 0.14006 | 0.0020974
139151 | 41683.1576 | 41683.2819 | 74 | 176 | 12953.2067 | 73.5978 | 0.039894 | 0.00022791 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | C | 73.5978 | 0.039894 | 0.00022791
139152 | 41683.4153 | 41683.4333 | 183 | 23 | 4209 | 183 | 0.012963 | 0.00056361 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | C | 183 | 0.012963 | 0.00056361
139153 | 41683.3917 | 41683.5306 | 3 | 197 | 591 | 3 | 0.0018202 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | B | 3 | 0.0018202 | 9.2395e-06
139154 | 41683.5 | 41683.5764 | 12 | 107 | 1284 | 12 | 0.0039545 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | B | 12 | 0.0039545 | 3.6958e-05
139157 | 41683.375 | 41683.616 | 42 | 344 | 14448 | 42 | 0.044498 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | B | 42 | 0.044498 | 0.00012935
139160 | 41683.8382 | 41683.8764 | 29 | 52 | 1508 | 29 | 0.0046444 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-13 | 2014 | 2014 | 2014-02-13 | C | 29 | 0.0046444 | 8.9315e-05
139162 | 41684.5417 | 41684.5715 | 6 | 40 | 240 | 6 | 0.00073916 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-14 | 2014 | 2014 | 2014-02-14 | B | 6 | 0.00073916 | 1.8479e-05
139163 | 41684.3993 | 41684.4389 | 7 | 54 | 378 | 7 | 0.0011642 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-14 | 2014 | 2014 | 2014-02-14 | B | 7 | 0.0011642 | 2.1559e-05
139164 | 41684.4722 | 41684.5139 | 10 | 57 | 570 | 10 | 0.0017555 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-14 | 2014 | 2014 | 2014-02-14 | B | 10 | 0.0017555 | 3.0798e-05
139165 | 41684.4056 | 41684.4882 | 4 | 116 | 464 | 4 | 0.001429 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-14 | 2014 | 2014 | 2014-02-14 | B | 4 | 0.001429 | 1.2319e-05
139168 | 41685.2361 | 41685.2549 | 60 | 24 | 1440 | 60 | 0.004435 | 0.00018479 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-15 | 2014 | 2014 | 2014-02-15 | C | 60 | 0.004435 | 0.00018479
139169 | 41685.2951 | 41685.3618 | 83 | 93 | 4657.75 | 50.0833 | 0.014345 | 0.00025563 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-15 | 2014 | 2014 | 2014-02-15 | C | 50.0833 | 0.014345 | 0.00025563
139174 | 41686.1687 | 41686.4347 | 255 | 380 | 24699.0078 | 64.9974 | 0.076069 | 0.00078536 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | C | 64.9974 | 0.076069 | 0.00078536
139176 | 41685.7257 | 41685.7708 | 125 | 62 | 7750 | 125 | 0.023869 | 0.00038498 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-15 | 2014 | 2014 | 2014-02-15 | C | 125 | 0.023869 | 0.00038498
139177 | 41686.3736 | 41686.4069 | 11 | 45 | 495 | 11 | 0.0015245 | 3.3878e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | C | 11 | 0.0015245 | 3.3878e-05
139179 | 41686.3472 | 41686.3972 | 2 | 69 | 138 | 2 | 0.00042502 | 6.1597e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | C | 2 | 0.00042502 | 6.1597e-06
139181 | 41686.3854 | 41686.4618 | 5 | 107 | 535 | 5 | 0.0016477 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | B | 5 | 0.0016477 | 1.5399e-05
139182 | 41686.375 | 41686.5417 | 118 | 237 | 27966 | 118 | 0.086131 | 0.00036342 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | B | 118 | 0.086131 | 0.00036342
139183 | 41685.3854 | 41685.5889 | 109 | 290 | 31610 | 109 | 0.097354 | 0.0003357 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-15 | 2014 | 2014 | 2014-02-15 | B | 109 | 0.097354 | 0.0003357
139185 | 41686.7917 | 41686.8451 | 1 | 74 | 74 | 1 | 0.00022791 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-16 | 2014 | 2014 | 2014-02-16 | C | 1 | 0.00022791 | 3.0798e-06
139186 | 41685.3486 | 41685.5764 | 44 | 325 | 14300 | 44 | 0.044042 | 0.00013551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-15 | 2014 | 2014 | 2014-02-15 | B | 44 | 0.044042 | 0.00013551
139187 | 41687.3854 | 41687.4306 | 4 | 62 | 248 | 4 | 0.0007638 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 4 | 0.0007638 | 1.2319e-05
139188 | 41684.4167 | 41684.5035 | 1 | 122 | 122 | 1 | 0.00037574 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-14 | 2014 | 2014 | 2014-02-14 | B | 1 | 0.00037574 | 3.0798e-06
139189 | 41687.4653 | 41687.5056 | 3 | 55 | 165 | 3 | 0.00050817 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 3 | 0.00050817 | 9.2395e-06
139190 | 41687.5417 | 41687.5972 | 2 | 77 | 154 | 2 | 0.0004743 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 2 | 0.0004743 | 6.1597e-06
139192 | 41687.3438 | 41687.6667 | 73 | 462 | 33726 | 73 | 0.10387 | 0.00022483 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 73 | 0.10387 | 0.00022483
139194 | 41687.4215 | 41687.5729 | 4 | 215 | 860 | 4 | 0.0026487 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 4 | 0.0026487 | 1.2319e-05
139198 | 41687.4375 | 41687.4896 | 8 | 72 | 576 | 8 | 0.001774 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | C | 8 | 0.001774 | 2.4639e-05
139200 | 41687.3542 | 41687.625 | 1 | 387 | 387 | 1 | 0.0011919 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 1 | 0.0011919 | 3.0798e-06
139204 | 41687.3771 | 41687.6729 | 32 | 423 | 13536 | 32 | 0.041689 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | B | 32 | 0.041689 | 9.8555e-05
139207 | 41687.6639 | 41687.7056 | 99 | 57 | 3173 | 55.6667 | 0.0097723 | 0.0003049 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-17 | 2014 | 2014 | 2014-02-17 | C | 55.6667 | 0.0097723 | 0.0003049
139213 | 41688.3306 | 41688.3382 | 417 | 8 | 3336 | 417 | 0.010274 | 0.0012843 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | C | 417 | 0.010274 | 0.0012843
139215 | 41688.3861 | 41688.4264 | 4 | 55 | 220 | 4 | 0.00067757 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | B | 4 | 0.00067757 | 1.2319e-05
139216 | 41688.3951 | 41688.4118 | 2259 | 21 | 26537.875 | 1263.7083 | 0.081732 | 0.0069574 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | C | 1263.7083 | 0.081732 | 0.0069574
139218 | 41688.3646 | 41688.6438 | 1 | 399 | 399 | 1 | 0.0012289 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | B | 1 | 0.0012289 | 3.0798e-06
139220 | 41688.3875 | 41688.5979 | 3 | 300 | 900 | 3 | 0.0027719 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | B | 3 | 0.0027719 | 9.2395e-06
139230 | 41688.3875 | 41688.6361 | 147 | 355 | 52185 | 147 | 0.16072 | 0.00045274 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | B | 147 | 0.16072 | 0.00045274
139231 | 41688.375 | 41688.625 | 42 | 357 | 14994 | 42 | 0.046179 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | B | 42 | 0.046179 | 0.00012935
139232 | 41688.8417 | 41689.1076 | 316 | 380 | 70656.188 | 185.9373 | 0.21761 | 0.00097323 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-18 | 2014 | 2014 | 2014-02-18 | C | 185.9373 | 0.21761 | 0.00097323
139237 | 41689.3646 | 41689.6368 | 32 | 389 | 12448 | 32 | 0.038338 | 9.8555e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 32 | 0.038338 | 9.8555e-05
139238 | 41689.625 | 41689.6854 | 1 | 84 | 84 | 1 | 0.00025871 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | C | 1 | 0.00025871 | 3.0798e-06
139241 | 41689.4917 | 41689.5903 | 55 | 139 | 7645 | 55 | 0.023545 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 55 | 0.023545 | 0.00016939
139242 | 41689.4069 | 41689.6132 | 12 | 294 | 3528 | 12 | 0.010866 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 12 | 0.010866 | 3.6958e-05
139243 | 41689.3854 | 41689.4132 | 3 | 37 | 111 | 3 | 0.00034186 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 3 | 0.00034186 | 9.2395e-06
139244 | 41689.4618 | 41689.5139 | 4 | 72 | 288 | 4 | 0.00088699 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 4 | 0.00088699 | 1.2319e-05
139245 | 41689.4479 | 41689.4882 | 5 | 55 | 275 | 5 | 0.00084696 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 5 | 0.00084696 | 1.5399e-05
139246 | 41689.5458 | 41689.5694 | 5 | 31 | 155 | 5 | 0.00047738 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 5 | 0.00047738 | 1.5399e-05
139247 | 41689.3889 | 41689.4271 | 3 | 52 | 156 | 3 | 0.00048046 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 3 | 0.00048046 | 9.2395e-06
139248 | 41689.3826 | 41689.5868 | 5 | 291 | 1455 | 5 | 0.0044812 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 5 | 0.0044812 | 1.5399e-05
139250 | 41689.9201 | 41689.9965 | 19 | 107 | 2033 | 19 | 0.0062613 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | B | 19 | 0.0062613 | 5.8517e-05
139252 | 41689.9076 | 41689.9437 | 62 | 49 | 3038 | 62 | 0.0093566 | 0.00019095 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | C | 62 | 0.0093566 | 0.00019095
139253 | 41689.6667 | 41689.8604 | 124 | 276 | 1996.3011 | 7.233 | 0.0061483 | 0.0003819 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | C | 7.233 | 0.0061483 | 0.0003819
139255 | 41689.3396 | 41689.5833 | 616 | 348 | 95995.453 | 275.849 | 0.29565 | 0.0018972 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-19 | 2014 | 2014 | 2014-02-19 | C | 275.849 | 0.29565 | 0.0018972
139256 | 41690.4958 | 41690.55 | 423 | 75 | 16376.9231 | 218.359 | 0.050438 | 0.0013028 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | C | 218.359 | 0.050438 | 0.0013028
139258 | 41690.3438 | 41690.6285 | 13 | 407 | 5291 | 13 | 0.016295 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 13 | 0.016295 | 4.0038e-05
139259 | 41690.6736 | 41690.7014 | 520 | 37 | 15170 | 410 | 0.046721 | 0.0016015 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | C | 410 | 0.046721 | 0.0016015
139263 | 41690.5208 | 41690.6146 | 7 | 132 | 924 | 7 | 0.0028458 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 7 | 0.0028458 | 2.1559e-05
139265 | 41690.3854 | 41690.4514 | 6 | 92 | 552 | 6 | 0.0017001 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 6 | 0.0017001 | 1.8479e-05
139268 | 41690.4319 | 41690.4403 | 417 | 9 | 3753 | 417 | 0.011559 | 0.0012843 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | C | 417 | 0.011559 | 0.0012843
139270 | 41690.9618 | 41690.9931 | 225 | 42 | 9450 | 225 | 0.029105 | 0.00069296 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 225 | 0.029105 | 0.00069296
139271 | 41690.866 | 41690.9354 | 407 | 97 | 35795.91 | 369.03 | 0.11025 | 0.0012535 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | C | 369.03 | 0.11025 | 0.0012535
139272 | 41691.0028 | 41691.1083 | 257 | 149 | 21882.4145 | 146.8618 | 0.067394 | 0.00079152 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | C | 146.8618 | 0.067394 | 0.00079152
139273 | 41691.1687 | 41691.2188 | 636 | 69 | 33177.5 | 480.8333 | 0.10218 | 0.0019588 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | C | 480.8333 | 0.10218 | 0.0019588
139274 | 41691.3618 | 41691.5431 | 695 | 258 | 53786.5747 | 208.4751 | 0.16565 | 0.0021405 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | C | 208.4751 | 0.16565 | 0.0021405
139275 | 41691.4757 | 41691.6146 | 1 | 197 | 197 | 1 | 0.00060673 | 3.0798e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | C | 1 | 0.00060673 | 3.0798e-06
139276 | 41681.9708 | 41681.9792 | 154 | 9 | 1386 | 154 | 0.0042687 | 0.0004743 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-02-11 | 2014 | 2014 | 2014-02-11 | C | 154 | 0.0042687 | 0.0004743
139277 | 41690.3854 | 41690.5868 | 10 | 287 | 2870 | 10 | 0.0088391 | 3.0798e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 10 | 0.0088391 | 3.0798e-05
139278 | 41691.3646 | 41691.6222 | 84 | 368 | 30912 | 84 | 0.095204 | 0.00025871 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | B | 84 | 0.095204 | 0.00025871
139279 | 41690.375 | 41690.6285 | 38 | 362 | 13756 | 38 | 0.042366 | 0.00011703 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-20 | 2014 | 2014 | 2014-02-20 | B | 38 | 0.042366 | 0.00011703
139280 | 41691.5431 | 41691.5826 | 61 | 54 | 3294 | 61 | 0.010145 | 0.00018787 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | B | 61 | 0.010145 | 0.00018787
139281 | 41691.3854 | 41691.5639 | 1 | 254 | 254 | 1 | 0.00078228 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | B | 1 | 0.00078228 | 3.0798e-06
139282 | 41691.3542 | 41691.5625 | 42 | 297 | 12474 | 42 | 0.038418 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | B | 42 | 0.038418 | 0.00012935
139284 | 41691.716 | 41691.9236 | 67 | 296 | 12216.1873 | 41.2709 | 0.037624 | 0.00020635 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-21 | 2014 | 2014 | 2014-02-21 | C | 41.2709 | 0.037624 | 0.00020635
139287 | 41692.8618 | 41693.0493 | 326 | 267 | 46630.0667 | 174.6444 | 0.14361 | 0.001004 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-22 | 2014 | 2014 | 2014-02-22 | C | 174.6444 | 0.14361 | 0.001004
139288 | 41693.2174 | 41693.2778 | 66 | 84 | 5318.069 | 63.3103 | 0.016379 | 0.00020327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-23 | 2014 | 2014 | 2014-02-23 | C | 63.3103 | 0.016379 | 0.00020327
139290 | 41692.8847 | 41692.9882 | 604 | 146 | 52216.0671 | 357.6443 | 0.16082 | 0.0018602 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-22 | 2014 | 2014 | 2014-02-22 | C | 357.6443 | 0.16082 | 0.0018602
139291 | 41693.2271 | 41693.2847 | 254 | 80 | 1504.5783 | 18.8072 | 0.0046339 | 0.00078228 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-23 | 2014 | 2014 | 2014-02-23 | C | 18.8072 | 0.0046339 | 0.00078228
139292 | 41662.3542 | 41662.5264 | 1 | 245 | 245 | 1 | 0.00075456 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-01-23 | 2014 | 2014 | 2014-01-23 | B | 1 | 0.00075456 | 3.0798e-06
139294 | 41692.375 | 41692.3993 | 1 | 32 | 32 | 1 | 9.8555e-05 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-22 | 2014 | 2014 | 2014-02-22 | B | 1 | 9.8555e-05 | 3.0798e-06
139295 | 41693.7181 | 41693.8632 | 116 | 206 | 23896 | 116 | 0.073596 | 0.00035726 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-23 | 2014 | 2014 | 2014-02-23 | C | 116 | 0.073596 | 0.00035726
139302 | 41694.4583 | 41694.4722 | 1 | 17 | 17 | 1 | 5.2357e-05 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 1 | 5.2357e-05 | 3.0798e-06
139304 | 41694.4167 | 41694.4306 | 3 | 17 | 51 | 3 | 0.00015707 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 3 | 0.00015707 | 9.2395e-06
139306 | 41694.4375 | 41694.4514 | 1 | 17 | 17 | 1 | 5.2357e-05 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 1 | 5.2357e-05 | 3.0798e-06
139308 | 41694.3854 | 41694.4965 | 8 | 157 | 1256 | 8 | 0.0038683 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 8 | 0.0038683 | 2.4639e-05
139310 | 41694.5625 | 41694.5972 | 9 | 47 | 423 | 9 | 0.0013028 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 9 | 0.0013028 | 2.7719e-05
139311 | 41694.3875 | 41694.6951 | 64 | 440 | 28160 | 64 | 0.086728 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 64 | 0.086728 | 0.00019711
139313 | 41694.3819 | 41694.4917 | 2 | 155 | 310 | 2 | 0.00095475 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 2 | 0.00095475 | 6.1597e-06
139317 | 41694.4167 | 41694.5139 | 4 | 137 | 548 | 4 | 0.0016878 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 4 | 0.0016878 | 1.2319e-05
139318 | 41694.3889 | 41694.4299 | 32 | 56 | 1792 | 32 | 0.0055191 | 9.8555e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | C | 32 | 0.0055191 | 9.8555e-05
139319 | 41694.4417 | 41694.5625 | 1212 | 171 | 26139.4138 | 152.8621 | 0.080505 | 0.0037328 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | C | 152.8621 | 0.080505 | 0.0037328
139323 | 41694.309 | 41694.734 | 75 | 609 | 18685.951 | 30.683 | 0.05755 | 0.00023099 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | C | 30.683 | 0.05755 | 0.00023099
139329 | 41694.3681 | 41694.6785 | 2 | 444 | 888 | 2 | 0.0027349 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 2 | 0.0027349 | 6.1597e-06
139330 | 41694.7271 | 41694.7799 | 23 | 73 | 1537.8026 | 21.0658 | 0.0047362 | 7.0836e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | C | 21.0658 | 0.0047362 | 7.0836e-05
139331 | 41694.6611 | 41694.8806 | 77 | 313 | 24101 | 77 | 0.074227 | 0.00023715 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | C | 77 | 0.074227 | 0.00023715
139338 | 41695.3924 | 41695.5021 | 26 | 155 | 4030 | 26 | 0.012412 | 8.0076e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 26 | 0.012412 | 8.0076e-05
139339 | 41695.375 | 41695.5174 | 160 | 202 | 32320 | 160 | 0.09954 | 0.00049277 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 160 | 0.09954 | 0.00049277
139341 | 41695.3993 | 41695.4757 | 1 | 107 | 107 | 1 | 0.00032954 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 1 | 0.00032954 | 3.0798e-06
139345 | 41695.3958 | 41695.4757 | 24 | 112 | 2688 | 24 | 0.0082786 | 7.3916e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 24 | 0.0082786 | 7.3916e-05
139347 | 41695.3438 | 41695.5708 | 13 | 324 | 4212 | 13 | 0.012972 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 13 | 0.012972 | 4.0038e-05
139349 | 41695.375 | 41695.5938 | 108 | 312 | 33696 | 108 | 0.10378 | 0.00033262 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 108 | 0.10378 | 0.00033262
139353 | 41695.3854 | 41695.6521 | 15 | 381 | 5715 | 15 | 0.017601 | 4.6198e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 15 | 0.017601 | 4.6198e-05
139355 | 41695.3333 | 41695.6729 | 64 | 486 | 31104 | 64 | 0.095795 | 0.00019711 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 64 | 0.095795 | 0.00019711
139360 | 41695.375 | 41695.6611 | 373 | 409 | 45760.3495 | 111.8835 | 0.14093 | 0.0011488 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 111.8835 | 0.14093 | 0.0011488
139363 | 41695.6528 | 41695.6562 | 5 | 2 | 10 | 5 | 3.0798e-05 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | C | 5 | 3.0798e-05 | 1.5399e-05
139366 | 41695.7688 | 41695.8125 | 34 | 60 | 2040 | 34 | 0.0062829 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | C | 34 | 0.0062829 | 0.00010471
139370 | 41696.3757 | 41696.4486 | 257 | 102 | 15813.8857 | 155.0381 | 0.048704 | 0.00079152 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 155.0381 | 0.048704 | 0.00079152
139372 | 41696.4722 | 41696.5958 | 7 | 175 | 1225 | 7 | 0.0037728 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 7 | 0.0037728 | 2.1559e-05
139375 | 41696.3681 | 41696.5799 | 71 | 302 | 21442 | 71 | 0.066038 | 0.00021867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 71 | 0.066038 | 0.00021867
139377 | 41696.3854 | 41696.4167 | 59 | 42 | 2478 | 59 | 0.0076318 | 0.00018171 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 59 | 0.0076318 | 0.00018171
139379 | 41696.3854 | 41696.6319 | 9 | 352 | 3168 | 9 | 0.0097569 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 9 | 0.0097569 | 2.7719e-05
139380 | 41696.5472 | 41696.5708 | 178 | 31 | 5518 | 178 | 0.016995 | 0.00054821 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 178 | 0.016995 | 0.00054821
139382 | 41696.4069 | 41696.45 | 5 | 59 | 295 | 5 | 0.00090855 | 1.5399e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 5 | 0.00090855 | 1.5399e-05
139386 | 41696.3653 | 41696.6236 | 236 | 369 | 87084 | 236 | 0.2682 | 0.00072684 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 236 | 0.2682 | 0.00072684
139389 | 41696.375 | 41696.6667 | 66 | 417 | 27522 | 66 | 0.084763 | 0.00020327 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 66 | 0.084763 | 0.00020327
139391 | 41696.3438 | 41696.6243 | 34 | 401 | 13634 | 34 | 0.041991 | 0.00010471 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 34 | 0.041991 | 0.00010471
139393 | 41695.3549 | 41695.6493 | 2 | 421 | 842 | 2 | 0.0025932 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-25 | 2014 | 2014 | 2014-02-25 | B | 2 | 0.0025932 | 6.1597e-06
139395 | 41696.5208 | 41696.5625 | 12 | 57 | 684 | 12 | 0.0021066 | 3.6958e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 12 | 0.0021066 | 3.6958e-05
139396 | 41696.7347 | 41696.8194 | 6 | 119 | 714 | 6 | 0.002199 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 6 | 0.002199 | 1.8479e-05
139397 | 41696.7271 | 41696.8319 | 9 | 148 | 1332 | 9 | 0.0041023 | 2.7719e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 9 | 0.0041023 | 2.7719e-05
139400 | 41696.8826 | 41697.0479 | 111 | 235 | 26085 | 111 | 0.080338 | 0.00034186 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 111 | 0.080338 | 0.00034186
139401 | 41696.8826 | 41697.0104 | 833 | 181 | 44241.712 | 244.4293 | 0.13626 | 0.0025655 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | C | 244.4293 | 0.13626 | 0.0025655
139402 | 41694.375 | 41694.5 | 8 | 177 | 1416 | 8 | 0.0043611 | 2.4639e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-24 | 2014 | 2014 | 2014-02-24 | B | 8 | 0.0043611 | 2.4639e-05
139403 | 41696.3854 | 41696.4563 | 3 | 99 | 297 | 3 | 0.00091471 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-26 | 2014 | 2014 | 2014-02-26 | B | 3 | 0.00091471 | 9.2395e-06
139404 | 41697.3958 | 41697.4493 | 4 | 74 | 296 | 4 | 0.00091163 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 4 | 0.00091163 | 1.2319e-05
139407 | 41697.4465 | 41697.5229 | 36 | 107 | 3852 | 36 | 0.011864 | 0.00011087 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 36 | 0.011864 | 0.00011087
139409 | 41697.3535 | 41697.6236 | 12 | 386 | 4632 | 12 | 0.014266 | 3.6958e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | C | 12 | 0.014266 | 3.6958e-05
139411 | 41698.3521 | 41698.4382 | 1719 | 121 | 82882.0726 | 684.9758 | 0.25526 | 0.0052942 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 684.9758 | 0.25526 | 0.0052942
139413 | 41698.4479 | 41698.5278 | 14 | 112 | 1568 | 14 | 0.0048292 | 4.3118e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 14 | 0.0048292 | 4.3118e-05
139414 | 41698.4431 | 41698.6944 | 414 | 359 | 20464.9834 | 57.0055 | 0.063029 | 0.0012751 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 57.0055 | 0.063029 | 0.0012751
139415 | 41698.3958 | 41698.4819 | 133 | 121 | 16093 | 133 | 0.049564 | 0.00040962 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | B | 133 | 0.049564 | 0.00040962
139416 | 41698.375 | 41698.5 | 7 | 177 | 1239 | 7 | 0.0038159 | 2.1559e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | B | 7 | 0.0038159 | 2.1559e-05
139417 | 41698.375 | 41698.6215 | 11 | 352 | 3872 | 11 | 0.011925 | 3.3878e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | B | 11 | 0.011925 | 3.3878e-05
139419 | 41698.6562 | 41698.8021 | 5 | 207 | 1035 | 5 | 0.0031876 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 5 | 0.0031876 | 1.5399e-05
139420 | 41698.8056 | 41698.8215 | 6 | 20 | 120 | 6 | 0.00036958 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 6 | 0.00036958 | 1.8479e-05
139423 | 41699.3965 | 41699.4854 | 903 | 125 | 16613.2812 | 132.9062 | 0.051166 | 0.0027811 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-01 | 2014 | 2014 | 2014-03-01 | C | 132.9062 | 0.051166 | 0.0027811
139425 | 41699.5833 | 41699.6764 | 17 | 131 | 2227 | 17 | 0.0068588 | 5.2357e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-01 | 2014 | 2014 | 2014-03-01 | B | 17 | 0.0068588 | 5.2357e-05
139426 | 41697.3958 | 41697.5868 | 42 | 272 | 11424 | 42 | 0.035184 | 0.00012935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 42 | 0.035184 | 0.00012935
139427 | 41697.5708 | 41697.6028 | 1 | 43 | 43 | 1 | 0.00013243 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 1 | 0.00013243 | 3.0798e-06
139429 | 41697.3542 | 41697.5694 | 78 | 307 | 23946 | 78 | 0.07375 | 0.00024023 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 78 | 0.07375 | 0.00024023
139430 | 41698.3646 | 41698.5542 | 78 | 270 | 21060 | 78 | 0.064861 | 0.00024023 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | B | 78 | 0.064861 | 0.00024023
139432 | 41698.7417 | 41698.784 | 39 | 58 | 2262 | 39 | 0.0069666 | 0.00012011 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 39 | 0.0069666 | 0.00012011
139433 | 41700.2292 | 41700.3993 | 13 | 242 | 3146 | 13 | 0.0096892 | 4.0038e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-02 | 2014 | 2014 | 2014-03-02 | C | 13 | 0.0096892 | 4.0038e-05
139434 | 41700.3319 | 41700.341 | 417 | 10 | 3992.3077 | 399.2308 | 0.012296 | 0.0012843 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-02 | 2014 | 2014 | 2014-03-02 | C | 399.2308 | 0.012296 | 0.0012843
139435 | 41698.4431 | 41698.4688 | 151 | 34 | 5134 | 151 | 0.015812 | 0.00046506 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 151 | 0.015812 | 0.00046506
139438 | 41699.8021 | 41699.8125 | 34 | 12 | 408 | 34 | 0.0012566 | 0.00010471 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-01 | 2014 | 2014 | 2014-03-01 | C | 34 | 0.0012566 | 0.00010471
139440 | 41701.3785 | 41701.3889 | 3 | 12 | 36 | 3 | 0.00011087 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 3 | 0.00011087 | 9.2395e-06
139442 | 41701.3972 | 41701.4104 | 239 | 16 | 3824 | 239 | 0.011777 | 0.00073608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 239 | 0.011777 | 0.00073608
139443 | 41701.3542 | 41701.5 | 4 | 207 | 828 | 4 | 0.0025501 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | B | 4 | 0.0025501 | 1.2319e-05
139444 | 41701.4354 | 41701.4715 | 220 | 49 | 7015.4808 | 143.1731 | 0.021607 | 0.00067757 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 143.1731 | 0.021607 | 0.00067757
139445 | 41698.7042 | 41698.7986 | 366 | 133 | 23118.5294 | 173.8235 | 0.071201 | 0.0011272 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 173.8235 | 0.071201 | 0.0011272
139446 | 41698.7375 | 41698.8472 | 681 | 155 | 49313.5443 | 318.1519 | 0.15188 | 0.0020974 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-02-28 | 2014 | 2014 | 2014-02-28 | C | 318.1519 | 0.15188 | 0.0020974
139447 | 41701.3792 | 41701.684 | 678 | 436 | 33150.8975 | 76.0342 | 0.1021 | 0.0020881 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 76.0342 | 0.1021 | 0.0020881
139450 | 41701.5938 | 41701.6076 | 49 | 17 | 833 | 49 | 0.0025655 | 0.00015091 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 49 | 0.0025655 | 0.00015091
139451 | 41701.6278 | 41701.6375 | 8 | 11 | 88 | 8 | 0.00027103 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 8 | 0.00027103 | 2.4639e-05
139453 | 41701.3958 | 41701.5674 | 2 | 244 | 488 | 2 | 0.001503 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | B | 2 | 0.001503 | 6.1597e-06
139455 | 41697.375 | 41697.6368 | 155 | 374 | 57970 | 155 | 0.17854 | 0.00047738 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-02-27 | 2014 | 2014 | 2014-02-27 | B | 155 | 0.17854 | 0.00047738
139456 | 41701.3826 | 41701.6736 | 6 | 416 | 2496 | 6 | 0.0076873 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | B | 6 | 0.0076873 | 1.8479e-05
139458 | 41701.7819 | 41701.8326 | 2051 | 70 | 126710.5479 | 1810.1507 | 0.39025 | 0.0063168 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-03 | 2014 | 2014 | 2014-03-03 | C | 1810.1507 | 0.39025 | 0.0063168
139465 | 41702.3889 | 41702.434 | 3 | 62 | 186 | 3 | 0.00057285 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 3 | 0.00057285 | 9.2395e-06
139466 | 41702.3229 | 41702.4799 | 2 | 223 | 446 | 2 | 0.0013736 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 2 | 0.0013736 | 6.1597e-06
139468 | 41702.375 | 41702.4861 | 13 | 157 | 2041 | 13 | 0.006286 | 4.0038e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 13 | 0.006286 | 4.0038e-05
139474 | 41702.3958 | 41702.5757 | 18 | 256 | 4608 | 18 | 0.014192 | 5.5437e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 18 | 0.014192 | 5.5437e-05
139475 | 41699.375 | 41700.4319 | 1 | 1519 | 1519 | 1 | 0.0046783 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-01 | 2014 | 2014 | 2014-03-01 | C | 1 | 0.0046783 | 3.0798e-06
139476 | 41702.5028 | 41702.6208 | 344 | 167 | 18428.9412 | 110.3529 | 0.056758 | 0.0010595 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | C | 110.3529 | 0.056758 | 0.0010595
139479 | 41702.375 | 41702.6354 | 85 | 372 | 31620 | 85 | 0.097385 | 0.00026179 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 85 | 0.097385 | 0.00026179
139481 | 41702.3556 | 41702.6417 | 6 | 409 | 2454 | 6 | 0.0075579 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | B | 6 | 0.0075579 | 1.8479e-05
139484 | 41702.9299 | 41702.9403 | 231 | 12 | 2772 | 231 | 0.0085373 | 0.00071144 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | C | 231 | 0.0085373 | 0.00071144
139485 | 41702.9299 | 41702.9417 | 156 | 14 | 2132.9412 | 152.3529 | 0.0065691 | 0.00048046 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | C | 152.3529 | 0.0065691 | 0.00048046
139486 | 41703.0021 | 41703.0597 | 207 | 80 | 12460.7229 | 155.759 | 0.038377 | 0.00063753 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 155.759 | 0.038377 | 0.00063753
139487 | 41703.0563 | 41703.4597 | 94 | 578 | 33908.0069 | 58.6644 | 0.10443 | 0.00028951 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 58.6644 | 0.10443 | 0.00028951
139488 | 41702.9875 | 41703.1312 | 286 | 204 | 16282.5507 | 79.8164 | 0.050148 | 0.00088083 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | C | 79.8164 | 0.050148 | 0.00088083
139490 | 41702.5028 | 41702.5132 | 170 | 12 | 2040 | 170 | 0.0062829 | 0.00052357 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-04 | 2014 | 2014 | 2014-03-04 | C | 170 | 0.0062829 | 0.00052357
139493 | 41703.2618 | 41703.3486 | 254 | 122 | 16752.064 | 137.312 | 0.051594 | 0.00078228 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 137.312 | 0.051594 | 0.00078228
139494 | 41703.2792 | 41703.4132 | 373 | 190 | 38515.8549 | 202.715 | 0.11862 | 0.0011488 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 202.715 | 0.11862 | 0.0011488
139495 | 41703.1549 | 41703.3785 | 298 | 319 | 23450.4627 | 73.5124 | 0.072224 | 0.00091779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 73.5124 | 0.072224 | 0.00091779
139496 | 41703.2951 | 41703.4257 | 131 | 185 | 23514.6809 | 127.1064 | 0.072421 | 0.00040346 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 127.1064 | 0.072421 | 0.00040346
139497 | 41703.4847 | 41703.5069 | 10 | 29 | 290 | 10 | 0.00089315 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 10 | 0.00089315 | 3.0798e-05
139499 | 41703.3049 | 41703.3083 | 298 | 2 | 596 | 298 | 0.0018356 | 0.00091779 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 298 | 0.0018356 | 0.00091779
139500 | 41703.3854 | 41703.5854 | 114 | 285 | 32490 | 114 | 0.10006 | 0.0003511 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | B | 114 | 0.10006 | 0.0003511
139501 | 41703.5729 | 41703.6382 | 2 | 91 | 182 | 2 | 0.00056053 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 2 | 0.00056053 | 6.1597e-06
139502 | 41703.6146 | 41703.6771 | 857 | 87 | 40386.3667 | 464.2111 | 0.12438 | 0.0026394 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 464.2111 | 0.12438 | 0.0026394
139503 | 41703.25 | 41703.6694 | 116 | 601 | 69716 | 116 | 0.21471 | 0.00035726 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 116 | 0.21471 | 0.00035726
139504 | 41703.0528 | 41703.1979 | 676 | 206 | 99073.1866 | 480.9378 | 0.30513 | 0.002082 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 480.9378 | 0.30513 | 0.002082
139505 | 41703.6028 | 41703.6479 | 126 | 62 | 7812 | 126 | 0.02406 | 0.00038806 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 126 | 0.02406 | 0.00038806
139507 | 41703.5208 | 41703.5632 | 70 | 58 | 4060 | 70 | 0.012504 | 0.00021559 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | B | 70 | 0.012504 | 0.00021559
139508 | 41703.3944 | 41703.5931 | 19 | 283 | 5377 | 19 | 0.01656 | 5.8517e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | B | 19 | 0.01656 | 5.8517e-05
139510 | 41703.7708 | 41703.8313 | 3 | 84 | 252 | 3 | 0.00077612 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 3 | 0.00077612 | 9.2395e-06
139511 | 41703.6993 | 41703.8931 | 121 | 276 | 26500.9462 | 96.0179 | 0.081619 | 0.00037266 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 96.0179 | 0.081619 | 0.00037266
139513 | 41703.7701 | 41703.8542 | 106 | 118 | 12297.3554 | 104.2149 | 0.037874 | 0.00032646 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 104.2149 | 0.037874 | 0.00032646
139514 | 41703.966 | 41704.0326 | 121 | 93 | 8599.5938 | 92.4688 | 0.026485 | 0.00037266 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 92.4688 | 0.026485 | 0.00037266
139517 | 41704.0604 | 41704.2181 | 121 | 224 | 20176.7753 | 90.0749 | 0.062141 | 0.00037266 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | C | 90.0749 | 0.062141 | 0.00037266
139519 | 41703.3972 | 41703.4424 | 1 | 62 | 62 | 1 | 0.00019095 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | B | 1 | 0.00019095 | 3.0798e-06
139522 | 41704.4028 | 41704.6125 | 29 | 299 | 8671 | 29 | 0.026705 | 8.9315e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | B | 29 | 0.026705 | 8.9315e-05
139523 | 41703.7215 | 41704.5104 | 75 | 1133 | 27612.8856 | 24.3715 | 0.085043 | 0.00023099 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-05 | 2014 | 2014 | 2014-03-05 | C | 24.3715 | 0.085043 | 0.00023099
139524 | 41704.3542 | 41704.5451 | 6 | 272 | 1632 | 6 | 0.0050263 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | B | 6 | 0.0050263 | 1.8479e-05
139527 | 41704.3646 | 41704.5729 | 55 | 297 | 16335 | 55 | 0.050309 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | B | 55 | 0.050309 | 0.00016939
139529 | 41704.3542 | 41704.7174 | 307 | 520 | 42022.5621 | 80.8126 | 0.12942 | 0.00094551 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | B | 80.8126 | 0.12942 | 0.00094551
139532 | 41705.5833 | 41705.6333 | 25 | 69 | 1725 | 25 | 0.0053127 | 7.6996e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | B | 25 | 0.0053127 | 7.6996e-05
139536 | 41705.4583 | 41705.4958 | 4 | 51 | 204 | 4 | 0.00062829 | 1.2319e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | B | 4 | 0.00062829 | 1.2319e-05
139537 | 41705.5625 | 41705.5944 | 2 | 43 | 86 | 2 | 0.00026487 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | B | 2 | 0.00026487 | 6.1597e-06
139543 | 41704.525 | 41704.7778 | 37 | 361 | 7838.8571 | 21.7143 | 0.024142 | 0.00011395 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-06 | 2014 | 2014 | 2014-03-06 | C | 21.7143 | 0.024142 | 0.00011395
139545 | 41706.7917 | 41706.8333 | 22 | 57 | 1254 | 22 | 0.0038621 | 6.7757e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-08 | 2014 | 2014 | 2014-03-08 | C | 22 | 0.0038621 | 6.7757e-05
139546 | 41705.7049 | 41705.7396 | 54 | 47 | 2538 | 54 | 0.0078166 | 0.00016631 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | C | 54 | 0.0078166 | 0.00016631
139549 | 41707.0111 | 41707.1007 | 162 | 126 | 13715.4419 | 108.8527 | 0.042241 | 0.00049893 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 108.8527 | 0.042241 | 0.00049893
139550 | 41707.0674 | 41707.0813 | 87 | 17 | 1479 | 87 | 0.0045551 | 0.00026795 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 87 | 0.0045551 | 0.00026795
139551 | 41707.2861 | 41707.366 | 276 | 112 | 9271.6522 | 82.7826 | 0.028555 | 0.00085004 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 82.7826 | 0.028555 | 0.00085004
139552 | 41707.4354 | 41707.4472 | 1336 | 14 | 16839.5294 | 1202.8235 | 0.051863 | 0.0041147 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 1202.8235 | 0.051863 | 0.0041147
139553 | 41706.4458 | 41706.5653 | 182 | 169 | 17795.1105 | 105.2965 | 0.054806 | 0.00056053 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-08 | 2014 | 2014 | 2014-03-08 | C | 105.2965 | 0.054806 | 0.00056053
139555 | 41705.3583 | 41705.616 | 3 | 368 | 1104 | 3 | 0.0034001 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | B | 3 | 0.0034001 | 9.2395e-06
139556 | 41706.3542 | 41706.5146 | 124 | 228 | 28272 | 124 | 0.087073 | 0.0003819 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-08 | 2014 | 2014 | 2014-03-08 | B | 124 | 0.087073 | 0.0003819
139557 | 41706.4118 | 41706.5451 | 30 | 189 | 5640.4688 | 29.8438 | 0.017372 | 9.2395e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-08 | 2014 | 2014 | 2014-03-08 | B | 29.8438 | 0.017372 | 9.2395e-05
139558 | 41705.3764 | 41705.4771 | 3 | 142 | 423.0621 | 2.9793 | 0.001303 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-07 | 2014 | 2014 | 2014-03-07 | B | 2.9793 | 0.001303 | 9.2395e-06
139559 | 41706.6875 | 41706.7625 | 673 | 105 | 26551.3889 | 252.8704 | 0.081774 | 0.0020727 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-08 | 2014 | 2014 | 2014-03-08 | C | 252.8704 | 0.081774 | 0.0020727
139561 | 41707.7653 | 41707.7799 | 19 | 18 | 342 | 19 | 0.0010533 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 19 | 0.0010533 | 5.8517e-05
139563 | 41708.4583 | 41708.5625 | 9 | 147 | 1323 | 9 | 0.0040746 | 2.7719e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-10 | 2014 | 2014 | 2014-03-10 | B | 9 | 0.0040746 | 2.7719e-05
139565 | 41708.2382 | 41708.6917 | 58 | 650 | 23235.758 | 35.7473 | 0.071562 | 0.00017863 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-10 | 2014 | 2014 | 2014-03-10 | C | 35.7473 | 0.071562 | 0.00017863
139569 | 41708.9167 | 41708.9674 | 160 | 70 | 11200 | 160 | 0.034494 | 0.00049277 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-10 | 2014 | 2014 | 2014-03-10 | B | 160 | 0.034494 | 0.00049277
139571 | 41709.1278 | 41709.1396 | 261 | 14 | 3654 | 261 | 0.011254 | 0.00080384 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | C | 261 | 0.011254 | 0.00080384
139572 | 41707.6611 | 41707.7396 | 2 | 110 | 220 | 2 | 0.00067757 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 2 | 0.00067757 | 6.1597e-06
139573 | 41707.4354 | 41707.4431 | 2 | 8 | 16 | 2 | 4.9277e-05 | 6.1597e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-09 | 2014 | 2014 | 2014-03-09 | C | 2 | 4.9277e-05 | 6.1597e-06
139578 | 41709.0104 | 41709.0563 | 449 | 63 | 28287 | 449 | 0.087119 | 0.0013828 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | B | 449 | 0.087119 | 0.0013828
139580 | 41709.4181 | 41709.6368 | 51 | 312 | 15912 | 51 | 0.049006 | 0.00015707 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | B | 51 | 0.049006 | 0.00015707
139582 | 41709.4181 | 41709.4583 | 6 | 55 | 330 | 6 | 0.0010163 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | B | 6 | 0.0010163 | 1.8479e-05
139586 | 41709.4271 | 41709.609 | 3 | 259 | 777 | 3 | 0.002393 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | B | 3 | 0.002393 | 9.2395e-06
139590 | 41709.384 | 41709.6868 | 55 | 433 | 23815 | 55 | 0.073346 | 0.00016939 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | B | 55 | 0.073346 | 0.00016939
139592 | 41709.7917 | 41709.9028 | 4 | 157 | 628 | 4 | 0.0019341 | 1.2319e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-11 | 2014 | 2014 | 2014-03-11 | C | 4 | 0.0019341 | 1.2319e-05
139595 | 41710.1361 | 41710.2882 | 323 | 216 | 47041.6438 | 217.7854 | 0.14488 | 0.00099479 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | C | 217.7854 | 0.14488 | 0.00099479
139597 | 41710.3708 | 41710.4257 | 6 | 76 | 456 | 6 | 0.0014044 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | B | 6 | 0.0014044 | 1.8479e-05
139599 | 41710.5208 | 41710.5486 | 3 | 37 | 111 | 3 | 0.00034186 | 9.2395e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | B | 3 | 0.00034186 | 9.2395e-06
139601 | 41710.4306 | 41710.5799 | 1 | 212 | 212 | 1 | 0.00065293 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | B | 1 | 0.00065293 | 3.0798e-06
139605 | 41710.5208 | 41710.6056 | 141 | 119 | 16779 | 141 | 0.051677 | 0.00043426 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | B | 141 | 0.051677 | 0.00043426
139608 | 41710.3854 | 41710.4583 | 6 | 102 | 612 | 6 | 0.0018849 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-12 | 2014 | 2014 | 2014-03-12 | B | 6 | 0.0018849 | 1.8479e-05
139612 | 41711.3514 | 41711.4021 | 20 | 70 | 1400 | 20 | 0.0043118 | 6.1597e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | C | 20 | 0.0043118 | 6.1597e-05
139614 | 41711.4437 | 41711.466 | 766 | 29 | 22214 | 766 | 0.068416 | 0.0023592 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | C | 766 | 0.068416 | 0.0023592
139616 | 41711.4375 | 41711.5625 | 65 | 177 | 11505 | 65 | 0.035434 | 0.00020019 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | B | 65 | 0.035434 | 0.00020019
139617 | 41711.3576 | 41711.6347 | 69 | 396 | 27324 | 69 | 0.084154 | 0.00021251 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | B | 69 | 0.084154 | 0.00021251
139618 | 41711.5243 | 41711.6521 | 6 | 181 | 1086 | 6 | 0.0033447 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | C | 6 | 0.0033447 | 1.8479e-05
139619 | 41711.4132 | 41711.5097 | 153 | 136 | 15018.705 | 110.4317 | 0.046255 | 0.00047122 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-13 | 2014 | 2014 | 2014-03-13 | C | 110.4317 | 0.046255 | 0.00047122
139623 | 41712.6104 | 41712.641 | 75 | 41 | 3075 | 75 | 0.0094705 | 0.00023099 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-14 | 2014 | 2014 | 2014-03-14 | C | 75 | 0.0094705 | 0.00023099
139629 | 41713.3667 | 41713.3806 | 262 | 17 | 4454 | 262 | 0.013718 | 0.00080692 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 262 | 0.013718 | 0.00080692
139631 | 41713.3396 | 41713.3889 | 64 | 68 | 4352 | 64 | 0.013403 | 0.00019711 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 64 | 0.013403 | 0.00019711
139632 | 41713.3708 | 41713.3785 | 1788 | 8 | 14304 | 1788 | 0.044054 | 0.0055068 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 1788 | 0.044054 | 0.0055068
139633 | 41713.4861 | 41713.5729 | 292 | 122 | 29566.944 | 242.352 | 0.091062 | 0.00089931 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 242.352 | 0.091062 | 0.00089931
139634 | 41713.4903 | 41713.5958 | 239 | 149 | 28911.8816 | 194.0395 | 0.089044 | 0.00073608 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 194.0395 | 0.089044 | 0.00073608
139642 | 41713.4563 | 41713.5028 | 410 | 64 | 18011.7015 | 281.4328 | 0.055473 | 0.0012627 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 281.4328 | 0.055473 | 0.0012627
139643 | 41713.1458 | 41713.4556 | 2651 | 443 | 899043.6682 | 2029.4439 | 2.7689 | 0.0081647 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 2029.4439 | 2.7689 | 0.0081647
139644 | 41713.5833 | 41713.6854 | 401 | 144 | 38896.6531 | 270.1156 | 0.1198 | 0.001235 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 270.1156 | 0.1198 | 0.001235
139645 | 41713.5333 | 41713.5986 | 714 | 91 | 40659.5745 | 446.8085 | 0.12523 | 0.002199 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 446.8085 | 0.12523 | 0.002199
139646 | 41713.6403 | 41713.75 | 238 | 155 | 30196.5506 | 194.8165 | 0.093001 | 0.000733 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 194.8165 | 0.093001 | 0.000733
139648 | 41713.7639 | 41713.7917 | 240 | 37 | 6911.6 | 186.8 | 0.021287 | 0.00073916 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 186.8 | 0.021287 | 0.00073916
139649 | 41713.3903 | 41713.4965 | 170 | 150 | 18343.1373 | 122.2876 | 0.056494 | 0.00052357 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 122.2876 | 0.056494 | 0.00052357
139650 | 41713.6771 | 41713.7146 | 15 | 51 | 765 | 15 | 0.0023561 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 15 | 0.0023561 | 4.6198e-05
139651 | 41713.475 | 41713.5847 | 9 | 155 | 1395 | 9 | 0.0042964 | 2.7719e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 9 | 0.0042964 | 2.7719e-05
139654 | 41713.6493 | 41713.8736 | 576 | 320 | 54056.2229 | 168.9257 | 0.16648 | 0.001774 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 168.9257 | 0.16648 | 0.001774
139655 | 41713.5583 | 41714.6181 | 304 | 1523 | 30235.4423 | 19.8526 | 0.09312 | 0.00093627 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 19.8526 | 0.09312 | 0.00093627
139657 | 41713.7236 | 41713.9965 | 77 | 390 | 12025.4962 | 30.8346 | 0.037037 | 0.00023715 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 30.8346 | 0.037037 | 0.00023715
139661 | 41714.316 | 41714.3438 | 6 | 37 | 222 | 6 | 0.00068372 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 6 | 0.00068372 | 1.8479e-05
139662 | 41713.4493 | 41713.8097 | 414 | 516 | 48056.6012 | 93.1329 | 0.14801 | 0.0012751 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 93.1329 | 0.14801 | 0.0012751
139663 | 41713.4722 | 41713.8042 | 282 | 475 | 33682.2699 | 70.91 | 0.10374 | 0.00086852 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 70.91 | 0.10374 | 0.00086852
139664 | 41713.9396 | 41714.0569 | 11 | 166 | 1826 | 11 | 0.0056238 | 3.3878e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 11 | 0.0056238 | 3.3878e-05
139665 | 41713.9062 | 41713.9653 | 24 | 82 | 1968 | 24 | 0.0060611 | 7.3916e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 24 | 0.0060611 | 7.3916e-05
139666 | 41713.5014 | 41713.6069 | 526 | 149 | 29104.9934 | 195.3355 | 0.089639 | 0.00162 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 195.3355 | 0.089639 | 0.00162
139667 | 41713.8028 | 41713.8264 | 108 | 31 | 3215.7941 | 103.7353 | 0.0099041 | 0.00033262 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 103.7353 | 0.0099041 | 0.00033262
139668 | 41713.9361 | 41713.9708 | 35 | 47 | 1645 | 35 | 0.0050663 | 0.00010779 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 35 | 0.0050663 | 0.00010779
139670 | 41714.0174 | 41714.0444 | 457 | 36 | 16452 | 457 | 0.05067 | 0.0014075 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 457 | 0.05067 | 0.0014075
139671 | 41713.8403 | 41713.8694 | 50 | 39 | 1657.5 | 42.5 | 0.0051048 | 0.00015399 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 42.5 | 0.0051048 | 0.00015399
139672 | 41713.8313 | 41714.6111 | 3 | 1120 | 3360 | 3 | 0.010348 | 9.2395e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 3 | 0.010348 | 9.2395e-06
139673 | 41713.6069 | 41713.6097 | 325 | 1 | 325 | 325 | 0.0010009 | 0.0010009 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 325 | 0.0010009 | 0.0010009
139674 | 41713.7937 | 41713.8229 | 173 | 39 | 6747 | 173 | 0.02078 | 0.00053281 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 173 | 0.02078 | 0.00053281
139675 | 41713.9882 | 41714.1986 | 517 | 300 | 91749.505 | 305.8317 | 0.28257 | 0.0015923 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 305.8317 | 0.28257 | 0.0015923
139676 | 41713.834 | 41713.9118 | 153 | 109 | 16253.6518 | 149.1161 | 0.050059 | 0.00047122 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 149.1161 | 0.050059 | 0.00047122
139677 | 41713.6146 | 41713.6653 | 44 | 70 | 3080 | 44 | 0.0094859 | 0.00013551 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 44 | 0.0094859 | 0.00013551
139678 | 41713.559 | 41713.8056 | 325 | 352 | 65603.8761 | 186.3746 | 0.20205 | 0.0010009 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 186.3746 | 0.20205 | 0.0010009
139679 | 41714.1208 | 41714.125 | 2 | 3 | 6 | 2 | 1.8479e-05 | 6.1597e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 2 | 1.8479e-05 | 6.1597e-06
139680 | 41714.0549 | 41714.1285 | 1367 | 103 | 139171.4623 | 1351.1792 | 0.42863 | 0.0042101 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 1351.1792 | 0.42863 | 0.0042101
139681 | 41714.116 | 41714.4833 | 41 | 526 | 21566 | 41 | 0.06642 | 0.00012627 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 41 | 0.06642 | 0.00012627
139682 | 41713.9201 | 41714.4826 | 94 | 807 | 75858 | 94 | 0.23363 | 0.00028951 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 94 | 0.23363 | 0.00028951
139683 | 41713.7812 | 41714.3986 | 272 | 886 | 67754.5827 | 76.4724 | 0.20867 | 0.00083772 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 76.4724 | 0.20867 | 0.00083772
139684 | 41713.8271 | 41713.9132 | 467 | 121 | 47210.4919 | 390.1694 | 0.1454 | 0.0014383 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 390.1694 | 0.1454 | 0.0014383
139685 | 41713.9944 | 41714.0854 | 170 | 128 | 7349.7405 | 57.4198 | 0.022636 | 0.00052357 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 57.4198 | 0.022636 | 0.00052357
139686 | 41714.3993 | 41714.4917 | 1457 | 130 | 186139.4737 | 1431.8421 | 0.57328 | 0.0044873 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 1431.8421 | 0.57328 | 0.0044873
139687 | 41714.0535 | 41714.0757 | 65 | 29 | 1885 | 65 | 0.0058055 | 0.00020019 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 65 | 0.0058055 | 0.00020019
139688 | 41713.8167 | 41713.8472 | 56 | 41 | 2296 | 56 | 0.0070713 | 0.00017247 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 56 | 0.0070713 | 0.00017247
139689 | 41713.7118 | 41713.7639 | 8 | 72 | 576 | 8 | 0.001774 | 2.4639e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 8 | 0.001774 | 2.4639e-05
139690 | 41713.8701 | 41713.9375 | 821 | 94 | 15667.9588 | 166.6804 | 0.048255 | 0.0025286 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 166.6804 | 0.048255 | 0.0025286
139691 | 41714.4569 | 41714.4965 | 42 | 54 | 2268 | 42 | 0.0069851 | 0.00012935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 42 | 0.0069851 | 0.00012935
139694 | 41713.6014 | 41713.6431 | 947 | 57 | 53979 | 947 | 0.16625 | 0.0029166 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 947 | 0.16625 | 0.0029166
139699 | 41714.5792 | 41714.7035 | 5 | 176 | 880 | 5 | 0.0027103 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 5 | 0.0027103 | 1.5399e-05
139700 | 41714.6042 | 41714.6146 | 11 | 12 | 132 | 11 | 0.00040654 | 3.3878e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 11 | 0.00040654 | 3.3878e-05
139701 | 41714.5312 | 41714.5486 | 8 | 22 | 176 | 8 | 0.00054205 | 2.4639e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 8 | 0.00054205 | 2.4639e-05
139702 | 41714.6493 | 41714.7014 | 2 | 72 | 144 | 2 | 0.0004435 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 2 | 0.0004435 | 6.1597e-06
139703 | 41714.5306 | 41714.5486 | 29 | 23 | 667 | 29 | 0.0020543 | 8.9315e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 29 | 0.0020543 | 8.9315e-05
139704 | 41714.5889 | 41714.5972 | 4 | 9 | 36 | 4 | 0.00011087 | 1.2319e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 4 | 0.00011087 | 1.2319e-05
139705 | 41714.6215 | 41714.6771 | 3 | 77 | 231 | 3 | 0.00071144 | 9.2395e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 3 | 0.00071144 | 9.2395e-06
139706 | 41714.3583 | 41714.5556 | 19 | 281 | 5339 | 19 | 0.016443 | 5.8517e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 19 | 0.016443 | 5.8517e-05
139707 | 41714.5472 | 41714.6597 | 5 | 159 | 795 | 5 | 0.0024485 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 5 | 0.0024485 | 1.5399e-05
139708 | 41714.6958 | 41714.741 | 12 | 62 | 744 | 12 | 0.0022914 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 12 | 0.0022914 | 3.6958e-05
139709 | 41714.3368 | 41714.3667 | 8 | 40 | 320 | 8 | 0.00098555 | 2.4639e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 8 | 0.00098555 | 2.4639e-05
139710 | 41714.5799 | 41714.6542 | 6 | 104 | 624 | 6 | 0.0019218 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 6 | 0.0019218 | 1.8479e-05
139711 | 41714.4201 | 41714.441 | 1362 | 27 | 36774 | 1362 | 0.11326 | 0.0041947 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 1362 | 0.11326 | 0.0041947
139713 | 41714.666 | 41714.8368 | 18 | 243 | 4374 | 18 | 0.013471 | 5.5437e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 18 | 0.013471 | 5.5437e-05
139714 | 41714.7389 | 41714.8785 | 639 | 198 | 41497.2537 | 209.5821 | 0.1278 | 0.001968 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 209.5821 | 0.1278 | 0.001968
139715 | 41714.8194 | 41714.9292 | 1974 | 155 | 56066.8354 | 361.7215 | 0.17268 | 0.0060796 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 361.7215 | 0.17268 | 0.0060796
139716 | 41714.9819 | 41715.4479 | 63 | 668 | 9634.7303 | 14.4232 | 0.029673 | 0.00019403 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 14.4232 | 0.029673 | 0.00019403
139717 | 41714.8569 | 41714.8604 | 1089 | 2 | 1475.6 | 737.8 | 0.0045446 | 0.0033539 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 737.8 | 0.0045446 | 0.0033539
139718 | 41715.0903 | 41715.2146 | 72 | 176 | 7991.7765 | 45.4078 | 0.024613 | 0.00022175 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 45.4078 | 0.024613 | 0.00022175
139721 | 41715.0167 | 41715.2889 | 819 | 389 | 149367.0689 | 383.977 | 0.46003 | 0.0025224 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 383.977 | 0.46003 | 0.0025224
139722 | 41714.5944 | 41714.725 | 6 | 185 | 1110 | 6 | 0.0034186 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 6 | 0.0034186 | 1.8479e-05
139723 | 41713.8208 | 41713.9708 | 143 | 213 | 22828.4722 | 107.1759 | 0.070308 | 0.00044042 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-15 | 2014 | 2014 | 2014-03-15 | C | 107.1759 | 0.070308 | 0.00044042
139724 | 41714.0549 | 41714.1292 | 1128 | 104 | 97472.2991 | 937.2336 | 0.3002 | 0.0034741 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 937.2336 | 0.3002 | 0.0034741
139725 | 41715.5417 | 41715.5583 | 28 | 21 | 588 | 28 | 0.0018109 | 8.6236e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 28 | 0.0018109 | 8.6236e-05
139726 | 41715.5382 | 41715.6451 | 14 | 151 | 2114 | 14 | 0.0065108 | 4.3118e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 14 | 0.0065108 | 4.3118e-05
139728 | 41715.6035 | 41715.6507 | 80 | 65 | 5200 | 80 | 0.016015 | 0.00024639 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 80 | 0.016015 | 0.00024639
139730 | 41715.5833 | 41715.7118 | 1 | 182 | 182 | 1 | 0.00056053 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 1 | 0.00056053 | 3.0798e-06
139733 | 41715.6354 | 41715.6667 | 72 | 42 | 3024 | 72 | 0.0093134 | 0.00022175 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 72 | 0.0093134 | 0.00022175
139734 | 41715.4278 | 41715.4667 | 48 | 53 | 2544 | 48 | 0.0078351 | 0.00014783 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 48 | 0.0078351 | 0.00014783
139735 | 41715.584 | 41715.6181 | 85 | 46 | 3910 | 85 | 0.012042 | 0.00026179 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 85 | 0.012042 | 0.00026179
139737 | 41715.6458 | 41715.6771 | 47 | 42 | 1974 | 47 | 0.0060796 | 0.00014475 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 47 | 0.0060796 | 0.00014475
139739 | 41715.8326 | 41715.8528 | 5 | 26 | 130 | 5 | 0.00040038 | 1.5399e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-17 | 2014 | 2014 | 2014-03-17 | C | 5 | 0.00040038 | 1.5399e-05
139740 | 41716.5687 | 41716.641 | 94 | 101 | 9494 | 94 | 0.02924 | 0.00028951 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-18 | 2014 | 2014 | 2014-03-18 | C | 94 | 0.02924 | 0.00028951
139742 | 41716.55 | 41716.6549 | 370 | 148 | 21312.9801 | 144.0066 | 0.065641 | 0.0011395 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-18 | 2014 | 2014 | 2014-03-18 | C | 144.0066 | 0.065641 | 0.0011395
139743 | 41716.3542 | 41716.6424 | 1 | 412 | 412 | 1 | 0.0012689 | 3.0798e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-18 | 2014 | 2014 | 2014-03-18 | B | 1 | 0.0012689 | 3.0798e-06
139744 | 41716.5444 | 41716.6667 | 114 | 173 | 12905.2102 | 74.5966 | 0.039746 | 0.0003511 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-18 | 2014 | 2014 | 2014-03-18 | C | 74.5966 | 0.039746 | 0.0003511
139745 | 41716.3785 | 41716.5069 | 6 | 182 | 1092 | 6 | 0.0033632 | 1.8479e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-18 | 2014 | 2014 | 2014-03-18 | B | 6 | 0.0033632 | 1.8479e-05
139751 | 41717.4125 | 41717.425 | 210 | 15 | 3150 | 210 | 0.0097015 | 0.00064677 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 210 | 0.0097015 | 0.00064677
139752 | 41717.4125 | 41717.4875 | 614 | 105 | 37665.8333 | 358.7222 | 0.116 | 0.001891 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 358.7222 | 0.116 | 0.001891
139756 | 41717.5375 | 41717.5403 | 3 | 1 | 3 | 3 | 9.2395e-06 | 9.2395e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 3 | 9.2395e-06 | 9.2395e-06
139762 | 41717.4861 | 41717.5312 | 1 | 62 | 62 | 1 | 0.00019095 | 3.0798e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 1 | 0.00019095 | 3.0798e-06
139767 | 41717.9861 | 41718.1396 | 1620 | 218 | 94451.2127 | 433.2624 | 0.29089 | 0.0049893 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 433.2624 | 0.29089 | 0.0049893
139769 | 41717.4333 | 41717.5868 | 2308 | 218 | 135057.4118 | 619.5294 | 0.41596 | 0.0071083 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 619.5294 | 0.41596 | 0.0071083
139770 | 41717.6743 | 41717.6799 | 712 | 5 | 3560 | 712 | 0.010964 | 0.0021928 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 712 | 0.010964 | 0.0021928
139771 | 41717.4333 | 41717.8021 | 713 | 528 | 107360 | 203.3333 | 0.33065 | 0.0021959 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 203.3333 | 0.33065 | 0.0021959
139772 | 41717.5208 | 41717.5319 | 800 | 13 | 7442.5 | 572.5 | 0.022922 | 0.0024639 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-03-19 | 2014 | 2014 | 2014-03-19 | C | 572.5 | 0.022922 | 0.0024639
139775 | 41718.375 | 41718.4444 | 2 | 97 | 194 | 2 | 0.00059749 | 6.1597e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2014-03-20 | 2014 | 2014 | 2014-03-20 | B | 2 | 0.00059749 | 6.1597e-06
139786 | 41719.991 | 41720.4028 | 343 | 590 | 29349.7639 | 49.7454 | 0.090393 | 0.0010564 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-21 | 2014 | 2014 | 2014-03-21 | C | 49.7454 | 0.090393 | 0.0010564
139788 | 41720.2188 | 41720.2451 | 42 | 35 | 1470 | 42 | 0.0045274 | 0.00012935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-22 | 2014 | 2014 | 2014-03-22 | C | 42 | 0.0045274 | 0.00012935
139789 | 41720.3042 | 41720.3542 | 15 | 69 | 1035 | 15 | 0.0031876 | 4.6198e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-22 | 2014 | 2014 | 2014-03-22 | C | 15 | 0.0031876 | 4.6198e-05
139790 | 41720.3611 | 41720.4812 | 6 | 170 | 1020 | 6 | 0.0031414 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-22 | 2014 | 2014 | 2014-03-22 | C | 6 | 0.0031414 | 1.8479e-05
139791 | 41720.4528 | 41720.5618 | 196 | 154 | 3214.3822 | 20.8726 | 0.0098998 | 0.00060365 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-03-22 | 2014 | 2014 | 2014-03-22 | C | 20.8726 | 0.0098998 | 0.00060365
139798 | 41721.5521 | 41721.5694 | 10 | 22 | 220 | 10 | 0.00067757 | 3.0798e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2014-03-23 | 2014 | 2014 | 2014-03-23 | C | 10 | 0.00067757 | 3.0798e-05
139801 | 41722.1743 | 41722.325 | 809 | 214 | 50435.9539 | 235.682 | 0.15533 | 0.0024916 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-24 | 2014 | 2014 | 2014-03-24 | C | 235.682 | 0.15533 | 0.0024916
139811 | 41723.4479 | 41723.4722 | 2 | 32 | 64 | 2 | 0.00019711 | 6.1597e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-25 | 2014 | 2014 | 2014-03-25 | C | 2 | 0.00019711 | 6.1597e-06
139813 | 41723.8715 | 41723.9299 | 1120 | 81 | 37981.2857 | 468.9048 | 0.11698 | 0.0034494 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-25 | 2014 | 2014 | 2014-03-25 | C | 468.9048 | 0.11698 | 0.0034494
139814 | 41724.4583 | 41724.4931 | 6 | 47 | 282 | 6 | 0.00086852 | 1.8479e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-26 | 2014 | 2014 | 2014-03-26 | C | 6 | 0.00086852 | 1.8479e-05
139818 | 41724.2708 | 41724.3854 | 191 | 162 | 8669.4545 | 53.5152 | 0.026701 | 0.00058825 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-26 | 2014 | 2014 | 2014-03-26 | C | 53.5152 | 0.026701 | 0.00058825
139831 | 41725.3194 | 41725.3236 | 178 | 3 | 534 | 178 | 0.0016446 | 0.00054821 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2014-03-27 | 2014 | 2014 | 2014-03-27 | C | 178 | 0.0016446 | 0.00054821
139832 | 41726.3528 | 41726.3889 | 920 | 49 | 45080 | 920 | 0.13884 | 0.0028335 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-28 | 2014 | 2014 | 2014-03-28 | C | 920 | 0.13884 | 0.0028335
139833 | 41726.5194 | 41726.5576 | 1130 | 52 | 42422.5455 | 815.8182 | 0.13065 | 0.0034802 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-28 | 2014 | 2014 | 2014-03-28 | C | 815.8182 | 0.13065 | 0.0034802
139839 | 41726.8201 | 41726.8319 | 164 | 14 | 2296 | 164 | 0.0070713 | 0.00050509 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2014-03-28 | 2014 | 2014 | 2014-03-28 | C | 164 | 0.0070713 | 0.00050509
139842 | 41728.1028 | 41728.309 | 27 | 294 | 7938 | 27 | 0.024448 | 8.3156e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-30 | 2014 | 2014 | 2014-03-30 | C | 27 | 0.024448 | 8.3156e-05
139845 | 41714.2889 | 41715.4618 | 12 | 1686 | 20232 | 12 | 0.062311 | 3.6958e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-16 | 2014 | 2014 | 2014-03-16 | C | 12 | 0.062311 | 3.6958e-05
139847 | 41729.3097 | 41729.3778 | 1351 | 95 | 116245.102 | 1223.6327 | 0.35802 | 0.0041609 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-31 | 2014 | 2014 | 2014-03-31 | C | 1223.6327 | 0.35802 | 0.0041609
139857 | 41729.4347 | 41729.4611 | 61 | 35 | 2135 | 61 | 0.0065755 | 0.00018787 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2014-03-31 | 2014 | 2014 | 2014-03-31 | C | 61 | 0.0065755 | 0.00018787
139863 | 41729.3097 | 41729.5042 | 39 | 277 | 6319.5571 | 22.8143 | 0.019463 | 0.00012011 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2014-03-31 | 2014 | 2014 | 2014-03-31 | C | 22.8143 | 0.019463 | 0.00012011
3477 | [6 empty] | 226.4104 | 2.2892
Formulas:
Day = INT([Interruption Date/Time])
date = INT([Interruption Date/Time])

## 2013
Fault Record ID | F_Date_of_interruption | F_Restoration_time | F_Total_interrupted_customers | Adjusted Duration | Adjusted Cust_Mins | Adjusted Cust_Ints | Adjusted SAIDI | Adjusted SAIFI | Fault Description | Planned / Unplanned | class | MOC Classification | Owner | Day | Year | disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
128736 | 2012-04-01 14:30 | 2012-04-01 16:07 | 667 | 94 | 45072.5155 | 479.4948 | 0.13991 | 0.0020704 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-01 | 2013 | 2013 | 2012-04-01 | C | 479.4948 | 0.13991 | 0.0020704
128739 | 2012-04-01 22:39 | 2012-04-02 03:12 | 659 | 270 | 58811.5385 | 217.8205 | 0.18255 | 0.0020456 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-01 | 2013 | 2013 | 2012-04-01 | C | 217.8205 | 0.18255 | 0.0020456
128741 | 2012-04-02 07:19 | 2012-04-02 07:46 | 639 | 24 | 15336 | 639 | 0.047603 | 0.0019835 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 639 | 0.047603 | 0.0019835
128742 | 2012-04-02 07:19 | 2012-04-02 07:46 | 583 | 24 | 13992 | 583 | 0.043432 | 0.0018096 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 583 | 0.043432 | 0.0018096
128743 | 2012-04-02 07:19 | 2012-04-02 09:30 | 153 | 128 | 9958.5954 | 77.8015 | 0.030912 | 0.00047492 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 77.8015 | 0.030912 | 0.00047492
128745 | 2012-04-02 08:58 | 2012-04-02 12:12 | 92 | 191 | 17572 | 92 | 0.054544 | 0.00028557 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 92 | 0.054544 | 0.00028557
128747 | 2012-04-02 09:10 | 2012-04-02 12:15 | 3 | 182 | 546 | 3 | 0.0016948 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 3 | 0.0016948 | 9.3121e-06
128748 | 2012-04-02 11:45 | 2012-04-02 12:40 | 34 | 52 | 1768 | 34 | 0.0054879 | 0.00010554 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 34 | 0.0054879 | 0.00010554
128752 | 2012-04-02 09:34 | 2012-04-02 14:52 | 15 | 315 | 2316.934 | 7.3553 | 0.0071918 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 7.3553 | 0.0071918 | 4.656e-05
128753 | 2012-04-02 10:31 | 2012-04-02 10:41 | 24 | 7 | 168 | 24 | 0.00052148 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 24 | 0.00052148 | 7.4497e-05
128754 | 2012-04-02 13:30 | 2012-04-02 13:34 | 34 | 1 | 34 | 34 | 0.00010554 | 0.00010554 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 34 | 0.00010554 | 0.00010554
128755 | 2012-04-02 12:30 | 2012-04-02 14:15 | 2 | 102 | 204 | 2 | 0.00063322 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | B | 2 | 0.00063322 | 6.2081e-06
128759 | 2012-04-02 20:30 | 2012-04-02 23:38 | 402 | 185 | 74370 | 402 | 0.23085 | 0.0012478 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 402 | 0.23085 | 0.0012478
128760 | 2012-04-03 01:25 | 2012-04-03 02:19 | 695 | 51 | 30632.1111 | 600.6296 | 0.095083 | 0.0021573 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 600.6296 | 0.095083 | 0.0021573
128761 | 2012-04-02 23:34 | 2012-04-03 03:22 | 297 | 225 | 35089.1447 | 155.9518 | 0.10892 | 0.0009219 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-02 | 2013 | 2013 | 2012-04-02 | C | 155.9518 | 0.10892 | 0.0009219
128765 | 2012-04-03 09:00 | 2012-04-03 11:00 | 38 | 117 | 4446 | 38 | 0.013801 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | B | 38 | 0.013801 | 0.00011795
128766 | 2012-04-03 09:30 | 2012-04-03 11:20 | 2 | 107 | 214 | 2 | 0.00066426 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | B | 2 | 0.00066426 | 6.2081e-06
128767 | 2012-04-03 09:33 | 2012-04-03 14:40 | 31 | 304 | 9424 | 31 | 0.029252 | 9.6225e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | B | 31 | 0.029252 | 9.6225e-05
128768 | 2012-04-03 14:15 | 2012-04-03 15:18 | 9 | 60 | 540 | 9 | 0.0016762 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 9 | 0.0016762 | 2.7936e-05
128769 | 2012-04-03 09:33 | 2012-04-03 14:39 | 68 | 303 | 20604 | 68 | 0.063955 | 0.00021107 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | B | 68 | 0.063955 | 0.00021107
128770 | 2012-04-03 09:10 | 2012-04-03 15:19 | 3 | 366 | 1098 | 3 | 0.0034082 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | B | 3 | 0.0034082 | 9.3121e-06
128771 | 2012-04-03 13:35 | 2012-04-03 13:51 | 312 | 13 | 4056 | 312 | 0.01259 | 0.00096846 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 312 | 0.01259 | 0.00096846
128772 | 2012-04-03 14:16 | 2012-04-03 14:22 | 61 | 3 | 183 | 61 | 0.00056804 | 0.00018935 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 61 | 0.00056804 | 0.00018935
128773 | 2012-04-03 14:16 | 2012-04-03 14:22 | 36 | 3 | 108 | 36 | 0.00033524 | 0.00011175 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 36 | 0.00033524 | 0.00011175
128774 | 2012-04-03 14:16 | 2012-04-03 14:22 | 1352 | 3 | 4056 | 1352 | 0.01259 | 0.0041966 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-04-03 | 2013 | 2013 | 2012-04-03 | C | 1352 | 0.01259 | 0.0041966
128778 | 2012-04-04 03:20 | 2012-04-04 05:40 | 61 | 137 | 8357 | 61 | 0.02594 | 0.00018935 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 61 | 0.02594 | 0.00018935
128779 | 2012-04-04 09:18 | 2012-04-04 14:06 | 1 | 285 | 285 | 1 | 0.00088465 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | B | 1 | 0.00088465 | 3.104e-06
128782 | 2012-04-04 10:00 | 2012-04-04 13:20 | 19 | 197 | 3743 | 19 | 0.011618 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | B | 19 | 0.011618 | 5.8977e-05
128783 | 2012-04-04 13:30 | 2012-04-04 14:15 | 50 | 42 | 2100 | 50 | 0.0065185 | 0.0001552 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 50 | 0.0065185 | 0.0001552
128785 | 2012-04-04 12:42 | 2012-04-04 13:56 | 62 | 71 | 4402 | 62 | 0.013664 | 0.00019245 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 62 | 0.013664 | 0.00019245
128786 | 2012-04-04 13:00 | 2012-04-04 13:38 | 4 | 35 | 140 | 4 | 0.00043456 | 1.2416e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 4 | 0.00043456 | 1.2416e-05
128787 | 2012-04-04 11:55 | 2012-04-04 12:45 | 28 | 47 | 1316 | 28 | 0.0040849 | 8.6913e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 28 | 0.0040849 | 8.6913e-05
128789 | 2012-04-04 10:10 | 2012-04-04 11:37 | 27 | 84 | 2268 | 27 | 0.0070399 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 27 | 0.0070399 | 8.3809e-05
128791 | 2012-04-04 07:55 | 2012-04-04 19:36 | 8 | 698 | 5584 | 8 | 0.017333 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 8 | 0.017333 | 2.4832e-05
128793 | 2012-04-04 15:48 | 2012-04-04 16:02 | 11 | 11 | 121 | 11 | 0.00037559 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 11 | 0.00037559 | 3.4144e-05
128794 | 2012-04-04 17:16 | 2012-04-04 17:54 | 9 | 35 | 315 | 9 | 0.00097777 | 2.7936e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 9 | 0.00097777 | 2.7936e-05
128795 | 2012-04-04 11:33 | 2012-04-04 19:28 | 491 | 472 | 24992.1516 | 52.9495 | 0.077576 | 0.0015241 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | C | 52.9495 | 0.077576 | 0.0015241
128798 | 2012-04-05 09:00 | 2012-04-05 13:15 | 3 | 252 | 756 | 3 | 0.0023466 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | B | 3 | 0.0023466 | 9.3121e-06
128800 | 2012-04-05 10:00 | 2012-04-05 14:51 | 57 | 288 | 16416 | 57 | 0.050956 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | B | 57 | 0.050956 | 0.00017693
128801 | 2012-04-05 11:05 | 2012-04-05 12:00 | 17 | 52 | 884 | 17 | 0.002744 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | C | 17 | 0.002744 | 5.2768e-05
128803 | 2012-04-05 09:30 | 2012-04-05 11:44 | 79 | 131 | 10349 | 79 | 0.032124 | 0.00024522 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | B | 79 | 0.032124 | 0.00024522
128808 | 2012-04-05 19:55 | 2012-04-06 00:05 | 195 | 247 | 48165 | 195 | 0.14951 | 0.00060529 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | C | 195 | 0.14951 | 0.00060529
128809 | 2012-04-05 18:10 | 2012-04-05 20:05 | 5 | 112 | 560 | 5 | 0.0017383 | 1.552e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-05 | 2013 | 2013 | 2012-04-05 | C | 5 | 0.0017383 | 1.552e-05
128811 | 2012-04-06 09:15 | 2012-04-06 09:47 | 3 | 29 | 87 | 3 | 0.00027005 | 9.3121e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | C | 3 | 0.00027005 | 9.3121e-06
128812 | 2012-04-06 23:50 | 2012-04-07 03:50 | 319 | 237 | 35883.775 | 151.4083 | 0.11138 | 0.00099019 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | C | 151.4083 | 0.11138 | 0.00099019
128813 | 2012-04-06 18:21 | 2012-04-07 00:23 | 35 | 359 | 12565 | 35 | 0.039002 | 0.00010864 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | C | 35 | 0.039002 | 0.00010864
128815 | 2012-04-06 11:53 | 2012-04-06 12:18 | 361 | 22 | 7942 | 361 | 0.024652 | 0.0011206 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | C | 361 | 0.024652 | 0.0011206
128816 | 2012-04-07 08:30 | 2012-04-07 10:14 | 25 | 101 | 2525 | 25 | 0.0078377 | 7.7601e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-07 | 2013 | 2013 | 2012-04-07 | C | 25 | 0.0078377 | 7.7601e-05
128817 | 2012-04-06 07:10 | 2012-04-06 09:40 | 1 | 147 | 147 | 1 | 0.00045629 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | B | 1 | 0.00045629 | 3.104e-06
128818 | 2012-04-08 03:24 | 2012-04-08 03:34 | 344 | 7 | 2408 | 344 | 0.0074745 | 0.0010678 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-08 | 2013 | 2013 | 2012-04-08 | C | 344 | 0.0074745 | 0.0010678
128819 | 2012-04-08 02:52 | 2012-04-08 04:42 | 296 | 107 | 25673.1909 | 239.9364 | 0.07969 | 0.00091879 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-08 | 2013 | 2013 | 2012-04-08 | C | 239.9364 | 0.07969 | 0.00091879
128820 | 2012-04-08 07:26 | 2012-04-08 11:50 | 4 | 261 | 1044 | 4 | 0.0032406 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-08 | 2013 | 2013 | 2012-04-08 | C | 4 | 0.0032406 | 1.2416e-05
128823 | 2012-04-08 16:10 | 2012-04-08 17:11 | 32 | 58 | 1856 | 32 | 0.0057611 | 9.9329e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-08 | 2013 | 2013 | 2012-04-08 | C | 32 | 0.0057611 | 9.9329e-05
128824 | 2012-04-06 11:52 | 2012-04-06 12:25 | 3 | 30 | 90 | 3 | 0.00027936 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-06 | 2013 | 2013 | 2012-04-06 | C | 3 | 0.00027936 | 9.3121e-06
128828 | 2012-04-09 01:59 | 2012-04-09 03:38 | 1268 | 96 | 65383.7576 | 681.0808 | 0.20295 | 0.0039359 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-09 | 2013 | 2013 | 2012-04-09 | C | 681.0808 | 0.20295 | 0.0039359
128829 | 2012-04-08 22:09 | 2012-04-08 23:16 | 289 | 64 | 17586.6269 | 274.791 | 0.054589 | 0.00089706 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-08 | 2013 | 2013 | 2012-04-08 | C | 274.791 | 0.054589 | 0.00089706
128831 | 2012-04-10 09:00 | 2012-04-10 13:27 | 167 | 264 | 44088 | 167 | 0.13685 | 0.00051837 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 167 | 0.13685 | 0.00051837
128832 | 2012-04-10 10:00 | 2012-04-10 13:28 | 16 | 205 | 3280 | 16 | 0.010181 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 16 | 0.010181 | 4.9664e-05
128833 | 2012-04-10 10:15 | 2012-04-10 14:50 | 12 | 272 | 3264 | 12 | 0.010132 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 12 | 0.010132 | 3.7248e-05
128834 | 2012-04-10 07:11 | 2012-04-10 15:08 | 19 | 474 | 9006 | 19 | 0.027955 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 19 | 0.027955 | 5.8977e-05
128835 | 2012-04-10 08:58 | 2012-04-10 14:27 | 96 | 326 | 31296 | 96 | 0.097144 | 0.00029799 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 96 | 0.097144 | 0.00029799
128836 | 2012-04-10 10:17 | 2012-04-10 14:00 | 48 | 220 | 10560 | 48 | 0.032779 | 0.00014899 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 48 | 0.032779 | 0.00014899
128837 | 2012-04-10 09:00 | 2012-04-10 14:59 | 62 | 356 | 22072 | 62 | 0.068512 | 0.00019245 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 62 | 0.068512 | 0.00019245
128838 | 2012-04-10 13:24 | 2012-04-10 14:54 | 120 | 87 | 10440 | 120 | 0.032406 | 0.00037248 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | B | 120 | 0.032406 | 0.00037248
128839 | 2012-04-10 12:38 | 2012-04-10 13:23 | 80 | 42 | 3360 | 80 | 0.01043 | 0.00024832 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | C | 80 | 0.01043 | 0.00024832
128841 | 2012-04-10 14:25 | 2012-04-10 15:32 | 50 | 64 | 3200 | 50 | 0.0099329 | 0.0001552 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | C | 50 | 0.0099329 | 0.0001552
128847 | 2012-04-10 01:12 | 2012-04-10 17:58 | 1 | 1003 | 1003 | 1 | 0.0031133 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | C | 1 | 0.0031133 | 3.104e-06
128848 | 2012-04-10 22:00 | 2012-04-11 02:54 | 34 | 291 | 9894 | 34 | 0.030711 | 0.00010554 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-10 | 2013 | 2013 | 2012-04-10 | C | 34 | 0.030711 | 0.00010554
128859 | 2012-04-11 10:14 | 2012-04-11 11:54 | 176 | 97 | 13531.5 | 139.5 | 0.042002 | 0.00054631 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | C | 139.5 | 0.042002 | 0.00054631
128862 | 2012-04-11 08:45 | 2012-04-11 13:35 | 9 | 287 | 2583 | 9 | 0.0080177 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | B | 9 | 0.0080177 | 2.7936e-05
128864 | 2012-04-11 09:00 | 2012-04-11 14:19 | 24 | 316 | 7584 | 24 | 0.023541 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | B | 24 | 0.023541 | 7.4497e-05
128866 | 2012-04-11 17:10 | 2012-04-11 21:50 | 744 | 277 | 192431.9 | 694.7 | 0.59731 | 0.0023094 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | C | 694.7 | 0.59731 | 0.0023094
128867 | 2012-04-11 17:14 | 2012-04-11 21:36 | 1093 | 259 | 107780.5763 | 416.1412 | 0.33455 | 0.0033927 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | C | 416.1412 | 0.33455 | 0.0033927
128868 | 2012-04-11 17:14 | 2012-04-11 19:45 | 1265 | 148 | 124068.106 | 838.298 | 0.38511 | 0.0039266 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | C | 838.298 | 0.38511 | 0.0039266
128870 | 2012-04-12 23:16 | 2012-04-12 23:31 | 119 | 12 | 1428 | 119 | 0.0044326 | 0.00036938 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 119 | 0.0044326 | 0.00036938
128871 | 2012-04-11 23:21 | 2012-04-12 04:47 | 162 | 323 | 22765.5552 | 70.4816 | 0.070665 | 0.00050285 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | C | 70.4816 | 0.070665 | 0.00050285
128872 | 2012-04-12 09:48 | 2012-04-12 12:50 | 9 | 179 | 1611 | 9 | 0.0050006 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 9 | 0.0050006 | 2.7936e-05
128875 | 2012-04-11 10:02 | 2012-04-11 13:46 | 50 | 221 | 11050 | 50 | 0.0343 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | B | 50 | 0.0343 | 0.0001552
128876 | 2012-04-12 11:25 | 2012-04-12 12:40 | 46 | 72 | 3312 | 46 | 0.010281 | 0.00014279 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 46 | 0.010281 | 0.00014279
128877 | 2012-04-11 09:00 | 2012-04-11 15:30 | 71 | 387 | 27477 | 71 | 0.085289 | 0.00022039 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-11 | 2013 | 2013 | 2012-04-11 | B | 71 | 0.085289 | 0.00022039
128878 | 2012-04-12 10:00 | 2012-04-12 12:26 | 360 | 143 | 51480 | 360 | 0.1598 | 0.0011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 360 | 0.1598 | 0.0011175
128880 | 2012-04-12 09:00 | 2012-04-12 12:50 | 17 | 227 | 3859 | 17 | 0.011978 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 17 | 0.011978 | 5.2768e-05
128882 | 2012-04-12 09:15 | 2012-04-12 14:57 | 46 | 339 | 15594 | 46 | 0.048404 | 0.00014279 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 46 | 0.048404 | 0.00014279
128883 | 2012-04-12 09:18 | 2012-04-12 10:10 | 46 | 49 | 2254 | 46 | 0.0069965 | 0.00014279 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 46 | 0.0069965 | 0.00014279
128884 | 2012-04-12 09:00 | 2012-04-12 14:55 | 4 | 352 | 1408 | 4 | 0.0043705 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 4 | 0.0043705 | 1.2416e-05
128886 | 2012-04-12 13:25 | 2012-04-12 16:52 | 44 | 204 | 8976 | 44 | 0.027862 | 0.00013658 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 44 | 0.027862 | 0.00013658
128888 | 2012-04-12 20:55 | 2012-04-12 22:12 | 83 | 74 | 6142 | 83 | 0.019065 | 0.00025763 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 83 | 0.019065 | 0.00025763
128890 | 2012-04-12 17:05 | 2012-04-12 18:39 | 180 | 91 | 15365.4468 | 168.8511 | 0.047695 | 0.00055873 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | C | 168.8511 | 0.047695 | 0.00055873
128892 | 2012-04-13 09:00 | 2012-04-13 11:50 | 29 | 167 | 4843 | 29 | 0.015033 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | B | 29 | 0.015033 | 9.0017e-05
128893 | 2012-04-13 08:52 | 2012-04-13 12:55 | 55 | 240 | 13200 | 55 | 0.040973 | 0.00017072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | B | 55 | 0.040973 | 0.00017072
128895 | 2012-04-13 09:00 | 2012-04-13 14:34 | 36 | 331 | 11916 | 36 | 0.036988 | 0.00011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | B | 36 | 0.036988 | 0.00011175
128896 | 2012-04-13 09:00 | 2012-04-13 14:11 | 16 | 308 | 4928 | 16 | 0.015297 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | B | 16 | 0.015297 | 4.9664e-05
128901 | 2012-04-13 17:30 | 2012-04-13 18:57 | 13 | 84 | 1092 | 13 | 0.0033896 | 4.0352e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | C | 13 | 0.0033896 | 4.0352e-05
128902 | 2012-04-13 21:44 | 2012-04-13 22:44 | 307 | 57 | 9551.3 | 167.5667 | 0.029648 | 0.00095294 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | C | 167.5667 | 0.029648 | 0.00095294
128904 | 2012-04-13 10:59 | 2012-04-13 16:45 | 1 | 343 | 343 | 1 | 0.0010647 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | C | 1 | 0.0010647 | 3.104e-06
128909 | 2012-04-14 16:53 | 2012-04-14 17:09 | 54 | 13 | 702 | 54 | 0.002179 | 0.00016762 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-14 | 2013 | 2013 | 2012-04-14 | C | 54 | 0.002179 | 0.00016762
128911 | 2012-04-15 06:13 | 2012-04-15 11:30 | 20 | 314 | 6280 | 20 | 0.019493 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-15 | 2013 | 2013 | 2012-04-15 | B | 20 | 0.019493 | 6.2081e-05
128913 | 2012-04-15 09:00 | 2012-04-15 13:23 | 87 | 260 | 22620 | 87 | 0.070213 | 0.00027005 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-15 | 2013 | 2013 | 2012-04-15 | B | 87 | 0.070213 | 0.00027005
128920 | 2012-04-16 09:00 | 2012-04-16 14:11 | 46 | 308 | 14168 | 46 | 0.043978 | 0.00014279 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-16 | 2013 | 2013 | 2012-04-16 | B | 46 | 0.043978 | 0.00014279
128922 | 2012-04-04 07:59 | 2012-04-04 14:16 | 11 | 374 | 4114 | 11 | 0.01277 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-04 | 2013 | 2013 | 2012-04-04 | B | 11 | 0.01277 | 3.4144e-05
128923 | 2012-04-16 09:00 | 2012-04-16 14:58 | 73 | 355 | 25915 | 73 | 0.080441 | 0.00022659 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-16 | 2013 | 2013 | 2012-04-16 | B | 73 | 0.080441 | 0.00022659
128924 | 2012-04-16 21:06 | 2012-04-16 22:05 | 185 | 56 | 6794.9831 | 121.339 | 0.021092 | 0.00057425 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-16 | 2013 | 2013 | 2012-04-16 | C | 121.339 | 0.021092 | 0.00057425
128927 | 2012-04-17 01:02 | 2012-04-17 03:57 | 23 | 172 | 3956 | 23 | 0.01228 | 7.1393e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | C | 23 | 0.01228 | 7.1393e-05
128929 | 2012-04-13 10:01 | 2012-04-13 14:30 | 50 | 266 | 13300 | 50 | 0.041284 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-13 | 2013 | 2013 | 2012-04-13 | B | 50 | 0.041284 | 0.0001552
128931 | 2012-04-12 09:05 | 2012-04-12 12:20 | 8 | 192 | 1536 | 8 | 0.0047678 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-12 | 2013 | 2013 | 2012-04-12 | B | 8 | 0.0047678 | 2.4832e-05
128940 | 2012-04-17 09:15 | 2012-04-17 14:28 | 8 | 310 | 2480 | 8 | 0.007698 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | B | 8 | 0.007698 | 2.4832e-05
128942 | 2012-04-17 10:00 | 2012-04-17 14:24 | 50 | 261 | 13050 | 50 | 0.040508 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | B | 50 | 0.040508 | 0.0001552
128943 | 2012-04-17 10:51 | 2012-04-17 13:02 | 38 | 128 | 4864 | 38 | 0.015098 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | C | 38 | 0.015098 | 0.00011795
128944 | 2012-04-17 09:03 | 2012-04-17 15:14 | 343 | 368 | 126224 | 343 | 0.3918 | 0.0010647 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | B | 343 | 0.3918 | 0.0010647
128949 | 2012-04-17 08:30 | 2012-04-17 16:02 | 49 | 449 | 22001 | 49 | 0.068292 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | B | 49 | 0.068292 | 0.0001521
128954 | 2012-04-18 08:49 | 2012-04-18 13:18 | 8 | 266 | 2128 | 8 | 0.0066054 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-18 | 2013 | 2013 | 2012-04-18 | B | 8 | 0.0066054 | 2.4832e-05
128956 | 2012-04-18 09:15 | 2012-04-18 14:37 | 14 | 319 | 4466 | 14 | 0.013863 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-18 | 2013 | 2013 | 2012-04-18 | B | 14 | 0.013863 | 4.3456e-05
128958 | 2012-04-18 10:00 | 2012-04-18 14:41 | 318 | 278 | 88404 | 318 | 0.27441 | 0.00098708 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-18 | 2013 | 2013 | 2012-04-18 | B | 318 | 0.27441 | 0.00098708
128966 | 2012-04-18 21:30 | 2012-04-19 01:07 | 171 | 214 | 36594 | 171 | 0.11359 | 0.00053079 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-18 | 2013 | 2013 | 2012-04-18 | B | 171 | 0.11359 | 0.00053079
128968 | 2012-04-19 09:30 | 2012-04-19 10:00 | 40 | 27 | 1080 | 40 | 0.0033524 | 0.00012416 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | C | 40 | 0.0033524 | 0.00012416
128969 | 2012-04-19 11:57 | 2012-04-19 13:51 | 73 | 111 | 8103 | 73 | 0.025152 | 0.00022659 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | C | 73 | 0.025152 | 0.00022659
128970 | 2012-04-19 09:40 | 2012-04-19 14:39 | 2 | 296 | 592 | 2 | 0.0018376 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 2 | 0.0018376 | 6.2081e-06
128972 | 2012-04-19 08:46 | 2012-04-19 14:55 | 37 | 366 | 13542 | 37 | 0.042035 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 37 | 0.042035 | 0.00011485
128973 | 2012-04-19 09:00 | 2012-04-19 15:04 | 33 | 361 | 11913 | 33 | 0.036978 | 0.00010243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 33 | 0.036978 | 0.00010243
128975 | 2012-04-19 09:30 | 2012-04-19 12:12 | 324 | 159 | 51516 | 324 | 0.15991 | 0.0010057 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 324 | 0.15991 | 0.0010057
128976 | 2012-04-19 10:01 | 2012-04-19 14:04 | 50 | 240 | 12000 | 50 | 0.037248 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 50 | 0.037248 | 0.0001552
128977 | 2012-04-19 09:06 | 2012-04-19 13:46 | 101 | 277 | 27977 | 101 | 0.086841 | 0.00031351 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-19 | 2013 | 2013 | 2012-04-19 | B | 101 | 0.086841 | 0.00031351
128980 | 2012-04-17 00:21 | 2012-04-17 03:08 | 312 | 164 | 51168 | 312 | 0.15883 | 0.00096846 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-17 | 2013 | 2013 | 2012-04-17 | B | 312 | 0.15883 | 0.00096846
128982 | 2012-04-20 09:47 | 2012-04-20 12:40 | 62 | 170 | 10540 | 62 | 0.032716 | 0.00019245 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 62 | 0.032716 | 0.00019245
128984 | 2012-04-20 09:00 | 2012-04-20 09:50 | 4 | 47 | 188 | 4 | 0.00058356 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 4 | 0.00058356 | 1.2416e-05
128985 | 2012-04-20 09:02 | 2012-04-20 15:00 | 114 | 355 | 40470 | 114 | 0.12562 | 0.00035386 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 114 | 0.12562 | 0.00035386
128986 | 2012-04-20 12:30 | 2012-04-20 13:40 | 3 | 67 | 201 | 3 | 0.00062391 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 3 | 0.00062391 | 9.3121e-06
128987 | 2012-04-20 12:34 | 2012-04-20 14:12 | 11 | 95 | 1045 | 11 | 0.0032437 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 11 | 0.0032437 | 3.4144e-05
128988 | 2012-04-20 10:35 | 2012-04-20 14:25 | 11 | 227 | 2497 | 11 | 0.0077508 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 11 | 0.0077508 | 3.4144e-05
128990 | 2012-04-20 09:00 | 2012-04-20 16:30 | 20 | 447 | 7541.3867 | 16.8711 | 0.023409 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-20 | 2013 | 2013 | 2012-04-20 | B | 16.8711 | 0.023409 | 6.2081e-05
128991 | 2012-04-21 03:38 | 2012-04-21 15:03 | 456 | 682 | 137128.7942 | 201.0686 | 0.42565 | 0.0014154 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-21 | 2013 | 2013 | 2012-04-21 | C | 201.0686 | 0.42565 | 0.0014154
128992 | 2012-04-21 03:38 | 2012-04-21 05:15 | 862 | 94 | 81028 | 862 | 0.25151 | 0.0026757 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-21 | 2013 | 2013 | 2012-04-21 | C | 862 | 0.25151 | 0.0026757
128993 | 2012-04-21 07:20 | 2012-04-21 08:15 | 2 | 52 | 104 | 2 | 0.00032282 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-21 | 2013 | 2013 | 2012-04-21 | C | 2 | 0.00032282 | 6.2081e-06
128995 | 2012-04-21 17:08 | 2012-04-21 17:56 | 33 | 45 | 1485 | 33 | 0.0046095 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-21 | 2013 | 2013 | 2012-04-21 | C | 33 | 0.0046095 | 0.00010243
128996 | 2012-04-22 09:33 | 2012-04-22 11:09 | 4066 | 93 | 370708.6562 | 3986.1146 | 1.1507 | 0.012621 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-22 | 2013 | 2013 | 2012-04-22 | C | 3986.1146 | 1.1507 | 0.012621
128998 | 2012-04-22 13:54 | 2012-04-22 14:50 | 67 | 53 | 3551 | 67 | 0.011022 | 0.00020797 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-22 | 2013 | 2013 | 2012-04-22 | C | 67 | 0.011022 | 0.00020797
128999 | 2012-04-22 20:33 | 2012-04-22 22:00 | 510 | 84 | 16340.4138 | 194.5287 | 0.050721 | 0.0015831 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-04-22 | 2013 | 2013 | 2012-04-22 | C | 194.5287 | 0.050721 | 0.0015831
129001 | 2012-04-22 08:36 | 2012-04-22 14:18 | 17 | 339 | 5763 | 17 | 0.017889 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-22 | 2013 | 2013 | 2012-04-22 | B | 17 | 0.017889 | 5.2768e-05
129002 | 2012-04-23 09:15 | 2012-04-23 14:17 | 29 | 299 | 8671 | 29 | 0.026915 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-23 | 2013 | 2013 | 2012-04-23 | B | 29 | 0.026915 | 9.0017e-05
129006 | 2012-04-23 11:52 | 2012-04-23 12:02 | 89 | 7 | 623 | 89 | 0.0019338 | 0.00027626 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-23 | 2013 | 2013 | 2012-04-23 | C | 89 | 0.0019338 | 0.00027626
129007 | 2012-04-23 06:48 | 2012-04-23 07:03 | 1 | 12 | 12 | 1 | 3.7248e-05 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-23 | 2013 | 2013 | 2012-04-23 | C | 1 | 3.7248e-05 | 3.104e-06
129008 | 2012-04-24 03:17 | 2012-04-24 06:43 | 725 | 203 | 59287.8252 | 292.0583 | 0.18403 | 0.0022504 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | C | 292.0583 | 0.18403 | 0.0022504
129013 | 2012-04-24 13:01 | 2012-04-24 13:29 | 50 | 25 | 1250 | 50 | 0.00388 | 0.0001552 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | C | 50 | 0.00388 | 0.0001552
129014 | 2012-04-24 11:15 | 2012-04-24 13:55 | 1 | 157 | 157 | 1 | 0.00048733 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | C | 1 | 0.00048733 | 3.104e-06
129016 | 2012-04-24 09:00 | 2012-04-24 14:55 | 17 | 352 | 5984 | 17 | 0.018575 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 17 | 0.018575 | 5.2768e-05
129017 | 2012-04-24 09:32 | 2012-04-24 14:05 | 11 | 270 | 2970 | 11 | 0.009219 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 11 | 0.009219 | 3.4144e-05
129018 | 2012-04-24 09:05 | 2012-04-24 14:51 | 2 | 343 | 686 | 2 | 0.0021294 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 2 | 0.0021294 | 6.2081e-06
129020 | 2012-04-24 09:00 | 2012-04-24 14:20 | 23 | 317 | 7291 | 23 | 0.022631 | 7.1393e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 23 | 0.022631 | 7.1393e-05
129021 | 2012-04-24 09:30 | 2012-04-24 12:31 | 2 | 178 | 356 | 2 | 0.001105 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 2 | 0.001105 | 6.2081e-06
129022 | 2012-04-24 09:38 | 2012-04-24 14:41 | 132 | 300 | 39600 | 132 | 0.12292 | 0.00040973 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 132 | 0.12292 | 0.00040973
129023 | 2012-04-24 09:15 | 2012-04-24 10:45 | 3 | 87 | 261 | 3 | 0.00081015 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | B | 3 | 0.00081015 | 9.3121e-06
129024 | 2012-04-24 16:50 | 2012-04-24 17:19 | 5 | 26 | 130 | 5 | 0.00040352 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-24 | 2013 | 2013 | 2012-04-24 | C | 5 | 0.00040352 | 1.552e-05
129028 | 2012-04-25 00:06 | 2012-04-25 04:06 | 1 | 237 | 237 | 1 | 0.00073565 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-25 | 2013 | 2013 | 2012-04-25 | B | 1 | 0.00073565 | 3.104e-06
129029 | 2012-04-25 03:13 | 2012-04-25 04:16 | 163 | 60 | 9780 | 163 | 0.030357 | 0.00050596 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-25 | 2013 | 2013 | 2012-04-25 | C | 163 | 0.030357 | 0.00050596
129030 | 2012-04-25 03:13 | 2012-04-25 05:24 | 513 | 128 | 56840.7939 | 444.0687 | 0.17644 | 0.0015924 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-25 | 2013 | 2013 | 2012-04-25 | C | 444.0687 | 0.17644 | 0.0015924
129033 | 2012-04-25 13:39 | 2012-04-25 18:07 | 29 | 265 | 7685 | 29 | 0.023854 | 9.0017e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-25 | 2013 | 2013 | 2012-04-25 | C | 29 | 0.023854 | 9.0017e-05
129034 | 2012-04-25 18:42 | 2012-04-25 19:27 | 11 | 42 | 462 | 11 | 0.0014341 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-25 | 2013 | 2013 | 2012-04-25 | C | 11 | 0.0014341 | 3.4144e-05
129035 | 2012-04-26 09:30 | 2012-04-26 10:39 | 401 | 66 | 26466 | 401 | 0.082151 | 0.0012447 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 401 | 0.082151 | 0.0012447
129036 | 2012-04-26 10:29 | 2012-04-26 11:08 | 9 | 36 | 324 | 9 | 0.0010057 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 9 | 0.0010057 | 2.7936e-05
129037 | 2012-04-26 09:00 | 2012-04-26 12:54 | 59 | 231 | 13629 | 59 | 0.042305 | 0.00018314 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 59 | 0.042305 | 0.00018314
129038 | 2012-04-26 13:34 | 2012-04-26 16:34 | 198 | 177 | 35046 | 198 | 0.10878 | 0.0006146 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | C | 198 | 0.10878 | 0.0006146
129040 | 2012-04-26 12:00 | 2012-04-26 13:26 | 15 | 83 | 1245 | 15 | 0.0038645 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 15 | 0.0038645 | 4.656e-05
129043 | 2012-04-26 08:53 | 2012-04-26 14:21 | 75 | 325 | 24375 | 75 | 0.075661 | 0.0002328 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 75 | 0.075661 | 0.0002328
129046 | 2012-04-26 09:09 | 2012-04-26 14:42 | 10 | 330 | 3300 | 10 | 0.010243 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 10 | 0.010243 | 3.104e-05
129048 | 2012-04-26 09:17 | 2012-04-26 14:56 | 76 | 336 | 25536 | 76 | 0.079264 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 76 | 0.079264 | 0.00023591
129050 | 2012-04-26 09:02 | 2012-04-26 15:10 | 264 | 365 | 96360 | 264 | 0.2991 | 0.00081946 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 264 | 0.2991 | 0.00081946
129052 | 2012-04-26 22:00 | 2012-04-27 01:53 | 82 | 230 | 18860 | 82 | 0.058542 | 0.00025453 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-26 | 2013 | 2013 | 2012-04-26 | B | 82 | 0.058542 | 0.00025453
129055 | 2012-04-27 05:12 | 2012-04-27 06:54 | 2359 | 99 | 122781.3529 | 1240.2157 | 0.38112 | 0.0073224 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | C | 1240.2157 | 0.38112 | 0.0073224
129060 | 2012-04-27 08:45 | 2012-04-27 12:59 | 76 | 251 | 19076 | 76 | 0.059212 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | B | 76 | 0.059212 | 0.00023591
129061 | 2012-04-27 08:45 | 2012-04-27 13:12 | 44 | 264 | 11616 | 44 | 0.036056 | 0.00013658 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | B | 44 | 0.036056 | 0.00013658
129062 | 2012-04-27 12:43 | 2012-04-27 16:50 | 158 | 244 | 20536.502 | 84.166 | 0.063746 | 0.00049044 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | C | 84.166 | 0.063746 | 0.00049044
129063 | 2012-04-27 16:26 | 2012-04-27 17:48 | 668 | 79 | 52772 | 668 | 0.16381 | 0.0020735 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | C | 668 | 0.16381 | 0.0020735
129065 | 2012-04-28 00:04 | 2012-04-28 03:34 | 14 | 207 | 2898 | 14 | 0.0089955 | 4.3456e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 14 | 0.0089955 | 4.3456e-05
129069 | 2012-04-28 07:35 | 2012-04-28 08:21 | 6 | 43 | 258 | 6 | 0.00080084 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 6 | 0.00080084 | 1.8624e-05
129071 | 2012-04-28 13:00 | 2012-04-28 13:42 | 6 | 39 | 234 | 6 | 0.00072634 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 6 | 0.00072634 | 1.8624e-05
129073 | 2012-04-28 10:20 | 2012-04-28 16:53 | 13 | 390 | 3882.1374 | 9.9542 | 0.01205 | 4.0352e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 9.9542 | 0.01205 | 4.0352e-05
129074 | 2012-04-28 10:31 | 2012-04-28 11:49 | 27 | 75 | 2025 | 27 | 0.0062857 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 27 | 0.0062857 | 8.3809e-05
129076 | 2012-04-28 23:03 | 2012-04-29 02:32 | 339 | 206 | 28715.8086 | 139.3971 | 0.089135 | 0.0010523 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-04-28 | 2013 | 2013 | 2012-04-28 | C | 139.3971 | 0.089135 | 0.0010523
129077 | 2012-04-29 06:32 | 2012-04-29 11:30 | 18 | 295 | 5310 | 18 | 0.016482 | 5.5873e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-29 | 2013 | 2013 | 2012-04-29 | B | 18 | 0.016482 | 5.5873e-05
129080 | 2012-04-29 12:48 | 2012-04-29 16:23 | 107 | 212 | 22684 | 107 | 0.070412 | 0.00033213 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-29 | 2013 | 2013 | 2012-04-29 | C | 107 | 0.070412 | 0.00033213
129082 | 2012-04-30 09:30 | 2012-04-30 13:45 | 78 | 252 | 19656 | 78 | 0.061013 | 0.00024211 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | B | 78 | 0.061013 | 0.00024211
129085 | 2012-04-30 09:00 | 2012-04-30 13:15 | 8 | 252 | 2016 | 8 | 0.0062577 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | B | 8 | 0.0062577 | 2.4832e-05
129086 | 2012-04-30 08:30 | 2012-04-30 12:43 | 125 | 250 | 18419.9605 | 73.6798 | 0.057176 | 0.000388 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | C | 73.6798 | 0.057176 | 0.000388
129087 | 2012-04-30 09:35 | 2012-04-30 10:35 | 7 | 57 | 399 | 7 | 0.0012385 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | C | 7 | 0.0012385 | 2.1728e-05
129088 | 2012-04-30 19:10 | 2012-04-30 20:42 | 1 | 89 | 89 | 1 | 0.00027626 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | C | 1 | 0.00027626 | 3.104e-06
129089 | 2012-04-30 17:47 | 2012-04-30 20:13 | 259 | 143 | 21164 | 148 | 0.065694 | 0.00080394 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | C | 148 | 0.065694 | 0.00080394
129090 | 2012-04-27 09:16 | 2012-04-27 13:39 | 44 | 260 | 11440 | 44 | 0.03551 | 0.00013658 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-27 | 2013 | 2013 | 2012-04-27 | B | 44 | 0.03551 | 0.00013658
129092 | 2012-04-30 09:45 | 2012-04-30 13:16 | 4 | 208 | 832 | 4 | 0.0025826 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-04-30 | 2013 | 2013 | 2012-04-30 | B | 4 | 0.0025826 | 1.2416e-05
129093 | 2012-05-01 09:40 | 2012-05-01 09:47 | 164 | 4 | 656 | 164 | 0.0020362 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 164 | 0.0020362 | 0.00050906
129094 | 2012-05-01 09:30 | 2012-05-01 12:40 | 7 | 187 | 1309 | 7 | 0.0040632 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 7 | 0.0040632 | 2.1728e-05
129095 | 2012-05-01 08:52 | 2012-05-01 13:26 | 8 | 271 | 2168 | 8 | 0.0067295 | 2.4832e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 8 | 0.0067295 | 2.4832e-05
129097 | 2012-05-01 09:07 | 2012-05-01 11:54 | 61 | 164 | 10004 | 61 | 0.031053 | 0.00018935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 61 | 0.031053 | 0.00018935
129098 | 2012-05-01 10:55 | 2012-05-01 11:25 | 2 | 27 | 54 | 2 | 0.00016762 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 2 | 0.00016762 | 6.2081e-06
129099 | 2012-05-01 09:35 | 2012-05-01 14:53 | 4 | 315 | 1260 | 4 | 0.0039111 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 4 | 0.0039111 | 1.2416e-05
129100 | 2012-05-01 13:20 | 2012-05-01 15:40 | 7 | 137 | 959 | 7 | 0.0029768 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 7 | 0.0029768 | 2.1728e-05
129101 | 2012-05-01 09:28 | 2012-05-01 15:07 | 1 | 336 | 336 | 1 | 0.001043 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 1 | 0.001043 | 3.104e-06
129102 | 2012-05-01 09:24 | 2012-05-01 15:35 | 9 | 368 | 3312 | 9 | 0.010281 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 9 | 0.010281 | 2.7936e-05
129103 | 2012-05-01 09:41 | 2012-05-01 14:42 | 29 | 298 | 8642 | 29 | 0.026825 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 29 | 0.026825 | 9.0017e-05
129105 | 2012-05-01 14:20 | 2012-05-01 14:58 | 4 | 35 | 140 | 4 | 0.00043456 | 1.2416e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 4 | 0.00043456 | 1.2416e-05
129107 | 2012-05-01 08:26 | 2012-05-01 09:22 | 57 | 53 | 1658.1429 | 31.2857 | 0.0051469 | 0.00017693 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 31.2857 | 0.0051469 | 0.00017693
129108 | 2012-05-01 09:00 | 2012-05-01 14:54 | 12 | 351 | 4212 | 12 | 0.013074 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | B | 12 | 0.013074 | 3.7248e-05
129110 | 2012-05-02 04:45 | 2012-05-02 06:44 | 325 | 116 | 30716.605 | 264.7983 | 0.095345 | 0.0010088 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 264.7983 | 0.095345 | 0.0010088
129111 | 2012-05-02 04:45 | 2012-05-02 10:46 | 79 | 358 | 22974.4765 | 64.1745 | 0.071313 | 0.00024522 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 64.1745 | 0.071313 | 0.00024522
129112 | 2012-05-02 09:45 | 2012-05-02 12:14 | 6 | 146 | 876 | 6 | 0.0027191 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 6 | 0.0027191 | 1.8624e-05
129115 | 2012-05-02 11:50 | 2012-05-02 12:19 | 304 | 26 | 7904 | 304 | 0.024534 | 0.00094362 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 304 | 0.024534 | 0.00094362
129116 | 2012-05-02 11:50 | 2012-05-02 14:47 | 708 | 174 | 72847.0169 | 418.661 | 0.22612 | 0.0021977 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 418.661 | 0.22612 | 0.0021977
129117 | 2012-05-02 09:16 | 2012-05-02 14:36 | 166 | 317 | 52622 | 166 | 0.16334 | 0.00051527 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 166 | 0.16334 | 0.00051527
129118 | 2012-05-02 09:03 | 2012-05-02 14:03 | 4 | 297 | 1188 | 4 | 0.0036876 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 4 | 0.0036876 | 1.2416e-05
129120 | 2012-05-02 09:25 | 2012-05-02 13:56 | 4 | 268 | 1072 | 4 | 0.0033275 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 4 | 0.0033275 | 1.2416e-05
129121 | 2012-05-02 10:30 | 2012-05-02 10:38 | 24 | 5 | 120 | 24 | 0.00037248 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 24 | 0.00037248 | 7.4497e-05
129122 | 2012-05-02 09:46 | 2012-05-02 15:06 | 1 | 317 | 317 | 1 | 0.00098398 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 1 | 0.00098398 | 3.104e-06
129124 | 2012-05-02 09:25 | 2012-05-02 14:55 | 24 | 327 | 7848 | 24 | 0.02436 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | B | 24 | 0.02436 | 7.4497e-05
129128 | 2012-05-02 10:06 | 2012-05-02 11:15 | 7 | 66 | 462 | 7 | 0.0014341 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-02 | 2013 | 2013 | 2012-05-02 | C | 7 | 0.0014341 | 2.1728e-05
129129 | 2012-05-03 08:10 | 2012-05-03 09:48 | 133 | 95 | 9029.8469 | 95.051 | 0.028029 | 0.00041284 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | C | 95.051 | 0.028029 | 0.00041284
129130 | 2012-05-03 10:20 | 2012-05-03 11:36 | 1 | 73 | 73 | 1 | 0.00022659 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 1 | 0.00022659 | 3.104e-06
129132 | 2012-05-03 09:53 | 2012-05-03 13:53 | 4 | 237 | 948 | 4 | 0.0029426 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 4 | 0.0029426 | 1.2416e-05
129133 | 2012-05-01 20:00 | 2012-05-02 00:20 | 8 | 257 | 2056 | 8 | 0.0063819 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 8 | 0.0063819 | 2.4832e-05
129134 | 2012-05-03 09:37 | 2012-05-03 14:22 | 1 | 282 | 282 | 1 | 0.00087534 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 1 | 0.00087534 | 3.104e-06
129137 | 2012-05-03 13:38 | 2012-05-03 14:13 | 87 | 32 | 2784 | 87 | 0.0086416 | 0.00027005 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | C | 87 | 0.0086416 | 0.00027005
129138 | 2012-05-03 10:00 | 2012-05-03 14:00 | 65 | 237 | 15405 | 65 | 0.047818 | 0.00020176 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 65 | 0.047818 | 0.00020176
129139 | 2012-05-03 09:16 | 2012-05-03 13:10 | 2 | 231 | 462 | 2 | 0.0014341 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 2 | 0.0014341 | 6.2081e-06
129140 | 2012-05-03 07:02 | 2012-05-03 07:13 | 5 | 8 | 40 | 5 | 0.00012416 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 5 | 0.00012416 | 1.552e-05
129142 | 2012-05-03 09:41 | 2012-05-03 15:51 | 172 | 367 | 63124 | 172 | 0.19594 | 0.00053389 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 172 | 0.19594 | 0.00053389
129145 | 2012-05-04 00:41 | 2012-05-04 02:27 | 146 | 103 | 9152.4245 | 88.8585 | 0.028409 | 0.00045319 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 88.8585 | 0.028409 | 0.00045319
129146 | 2012-05-04 11:46 | 2012-05-04 12:18 | 8 | 29 | 232 | 8 | 0.00072013 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 8 | 0.00072013 | 2.4832e-05
129149 | 2012-05-04 09:15 | 2012-05-04 10:15 | 3 | 57 | 171 | 3 | 0.00053079 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | B | 3 | 0.00053079 | 9.3121e-06
129152 | 2012-05-04 09:30 | 2012-05-04 14:37 | 26 | 304 | 7904 | 26 | 0.024534 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | B | 26 | 0.024534 | 8.0705e-05
129153 | 2012-05-04 09:30 | 2012-05-04 15:19 | 14 | 346 | 4844 | 14 | 0.015036 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | B | 14 | 0.015036 | 4.3456e-05
129154 | 2012-05-04 18:02 | 2012-05-04 19:00 | 11 | 55 | 605 | 11 | 0.0018779 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 11 | 0.0018779 | 3.4144e-05
129158 | 2012-05-04 20:05 | 2012-05-04 20:15 | 497 | 7 | 3479 | 497 | 0.010799 | 0.0015427 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 497 | 0.010799 | 0.0015427
129159 | 2012-05-04 15:49 | 2012-05-04 15:59 | 142 | 7 | 994 | 142 | 0.0030854 | 0.00044077 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 142 | 0.0030854 | 0.00044077
129160 | 2012-05-04 15:49 | 2012-05-04 15:59 | 136 | 7 | 952 | 136 | 0.002955 | 0.00042215 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-04 | 2013 | 2013 | 2012-05-04 | C | 136 | 0.002955 | 0.00042215
129161 | 2012-05-01 07:40 | 2012-05-01 07:45 | 839 | 2 | 1678 | 839 | 0.0052086 | 0.0026043 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 839 | 0.0052086 | 0.0026043
129162 | 2012-05-01 07:40 | 2012-05-01 07:45 | 672 | 2 | 1344 | 672 | 0.0041718 | 0.0020859 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-01 | 2013 | 2013 | 2012-05-01 | C | 672 | 0.0041718 | 0.0020859
129164 | 2012-05-05 09:30 | 2012-05-05 17:18 | 60 | 465 | 27900 | 60 | 0.086602 | 0.00018624 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | B | 60 | 0.086602 | 0.00018624
129166 | 2012-05-05 08:30 | 2012-05-05 16:40 | 48 | 487 | 23376 | 48 | 0.07256 | 0.00014899 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | B | 48 | 0.07256 | 0.00014899
129167 | 2012-05-05 12:45 | 2012-05-05 13:26 | 18 | 38 | 684 | 18 | 0.0021232 | 5.5873e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | C | 18 | 0.0021232 | 5.5873e-05
129169 | 2012-05-05 11:28 | 2012-05-05 12:24 | 72 | 53 | 2879.0357 | 54.3214 | 0.0089366 | 0.00022349 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | C | 54.3214 | 0.0089366 | 0.00022349
129170 | 2012-05-05 11:14 | 2012-05-05 11:29 | 122 | 12 | 1464 | 122 | 0.0045443 | 0.00037869 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | C | 122 | 0.0045443 | 0.00037869
129172 | 2012-05-06 06:25 | 2012-05-06 10:42 | 365 | 254 | 43555.5642 | 171.4786 | 0.1352 | 0.001133 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-06 | 2013 | 2013 | 2012-05-06 | C | 171.4786 | 0.1352 | 0.001133
129173 | 2012-05-06 06:18 | 2012-05-06 06:58 | 62 | 37 | 2294 | 62 | 0.0071206 | 0.00019245 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-06 | 2013 | 2013 | 2012-05-06 | C | 62 | 0.0071206 | 0.00019245
129174 | 2012-05-05 09:08 | 2012-05-05 13:36 | 14 | 265 | 3710 | 14 | 0.011516 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | B | 14 | 0.011516 | 4.3456e-05
129175 | 2012-05-05 07:57 | 2012-05-05 11:15 | 1360 | 195 | 235507.803 | 1207.7323 | 0.73102 | 0.0042215 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-05 | 2013 | 2013 | 2012-05-05 | C | 1207.7323 | 0.73102 | 0.0042215
129176 | 2012-05-06 19:36 | 2012-05-06 20:44 | 312 | 65 | 20280 | 312 | 0.06295 | 0.00096846 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-06 | 2013 | 2013 | 2012-05-06 | C | 312 | 0.06295 | 0.00096846
129181 | 2012-05-07 09:00 | 2012-05-07 11:19 | 1 | 136 | 136 | 1 | 0.00042215 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | B | 1 | 0.00042215 | 3.104e-06
129182 | 2012-05-07 09:00 | 2012-05-07 14:03 | 99 | 300 | 29700 | 99 | 0.09219 | 0.0003073 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | B | 99 | 0.09219 | 0.0003073
129183 | 2012-05-07 09:15 | 2012-05-07 14:30 | 4 | 312 | 1248 | 4 | 0.0038738 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | B | 4 | 0.0038738 | 1.2416e-05
129184 | 2012-05-07 09:20 | 2012-05-07 14:33 | 12 | 310 | 3720 | 12 | 0.011547 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | B | 12 | 0.011547 | 3.7248e-05
129185 | 2012-05-07 06:35 | 2012-05-07 07:39 | 590 | 61 | 35990 | 590 | 0.11171 | 0.0018314 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | C | 590 | 0.11171 | 0.0018314
129186 | 2012-05-07 13:08 | 2012-05-07 16:00 | 1 | 169 | 169 | 1 | 0.00052458 | 3.104e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | C | 1 | 0.00052458 | 3.104e-06
129188 | 2012-05-07 06:35 | 2012-05-07 08:25 | 626 | 107 | 66982 | 626 | 0.20791 | 0.0019431 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | C | 626 | 0.20791 | 0.0019431
129189 | 2012-05-07 11:50 | 2012-05-07 12:30 | 27 | 37 | 1073 | 29 | 0.0033306 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | C | 29 | 0.0033306 | 8.3809e-05
129193 | 2012-05-07 21:50 | 2012-05-07 23:25 | 2 | 92 | 184 | 2 | 0.00057114 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-07 | 2013 | 2013 | 2012-05-07 | C | 2 | 0.00057114 | 6.2081e-06
129197 | 2012-05-08 09:38 | 2012-05-08 10:02 | 14 | 21 | 294 | 14 | 0.00091258 | 4.3456e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 14 | 0.00091258 | 4.3456e-05
129198 | 2012-05-08 11:36 | 2012-05-08 12:25 | 31 | 46 | 1426 | 31 | 0.0044263 | 9.6225e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 31 | 0.0044263 | 9.6225e-05
129200 | 2012-05-08 09:00 | 2012-05-08 13:17 | 14 | 254 | 3556 | 14 | 0.011038 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | B | 14 | 0.011038 | 4.3456e-05
129203 | 2012-05-08 09:00 | 2012-05-08 15:23 | 129 | 380 | 49020 | 129 | 0.15216 | 0.00040042 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | B | 129 | 0.15216 | 0.00040042
129204 | 2012-05-08 09:00 | 2012-05-08 15:42 | 12 | 399 | 4788 | 12 | 0.014862 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | B | 12 | 0.014862 | 3.7248e-05
129208 | 2012-05-08 17:46 | 2012-05-08 18:00 | 47 | 11 | 528 | 48 | 0.0016389 | 0.00014589 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 48 | 0.0016389 | 0.00014589
129209 | 2012-05-08 18:55 | 2012-05-08 19:58 | 3 | 60 | 180 | 3 | 0.00055873 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 3 | 0.00055873 | 9.3121e-06
129210 | 2012-05-08 19:53 | 2012-05-08 21:37 | 35 | 101 | 3535 | 35 | 0.010973 | 0.00010864 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 35 | 0.010973 | 0.00010864
129211 | 2012-05-08 18:08 | 2012-05-08 21:22 | 46 | 191 | 8786 | 46 | 0.027272 | 0.00014279 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 46 | 0.027272 | 0.00014279
129212 | 2012-05-08 21:24 | 2012-05-09 01:26 | 589 | 239 | 29879.938 | 125.0207 | 0.092748 | 0.0018283 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-08 | 2013 | 2013 | 2012-05-08 | C | 125.0207 | 0.092748 | 0.0018283
129213 | 2012-05-09 00:45 | 2012-05-09 05:10 | 161 | 262 | 21814.2189 | 83.2604 | 0.067712 | 0.00049975 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 83.2604 | 0.067712 | 0.00049975
129216 | 2012-05-09 05:03 | 2012-05-09 10:10 | 1418 | 304 | 63402.3192 | 208.5603 | 0.1968 | 0.0044015 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 208.5603 | 0.1968 | 0.0044015
129217 | 2012-05-09 10:21 | 2012-05-09 12:01 | 596 | 97 | 36853.21 | 379.93 | 0.11439 | 0.00185 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 379.93 | 0.11439 | 0.00185
129218 | 2012-05-09 10:05 | 2012-05-09 12:30 | 2 | 142 | 284 | 2 | 0.00088154 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | B | 2 | 0.00088154 | 6.2081e-06
129219 | 2012-05-09 01:41 | 2012-05-09 08:40 | 922 | 416 | 79933.5561 | 192.148 | 0.24812 | 0.0028619 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 192.148 | 0.24812 | 0.0028619
129222 | 2012-05-09 09:12 | 2012-05-09 13:59 | 7 | 284 | 1988 | 7 | 0.0061708 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | B | 7 | 0.0061708 | 2.1728e-05
129223 | 2012-05-09 13:36 | 2012-05-09 13:57 | 75 | 18 | 1350 | 75 | 0.0041904 | 0.0002328 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 75 | 0.0041904 | 0.0002328
129224 | 2012-05-09 09:13 | 2012-05-09 10:01 | 1 | 45 | 45 | 1 | 0.00013968 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 1 | 0.00013968 | 3.104e-06
129226 | 2012-05-09 10:00 | 2012-05-09 11:04 | 9 | 61 | 549 | 9 | 0.0017041 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 9 | 0.0017041 | 2.7936e-05
129227 | 2012-05-09 09:13 | 2012-05-09 09:35 | 144 | 19 | 2888 | 152 | 0.0089644 | 0.00044698 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 152 | 0.0089644 | 0.00044698
129228 | 2012-05-09 12:03 | 2012-05-09 15:08 | 163 | 182 | 29666 | 163 | 0.092084 | 0.00050596 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | B | 163 | 0.092084 | 0.00050596
129229 | 2012-05-09 13:10 | 2012-05-09 15:00 | 3 | 107 | 321 | 3 | 0.00099639 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | B | 3 | 0.00099639 | 9.3121e-06
129230 | 2012-05-09 09:25 | 2012-05-09 15:00 | 97 | 332 | 32204 | 97 | 0.099962 | 0.00030109 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | B | 97 | 0.099962 | 0.00030109
129231 | 2012-05-09 14:24 | 2012-05-09 18:55 | 1 | 268 | 268 | 1 | 0.00083188 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 1 | 0.00083188 | 3.104e-06
129233 | 2012-05-09 09:13 | 2012-05-09 09:30 | 2193 | 14 | 30590 | 2185 | 0.094952 | 0.0068071 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-09 | 2013 | 2013 | 2012-05-09 | C | 2185 | 0.094952 | 0.0068071
129234 | 2012-05-10 09:40 | 2012-05-10 12:20 | 17 | 157 | 2669 | 17 | 0.0082847 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 17 | 0.0082847 | 5.2768e-05
129235 | 2012-05-10 09:10 | 2012-05-10 11:27 | 69 | 134 | 9246 | 69 | 0.0287 | 0.00021418 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 69 | 0.0287 | 0.00021418
129237 | 2012-05-10 08:30 | 2012-05-10 13:04 | 14 | 271 | 3794 | 14 | 0.011777 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 14 | 0.011777 | 4.3456e-05
129238 | 2012-05-10 09:30 | 2012-05-10 14:33 | 172 | 300 | 51600 | 172 | 0.16017 | 0.00053389 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 172 | 0.16017 | 0.00053389
129239 | 2012-05-10 09:00 | 2012-05-10 15:36 | 1 | 393 | 393 | 1 | 0.0012199 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 1 | 0.0012199 | 3.104e-06
129242 | 2012-05-10 09:45 | 2012-05-10 16:41 | 13 | 413 | 5369 | 13 | 0.016666 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 13 | 0.016666 | 4.0352e-05
129243 | 2012-05-10 09:15 | 2012-05-10 13:00 | 6 | 222 | 1332 | 6 | 0.0041346 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 6 | 0.0041346 | 1.8624e-05
129244 | 2012-05-10 13:00 | 2012-05-10 15:25 | 3 | 142 | 426 | 3 | 0.0013223 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 3 | 0.0013223 | 9.3121e-06
129245 | 2012-05-10 14:16 | 2012-05-10 16:39 | 295 | 140 | 22434.2657 | 160.2448 | 0.069637 | 0.00091569 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | C | 160.2448 | 0.069637 | 0.00091569
129248 | 2012-05-10 09:27 | 2012-05-10 15:08 | 20 | 338 | 6760 | 20 | 0.020983 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | B | 20 | 0.020983 | 6.2081e-05
129249 | 2012-05-03 09:10 | 2012-05-03 15:48 | 3 | 395 | 1185 | 3 | 0.0036783 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-03 | 2013 | 2013 | 2012-05-03 | B | 3 | 0.0036783 | 9.3121e-06
129250 | 2012-05-10 10:27 | 2012-05-10 13:23 | 93 | 173 | 15916 | 92 | 0.049404 | 0.00028867 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-10 | 2013 | 2013 | 2012-05-10 | C | 92 | 0.049404 | 0.00028867
129252 | 2012-05-11 08:30 | 2012-05-11 14:40 | 13 | 367 | 4771 | 13 | 0.014809 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | B | 13 | 0.014809 | 4.0352e-05
129254 | 2012-05-11 09:00 | 2012-05-11 14:45 | 11 | 342 | 3762 | 11 | 0.011677 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | B | 11 | 0.011677 | 3.4144e-05
129259 | 2012-05-11 09:20 | 2012-05-11 15:00 | 29 | 337 | 9773 | 29 | 0.030336 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | B | 29 | 0.030336 | 9.0017e-05
129260 | 2012-05-11 14:50 | 2012-05-11 16:36 | 164 | 103 | 13908.8868 | 135.0377 | 0.043174 | 0.00050906 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | C | 135.0377 | 0.043174 | 0.00050906
129261 | 2012-05-11 12:53 | 2012-05-11 14:13 | 1 | 77 | 77 | 1 | 0.00023901 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | C | 1 | 0.00023901 | 3.104e-06
129262 | 2012-05-11 15:25 | 2012-05-11 17:28 | 294 | 120 | 32085.8537 | 267.3821 | 0.099595 | 0.00091258 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-11 | 2013 | 2013 | 2012-05-11 | C | 267.3821 | 0.099595 | 0.00091258
129269 | 2012-05-13 04:32 | 2012-05-13 06:22 | 2745 | 107 | 282380.7818 | 2639.0727 | 0.87652 | 0.0085206 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-13 | 2013 | 2013 | 2012-05-13 | C | 2639.0727 | 0.87652 | 0.0085206
129271 | 2012-05-13 15:34 | 2012-05-13 17:12 | 10 | 95 | 950 | 10 | 0.0029488 | 3.104e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-13 | 2013 | 2013 | 2012-05-13 | C | 10 | 0.0029488 | 3.104e-05
129272 | 2012-05-13 18:05 | 2012-05-13 18:40 | 204 | 32 | 6528 | 204 | 0.020263 | 0.00063322 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-13 | 2013 | 2013 | 2012-05-13 | C | 204 | 0.020263 | 0.00063322
129273 | 2012-05-13 20:00 | 2012-05-13 21:10 | 7 | 67 | 469 | 7 | 0.0014558 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-13 | 2013 | 2013 | 2012-05-13 | C | 7 | 0.0014558 | 2.1728e-05
129276 | 2012-05-14 03:01 | 2012-05-14 06:00 | 768 | 176 | 56329.8324 | 320.0559 | 0.17485 | 0.0023839 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 320.0559 | 0.17485 | 0.0023839
129278 | 2012-05-14 09:00 | 2012-05-14 11:08 | 779 | 125 | 60773.4375 | 486.1875 | 0.18864 | 0.002418 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 486.1875 | 0.18864 | 0.002418
129279 | 2012-05-14 10:00 | 2012-05-14 13:44 | 33 | 221 | 7293 | 33 | 0.022638 | 0.00010243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | B | 33 | 0.022638 | 0.00010243
129281 | 2012-05-14 09:00 | 2012-05-14 12:10 | 20 | 187 | 3740 | 20 | 0.011609 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | B | 20 | 0.011609 | 6.2081e-05
129283 | 2012-05-14 11:33 | 2012-05-14 12:20 | 17 | 44 | 748 | 17 | 0.0023218 | 5.2768e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 17 | 0.0023218 | 5.2768e-05
129289 | 2012-05-14 18:22 | 2012-05-14 19:16 | 11 | 51 | 561 | 11 | 0.0017414 | 3.4144e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 11 | 0.0017414 | 3.4144e-05
129290 | 2012-05-14 18:25 | 2012-05-14 21:24 | 1 | 176 | 176 | 1 | 0.00054631 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 1 | 0.00054631 | 3.104e-06
129292 | 2012-05-14 22:35 | 2012-05-14 23:46 | 4 | 68 | 272 | 4 | 0.0008443 | 1.2416e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 4 | 0.0008443 | 1.2416e-05
129293 | 2012-05-15 03:56 | 2012-05-15 04:03 | 78 | 4 | 312 | 78 | 0.00096846 | 0.00024211 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 78 | 0.00096846 | 0.00024211
129297 | 2012-05-15 09:33 | 2012-05-15 10:09 | 63 | 33 | 2046 | 62 | 0.0063508 | 0.00019555 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 62 | 0.0063508 | 0.00019555
129298 | 2012-05-15 10:43 | 2012-05-15 11:19 | 2 | 33 | 66 | 2 | 0.00020487 | 6.2081e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 2 | 0.00020487 | 6.2081e-06
129299 | 2012-05-15 08:30 | 2012-05-15 11:30 | 8 | 177 | 1416 | 8 | 0.0043953 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 8 | 0.0043953 | 2.4832e-05
129300 | 2012-05-15 09:13 | 2012-05-15 12:53 | 8 | 217 | 1736 | 8 | 0.0053886 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 8 | 0.0053886 | 2.4832e-05
129301 | 2012-05-15 08:30 | 2012-05-15 12:25 | 41 | 232 | 9512 | 41 | 0.029526 | 0.00012727 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 41 | 0.029526 | 0.00012727
129302 | 2012-05-15 09:15 | 2012-05-15 13:20 | 6 | 242 | 1452 | 6 | 0.004507 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 6 | 0.004507 | 1.8624e-05
129303 | 2012-05-15 08:30 | 2012-05-15 16:15 | 3 | 462 | 1386 | 3 | 0.0043022 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 3 | 0.0043022 | 9.3121e-06
129304 | 2012-05-15 09:00 | 2012-05-15 15:27 | 21 | 384 | 8064 | 21 | 0.025031 | 6.5185e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 21 | 0.025031 | 6.5185e-05
129305 | 2012-05-15 09:00 | 2012-05-15 15:23 | 57 | 380 | 21660 | 57 | 0.067233 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 57 | 0.067233 | 0.00017693
129306 | 2012-05-15 09:10 | 2012-05-15 15:14 | 17 | 361 | 6137 | 17 | 0.019049 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | B | 17 | 0.019049 | 5.2768e-05
129307 | 2012-05-14 09:30 | 2012-05-14 13:30 | 41 | 237 | 9717 | 41 | 0.030162 | 0.00012727 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | B | 41 | 0.030162 | 0.00012727
129308 | 2012-05-15 12:26 | 2012-05-15 13:20 | 352 | 51 | 9746.6667 | 191.1111 | 0.030254 | 0.0010926 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 191.1111 | 0.030254 | 0.0010926
129309 | 2012-05-14 22:30 | 2012-05-15 11:00 | 2 | 747 | 1494 | 2 | 0.0046374 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-14 | 2013 | 2013 | 2012-05-14 | C | 2 | 0.0046374 | 6.2081e-06
129310 | 2012-05-15 16:03 | 2012-05-15 16:35 | 351 | 29 | 6380 | 220 | 0.019804 | 0.0010895 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 220 | 0.019804 | 0.0010895
129311 | 2012-05-15 20:34 | 2012-05-15 23:08 | 346 | 151 | 20992.9221 | 139.026 | 0.065163 | 0.001074 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-15 | 2013 | 2013 | 2012-05-15 | C | 139.026 | 0.065163 | 0.001074
129314 | 2012-05-16 09:00 | 2012-05-16 11:39 | 223 | 156 | 23476.5283 | 150.4906 | 0.072872 | 0.0006922 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 150.4906 | 0.072872 | 0.0006922
129316 | 2012-05-16 09:00 | 2012-05-16 12:00 | 37 | 177 | 6549 | 37 | 0.020328 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | B | 37 | 0.020328 | 0.00011485
129318 | 2012-05-16 09:00 | 2012-05-16 15:00 | 57 | 357 | 20349 | 57 | 0.063164 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | B | 57 | 0.063164 | 0.00017693
129319 | 2012-05-16 10:00 | 2012-05-16 13:55 | 31 | 232 | 7192 | 31 | 0.022324 | 9.6225e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | B | 31 | 0.022324 | 9.6225e-05
129320 | 2012-05-16 11:32 | 2012-05-16 13:26 | 5 | 111 | 555 | 5 | 0.0017227 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 5 | 0.0017227 | 1.552e-05
129321 | 2012-05-16 13:00 | 2012-05-16 14:38 | 187 | 95 | 13546.2245 | 142.5918 | 0.042048 | 0.00058045 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 142.5918 | 0.042048 | 0.00058045
129323 | 2012-05-16 15:05 | 2012-05-16 17:43 | 19 | 155 | 2945 | 19 | 0.0091414 | 5.8977e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 19 | 0.0091414 | 5.8977e-05
129324 | 2012-05-16 20:08 | 2012-05-16 22:15 | 42 | 124 | 5208 | 42 | 0.016166 | 0.00013037 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 42 | 0.016166 | 0.00013037
129327 | 2012-05-16 09:19 | 2012-05-16 10:53 | 155 | 91 | 14105 | 155 | 0.043782 | 0.00048112 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | B | 155 | 0.043782 | 0.00048112
129328 | 2012-05-17 09:00 | 2012-05-17 10:37 | 14 | 94 | 1316 | 14 | 0.0040849 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 14 | 0.0040849 | 4.3456e-05
129329 | 2012-05-16 10:04 | 2012-05-16 17:47 | 3 | 460 | 1380 | 3 | 0.0042836 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 3 | 0.0042836 | 9.3121e-06
129330 | 2012-05-17 10:00 | 2012-05-17 11:37 | 3 | 94 | 282 | 3 | 0.00087534 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 3 | 0.00087534 | 9.3121e-06
129331 | 2012-05-17 09:15 | 2012-05-17 13:58 | 17 | 280 | 4760 | 17 | 0.014775 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 17 | 0.014775 | 5.2768e-05
129332 | 2012-05-17 09:00 | 2012-05-17 13:38 | 57 | 275 | 15675 | 57 | 0.048656 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 57 | 0.048656 | 0.00017693
129333 | 2012-05-17 12:48 | 2012-05-17 13:52 | 24 | 61 | 1464 | 24 | 0.0045443 | 7.4497e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 24 | 0.0045443 | 7.4497e-05
129334 | 2012-05-17 09:15 | 2012-05-17 15:06 | 99 | 348 | 34452 | 99 | 0.10694 | 0.0003073 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 99 | 0.10694 | 0.0003073
129336 | 2012-05-17 09:27 | 2012-05-17 15:10 | 32 | 340 | 10880 | 32 | 0.033772 | 9.9329e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 32 | 0.033772 | 9.9329e-05
129337 | 2012-05-17 09:35 | 2012-05-17 12:28 | 4 | 170 | 680 | 4 | 0.0021107 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 4 | 0.0021107 | 1.2416e-05
129338 | 2012-05-17 13:15 | 2012-05-17 15:05 | 8 | 107 | 856 | 8 | 0.002657 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 8 | 0.002657 | 2.4832e-05
129339 | 2012-05-17 09:00 | 2012-05-17 14:54 | 4 | 351 | 1404 | 4 | 0.0043581 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 4 | 0.0043581 | 1.2416e-05
129342 | 2012-05-17 09:01 | 2012-05-17 12:54 | 28 | 230 | 6440 | 28 | 0.01999 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 28 | 0.01999 | 8.6913e-05
129343 | 2012-05-17 10:30 | 2012-05-17 16:23 | 92 | 350 | 32200 | 92 | 0.09995 | 0.00028557 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | B | 92 | 0.09995 | 0.00028557
129344 | 2012-05-17 12:47 | 2012-05-17 15:24 | 218 | 154 | 17884.5987 | 116.1338 | 0.055514 | 0.00067668 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 116.1338 | 0.055514 | 0.00067668
129346 | 2012-05-17 12:02 | 2012-05-17 16:45 | 6 | 280 | 1680 | 6 | 0.0052148 | 1.8624e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 6 | 0.0052148 | 1.8624e-05
129347 | 2012-05-17 16:28 | 2012-05-17 17:03 | 900 | 32 | 24492.8 | 765.4 | 0.076026 | 0.0027936 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 765.4 | 0.076026 | 0.0027936
129348 | 2012-05-17 14:45 | 2012-05-17 18:20 | 5 | 212 | 1060 | 5 | 0.0032903 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 5 | 0.0032903 | 1.552e-05
129350 | 2012-05-18 06:51 | 2012-05-18 15:39 | 13 | 525 | 6825 | 13 | 0.021185 | 4.0352e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | C | 13 | 0.021185 | 4.0352e-05
129352 | 2012-05-17 17:30 | 2012-05-18 08:56 | 189 | 923 | 19494.6371 | 21.121 | 0.060512 | 0.00058666 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-17 | 2013 | 2013 | 2012-05-17 | C | 21.121 | 0.060512 | 0.00058666
129353 | 2012-05-18 09:50 | 2012-05-18 14:42 | 14 | 289 | 4046 | 14 | 0.012559 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 14 | 0.012559 | 4.3456e-05
129356 | 2012-05-18 09:05 | 2012-05-18 14:58 | 5 | 350 | 1750 | 5 | 0.005432 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 5 | 0.005432 | 1.552e-05
129357 | 2012-05-18 13:55 | 2012-05-18 15:46 | 5 | 108 | 540 | 5 | 0.0016762 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 5 | 0.0016762 | 1.552e-05
129359 | 2012-05-18 08:30 | 2012-05-18 15:42 | 20 | 429 | 4614.7292 | 10.7569 | 0.014324 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 10.7569 | 0.014324 | 6.2081e-05
129360 | 2012-05-16 08:58 | 2012-05-16 13:10 | 2 | 249 | 498 | 2 | 0.0015458 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | B | 2 | 0.0015458 | 6.2081e-06
129362 | 2012-05-18 10:18 | 2012-05-18 14:10 | 5 | 229 | 1145 | 5 | 0.0035541 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 5 | 0.0035541 | 1.552e-05
129363 | 2012-05-18 10:30 | 2012-05-18 14:00 | 3 | 207 | 621 | 3 | 0.0019276 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | C | 3 | 0.0019276 | 9.3121e-06
129365 | 2012-05-18 17:01 | 2012-05-18 17:40 | 51 | 36 | 1836 | 51 | 0.005699 | 0.00015831 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | C | 51 | 0.005699 | 0.00015831
129366 | 2012-05-18 16:31 | 2012-05-18 19:16 | 110 | 162 | 12720.4364 | 78.5212 | 0.039485 | 0.00034144 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | C | 78.5212 | 0.039485 | 0.00034144
129367 | 2012-05-19 10:10 | 2012-05-19 14:00 | 183 | 227 | 9563.6087 | 42.1304 | 0.029686 | 0.00056804 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-19 | 2013 | 2013 | 2012-05-19 | C | 42.1304 | 0.029686 | 0.00056804
129369 | 2012-05-19 08:30 | 2012-05-19 13:01 | 17 | 268 | 4556 | 17 | 0.014142 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-19 | 2013 | 2013 | 2012-05-19 | B | 17 | 0.014142 | 5.2768e-05
129370 | 2012-05-19 14:39 | 2012-05-19 14:47 | 1 | 5 | 5 | 1 | 1.552e-05 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-19 | 2013 | 2013 | 2012-05-19 | C | 1 | 1.552e-05 | 3.104e-06
129372 | 2012-05-20 01:57 | 2012-05-20 03:54 | 362 | 114 | 29530.8718 | 259.0427 | 0.091665 | 0.0011237 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-20 | 2013 | 2013 | 2012-05-20 | C | 259.0427 | 0.091665 | 0.0011237
129375 | 2012-05-20 15:14 | 2012-05-20 15:37 | 4 | 20 | 80 | 4 | 0.00024832 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-20 | 2013 | 2013 | 2012-05-20 | C | 4 | 0.00024832 | 1.2416e-05
129377 | 2012-05-16 17:53 | 2012-05-16 17:57 | 1141 | 1 | 1141 | 1141 | 0.0035417 | 0.0035417 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-16 | 2013 | 2013 | 2012-05-16 | C | 1141 | 0.0035417 | 0.0035417
129378 | 2012-05-21 10:33 | 2012-05-21 12:30 | 33 | 114 | 3762 | 33 | 0.011677 | 0.00010243 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | C | 33 | 0.011677 | 0.00010243
129381 | 2012-05-21 09:03 | 2012-05-21 14:34 | 11 | 328 | 3608 | 11 | 0.011199 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | B | 11 | 0.011199 | 3.4144e-05
129382 | 2012-05-21 13:22 | 2012-05-21 14:35 | 17 | 70 | 1190 | 17 | 0.0036938 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | B | 17 | 0.0036938 | 5.2768e-05
129383 | 2012-05-21 11:55 | 2012-05-21 13:02 | 8 | 64 | 512 | 8 | 0.0015893 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | B | 8 | 0.0015893 | 2.4832e-05
129384 | 2012-05-20 13:08 | 2012-05-20 13:30 | 7 | 19 | 133 | 7 | 0.00041284 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-20 | 2013 | 2013 | 2012-05-20 | C | 7 | 0.00041284 | 2.1728e-05
129385 | 2012-05-21 18:50 | 2012-05-23 14:35 | 3 | 2622 | 7866 | 3 | 0.024416 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | C | 3 | 0.024416 | 9.3121e-06
129387 | 2012-05-21 19:55 | 2012-05-21 22:49 | 1 | 171 | 171 | 1 | 0.00053079 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | C | 1 | 0.00053079 | 3.104e-06
129388 | 2012-05-21 22:31 | 2012-05-21 23:35 | 26 | 61 | 1586 | 26 | 0.004923 | 8.0705e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | C | 26 | 0.004923 | 8.0705e-05
129391 | 2012-05-21 10:09 | 2012-05-21 13:05 | 17 | 173 | 2941 | 17 | 0.0091289 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-21 | 2013 | 2013 | 2012-05-21 | C | 17 | 0.0091289 | 5.2768e-05
129394 | 2012-05-22 08:30 | 2012-05-22 12:20 | 89 | 227 | 20203 | 89 | 0.062711 | 0.00027626 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 89 | 0.062711 | 0.00027626
129396 | 2012-05-22 10:25 | 2012-05-22 12:30 | 9 | 122 | 1098 | 9 | 0.0034082 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 9 | 0.0034082 | 2.7936e-05
129397 | 2012-05-22 08:30 | 2012-05-22 13:31 | 1 | 298 | 298 | 1 | 0.000925 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 1 | 0.000925 | 3.104e-06
129398 | 2012-05-22 09:00 | 2012-05-22 14:55 | 57 | 352 | 20064 | 57 | 0.062279 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 57 | 0.062279 | 0.00017693
129399 | 2012-05-22 11:50 | 2012-05-22 14:52 | 17 | 179 | 3043 | 17 | 0.0094456 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | C | 17 | 0.0094456 | 5.2768e-05
129400 | 2012-05-22 09:15 | 2012-05-22 15:29 | 11 | 371 | 4081 | 11 | 0.012668 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 11 | 0.012668 | 3.4144e-05
129401 | 2012-05-22 10:14 | 2012-05-22 15:42 | 39 | 325 | 12675 | 39 | 0.039344 | 0.00012106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-22 | 2013 | 2013 | 2012-05-22 | B | 39 | 0.039344 | 0.00012106
129405 | 2012-05-23 01:29 | 2012-05-23 02:30 | 849 | 58 | 28071.0492 | 483.9836 | 0.087133 | 0.0026353 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | C | 483.9836 | 0.087133 | 0.0026353
129406 | 2012-05-23 13:48 | 2012-05-23 14:36 | 12 | 45 | 540 | 12 | 0.0016762 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | C | 12 | 0.0016762 | 3.7248e-05
129407 | 2012-05-23 09:00 | 2012-05-23 14:36 | 92 | 333 | 30636 | 92 | 0.095095 | 0.00028557 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 92 | 0.095095 | 0.00028557
129409 | 2012-05-23 14:18 | 2012-05-23 15:24 | 1 | 63 | 63 | 1 | 0.00019555 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 1 | 0.00019555 | 3.104e-06
129410 | 2012-05-23 09:04 | 2012-05-23 15:30 | 122 | 383 | 46726 | 122 | 0.14504 | 0.00037869 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 122 | 0.14504 | 0.00037869
129412 | 2012-05-23 12:30 | 2012-05-23 13:32 | 1 | 59 | 59 | 1 | 0.00018314 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 1 | 0.00018314 | 3.104e-06
129413 | 2012-05-23 09:03 | 2012-05-23 13:23 | 34 | 257 | 8738 | 34 | 0.027123 | 0.00010554 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 34 | 0.027123 | 0.00010554
129414 | 2012-05-23 09:22 | 2012-05-23 16:05 | 3 | 400 | 1200 | 3 | 0.0037248 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | B | 3 | 0.0037248 | 9.3121e-06
129415 | 2012-05-23 14:02 | 2012-05-23 18:38 | 57 | 273 | 15561 | 57 | 0.048302 | 0.00017693 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | C | 57 | 0.048302 | 0.00017693
129416 | 2012-05-23 15:47 | 2012-05-23 17:00 | 1033 | 70 | 65420.274 | 934.5753 | 0.20307 | 0.0032065 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-23 | 2013 | 2013 | 2012-05-23 | C | 934.5753 | 0.20307 | 0.0032065
129417 | 2012-05-24 09:00 | 2012-05-24 13:53 | 57 | 290 | 16530 | 57 | 0.05131 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 57 | 0.05131 | 0.00017693
129418 | 2012-05-24 10:13 | 2012-05-24 14:45 | 7 | 269 | 1883 | 7 | 0.0058449 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 7 | 0.0058449 | 2.1728e-05
129419 | 2012-05-24 09:14 | 2012-05-24 14:55 | 28 | 338 | 9464 | 28 | 0.029377 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 28 | 0.029377 | 8.6913e-05
129420 | 2012-05-24 10:00 | 2012-05-24 14:12 | 50 | 249 | 12450 | 50 | 0.038645 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 50 | 0.038645 | 0.0001552
129421 | 2012-05-24 09:30 | 2012-05-24 15:30 | 74 | 357 | 26418 | 74 | 0.082002 | 0.0002297 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 74 | 0.082002 | 0.0002297
129422 | 2012-05-24 09:06 | 2012-05-24 16:05 | 12 | 416 | 4992 | 12 | 0.015495 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 12 | 0.015495 | 3.7248e-05
129423 | 2012-05-24 12:58 | 2012-05-24 16:55 | 339 | 234 | 16361.2405 | 69.9198 | 0.050786 | 0.0010523 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | C | 69.9198 | 0.050786 | 0.0010523
129424 | 2012-05-24 17:58 | 2012-05-24 19:05 | 2 | 64 | 128 | 2 | 0.00039732 | 6.2081e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | C | 2 | 0.00039732 | 6.2081e-06
129425 | 2012-05-25 09:19 | 2012-05-25 10:14 | 57 | 52 | 2964 | 57 | 0.0092003 | 0.00017693 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | C | 57 | 0.0092003 | 0.00017693
129427 | 2012-05-25 09:15 | 2012-05-25 12:20 | 1 | 182 | 182 | 1 | 0.00056493 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | B | 1 | 0.00056493 | 3.104e-06
129429 | 2012-05-25 12:05 | 2012-05-25 13:41 | 22 | 93 | 2046 | 22 | 0.0063508 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | B | 22 | 0.0063508 | 6.8289e-05
129430 | 2012-05-25 10:08 | 2012-05-25 14:25 | 230 | 254 | 58420 | 230 | 0.18134 | 0.00071393 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | B | 230 | 0.18134 | 0.00071393
129432 | 2012-05-25 09:00 | 2012-05-25 15:33 | 122 | 390 | 47580 | 122 | 0.14769 | 0.00037869 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | B | 122 | 0.14769 | 0.00037869
129434 | 2012-05-25 15:41 | 2012-05-25 16:10 | 3 | 26 | 78 | 3 | 0.00024211 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | C | 3 | 0.00024211 | 9.3121e-06
129436 | 2012-05-25 15:58 | 2012-05-25 17:40 | 114 | 99 | 10897.7647 | 110.0784 | 0.033827 | 0.00035386 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | C | 110.0784 | 0.033827 | 0.00035386
129441 | 2012-05-26 09:53 | 2012-05-26 10:35 | 5 | 39 | 195 | 5 | 0.00060529 | 1.552e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-26 | 2013 | 2013 | 2012-05-26 | C | 5 | 0.00060529 | 1.552e-05
129442 | 2012-05-25 15:37 | 2012-05-26 12:24 | 1 | 1244 | 1244 | 1 | 0.0038614 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | C | 1 | 0.0038614 | 3.104e-06
129444 | 2012-05-26 10:00 | 2012-05-26 17:27 | 1 | 444 | 444 | 1 | 0.0013782 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-26 | 2013 | 2013 | 2012-05-26 | B | 1 | 0.0013782 | 3.104e-06
129445 | 2012-05-26 06:19 | 2012-05-26 17:10 | 481 | 648 | 31484.2396 | 48.5868 | 0.097728 | 0.001493 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-26 | 2013 | 2013 | 2012-05-26 | C | 48.5868 | 0.097728 | 0.001493
129447 | 2012-05-26 21:27 | 2012-05-26 23:20 | 1 | 110 | 110 | 1 | 0.00034144 | 3.104e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-26 | 2013 | 2013 | 2012-05-26 | C | 1 | 0.00034144 | 3.104e-06
129448 | 2012-05-27 09:16 | 2012-05-27 10:39 | 3 | 80 | 240 | 3 | 0.00074497 | 9.3121e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-05-27 | 2013 | 2013 | 2012-05-27 | C | 3 | 0.00074497 | 9.3121e-06
129449 | 2012-05-27 11:19 | 2012-05-27 12:21 | 36 | 59 | 2124 | 36 | 0.006593 | 0.00011175 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-27 | 2013 | 2013 | 2012-05-27 | C | 36 | 0.006593 | 0.00011175
129450 | 2012-05-27 01:39 | 2012-05-27 02:07 | 903 | 25 | 18291.9643 | 731.6786 | 0.056779 | 0.0028029 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-27 | 2013 | 2013 | 2012-05-27 | C | 731.6786 | 0.056779 | 0.0028029
129456 | 2012-05-27 15:53 | 2012-05-27 16:26 | 159 | 30 | 4770 | 159 | 0.014806 | 0.00049354 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-27 | 2013 | 2013 | 2012-05-27 | C | 159 | 0.014806 | 0.00049354
129457 | 2012-05-27 17:52 | 2012-05-27 21:54 | 71 | 239 | 10901.1653 | 45.6116 | 0.033838 | 0.00022039 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-27 | 2013 | 2013 | 2012-05-27 | C | 45.6116 | 0.033838 | 0.00022039
129458 | 2012-05-25 09:15 | 2012-05-25 13:39 | 1 | 261 | 261 | 1 | 0.00081015 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-25 | 2013 | 2013 | 2012-05-25 | B | 1 | 0.00081015 | 3.104e-06
129459 | 2012-05-24 22:30 | 2012-05-25 00:09 | 223 | 96 | 21408 | 223 | 0.066451 | 0.0006922 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-24 | 2013 | 2013 | 2012-05-24 | B | 223 | 0.066451 | 0.0006922
129460 | 2012-05-28 06:58 | 2012-05-28 09:28 | 1389 | 147 | 166821.48 | 1134.84 | 0.51782 | 0.0043115 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 1134.84 | 0.51782 | 0.0043115
129464 | 2012-05-28 09:24 | 2012-05-28 10:04 | 20 | 37 | 740 | 20 | 0.002297 | 6.2081e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 20 | 0.002297 | 6.2081e-05
129467 | 2012-05-28 10:00 | 2012-05-28 11:49 | 43 | 106 | 4558 | 43 | 0.014148 | 0.00013347 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | B | 43 | 0.014148 | 0.00013347
129468 | 2012-05-28 12:35 | 2012-05-28 13:13 | 32 | 35 | 1120 | 32 | 0.0034765 | 9.9329e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 32 | 0.0034765 | 9.9329e-05
129470 | 2012-05-28 09:00 | 2012-05-28 14:48 | 5 | 345 | 1725 | 5 | 0.0053544 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | B | 5 | 0.0053544 | 1.552e-05
129474 | 2012-05-28 10:20 | 2012-05-28 15:34 | 31 | 311 | 9641 | 31 | 0.029926 | 9.6225e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | B | 31 | 0.029926 | 9.6225e-05
129475 | 2012-05-28 15:44 | 2012-05-28 17:23 | 30 | 96 | 761.2121 | 7.9293 | 0.0023628 | 9.3121e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 7.9293 | 0.0023628 | 9.3121e-05
129477 | 2012-05-28 14:34 | 2012-05-28 15:13 | 751 | 36 | 26533.8462 | 737.0513 | 0.082362 | 0.0023311 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 737.0513 | 0.082362 | 0.0023311
129478 | 2012-05-28 17:16 | 2012-05-28 22:57 | 267 | 338 | 35503.8768 | 105.0411 | 0.11021 | 0.00082878 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 105.0411 | 0.11021 | 0.00082878
129479 | 2012-05-28 17:40 | 2012-05-29 00:12 | 111 | 389 | 43179 | 111 | 0.13403 | 0.00034455 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-28 | 2013 | 2013 | 2012-05-28 | C | 111 | 0.13403 | 0.00034455
129481 | 2012-05-29 09:35 | 2012-05-29 10:41 | 68 | 63 | 4284 | 68 | 0.013298 | 0.00021107 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | C | 68 | 0.013298 | 0.00021107
129483 | 2012-05-29 08:30 | 2012-05-29 15:57 | 164 | 444 | 72816 | 164 | 0.22602 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | B | 164 | 0.22602 | 0.00050906
129485 | 2012-05-29 08:35 | 2012-05-29 14:08 | 13 | 330 | 4290 | 13 | 0.013316 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | B | 13 | 0.013316 | 4.0352e-05
129488 | 2012-05-29 09:00 | 2012-05-29 14:53 | 39 | 350 | 13650 | 39 | 0.04237 | 0.00012106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | B | 39 | 0.04237 | 0.00012106
129489 | 2012-05-29 08:55 | 2012-05-29 11:10 | 5 | 132 | 660 | 5 | 0.0020487 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | B | 5 | 0.0020487 | 1.552e-05
129491 | 2012-05-29 16:36 | 2012-05-29 17:43 | 41 | 64 | 2624 | 41 | 0.008145 | 0.00012727 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | C | 41 | 0.008145 | 0.00012727
129493 | 2012-05-29 13:23 | 2012-05-29 14:42 | 45 | 76 | 3420 | 45 | 0.010616 | 0.00013968 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | C | 45 | 0.010616 | 0.00013968
129497 | 2012-05-29 09:00 | 2012-05-29 15:52 | 3 | 409 | 1227 | 3 | 0.0038086 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-29 | 2013 | 2013 | 2012-05-29 | B | 3 | 0.0038086 | 9.3121e-06
129499 | 2012-05-18 09:07 | 2012-05-18 16:17 | 36 | 427 | 15372 | 36 | 0.047715 | 0.00011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-18 | 2013 | 2013 | 2012-05-18 | B | 36 | 0.047715 | 0.00011175
129504 | 2012-05-30 10:53 | 2012-05-30 13:10 | 4 | 134 | 536 | 4 | 0.0016638 | 1.2416e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | C | 4 | 0.0016638 | 1.2416e-05
129505 | 2012-05-30 09:15 | 2012-05-30 15:20 | 54 | 362 | 19548 | 54 | 0.060678 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | B | 54 | 0.060678 | 0.00016762
129506 | 2012-05-30 09:30 | 2012-05-30 13:30 | 17 | 237 | 4029 | 17 | 0.012506 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | B | 17 | 0.012506 | 5.2768e-05
129507 | 2012-05-30 10:00 | 2012-05-30 13:38 | 28 | 215 | 6020 | 28 | 0.018686 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | B | 28 | 0.018686 | 8.6913e-05
129508 | 2012-05-30 12:00 | 2012-05-30 13:55 | 1 | 112 | 112 | 1 | 0.00034765 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | C | 1 | 0.00034765 | 3.104e-06
129509 | 2012-05-30 09:50 | 2012-05-30 13:30 | 6 | 217 | 1302 | 6 | 0.0040414 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | B | 6 | 0.0040414 | 1.8624e-05
129510 | 2012-05-30 11:25 | 2012-05-30 12:43 | 33 | 75 | 2475 | 33 | 0.0076825 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | C | 33 | 0.0076825 | 0.00010243
129511 | 2012-05-30 07:15 | 2012-05-30 09:21 | 26 | 123 | 3198 | 26 | 0.0099267 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-30 | 2013 | 2013 | 2012-05-30 | B | 26 | 0.0099267 | 8.0705e-05
129513 | 2012-05-31 09:50 | 2012-05-31 11:02 | 1 | 69 | 69 | 1 | 0.00021418 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | B | 1 | 0.00021418 | 3.104e-06
129515 | 2012-05-31 09:00 | 2012-05-31 13:10 | 1 | 247 | 247 | 1 | 0.0007667 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | B | 1 | 0.0007667 | 3.104e-06
129517 | 2012-05-31 09:00 | 2012-05-31 15:08 | 81 | 365 | 29565 | 81 | 0.091771 | 0.00025143 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | B | 81 | 0.091771 | 0.00025143
129518 | 2012-05-31 09:00 | 2012-05-31 15:24 | 169 | 381 | 64389 | 169 | 0.19987 | 0.00052458 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | B | 169 | 0.19987 | 0.00052458
129519 | 2012-05-31 09:58 | 2012-05-31 14:45 | 3 | 284 | 852 | 3 | 0.0026446 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | B | 3 | 0.0026446 | 9.3121e-06
129521 | 2012-05-31 18:08 | 2012-05-31 19:12 | 80 | 61 | 4880 | 80 | 0.015148 | 0.00024832 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-05-31 | 2013 | 2013 | 2012-05-31 | C | 80 | 0.015148 | 0.00024832
129523 | 2012-05-19 07:32 | 2012-05-19 15:51 | 1 | 496 | 496 | 1 | 0.0015396 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-19 | 2013 | 2013 | 2012-05-19 | B | 1 | 0.0015396 | 3.104e-06
129525 | 2012-06-01 08:15 | 2012-06-01 10:15 | 8 | 117 | 936 | 8 | 0.0029054 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 8 | 0.0029054 | 2.4832e-05
129526 | 2012-06-01 09:15 | 2012-06-01 10:41 | 5 | 83 | 415 | 5 | 0.0012882 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 5 | 0.0012882 | 1.552e-05
129527 | 2012-06-01 10:25 | 2012-06-01 10:33 | 421 | 5 | 2105 | 421 | 0.006534 | 0.0013068 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | C | 421 | 0.006534 | 0.0013068
129528 | 2012-06-01 09:30 | 2012-06-01 11:38 | 188 | 125 | 23500 | 188 | 0.072945 | 0.00058356 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 188 | 0.072945 | 0.00058356
129529 | 2012-06-01 09:06 | 2012-06-01 12:50 | 2 | 221 | 442 | 2 | 0.001372 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 2 | 0.001372 | 6.2081e-06
129530 | 2012-06-01 13:00 | 2012-06-01 13:35 | 98 | 32 | 3136 | 98 | 0.0097342 | 0.00030419 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 98 | 0.0097342 | 0.00030419
129532 | 2012-06-01 09:31 | 2012-06-01 14:15 | 29 | 281 | 8149 | 29 | 0.025295 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 29 | 0.025295 | 9.0017e-05
129536 | 2012-06-01 10:00 | 2012-06-01 15:13 | 217 | 310 | 67270 | 217 | 0.20881 | 0.00067357 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 217 | 0.20881 | 0.00067357
129537 | 2012-06-01 09:28 | 2012-06-01 15:52 | 24 | 381 | 9144 | 24 | 0.028383 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 24 | 0.028383 | 7.4497e-05
129538 | 2012-06-01 11:52 | 2012-06-01 16:22 | 24 | 267 | 6056.9444 | 22.6852 | 0.018801 | 7.4497e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | C | 22.6852 | 0.018801 | 7.4497e-05
129539 | 2012-06-01 08:30 | 2012-06-01 16:09 | 164 | 456 | 74784 | 164 | 0.23213 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-01 | 2013 | 2013 | 2012-06-01 | B | 164 | 0.23213 | 0.00050906
129542 | 2012-06-02 05:18 | 2012-06-02 11:05 | 413 | 344 | 40800.1844 | 118.6052 | 0.12664 | 0.001282 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-02 | 2013 | 2013 | 2012-06-02 | C | 118.6052 | 0.12664 | 0.001282
129544 | 2012-06-02 08:59 | 2012-06-02 09:49 | 78 | 47 | 2515.44 | 53.52 | 0.007808 | 0.00024211 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-02 | 2013 | 2013 | 2012-06-02 | C | 53.52 | 0.007808 | 0.00024211
129545 | 2012-06-02 02:49 | 2012-06-02 07:15 | 322 | 263 | 27783.0827 | 105.6391 | 0.086239 | 0.0009995 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-02 | 2013 | 2013 | 2012-06-02 | C | 105.6391 | 0.086239 | 0.0009995
129548 | 2012-06-02 21:15 | 2012-06-03 15:20 | 985 | 1082 | 63486.9733 | 58.6756 | 0.19707 | 0.0030575 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-02 | 2013 | 2013 | 2012-06-02 | C | 58.6756 | 0.19707 | 0.0030575
129550 | 2012-06-03 15:56 | 2012-06-03 17:20 | 24 | 81 | 1944 | 24 | 0.0060342 | 7.4497e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-03 | 2013 | 2013 | 2012-06-03 | C | 24 | 0.0060342 | 7.4497e-05
129551 | 2012-06-03 12:21 | 2012-06-03 13:15 | 16 | 51 | 816 | 16 | 0.0025329 | 4.9664e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-03 | 2013 | 2013 | 2012-06-03 | C | 16 | 0.0025329 | 4.9664e-05
129555 | 2012-06-03 18:33 | 2012-06-03 19:28 | 14 | 52 | 728 | 14 | 0.0022597 | 4.3456e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-03 | 2013 | 2013 | 2012-06-03 | C | 14 | 0.0022597 | 4.3456e-05
129556 | 2012-06-04 05:46 | 2012-06-04 07:10 | 148 | 81 | 9529.0714 | 117.6429 | 0.029579 | 0.0004594 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 117.6429 | 0.029579 | 0.0004594
129557 | 2012-06-04 10:00 | 2012-06-04 12:00 | 29 | 117 | 3393 | 29 | 0.010532 | 9.0017e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 29 | 0.010532 | 9.0017e-05
129558 | 2012-06-04 09:10 | 2012-06-04 15:20 | 7 | 367 | 2569 | 7 | 0.0079742 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 7 | 0.0079742 | 2.1728e-05
129561 | 2012-06-04 19:20 | 2012-06-04 21:29 | 67 | 126 | 7407.6279 | 58.7907 | 0.022993 | 0.00020797 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 58.7907 | 0.022993 | 0.00020797
129562 | 2012-06-04 22:20 | 2012-06-04 22:50 | 61 | 27 | 1647 | 61 | 0.0051123 | 0.00018935 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 61 | 0.0051123 | 0.00018935
129563 | 2012-06-04 22:45 | 2012-06-05 00:03 | 13 | 75 | 975 | 13 | 0.0030264 | 4.0352e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-04 | 2013 | 2013 | 2012-06-04 | C | 13 | 0.0030264 | 4.0352e-05
129565 | 2012-06-05 09:48 | 2012-06-05 10:18 | 8 | 27 | 216 | 8 | 0.00067047 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | C | 8 | 0.00067047 | 2.4832e-05
129566 | 2012-06-05 11:07 | 2012-06-05 12:51 | 25 | 101 | 2525 | 25 | 0.0078377 | 7.7601e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | C | 25 | 0.0078377 | 7.7601e-05
129569 | 2012-06-05 10:50 | 2012-06-05 12:00 | 9 | 67 | 603 | 9 | 0.0018717 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 9 | 0.0018717 | 2.7936e-05
129570 | 2012-06-05 13:14 | 2012-06-05 14:45 | 7 | 88 | 616 | 7 | 0.0019121 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 7 | 0.0019121 | 2.1728e-05
129572 | 2012-06-05 09:00 | 2012-06-05 16:34 | 10 | 451 | 4510 | 10 | 0.013999 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 10 | 0.013999 | 3.104e-05
129574 | 2012-06-05 09:14 | 2012-06-05 10:30 | 102 | 73 | 7446 | 102 | 0.023113 | 0.00031661 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 102 | 0.023113 | 0.00031661
129575 | 2012-06-05 10:44 | 2012-06-05 13:42 | 1 | 175 | 175 | 1 | 0.0005432 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 1 | 0.0005432 | 3.104e-06
129577 | 2012-06-05 17:36 | 2012-06-05 19:07 | 33 | 88 | 2904 | 33 | 0.0090141 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | C | 33 | 0.0090141 | 0.00010243
129578 | 2012-06-05 20:52 | 2012-06-06 00:05 | 276 | 190 | 16668.8083 | 87.7306 | 0.05174 | 0.00085671 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | C | 87.7306 | 0.05174 | 0.00085671
129580 | 2012-06-06 09:06 | 2012-06-06 13:43 | 39 | 274 | 10686 | 39 | 0.03317 | 0.00012106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 39 | 0.03317 | 0.00012106
129581 | 2012-06-06 09:04 | 2012-06-06 14:38 | 92 | 331 | 30452 | 92 | 0.094524 | 0.00028557 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 92 | 0.094524 | 0.00028557
129582 | 2012-06-05 08:30 | 2012-06-05 12:05 | 84 | 212 | 17808 | 84 | 0.055277 | 0.00026074 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 84 | 0.055277 | 0.00026074
129583 | 2012-06-06 09:17 | 2012-06-06 13:45 | 24 | 265 | 6360 | 24 | 0.019742 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 24 | 0.019742 | 7.4497e-05
129584 | 2012-06-06 09:02 | 2012-06-06 15:26 | 54 | 381 | 20574 | 54 | 0.063862 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 54 | 0.063862 | 0.00016762
129585 | 2012-06-06 09:00 | 2012-06-06 13:58 | 4 | 295 | 1180 | 4 | 0.0036628 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 4 | 0.0036628 | 1.2416e-05
129587 | 2012-06-06 07:55 | 2012-06-06 10:44 | 38 | 166 | 6308 | 38 | 0.01958 | 0.00011795 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | C | 38 | 0.01958 | 0.00011795
129588 | 2012-06-06 15:00 | 2012-06-06 19:07 | 1 | 244 | 244 | 1 | 0.00075738 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | C | 1 | 0.00075738 | 3.104e-06
129590 | 2012-06-07 09:00 | 2012-06-07 14:15 | 39 | 312 | 12168 | 39 | 0.03777 | 0.00012106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 39 | 0.03777 | 0.00012106
129591 | 2012-06-06 07:59 | 2012-06-06 08:18 | 8442 | 16 | 107715.3684 | 6732.2105 | 0.33435 | 0.026204 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | C | 6732.2105 | 0.33435 | 0.026204
129592 | 2012-06-07 09:15 | 2012-06-07 15:08 | 3 | 350 | 1050 | 3 | 0.0032592 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 3 | 0.0032592 | 9.3121e-06
129593 | 2012-06-07 10:25 | 2012-06-07 14:15 | 50 | 227 | 11350 | 50 | 0.035231 | 0.0001552 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 50 | 0.035231 | 0.0001552
129595 | 2012-06-07 12:17 | 2012-06-07 13:30 | 13 | 70 | 910 | 13 | 0.0028247 | 4.0352e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | C | 13 | 0.0028247 | 4.0352e-05
129596 | 2012-06-07 09:25 | 2012-06-07 12:15 | 13 | 167 | 2171 | 13 | 0.0067388 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 13 | 0.0067388 | 4.0352e-05
129597 | 2012-06-07 08:40 | 2012-06-07 15:14 | 37 | 391 | 14467 | 37 | 0.044906 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 37 | 0.044906 | 0.00011485
129598 | 2012-06-07 08:52 | 2012-06-07 12:49 | 365 | 234 | 27761.0886 | 118.6371 | 0.086171 | 0.001133 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | C | 118.6371 | 0.086171 | 0.001133
129601 | 2012-06-08 10:00 | 2012-06-08 13:56 | 36 | 233 | 8388 | 36 | 0.026037 | 0.00011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | B | 36 | 0.026037 | 0.00011175
129602 | 2012-06-07 08:45 | 2012-06-07 10:01 | 176 | 73 | 12848 | 176 | 0.039881 | 0.00054631 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | B | 176 | 0.039881 | 0.00054631
129603 | 2012-06-07 10:38 | 2012-06-08 14:35 | 1 | 1674 | 1674 | 1 | 0.0051961 | 3.104e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-07 | 2013 | 2013 | 2012-06-07 | C | 1 | 0.0051961 | 3.104e-06
129604 | 2012-06-08 08:30 | 2012-06-08 14:44 | 37 | 371 | 13727 | 37 | 0.042609 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | B | 37 | 0.042609 | 0.00011485
129605 | 2012-06-08 09:00 | 2012-06-08 15:51 | 6 | 408 | 2448 | 6 | 0.0075987 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | B | 6 | 0.0075987 | 1.8624e-05
129606 | 2012-06-08 14:55 | 2012-06-08 16:18 | 16 | 80 | 1280 | 16 | 0.0039732 | 4.9664e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | C | 16 | 0.0039732 | 4.9664e-05
129607 | 2012-06-08 10:30 | 2012-06-08 12:00 | 1 | 87 | 87 | 1 | 0.00027005 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | B | 1 | 0.00027005 | 3.104e-06
129613 | 2012-06-09 08:30 | 2012-06-09 10:37 | 3 | 124 | 372 | 3 | 0.0011547 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-09 | 2013 | 2013 | 2012-06-09 | B | 3 | 0.0011547 | 9.3121e-06
129614 | 2012-06-08 20:45 | 2012-06-09 10:45 | 4 | 837 | 3348 | 4 | 0.010392 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | C | 4 | 0.010392 | 1.2416e-05
129622 | 2012-06-10 09:08 | 2012-06-10 09:43 | 16 | 32 | 512 | 16 | 0.0015893 | 4.9664e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-10 | 2013 | 2013 | 2012-06-10 | C | 16 | 0.0015893 | 4.9664e-05
129625 | 2012-06-11 00:50 | 2012-06-11 01:20 | 209 | 27 | 5643 | 209 | 0.017516 | 0.00064874 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 209 | 0.017516 | 0.00064874
129628 | 2012-06-10 19:01 | 2012-06-10 23:41 | 4 | 277 | 1108 | 4 | 0.0034393 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-10 | 2013 | 2013 | 2012-06-10 | C | 4 | 0.0034393 | 1.2416e-05
129629 | 2012-06-10 03:07 | 2012-06-10 12:55 | 253 | 585 | 51329.7704 | 87.7432 | 0.15933 | 0.00078532 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-10 | 2013 | 2013 | 2012-06-10 | C | 87.7432 | 0.15933 | 0.00078532
129630 | 2012-06-11 09:10 | 2012-06-11 10:20 | 3 | 67 | 201 | 3 | 0.00062391 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 3 | 0.00062391 | 9.3121e-06
129631 | 2012-06-11 11:10 | 2012-06-11 11:20 | 255 | 7 | 1785 | 255 | 0.0055407 | 0.00079153 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 255 | 0.0055407 | 0.00079153
129632 | 2012-06-11 10:10 | 2012-06-11 11:48 | 5 | 95 | 475 | 5 | 0.0014744 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 5 | 0.0014744 | 1.552e-05
129633 | 2012-06-11 10:00 | 2012-06-11 12:20 | 218 | 137 | 12052.0857 | 87.9714 | 0.03741 | 0.00067668 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 87.9714 | 0.03741 | 0.00067668
129635 | 2012-06-11 12:45 | 2012-06-11 14:20 | 2 | 92 | 184 | 2 | 0.00057114 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 2 | 0.00057114 | 6.2081e-06
129637 | 2012-06-11 13:40 | 2012-06-11 16:00 | 301 | 137 | 20810.3 | 151.9 | 0.064596 | 0.00093431 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 151.9 | 0.064596 | 0.00093431
129638 | 2012-06-11 08:35 | 2012-06-11 15:28 | 164 | 410 | 67240 | 164 | 0.20871 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 164 | 0.20871 | 0.00050906
129639 | 2012-06-11 22:13 | 2012-06-11 22:23 | 37 | 7 | 259 | 37 | 0.00080394 | 0.00011485 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 37 | 0.00080394 | 0.00011485
129640 | 2012-06-11 16:00 | 2012-06-11 18:30 | 3 | 147 | 441 | 3 | 0.0013689 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | C | 3 | 0.0013689 | 9.3121e-06
129641 | 2012-06-12 10:05 | 2012-06-12 10:16 | 939 | 8 | 7512 | 939 | 0.023317 | 0.0029147 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | C | 939 | 0.023317 | 0.0029147
129642 | 2012-06-12 10:05 | 2012-06-12 10:16 | 324 | 8 | 477.8182 | 59.7273 | 0.0014832 | 0.0010057 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | C | 59.7273 | 0.0014832 | 0.0010057
129643 | 2012-06-12 17:00 | 2012-06-12 22:05 | 93 | 302 | 28086 | 93 | 0.08718 | 0.00028867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | C | 93 | 0.08718 | 0.00028867
129644 | 2012-06-12 09:20 | 2012-06-12 11:16 | 6 | 113 | 678 | 6 | 0.0021045 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 6 | 0.0021045 | 1.8624e-05
129645 | 2012-06-12 12:14 | 2012-06-12 14:09 | 15 | 112 | 1680 | 15 | 0.0052148 | 4.656e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | C | 15 | 0.0052148 | 4.656e-05
129646 | 2012-06-12 09:00 | 2012-06-12 14:00 | 48 | 297 | 14256 | 48 | 0.044251 | 0.00014899 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 48 | 0.044251 | 0.00014899
129649 | 2012-06-12 11:00 | 2012-06-12 14:17 | 9 | 194 | 1746 | 9 | 0.0054196 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 9 | 0.0054196 | 2.7936e-05
129650 | 2012-06-12 12:00 | 2012-06-12 15:25 | 13 | 202 | 2626 | 13 | 0.0081512 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 13 | 0.0081512 | 4.0352e-05
129651 | 2012-06-12 09:08 | 2012-06-12 14:38 | 25 | 327 | 8175 | 25 | 0.025375 | 7.7601e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 25 | 0.025375 | 7.7601e-05
129653 | 2012-06-12 09:33 | 2012-06-12 14:04 | 22 | 268 | 5896 | 22 | 0.018301 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 22 | 0.018301 | 6.8289e-05
129654 | 2012-06-12 09:00 | 2012-06-12 14:13 | 22 | 310 | 6820 | 22 | 0.021169 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 22 | 0.021169 | 6.8289e-05
129655 | 2012-06-12 08:40 | 2012-06-12 16:30 | 100 | 467 | 46700 | 100 | 0.14496 | 0.0003104 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 100 | 0.14496 | 0.0003104
129656 | 2012-06-12 09:10 | 2012-06-12 10:30 | 6 | 77 | 462 | 6 | 0.0014341 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 6 | 0.0014341 | 1.8624e-05
129657 | 2012-06-12 09:06 | 2012-06-12 16:50 | 82 | 461 | 37802 | 82 | 0.11734 | 0.00025453 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 82 | 0.11734 | 0.00025453
129659 | 2012-06-13 01:20 | 2012-06-13 04:18 | 497 | 175 | 72009.5506 | 411.4831 | 0.22352 | 0.0015427 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | C | 411.4831 | 0.22352 | 0.0015427
129663 | 2012-06-09 08:30 | 2012-06-09 13:35 | 6 | 302 | 1812 | 6 | 0.0056245 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-09 | 2013 | 2013 | 2012-06-09 | B | 6 | 0.0056245 | 1.8624e-05
129665 | 2012-06-11 09:18 | 2012-06-11 10:50 | 6 | 89 | 534 | 6 | 0.0016576 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 6 | 0.0016576 | 1.8624e-05
129667 | 2012-06-05 09:06 | 2012-06-05 14:22 | 4 | 313 | 1252 | 4 | 0.0038862 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-05 | 2013 | 2013 | 2012-06-05 | B | 4 | 0.0038862 | 1.2416e-05
129669 | 2012-06-02 09:21 | 2012-06-02 16:04 | 1 | 400 | 400 | 1 | 0.0012416 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-02 | 2013 | 2013 | 2012-06-02 | B | 1 | 0.0012416 | 3.104e-06
129671 | 2012-06-06 09:01 | 2012-06-06 14:37 | 4 | 333 | 1332 | 4 | 0.0041346 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-06 | 2013 | 2013 | 2012-06-06 | B | 4 | 0.0041346 | 1.2416e-05
129677 | 2012-06-11 05:01 | 2012-06-11 05:29 | 19 | 25 | 475 | 19 | 0.0014744 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-11 | 2013 | 2013 | 2012-06-11 | B | 19 | 0.0014744 | 5.8977e-05
129679 | 2012-06-08 04:00 | 2012-06-08 06:05 | 44 | 122 | 5368 | 44 | 0.016662 | 0.00013658 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-08 | 2013 | 2013 | 2012-06-08 | B | 44 | 0.016662 | 0.00013658
129680 | 2012-06-13 11:01 | 2012-06-13 15:57 | 12 | 293 | 3516 | 12 | 0.010914 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 12 | 0.010914 | 3.7248e-05
129683 | 2012-06-13 12:00 | 2012-06-13 13:30 | 5 | 87 | 435 | 5 | 0.0013503 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 5 | 0.0013503 | 1.552e-05
129685 | 2012-06-13 08:45 | 2012-06-13 14:03 | 13 | 315 | 4095 | 13 | 0.012711 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 13 | 0.012711 | 4.0352e-05
129686 | 2012-06-13 09:12 | 2012-06-13 15:02 | 28 | 347 | 9716 | 28 | 0.030159 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 28 | 0.030159 | 8.6913e-05
129687 | 2012-06-13 09:25 | 2012-06-13 12:59 | 124 | 211 | 26164 | 124 | 0.081214 | 0.0003849 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 124 | 0.081214 | 0.0003849
129688 | 2012-06-13 09:41 | 2012-06-13 14:00 | 9 | 256 | 2304 | 9 | 0.0071517 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 9 | 0.0071517 | 2.7936e-05
129689 | 2012-06-13 09:19 | 2012-06-13 10:00 | 5 | 38 | 190 | 5 | 0.00058977 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 5 | 0.00058977 | 1.552e-05
129690 | 2012-06-12 09:35 | 2012-06-12 12:10 | 26 | 152 | 3952 | 26 | 0.012267 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-12 | 2013 | 2013 | 2012-06-12 | B | 26 | 0.012267 | 8.0705e-05
129691 | 2012-06-13 09:00 | 2012-06-13 12:30 | 106 | 207 | 21942 | 106 | 0.068109 | 0.00032903 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 106 | 0.068109 | 0.00032903
129693 | 2012-06-14 00:18 | 2012-06-14 05:58 | 1333 | 337 | 40032.6265 | 118.7912 | 0.12426 | 0.0041377 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | C | 118.7912 | 0.12426 | 0.0041377
129694 | 2012-06-13 12:00 | 2012-06-13 14:35 | 2 | 152 | 304 | 2 | 0.00094362 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | C | 2 | 0.00094362 | 6.2081e-06
129695 | 2012-06-14 09:30 | 2012-06-14 12:50 | 30 | 197 | 5910 | 30 | 0.018345 | 9.3121e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 30 | 0.018345 | 9.3121e-05
129696 | 2012-06-14 09:57 | 2012-06-14 12:28 | 17 | 148 | 2516 | 17 | 0.0078097 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 17 | 0.0078097 | 5.2768e-05
129697 | 2012-06-14 09:13 | 2012-06-14 11:51 | 6 | 155 | 930 | 6 | 0.0028867 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 6 | 0.0028867 | 1.8624e-05
129698 | 2012-06-14 09:30 | 2012-06-14 15:33 | 24 | 360 | 8640 | 24 | 0.026819 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 24 | 0.026819 | 7.4497e-05
129699 | 2012-06-14 09:15 | 2012-06-14 14:45 | 63 | 327 | 20601 | 63 | 0.063946 | 0.00019555 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 63 | 0.063946 | 0.00019555
129700 | 2012-06-14 09:00 | 2012-06-14 15:21 | 20 | 378 | 7560 | 20 | 0.023466 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 20 | 0.023466 | 6.2081e-05
129701 | 2012-06-14 09:00 | 2012-06-14 14:28 | 15 | 325 | 4875 | 15 | 0.015132 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 15 | 0.015132 | 4.656e-05
129702 | 2012-06-14 08:48 | 2012-06-14 13:47 | 120 | 296 | 35520 | 120 | 0.11026 | 0.00037248 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 120 | 0.11026 | 0.00037248
129703 | 2012-06-14 10:00 | 2012-06-14 14:11 | 58 | 248 | 14384 | 58 | 0.044648 | 0.00018003 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 58 | 0.044648 | 0.00018003
129704 | 2012-06-14 09:00 | 2012-06-14 11:22 | 4 | 139 | 556 | 4 | 0.0017258 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 4 | 0.0017258 | 1.2416e-05
129706 | 2012-06-14 09:05 | 2012-06-14 15:49 | 60 | 401 | 24060 | 60 | 0.074683 | 0.00018624 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-14 | 2013 | 2013 | 2012-06-14 | B | 60 | 0.074683 | 0.00018624
129709 | 2012-06-13 18:13 | 2012-06-13 18:48 | 4 | 32 | 128 | 4 | 0.00039732 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 4 | 0.00039732 | 1.2416e-05
129711 | 2012-06-13 08:22 | 2012-06-13 12:07 | 1 | 222 | 222 | 1 | 0.00068909 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-13 | 2013 | 2013 | 2012-06-13 | B | 1 | 0.00068909 | 3.104e-06
129712 | 2012-06-15 09:23 | 2012-06-15 13:20 | 13 | 234 | 3042 | 13 | 0.0094425 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | B | 13 | 0.0094425 | 4.0352e-05
129713 | 2012-06-15 10:00 | 2012-06-15 10:30 | 2 | 27 | 54 | 2 | 0.00016762 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | B | 2 | 0.00016762 | 6.2081e-06
129716 | 2012-06-15 09:00 | 2012-06-15 14:25 | 3 | 322 | 966 | 3 | 0.0029985 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | B | 3 | 0.0029985 | 9.3121e-06
129718 | 2012-06-15 09:01 | 2012-06-15 10:15 | 6 | 71 | 426 | 6 | 0.0013223 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | B | 6 | 0.0013223 | 1.8624e-05
129720 | 2012-06-16 08:30 | 2012-06-16 14:49 | 2 | 376 | 752 | 2 | 0.0023342 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | B | 2 | 0.0023342 | 6.2081e-06
129722 | 2012-06-16 22:37 | 2012-06-17 03:33 | 30 | 293 | 8790 | 30 | 0.027284 | 9.3121e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | C | 30 | 0.027284 | 9.3121e-05
129723 | 2012-06-17 06:00 | 2012-06-17 06:40 | 3 | 37 | 111 | 3 | 0.00034455 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-17 | 2013 | 2013 | 2012-06-17 | B | 3 | 0.00034455 | 9.3121e-06
129726 | 2012-06-17 08:30 | 2012-06-17 10:30 | 2 | 117 | 234 | 2 | 0.00072634 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-17 | 2013 | 2013 | 2012-06-17 | B | 2 | 0.00072634 | 6.2081e-06
129727 | 2012-06-17 12:33 | 2012-06-17 13:09 | 22 | 33 | 726 | 22 | 0.0022535 | 6.8289e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-17 | 2013 | 2013 | 2012-06-17 | C | 22 | 0.0022535 | 6.8289e-05
129728 | 2012-06-17 11:03 | 2012-06-17 13:35 | 4 | 149 | 596 | 4 | 0.00185 | 1.2416e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-17 | 2013 | 2013 | 2012-06-17 | C | 4 | 0.00185 | 1.2416e-05
129729 | 2012-05-19 08:30 | 2012-05-19 13:30 | 182 | 297 | 54054 | 182 | 0.16779 | 0.00056493 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-05-19 | 2013 | 2013 | 2012-05-19 | B | 182 | 0.16779 | 0.00056493
129730 | 2012-06-17 08:15 | 2012-06-17 14:15 | 30 | 357 | 10710 | 30 | 0.033244 | 9.3121e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-17 | 2013 | 2013 | 2012-06-17 | B | 30 | 0.033244 | 9.3121e-05
129732 | 2012-06-16 09:22 | 2012-06-16 16:29 | 3 | 424 | 1272 | 3 | 0.0039483 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | B | 3 | 0.0039483 | 9.3121e-06
129733 | 2012-06-16 09:13 | 2012-06-16 12:58 | 27 | 222 | 5994 | 27 | 0.018606 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | B | 27 | 0.018606 | 8.3809e-05
129734 | 2012-06-16 08:53 | 2012-06-16 16:34 | 2 | 458 | 916 | 2 | 0.0028433 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | B | 2 | 0.0028433 | 6.2081e-06
129735 | 2012-06-16 05:13 | 2012-06-16 06:58 | 41 | 102 | 4182 | 41 | 0.012981 | 0.00012727 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-16 | 2013 | 2013 | 2012-06-16 | C | 41 | 0.012981 | 0.00012727
129736 | 2012-06-15 17:10 | 2012-06-15 17:35 | 125 | 22 | 2750 | 125 | 0.0085361 | 0.000388 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | C | 125 | 0.0085361 | 0.000388
129739 | 2012-06-18 08:35 | 2012-06-18 10:32 | 16 | 114 | 1824 | 16 | 0.0056617 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 16 | 0.0056617 | 4.9664e-05
129740 | 2012-06-18 11:20 | 2012-06-18 11:47 | 87 | 24 | 2088 | 87 | 0.0064812 | 0.00027005 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 87 | 0.0064812 | 0.00027005
129741 | 2012-06-18 11:20 | 2012-06-18 11:50 | 163 | 27 | 4401 | 163 | 0.013661 | 0.00050596 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 163 | 0.013661 | 0.00050596
129742 | 2012-06-18 10:42 | 2012-06-18 12:08 | 3 | 83 | 249 | 3 | 0.0007729 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 3 | 0.0007729 | 9.3121e-06
129743 | 2012-06-18 09:00 | 2012-06-18 13:51 | 6 | 288 | 1728 | 6 | 0.0053638 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 6 | 0.0053638 | 1.8624e-05
129744 | 2012-06-18 10:42 | 2012-06-18 12:39 | 13 | 114 | 1482 | 13 | 0.0046002 | 4.0352e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 13 | 0.0046002 | 4.0352e-05
129745 | 2012-06-18 08:00 | 2012-06-18 14:38 | 10 | 395 | 3950 | 10 | 0.012261 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 10 | 0.012261 | 3.104e-05
129746 | 2012-06-18 14:13 | 2012-06-18 14:42 | 436 | 26 | 11336 | 436 | 0.035187 | 0.0013534 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 436 | 0.035187 | 0.0013534
129748 | 2012-06-18 08:15 | 2012-06-18 15:30 | 65 | 432 | 28080 | 65 | 0.087161 | 0.00020176 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 65 | 0.087161 | 0.00020176
129749 | 2012-06-18 14:30 | 2012-06-18 15:40 | 9 | 67 | 603 | 9 | 0.0018717 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 9 | 0.0018717 | 2.7936e-05
129751 | 2012-06-18 13:25 | 2012-06-18 13:29 | 2 | 1 | 2 | 2 | 6.2081e-06 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | B | 2 | 6.2081e-06 | 6.2081e-06
129752 | 2012-06-18 18:03 | 2012-06-18 19:31 | 12 | 85 | 1020 | 12 | 0.0031661 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 12 | 0.0031661 | 3.7248e-05
129753 | 2012-06-18 20:07 | 2012-06-18 20:26 | 1 | 16 | 16 | 1 | 4.9664e-05 | 3.104e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 1 | 4.9664e-05 | 3.104e-06
129756 | 2012-06-18 20:07 | 2012-06-18 20:50 | 2188 | 40 | 87520 | 2188 | 0.27166 | 0.0067916 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 2188 | 0.27166 | 0.0067916
129757 | 2012-06-18 20:07 | 2012-06-18 20:21 | 152 | 11 | 1672 | 152 | 0.0051899 | 0.00047181 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 152 | 0.0051899 | 0.00047181
129758 | 2012-06-18 21:44 | 2012-06-19 03:08 | 1742 | 321 | 313078.037 | 975.321 | 0.9718 | 0.0054072 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 975.321 | 0.9718 | 0.0054072
129759 | 2012-06-18 21:43 | 2012-06-18 22:44 | 675 | 58 | 39150 | 675 | 0.12152 | 0.0020952 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 675 | 0.12152 | 0.0020952
129761 | 2012-06-18 21:44 | 2012-06-19 00:15 | 311 | 148 | 27001.6689 | 182.4437 | 0.083814 | 0.00096535 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-18 | 2013 | 2013 | 2012-06-18 | C | 182.4437 | 0.083814 | 0.00096535
129762 | 2012-06-19 12:00 | 2012-06-19 14:00 | 2 | 117 | 234 | 2 | 0.00072634 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 2 | 0.00072634 | 6.2081e-06
129763 | 2012-06-19 10:00 | 2012-06-19 11:21 | 2 | 78 | 156 | 2 | 0.00048423 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 2 | 0.00048423 | 6.2081e-06
129764 | 2012-06-19 | 2012-06-19 10:12 | 2 | 609 | 1218 | 2 | 0.0037807 | 6.2081e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | C | 2 | 0.0037807 | 6.2081e-06
129765 | 2012-06-19 13:04 | 2012-06-19 13:36 | 7 | 29 | 203 | 7 | 0.00063012 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 7 | 0.00063012 | 2.1728e-05
129766 | 2012-06-19 09:06 | 2012-06-19 09:20 | 11 | 11 | 121 | 11 | 0.00037559 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 11 | 0.00037559 | 3.4144e-05
129768 | 2012-06-19 08:00 | 2012-06-19 14:07 | 17 | 364 | 6188 | 17 | 0.019208 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 17 | 0.019208 | 5.2768e-05
129770 | 2012-06-19 08:30 | 2012-06-19 14:10 | 20 | 337 | 6740 | 20 | 0.020921 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 20 | 0.020921 | 6.2081e-05
129771 | 2012-06-19 09:30 | 2012-06-19 11:15 | 5 | 102 | 510 | 5 | 0.0015831 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 5 | 0.0015831 | 1.552e-05
129772 | 2012-06-19 09:17 | 2012-06-19 13:03 | 93 | 223 | 20739 | 93 | 0.064374 | 0.00028867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 93 | 0.064374 | 0.00028867
129773 | 2012-06-19 12:13 | 2012-06-19 14:54 | 193 | 158 | 16990.3975 | 107.5342 | 0.052739 | 0.00059908 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | C | 107.5342 | 0.052739 | 0.00059908
129776 | 2012-06-19 11:48 | 2012-06-19 13:50 | 535 | 119 | 34394.9016 | 289.0328 | 0.10676 | 0.0016607 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | C | 289.0328 | 0.10676 | 0.0016607
129777 | 2012-06-19 08:02 | 2012-06-19 15:40 | 28 | 455 | 12740 | 28 | 0.039545 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 28 | 0.039545 | 8.6913e-05
129780 | 2012-06-19 08:55 | 2012-06-19 15:06 | 13 | 368 | 4784 | 13 | 0.01485 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 13 | 0.01485 | 4.0352e-05
129781 | 2012-06-19 11:50 | 2012-06-19 15:05 | 13 | 192 | 2496 | 13 | 0.0077477 | 4.0352e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | C | 13 | 0.0077477 | 4.0352e-05
129782 | 2012-06-19 12:52 | 2012-06-19 17:45 | 157 | 290 | 16899.1809 | 58.273 | 0.052456 | 0.00048733 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | C | 58.273 | 0.052456 | 0.00048733
129784 | 2012-06-19 09:00 | 2012-06-19 09:30 | 8 | 27 | 216 | 8 | 0.00067047 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 8 | 0.00067047 | 2.4832e-05
129786 | 2012-06-19 12:30 | 2012-06-19 13:00 | 5 | 27 | 135 | 5 | 0.00041904 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-19 | 2013 | 2013 | 2012-06-19 | B | 5 | 0.00041904 | 1.552e-05
129787 | 2012-06-20 03:23 | 2012-06-20 08:21 | 304 | 295 | 51710.1342 | 175.2886 | 0.16051 | 0.00094362 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | C | 175.2886 | 0.16051 | 0.00094362
129788 | 2012-06-20 09:30 | 2012-06-20 14:14 | 11 | 281 | 3091 | 11 | 0.0095946 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 11 | 0.0095946 | 3.4144e-05
129789 | 2012-06-20 16:51 | 2012-06-20 18:00 | 92 | 66 | 6072 | 92 | 0.018848 | 0.00028557 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | C | 92 | 0.018848 | 0.00028557
129790 | 2012-06-20 13:00 | 2012-06-20 13:45 | 3 | 42 | 126 | 3 | 0.00039111 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | C | 3 | 0.00039111 | 9.3121e-06
129792 | 2012-06-20 08:48 | 2012-06-20 14:50 | 66 | 359 | 23694 | 66 | 0.073547 | 0.00020487 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 66 | 0.073547 | 0.00020487
129793 | 2012-06-20 08:07 | 2012-06-20 14:12 | 19 | 362 | 6878 | 19 | 0.02135 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 19 | 0.02135 | 5.8977e-05
129794 | 2012-06-20 08:45 | 2012-06-20 15:43 | 55 | 415 | 22825 | 55 | 0.070849 | 0.00017072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 55 | 0.070849 | 0.00017072
129796 | 2012-06-20 09:20 | 2012-06-20 16:27 | 26 | 424 | 11024 | 26 | 0.034219 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 26 | 0.034219 | 8.0705e-05
129801 | 2012-06-21 09:01 | 2012-06-21 10:01 | 173 | 57 | 9861 | 173 | 0.030609 | 0.000537 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 173 | 0.030609 | 0.000537
129802 | 2012-06-21 08:43 | 2012-06-21 09:03 | 419 | 17 | 7123 | 419 | 0.02211 | 0.0013006 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | C | 419 | 0.02211 | 0.0013006
129803 | 2012-06-21 08:52 | 2012-06-21 14:47 | 1 | 352 | 352 | 1 | 0.0010926 | 3.104e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | C | 1 | 0.0010926 | 3.104e-06
129805 | 2012-06-21 08:30 | 2012-06-21 11:45 | 20 | 192 | 3840 | 20 | 0.011919 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 20 | 0.011919 | 6.2081e-05
129807 | 2012-06-21 09:00 | 2012-06-21 14:14 | 17 | 311 | 5287 | 17 | 0.016411 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 17 | 0.016411 | 5.2768e-05
129809 | 2012-06-21 08:47 | 2012-06-21 15:01 | 28 | 371 | 10388 | 28 | 0.032245 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 28 | 0.032245 | 8.6913e-05
129811 | 2012-06-21 08:30 | 2012-06-21 15:02 | 20 | 389 | 7780 | 20 | 0.024149 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 20 | 0.024149 | 6.2081e-05
129813 | 2012-06-21 09:15 | 2012-06-21 14:16 | 172 | 298 | 51256 | 172 | 0.1591 | 0.00053389 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 172 | 0.1591 | 0.00053389
129814 | 2012-06-20 23:00 | 2012-06-21 08:15 | 26 | 552 | 14352 | 26 | 0.044549 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-20 | 2013 | 2013 | 2012-06-20 | B | 26 | 0.044549 | 8.0705e-05
129815 | 2012-06-21 08:00 | 2012-06-21 15:45 | 16 | 462 | 7392 | 16 | 0.022945 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 16 | 0.022945 | 4.9664e-05
129816 | 2012-06-21 09:35 | 2012-06-21 15:25 | 5 | 347 | 1735 | 5 | 0.0053855 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | C | 5 | 0.0053855 | 1.552e-05
129818 | 2012-06-21 20:32 | 2012-06-21 21:37 | 293 | 62 | 10423.6308 | 168.1231 | 0.032355 | 0.00090948 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | C | 168.1231 | 0.032355 | 0.00090948
129819 | 2012-06-21 18:40 | 2012-06-22 02:20 | 28 | 457 | 1688.913 | 3.6957 | 0.0052424 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-21 | 2013 | 2013 | 2012-06-21 | B | 3.6957 | 0.0052424 | 8.6913e-05
129821 | 2012-06-15 09:34 | 2012-06-15 14:21 | 1 | 284 | 284 | 1 | 0.00088154 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-15 | 2013 | 2013 | 2012-06-15 | B | 1 | 0.00088154 | 3.104e-06
129822 | 2012-06-22 09:00 | 2012-06-22 11:16 | 14 | 133 | 1862 | 14 | 0.0057797 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 14 | 0.0057797 | 4.3456e-05
129823 | 2012-06-22 10:03 | 2012-06-22 13:13 | 2 | 187 | 374 | 2 | 0.0011609 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 2 | 0.0011609 | 6.2081e-06
129825 | 2012-06-22 09:46 | 2012-06-22 12:59 | 25 | 190 | 4750 | 25 | 0.014744 | 7.7601e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 25 | 0.014744 | 7.7601e-05
129826 | 2012-06-22 09:30 | 2012-06-22 14:06 | 24 | 273 | 6552 | 24 | 0.020338 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 24 | 0.020338 | 7.4497e-05
129827 | 2012-06-22 09:25 | 2012-06-22 15:37 | 5 | 369 | 1845 | 5 | 0.0057269 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 5 | 0.0057269 | 1.552e-05
129828 | 2012-06-22 08:00 | 2012-06-22 14:37 | 18 | 394 | 7092 | 18 | 0.022014 | 5.5873e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 18 | 0.022014 | 5.5873e-05
129829 | 2012-06-22 09:15 | 2012-06-22 15:25 | 74 | 367 | 27158 | 74 | 0.084299 | 0.0002297 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 74 | 0.084299 | 0.0002297
129830 | 2012-06-22 14:01 | 2012-06-22 15:01 | 10 | 57 | 570 | 10 | 0.0017693 | 3.104e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | C | 10 | 0.0017693 | 3.104e-05
129831 | 2012-06-22 14:05 | 2012-06-22 14:31 | 421 | 23 | 9683 | 421 | 0.030056 | 0.0013068 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | C | 421 | 0.030056 | 0.0013068
129832 | 2012-06-22 14:05 | 2012-06-22 14:31 | 825 | 23 | 18975 | 825 | 0.058899 | 0.0025608 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | C | 825 | 0.058899 | 0.0025608
129833 | 2012-06-22 09:15 | 2012-06-22 16:58 | 110 | 460 | 15303.1965 | 33.2678 | 0.047502 | 0.00034144 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | B | 33.2678 | 0.047502 | 0.00034144
129834 | 2012-06-22 12:40 | 2012-06-22 13:25 | 18 | 42 | 756 | 18 | 0.0023466 | 5.5873e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | C | 18 | 0.0023466 | 5.5873e-05
129836 | 2012-06-22 12:45 | 2012-06-22 16:10 | 5 | 202 | 1010 | 5 | 0.0031351 | 1.552e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-06-22 | 2013 | 2013 | 2012-06-22 | C | 5 | 0.0031351 | 1.552e-05
129837 | 2012-06-23 01:00 | 2012-06-23 03:35 | 49 | 152 | 6266.3226 | 41.2258 | 0.019451 | 0.0001521 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 41.2258 | 0.019451 | 0.0001521
129840 | 2012-06-23 08:00 | 2012-06-23 15:37 | 1 | 454 | 454 | 1 | 0.0014092 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | B | 1 | 0.0014092 | 3.104e-06
129842 | 2012-06-24 00:43 | 2012-06-24 04:04 | 173 | 198 | 30047.7313 | 151.7562 | 0.093269 | 0.000537 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 151.7562 | 0.093269 | 0.000537
129843 | 2012-06-23 09:03 | 2012-06-23 12:36 | 46 | 210 | 9660 | 46 | 0.029985 | 0.00014279 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | B | 46 | 0.029985 | 0.00014279
129844 | 2012-06-23 16:20 | 2012-06-23 16:56 | 33 | 33 | 1089 | 33 | 0.0033803 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 33 | 0.0033803 | 0.00010243
129845 | 2012-06-24 12:33 | 2012-06-24 13:41 | 942 | 65 | 56445.8088 | 868.3971 | 0.17521 | 0.002924 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 868.3971 | 0.17521 | 0.002924
129847 | 2012-06-24 12:33 | 2012-06-24 13:53 | 19 | 77 | 1463 | 19 | 0.0045412 | 5.8977e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 19 | 0.0045412 | 5.8977e-05
129848 | 2012-06-24 13:29 | 2012-06-24 14:38 | 380 | 66 | 24872.4348 | 376.8551 | 0.077205 | 0.0011795 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 376.8551 | 0.077205 | 0.0011795
129849 | 2012-06-24 13:29 | 2012-06-24 14:39 | 187 | 67 | 12529 | 187 | 0.03889 | 0.00058045 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 187 | 0.03889 | 0.00058045
129850 | 2012-06-23 19:15 | 2012-06-24 08:45 | 198 | 807 | 89238.2593 | 110.5802 | 0.277 | 0.0006146 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 110.5802 | 0.277 | 0.0006146
129852 | 2012-06-24 06:06 | 2012-06-24 14:46 | 174 | 517 | 89958 | 174 | 0.27923 | 0.0005401 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 174 | 0.27923 | 0.0005401
129853 | 2012-06-23 16:32 | 2012-06-24 10:36 | 83 | 1081 | 54185.6236 | 50.1255 | 0.16819 | 0.00025763 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 50.1255 | 0.16819 | 0.00025763
129854 | 2012-06-23 21:28 | 2012-06-24 10:31 | 178 | 780 | 138840 | 178 | 0.43096 | 0.00055252 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 178 | 0.43096 | 0.00055252
129855 | 2012-06-24 20:04 | 2012-06-24 20:45 | 8 | 38 | 304 | 8 | 0.00094362 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 8 | 0.00094362 | 2.4832e-05
129856 | 2012-06-24 20:16 | 2012-06-24 21:20 | 3 | 61 | 183 | 3 | 0.00056804 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | C | 3 | 0.00056804 | 9.3121e-06
129859 | 2012-06-25 10:32 | 2012-06-25 12:34 | 89 | 119 | 10591 | 89 | 0.032875 | 0.00027626 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | C | 89 | 0.032875 | 0.00027626
129861 | 2012-06-25 10:00 | 2012-06-25 13:35 | 1 | 212 | 212 | 1 | 0.00065805 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 1 | 0.00065805 | 3.104e-06
129862 | 2012-06-25 10:35 | 2012-06-25 14:06 | 14 | 208 | 2912 | 14 | 0.0090389 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | C | 14 | 0.0090389 | 4.3456e-05
129863 | 2012-06-25 09:15 | 2012-06-25 14:08 | 7 | 290 | 2030 | 7 | 0.0063012 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 7 | 0.0063012 | 2.1728e-05
129865 | 2012-06-25 09:27 | 2012-06-25 14:20 | 28 | 290 | 8120 | 28 | 0.025205 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 28 | 0.025205 | 8.6913e-05
129866 | 2012-06-25 09:00 | 2012-06-25 14:52 | 24 | 349 | 8376 | 24 | 0.025999 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 24 | 0.025999 | 7.4497e-05
129867 | 2012-06-25 14:40 | 2012-06-25 15:27 | 12 | 44 | 528 | 12 | 0.0016389 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | C | 12 | 0.0016389 | 3.7248e-05
129870 | 2012-06-25 13:51 | 2012-06-25 15:44 | 32 | 110 | 3520 | 32 | 0.010926 | 9.9329e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | C | 32 | 0.010926 | 9.9329e-05
129871 | 2012-06-25 08:00 | 2012-06-25 16:46 | 11 | 523 | 5753 | 11 | 0.017857 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 11 | 0.017857 | 3.4144e-05
129872 | 2012-06-25 14:52 | 2012-06-25 15:05 | 785 | 10 | 7850 | 785 | 0.024367 | 0.0024367 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | C | 785 | 0.024367 | 0.0024367
129873 | 2012-06-25 09:41 | 2012-06-25 17:11 | 91 | 447 | 8582.4 | 19.2 | 0.02664 | 0.00028247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 19.2 | 0.02664 | 0.00028247
129874 | 2012-06-25 12:49 | 2012-06-25 16:59 | 140 | 247 | 13583.024 | 54.992 | 0.042162 | 0.00043456 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 54.992 | 0.042162 | 0.00043456
129875 | 2012-06-23 13:42 | 2012-06-23 14:55 | 1 | 70 | 70 | 1 | 0.00021728 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 1 | 0.00021728 | 3.104e-06
129877 | 2012-06-26 09:04 | 2012-06-26 09:54 | 82 | 47 | 3854 | 82 | 0.011963 | 0.00025453 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 82 | 0.011963 | 0.00025453
129880 | 2012-06-26 09:00 | 2012-06-26 11:55 | 8 | 172 | 1376 | 8 | 0.0042711 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 8 | 0.0042711 | 2.4832e-05
129884 | 2012-06-26 09:05 | 2012-06-26 14:09 | 3 | 301 | 903 | 3 | 0.0028029 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 3 | 0.0028029 | 9.3121e-06
129885 | 2012-06-26 09:30 | 2012-06-26 12:45 | 2 | 192 | 384 | 2 | 0.0011919 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 2 | 0.0011919 | 6.2081e-06
129887 | 2012-06-26 09:45 | 2012-06-26 14:09 | 90 | 261 | 23490 | 90 | 0.072914 | 0.00027936 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 90 | 0.072914 | 0.00027936
129888 | 2012-06-26 08:30 | 2012-06-26 14:30 | 5 | 357 | 1785 | 5 | 0.0055407 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 5 | 0.0055407 | 1.552e-05
129889 | 2012-06-26 09:49 | 2012-06-26 14:39 | 223 | 287 | 20166.2034 | 70.2655 | 0.062596 | 0.0006922 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 70.2655 | 0.062596 | 0.0006922
129890 | 2012-06-26 08:45 | 2012-06-26 14:13 | 92 | 325 | 29900 | 92 | 0.09281 | 0.00028557 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 92 | 0.09281 | 0.00028557
129891 | 2012-06-26 12:54 | 2012-06-26 15:09 | 105 | 132 | 9249.7778 | 70.0741 | 0.028712 | 0.00032592 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 70.0741 | 0.028712 | 0.00032592
129895 | 2012-06-26 14:00 | 2012-06-26 14:49 | 173 | 46 | 7958 | 173 | 0.024702 | 0.000537 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 173 | 0.024702 | 0.000537
129897 | 2012-06-26 09:20 | 2012-06-26 15:25 | 80 | 362 | 28960 | 80 | 0.089893 | 0.00024832 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 80 | 0.089893 | 0.00024832
129898 | 2012-06-26 08:00 | 2012-06-26 16:30 | 11 | 507 | 5577 | 11 | 0.017311 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 11 | 0.017311 | 3.4144e-05
129899 | 2012-06-26 15:37 | 2012-06-26 17:20 | 20 | 100 | 2000 | 20 | 0.0062081 | 6.2081e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 20 | 0.0062081 | 6.2081e-05
129900 | 2012-06-26 23:14 | 2012-06-27 00:46 | 928 | 89 | 63760.7609 | 716.413 | 0.19792 | 0.0028805 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 716.413 | 0.19792 | 0.0028805
129902 | 2012-06-27 05:17 | 2012-06-27 05:53 | 308 | 33 | 10164 | 308 | 0.031549 | 0.00095604 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 308 | 0.031549 | 0.00095604
129905 | 2012-06-27 06:49 | 2012-06-27 07:12 | 308 | 20 | 6160 | 308 | 0.019121 | 0.00095604 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 308 | 0.019121 | 0.00095604
129906 | 2012-06-23 11:30 | 2012-06-23 19:30 | 1 | 477 | 477 | 1 | 0.0014806 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-23 | 2013 | 2013 | 2012-06-23 | C | 1 | 0.0014806 | 3.104e-06
129907 | 2012-06-27 07:49 | 2012-06-27 11:30 | 299 | 218 | 30061.3122 | 137.8959 | 0.093311 | 0.0009281 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 137.8959 | 0.093311 | 0.0009281
129908 | 2012-06-26 23:14 | 2012-06-27 00:42 | 285 | 85 | 24225 | 285 | 0.075195 | 0.00088465 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | C | 285 | 0.075195 | 0.00088465
129910 | 2012-06-27 08:45 | 2012-06-27 13:30 | 28 | 282 | 7896 | 28 | 0.024509 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 28 | 0.024509 | 8.6913e-05
129911 | 2012-06-27 09:57 | 2012-06-27 11:37 | 22 | 97 | 2134 | 22 | 0.006624 | 6.8289e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 22 | 0.006624 | 6.8289e-05
129913 | 2012-06-27 09:30 | 2012-06-27 13:45 | 9 | 252 | 2268 | 9 | 0.0070399 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 9 | 0.0070399 | 2.7936e-05
129914 | 2012-06-27 13:03 | 2012-06-27 14:33 | 53 | 87 | 4611 | 53 | 0.014313 | 0.00016451 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 53 | 0.014313 | 0.00016451
129915 | 2012-06-27 07:10 | 2012-06-27 12:51 | 156 | 338 | 39954.3754 | 118.2082 | 0.12402 | 0.00048423 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 118.2082 | 0.12402 | 0.00048423
129917 | 2012-06-27 08:30 | 2012-06-27 15:01 | 156 | 388 | 60528 | 156 | 0.18788 | 0.00048423 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 156 | 0.18788 | 0.00048423
129922 | 2012-06-27 15:11 | 2012-06-27 15:42 | 10 | 28 | 280 | 10 | 0.00086913 | 3.104e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 10 | 0.00086913 | 3.104e-05
129924 | 2012-06-27 08:05 | 2012-06-27 16:03 | 16 | 475 | 7600 | 16 | 0.023591 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 16 | 0.023591 | 4.9664e-05
129925 | 2012-06-27 08:45 | 2012-06-27 16:12 | 5 | 444 | 2220 | 5 | 0.0068909 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 5 | 0.0068909 | 1.552e-05
129926 | 2012-06-27 10:05 | 2012-06-27 11:05 | 2 | 57 | 114 | 2 | 0.00035386 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 2 | 0.00035386 | 6.2081e-06
129927 | 2012-06-27 12:00 | 2012-06-27 14:10 | 1 | 127 | 127 | 1 | 0.00039421 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 1 | 0.00039421 | 3.104e-06
129928 | 2012-06-27 09:15 | 2012-06-27 16:20 | 46 | 422 | 19412 | 46 | 0.060255 | 0.00014279 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 46 | 0.060255 | 0.00014279
129930 | 2012-06-27 16:20 | 2012-06-27 18:33 | 46 | 130 | 5980 | 46 | 0.018562 | 0.00014279 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 46 | 0.018562 | 0.00014279
129932 | 2012-06-27 21:37 | 2012-06-27 21:54 | 163 | 14 | 2282 | 163 | 0.0070834 | 0.00050596 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | C | 163 | 0.0070834 | 0.00050596
129933 | 2012-06-28 09:54 | 2012-06-28 13:40 | 282 | 223 | 31760.7257 | 142.4248 | 0.098586 | 0.00087534 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 142.4248 | 0.098586 | 0.00087534
129934 | 2012-06-28 09:54 | 2012-06-28 11:01 | 162 | 64 | 10368 | 162 | 0.032183 | 0.00050285 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 162 | 0.032183 | 0.00050285
129935 | 2012-06-28 10:04 | 2012-06-28 13:00 | 30 | 173 | 5190 | 30 | 0.01611 | 9.3121e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 30 | 0.01611 | 9.3121e-05
129937 | 2012-06-28 09:02 | 2012-06-28 13:24 | 16 | 259 | 4144 | 16 | 0.012863 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 16 | 0.012863 | 4.9664e-05
129938 | 2012-06-28 09:03 | 2012-06-28 13:10 | 76 | 244 | 18544 | 76 | 0.057561 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 76 | 0.057561 | 0.00023591
129941 | 2012-06-28 14:40 | 2012-06-28 16:03 | 47 | 80 | 3760 | 47 | 0.011671 | 0.00014589 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 47 | 0.011671 | 0.00014589
129942 | 2012-06-28 09:00 | 2012-06-28 15:42 | 23 | 399 | 9177 | 23 | 0.028486 | 7.1393e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 23 | 0.028486 | 7.1393e-05
129944 | 2012-06-28 08:00 | 2012-06-28 14:56 | 5 | 413 | 2065 | 5 | 0.0064098 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 5 | 0.0064098 | 1.552e-05
129945 | 2012-06-28 10:05 | 2012-06-28 17:04 | 8 | 416 | 3328 | 8 | 0.01033 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 8 | 0.01033 | 2.4832e-05
129946 | 2012-06-28 08:45 | 2012-06-28 15:26 | 3 | 398 | 1194 | 3 | 0.0037062 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 3 | 0.0037062 | 9.3121e-06
129947 | 2012-06-28 09:36 | 2012-06-28 13:19 | 70 | 220 | 15400 | 70 | 0.047802 | 0.00021728 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 70 | 0.047802 | 0.00021728
129951 | 2012-06-28 17:21 | 2012-06-28 18:38 | 59 | 74 | 4366 | 59 | 0.013552 | 0.00018314 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 59 | 0.013552 | 0.00018314
129952 | 2012-06-28 22:00 | 2012-06-29 04:06 | 300 | 363 | 108900 | 300 | 0.33803 | 0.00093121 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 300 | 0.33803 | 0.00093121
129953 | 2012-06-28 20:15 | 2012-06-28 20:22 | 58 | 4 | 232 | 58 | 0.00072013 | 0.00018003 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | C | 58 | 0.00072013 | 0.00018003
129954 | 2012-06-26 09:24 | 2012-06-26 12:33 | 23 | 186 | 4278 | 23 | 0.013279 | 7.1393e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-26 | 2013 | 2013 | 2012-06-26 | B | 23 | 0.013279 | 7.1393e-05
129955 | 2012-06-25 09:32 | 2012-06-25 15:14 | 1 | 339 | 339 | 1 | 0.0010523 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-25 | 2013 | 2013 | 2012-06-25 | B | 1 | 0.0010523 | 3.104e-06
129958 | 2012-06-24 06:00 | 2012-06-24 08:42 | 42 | 159 | 6678 | 42 | 0.020729 | 0.00013037 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-24 | 2013 | 2013 | 2012-06-24 | B | 42 | 0.020729 | 0.00013037
129959 | 2012-06-27 09:00 | 2012-06-27 15:11 | 276 | 368 | 101568 | 276 | 0.31527 | 0.00085671 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 276 | 0.31527 | 0.00085671
129960 | 2012-06-29 09:35 | 2012-06-29 09:45 | 1 | 7 | 7 | 1 | 2.1728e-05 | 3.104e-06 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | C | 1 | 2.1728e-05 | 3.104e-06
129961 | 2012-06-29 15:17 | 2012-06-29 15:50 | 19 | 30 | 570 | 19 | 0.0017693 | 5.8977e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | C | 19 | 0.0017693 | 5.8977e-05
129962 | 2012-06-29 09:15 | 2012-06-29 13:05 | 6 | 227 | 1362 | 6 | 0.0042277 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 6 | 0.0042277 | 1.8624e-05
129963 | 2012-06-29 09:30 | 2012-06-29 12:50 | 1 | 197 | 197 | 1 | 0.00061149 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 1 | 0.00061149 | 3.104e-06
129964 | 2012-06-29 09:08 | 2012-06-29 14:58 | 45 | 347 | 15615 | 45 | 0.048469 | 0.00013968 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 45 | 0.048469 | 0.00013968
129965 | 2012-06-29 12:24 | 2012-06-29 15:45 | 7 | 198 | 1386 | 7 | 0.0043022 | 2.1728e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | C | 7 | 0.0043022 | 2.1728e-05
129967 | 2012-06-29 10:30 | 2012-06-29 13:30 | 3 | 177 | 531 | 3 | 0.0016482 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 3 | 0.0016482 | 9.3121e-06
129968 | 2012-06-29 09:37 | 2012-06-29 14:15 | 18 | 275 | 4950 | 18 | 0.015365 | 5.5873e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 18 | 0.015365 | 5.5873e-05
129969 | 2012-06-29 09:10 | 2012-06-29 14:40 | 3 | 327 | 981 | 3 | 0.0030451 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | B | 3 | 0.0030451 | 9.3121e-06
129970 | 2012-06-29 14:25 | 2012-06-29 19:05 | 905 | 277 | 8757.1571 | 31.6143 | 0.027182 | 0.0028091 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-06-29 | 2013 | 2013 | 2012-06-29 | C | 31.6143 | 0.027182 | 0.0028091
129971 | 2012-06-30 07:15 | 2012-06-30 10:17 | 640 | 179 | 43234.4011 | 241.533 | 0.1342 | 0.0019866 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 241.533 | 0.1342 | 0.0019866
129973 | 2012-06-30 05:19 | 2012-06-30 11:30 | 911 | 368 | 69966.6199 | 190.1267 | 0.21718 | 0.0028278 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 190.1267 | 0.21718 | 0.0028278
129974 | 2012-06-30 05:19 | 2012-06-30 05:48 | 446 | 26 | 11596 | 446 | 0.035994 | 0.0013844 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 446 | 0.035994 | 0.0013844
129975 | 2012-06-30 20:04 | 2012-06-30 20:39 | 554 | 32 | 17728 | 554 | 0.055028 | 0.0017196 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 554 | 0.055028 | 0.0017196
129976 | 2012-06-30 08:40 | 2012-06-30 09:56 | 4 | 73 | 292 | 4 | 0.00090638 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | B | 4 | 0.00090638 | 1.2416e-05
129977 | 2012-07-01 14:20 | 2012-07-01 16:35 | 1 | 132 | 132 | 1 | 0.00040973 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-01 | 2013 | 2013 | 2012-07-01 | C | 1 | 0.00040973 | 3.104e-06
129979 | 2012-06-30 22:33 | 2012-07-01 11:32 | 1 | 776 | 776 | 1 | 0.0024087 | 3.104e-06 | No Power | Unplanned | Class C | ADVERSE ENVIRONMENT | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 1 | 0.0024087 | 3.104e-06
129980 | 2012-07-01 20:06 | 2012-07-01 20:18 | 2585 | 9 | 18747 | 2083 | 0.058191 | 0.0080239 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-01 | 2013 | 2013 | 2012-07-01 | C | 2083 | 0.058191 | 0.0080239
129981 | 2012-07-01 20:52 | 2012-07-01 21:10 | 55 | 15 | 825 | 55 | 0.0025608 | 0.00017072 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-01 | 2013 | 2013 | 2012-07-01 | C | 55 | 0.0025608 | 0.00017072
129982 | 2012-07-02 07:43 | 2012-07-02 14:12 | 1 | 386 | 386 | 1 | 0.0011982 | 3.104e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 1 | 0.0011982 | 3.104e-06
129983 | 2012-07-02 07:50 | 2012-07-02 10:07 | 38 | 134 | 4121.7226 | 30.7591 | 0.012794 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 30.7591 | 0.012794 | 0.00011795
129984 | 2012-07-02 09:35 | 2012-07-02 11:41 | 89 | 123 | 10947 | 89 | 0.03398 | 0.00027626 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 89 | 0.03398 | 0.00027626
129985 | 2012-07-02 09:05 | 2012-07-02 14:53 | 15 | 345 | 5175 | 15 | 0.016063 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | B | 15 | 0.016063 | 4.656e-05
129986 | 2012-07-02 11:30 | 2012-07-02 15:16 | 33 | 223 | 3925.1947 | 17.6018 | 0.012184 | 0.00010243 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 17.6018 | 0.012184 | 0.00010243
129989 | 2012-07-02 09:30 | 2012-07-02 14:30 | 9 | 297 | 2673 | 9 | 0.0082971 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 9 | 0.0082971 | 2.7936e-05
129992 | 2012-07-02 09:50 | 2012-07-02 15:00 | 4 | 307 | 1228 | 4 | 0.0038117 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | B | 4 | 0.0038117 | 1.2416e-05
129994 | 2012-07-02 10:02 | 2012-07-02 19:05 | 1 | 540 | 540 | 1 | 0.0016762 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | C | 1 | 0.0016762 | 3.104e-06
129995 | 2012-07-03 03:41 | 2012-07-03 03:52 | 577 | 8 | 4616 | 577 | 0.014328 | 0.001791 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 577 | 0.014328 | 0.001791
129996 | 2012-07-02 14:24 | 2012-07-02 14:38 | 212 | 11 | 2332 | 212 | 0.0072386 | 0.00065805 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | B | 212 | 0.0072386 | 0.00065805
129997 | 2012-06-30 11:30 | 2012-06-30 16:30 | 4 | 297 | 1188 | 4 | 0.0036876 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-06-30 | 2013 | 2013 | 2012-06-30 | C | 4 | 0.0036876 | 1.2416e-05
129998 | 2012-07-03 09:43 | 2012-07-03 10:06 | 243 | 20 | 4860 | 243 | 0.015086 | 0.00075428 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 243 | 0.015086 | 0.00075428
130001 | 2012-07-03 08:05 | 2012-07-03 11:21 | 638 | 193 | 54584.5357 | 282.8214 | 0.16943 | 0.0019804 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 282.8214 | 0.16943 | 0.0019804
130002 | 2012-07-03 10:45 | 2012-07-03 12:00 | 26 | 72 | 1872 | 26 | 0.0058107 | 8.0705e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 26 | 0.0058107 | 8.0705e-05
130005 | 2012-06-28 09:30 | 2012-06-28 13:00 | 1 | 207 | 207 | 1 | 0.00064253 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-28 | 2013 | 2013 | 2012-06-28 | B | 1 | 0.00064253 | 3.104e-06
130007 | 2012-07-03 09:23 | 2012-07-03 14:30 | 53 | 304 | 16112 | 53 | 0.050012 | 0.00016451 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 53 | 0.050012 | 0.00016451
130008 | 2012-07-03 09:35 | 2012-07-03 15:57 | 157 | 379 | 59503 | 157 | 0.1847 | 0.00048733 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 157 | 0.1847 | 0.00048733
130009 | 2012-07-03 14:50 | 2012-07-03 15:25 | 5 | 32 | 160 | 5 | 0.00049664 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 5 | 0.00049664 | 1.552e-05
130012 | 2012-07-03 16:00 | 2012-07-03 16:26 | 6 | 23 | 138 | 6 | 0.00042836 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 6 | 0.00042836 | 1.8624e-05
130014 | 2012-07-03 08:30 | 2012-07-03 15:22 | 128 | 409 | 52352 | 128 | 0.1625 | 0.00039732 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 128 | 0.1625 | 0.00039732
130016 | 2012-07-03 06:00 | 2012-07-03 07:27 | 144 | 84 | 12096 | 144 | 0.037546 | 0.00044698 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 144 | 0.037546 | 0.00044698
130017 | 2012-07-03 15:20 | 2012-07-03 19:25 | 7 | 242 | 1694 | 7 | 0.0052582 | 2.1728e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 7 | 0.0052582 | 2.1728e-05
130018 | 2012-07-03 17:34 | 2012-07-03 17:50 | 275 | 13 | 3575 | 275 | 0.011097 | 0.00085361 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 275 | 0.011097 | 0.00085361
130019 | 2012-07-03 22:00 | 2012-07-03 23:16 | 88 | 73 | 6424 | 88 | 0.01994 | 0.00027315 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 88 | 0.01994 | 0.00027315
130020 | 2012-07-03 18:45 | 2012-07-03 21:18 | 404 | 150 | 34988.2353 | 233.2549 | 0.1086 | 0.001254 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 233.2549 | 0.1086 | 0.001254
130021 | 2012-07-03 21:16 | 2012-07-03 22:06 | 279 | 47 | 8249.44 | 175.52 | 0.025606 | 0.00086602 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 175.52 | 0.025606 | 0.00086602
130022 | 2012-07-03 23:56 | 2012-07-04 00:13 | 119 | 14 | 1666 | 119 | 0.0051713 | 0.00036938 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 119 | 0.0051713 | 0.00036938
130023 | 2012-07-03 14:28 | 2012-07-03 21:30 | 83 | 419 | 12559.0782 | 29.9739 | 0.038984 | 0.00025763 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 29.9739 | 0.038984 | 0.00025763
130024 | 2012-07-03 20:59 | 2012-07-04 00:41 | 692 | 219 | 83708.3108 | 382.2297 | 0.25983 | 0.002148 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | C | 382.2297 | 0.25983 | 0.002148
130025 | 2012-07-03 09:48 | 2012-07-03 18:40 | 56 | 529 | 29624 | 56 | 0.091954 | 0.00017383 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 56 | 0.091954 | 0.00017383
130026 | 2012-07-04 02:16 | 2012-07-04 05:49 | 367 | 210 | 77070 | 367 | 0.23923 | 0.0011392 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 367 | 0.23923 | 0.0011392
130029 | 2012-07-04 10:53 | 2012-07-04 11:55 | 377 | 59 | 22149.7419 | 375.4194 | 0.068753 | 0.0011702 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 375.4194 | 0.068753 | 0.0011702
130031 | 2012-07-04 06:00 | 2012-07-04 07:07 | 88 | 64 | 5632 | 88 | 0.017482 | 0.00027315 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | B | 88 | 0.017482 | 0.00027315
130033 | 2012-07-04 09:30 | 2012-07-04 12:25 | 5 | 172 | 860 | 5 | 0.0026695 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | B | 5 | 0.0026695 | 1.552e-05
130034 | 2012-07-04 09:46 | 2012-07-04 14:04 | 24 | 255 | 6120 | 24 | 0.018997 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | B | 24 | 0.018997 | 7.4497e-05
130035 | 2012-07-04 11:49 | 2012-07-04 12:48 | 883 | 56 | 36464.5424 | 651.1525 | 0.11319 | 0.0027409 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 651.1525 | 0.11319 | 0.0027409
130036 | 2012-07-04 12:10 | 2012-07-04 15:20 | 2 | 187 | 374 | 2 | 0.0011609 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 2 | 0.0011609 | 6.2081e-06
130037 | 2012-07-04 14:55 | 2012-07-04 16:04 | 17 | 66 | 1122 | 17 | 0.0034827 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 17 | 0.0034827 | 5.2768e-05
130038 | 2012-07-04 16:51 | 2012-07-04 16:59 | 3782 | 5 | 18910 | 3782 | 0.058697 | 0.011739 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 3782 | 0.058697 | 0.011739
130039 | 2012-07-03 09:30 | 2012-07-03 13:15 | 3 | 222 | 666 | 3 | 0.0020673 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 3 | 0.0020673 | 9.3121e-06
130040 | 2012-07-03 09:00 | 2012-07-03 13:56 | 3 | 293 | 879 | 3 | 0.0027284 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-03 | 2013 | 2013 | 2012-07-03 | B | 3 | 0.0027284 | 9.3121e-06
130041 | 2012-07-04 02:24 | 2012-07-04 05:22 | 408 | 175 | 29015.5899 | 165.8034 | 0.090065 | 0.0012664 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 165.8034 | 0.090065 | 0.0012664
130044 | 2012-07-05 10:00 | 2012-07-05 11:55 | 2 | 112 | 224 | 2 | 0.0006953 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 2 | 0.0006953 | 6.2081e-06
130050 | 2012-07-05 10:00 | 2012-07-05 15:00 | 24 | 297 | 7128 | 24 | 0.022126 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 24 | 0.022126 | 7.4497e-05
130052 | 2012-07-05 09:15 | 2012-07-05 14:52 | 54 | 334 | 18036 | 54 | 0.055984 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 54 | 0.055984 | 0.00016762
130053 | 2012-07-05 10:48 | 2012-07-05 15:53 | 79 | 302 | 9776.8787 | 32.3738 | 0.030348 | 0.00024522 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | C | 32.3738 | 0.030348 | 0.00024522
130054 | 2012-07-05 13:06 | 2012-07-05 15:29 | 7 | 140 | 980 | 7 | 0.0030419 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | C | 7 | 0.0030419 | 2.1728e-05
130055 | 2012-07-05 08:15 | 2012-07-05 17:20 | 164 | 542 | 88888 | 164 | 0.27591 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 164 | 0.27591 | 0.00050906
130057 | 2012-06-27 08:15 | 2012-06-27 15:34 | 1 | 436 | 436 | 1 | 0.0013534 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-06-27 | 2013 | 2013 | 2012-06-27 | B | 1 | 0.0013534 | 3.104e-06
130058 | 2012-07-05 08:45 | 2012-07-05 14:27 | 62 | 339 | 21018 | 62 | 0.06524 | 0.00019245 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 62 | 0.06524 | 0.00019245
130059 | 2012-07-05 10:04 | 2012-07-05 14:28 | 61 | 261 | 15921 | 61 | 0.049419 | 0.00018935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 61 | 0.049419 | 0.00018935
130060 | 2012-07-05 09:12 | 2012-07-05 14:36 | 22 | 321 | 7062 | 22 | 0.021921 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 22 | 0.021921 | 6.8289e-05
130061 | 2012-07-05 18:48 | 2012-07-06 03:27 | 615 | 516 | 187336.8324 | 363.0559 | 0.5815 | 0.001909 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | C | 363.0559 | 0.5815 | 0.001909
130063 | 2012-07-06 09:08 | 2012-07-06 10:27 | 21 | 76 | 1596 | 21 | 0.004954 | 6.5185e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 21 | 0.004954 | 6.5185e-05
130064 | 2012-07-06 11:27 | 2012-07-06 12:42 | 5 | 72 | 360 | 5 | 0.0011175 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 5 | 0.0011175 | 1.552e-05
130065 | 2012-07-06 12:25 | 2012-07-06 14:03 | 1 | 95 | 95 | 1 | 0.00029488 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | B | 1 | 0.00029488 | 3.104e-06
130066 | 2012-07-06 15:18 | 2012-07-06 15:49 | 421 | 28 | 11788 | 421 | 0.03659 | 0.0013068 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 421 | 0.03659 | 0.0013068
130067 | 2012-07-06 15:18 | 2012-07-06 15:52 | 825 | 31 | 25575 | 825 | 0.079386 | 0.0025608 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 825 | 0.079386 | 0.0025608
130069 | 2012-07-06 09:30 | 2012-07-06 12:18 | 3 | 165 | 495 | 3 | 0.0015365 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | B | 3 | 0.0015365 | 9.3121e-06
130070 | 2012-07-06 09:00 | 2012-07-06 10:55 | 1 | 112 | 112 | 1 | 0.00034765 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | B | 1 | 0.00034765 | 3.104e-06
130073 | 2012-07-06 17:59 | 2012-07-06 18:15 | 238 | 13 | 3086.6875 | 237.4375 | 0.0095812 | 0.00073876 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 237.4375 | 0.0095812 | 0.00073876
130076 | 2012-07-07 10:32 | 2012-07-07 14:00 | 27 | 205 | 5535 | 27 | 0.017181 | 8.3809e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-07 | 2013 | 2013 | 2012-07-07 | C | 27 | 0.017181 | 8.3809e-05
130079 | 2012-07-07 20:38 | 2012-07-07 21:08 | 24 | 27 | 648 | 24 | 0.0020114 | 7.4497e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-07 | 2013 | 2013 | 2012-07-07 | C | 24 | 0.0020114 | 7.4497e-05
130082 | 2012-07-08 06:12 | 2012-07-08 17:55 | 17 | 700 | 11900 | 17 | 0.036938 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-08 | 2013 | 2013 | 2012-07-08 | B | 17 | 0.036938 | 5.2768e-05
130084 | 2012-07-09 06:00 | 2012-07-09 07:00 | 16 | 57 | 912 | 16 | 0.0028309 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 16 | 0.0028309 | 4.9664e-05
130085 | 2012-07-06 12:44 | 2012-07-06 15:50 | 193 | 183 | 30313.0645 | 165.6452 | 0.094093 | 0.00059908 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | C | 165.6452 | 0.094093 | 0.00059908
130087 | 2012-07-09 08:20 | 2012-07-09 09:17 | 19 | 54 | 1026 | 19 | 0.0031847 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 19 | 0.0031847 | 5.8977e-05
130089 | 2012-07-04 16:25 | 2012-07-04 18:32 | 7 | 124 | 868 | 7 | 0.0026943 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-04 | 2013 | 2013 | 2012-07-04 | C | 7 | 0.0026943 | 2.1728e-05
130091 | 2012-07-09 09:00 | 2012-07-09 12:50 | 1 | 227 | 227 | 1 | 0.00070461 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 1 | 0.00070461 | 3.104e-06
130092 | 2012-07-09 10:05 | 2012-07-09 14:40 | 49 | 272 | 13328 | 49 | 0.04137 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 49 | 0.04137 | 0.0001521
130094 | 2012-07-09 09:00 | 2012-07-09 14:30 | 38 | 327 | 12426 | 38 | 0.038571 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 38 | 0.038571 | 0.00011795
130097 | 2012-07-09 09:30 | 2012-07-09 12:30 | 2 | 177 | 354 | 2 | 0.0010988 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 2 | 0.0010988 | 6.2081e-06
130098 | 2012-07-09 09:30 | 2012-07-09 12:45 | 3 | 192 | 576 | 3 | 0.0017879 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 3 | 0.0017879 | 9.3121e-06
130099 | 2012-07-09 12:15 | 2012-07-09 16:00 | 616 | 222 | 21300.16 | 95.9467 | 0.066116 | 0.0019121 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | C | 95.9467 | 0.066116 | 0.0019121
130100 | 2012-07-09 10:05 | 2012-07-09 10:10 | 37 | 2 | 74 | 37 | 0.0002297 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | B | 37 | 0.0002297 | 0.00011485
130102 | 2012-07-09 13:06 | 2012-07-09 17:26 | 70 | 257 | 8391.05 | 32.65 | 0.026046 | 0.00021728 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | C | 32.65 | 0.026046 | 0.00021728
130103 | 2012-07-09 13:27 | 2012-07-09 15:01 | 10 | 91 | 910 | 10 | 0.0028247 | 3.104e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | C | 10 | 0.0028247 | 3.104e-05
130104 | 2012-07-09 11:58 | 2012-07-09 13:41 | 672 | 100 | 35930.0971 | 359.301 | 0.11153 | 0.0020859 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | C | 359.301 | 0.11153 | 0.0020859
130105 | 2012-07-09 11:58 | 2012-07-09 12:53 | 376 | 52 | 19552 | 376 | 0.06069 | 0.0011671 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-09 | 2013 | 2013 | 2012-07-09 | C | 376 | 0.06069 | 0.0011671
130107 | 2012-07-10 09:55 | 2012-07-10 11:09 | 1 | 71 | 71 | 1 | 0.00022039 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 1 | 0.00022039 | 3.104e-06
130109 | 2012-07-10 09:30 | 2012-07-10 14:49 | 49 | 316 | 15484 | 49 | 0.048063 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 49 | 0.048063 | 0.0001521
130111 | 2012-07-10 08:40 | 2012-07-10 14:58 | 1 | 375 | 375 | 1 | 0.001164 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 1 | 0.001164 | 3.104e-06
130114 | 2012-07-10 09:40 | 2012-07-10 12:04 | 146 | 141 | 20586 | 146 | 0.0639 | 0.00045319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 146 | 0.0639 | 0.00045319
130115 | 2012-07-10 09:54 | 2012-07-10 15:38 | 13 | 341 | 4433 | 13 | 0.01376 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 13 | 0.01376 | 4.0352e-05
130116 | 2012-07-10 09:06 | 2012-07-10 15:22 | 111 | 373 | 41403 | 111 | 0.12852 | 0.00034455 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 111 | 0.12852 | 0.00034455
130117 | 2012-07-10 08:51 | 2012-07-10 14:36 | 43 | 342 | 14706 | 43 | 0.045648 | 0.00013347 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 43 | 0.045648 | 0.00013347
130118 | 2012-07-10 08:44 | 2012-07-10 13:56 | 1 | 309 | 309 | 1 | 0.00095914 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | B | 1 | 0.00095914 | 3.104e-06
130120 | 2012-07-10 13:58 | 2012-07-10 14:24 | 4067 | 23 | 83527.1538 | 3631.6154 | 0.25927 | 0.012624 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | C | 3631.6154 | 0.25927 | 0.012624
130124 | 2012-07-07 13:00 | 2012-07-07 20:00 | 6 | 417 | 2502 | 6 | 0.0077663 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-07 | 2013 | 2013 | 2012-07-07 | C | 6 | 0.0077663 | 1.8624e-05
130125 | 2012-07-10 13:42 | 2012-07-10 16:46 | 12 | 181 | 2172 | 12 | 0.0067419 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | C | 12 | 0.0067419 | 3.7248e-05
130126 | 2012-07-11 08:00 | 2012-07-11 09:23 | 32 | 80 | 2560 | 32 | 0.0079463 | 9.9329e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | C | 32 | 0.0079463 | 9.9329e-05
130127 | 2012-07-11 09:30 | 2012-07-11 11:30 | 19 | 117 | 2223 | 19 | 0.0069003 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 19 | 0.0069003 | 5.8977e-05
130129 | 2012-07-11 13:25 | 2012-07-11 13:35 | 114 | 7 | 798 | 114 | 0.002477 | 0.00035386 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | C | 114 | 0.002477 | 0.00035386
130130 | 2012-07-11 10:41 | 2012-07-11 14:10 | 772 | 206 | 76591.5885 | 371.8038 | 0.23774 | 0.0023963 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | C | 371.8038 | 0.23774 | 0.0023963
130131 | 2012-07-11 11:52 | 2012-07-11 13:10 | 74 | 75 | 5550 | 74 | 0.017227 | 0.0002297 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | C | 74 | 0.017227 | 0.0002297
130132 | 2012-07-10 13:19 | 2012-07-10 16:03 | 86 | 161 | 6634.378 | 41.2073 | 0.020593 | 0.00026695 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-10 | 2013 | 2013 | 2012-07-10 | C | 41.2073 | 0.020593 | 0.00026695
130134 | 2012-07-11 09:30 | 2012-07-11 10:30 | 8 | 57 | 456 | 8 | 0.0014154 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 8 | 0.0014154 | 2.4832e-05
130135 | 2012-07-11 09:00 | 2012-07-11 15:20 | 18 | 377 | 6786 | 18 | 0.021064 | 5.5873e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 18 | 0.021064 | 5.5873e-05
130136 | 2012-07-06 08:21 | 2012-07-06 09:34 | 57 | 70 | 3990 | 57 | 0.012385 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-06 | 2013 | 2013 | 2012-07-06 | B | 57 | 0.012385 | 0.00017693
130138 | 2012-07-11 09:17 | 2012-07-11 12:07 | 20 | 167 | 3340 | 20 | 0.010367 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 20 | 0.010367 | 6.2081e-05
130139 | 2012-07-11 09:17 | 2012-07-11 15:45 | 28 | 385 | 10780 | 28 | 0.033461 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 28 | 0.033461 | 8.6913e-05
130140 | 2012-07-11 09:30 | 2012-07-11 13:30 | 11 | 237 | 2607 | 11 | 0.0080922 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | B | 11 | 0.0080922 | 3.4144e-05
130142 | 2012-07-02 09:21 | 2012-07-02 10:27 | 56 | 63 | 3528 | 56 | 0.010951 | 0.00017383 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | B | 56 | 0.010951 | 0.00017383
130144 | 2012-07-12 09:30 | 2012-07-12 10:10 | 38 | 37 | 1406 | 38 | 0.0043643 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | C | 38 | 0.0043643 | 0.00011795
130146 | 2012-07-12 09:50 | 2012-07-12 12:02 | 57 | 129 | 7353 | 57 | 0.022824 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | B | 57 | 0.022824 | 0.00017693
130147 | 2012-07-11 13:25 | 2012-07-12 11:45 | 1 | 1337 | 1337 | 1 | 0.0041501 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-11 | 2013 | 2013 | 2012-07-11 | C | 1 | 0.0041501 | 3.104e-06
130149 | 2012-07-12 09:41 | 2012-07-12 13:53 | 5 | 249 | 1245 | 5 | 0.0038645 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | B | 5 | 0.0038645 | 1.552e-05
130150 | 2012-07-12 09:30 | 2012-07-12 13:55 | 36 | 262 | 9432 | 36 | 0.029277 | 0.00011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | B | 36 | 0.029277 | 0.00011175
130151 | 2012-07-12 16:54 | 2012-07-12 17:37 | 14 | 40 | 560 | 14 | 0.0017383 | 4.3456e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | C | 14 | 0.0017383 | 4.3456e-05
130153 | 2012-07-12 16:23 | 2012-07-12 18:42 | 1777 | 136 | 105039.9424 | 772.3525 | 0.32605 | 0.0055159 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | C | 772.3525 | 0.32605 | 0.0055159
130154 | 2012-07-12 23:09 | 2012-07-13 04:07 | 52 | 295 | 15340 | 52 | 0.047616 | 0.00016141 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-12 | 2013 | 2013 | 2012-07-12 | C | 52 | 0.047616 | 0.00016141
130156 | 2012-07-13 08:58 | 2012-07-13 10:00 | 5 | 59 | 295 | 5 | 0.00091569 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-13 | 2013 | 2013 | 2012-07-13 | B | 5 | 0.00091569 | 1.552e-05
130159 | 2012-07-13 10:30 | 2012-07-13 13:27 | 71 | 174 | 12354 | 71 | 0.038347 | 0.00022039 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-13 | 2013 | 2013 | 2012-07-13 | B | 71 | 0.038347 | 0.00022039
130162 | 2012-07-05 11:05 | 2012-07-05 14:50 | 5 | 222 | 1110 | 5 | 0.0034455 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-05 | 2013 | 2013 | 2012-07-05 | B | 5 | 0.0034455 | 1.552e-05
130164 | 2012-07-14 07:23 | 2012-07-14 09:40 | 34 | 134 | 4556 | 34 | 0.014142 | 0.00010554 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 34 | 0.014142 | 0.00010554
130165 | 2012-07-14 08:20 | 2012-07-14 09:50 | 39 | 87 | 3393 | 39 | 0.010532 | 0.00012106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 39 | 0.010532 | 0.00012106
130168 | 2012-07-14 08:15 | 2012-07-14 14:49 | 1 | 391 | 391 | 1 | 0.0012137 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | B | 1 | 0.0012137 | 3.104e-06
130169 | 2012-07-13 20:02 | 2012-07-13 21:08 | 47 | 63 | 2961 | 47 | 0.009191 | 0.00014589 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-13 | 2013 | 2013 | 2012-07-13 | C | 47 | 0.009191 | 0.00014589
130170 | 2012-07-13 19:50 | 2012-07-13 21:08 | 2 | 75 | 150 | 2 | 0.0004656 | 6.2081e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-13 | 2013 | 2013 | 2012-07-13 | C | 2 | 0.0004656 | 6.2081e-06
130173 | 2012-07-14 15:59 | 2012-07-14 17:06 | 2906 | 64 | 181565.1343 | 2836.9552 | 0.56358 | 0.0090203 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 2836.9552 | 0.56358 | 0.0090203
130181 | 2012-07-15 12:43 | 2012-07-15 13:50 | 2907 | 64 | 180540.1791 | 2820.9403 | 0.5604 | 0.0090234 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 2820.9403 | 0.5604 | 0.0090234
130182 | 2012-07-15 13:00 | 2012-07-15 14:01 | 11 | 58 | 638 | 11 | 0.0019804 | 3.4144e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 11 | 0.0019804 | 3.4144e-05
130183 | 2012-07-15 13:13 | 2012-07-15 16:32 | 184 | 196 | 22191.3367 | 113.2211 | 0.068883 | 0.00057114 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 113.2211 | 0.068883 | 0.00057114
130185 | 2012-07-15 15:03 | 2012-07-15 15:58 | 2 | 52 | 104 | 2 | 0.00032282 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 2 | 0.00032282 | 6.2081e-06
130186 | 2012-07-15 11:45 | 2012-07-15 13:00 | 706 | 72 | 37190.4 | 516.5333 | 0.11544 | 0.0021914 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 516.5333 | 0.11544 | 0.0021914
130187 | 2012-07-15 13:23 | 2012-07-15 19:10 | 116 | 344 | 9604.2421 | 27.9193 | 0.029812 | 0.00036007 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 27.9193 | 0.029812 | 0.00036007
130190 | 2012-07-15 22:28 | 2012-07-15 22:45 | 276 | 14 | 3864 | 276 | 0.011994 | 0.00085671 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 276 | 0.011994 | 0.00085671
130191 | 2012-07-15 22:59 | 2012-07-16 00:31 | 281 | 89 | 13539.6087 | 152.1304 | 0.042027 | 0.00087223 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 152.1304 | 0.042027 | 0.00087223
130193 | 2012-07-15 14:36 | 2012-07-15 16:47 | 19 | 128 | 2432 | 19 | 0.007549 | 5.8977e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-07-15 | 2013 | 2013 | 2012-07-15 | C | 19 | 0.007549 | 5.8977e-05
130194 | 2012-07-16 10:20 | 2012-07-16 11:19 | 9 | 56 | 504 | 9 | 0.0015644 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 9 | 0.0015644 | 2.7936e-05
130196 | 2012-07-16 08:30 | 2012-07-16 11:40 | 3 | 187 | 561 | 3 | 0.0017414 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | B | 3 | 0.0017414 | 9.3121e-06
130197 | 2012-07-14 09:08 | 2012-07-14 12:43 | 47 | 212 | 9964 | 47 | 0.030929 | 0.00014589 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 47 | 0.030929 | 0.00014589
130198 | 2012-07-14 09:00 | 2012-07-14 12:50 | 2 | 227 | 454 | 2 | 0.0014092 | 6.2081e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 2 | 0.0014092 | 6.2081e-06
130199 | 2012-07-16 10:14 | 2012-07-16 10:58 | 30 | 41 | 1230 | 30 | 0.003818 | 9.3121e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 30 | 0.003818 | 9.3121e-05
130200 | 2012-07-16 05:30 | 2012-07-16 10:34 | 146 | 301 | 43946 | 146 | 0.13641 | 0.00045319 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 146 | 0.13641 | 0.00045319
130201 | 2012-07-16 11:55 | 2012-07-16 13:55 | 268 | 117 | 9036.3 | 77.2333 | 0.028049 | 0.00083188 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 77.2333 | 0.028049 | 0.00083188
130202 | 2012-07-16 12:37 | 2012-07-16 17:16 | 155 | 276 | 20225.1613 | 73.2796 | 0.062779 | 0.00048112 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 73.2796 | 0.062779 | 0.00048112
130204 | 2012-07-16 14:00 | 2012-07-16 15:30 | 6 | 87 | 522 | 6 | 0.0016203 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 6 | 0.0016203 | 1.8624e-05
130205 | 2012-07-16 16:20 | 2012-07-16 18:06 | 236 | 103 | 19001.5566 | 184.4811 | 0.058981 | 0.00073255 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-16 | 2013 | 2013 | 2012-07-16 | C | 184.4811 | 0.058981 | 0.00073255
130206 | 2012-07-14 17:39 | 2012-07-14 18:26 | 2906 | 44 | 127559.7447 | 2899.0851 | 0.39595 | 0.0090203 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-14 | 2013 | 2013 | 2012-07-14 | C | 2899.0851 | 0.39595 | 0.0090203
130207 | 2012-07-17 09:45 | 2012-07-17 11:00 | 27 | 72 | 1944 | 27 | 0.0060342 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | B | 27 | 0.0060342 | 8.3809e-05
130208 | 2012-07-17 09:15 | 2012-07-17 11:57 | 27 | 159 | 4293 | 27 | 0.013326 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | B | 27 | 0.013326 | 8.3809e-05
130209 | 2012-07-17 10:00 | 2012-07-17 14:00 | 33 | 237 | 7821 | 33 | 0.024277 | 0.00010243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | B | 33 | 0.024277 | 0.00010243
130214 | 2012-07-17 09:18 | 2012-07-17 15:14 | 14 | 353 | 4942 | 14 | 0.01534 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | B | 14 | 0.01534 | 4.3456e-05
130218 | 2012-07-02 08:36 | 2012-07-02 09:48 | 8 | 69 | 552 | 8 | 0.0017134 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-02 | 2013 | 2013 | 2012-07-02 | B | 8 | 0.0017134 | 2.4832e-05
130219 | 2012-07-17 19:29 | 2012-07-18 10:52 | 3 | 920 | 2760 | 3 | 0.0085671 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | C | 3 | 0.0085671 | 9.3121e-06
130220 | 2012-07-18 09:10 | 2012-07-18 11:15 | 3 | 122 | 366 | 3 | 0.0011361 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-18 | 2013 | 2013 | 2012-07-18 | B | 3 | 0.0011361 | 9.3121e-06
130224 | 2012-07-18 08:45 | 2012-07-18 15:10 | 20 | 382 | 7640 | 20 | 0.023715 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-18 | 2013 | 2013 | 2012-07-18 | B | 20 | 0.023715 | 6.2081e-05
130228 | 2012-07-18 09:23 | 2012-07-18 10:29 | 243 | 63 | 15309 | 243 | 0.04752 | 0.00075428 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-18 | 2013 | 2013 | 2012-07-18 | B | 243 | 0.04752 | 0.00075428
130229 | 2012-07-18 11:43 | 2012-07-18 13:12 | 1 | 86 | 86 | 1 | 0.00026695 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-18 | 2013 | 2013 | 2012-07-18 | C | 1 | 0.00026695 | 3.104e-06
130232 | 2012-07-19 09:35 | 2012-07-19 11:55 | 1 | 137 | 137 | 1 | 0.00042525 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 1 | 0.00042525 | 3.104e-06
130235 | 2012-07-19 08:45 | 2012-07-19 13:00 | 4 | 252 | 1008 | 4 | 0.0031289 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 4 | 0.0031289 | 1.2416e-05
130236 | 2012-07-19 09:25 | 2012-07-19 13:30 | 1 | 242 | 242 | 1 | 0.00075117 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 1 | 0.00075117 | 3.104e-06
130237 | 2012-07-19 09:15 | 2012-07-19 14:06 | 27 | 288 | 7776 | 27 | 0.024137 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 27 | 0.024137 | 8.3809e-05
130241 | 2012-07-19 08:49 | 2012-07-19 15:15 | 14 | 383 | 5362 | 14 | 0.016644 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 14 | 0.016644 | 4.3456e-05
130244 | 2012-07-19 09:30 | 2012-07-19 14:08 | 42 | 275 | 11550 | 42 | 0.035852 | 0.00013037 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | B | 42 | 0.035852 | 0.00013037
130246 | 2012-07-19 03:46 | 2012-07-19 05:28 | 226 | 99 | 19987.3235 | 201.8922 | 0.062041 | 0.00070151 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | C | 201.8922 | 0.062041 | 0.00070151
130248 | 2012-07-19 19:00 | 2012-07-19 20:00 | 4 | 57 | 228 | 4 | 0.00070772 | 1.2416e-05 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-07-19 | 2013 | 2013 | 2012-07-19 | C | 4 | 0.00070772 | 1.2416e-05
130250 | 2012-07-17 10:37 | 2012-07-17 11:47 | 9 | 67 | 603 | 9 | 0.0018717 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-17 | 2013 | 2013 | 2012-07-17 | B | 9 | 0.0018717 | 2.7936e-05
130251 | 2012-07-20 11:04 | 2012-07-20 11:45 | 11 | 38 | 418 | 11 | 0.0012975 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | C | 11 | 0.0012975 | 3.4144e-05
130254 | 2012-07-20 08:45 | 2012-07-20 11:14 | 243 | 146 | 35478 | 243 | 0.11012 | 0.00075428 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | B | 243 | 0.11012 | 0.00075428
130255 | 2012-07-20 16:24 | 2012-07-20 17:28 | 25 | 61 | 1525 | 25 | 0.0047336 | 7.7601e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | C | 25 | 0.0047336 | 7.7601e-05
130256 | 2012-07-20 09:30 | 2012-07-20 14:15 | 3 | 282 | 846 | 3 | 0.002626 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | B | 3 | 0.002626 | 9.3121e-06
130258 | 2012-07-20 09:30 | 2012-07-20 15:25 | 2 | 352 | 704 | 2 | 0.0021852 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | B | 2 | 0.0021852 | 6.2081e-06
130259 | 2012-07-20 16:42 | 2012-07-20 17:30 | 4 | 45 | 180 | 4 | 0.00055873 | 1.2416e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-20 | 2013 | 2013 | 2012-07-20 | C | 4 | 0.00055873 | 1.2416e-05
130260 | 2012-07-21 09:30 | 2012-07-21 13:00 | 6 | 207 | 1242 | 6 | 0.0038552 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-21 | 2013 | 2013 | 2012-07-21 | C | 6 | 0.0038552 | 1.8624e-05
130262 | 2012-07-21 10:26 | 2012-07-21 11:35 | 7 | 66 | 462 | 7 | 0.0014341 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-21 | 2013 | 2013 | 2012-07-21 | C | 7 | 0.0014341 | 2.1728e-05
130263 | 2012-07-21 15:45 | 2012-07-21 16:35 | 5 | 47 | 235 | 5 | 0.00072945 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-21 | 2013 | 2013 | 2012-07-21 | C | 5 | 0.00072945 | 1.552e-05
130264 | 2012-07-21 08:07 | 2012-07-21 10:27 | 6 | 137 | 822 | 6 | 0.0025515 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-21 | 2013 | 2013 | 2012-07-21 | B | 6 | 0.0025515 | 1.8624e-05
130265 | 2012-07-21 22:22 | 2012-07-21 23:43 | 33 | 78 | 2574 | 33 | 0.0079898 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-21 | 2013 | 2013 | 2012-07-21 | C | 33 | 0.0079898 | 0.00010243
130268 | 2012-07-22 11:01 | 2012-07-22 11:17 | 373 | 13 | 4849 | 373 | 0.015051 | 0.0011578 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-22 | 2013 | 2013 | 2012-07-22 | C | 373 | 0.015051 | 0.0011578
130269 | 2012-07-22 12:40 | 2012-07-22 16:30 | 1 | 227 | 227 | 1 | 0.00070461 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-22 | 2013 | 2013 | 2012-07-22 | C | 1 | 0.00070461 | 3.104e-06
130270 | 2012-07-22 20:10 | 2012-07-22 23:10 | 738 | 177 | 30567.9 | 172.7 | 0.094884 | 0.0022908 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-22 | 2013 | 2013 | 2012-07-22 | C | 172.7 | 0.094884 | 0.0022908
130271 | 2012-07-23 01:28 | 2012-07-23 07:48 | 455 | 377 | 53234.3842 | 141.2053 | 0.16524 | 0.0014123 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 141.2053 | 0.16524 | 0.0014123
130272 | 2012-07-23 09:30 | 2012-07-23 10:35 | 18 | 62 | 1116 | 18 | 0.0034641 | 5.5873e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 18 | 0.0034641 | 5.5873e-05
130273 | 2012-07-23 08:55 | 2012-07-23 12:20 | 14 | 202 | 2828 | 14 | 0.0087782 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | B | 14 | 0.0087782 | 4.3456e-05
130274 | 2012-07-23 10:10 | 2012-07-23 15:00 | 1 | 287 | 287 | 1 | 0.00089086 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 1 | 0.00089086 | 3.104e-06
130275 | 2012-07-23 14:09 | 2012-07-23 17:28 | 375 | 196 | 28276.201 | 144.2663 | 0.08777 | 0.001164 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 144.2663 | 0.08777 | 0.001164
130276 | 2012-07-23 14:33 | 2012-07-23 15:23 | 95 | 47 | 4465 | 95 | 0.013859 | 0.00029488 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 95 | 0.013859 | 0.00029488
130277 | 2012-07-23 10:00 | 2012-07-23 11:00 | 9 | 57 | 513 | 9 | 0.0015924 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | B | 9 | 0.0015924 | 2.7936e-05
130278 | 2012-07-23 13:01 | 2012-07-23 13:42 | 371 | 38 | 13141.5122 | 345.8293 | 0.040792 | 0.0011516 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 345.8293 | 0.040792 | 0.0011516
130279 | 2012-07-23 09:30 | 2012-07-23 10:17 | 30 | 44 | 1320 | 30 | 0.0040973 | 9.3121e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 30 | 0.0040973 | 9.3121e-05
130280 | 2012-07-23 10:25 | 2012-07-23 18:24 | 1 | 476 | 476 | 1 | 0.0014775 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 1 | 0.0014775 | 3.104e-06
130281 | 2012-07-23 18:48 | 2012-07-23 19:20 | 48 | 29 | 1392 | 48 | 0.0043208 | 0.00014899 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | C | 48 | 0.0043208 | 0.00014899
130286 | 2012-07-24 02:20 | 2012-07-24 03:55 | 161 | 92 | 14812 | 161 | 0.045977 | 0.00049975 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 161 | 0.045977 | 0.00049975
130288 | 2012-07-24 09:06 | 2012-07-24 11:29 | 91 | 140 | 12740 | 91 | 0.039545 | 0.00028247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | B | 91 | 0.039545 | 0.00028247
130289 | 2012-07-24 11:28 | 2012-07-24 12:36 | 91 | 65 | 5915 | 91 | 0.01836 | 0.00028247 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 91 | 0.01836 | 0.00028247
130290 | 2012-07-24 14:15 | 2012-07-24 15:00 | 1 | 42 | 42 | 1 | 0.00013037 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 1 | 0.00013037 | 3.104e-06
130291 | 2012-07-24 11:05 | 2012-07-24 11:15 | 5 | 7 | 35 | 5 | 0.00010864 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 5 | 0.00010864 | 1.552e-05
130292 | 2012-07-24 09:00 | 2012-07-24 14:10 | 19 | 307 | 5833 | 19 | 0.018106 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | B | 19 | 0.018106 | 5.8977e-05
130294 | 2012-07-24 13:00 | 2012-07-24 13:51 | 38 | 48 | 1824 | 38 | 0.0056617 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 38 | 0.0056617 | 0.00011795
130296 | 2012-07-25 09:45 | 2012-07-25 11:15 | 7 | 87 | 609 | 7 | 0.0018904 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | B | 7 | 0.0018904 | 2.1728e-05
130297 | 2012-07-25 05:04 | 2012-07-25 11:17 | 236 | 370 | 29344.0751 | 79.3083 | 0.091085 | 0.00073255 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | C | 79.3083 | 0.091085 | 0.00073255
130298 | 2012-07-25 10:30 | 2012-07-25 12:06 | 11 | 93 | 1023 | 11 | 0.0031754 | 3.4144e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | C | 11 | 0.0031754 | 3.4144e-05
130299 | 2012-07-25 09:00 | 2012-07-25 13:40 | 42 | 277 | 11634 | 42 | 0.036112 | 0.00013037 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | B | 42 | 0.036112 | 0.00013037
130302 | 2012-07-25 15:00 | 2012-07-25 15:40 | 116 | 37 | 4292 | 116 | 0.013322 | 0.00036007 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | C | 116 | 0.013322 | 0.00036007
130303 | 2012-07-25 16:47 | 2012-07-25 17:12 | 21 | 22 | 462 | 21 | 0.0014341 | 6.5185e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | C | 21 | 0.0014341 | 6.5185e-05
130304 | 2012-07-25 17:00 | 2012-07-25 17:32 | 9 | 29 | 261 | 9 | 0.00081015 | 2.7936e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-25 | 2013 | 2013 | 2012-07-25 | C | 9 | 0.00081015 | 2.7936e-05
130305 | 2012-07-26 01:00 | 2012-07-26 04:00 | 715 | 177 | 29991.6667 | 169.4444 | 0.093095 | 0.0022194 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 169.4444 | 0.093095 | 0.0022194
130306 | 2012-07-24 20:12 | 2012-07-24 21:12 | 100 | 57 | 5700 | 100 | 0.017693 | 0.0003104 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-24 | 2013 | 2013 | 2012-07-24 | C | 100 | 0.017693 | 0.0003104
130307 | 2012-07-26 06:30 | 2012-07-26 07:29 | 37 | 56 | 2072 | 37 | 0.0064315 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | B | 37 | 0.0064315 | 0.00011485
130308 | 2012-07-26 10:15 | 2012-07-26 10:59 | 62 | 41 | 2542 | 62 | 0.0078904 | 0.00019245 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 62 | 0.0078904 | 0.00019245
130313 | 2012-07-26 09:15 | 2012-07-26 14:09 | 24 | 291 | 6984 | 24 | 0.021679 | 7.4497e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | B | 24 | 0.021679 | 7.4497e-05
130314 | 2012-07-26 09:30 | 2012-07-26 14:10 | 51 | 277 | 14127 | 51 | 0.043851 | 0.00015831 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | B | 51 | 0.043851 | 0.00015831
130317 | 2012-07-26 13:56 | 2012-07-26 14:31 | 93 | 32 | 2976 | 93 | 0.0092376 | 0.00028867 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 93 | 0.0092376 | 0.00028867
130318 | 2012-07-26 09:00 | 2012-07-26 15:52 | 318 | 409 | 130062 | 318 | 0.40372 | 0.00098708 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | B | 318 | 0.40372 | 0.00098708
130319 | 2012-07-26 21:18 | 2012-07-27 01:00 | 52 | 219 | 7959.9595 | 36.3468 | 0.024708 | 0.00016141 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 36.3468 | 0.024708 | 0.00016141
130320 | 2012-07-26 23:09 | 2012-07-27 06:58 | 121 | 466 | 31347.194 | 67.2687 | 0.097303 | 0.00037559 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | B | 67.2687 | 0.097303 | 0.00037559
130322 | 2012-07-27 10:15 | 2012-07-27 10:49 | 7 | 31 | 217 | 7 | 0.00067357 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | B | 7 | 0.00067357 | 2.1728e-05
130324 | 2012-07-27 09:50 | 2012-07-27 11:05 | 13 | 72 | 936 | 13 | 0.0029054 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | B | 13 | 0.0029054 | 4.0352e-05
130325 | 2012-07-27 09:30 | 2012-07-27 14:07 | 132 | 274 | 36168 | 132 | 0.11227 | 0.00040973 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | B | 132 | 0.11227 | 0.00040973
130328 | 2012-07-27 16:07 | 2012-07-27 17:40 | 76 | 90 | 2236.4516 | 24.8495 | 0.006942 | 0.00023591 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | C | 24.8495 | 0.006942 | 0.00023591
130330 | 2012-07-27 07:20 | 2012-07-27 08:50 | 76 | 87 | 6612 | 76 | 0.020524 | 0.00023591 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | C | 76 | 0.020524 | 0.00023591
130331 | 2012-07-27 15:49 | 2012-07-27 17:33 | 523 | 101 | 29648.3558 | 293.5481 | 0.092029 | 0.0016234 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | C | 293.5481 | 0.092029 | 0.0016234
130332 | 2012-07-26 20:25 | 2012-07-26 22:18 | 1 | 110 | 110 | 1 | 0.00034144 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 1 | 0.00034144 | 3.104e-06
130333 | 2012-07-27 12:40 | 2012-07-27 14:00 | 1 | 77 | 77 | 1 | 0.00023901 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-27 | 2013 | 2013 | 2012-07-27 | C | 1 | 0.00023901 | 3.104e-06
130334 | 2012-07-28 02:19 | 2012-07-28 03:50 | 825 | 88 | 64703.2088 | 735.2637 | 0.20084 | 0.0025608 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-28 | 2013 | 2013 | 2012-07-28 | C | 735.2637 | 0.20084 | 0.0025608
130336 | 2012-07-29 09:00 | 2012-07-29 11:40 | 86 | 157 | 13502 | 86 | 0.041911 | 0.00026695 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | B | 86 | 0.041911 | 0.00026695
130337 | 2012-07-29 21:01 | 2012-07-29 21:21 | 168 | 17 | 2856 | 168 | 0.0088651 | 0.00052148 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | C | 168 | 0.0088651 | 0.00052148
130338 | 2012-07-29 16:38 | 2012-07-30 00:17 | 572 | 456 | 78449.8824 | 172.0392 | 0.24351 | 0.0017755 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | C | 172.0392 | 0.24351 | 0.0017755
130339 | 2012-07-29 22:31 | 2012-07-30 01:02 | 197 | 148 | 17083.7086 | 115.4305 | 0.053028 | 0.00061149 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | C | 115.4305 | 0.053028 | 0.00061149
130340 | 2012-07-29 20:00 | 2012-07-29 22:34 | 2 | 151 | 302 | 2 | 0.00093742 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | C | 2 | 0.00093742 | 6.2081e-06
130341 | 2012-07-29 23:10 | 2012-07-30 03:15 | 1342 | 242 | 194131.4122 | 802.1959 | 0.60259 | 0.0041656 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-29 | 2013 | 2013 | 2012-07-29 | C | 802.1959 | 0.60259 | 0.0041656
130344 | 2012-07-26 20:25 | 2012-07-26 21:09 | 2189 | 41 | 69267.6364 | 1689.4545 | 0.21501 | 0.0067947 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 1689.4545 | 0.21501 | 0.0067947
130345 | 2012-07-26 20:25 | 2012-07-26 21:30 | 152 | 62 | 9406.8308 | 151.7231 | 0.029199 | 0.00047181 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-26 | 2013 | 2013 | 2012-07-26 | C | 151.7231 | 0.029199 | 0.00047181
130350 | 2012-07-30 10:02 | 2012-07-30 12:05 | 20 | 120 | 2400 | 20 | 0.0074497 | 6.2081e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 20 | 0.0074497 | 6.2081e-05
130351 | 2012-07-30 07:54 | 2012-07-30 10:08 | 591 | 131 | 40421.3209 | 308.5597 | 0.12547 | 0.0018345 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 308.5597 | 0.12547 | 0.0018345
130353 | 2012-07-30 12:03 | 2012-07-30 12:18 | 22 | 12 | 264 | 22 | 0.00081946 | 6.8289e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 22 | 0.00081946 | 6.8289e-05
130354 | 2012-07-30 10:55 | 2012-07-30 11:01 | 291 | 3 | 873 | 291 | 0.0027098 | 0.00090327 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 291 | 0.0027098 | 0.00090327
130355 | 2012-07-30 14:00 | 2012-07-30 15:13 | 41 | 70 | 2817.2603 | 40.2466 | 0.0087449 | 0.00012727 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 40.2466 | 0.0087449 | 0.00012727
130356 | 2012-07-30 09:58 | 2012-07-30 15:07 | 21 | 306 | 6292.3107 | 20.5631 | 0.019532 | 6.5185e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 20.5631 | 0.019532 | 6.5185e-05
130357 | 2012-07-30 01:30 | 2012-07-30 13:41 | 236 | 728 | 47180.5746 | 64.8085 | 0.14645 | 0.00073255 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 64.8085 | 0.14645 | 0.00073255
130358 | 2012-07-30 12:50 | 2012-07-30 15:00 | 2 | 127 | 254 | 2 | 0.00078842 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 2 | 0.00078842 | 6.2081e-06
130359 | 2012-07-30 04:13 | 2012-07-30 15:10 | 1371 | 654 | 336111.2055 | 513.9315 | 1.0433 | 0.0042556 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 513.9315 | 1.0433 | 0.0042556
130360 | 2012-07-30 06:25 | 2012-07-30 13:03 | 534 | 395 | 75834.0452 | 191.9849 | 0.23539 | 0.0016576 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 191.9849 | 0.23539 | 0.0016576
130361 | 2012-07-30 13:46 | 2012-07-30 16:45 | 1 | 176 | 176 | 1 | 0.00054631 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 1 | 0.00054631 | 3.104e-06
130362 | 2012-07-30 15:24 | 2012-07-30 15:34 | 150 | 7 | 1050 | 150 | 0.0032592 | 0.0004656 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 150 | 0.0032592 | 0.0004656
130363 | 2012-07-30 15:39 | 2012-07-30 17:15 | 149 | 93 | 9061.6875 | 97.4375 | 0.028128 | 0.0004625 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 97.4375 | 0.028128 | 0.0004625
130364 | 2012-07-30 17:00 | 2012-07-31 13:55 | 21 | 1252 | 25104.8446 | 20.0518 | 0.077926 | 6.5185e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 20.0518 | 0.077926 | 6.5185e-05
130365 | 2012-07-30 16:28 | 2012-07-30 18:47 | 218 | 136 | 23248.1727 | 170.9424 | 0.072163 | 0.00067668 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 170.9424 | 0.072163 | 0.00067668
130366 | 2012-07-30 22:57 | 2012-07-31 00:16 | 1398 | 76 | 80281.0127 | 1056.3291 | 0.24919 | 0.0043394 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 1056.3291 | 0.24919 | 0.0043394
130367 | 2012-07-30 21:14 | 2012-07-31 11:07 | 612 | 830 | 69220.8043 | 83.3986 | 0.21486 | 0.0018997 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 83.3986 | 0.21486 | 0.0018997
130368 | 2012-07-30 02:37 | 2012-07-30 05:09 | 573 | 149 | 85377 | 573 | 0.26501 | 0.0017786 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 573 | 0.26501 | 0.0017786
130370 | 2012-07-31 10:15 | 2012-07-31 10:55 | 3 | 37 | 111 | 3 | 0.00034455 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | B | 3 | 0.00034455 | 9.3121e-06
130372 | 2012-07-31 10:00 | 2012-07-31 12:20 | 4 | 137 | 548 | 4 | 0.001701 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 4 | 0.001701 | 1.2416e-05
130373 | 2012-07-31 09:30 | 2012-07-31 14:15 | 57 | 282 | 16074 | 57 | 0.049894 | 0.00017693 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | B | 57 | 0.049894 | 0.00017693
130377 | 2012-07-31 10:55 | 2012-07-31 12:56 | 36 | 118 | 4248 | 36 | 0.013186 | 0.00011175 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 36 | 0.013186 | 0.00011175
130378 | 2012-08-01 09:10 | 2012-08-01 12:15 | 296 | 182 | 53872 | 296 | 0.16722 | 0.00091879 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 296 | 0.16722 | 0.00091879
130379 | 2012-08-01 10:00 | 2012-08-01 10:50 | 27 | 47 | 1269 | 27 | 0.003939 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 27 | 0.003939 | 8.3809e-05
130381 | 2012-08-01 09:15 | 2012-08-01 13:50 | 72 | 272 | 19584 | 72 | 0.060789 | 0.00022349 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 72 | 0.060789 | 0.00022349
130382 | 2012-07-31 22:19 | 2012-08-01 01:21 | 53 | 179 | 5539.1648 | 30.9451 | 0.017194 | 0.00016451 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 30.9451 | 0.017194 | 0.00016451
130384 | 2012-08-01 13:35 | 2012-08-01 14:25 | 5 | 47 | 235 | 5 | 0.00072945 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | C | 5 | 0.00072945 | 1.552e-05
130385 | 2012-08-01 08:16 | 2012-08-01 09:40 | 276 | 81 | 18219.2143 | 224.9286 | 0.056553 | 0.00085671 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | C | 224.9286 | 0.056553 | 0.00085671
130387 | 2012-08-01 09:03 | 2012-08-01 14:10 | 51 | 304 | 15504 | 51 | 0.048125 | 0.00015831 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 51 | 0.048125 | 0.00015831
130388 | 2012-08-01 08:47 | 2012-08-01 14:08 | 200 | 318 | 63600 | 200 | 0.19742 | 0.00062081 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 200 | 0.19742 | 0.00062081
130389 | 2012-07-31 15:00 | 2012-07-31 20:03 | 700 | 300 | 210000 | 700 | 0.65185 | 0.0021728 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 700 | 0.65185 | 0.0021728
130390 | 2012-08-01 14:57 | 2012-08-01 15:50 | 76 | 50 | 3800 | 76 | 0.011795 | 0.00023591 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | C | 76 | 0.011795 | 0.00023591
130391 | 2012-08-01 09:08 | 2012-08-01 15:45 | 45 | 394 | 17730 | 45 | 0.055034 | 0.00013968 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 45 | 0.055034 | 0.00013968
130394 | 2012-08-01 09:18 | 2012-08-01 14:49 | 76 | 328 | 24928 | 76 | 0.077377 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | B | 76 | 0.077377 | 0.00023591
130397 | 2012-07-31 22:54 | 2012-07-31 22:59 | 287 | 2 | 574 | 287 | 0.0017817 | 0.00089086 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 287 | 0.0017817 | 0.00089086
130398 | 2012-08-01 00:49 | 2012-08-01 00:53 | 130 | 1 | 130 | 130 | 0.00040352 | 0.00040352 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | C | 130 | 0.00040352 | 0.00040352
130399 | 2012-08-01 05:03 | 2012-08-01 05:07 | 339 | 1 | 339 | 339 | 0.0010523 | 0.0010523 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-08-01 | 2013 | 2013 | 2012-08-01 | C | 339 | 0.0010523 | 0.0010523
130404 | 2012-07-23 05:00 | 2012-07-23 06:17 | 234 | 74 | 17316 | 234 | 0.053749 | 0.00072634 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-07-23 | 2013 | 2013 | 2012-07-23 | B | 234 | 0.053749 | 0.00072634
130405 | 2012-08-02 09:30 | 2012-08-02 11:02 | 3 | 89 | 267 | 3 | 0.00082878 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 3 | 0.00082878 | 9.3121e-06
130406 | 2012-07-31 23:08 | 2012-08-01 15:00 | 109 | 949 | 62858.291 | 66.2363 | 0.19511 | 0.00033834 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-07-31 | 2013 | 2013 | 2012-07-31 | C | 66.2363 | 0.19511 | 0.00033834
130409 | 2012-07-30 17:45 | 2012-07-30 22:02 | 3 | 254 | 762 | 3 | 0.0023653 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-07-30 | 2013 | 2013 | 2012-07-30 | C | 3 | 0.0023653 | 9.3121e-06
130410 | 2012-08-02 08:15 | 2012-08-02 13:00 | 22 | 282 | 6204 | 22 | 0.019257 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 22 | 0.019257 | 6.8289e-05
130412 | 2012-08-02 10:00 | 2012-08-02 11:15 | 10 | 72 | 720 | 10 | 0.0022349 | 3.104e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 10 | 0.0022349 | 3.104e-05
130414 | 2012-08-02 07:50 | 2012-08-02 08:43 | 829 | 50 | 41450 | 829 | 0.12866 | 0.0025732 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 829 | 0.12866 | 0.0025732
130415 | 2012-08-02 07:50 | 2012-08-02 08:14 | 475 | 21 | 9975 | 475 | 0.030963 | 0.0014744 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 475 | 0.030963 | 0.0014744
130416 | 2012-08-02 07:50 | 2012-08-02 08:48 | 3 | 55 | 165 | 3 | 0.00051216 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 3 | 0.00051216 | 9.3121e-06
130419 | 2012-08-02 13:17 | 2012-08-02 14:20 | 54 | 60 | 3240 | 54 | 0.010057 | 0.00016762 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 54 | 0.010057 | 0.00016762
130420 | 2012-08-02 09:45 | 2012-08-02 16:15 | 20 | 387 | 7740 | 20 | 0.024025 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 20 | 0.024025 | 6.2081e-05
130423 | 2012-08-02 09:59 | 2012-08-02 16:24 | 1 | 382 | 382 | 1 | 0.0011857 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 1 | 0.0011857 | 3.104e-06
130424 | 2012-08-02 16:30 | 2012-08-02 16:45 | 68 | 12 | 816 | 68 | 0.0025329 | 0.00021107 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 68 | 0.0025329 | 0.00021107
130432 | 2012-08-02 19:52 | 2012-08-02 20:20 | 368 | 25 | 9200 | 368 | 0.028557 | 0.0011423 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | C | 368 | 0.028557 | 0.0011423
130433 | 2012-08-03 07:40 | 2012-08-03 09:20 | 7 | 97 | 679 | 7 | 0.0021076 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | C | 7 | 0.0021076 | 2.1728e-05
130435 | 2012-08-03 09:35 | 2012-08-03 11:05 | 1 | 87 | 87 | 1 | 0.00027005 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 1 | 0.00027005 | 3.104e-06
130436 | 2012-08-03 06:21 | 2012-08-03 08:50 | 51 | 146 | 7446 | 51 | 0.023113 | 0.00015831 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | C | 51 | 0.023113 | 0.00015831
130437 | 2012-08-03 10:45 | 2012-08-03 11:00 | 1 | 12 | 12 | 1 | 3.7248e-05 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | C | 1 | 3.7248e-05 | 3.104e-06
130440 | 2012-08-03 09:30 | 2012-08-03 12:30 | 1 | 177 | 177 | 1 | 0.00054941 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 1 | 0.00054941 | 3.104e-06
130441 | 2012-08-03 09:37 | 2012-08-03 12:25 | 14 | 165 | 2310 | 14 | 0.0071703 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 14 | 0.0071703 | 4.3456e-05
130444 | 2012-08-03 09:30 | 2012-08-03 15:09 | 40 | 336 | 13440 | 40 | 0.041718 | 0.00012416 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 40 | 0.041718 | 0.00012416
130445 | 2012-08-03 08:56 | 2012-08-03 15:42 | 11 | 403 | 4433 | 11 | 0.01376 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 11 | 0.01376 | 3.4144e-05
130446 | 2012-08-03 14:28 | 2012-08-03 15:39 | 16 | 68 | 1088 | 16 | 0.0033772 | 4.9664e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | C | 16 | 0.0033772 | 4.9664e-05
130447 | 2012-08-03 09:00 | 2012-08-03 15:10 | 13 | 367 | 4771 | 13 | 0.014809 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 13 | 0.014809 | 4.0352e-05
130448 | 2012-08-04 02:25 | 2012-08-04 04:26 | 268 | 118 | 15240.5289 | 129.157 | 0.047307 | 0.00083188 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 129.157 | 0.047307 | 0.00083188
130449 | 2012-08-04 08:30 | 2012-08-04 14:46 | 38 | 373 | 14174 | 38 | 0.043996 | 0.00011795 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 38 | 0.043996 | 0.00011795
130450 | 2012-08-04 08:42 | 2012-08-04 08:48 | 421 | 3 | 1263 | 421 | 0.0039204 | 0.0013068 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 421 | 0.0039204 | 0.0013068
130451 | 2012-08-04 06:31 | 2012-08-04 07:44 | 193 | 70 | 5219.3151 | 74.5616 | 0.016201 | 0.00059908 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 74.5616 | 0.016201 | 0.00059908
130452 | 2012-08-04 08:24 | 2012-08-04 09:07 | 1353 | 40 | 54120 | 1353 | 0.16799 | 0.0041998 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 1353 | 0.16799 | 0.0041998
130453 | 2012-08-04 02:33 | 2012-08-04 03:20 | 591 | 44 | 26004 | 591 | 0.080717 | 0.0018345 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 591 | 0.080717 | 0.0018345
130454 | 2012-08-04 02:33 | 2012-08-04 03:20 | 629 | 44 | 27676 | 629 | 0.085907 | 0.0019524 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 629 | 0.085907 | 0.0019524
130455 | 2012-08-04 13:00 | 2012-08-04 16:34 | 14 | 211 | 2954 | 14 | 0.0091693 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | B | 14 | 0.0091693 | 4.3456e-05
130459 | 2012-08-04 20:22 | 2012-08-04 22:12 | 1398 | 107 | 50026.3909 | 467.5364 | 0.15528 | 0.0043394 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-04 | 2013 | 2013 | 2012-08-04 | C | 467.5364 | 0.15528 | 0.0043394
130464 | 2012-08-05 07:26 | 2012-08-05 11:29 | 20 | 240 | 4800 | 20 | 0.014899 | 6.2081e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-05 | 2013 | 2013 | 2012-08-05 | C | 20 | 0.014899 | 6.2081e-05
130465 | 2012-08-06 05:52 | 2012-08-06 06:50 | 569 | 55 | 31295 | 569 | 0.097141 | 0.0017662 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 569 | 0.097141 | 0.0017662
130466 | 2012-08-06 04:10 | 2012-08-06 08:32 | 205 | 259 | 25887.1489 | 99.9504 | 0.080354 | 0.00063633 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 99.9504 | 0.080354 | 0.00063633
130468 | 2012-08-06 08:10 | 2012-08-06 11:50 | 11 | 217 | 2387 | 11 | 0.0074093 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 11 | 0.0074093 | 3.4144e-05
130470 | 2012-08-06 07:08 | 2012-08-06 10:32 | 95 | 201 | 19095 | 95 | 0.059271 | 0.00029488 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | B | 95 | 0.059271 | 0.00029488
130473 | 2012-08-06 09:02 | 2012-08-06 11:51 | 4 | 166 | 664 | 4 | 0.0020611 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | B | 4 | 0.0020611 | 1.2416e-05
130474 | 2012-08-06 09:30 | 2012-08-06 12:23 | 4 | 170 | 680 | 4 | 0.0021107 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | B | 4 | 0.0021107 | 1.2416e-05
130475 | 2012-08-06 12:35 | 2012-08-06 12:50 | 2 | 12 | 24 | 2 | 7.4497e-05 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 2 | 7.4497e-05 | 6.2081e-06
130478 | 2012-08-06 13:10 | 2012-08-06 13:19 | 1 | 6 | 6 | 1 | 1.8624e-05 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 1 | 1.8624e-05 | 3.104e-06
130480 | 2012-08-06 10:00 | 2012-08-06 14:02 | 3 | 239 | 717 | 3 | 0.0022256 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | B | 3 | 0.0022256 | 9.3121e-06
130482 | 2012-08-06 09:00 | 2012-08-06 15:10 | 13 | 367 | 4771 | 13 | 0.014809 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | B | 13 | 0.014809 | 4.0352e-05
130484 | 2012-08-06 16:05 | 2012-08-06 16:25 | 6 | 17 | 102 | 6 | 0.00031661 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-06 | 2013 | 2013 | 2012-08-06 | C | 6 | 0.00031661 | 1.8624e-05
130486 | 2012-08-07 09:28 | 2012-08-07 11:30 | 2 | 119 | 238 | 2 | 0.00073876 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 2 | 0.00073876 | 6.2081e-06
130487 | 2012-08-07 12:18 | 2012-08-07 12:50 | 17 | 29 | 493 | 17 | 0.0015303 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | C | 17 | 0.0015303 | 5.2768e-05
130488 | 2012-08-07 09:30 | 2012-08-07 14:35 | 19 | 302 | 5738 | 19 | 0.017811 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 19 | 0.017811 | 5.8977e-05
130489 | 2012-08-07 09:09 | 2012-08-07 14:18 | 19 | 306 | 5814 | 19 | 0.018047 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 19 | 0.018047 | 5.8977e-05
130490 | 2012-08-07 10:37 | 2012-08-07 15:05 | 179 | 265 | 33065.6716 | 124.7761 | 0.10264 | 0.00055562 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | C | 124.7761 | 0.10264 | 0.00055562
130491 | 2012-08-07 09:27 | 2012-08-07 15:11 | 19 | 341 | 6479 | 19 | 0.020111 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 19 | 0.020111 | 5.8977e-05
130492 | 2012-08-07 09:15 | 2012-08-07 14:59 | 3 | 341 | 1023 | 3 | 0.0031754 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 3 | 0.0031754 | 9.3121e-06
130493 | 2012-08-07 09:30 | 2012-08-07 14:24 | 38 | 291 | 11058 | 38 | 0.034324 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 38 | 0.034324 | 0.00011795
130494 | 2012-08-07 08:15 | 2012-08-07 16:21 | 3 | 483 | 1449 | 3 | 0.0044977 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 3 | 0.0044977 | 9.3121e-06
130495 | 2012-08-07 09:30 | 2012-08-07 13:20 | 2 | 227 | 454 | 2 | 0.0014092 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | C | 2 | 0.0014092 | 6.2081e-06
130496 | 2012-08-07 10:15 | 2012-08-07 17:28 | 16 | 430 | 6880 | 16 | 0.021356 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 16 | 0.021356 | 4.9664e-05
130498 | 2012-08-08 05:03 | 2012-08-08 11:22 | 66 | 376 | 24816 | 66 | 0.07703 | 0.00020487 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 66 | 0.07703 | 0.00020487
130500 | 2012-08-08 06:47 | 2012-08-08 08:36 | 1180 | 106 | 99293.7982 | 936.7339 | 0.30821 | 0.0036628 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 936.7339 | 0.30821 | 0.0036628
130507 | 2012-08-08 08:02 | 2012-08-08 14:45 | 5 | 400 | 2000 | 5 | 0.0062081 | 1.552e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 5 | 0.0062081 | 1.552e-05
130509 | 2012-08-08 09:30 | 2012-08-08 13:10 | 102 | 217 | 22134 | 102 | 0.068705 | 0.00031661 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | B | 102 | 0.068705 | 0.00031661
130511 | 2012-08-08 09:15 | 2012-08-08 13:39 | 47 | 261 | 12267 | 47 | 0.038077 | 0.00014589 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | B | 47 | 0.038077 | 0.00014589
130512 | 2012-08-08 10:30 | 2012-08-08 13:01 | 53 | 148 | 7844 | 53 | 0.024348 | 0.00016451 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 53 | 0.024348 | 0.00016451
130513 | 2012-08-08 12:13 | 2012-08-08 15:24 | 257 | 188 | 23367.1204 | 124.2932 | 0.072532 | 0.00079774 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 124.2932 | 0.072532 | 0.00079774
130514 | 2012-08-08 20:01 | 2012-08-08 22:42 | 733 | 158 | 46453.9627 | 294.0124 | 0.14419 | 0.0022753 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-08 | 2013 | 2013 | 2012-08-08 | C | 294.0124 | 0.14419 | 0.0022753
130518 | 2012-08-09 09:14 | 2012-08-09 10:12 | 51 | 55 | 2805 | 51 | 0.0087068 | 0.00015831 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | C | 51 | 0.0087068 | 0.00015831
130520 | 2012-08-09 09:00 | 2012-08-09 10:41 | 3 | 98 | 294 | 3 | 0.00091258 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 3 | 0.00091258 | 9.3121e-06
130522 | 2012-08-09 09:30 | 2012-08-09 10:30 | 13 | 57 | 741 | 13 | 0.0023001 | 4.0352e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 13 | 0.0023001 | 4.0352e-05
130524 | 2012-08-09 10:40 | 2012-08-09 14:28 | 3 | 225 | 675 | 3 | 0.0020952 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 3 | 0.0020952 | 9.3121e-06
130526 | 2012-08-09 09:00 | 2012-08-09 14:40 | 43 | 337 | 14491 | 43 | 0.04498 | 0.00013347 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 43 | 0.04498 | 0.00013347
130528 | 2012-08-09 13:00 | 2012-08-09 14:45 | 1 | 102 | 102 | 1 | 0.00031661 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 1 | 0.00031661 | 3.104e-06
130529 | 2012-08-09 10:15 | 2012-08-09 14:55 | 30 | 277 | 8310 | 30 | 0.025794 | 9.3121e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 30 | 0.025794 | 9.3121e-05
130530 | 2012-08-09 08:45 | 2012-08-09 16:00 | 59 | 432 | 25488 | 59 | 0.079115 | 0.00018314 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 59 | 0.079115 | 0.00018314
130533 | 2012-08-09 09:42 | 2012-08-09 16:55 | 31 | 430 | 13330 | 31 | 0.041377 | 9.6225e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-09 | 2013 | 2013 | 2012-08-09 | B | 31 | 0.041377 | 9.6225e-05
130537 | 2012-08-10 09:10 | 2012-08-10 11:13 | 109 | 120 | 13080 | 109 | 0.040601 | 0.00033834 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | C | 109 | 0.040601 | 0.00033834
130540 | 2012-08-10 10:23 | 2012-08-10 10:49 | 290 | 23 | 6670 | 290 | 0.020704 | 0.00090017 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | C | 290 | 0.020704 | 0.00090017
130542 | 2012-08-10 11:30 | 2012-08-10 12:35 | 8 | 62 | 496 | 8 | 0.0015396 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | C | 8 | 0.0015396 | 2.4832e-05
130544 | 2012-08-10 09:30 | 2012-08-10 14:00 | 240 | 267 | 64080 | 240 | 0.19891 | 0.00074497 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | B | 240 | 0.19891 | 0.00074497
130546 | 2012-08-10 11:58 | 2012-08-10 16:15 | 1 | 254 | 254 | 1 | 0.00078842 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | B | 1 | 0.00078842 | 3.104e-06
130548 | 2012-08-11 01:16 | 2012-08-11 02:47 | 1 | 88 | 88 | 1 | 0.00027315 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | B | 1 | 0.00027315 | 3.104e-06
130549 | 2012-08-10 21:00 | 2012-08-10 23:45 | 1 | 162 | 162 | 1 | 0.00050285 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | B | 1 | 0.00050285 | 3.104e-06
130550 | 2012-08-11 08:00 | 2012-08-11 08:34 | 1 | 31 | 31 | 1 | 9.6225e-05 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | C | 1 | 9.6225e-05 | 3.104e-06
130551 | 2012-08-10 22:42 | 2012-08-11 12:00 | 10 | 795 | 7950 | 10 | 0.024677 | 3.104e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | C | 10 | 0.024677 | 3.104e-05
130552 | 2012-08-10 21:15 | 2012-08-10 22:05 | 560 | 47 | 26320 | 560 | 0.081698 | 0.0017383 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-10 | 2013 | 2013 | 2012-08-10 | C | 560 | 0.081698 | 0.0017383
130553 | 2012-08-11 20:31 | 2012-08-12 02:52 | 155 | 378 | 22909.1811 | 60.6063 | 0.071111 | 0.00048112 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | C | 60.6063 | 0.071111 | 0.00048112
130555 | 2012-08-12 09:06 | 2012-08-12 10:47 | 77 | 98 | 7546 | 77 | 0.023423 | 0.00023901 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 77 | 0.023423 | 0.00023901
130556 | 2012-08-12 09:03 | 2012-08-12 12:00 | 1 | 174 | 174 | 1 | 0.0005401 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 1 | 0.0005401 | 3.104e-06
130557 | 2012-08-11 11:02 | 2012-08-11 19:40 | 464 | 515 | 11483.1081 | 22.2973 | 0.035644 | 0.0014403 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | C | 22.2973 | 0.035644 | 0.0014403
130558 | 2012-08-12 08:11 | 2012-08-12 09:46 | 559 | 92 | 51426.0632 | 558.9789 | 0.15963 | 0.0017352 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 558.9789 | 0.15963 | 0.0017352
130559 | 2012-08-12 08:11 | 2012-08-12 08:59 | 138 | 45 | 5318.4375 | 118.1875 | 0.016509 | 0.00042836 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 118.1875 | 0.016509 | 0.00042836
130561 | 2012-08-12 08:42 | 2012-08-12 13:30 | 251 | 285 | 19706.5625 | 69.1458 | 0.06117 | 0.00077911 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 69.1458 | 0.06117 | 0.00077911
130562 | 2012-08-11 15:01 | 2012-08-11 20:25 | 1329 | 321 | 139120.8056 | 433.3981 | 0.43183 | 0.0041253 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | C | 433.3981 | 0.43183 | 0.0041253
130563 | 2012-08-12 13:35 | 2012-08-12 17:05 | 368 | 207 | 28021.8857 | 135.3714 | 0.086981 | 0.0011423 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 135.3714 | 0.086981 | 0.0011423
130564 | 2012-08-12 15:37 | 2012-08-12 16:15 | 14 | 35 | 490 | 14 | 0.001521 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 14 | 0.001521 | 4.3456e-05
130565 | 2012-08-12 00:35 | 2012-08-12 11:20 | 39 | 642 | 25038 | 39 | 0.077719 | 0.00012106 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 39 | 0.077719 | 0.00012106
130566 | 2012-08-11 22:00 | 2012-08-12 12:46 | 97 | 883 | 85651 | 97 | 0.26586 | 0.00030109 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-11 | 2013 | 2013 | 2012-08-11 | C | 97 | 0.26586 | 0.00030109
130567 | 2012-08-12 21:00 | 2012-08-13 00:30 | 14 | 207 | 2898 | 14 | 0.0089955 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 14 | 0.0089955 | 4.3456e-05
130568 | 2012-08-13 02:03 | 2012-08-13 10:10 | 186 | 484 | 18314.4805 | 37.8398 | 0.056849 | 0.00057735 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 37.8398 | 0.056849 | 0.00057735
130569 | 2012-08-13 04:45 | 2012-08-13 07:08 | 449 | 140 | 25735.5245 | 183.8252 | 0.079884 | 0.0013937 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 183.8252 | 0.079884 | 0.0013937
130570 | 2012-08-12 20:34 | 2012-08-13 15:53 | 78 | 1156 | 90168 | 78 | 0.27988 | 0.00024211 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-08-12 | 2013 | 2013 | 2012-08-12 | C | 78 | 0.27988 | 0.00024211
130572 | 2012-08-13 09:00 | 2012-08-13 10:23 | 2 | 80 | 160 | 2 | 0.00049664 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | B | 2 | 0.00049664 | 6.2081e-06
130573 | 2012-08-13 10:12 | 2012-08-13 10:17 | 221 | 2 | 442 | 221 | 0.001372 | 0.00068599 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 221 | 0.001372 | 0.00068599
130574 | 2012-08-13 10:35 | 2012-08-13 11:22 | 128 | 44 | 2928.3404 | 66.5532 | 0.0090897 | 0.00039732 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 66.5532 | 0.0090897 | 0.00039732
130575 | 2012-08-13 09:00 | 2012-08-13 13:21 | 14 | 258 | 3612 | 14 | 0.011212 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | B | 14 | 0.011212 | 4.3456e-05
130576 | 2012-08-13 13:20 | 2012-08-13 14:15 | 10 | 52 | 520 | 10 | 0.0016141 | 3.104e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 10 | 0.0016141 | 3.104e-05
130580 | 2012-08-13 08:00 | 2012-08-13 14:27 | 21 | 384 | 7666.1085 | 19.9638 | 0.023796 | 6.5185e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 19.9638 | 0.023796 | 6.5185e-05
130581 | 2012-08-13 13:54 | 2012-08-13 15:27 | 774 | 90 | 36871.9355 | 409.6882 | 0.11445 | 0.0024025 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | C | 409.6882 | 0.11445 | 0.0024025
130583 | 2012-08-13 08:30 | 2012-08-13 16:07 | 164 | 454 | 74456 | 164 | 0.23111 | 0.00050906 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-13 | 2013 | 2013 | 2012-08-13 | B | 164 | 0.23111 | 0.00050906
130587 | 2012-08-14 11:12 | 2012-08-14 11:49 | 8 | 34 | 272 | 8 | 0.0008443 | 2.4832e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | C | 8 | 0.0008443 | 2.4832e-05
130588 | 2012-08-14 10:15 | 2012-08-14 12:11 | 43 | 113 | 4859 | 43 | 0.015082 | 0.00013347 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | C | 43 | 0.015082 | 0.00013347
130589 | 2012-08-14 09:00 | 2012-08-14 13:08 | 1 | 245 | 245 | 1 | 0.00076049 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 1 | 0.00076049 | 3.104e-06
130590 | 2012-08-14 12:34 | 2012-08-14 15:19 | 26 | 162 | 4212 | 26 | 0.013074 | 8.0705e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | C | 26 | 0.013074 | 8.0705e-05
130591 | 2012-08-14 09:30 | 2012-08-14 14:00 | 233 | 267 | 62211 | 233 | 0.1931 | 0.00072324 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 233 | 0.1931 | 0.00072324
130592 | 2012-08-14 08:45 | 2012-08-14 14:25 | 49 | 337 | 16513 | 49 | 0.051257 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 49 | 0.051257 | 0.0001521
130593 | 2012-08-14 09:12 | 2012-08-14 14:45 | 3 | 330 | 990 | 3 | 0.003073 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 3 | 0.003073 | 9.3121e-06
130595 | 2012-08-14 09:15 | 2012-08-14 15:28 | 10 | 370 | 3700 | 10 | 0.011485 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 10 | 0.011485 | 3.104e-05
130596 | 2012-08-14 15:10 | 2012-08-14 17:07 | 7 | 114 | 798 | 7 | 0.002477 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | C | 7 | 0.002477 | 2.1728e-05
130599 | 2012-08-14 08:00 | 2012-08-14 15:50 | 68 | 467 | 31756 | 68 | 0.098572 | 0.00021107 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-14 | 2013 | 2013 | 2012-08-14 | B | 68 | 0.098572 | 0.00021107
130602 | 2012-08-15 07:40 | 2012-08-15 08:44 | 2 | 61 | 122 | 2 | 0.00037869 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | C | 2 | 0.00037869 | 6.2081e-06
130603 | 2012-08-15 09:00 | 2012-08-15 09:50 | 5 | 47 | 235 | 5 | 0.00072945 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | B | 5 | 0.00072945 | 1.552e-05
130604 | 2012-08-15 09:00 | 2012-08-15 11:06 | 62 | 123 | 7626 | 62 | 0.023671 | 0.00019245 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | C | 62 | 0.023671 | 0.00019245
130605 | 2012-08-15 08:33 | 2012-08-15 11:35 | 11 | 179 | 1969 | 11 | 0.0061118 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | B | 11 | 0.0061118 | 3.4144e-05
130606 | 2012-08-15 11:45 | 2012-08-15 13:00 | 19 | 72 | 1368 | 19 | 0.0042463 | 5.8977e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | C | 19 | 0.0042463 | 5.8977e-05
130607 | 2012-08-15 12:47 | 2012-08-15 12:59 | 11 | 9 | 99 | 11 | 0.0003073 | 3.4144e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | C | 11 | 0.0003073 | 3.4144e-05
130608 | 2012-08-15 12:00 | 2012-08-15 14:25 | 12 | 142 | 1704 | 12 | 0.0052893 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | B | 12 | 0.0052893 | 3.7248e-05
130609 | 2012-08-15 08:45 | 2012-08-15 15:33 | 103 | 405 | 41715 | 103 | 0.12948 | 0.00031971 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | B | 103 | 0.12948 | 0.00031971
130611 | 2012-08-16 02:27 | 2012-08-16 02:42 | 306 | 12 | 3672 | 306 | 0.011398 | 0.00094983 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 306 | 0.011398 | 0.00094983
130612 | 2012-08-16 11:22 | 2012-08-16 12:07 | 30 | 42 | 1260 | 30 | 0.0039111 | 9.3121e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 30 | 0.0039111 | 9.3121e-05
130613 | 2012-08-16 11:30 | 2012-08-16 13:03 | 366 | 90 | 8285.8065 | 92.0645 | 0.025719 | 0.0011361 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 92.0645 | 0.025719 | 0.0011361
130614 | 2012-08-16 09:00 | 2012-08-16 14:02 | 49 | 299 | 14651 | 49 | 0.045477 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | B | 49 | 0.045477 | 0.0001521
130616 | 2012-08-16 13:35 | 2012-08-16 14:26 | 12 | 48 | 576 | 12 | 0.0017879 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 12 | 0.0017879 | 3.7248e-05
130619 | 2012-08-16 12:12 | 2012-08-16 13:38 | 779 | 83 | 31210.8953 | 376.0349 | 0.09688 | 0.002418 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 376.0349 | 0.09688 | 0.002418
130620 | 2012-08-16 09:31 | 2012-08-16 14:00 | 240 | 266 | 63840 | 240 | 0.19816 | 0.00074497 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | B | 240 | 0.19816 | 0.00074497
130622 | 2012-08-16 08:45 | 2012-08-16 15:28 | 2 | 400 | 800 | 2 | 0.0024832 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | B | 2 | 0.0024832 | 6.2081e-06
130623 | 2012-08-16 13:25 | 2012-08-16 16:45 | 401 | 197 | 78997 | 401 | 0.24521 | 0.0012447 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 401 | 0.24521 | 0.0012447
130624 | 2012-08-16 07:45 | 2012-08-16 10:35 | 533 | 167 | 18463.3235 | 110.5588 | 0.057311 | 0.0016544 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 110.5588 | 0.057311 | 0.0016544
130625 | 2012-08-16 08:14 | 2012-08-16 11:18 | 503 | 181 | 31680.9022 | 175.0326 | 0.098338 | 0.0015613 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 175.0326 | 0.098338 | 0.0015613
130626 | 2012-08-16 18:49 | 2012-08-16 19:50 | 63 | 58 | 3654 | 63 | 0.011342 | 0.00019555 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 63 | 0.011342 | 0.00019555
130627 | 2012-08-16 17:00 | 2012-08-16 19:05 | 13 | 122 | 1586 | 13 | 0.004923 | 4.0352e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-16 | 2013 | 2013 | 2012-08-16 | C | 13 | 0.004923 | 4.0352e-05
130628 | 2012-08-17 09:46 | 2012-08-17 10:47 | 6 | 58 | 348 | 6 | 0.0010802 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-17 | 2013 | 2013 | 2012-08-17 | B | 6 | 0.0010802 | 1.8624e-05
130629 | 2012-08-17 09:30 | 2012-08-17 14:10 | 233 | 277 | 64541 | 233 | 0.20034 | 0.00072324 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-17 | 2013 | 2013 | 2012-08-17 | B | 233 | 0.20034 | 0.00072324
130632 | 2012-08-18 08:30 | 2012-08-18 12:57 | 42 | 264 | 11088 | 42 | 0.034417 | 0.00013037 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-18 | 2013 | 2013 | 2012-08-18 | B | 42 | 0.034417 | 0.00013037
130633 | 2012-08-18 14:04 | 2012-08-18 16:07 | 793 | 120 | 50319.0244 | 419.3252 | 0.15619 | 0.0024615 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-18 | 2013 | 2013 | 2012-08-18 | C | 419.3252 | 0.15619 | 0.0024615
130636 | 2012-08-18 08:15 | 2012-08-18 11:38 | 1 | 200 | 200 | 1 | 0.00062081 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-18 | 2013 | 2013 | 2012-08-18 | B | 1 | 0.00062081 | 3.104e-06
130637 | 2012-08-18 12:54 | 2012-08-18 14:51 | 429 | 114 | 48906 | 429 | 0.15181 | 0.0013316 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-18 | 2013 | 2013 | 2012-08-18 | C | 429 | 0.15181 | 0.0013316
130639 | 2012-08-19 05:31 | 2012-08-19 06:04 | 105 | 30 | 2997.2727 | 99.9091 | 0.0093036 | 0.00032592 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-19 | 2013 | 2013 | 2012-08-19 | C | 99.9091 | 0.0093036 | 0.00032592
130640 | 2012-08-19 07:21 | 2012-08-19 11:45 | 30 | 261 | 6451.8409 | 24.7197 | 0.020027 | 9.3121e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-19 | 2013 | 2013 | 2012-08-19 | C | 24.7197 | 0.020027 | 9.3121e-05
130641 | 2012-08-19 12:16 | 2012-08-19 12:56 | 160 | 37 | 5920 | 160 | 0.018376 | 0.00049664 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-19 | 2013 | 2013 | 2012-08-19 | C | 160 | 0.018376 | 0.00049664
130643 | 2012-08-19 20:30 | 2012-08-19 21:52 | 89 | 79 | 2975.9878 | 37.6707 | 0.0092376 | 0.00027626 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-19 | 2013 | 2013 | 2012-08-19 | C | 37.6707 | 0.0092376 | 0.00027626
130650 | 2012-08-19 05:31 | 2012-08-19 07:56 | 123 | 142 | 6884.5517 | 48.4828 | 0.02137 | 0.0003818 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-19 | 2013 | 2013 | 2012-08-19 | C | 48.4828 | 0.02137 | 0.0003818
130651 | 2012-08-20 07:40 | 2012-08-20 08:30 | 12 | 47 | 564 | 12 | 0.0017507 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 12 | 0.0017507 | 3.7248e-05
130652 | 2012-08-20 01:49 | 2012-08-20 10:33 | 64 | 521 | 31163.5553 | 59.8149 | 0.096733 | 0.00019866 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 59.8149 | 0.096733 | 0.00019866
130655 | 2012-08-20 09:30 | 2012-08-20 15:25 | 10 | 352 | 3520 | 10 | 0.010926 | 3.104e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 10 | 0.010926 | 3.104e-05
130656 | 2012-08-20 09:45 | 2012-08-20 14:25 | 1 | 277 | 277 | 1 | 0.00085982 | 3.104e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 1 | 0.00085982 | 3.104e-06
130659 | 2012-08-20 10:20 | 2012-08-20 14:46 | 4 | 263 | 1052 | 4 | 0.0032654 | 1.2416e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 4 | 0.0032654 | 1.2416e-05
130660 | 2012-08-03 08:30 | 2012-08-03 14:40 | 135 | 367 | 21200.6973 | 57.7676 | 0.065808 | 0.00041904 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-03 | 2013 | 2013 | 2012-08-03 | B | 57.7676 | 0.065808 | 0.00041904
130661 | 2012-08-20 15:00 | 2012-08-20 17:36 | 4 | 153 | 612 | 4 | 0.0018997 | 1.2416e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 4 | 0.0018997 | 1.2416e-05
130662 | 2012-08-20 09:00 | 2012-08-20 15:00 | 120 | 357 | 42840 | 120 | 0.13298 | 0.00037248 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | B | 120 | 0.13298 | 0.00037248
130663 | 2012-08-20 09:48 | 2012-08-20 15:39 | 31 | 348 | 10788 | 31 | 0.033486 | 9.6225e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | B | 31 | 0.033486 | 9.6225e-05
130664 | 2012-08-20 16:00 | 2012-08-20 16:51 | 2 | 48 | 96 | 2 | 0.00029799 | 6.2081e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 2 | 0.00029799 | 6.2081e-06
130665 | 2012-08-20 17:30 | 2012-08-20 18:00 | 27 | 27 | 729 | 27 | 0.0022628 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 27 | 0.0022628 | 8.3809e-05
130666 | 2012-08-20 17:15 | 2012-08-20 18:05 | 21 | 47 | 987 | 21 | 0.0030637 | 6.5185e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 21 | 0.0030637 | 6.5185e-05
130667 | 2012-08-20 09:30 | 2012-08-20 18:25 | 3 | 532 | 3284.4785 | 6.1738 | 0.010195 | 9.3121e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 6.1738 | 0.010195 | 9.3121e-06
130670 | 2012-08-21 09:45 | 2012-08-21 12:13 | 2 | 145 | 290 | 2 | 0.00090017 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | B | 2 | 0.00090017 | 6.2081e-06
130671 | 2012-08-21 12:13 | 2012-08-21 12:20 | 139 | 4 | 556 | 139 | 0.0017258 | 0.00043146 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | C | 139 | 0.0017258 | 0.00043146
130675 | 2012-08-21 10:20 | 2012-08-21 14:05 | 46 | 222 | 10212 | 46 | 0.031698 | 0.00014279 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | B | 46 | 0.031698 | 0.00014279
130676 | 2012-08-21 13:45 | 2012-08-21 15:10 | 12 | 82 | 984 | 12 | 0.0030544 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | C | 12 | 0.0030544 | 3.7248e-05
130677 | 2012-08-21 15:43 | 2012-08-21 17:35 | 7 | 109 | 763 | 7 | 0.0023684 | 2.1728e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | C | 7 | 0.0023684 | 2.1728e-05
130678 | 2012-08-21 09:17 | 2012-08-21 15:00 | 27 | 340 | 9180 | 27 | 0.028495 | 8.3809e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | B | 27 | 0.028495 | 8.3809e-05
130680 | 2012-08-21 12:15 | 2012-08-21 17:15 | 1 | 297 | 297 | 1 | 0.0009219 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | C | 1 | 0.0009219 | 3.104e-06
130681 | 2012-08-21 11:39 | 2012-08-21 14:08 | 781 | 146 | 67851.7852 | 464.7383 | 0.21061 | 0.0024242 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | C | 464.7383 | 0.21061 | 0.0024242
130682 | 2012-08-21 08:48 | 2012-08-21 12:30 | 139 | 219 | 30441 | 139 | 0.09449 | 0.00043146 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | B | 139 | 0.09449 | 0.00043146
130683 | 2012-08-21 09:03 | 2012-08-21 15:53 | 146 | 407 | 59422 | 146 | 0.18445 | 0.00045319 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-21 | 2013 | 2013 | 2012-08-21 | B | 146 | 0.18445 | 0.00045319
130687 | 2012-08-20 03:30 | 2012-08-21 14:40 | 1 | 2107 | 2107 | 1 | 0.0065402 | 3.104e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-20 | 2013 | 2013 | 2012-08-20 | C | 1 | 0.0065402 | 3.104e-06
130689 | 2012-08-22 09:00 | 2012-08-22 10:55 | 7 | 112 | 784 | 7 | 0.0024336 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-22 | 2013 | 2013 | 2012-08-22 | B | 7 | 0.0024336 | 2.1728e-05
130691 | 2012-08-02 09:05 | 2012-08-02 10:10 | 2 | 62 | 124 | 2 | 0.0003849 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 2 | 0.0003849 | 6.2081e-06
130692 | 2012-08-22 10:00 | 2012-08-22 13:58 | 221 | 235 | 51935 | 221 | 0.16121 | 0.00068599 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-22 | 2013 | 2013 | 2012-08-22 | C | 221 | 0.16121 | 0.00068599
130693 | 2012-08-07 13:05 | 2012-08-07 15:00 | 4 | 112 | 448 | 4 | 0.0013906 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-07 | 2013 | 2013 | 2012-08-07 | B | 4 | 0.0013906 | 1.2416e-05
130694 | 2012-08-15 09:17 | 2012-08-15 15:29 | 3 | 369 | 1107 | 3 | 0.0034362 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-15 | 2013 | 2013 | 2012-08-15 | B | 3 | 0.0034362 | 9.3121e-06
130696 | 2012-08-22 09:11 | 2012-08-22 13:51 | 2 | 277 | 554 | 2 | 0.0017196 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-22 | 2013 | 2013 | 2012-08-22 | B | 2 | 0.0017196 | 6.2081e-06
130699 | 2012-08-22 13:00 | 2012-08-22 14:20 | 3 | 77 | 231 | 3 | 0.00071703 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-22 | 2013 | 2013 | 2012-08-22 | B | 3 | 0.00071703 | 9.3121e-06
130701 | 2012-08-22 09:04 | 2012-08-22 15:52 | 12 | 405 | 4860 | 12 | 0.015086 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-22 | 2013 | 2013 | 2012-08-22 | B | 12 | 0.015086 | 3.7248e-05
130705 | 2012-08-23 09:41 | 2012-08-23 12:38 | 15 | 174 | 2610 | 15 | 0.0081015 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-23 | 2013 | 2013 | 2012-08-23 | B | 15 | 0.0081015 | 4.656e-05
130710 | 2012-08-23 11:04 | 2012-08-23 13:52 | 2 | 165 | 330 | 2 | 0.0010243 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-23 | 2013 | 2013 | 2012-08-23 | C | 2 | 0.0010243 | 6.2081e-06
130711 | 2012-08-23 21:05 | 2012-08-23 22:20 | 4 | 72 | 138.24 | 1.92 | 0.0004291 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-23 | 2013 | 2013 | 2012-08-23 | B | 1.92 | 0.0004291 | 1.2416e-05
130715 | 2012-08-24 18:56 | 2012-08-24 20:45 | 8 | 106 | 848 | 8 | 0.0026322 | 2.4832e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 8 | 0.0026322 | 2.4832e-05
130716 | 2012-08-25 02:37 | 2012-08-25 02:52 | 1303 | 12 | 15636 | 1303 | 0.048535 | 0.0040445 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-25 | 2013 | 2013 | 2012-08-25 | C | 1303 | 0.048535 | 0.0040445
130718 | 2012-08-24 10:15 | 2012-08-24 12:17 | 457 | 119 | 3774.8361 | 31.7213 | 0.011717 | 0.0014185 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 31.7213 | 0.011717 | 0.0014185
130719 | 2012-08-24 13:48 | 2012-08-24 16:00 | 108 | 129 | 13932 | 108 | 0.043245 | 0.00033524 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 108 | 0.043245 | 0.00033524
130720 | 2012-08-24 13:20 | 2012-08-24 14:05 | 29 | 42 | 1218 | 29 | 0.0037807 | 9.0017e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 29 | 0.0037807 | 9.0017e-05
130721 | 2012-08-24 10:12 | 2012-08-24 15:05 | 23 | 290 | 6670 | 23 | 0.020704 | 7.1393e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | B | 23 | 0.020704 | 7.1393e-05
130722 | 2012-08-24 07:29 | 2012-08-24 09:50 | 710 | 138 | 64031.0213 | 463.9929 | 0.19875 | 0.0022039 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 463.9929 | 0.19875 | 0.0022039
130724 | 2012-08-26 05:59 | 2012-08-26 09:16 | 1615 | 194 | 85533.3198 | 440.8934 | 0.2655 | 0.005013 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-26 | 2013 | 2013 | 2012-08-26 | C | 440.8934 | 0.2655 | 0.005013
130725 | 2012-08-27 04:39 | 2012-08-27 06:05 | 82 | 83 | 6806 | 82 | 0.021126 | 0.00025453 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 82 | 0.021126 | 0.00025453
130727 | 2012-08-27 09:31 | 2012-08-27 12:39 | 38 | 185 | 7030 | 38 | 0.021821 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | B | 38 | 0.021821 | 0.00011795
130729 | 2012-08-27 11:19 | 2012-08-27 16:30 | 94 | 308 | 28952 | 94 | 0.089868 | 0.00029178 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 94 | 0.089868 | 0.00029178
130731 | 2012-08-27 14:30 | 2012-08-27 15:35 | 33 | 62 | 2046 | 33 | 0.0063508 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 33 | 0.0063508 | 0.00010243
130732 | 2012-08-27 14:50 | 2012-08-27 15:38 | 1 | 45 | 45 | 1 | 0.00013968 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 1 | 0.00013968 | 3.104e-06
130733 | 2012-08-27 16:38 | 2012-08-27 17:22 | 2 | 41 | 82 | 2 | 0.00025453 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 2 | 0.00025453 | 6.2081e-06
130734 | 2012-08-28 01:37 | 2012-08-28 03:34 | 32 | 114 | 3648 | 32 | 0.011323 | 9.9329e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 32 | 0.011323 | 9.9329e-05
130735 | 2012-08-27 22:14 | 2012-08-27 23:56 | 2 | 99 | 198 | 2 | 0.0006146 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | B | 2 | 0.0006146 | 6.2081e-06
130738 | 2012-08-24 09:32 | 2012-08-24 13:24 | 10 | 229 | 2290 | 10 | 0.0071082 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | B | 10 | 0.0071082 | 3.104e-05
130739 | 2012-08-02 09:26 | 2012-08-02 10:20 | 2 | 51 | 102 | 2 | 0.00031661 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-02 | 2013 | 2013 | 2012-08-02 | B | 2 | 0.00031661 | 6.2081e-06
130740 | 2012-08-24 17:44 | 2012-08-25 10:28 | 6 | 1001 | 6006 | 6 | 0.018643 | 1.8624e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-08-24 | 2013 | 2013 | 2012-08-24 | C | 6 | 0.018643 | 1.8624e-05
130742 | 2012-08-28 09:15 | 2012-08-28 09:21 | 5 | 3 | 15 | 5 | 4.656e-05 | 1.552e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | C | 5 | 4.656e-05 | 1.552e-05
130745 | 2012-08-28 10:12 | 2012-08-28 11:47 | 6 | 92 | 552 | 6 | 0.0017134 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 6 | 0.0017134 | 1.8624e-05
130746 | 2012-08-28 09:03 | 2012-08-28 11:55 | 33 | 169 | 5577 | 33 | 0.017311 | 0.00010243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 33 | 0.017311 | 0.00010243
130747 | 2012-08-28 09:00 | 2012-08-28 13:58 | 64 | 295 | 18880 | 64 | 0.058604 | 0.00019866 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 64 | 0.058604 | 0.00019866
130748 | 2012-08-28 09:00 | 2012-08-28 15:00 | 12 | 357 | 4284 | 12 | 0.013298 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 12 | 0.013298 | 3.7248e-05
130750 | 2012-08-28 09:00 | 2012-08-28 15:00 | 62 | 357 | 22134 | 62 | 0.068705 | 0.00019245 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 62 | 0.068705 | 0.00019245
130753 | 2012-08-27 16:34 | 2012-08-27 18:18 | 67 | 101 | 6767 | 67 | 0.021005 | 0.00020797 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-27 | 2013 | 2013 | 2012-08-27 | C | 67 | 0.021005 | 0.00020797
130754 | 2012-08-29 01:30 | 2012-08-29 03:00 | 6 | 87 | 522 | 6 | 0.0016203 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 6 | 0.0016203 | 1.8624e-05
130756 | 2012-08-28 22:03 | 2012-08-28 23:33 | 2 | 87 | 174 | 2 | 0.0005401 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-28 | 2013 | 2013 | 2012-08-28 | B | 2 | 0.0005401 | 6.2081e-06
130757 | 2012-08-29 10:50 | 2012-08-29 12:00 | 231 | 67 | 7102 | 106 | 0.022045 | 0.00071703 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | C | 106 | 0.022045 | 0.00071703
130762 | 2012-08-29 14:00 | 2012-08-29 14:08 | 111 | 5 | 555 | 111 | 0.0017227 | 0.00034455 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | C | 111 | 0.0017227 | 0.00034455
130763 | 2012-08-29 10:45 | 2012-08-29 14:15 | 5 | 207 | 1035 | 5 | 0.0032127 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 5 | 0.0032127 | 1.552e-05
130764 | 2012-08-29 09:45 | 2012-08-29 14:17 | 94 | 269 | 25286 | 94 | 0.078488 | 0.00029178 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 94 | 0.078488 | 0.00029178
130765 | 2012-08-29 09:07 | 2012-08-29 15:10 | 10 | 360 | 3600 | 10 | 0.011175 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 10 | 0.011175 | 3.104e-05
130767 | 2012-08-29 09:30 | 2012-08-29 15:50 | 2 | 377 | 754 | 2 | 0.0023404 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 2 | 0.0023404 | 6.2081e-06
130768 | 2012-08-29 12:08 | 2012-08-29 15:05 | 132 | 174 | 22968 | 132 | 0.071293 | 0.00040973 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | C | 132 | 0.071293 | 0.00040973
130771 | 2012-08-29 10:05 | 2012-08-29 12:45 | 1 | 157 | 157 | 1 | 0.00048733 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 1 | 0.00048733 | 3.104e-06
130773 | 2012-08-29 13:31 | 2012-08-29 17:19 | 185 | 225 | 15860.5263 | 70.4912 | 0.049232 | 0.00057425 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | C | 70.4912 | 0.049232 | 0.00057425
130780 | 2012-08-30 09:00 | 2012-08-30 15:42 | 12 | 399 | 4788 | 12 | 0.014862 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-30 | 2013 | 2013 | 2012-08-30 | B | 12 | 0.014862 | 3.7248e-05
130782 | 2012-08-29 23:57 | 2012-08-30 01:17 | 1 | 77 | 77 | 1 | 0.00023901 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-29 | 2013 | 2013 | 2012-08-29 | B | 1 | 0.00023901 | 3.104e-06
130785 | 2012-08-31 10:05 | 2012-08-31 10:48 | 247 | 40 | 9880 | 247 | 0.030668 | 0.0007667 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-31 | 2013 | 2013 | 2012-08-31 | C | 247 | 0.030668 | 0.0007667
130787 | 2012-09-01 02:05 | 2012-09-01 03:20 | 45 | 72 | 3240 | 45 | 0.010057 | 0.00013968 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 45 | 0.010057 | 0.00013968
130789 | 2012-09-01 05:11 | 2012-09-01 07:20 | 167 | 126 | 14380.6047 | 114.1318 | 0.044638 | 0.00051837 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 114.1318 | 0.044638 | 0.00051837
130790 | 2012-08-31 09:59 | 2012-08-31 12:29 | 3 | 147 | 441 | 3 | 0.0013689 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-31 | 2013 | 2013 | 2012-08-31 | B | 3 | 0.0013689 | 9.3121e-06
130796 | 2012-08-31 12:05 | 2012-08-31 12:35 | 933 | 27 | 22948.2 | 849.9333 | 0.071232 | 0.0028961 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-08-31 | 2013 | 2013 | 2012-08-31 | C | 849.9333 | 0.071232 | 0.0028961
130797 | 2012-09-01 18:24 | 2012-09-01 19:43 | 232 | 76 | 17632 | 232 | 0.05473 | 0.00072013 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 232 | 0.05473 | 0.00072013
130798 | 2012-09-01 21:03 | 2012-09-01 21:31 | 1 | 25 | 25 | 1 | 7.7601e-05 | 3.104e-06 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 1 | 7.7601e-05 | 3.104e-06
130800 | 2012-09-02 06:32 | 2012-09-02 06:47 | 529 | 12 | 6348 | 529 | 0.019704 | 0.001642 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-02 | 2013 | 2013 | 2012-09-02 | C | 529 | 0.019704 | 0.001642
130801 | 2012-09-02 13:52 | 2012-09-02 14:08 | 55 | 13 | 715 | 55 | 0.0022194 | 0.00017072 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-02 | 2013 | 2013 | 2012-09-02 | C | 55 | 0.0022194 | 0.00017072
130803 | 2012-09-02 03:14 | 2012-09-02 06:20 | 131 | 183 | 15375.9355 | 84.0215 | 0.047727 | 0.00040663 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-02 | 2013 | 2013 | 2012-09-02 | C | 84.0215 | 0.047727 | 0.00040663
130804 | 2012-09-01 09:53 | 2012-09-01 12:39 | 165 | 163 | 18093 | 111 | 0.056161 | 0.00051216 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 111 | 0.056161 | 0.00051216
130807 | 2012-09-02 14:51 | 2012-09-02 17:44 | 201 | 170 | 24524.2197 | 144.2601 | 0.076124 | 0.00062391 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-02 | 2013 | 2013 | 2012-09-02 | C | 144.2601 | 0.076124 | 0.00062391
130810 | 2012-08-31 10:41 | 2012-08-31 13:20 | 50 | 156 | 7800 | 50 | 0.024211 | 0.0001552 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-08-31 | 2013 | 2013 | 2012-08-31 | C | 50 | 0.024211 | 0.0001552
130811 | 2012-09-01 10:25 | 2012-09-01 10:58 | 35 | 30 | 1050 | 35 | 0.0032592 | 0.00010864 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | C | 35 | 0.0032592 | 0.00010864
130813 | 2012-09-02 22:50 | 2012-09-02 23:07 | 94 | 14 | 1316 | 94 | 0.0040849 | 0.00029178 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-02 | 2013 | 2013 | 2012-09-02 | C | 94 | 0.0040849 | 0.00029178
130814 | 2012-08-30 07:58 | 2012-08-30 22:02 | 1 | 841 | 841 | 1 | 0.0026105 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-08-30 | 2013 | 2013 | 2012-08-30 | B | 1 | 0.0026105 | 3.104e-06
130815 | 2012-09-03 09:30 | 2012-09-03 10:00 | 7 | 27 | 189 | 7 | 0.00058666 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 7 | 0.00058666 | 2.1728e-05
130816 | 2012-09-03 09:20 | 2012-09-03 10:15 | 13 | 52 | 676 | 13 | 0.0020983 | 4.0352e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 13 | 0.0020983 | 4.0352e-05
130817 | 2012-09-03 00:56 | 2012-09-03 11:10 | 1043 | 611 | 128672.2215 | 210.5928 | 0.3994 | 0.0032375 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 210.5928 | 0.3994 | 0.0032375
130821 | 2012-09-03 12:42 | 2012-09-03 13:42 | 73 | 57 | 4161 | 73 | 0.012916 | 0.00022659 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 73 | 0.012916 | 0.00022659
130825 | 2012-09-03 14:45 | 2012-09-03 15:35 | 2 | 47 | 94 | 2 | 0.00029178 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 2 | 0.00029178 | 6.2081e-06
130827 | 2012-09-03 13:37 | 2012-09-03 15:31 | 124 | 111 | 13764 | 124 | 0.042724 | 0.0003849 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | B | 124 | 0.042724 | 0.0003849
130828 | 2012-09-03 21:32 | 2012-09-03 23:27 | 1 | 112 | 112 | 1 | 0.00034765 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | B | 1 | 0.00034765 | 3.104e-06
130829 | 2012-09-03 16:06 | 2012-09-03 20:36 | 945 | 267 | 58819.1111 | 220.2963 | 0.18258 | 0.0029333 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | C | 220.2963 | 0.18258 | 0.0029333
130830 | 2012-09-03 22:30 | 2012-09-04 03:55 | 510 | 322 | 164220 | 510 | 0.50974 | 0.0015831 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-03 | 2013 | 2013 | 2012-09-03 | B | 510 | 0.50974 | 0.0015831
130833 | 2012-09-04 12:37 | 2012-09-04 13:15 | 515 | 35 | 18025 | 515 | 0.05595 | 0.0015986 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 515 | 0.05595 | 0.0015986
130834 | 2012-09-04 12:37 | 2012-09-04 13:17 | 41 | 37 | 1517 | 41 | 0.0047088 | 0.00012727 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 41 | 0.0047088 | 0.00012727
130835 | 2012-09-04 12:29 | 2012-09-04 15:48 | 616 | 196 | 27102.1709 | 138.2764 | 0.084126 | 0.0019121 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 138.2764 | 0.084126 | 0.0019121
130836 | 2012-09-04 12:04 | 2012-09-04 13:11 | 417 | 64 | 13876.5373 | 216.8209 | 0.043073 | 0.0012944 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 216.8209 | 0.043073 | 0.0012944
130837 | 2012-09-04 08:45 | 2012-09-04 14:44 | 3 | 356 | 1068 | 3 | 0.0033151 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 3 | 0.0033151 | 9.3121e-06
130838 | 2012-09-04 09:05 | 2012-09-04 14:30 | 134 | 322 | 43148 | 134 | 0.13393 | 0.00041594 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 134 | 0.13393 | 0.00041594
130839 | 2012-09-04 08:30 | 2012-09-04 14:22 | 53 | 349 | 18497 | 53 | 0.057415 | 0.00016451 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 53 | 0.057415 | 0.00016451
130840 | 2012-09-04 04:51 | 2012-09-04 06:30 | 101 | 96 | 9696 | 101 | 0.030097 | 0.00031351 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 101 | 0.030097 | 0.00031351
130842 | 2012-09-04 15:34 | 2012-09-04 16:17 | 1272 | 40 | 43164.6512 | 1079.1163 | 0.13398 | 0.0039483 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 1079.1163 | 0.13398 | 0.0039483
130845 | 2012-09-04 09:23 | 2012-09-04 16:30 | 33 | 424 | 13992 | 33 | 0.043432 | 0.00010243 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 33 | 0.043432 | 0.00010243
130846 | 2012-09-04 17:35 | 2012-09-04 18:12 | 105 | 34 | 3570 | 105 | 0.011081 | 0.00032592 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 105 | 0.011081 | 0.00032592
130847 | 2012-09-04 19:50 | 2012-09-04 20:15 | 56 | 22 | 1232 | 56 | 0.0038242 | 0.00017383 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 56 | 0.0038242 | 0.00017383
130848 | 2012-09-04 23:10 | 2012-09-05 02:10 | 1340 | 177 | 107517.6667 | 607.4444 | 0.33374 | 0.0041594 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 607.4444 | 0.33374 | 0.0041594
130849 | 2012-09-04 23:16 | 2012-09-05 02:31 | 232 | 192 | 20435.6923 | 106.4359 | 0.063433 | 0.00072013 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 106.4359 | 0.063433 | 0.00072013
130850 | 2012-09-04 15:36 | 2012-09-05 12:30 | 781 | 1251 | 65362.256 | 52.248 | 0.20289 | 0.0024242 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | C | 52.248 | 0.20289 | 0.0024242
130851 | 2012-09-05 07:10 | 2012-09-05 07:25 | 7 | 12 | 84 | 7 | 0.00026074 | 2.1728e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 7 | 0.00026074 | 2.1728e-05
130853 | 2012-09-05 07:42 | 2012-09-05 15:50 | 253 | 485 | 13370.2971 | 27.5676 | 0.041502 | 0.00078532 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 27.5676 | 0.041502 | 0.00078532
130854 | 2012-09-05 09:10 | 2012-09-05 12:36 | 77 | 203 | 15631 | 77 | 0.048519 | 0.00023901 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 77 | 0.048519 | 0.00023901
130855 | 2012-09-05 09:29 | 2012-09-05 12:31 | 49 | 179 | 8771 | 49 | 0.027225 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 49 | 0.027225 | 0.0001521
130856 | 2012-09-05 12:57 | 2012-09-05 13:12 | 178 | 12 | 2136 | 178 | 0.0066302 | 0.00055252 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 178 | 0.0066302 | 0.00055252
130857 | 2012-09-05 12:25 | 2012-09-05 13:45 | 3 | 77 | 231 | 3 | 0.00071703 | 9.3121e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 3 | 0.00071703 | 9.3121e-06
130858 | 2012-09-05 09:30 | 2012-09-05 12:50 | 36 | 197 | 7092 | 36 | 0.022014 | 0.00011175 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 36 | 0.022014 | 0.00011175
130859 | 2012-09-05 11:05 | 2012-09-05 12:20 | 5 | 72 | 360 | 5 | 0.0011175 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 5 | 0.0011175 | 1.552e-05
130861 | 2012-09-05 09:22 | 2012-09-05 14:00 | 17 | 275 | 4675 | 17 | 0.014511 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 17 | 0.014511 | 5.2768e-05
130863 | 2012-09-05 09:00 | 2012-09-05 14:19 | 8 | 316 | 2528 | 8 | 0.007847 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 8 | 0.007847 | 2.4832e-05
130865 | 2012-09-05 09:10 | 2012-09-05 14:55 | 102 | 342 | 34884 | 102 | 0.10828 | 0.00031661 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 102 | 0.10828 | 0.00031661
130866 | 2012-09-05 12:36 | 2012-09-05 14:14 | 256 | 95 | 13757.551 | 144.8163 | 0.042704 | 0.00079463 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 144.8163 | 0.042704 | 0.00079463
130867 | 2012-09-05 14:32 | 2012-09-05 15:29 | 25 | 54 | 1350 | 25 | 0.0041904 | 7.7601e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 25 | 0.0041904 | 7.7601e-05
130869 | 2012-09-04 15:40 | 2012-09-04 16:44 | 32 | 61 | 1952 | 32 | 0.0060591 | 9.9329e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-04 | 2013 | 2013 | 2012-09-04 | B | 32 | 0.0060591 | 9.9329e-05
130871 | 2012-09-05 09:15 | 2012-09-05 14:25 | 32 | 307 | 9824 | 32 | 0.030494 | 9.9329e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 32 | 0.030494 | 9.9329e-05
130872 | 2012-09-05 09:30 | 2012-09-05 15:00 | 82 | 327 | 26814 | 82 | 0.083231 | 0.00025453 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 82 | 0.083231 | 0.00025453
130877 | 2012-09-05 09:31 | 2012-09-05 13:38 | 55 | 244 | 13420 | 55 | 0.041656 | 0.00017072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 55 | 0.041656 | 0.00017072
130879 | 2012-09-05 15:11 | 2012-09-05 17:24 | 229 | 130 | 25633.4586 | 197.1805 | 0.079567 | 0.00071082 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | C | 197.1805 | 0.079567 | 0.00071082
130880 | 2012-09-06 06:48 | 2012-09-06 08:44 | 787 | 113 | 50313.25 | 445.25 | 0.15617 | 0.0024429 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 445.25 | 0.15617 | 0.0024429
130882 | 2012-09-06 08:45 | 2012-09-06 10:30 | 9 | 102 | 918 | 9 | 0.0028495 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 9 | 0.0028495 | 2.7936e-05
130885 | 2012-09-06 09:00 | 2012-09-06 10:00 | 1 | 57 | 57 | 1 | 0.00017693 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 1 | 0.00017693 | 3.104e-06
130890 | 2012-09-06 14:41 | 2012-09-06 15:55 | 342 | 71 | 16726.2568 | 235.5811 | 0.051919 | 0.0010616 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 235.5811 | 0.051919 | 0.0010616
130891 | 2012-09-06 10:37 | 2012-09-06 12:52 | 228 | 132 | 27200.8 | 206.0667 | 0.084432 | 0.00070772 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 206.0667 | 0.084432 | 0.00070772
130892 | 2012-09-06 09:36 | 2012-09-06 14:29 | 6 | 290 | 1740 | 6 | 0.005401 | 1.8624e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 6 | 0.005401 | 1.8624e-05
130893 | 2012-09-06 08:30 | 2012-09-06 11:39 | 53 | 186 | 9858 | 53 | 0.0306 | 0.00016451 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 53 | 0.0306 | 0.00016451
130894 | 2012-09-06 08:30 | 2012-09-06 12:38 | 16 | 245 | 3920 | 16 | 0.012168 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 16 | 0.012168 | 4.9664e-05
130895 | 2012-09-06 12:54 | 2012-09-06 14:55 | 1 | 118 | 118 | 1 | 0.00036628 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 1 | 0.00036628 | 3.104e-06
130896 | 2012-09-06 07:00 | 2012-09-06 10:11 | 259 | 188 | 34407.9372 | 183.0209 | 0.1068 | 0.00080394 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 183.0209 | 0.1068 | 0.00080394
130897 | 2012-09-06 14:57 | 2012-09-06 15:12 | 133 | 12 | 1596 | 133 | 0.004954 | 0.00041284 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 133 | 0.004954 | 0.00041284
130898 | 2012-09-06 18:08 | 2012-09-06 18:45 | 16 | 34 | 544 | 16 | 0.0016886 | 4.9664e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 16 | 0.0016886 | 4.9664e-05
130899 | 2012-09-06 16:09 | 2012-09-06 19:49 | 178 | 217 | 26723.55 | 123.15 | 0.082951 | 0.00055252 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 123.15 | 0.082951 | 0.00055252
130904 | 2012-09-07 04:08 | 2012-09-07 06:15 | 396 | 124 | 43104.1575 | 347.6142 | 0.1338 | 0.0012292 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 347.6142 | 0.1338 | 0.0012292
130905 | 2012-09-06 08:15 | 2012-09-06 12:13 | 38 | 235 | 8930 | 38 | 0.027719 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | B | 38 | 0.027719 | 0.00011795
130906 | 2012-09-07 09:55 | 2012-09-07 10:37 | 17 | 39 | 663 | 17 | 0.002058 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 17 | 0.002058 | 5.2768e-05
130907 | 2012-09-07 10:30 | 2012-09-07 11:30 | 128 | 57 | 7296 | 128 | 0.022647 | 0.00039732 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 128 | 0.022647 | 0.00039732
130908 | 2012-09-05 22:07 | 2012-09-05 23:33 | 1 | 83 | 83 | 1 | 0.00025763 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-05 | 2013 | 2013 | 2012-09-05 | B | 1 | 0.00025763 | 3.104e-06
130909 | 2012-09-01 09:03 | 2012-09-01 11:18 | 47 | 132 | 6204 | 47 | 0.019257 | 0.00014589 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-01 | 2013 | 2013 | 2012-09-01 | B | 47 | 0.019257 | 0.00014589
130910 | 2012-09-07 08:00 | 2012-09-07 11:58 | 130 | 235 | 20478.5714 | 87.1429 | 0.063566 | 0.00040352 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 87.1429 | 0.063566 | 0.00040352
130911 | 2012-09-07 10:12 | 2012-09-07 11:21 | 15 | 66 | 990 | 15 | 0.003073 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 15 | 0.003073 | 4.656e-05
130912 | 2012-09-07 09:15 | 2012-09-07 09:33 | 1 | 15 | 15 | 1 | 4.656e-05 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 1 | 4.656e-05 | 3.104e-06
130913 | 2012-09-07 09:00 | 2012-09-07 12:30 | 3 | 207 | 621 | 3 | 0.0019276 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 3 | 0.0019276 | 9.3121e-06
130916 | 2012-09-07 09:40 | 2012-09-07 13:20 | 26 | 217 | 5642 | 26 | 0.017513 | 8.0705e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 26 | 0.017513 | 8.0705e-05
130918 | 2012-09-07 09:19 | 2012-09-07 15:29 | 61 | 367 | 22387 | 61 | 0.06949 | 0.00018935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | B | 61 | 0.06949 | 0.00018935
130919 | 2012-09-07 14:45 | 2012-09-07 16:12 | 224 | 84 | 13375.3103 | 159.2299 | 0.041517 | 0.0006953 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 159.2299 | 0.041517 | 0.0006953
130920 | 2012-09-07 12:51 | 2012-09-07 14:50 | 307 | 116 | 35612 | 307 | 0.11054 | 0.00095294 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 307 | 0.11054 | 0.00095294
130921 | 2012-09-07 16:30 | 2012-09-07 17:06 | 11 | 33 | 363 | 11 | 0.0011268 | 3.4144e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 11 | 0.0011268 | 3.4144e-05
130922 | 2012-09-07 16:28 | 2012-09-07 17:47 | 76 | 76 | 5637.4684 | 74.1772 | 0.017499 | 0.00023591 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 74.1772 | 0.017499 | 0.00023591
130923 | 2012-09-07 11:27 | 2012-09-07 12:21 | 139 | 51 | 7089 | 139 | 0.022004 | 0.00043146 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 139 | 0.022004 | 0.00043146
130924 | 2012-09-07 12:43 | 2012-09-07 15:35 | 322 | 169 | 20724.1163 | 122.6279 | 0.064328 | 0.0009995 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 122.6279 | 0.064328 | 0.0009995
130925 | 2012-09-07 18:30 | 2012-09-07 18:40 | 66 | 7 | 462 | 66 | 0.0014341 | 0.00020487 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 66 | 0.0014341 | 0.00020487
130926 | 2012-09-07 13:07 | 2012-09-07 15:30 | 133 | 140 | 3101.5385 | 22.1538 | 0.0096273 | 0.00041284 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 22.1538 | 0.0096273 | 0.00041284
130927 | 2012-09-07 20:10 | 2012-09-07 20:25 | 367 | 12 | 4404 | 367 | 0.01367 | 0.0011392 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 367 | 0.01367 | 0.0011392
130928 | 2012-09-07 21:42 | 2012-09-07 22:46 | 284 | 61 | 13589.6562 | 222.7812 | 0.042183 | 0.00088154 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 222.7812 | 0.042183 | 0.00088154
130929 | 2012-09-08 05:31 | 2012-09-08 07:55 | 274 | 141 | 16499.9375 | 117.0208 | 0.051216 | 0.0008505 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 117.0208 | 0.051216 | 0.0008505
130931 | 2012-09-08 09:32 | 2012-09-08 12:18 | 49 | 163 | 7987 | 49 | 0.024792 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | B | 49 | 0.024792 | 0.0001521
130934 | 2012-09-08 20:16 | 2012-09-08 20:31 | 215 | 12 | 2580 | 215 | 0.0080084 | 0.00066737 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 215 | 0.0080084 | 0.00066737
130935 | 2012-09-08 21:52 | 2012-09-08 22:07 | 472 | 12 | 5664 | 472 | 0.017581 | 0.0014651 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 472 | 0.017581 | 0.0014651
130936 | 2012-09-09 07:26 | 2012-09-09 08:13 | 199 | 44 | 8756 | 199 | 0.027179 | 0.0006177 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 199 | 0.027179 | 0.0006177
130937 | 2012-09-09 07:26 | 2012-09-09 08:15 | 203 | 46 | 7291.4694 | 158.5102 | 0.022633 | 0.00063012 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 158.5102 | 0.022633 | 0.00063012
130938 | 2012-09-09 06:44 | 2012-09-09 08:01 | 186 | 74 | 11527.6623 | 155.7792 | 0.035782 | 0.00057735 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 155.7792 | 0.035782 | 0.00057735
130939 | 2012-09-09 09:06 | 2012-09-09 10:12 | 7 | 63 | 441 | 7 | 0.0013689 | 2.1728e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 7 | 0.0013689 | 2.1728e-05
130940 | 2012-09-09 09:25 | 2012-09-09 10:06 | 18 | 38 | 684 | 18 | 0.0021232 | 5.5873e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 18 | 0.0021232 | 5.5873e-05
130941 | 2012-09-09 09:23 | 2012-09-09 10:21 | 3 | 55 | 165 | 3 | 0.00051216 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 3 | 0.00051216 | 9.3121e-06
130942 | 2012-09-09 10:23 | 2012-09-09 11:29 | 27 | 63 | 1701 | 27 | 0.00528 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 27 | 0.00528 | 8.3809e-05
130943 | 2012-09-09 12:23 | 2012-09-09 12:33 | 56 | 7 | 392 | 56 | 0.0012168 | 0.00017383 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 56 | 0.0012168 | 0.00017383
130944 | 2012-09-09 10:39 | 2012-09-09 14:10 | 203 | 208 | 25891.564 | 124.4787 | 0.080368 | 0.00063012 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 124.4787 | 0.080368 | 0.00063012
130945 | 2012-09-09 11:17 | 2012-09-09 14:04 | 968 | 164 | 52933.7006 | 322.7665 | 0.16431 | 0.0030047 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 322.7665 | 0.16431 | 0.0030047
130946 | 2012-09-09 10:32 | 2012-09-09 14:03 | 1 | 208 | 208 | 1 | 0.00064564 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 1 | 0.00064564 | 3.104e-06
130947 | 2012-09-09 13:32 | 2012-09-09 14:00 | 12 | 25 | 300 | 12 | 0.00093121 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 12 | 0.00093121 | 3.7248e-05
130949 | 2012-09-08 17:01 | 2012-09-08 19:45 | 49 | 161 | 7889 | 49 | 0.024488 | 0.0001521 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 49 | 0.024488 | 0.0001521
130950 | 2012-09-09 17:12 | 2012-09-09 18:03 | 345 | 48 | 7946.3529 | 165.549 | 0.024666 | 0.0010709 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 165.549 | 0.024666 | 0.0010709
130952 | 2012-09-09 11:50 | 2012-09-09 12:39 | 546 | 46 | 25116 | 546 | 0.077961 | 0.0016948 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 546 | 0.077961 | 0.0016948
130953 | 2012-09-08 09:50 | 2012-09-08 10:56 | 19 | 63 | 1197 | 19 | 0.0037155 | 5.8977e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 19 | 0.0037155 | 5.8977e-05
130954 | 2012-09-09 19:12 | 2012-09-09 22:11 | 339 | 176 | 59664 | 339 | 0.1852 | 0.0010523 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 339 | 0.1852 | 0.0010523
130955 | 2012-09-09 21:23 | 2012-09-09 22:13 | 110 | 47 | 5170 | 110 | 0.016048 | 0.00034144 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 110 | 0.016048 | 0.00034144
130956 | 2012-09-08 11:42 | 2012-09-08 13:09 | 10 | 84 | 840 | 10 | 0.0026074 | 3.104e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 10 | 0.0026074 | 3.104e-05
130957 | 2012-09-08 14:07 | 2012-09-09 18:01 | 21 | 1671 | 35091 | 21 | 0.10892 | 6.5185e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 21 | 0.10892 | 6.5185e-05
130958 | 2012-09-08 15:00 | 2012-09-08 17:31 | 190 | 148 | 22976.2649 | 155.245 | 0.071319 | 0.00058977 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 155.245 | 0.071319 | 0.00058977
130960 | 2012-09-06 17:37 | 2012-09-08 14:05 | 21 | 2665 | 53367.9235 | 20.0255 | 0.16566 | 6.5185e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-06 | 2013 | 2013 | 2012-09-06 | C | 20.0255 | 0.16566 | 6.5185e-05
130962 | 2012-09-08 13:15 | 2012-09-08 18:02 | 268 | 284 | 43791.4146 | 154.1951 | 0.13593 | 0.00083188 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 154.1951 | 0.13593 | 0.00083188
130964 | 2012-09-08 17:53 | 2012-09-08 18:40 | 31 | 44 | 1364 | 31 | 0.0042339 | 9.6225e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 31 | 0.0042339 | 9.6225e-05
130965 | 2012-09-08 12:20 | 2012-09-08 15:07 | 781 | 164 | 61864.3353 | 377.2216 | 0.19203 | 0.0024242 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 377.2216 | 0.19203 | 0.0024242
130966 | 2012-09-08 12:42 | 2012-09-08 17:09 | 163 | 264 | 26576.9888 | 100.6704 | 0.082496 | 0.00050596 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 100.6704 | 0.082496 | 0.00050596
130967 | 2012-09-08 11:30 | 2012-09-08 13:24 | 23 | 111 | 2553 | 23 | 0.0079246 | 7.1393e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 23 | 0.0079246 | 7.1393e-05
130968 | 2012-09-08 11:29 | 2012-09-08 17:01 | 417 | 329 | 129285.1084 | 392.9639 | 0.4013 | 0.0012944 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 392.9639 | 0.4013 | 0.0012944
130969 | 2012-09-08 17:40 | 2012-09-08 17:50 | 235 | 7 | 1645 | 235 | 0.0051061 | 0.00072945 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 235 | 0.0051061 | 0.00072945
130970 | 2012-09-08 16:24 | 2012-09-08 16:36 | 311 | 9 | 2799 | 311 | 0.0086882 | 0.00096535 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 311 | 0.0086882 | 0.00096535
130971 | 2012-09-08 21:37 | 2012-09-08 21:58 | 43 | 18 | 774 | 43 | 0.0024025 | 0.00013347 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 43 | 0.0024025 | 0.00013347
130972 | 2012-09-09 00:13 | 2012-09-09 00:34 | 43 | 18 | 774 | 43 | 0.0024025 | 0.00013347 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 43 | 0.0024025 | 0.00013347
130973 | 2012-09-08 21:51 | 2012-09-08 22:12 | 677 | 18 | 12186 | 677 | 0.037826 | 0.0021014 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 677 | 0.037826 | 0.0021014
130976 | 2012-09-08 13:50 | 2012-09-08 16:50 | 77 | 177 | 7139 | 40.3333 | 0.02216 | 0.00023901 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 40.3333 | 0.02216 | 0.00023901
130979 | 2012-09-09 00:22 | 2012-09-09 06:29 | 215 | 364 | 27422.9864 | 75.3379 | 0.085122 | 0.00066737 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 75.3379 | 0.085122 | 0.00066737
130980 | 2012-09-09 22:14 | 2012-09-10 00:19 | 177 | 122 | 19813.776 | 162.408 | 0.061503 | 0.00054941 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 162.408 | 0.061503 | 0.00054941
130981 | 2012-09-09 22:55 | 2012-09-10 09:48 | 563 | 650 | 83215.9265 | 128.0245 | 0.2583 | 0.0017476 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 128.0245 | 0.2583 | 0.0017476
130982 | 2012-09-07 23:30 | 2012-09-08 01:24 | 43 | 111 | 4773 | 43 | 0.014816 | 0.00013347 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-07 | 2013 | 2013 | 2012-09-07 | C | 43 | 0.014816 | 0.00013347
130983 | 2012-09-08 14:15 | 2012-09-08 16:19 | 43 | 121 | 5203 | 43 | 0.01615 | 0.00013347 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 43 | 0.01615 | 0.00013347
130984 | 2012-09-08 11:02 | 2012-09-08 19:48 | 44 | 523 | 23012 | 44 | 0.07143 | 0.00013658 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 44 | 0.07143 | 0.00013658
130985 | 2012-09-08 17:40 | 2012-09-08 21:09 | 127 | 206 | 10729.7416 | 52.0861 | 0.033305 | 0.00039421 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 52.0861 | 0.033305 | 0.00039421
130986 | 2012-09-08 23:45 | 2012-09-09 12:27 | 109 | 759 | 82731 | 109 | 0.2568 | 0.00033834 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 109 | 0.2568 | 0.00033834
130987 | 2012-09-09 11:30 | 2012-09-09 13:16 | 2 | 103 | 206 | 2 | 0.00063943 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 2 | 0.00063943 | 6.2081e-06
130988 | 2012-09-10 09:16 | 2012-09-10 10:14 | 55 | 55 | 3025 | 55 | 0.0093897 | 0.00017072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | B | 55 | 0.0093897 | 0.00017072
130989 | 2012-09-10 10:00 | 2012-09-10 11:12 | 7 | 69 | 483 | 7 | 0.0014992 | 2.1728e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 7 | 0.0014992 | 2.1728e-05
130990 | 2012-09-10 09:54 | 2012-09-10 11:01 | 46 | 64 | 2944 | 46 | 0.0091383 | 0.00014279 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 46 | 0.0091383 | 0.00014279
130992 | 2012-09-08 12:38 | 2012-09-08 15:41 | 228 | 180 | 18927.541 | 105.153 | 0.058752 | 0.00070772 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-08 | 2013 | 2013 | 2012-09-08 | C | 105.153 | 0.058752 | 0.00070772
130993 | 2012-09-10 09:30 | 2012-09-10 10:00 | 3 | 27 | 81 | 3 | 0.00025143 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 3 | 0.00025143 | 9.3121e-06
130995 | 2012-09-10 08:42 | 2012-09-10 09:40 | 3 | 55 | 165 | 3 | 0.00051216 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 3 | 0.00051216 | 9.3121e-06
130998 | 2012-09-10 07:01 | 2012-09-10 12:25 | 238 | 321 | 63504.5 | 197.8333 | 0.19712 | 0.00073876 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 197.8333 | 0.19712 | 0.00073876
130999 | 2012-09-09 20:27 | 2012-09-10 13:05 | 2 | 995 | 1990 | 2 | 0.006177 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 2 | 0.006177 | 6.2081e-06
131001 | 2012-09-10 13:03 | 2012-09-10 14:21 | 43 | 75 | 3225 | 43 | 0.01001 | 0.00013347 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 43 | 0.01001 | 0.00013347
131002 | 2012-09-09 11:00 | 2012-09-09 14:00 | 11 | 177 | 1947 | 11 | 0.0060435 | 3.4144e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-09 | 2013 | 2013 | 2012-09-09 | C | 11 | 0.0060435 | 3.4144e-05
131003 | 2012-09-10 08:45 | 2012-09-10 10:25 | 2 | 97 | 194 | 2 | 0.00060218 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 2 | 0.00060218 | 6.2081e-06
131006 | 2012-09-10 21:32 | 2012-09-10 23:40 | 410 | 125 | 50908.2031 | 407.2656 | 0.15802 | 0.0012727 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 407.2656 | 0.15802 | 0.0012727
131009 | 2012-09-11 09:52 | 2012-09-11 10:11 | 99 | 16 | 1584 | 99 | 0.0049168 | 0.0003073 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 99 | 0.0049168 | 0.0003073
131012 | 2012-09-10 17:00 | 2012-09-11 10:08 | 1 | 1025 | 1025 | 1 | 0.0031816 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 1 | 0.0031816 | 3.104e-06
131015 | 2012-09-10 21:12 | 2012-09-10 22:28 | 3 | 73 | 219 | 3 | 0.00067978 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 3 | 0.00067978 | 9.3121e-06
131016 | 2012-09-10 18:42 | 2012-09-10 21:20 | 213 | 155 | 26664.9051 | 172.0316 | 0.082769 | 0.00066116 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 172.0316 | 0.082769 | 0.00066116
131018 | 2012-09-10 20:36 | 2012-09-11 01:51 | 180 | 312 | 56160 | 180 | 0.17432 | 0.00055873 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-10 | 2013 | 2013 | 2012-09-10 | C | 180 | 0.17432 | 0.00055873
131019 | 2012-09-11 04:30 | 2012-09-11 11:30 | 77 | 417 | 12410.7143 | 29.7619 | 0.038523 | 0.00023901 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 29.7619 | 0.038523 | 0.00023901
131021 | 2012-09-11 09:00 | 2012-09-11 12:52 | 15 | 229 | 3435 | 15 | 0.010662 | 4.656e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | B | 15 | 0.010662 | 4.656e-05
131024 | 2012-09-11 11:49 | 2012-09-11 15:03 | 132 | 191 | 8710.1907 | 45.6031 | 0.027037 | 0.00040973 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 45.6031 | 0.027037 | 0.00040973
131026 | 2012-09-11 12:10 | 2012-09-11 16:10 | 129 | 237 | 30573 | 129 | 0.094899 | 0.00040042 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | B | 129 | 0.094899 | 0.00040042
131028 | 2012-09-11 09:00 | 2012-09-11 16:15 | 17 | 432 | 7344 | 17 | 0.022796 | 5.2768e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | B | 17 | 0.022796 | 5.2768e-05
131029 | 2012-09-11 14:45 | 2012-09-11 15:38 | 14 | 50 | 700 | 14 | 0.0021728 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 14 | 0.0021728 | 4.3456e-05
131030 | 2012-09-11 13:50 | 2012-09-11 15:45 | 19 | 112 | 2128 | 19 | 0.0066054 | 5.8977e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 19 | 0.0066054 | 5.8977e-05
131031 | 2012-09-11 09:42 | 2012-09-11 14:32 | 407 | 287 | 116809 | 407 | 0.36258 | 0.0012633 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | B | 407 | 0.36258 | 0.0012633
131033 | 2012-09-11 09:29 | 2012-09-11 09:46 | 934 | 14 | 13076 | 934 | 0.040588 | 0.0028992 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 934 | 0.040588 | 0.0028992
131034 | 2012-09-11 10:41 | 2012-09-11 17:19 | 118 | 395 | 8380.3518 | 21.2161 | 0.026013 | 0.00036628 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 21.2161 | 0.026013 | 0.00036628
131035 | 2012-09-11 06:02 | 2012-09-11 15:15 | 918 | 550 | 170690.9584 | 310.3472 | 0.52983 | 0.0028495 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 310.3472 | 0.52983 | 0.0028495
131036 | 2012-09-11 18:54 | 2012-09-11 20:20 | 998 | 83 | 54804.1279 | 660.2907 | 0.17011 | 0.0030978 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 660.2907 | 0.17011 | 0.0030978
131037 | 2012-09-11 18:56 | 2012-09-11 21:22 | 676 | 143 | 70951.5068 | 496.1644 | 0.22024 | 0.0020983 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 496.1644 | 0.22024 | 0.0020983
131038 | 2012-09-11 22:00 | 2012-09-11 23:20 | 5 | 77 | 385 | 5 | 0.0011951 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 5 | 0.0011951 | 1.552e-05
131039 | 2012-09-12 00:05 | 2012-09-12 03:03 | 1 | 175 | 175 | 1 | 0.0005432 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | B | 1 | 0.0005432 | 3.104e-06
131040 | 2012-09-12 00:24 | 2012-09-12 06:46 | 88 | 379 | 22984.0681 | 60.644 | 0.071343 | 0.00027315 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 60.644 | 0.071343 | 0.00027315
131041 | 2012-09-12 09:13 | 2012-09-12 10:04 | 42 | 48 | 2016 | 42 | 0.0062577 | 0.00013037 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 42 | 0.0062577 | 0.00013037
131042 | 2012-09-12 08:31 | 2012-09-12 10:24 | 77 | 110 | 5496.1062 | 49.9646 | 0.01706 | 0.00023901 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 49.9646 | 0.01706 | 0.00023901
131045 | 2012-09-12 10:09 | 2012-09-12 13:36 | 20 | 204 | 4080 | 20 | 0.012664 | 6.2081e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 20 | 0.012664 | 6.2081e-05
131047 | 2012-09-12 09:00 | 2012-09-12 14:50 | 106 | 347 | 36782 | 106 | 0.11417 | 0.00032903 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | B | 106 | 0.11417 | 0.00032903
131048 | 2012-09-12 10:30 | 2012-09-12 12:54 | 27 | 141 | 2449.875 | 17.375 | 0.0076045 | 8.3809e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 17.375 | 0.0076045 | 8.3809e-05
131049 | 2012-09-12 12:45 | 2012-09-12 14:00 | 2 | 72 | 144 | 2 | 0.00044698 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 2 | 0.00044698 | 6.2081e-06
131050 | 2012-09-12 10:45 | 2012-09-12 11:45 | 3 | 57 | 171 | 3 | 0.00053079 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 3 | 0.00053079 | 9.3121e-06
131051 | 2012-09-12 11:01 | 2012-09-12 15:30 | 7 | 266 | 1862 | 7 | 0.0057797 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | B | 7 | 0.0057797 | 2.1728e-05
131052 | 2012-09-12 13:10 | 2012-09-12 14:50 | 12 | 97 | 1164 | 12 | 0.0036131 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 12 | 0.0036131 | 3.7248e-05
131053 | 2012-09-12 16:03 | 2012-09-12 17:19 | 77 | 73 | 2636.6447 | 36.1184 | 0.0081842 | 0.00023901 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 36.1184 | 0.0081842 | 0.00023901
131054 | 2012-09-12 08:30 | 2012-09-12 14:00 | 25 | 327 | 8175 | 25 | 0.025375 | 7.7601e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | B | 25 | 0.025375 | 7.7601e-05
131056 | 2012-09-12 21:46 | 2012-09-13 01:15 | 377 | 206 | 33854.9665 | 164.3445 | 0.10509 | 0.0011702 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 164.3445 | 0.10509 | 0.0011702
131058 | 2012-09-12 14:13 | 2012-09-12 14:19 | 918 | 3 | 2754 | 918 | 0.0085485 | 0.0028495 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 918 | 0.0085485 | 0.0028495
131059 | 2012-09-12 14:43 | 2012-09-12 16:53 | 109 | 127 | 6139.9615 | 48.3462 | 0.019059 | 0.00033834 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-12 | 2013 | 2013 | 2012-09-12 | C | 48.3462 | 0.019059 | 0.00033834
131060 | 2012-09-13 07:52 | 2012-09-13 09:23 | 171 | 88 | 15048 | 171 | 0.046709 | 0.00053079 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 171 | 0.046709 | 0.00053079
131061 | 2012-09-13 10:30 | 2012-09-13 12:15 | 3 | 102 | 306 | 3 | 0.00094983 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 3 | 0.00094983 | 9.3121e-06
131062 | 2012-09-13 09:15 | 2012-09-13 10:31 | 172 | 73 | 12556 | 172 | 0.038974 | 0.00053389 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 172 | 0.038974 | 0.00053389
131063 | 2012-09-13 08:40 | 2012-09-13 12:20 | 16 | 217 | 3472 | 16 | 0.010777 | 4.9664e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | B | 16 | 0.010777 | 4.9664e-05
131065 | 2012-09-13 09:19 | 2012-09-13 12:59 | 8 | 217 | 1736 | 8 | 0.0053886 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | B | 8 | 0.0053886 | 2.4832e-05
131066 | 2012-09-13 09:37 | 2012-09-13 14:00 | 171 | 260 | 44460 | 171 | 0.13801 | 0.00053079 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | B | 171 | 0.13801 | 0.00053079
131067 | 2012-09-13 13:24 | 2012-09-13 14:10 | 90 | 43 | 3870 | 90 | 0.012013 | 0.00027936 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 90 | 0.012013 | 0.00027936
131068 | 2012-09-13 13:49 | 2012-09-13 15:49 | 410 | 117 | 47970 | 410 | 0.1489 | 0.0012727 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 410 | 0.1489 | 0.0012727
131069 | 2012-09-13 15:52 | 2012-09-13 16:23 | 14 | 28 | 392 | 14 | 0.0012168 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 14 | 0.0012168 | 4.3456e-05
131073 | 2012-09-13 08:15 | 2012-09-13 11:15 | 3 | 177 | 531 | 3 | 0.0016482 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 3 | 0.0016482 | 9.3121e-06
131075 | 2012-09-13 23:43 | 2012-09-14 00:45 | 318 | 59 | 18762 | 318 | 0.058238 | 0.00098708 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-13 | 2013 | 2013 | 2012-09-13 | C | 318 | 0.058238 | 0.00098708
131077 | 2012-09-14 05:47 | 2012-09-14 06:33 | 701 | 43 | 22604.913 | 525.6957 | 0.070166 | 0.0021759 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-14 | 2013 | 2013 | 2012-09-14 | C | 525.6957 | 0.070166 | 0.0021759
131081 | 2012-09-14 14:13 | 2012-09-14 15:40 | 53 | 84 | 4452 | 53 | 0.013819 | 0.00016451 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-14 | 2013 | 2013 | 2012-09-14 | C | 53 | 0.013819 | 0.00016451
131086 | 2012-09-14 08:03 | 2012-09-14 08:50 | 91 | 44 | 4004 | 91 | 0.012429 | 0.00028247 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-14 | 2013 | 2013 | 2012-09-14 | B | 91 | 0.012429 | 0.00028247
131087 | 2012-09-14 10:30 | 2012-09-14 13:08 | 23 | 155 | 3565 | 23 | 0.011066 | 7.1393e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-14 | 2013 | 2013 | 2012-09-14 | B | 23 | 0.011066 | 7.1393e-05
131088 | 2012-09-14 18:19 | 2012-09-14 21:08 | 1240 | 166 | 103678.2959 | 624.568 | 0.32182 | 0.003849 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-14 | 2013 | 2013 | 2012-09-14 | C | 624.568 | 0.32182 | 0.003849
131089 | 2012-09-16 09:57 | 2012-09-16 11:25 | 26 | 85 | 2210 | 26 | 0.0068599 | 8.0705e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 26 | 0.0068599 | 8.0705e-05
131090 | 2012-09-16 10:43 | 2012-09-16 11:07 | 5 | 21 | 105 | 5 | 0.00032592 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 5 | 0.00032592 | 1.552e-05
131091 | 2012-09-16 09:05 | 2012-09-16 11:05 | 12 | 117 | 1404 | 12 | 0.0043581 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | B | 12 | 0.0043581 | 3.7248e-05
131092 | 2012-09-16 20:28 | 2012-09-16 23:58 | 186 | 207 | 22203.2143 | 107.2619 | 0.068919 | 0.00057735 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 107.2619 | 0.068919 | 0.00057735
131093 | 2012-09-16 19:51 | 2012-09-16 21:09 | 819 | 75 | 36190.3846 | 482.5385 | 0.11234 | 0.0025422 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 482.5385 | 0.11234 | 0.0025422
131094 | 2012-09-17 01:04 | 2012-09-17 01:52 | 237 | 45 | 10665 | 237 | 0.033104 | 0.00073565 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 237 | 0.033104 | 0.00073565
131096 | 2012-09-16 11:55 | 2012-09-16 12:23 | 58 | 25 | 1450 | 58 | 0.0045008 | 0.00018003 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 58 | 0.0045008 | 0.00018003
131097 | 2012-09-11 07:50 | 2012-09-11 08:32 | 191 | 39 | 7449 | 191 | 0.023122 | 0.00059287 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | C | 191 | 0.023122 | 0.00059287
131099 | 2012-09-15 16:29 | 2012-09-15 19:18 | 31 | 166 | 5146 | 31 | 0.015973 | 9.6225e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-15 | 2013 | 2013 | 2012-09-15 | C | 31 | 0.015973 | 9.6225e-05
131100 | 2012-09-16 13:44 | 2012-09-16 14:08 | 123 | 21 | 2583 | 123 | 0.0080177 | 0.0003818 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | C | 123 | 0.0080177 | 0.0003818
131101 | 2012-09-17 10:50 | 2012-09-17 11:58 | 15 | 65 | 975 | 15 | 0.0030264 | 4.656e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 15 | 0.0030264 | 4.656e-05
131102 | 2012-09-17 08:45 | 2012-09-17 14:09 | 226 | 321 | 72546 | 226 | 0.22518 | 0.00070151 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | B | 226 | 0.22518 | 0.00070151
131103 | 2012-09-17 13:44 | 2012-09-17 14:44 | 82 | 57 | 4674 | 82 | 0.014508 | 0.00025453 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 82 | 0.014508 | 0.00025453
131104 | 2012-09-17 15:48 | 2012-09-17 16:31 | 226 | 40 | 9040 | 226 | 0.02806 | 0.00070151 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 226 | 0.02806 | 0.00070151
131106 | 2012-09-17 12:38 | 2012-09-17 18:00 | 238 | 319 | 21968.4006 | 68.8665 | 0.068191 | 0.00073876 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 68.8665 | 0.068191 | 0.00073876
131107 | 2012-09-17 22:18 | 2012-09-18 13:48 | 5 | 927 | 4635 | 5 | 0.014387 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 5 | 0.014387 | 1.552e-05
131108 | 2012-09-17 23:33 | 2012-09-18 02:00 | 131 | 144 | 9695.0204 | 67.3265 | 0.030094 | 0.00040663 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 67.3265 | 0.030094 | 0.00040663
131109 | 2012-09-11 09:20 | 2012-09-11 09:29 | 8 | 6 | 48 | 8 | 0.00014899 | 2.4832e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-11 | 2013 | 2013 | 2012-09-11 | B | 8 | 0.00014899 | 2.4832e-05
131110 | 2012-09-17 21:33 | 2012-09-18 11:02 | 77 | 806 | 12301.2138 | 15.2621 | 0.038183 | 0.00023901 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-17 | 2013 | 2013 | 2012-09-17 | C | 15.2621 | 0.038183 | 0.00023901
131111 | 2012-09-18 08:45 | 2012-09-18 13:30 | 20 | 282 | 5640 | 20 | 0.017507 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | B | 20 | 0.017507 | 6.2081e-05
131112 | 2012-09-18 09:15 | 2012-09-18 14:56 | 87 | 338 | 29406 | 87 | 0.091277 | 0.00027005 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | B | 87 | 0.091277 | 0.00027005
131113 | 2012-09-18 11:41 | 2012-09-18 15:35 | 5 | 231 | 1155 | 5 | 0.0035852 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | C | 5 | 0.0035852 | 1.552e-05
131114 | 2012-09-18 09:30 | 2012-09-18 14:29 | 9 | 296 | 2664 | 9 | 0.0082691 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | B | 9 | 0.0082691 | 2.7936e-05
131115 | 2012-09-18 09:00 | 2012-09-18 11:47 | 130 | 164 | 21320 | 130 | 0.066178 | 0.00040352 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | B | 130 | 0.066178 | 0.00040352
131116 | 2012-09-18 16:43 | 2012-09-18 17:33 | 17 | 47 | 799 | 17 | 0.0024801 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | C | 17 | 0.0024801 | 5.2768e-05
131117 | 2012-09-18 10:43 | 2012-09-18 12:12 | 58 | 86 | 4988 | 58 | 0.015483 | 0.00018003 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | C | 58 | 0.015483 | 0.00018003
131119 | 2012-09-18 23:00 | 2012-09-19 02:05 | 143 | 182 | 19237.8919 | 105.7027 | 0.059715 | 0.00044388 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-18 | 2013 | 2013 | 2012-09-18 | B | 105.7027 | 0.059715 | 0.00044388
131120 | 2012-09-15 13:56 | 2012-09-15 19:04 | 286 | 305 | 45652.9545 | 149.6818 | 0.14171 | 0.00088775 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-15 | 2013 | 2013 | 2012-09-15 | C | 149.6818 | 0.14171 | 0.00088775
131121 | 2012-09-19 10:46 | 2012-09-19 11:52 | 68 | 63 | 4284 | 68 | 0.013298 | 0.00021107 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-19 | 2013 | 2013 | 2012-09-19 | C | 68 | 0.013298 | 0.00021107
131124 | 2012-09-19 09:20 | 2012-09-19 14:20 | 19 | 297 | 5643 | 19 | 0.017516 | 5.8977e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-19 | 2013 | 2013 | 2012-09-19 | B | 19 | 0.017516 | 5.8977e-05
131126 | 2012-09-19 09:00 | 2012-09-19 13:25 | 32 | 262 | 8384 | 32 | 0.026024 | 9.9329e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-19 | 2013 | 2013 | 2012-09-19 | B | 32 | 0.026024 | 9.9329e-05
131127 | 2012-09-19 09:00 | 2012-09-19 14:10 | 54 | 307 | 16578 | 54 | 0.051459 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-19 | 2013 | 2013 | 2012-09-19 | B | 54 | 0.051459 | 0.00016762
131129 | 2012-09-19 08:30 | 2012-09-19 15:39 | 342 | 426 | 62374.7413 | 146.4196 | 0.19361 | 0.0010616 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-19 | 2013 | 2013 | 2012-09-19 | B | 146.4196 | 0.19361 | 0.0010616
131132 | 2012-09-20 08:45 | 2012-09-20 15:10 | 59 | 382 | 22538 | 59 | 0.069959 | 0.00018314 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 59 | 0.069959 | 0.00018314
131133 | 2012-09-20 09:15 | 2012-09-20 15:30 | 64 | 372 | 23808 | 64 | 0.073901 | 0.00019866 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 64 | 0.073901 | 0.00019866
131134 | 2012-09-20 08:30 | 2012-09-20 15:50 | 12 | 437 | 5244 | 12 | 0.016278 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 12 | 0.016278 | 3.7248e-05
131139 | 2012-09-20 14:38 | 2012-09-20 17:46 | 132 | 185 | 24420 | 132 | 0.0758 | 0.00040973 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | C | 132 | 0.0758 | 0.00040973
131140 | 2012-09-20 09:00 | 2012-09-20 14:50 | 54 | 347 | 18738 | 54 | 0.058163 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 54 | 0.058163 | 0.00016762
131141 | 2012-09-20 09:06 | 2012-09-20 14:17 | 38 | 308 | 11704 | 38 | 0.03633 | 0.00011795 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 38 | 0.03633 | 0.00011795
131143 | 2012-09-20 08:32 | 2012-09-20 16:34 | 133 | 479 | 63707 | 133 | 0.19775 | 0.00041284 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | B | 133 | 0.19775 | 0.00041284
131144 | 2012-09-20 16:53 | 2012-09-21 10:26 | 485 | 1050 | 58482.906 | 55.698 | 0.18153 | 0.0015055 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-20 | 2013 | 2013 | 2012-09-20 | C | 55.698 | 0.18153 | 0.0015055
131148 | 2012-09-21 11:31 | 2012-09-21 12:34 | 858 | 60 | 51480 | 858 | 0.1598 | 0.0026633 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | C | 858 | 0.1598 | 0.0026633
131150 | 2012-09-21 09:29 | 2012-09-21 14:18 | 4 | 286 | 1144 | 4 | 0.003551 | 1.2416e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | B | 4 | 0.003551 | 1.2416e-05
131152 | 2012-09-21 08:30 | 2012-09-21 14:16 | 56 | 343 | 19208 | 56 | 0.059622 | 0.00017383 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | B | 56 | 0.059622 | 0.00017383
131153 | 2012-09-21 09:03 | 2012-09-21 14:38 | 123 | 332 | 10145.3254 | 30.5582 | 0.031491 | 0.0003818 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | C | 30.5582 | 0.031491 | 0.0003818
131154 | 2012-09-21 08:12 | 2012-09-21 09:04 | 90 | 49 | 4410 | 90 | 0.013689 | 0.00027936 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | C | 90 | 0.013689 | 0.00027936
131156 | 2012-09-21 08:45 | 2012-09-21 14:45 | 2 | 357 | 714 | 2 | 0.0022163 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | B | 2 | 0.0022163 | 6.2081e-06
131157 | 2012-09-21 19:30 | 2012-09-21 20:58 | 161 | 85 | 13685 | 161 | 0.042479 | 0.00049975 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-21 | 2013 | 2013 | 2012-09-21 | C | 161 | 0.042479 | 0.00049975
131159 | 2012-09-22 11:28 | 2012-09-22 11:49 | 1 | 18 | 18 | 1 | 5.5873e-05 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-22 | 2013 | 2013 | 2012-09-22 | B | 1 | 5.5873e-05 | 3.104e-06
131162 | 2012-09-23 04:00 | 2012-09-23 05:08 | 200 | 65 | 13000 | 200 | 0.040352 | 0.00062081 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-23 | 2013 | 2013 | 2012-09-23 | B | 200 | 0.040352 | 0.00062081
131163 | 2012-09-23 20:34 | 2012-09-23 21:40 | 89 | 63 | 5607 | 89 | 0.017404 | 0.00027626 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-23 | 2013 | 2013 | 2012-09-23 | C | 89 | 0.017404 | 0.00027626
131164 | 2012-09-16 04:07 | 2012-09-16 05:18 | 200 | 68 | 13600 | 200 | 0.042215 | 0.00062081 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-16 | 2013 | 2013 | 2012-09-16 | B | 200 | 0.042215 | 0.00062081
131166 | 2012-09-24 11:16 | 2012-09-24 11:51 | 38 | 32 | 1216 | 38 | 0.0037745 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | C | 38 | 0.0037745 | 0.00011795
131167 | 2012-09-24 08:30 | 2012-09-24 10:25 | 3 | 112 | 336 | 3 | 0.001043 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | B | 3 | 0.001043 | 9.3121e-06
131168 | 2012-09-24 10:19 | 2012-09-24 12:55 | 16 | 153 | 2448 | 16 | 0.0075987 | 4.9664e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | C | 16 | 0.0075987 | 4.9664e-05
131169 | 2012-09-24 08:45 | 2012-09-24 13:17 | 3 | 269 | 807 | 3 | 0.002505 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | B | 3 | 0.002505 | 9.3121e-06
131170 | 2012-09-24 11:08 | 2012-09-24 12:25 | 5 | 74 | 370 | 5 | 0.0011485 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | C | 5 | 0.0011485 | 1.552e-05
131171 | 2012-09-24 12:50 | 2012-09-24 14:05 | 1 | 72 | 72 | 1 | 0.00022349 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | B | 1 | 0.00022349 | 3.104e-06
131172 | 2012-09-24 09:45 | 2012-09-24 15:05 | 165 | 317 | 52305 | 165 | 0.16236 | 0.00051216 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | B | 165 | 0.16236 | 0.00051216
131177 | 2012-09-24 09:00 | 2012-09-24 15:23 | 10 | 380 | 3800 | 10 | 0.011795 | 3.104e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | B | 10 | 0.011795 | 3.104e-05
131178 | 2012-09-24 11:40 | 2012-09-24 11:44 | 1393 | 1 | 1393 | 1393 | 0.0043239 | 0.0043239 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-09-24 | 2013 | 2013 | 2012-09-24 | C | 1393 | 0.0043239 | 0.0043239
131180 | 2012-09-25 08:45 | 2012-09-25 11:08 | 28 | 140 | 3920 | 28 | 0.012168 | 8.6913e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | B | 28 | 0.012168 | 8.6913e-05
131183 | 2012-09-25 09:00 | 2012-09-25 12:26 | 11 | 203 | 2233 | 11 | 0.0069313 | 3.4144e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | B | 11 | 0.0069313 | 3.4144e-05
131186 | 2012-09-25 10:45 | 2012-09-25 12:50 | 6 | 122 | 732 | 6 | 0.0022721 | 1.8624e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | C | 6 | 0.0022721 | 1.8624e-05
131196 | 2012-09-25 09:00 | 2012-09-25 15:20 | 9 | 377 | 3393 | 9 | 0.010532 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | B | 9 | 0.010532 | 2.7936e-05
131198 | 2012-09-25 08:30 | 2012-09-25 15:01 | 12 | 388 | 4656 | 12 | 0.014452 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | B | 12 | 0.014452 | 3.7248e-05
131199 | 2012-09-25 08:41 | 2012-09-25 12:30 | 497 | 226 | 30754.7511 | 136.083 | 0.095464 | 0.0015427 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | C | 136.083 | 0.095464 | 0.0015427
131200 | 2012-09-25 20:15 | 2012-09-25 21:00 | 238 | 42 | 7838.1333 | 186.6222 | 0.02433 | 0.00073876 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | C | 186.6222 | 0.02433 | 0.00073876
131201 | 2012-09-25 22:00 | 2012-09-26 01:49 | 117 | 226 | 26442 | 117 | 0.082077 | 0.00036317 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | B | 117 | 0.082077 | 0.00036317
131203 | 2012-09-25 21:37 | 2012-09-25 23:04 | 1 | 84 | 84 | 1 | 0.00026074 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-25 | 2013 | 2013 | 2012-09-25 | C | 1 | 0.00026074 | 3.104e-06
131204 | 2012-09-26 11:36 | 2012-09-26 11:50 | 51 | 11 | 561 | 51 | 0.0017414 | 0.00015831 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | C | 51 | 0.0017414 | 0.00015831
131206 | 2012-09-26 09:06 | 2012-09-26 12:21 | 55 | 192 | 10560 | 55 | 0.032779 | 0.00017072 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 55 | 0.032779 | 0.00017072
131207 | 2012-09-26 10:10 | 2012-09-26 13:00 | 779 | 167 | 52696.3588 | 315.5471 | 0.16357 | 0.002418 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | C | 315.5471 | 0.16357 | 0.002418
131208 | 2012-09-26 08:30 | 2012-09-26 09:56 | 3 | 83 | 249 | 3 | 0.0007729 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 3 | 0.0007729 | 9.3121e-06
131209 | 2012-09-26 11:00 | 2012-09-26 12:15 | 2 | 72 | 144 | 2 | 0.00044698 | 6.2081e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 2 | 0.00044698 | 6.2081e-06
131211 | 2012-09-26 13:08 | 2012-09-26 14:00 | 18 | 49 | 882 | 18 | 0.0027378 | 5.5873e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | C | 18 | 0.0027378 | 5.5873e-05
131213 | 2012-09-26 09:30 | 2012-09-26 13:48 | 29 | 255 | 7395 | 29 | 0.022954 | 9.0017e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 29 | 0.022954 | 9.0017e-05
131214 | 2012-09-26 13:30 | 2012-09-26 15:25 | 1 | 112 | 112 | 1 | 0.00034765 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 1 | 0.00034765 | 3.104e-06
131215 | 2012-09-26 09:00 | 2012-09-26 15:45 | 87 | 402 | 34974 | 87 | 0.10856 | 0.00027005 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-26 | 2013 | 2013 | 2012-09-26 | B | 87 | 0.10856 | 0.00027005
131220 | 2012-09-27 06:50 | 2012-09-27 07:45 | 27 | 52 | 1404 | 27 | 0.0043581 | 8.3809e-05 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | C | 27 | 0.0043581 | 8.3809e-05
131223 | 2012-09-27 09:16 | 2012-09-27 11:30 | 1 | 131 | 131 | 1 | 0.00040663 | 3.104e-06 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | C | 1 | 0.00040663 | 3.104e-06
131231 | 2012-09-27 13:55 | 2012-09-27 15:23 | 22 | 85 | 1870 | 22 | 0.0058045 | 6.8289e-05 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | C | 22 | 0.0058045 | 6.8289e-05
131232 | 2012-09-22 11:00 | 2012-09-22 15:08 | 16 | 245 | 3920 | 16 | 0.012168 | 4.9664e-05 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-22 | 2013 | 2013 | 2012-09-22 | C | 16 | 0.012168 | 4.9664e-05
131233 | 2012-09-27 08:30 | 2012-09-27 15:46 | 20 | 433 | 8660 | 20 | 0.026881 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | B | 20 | 0.026881 | 6.2081e-05
131234 | 2012-09-27 09:00 | 2012-09-27 15:15 | 115 | 372 | 42780 | 115 | 0.13279 | 0.00035696 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | B | 115 | 0.13279 | 0.00035696
131236 | 2012-09-27 20:18 | 2012-09-27 21:52 | 15 | 91 | 1365 | 15 | 0.004237 | 4.656e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | C | 15 | 0.004237 | 4.656e-05
131237 | 2012-09-28 08:23 | 2012-09-28 14:32 | 868 | 366 | 21625.7398 | 59.0867 | 0.067127 | 0.0026943 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 59.0867 | 0.067127 | 0.0026943
131239 | 2012-09-28 08:35 | 2012-09-28 08:42 | 150 | 4 | 600 | 150 | 0.0018624 | 0.0004656 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 150 | 0.0018624 | 0.0004656
131240 | 2012-09-28 08:08 | 2012-09-28 09:37 | 229 | 86 | 8993.2809 | 104.573 | 0.027915 | 0.00071082 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 104.573 | 0.027915 | 0.00071082
131241 | 2012-09-28 07:23 | 2012-09-28 10:06 | 320 | 160 | 31625.0307 | 197.6564 | 0.098165 | 0.00099329 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 197.6564 | 0.098165 | 0.00099329
131245 | 2012-09-28 10:00 | 2012-09-28 10:25 | 289 | 22 | 6358 | 289 | 0.019735 | 0.00089706 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | B | 289 | 0.019735 | 0.00089706
131246 | 2012-09-28 10:08 | 2012-09-28 13:52 | 165 | 221 | 23313.5268 | 105.4911 | 0.072366 | 0.00051216 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 105.4911 | 0.072366 | 0.00051216
131247 | 2012-09-28 12:00 | 2012-09-28 13:49 | 38 | 106 | 4028 | 38 | 0.012503 | 0.00011795 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | C | 38 | 0.012503 | 0.00011795
131248 | 2012-09-28 09:00 | 2012-09-28 12:50 | 37 | 227 | 8399 | 37 | 0.026071 | 0.00011485 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | B | 37 | 0.026071 | 0.00011485
131249 | 2012-09-28 09:40 | 2012-09-28 15:15 | 14 | 332 | 4648 | 14 | 0.014428 | 4.3456e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-28 | 2013 | 2013 | 2012-09-28 | B | 14 | 0.014428 | 4.3456e-05
131250 | 2012-09-27 08:37 | 2012-09-28 16:15 | 1 | 1895 | 1895 | 1 | 0.0058821 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-27 | 2013 | 2013 | 2012-09-27 | B | 1 | 0.0058821 | 3.104e-06
131255 | 2012-09-29 10:59 | 2012-09-29 11:25 | 601 | 23 | 6820.3846 | 296.5385 | 0.021171 | 0.0018655 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | C | 296.5385 | 0.021171 | 0.0018655
131258 | 2012-09-29 09:45 | 2012-09-29 11:57 | 3 | 129 | 387 | 3 | 0.0012013 | 9.3121e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | B | 3 | 0.0012013 | 9.3121e-06
131259 | 2012-09-29 09:22 | 2012-09-29 13:07 | 7 | 222 | 1554 | 7 | 0.0048237 | 2.1728e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | B | 7 | 0.0048237 | 2.1728e-05
131262 | 2012-09-29 03:04 | 2012-09-29 03:10 | 51 | 3 | 153 | 51 | 0.00047492 | 0.00015831 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | C | 51 | 0.00047492 | 0.00015831
131264 | 2012-09-29 21:51 | 2012-09-29 23:08 | 160 | 74 | 8378.3377 | 113.2208 | 0.026007 | 0.00049664 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | C | 113.2208 | 0.026007 | 0.00049664
131265 | 2012-09-29 23:44 | 2012-09-29 23:59 | 272 | 12 | 3264 | 272 | 0.010132 | 0.0008443 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-09-29 | 2013 | 2013 | 2012-09-29 | C | 272 | 0.010132 | 0.0008443
131268 | 2012-09-30 08:30 | 2012-09-30 11:27 | 139 | 174 | 24186 | 139 | 0.075074 | 0.00043146 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-30 | 2013 | 2013 | 2012-09-30 | B | 139 | 0.075074 | 0.00043146
131269 | 2012-09-30 10:11 | 2012-09-30 12:00 | 143 | 106 | 15158 | 143 | 0.047051 | 0.00044388 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-09-30 | 2013 | 2013 | 2012-09-30 | B | 143 | 0.047051 | 0.00044388
131271 | 2012-10-01 01:51 | 2012-10-01 04:50 | 37 | 176 | 6512 | 37 | 0.020213 | 0.00011485 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 37 | 0.020213 | 0.00011485
131272 | 2012-10-01 09:06 | 2012-10-01 11:34 | 93 | 145 | 13485 | 93 | 0.041858 | 0.00028867 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | B | 93 | 0.041858 | 0.00028867
131273 | 2012-10-01 11:45 | 2012-10-01 11:54 | 208 | 6 | 1248 | 208 | 0.0038738 | 0.00064564 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 208 | 0.0038738 | 0.00064564
131276 | 2012-10-01 10:00 | 2012-10-01 14:30 | 49 | 267 | 13083 | 49 | 0.04061 | 0.0001521 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | B | 49 | 0.04061 | 0.0001521
131277 | 2012-10-01 11:45 | 2012-10-01 11:57 | 698 | 9 | 6282 | 698 | 0.0195 | 0.0021666 | No Power | Unplanned | Class C | HUMAN ELEMENT | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 698 | 0.0195 | 0.0021666
131280 | 2012-10-01 16:19 | 2012-10-01 16:34 | 1364 | 12 | 16368 | 1364 | 0.050807 | 0.0042339 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 1364 | 0.050807 | 0.0042339
131281 | 2012-10-01 20:59 | 2012-10-01 22:17 | 58 | 75 | 4350 | 58 | 0.013503 | 0.00018003 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 58 | 0.013503 | 0.00018003
131282 | 2012-10-01 21:08 | 2012-10-01 23:17 | 568 | 126 | 40646.2326 | 322.5891 | 0.12617 | 0.0017631 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 322.5891 | 0.12617 | 0.0017631
131284 | 2012-10-02 07:14 | 2012-10-02 08:00 | 57 | 43 | 2286.4783 | 53.1739 | 0.0070973 | 0.00017693 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 53.1739 | 0.0070973 | 0.00017693
131285 | 2012-10-02 09:30 | 2012-10-02 12:10 | 2 | 157 | 314 | 2 | 0.00097466 | 6.2081e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 2 | 0.00097466 | 6.2081e-06
131288 | 2012-10-02 08:00 | 2012-10-02 09:21 | 77 | 78 | 5122 | 65.6667 | 0.015899 | 0.00023901 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 65.6667 | 0.015899 | 0.00023901
131290 | 2012-10-02 08:54 | 2012-10-02 15:12 | 39 | 375 | 14625 | 39 | 0.045396 | 0.00012106 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 39 | 0.045396 | 0.00012106
131292 | 2012-10-02 09:00 | 2012-10-02 14:28 | 22 | 325 | 7150 | 22 | 0.022194 | 6.8289e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 22 | 0.022194 | 6.8289e-05
131294 | 2012-10-02 08:52 | 2012-10-02 15:44 | 5 | 409 | 2045 | 5 | 0.0063477 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 5 | 0.0063477 | 1.552e-05
131295 | 2012-10-02 09:35 | 2012-10-02 12:30 | 240 | 172 | 41280 | 240 | 0.12813 | 0.00074497 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 240 | 0.12813 | 0.00074497
131296 | 2012-10-02 08:18 | 2012-10-02 08:45 | 640 | 24 | 15360 | 640 | 0.047678 | 0.0019866 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 640 | 0.047678 | 0.0019866
131297 | 2012-10-02 08:45 | 2012-10-02 14:14 | 76 | 326 | 24776 | 76 | 0.076905 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 76 | 0.076905 | 0.00023591
131298 | 2012-10-02 09:30 | 2012-10-02 14:05 | 365 | 272 | 67313.5709 | 247.4764 | 0.20894 | 0.001133 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 247.4764 | 0.20894 | 0.001133
131301 | 2012-10-02 08:35 | 2012-10-02 15:22 | 61 | 404 | 24644 | 61 | 0.076496 | 0.00018935 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | B | 61 | 0.076496 | 0.00018935
131302 | 2012-10-02 22:59 | 2012-10-02 23:15 | 374 | 13 | 4862 | 374 | 0.015092 | 0.0011609 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 374 | 0.015092 | 0.0011609
131303 | 2012-10-01 13:42 | 2012-10-01 15:49 | 1 | 124 | 124 | 1 | 0.0003849 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-01 | 2013 | 2013 | 2012-10-01 | C | 1 | 0.0003849 | 3.104e-06
131306 | 2012-10-03 09:20 | 2012-10-03 12:25 | 9 | 182 | 1638 | 9 | 0.0050844 | 2.7936e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | B | 9 | 0.0050844 | 2.7936e-05
131307 | 2012-10-03 10:41 | 2012-10-03 10:56 | 905 | 12 | 10860 | 905 | 0.03371 | 0.0028091 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 905 | 0.03371 | 0.0028091
131310 | 2012-10-03 09:57 | 2012-10-03 12:53 | 108 | 173 | 18684 | 108 | 0.057996 | 0.00033524 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | B | 108 | 0.057996 | 0.00033524
131313 | 2012-10-03 09:16 | 2012-10-03 13:26 | 119 | 247 | 29393 | 119 | 0.091237 | 0.00036938 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | B | 119 | 0.091237 | 0.00036938
131314 | 2012-10-03 09:00 | 2012-10-03 12:02 | 135 | 179 | 24165 | 135 | 0.075009 | 0.00041904 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | B | 135 | 0.075009 | 0.00041904
131315 | 2012-10-03 14:30 | 2012-10-03 15:15 | 4 | 42 | 168 | 4 | 0.00052148 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 4 | 0.00052148 | 1.2416e-05
131319 | 2012-10-03 17:25 | 2012-10-03 17:55 | 14 | 27 | 378 | 14 | 0.0011733 | 4.3456e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 14 | 0.0011733 | 4.3456e-05
131320 | 2012-10-02 16:20 | 2012-10-02 23:00 | 4 | 397 | 1588 | 4 | 0.0049292 | 1.2416e-05 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-10-02 | 2013 | 2013 | 2012-10-02 | C | 4 | 0.0049292 | 1.2416e-05
131321 | 2012-10-03 20:00 | 2012-10-03 20:48 | 1 | 45 | 45 | 1 | 0.00013968 | 3.104e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 1 | 0.00013968 | 3.104e-06
131322 | 2012-10-03 21:20 | 2012-10-03 22:13 | 4 | 50 | 200 | 4 | 0.00062081 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 4 | 0.00062081 | 1.2416e-05
131323 | 2012-10-03 22:07 | 2012-10-03 22:50 | 76 | 40 | 3040 | 76 | 0.0094362 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | B | 76 | 0.0094362 | 0.00023591
131324 | 2012-10-03 23:50 | 2012-10-04 05:00 | 551 | 307 | 25178.9516 | 82.0161 | 0.078156 | 0.0017103 | No Power | Unplanned | Class C | FOREIGN INTERFERENCE | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 82.0161 | 0.078156 | 0.0017103
131325 | 2012-10-03 16:28 | 2012-10-03 17:12 | 33 | 41 | 1353 | 33 | 0.0041998 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 33 | 0.0041998 | 0.00010243
131326 | 2012-10-03 17:52 | 2012-10-03 18:16 | 12 | 21 | 252 | 12 | 0.00078222 | 3.7248e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-03 | 2013 | 2013 | 2012-10-03 | C | 12 | 0.00078222 | 3.7248e-05
131329 | 2012-10-04 08:52 | 2012-10-04 09:26 | 561 | 31 | 17391 | 561 | 0.053982 | 0.0017414 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 561 | 0.053982 | 0.0017414
131330 | 2012-10-04 06:30 | 2012-10-04 08:49 | 21 | 136 | 2856 | 21 | 0.0088651 | 6.5185e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 21 | 0.0088651 | 6.5185e-05
131332 | 2012-10-04 11:15 | 2012-10-04 13:05 | 2 | 107 | 214 | 2 | 0.00066426 | 6.2081e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 2 | 0.00066426 | 6.2081e-06
131333 | 2012-10-04 09:15 | 2012-10-04 12:55 | 292 | 217 | 63364 | 292 | 0.19668 | 0.00090638 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 292 | 0.19668 | 0.00090638
131334 | 2012-10-04 11:40 | 2012-10-04 12:49 | 17 | 66 | 1122 | 17 | 0.0034827 | 5.2768e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 17 | 0.0034827 | 5.2768e-05
131335 | 2012-10-04 09:16 | 2012-10-04 12:55 | 119 | 216 | 25704 | 119 | 0.079786 | 0.00036938 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 119 | 0.079786 | 0.00036938
131336 | 2012-10-04 08:30 | 2012-10-04 12:50 | 5 | 257 | 1285 | 5 | 0.0039887 | 1.552e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 5 | 0.0039887 | 1.552e-05
131337 | 2012-10-04 09:15 | 2012-10-04 13:07 | 76 | 229 | 17404 | 76 | 0.054023 | 0.00023591 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 76 | 0.054023 | 0.00023591
131338 | 2012-10-04 12:35 | 2012-10-04 13:53 | 1 | 75 | 75 | 1 | 0.0002328 | 3.104e-06 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 1 | 0.0002328 | 3.104e-06
131339 | 2012-10-04 08:30 | 2012-10-04 14:48 | 20 | 375 | 7500 | 20 | 0.02328 | 6.2081e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 20 | 0.02328 | 6.2081e-05
131340 | 2012-10-04 13:30 | 2012-10-04 15:53 | 4 | 140 | 560 | 4 | 0.0017383 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 4 | 0.0017383 | 1.2416e-05
131341 | 2012-10-04 15:45 | 2012-10-04 17:03 | 45 | 75 | 2355.7692 | 31.4103 | 0.0073124 | 0.00013968 | No Power | Unplanned | Class C | UNKNOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 31.4103 | 0.0073124 | 0.00013968
131342 | 2012-10-04 08:46 | 2012-10-04 16:49 | 5 | 480 | 2400 | 5 | 0.0074497 | 1.552e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 5 | 0.0074497 | 1.552e-05
131343 | 2012-10-04 22:00 | 2012-10-04 22:39 | 132 | 36 | 4752 | 132 | 0.01475 | 0.00040973 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | B | 132 | 0.01475 | 0.00040973
131346 | 2012-10-04 19:27 | 2012-10-04 22:46 | 3 | 196 | 588 | 3 | 0.0018252 | 9.3121e-06 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-04 | 2013 | 2013 | 2012-10-04 | C | 3 | 0.0018252 | 9.3121e-06
131348 | 2012-10-05 12:22 | 2012-10-05 13:20 | 64 | 55 | 3520 | 64 | 0.010926 | 0.00019866 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | C | 64 | 0.010926 | 0.00019866
131349 | 2012-10-05 09:00 | 2012-10-05 15:00 | 12 | 357 | 4284 | 12 | 0.013298 | 3.7248e-05 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | B | 12 | 0.013298 | 3.7248e-05
131350 | 2012-10-05 09:00 | 2012-10-05 17:25 | 54 | 502 | 27108 | 54 | 0.084144 | 0.00016762 | No Power | Planned | Class B | PLANNED SHUTDOWN | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | B | 54 | 0.084144 | 0.00016762
131351 | 2012-10-05 20:08 | 2012-10-05 20:46 | 54 | 35 | 1890 | 54 | 0.0058666 | 0.00016762 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | C | 54 | 0.0058666 | 0.00016762
131352 | 2012-10-05 19:15 | 2012-10-05 20:42 | 3 | 84 | 252 | 3 | 0.00078222 | 9.3121e-06 | No Power | Unplanned | Class C | TREE CONTACTS | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | C | 3 | 0.00078222 | 9.3121e-06
131353 | 2012-10-05 21:07 | 2012-10-05 22:15 | 110 | 65 | 7150 | 110 | 0.022194 | 0.00034144 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | C | 110 | 0.022194 | 0.00034144
131354 | 2012-10-05 15:52 | 2012-10-06 12:00 | 69 | 1205 | 15336.8171 | 12.7276 | 0.047606 | 0.00021418 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-05 | 2013 | 2013 | 2012-10-05 | C | 12.7276 | 0.047606 | 0.00021418
131357 | 2012-10-06 16:02 | 2012-10-06 19:40 | 76 | 215 | 16340 | 76 | 0.05072 | 0.00023591 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 76 | 0.05072 | 0.00023591
131359 | 2012-10-06 21:33 | 2012-10-06 22:44 | 33 | 68 | 2244 | 33 | 0.0069654 | 0.00010243 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 33 | 0.0069654 | 0.00010243
131360 | 2012-10-06 19:45 | 2012-10-06 20:57 | 15 | 69 | 1035 | 15 | 0.0032127 | 4.656e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 15 | 0.0032127 | 4.656e-05
131361 | 2012-10-06 20:06 | 2012-10-06 21:08 | 1084 | 59 | 45964.8065 | 779.0645 | 0.14268 | 0.0033648 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 779.0645 | 0.14268 | 0.0033648
131363 | 2012-10-07 01:32 | 2012-10-07 04:05 | 687 | 150 | 72555.8824 | 483.7059 | 0.22522 | 0.0021325 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-07 | 2013 | 2013 | 2012-10-07 | C | 483.7059 | 0.22522 | 0.0021325
131364 | 2012-10-06 21:26 | 2012-10-07 10:28 | 4 | 779 | 3116 | 4 | 0.0096722 | 1.2416e-05 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 4 | 0.0096722 | 1.2416e-05
131366 | 2012-10-07 11:39 | 2012-10-07 12:34 | 2 | 52 | 104 | 2 | 0.00032282 | 6.2081e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-10-07 | 2013 | 2013 | 2012-10-07 | C | 2 | 0.00032282 | 6.2081e-06
131367 | 2012-10-06 17:00 | 2012-10-06 18:05 | 10 | 62 | 620 | 10 | 0.0019245 | 3.104e-05 | No Power | Unplanned | Class C | ADVERSE WEATHER | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 10 | 0.0019245 | 3.104e-05
131368 | 2012-10-06 14:12 | 2012-10-06 16:57 | 587 | 162 | 31751.0182 | 195.9939 | 0.098556 | 0.0018221 | No Power | Unplanned | Class C | DEFECTIVE EQUIPMENT | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 195.9939 | 0.098556 | 0.0018221
131369 | 2012-10-06 20:50 | 2012-10-07 10:20 | 1 | 807 | 807 | 1 | 0.002505 | 3.104e-06 | No Power | Unplanned | Class C | LIGHTNING | Network (Powerco) | 2012-10-06 | 2013 | 2013 | 2012-10-06 | C | 1 | 0.002505 | 3.104e-06